## Sheet1
Date | Notes | SM | Flow
2017-09-04 12:31 | DOM.PROP. CHECK FOR SAFETY BEEN ADVISED BY **** THAT THE FUSE CARRIERS NEED REPLACING AS VERY OLD. CANT HAVE SMRT MTR FITTED OR HAVE CONSUMER UNIT FITTED UNTIL THIS IS DONE | Smart meter fitted later that month | No flow received
2017-10-18 09:01 | CUSTOMER HAD MOP AT PROPERTY YESTERDAY TO FIT SMART METER - MOP ADVISED THAT A DIFFERENT FUSE SIZE WAS REQUIRED - CUST IS ELDERLY AND NOT UNDERSTANDING WHAT IS HAPPENING | Smart meter fitted later that month | B11 code received the same day
2017-08-10 15:20 | CHECK FOR SAFETY. CUSTOMER HAD **** ROUND TO FIT SMRT MTR COULDN'T FIT MTR AS FUSE IS WELDED INTO THE FUSE CARRIER. MOP HAS ADVISED THE CONS THAT THE FUSE CARRIER WAS WARM. | Smart meter fitted later that month | No flow received
2017-10-12 14:52 | HAD A MOP OUT FROM SUPPLIER **** TODAY TO CHANGE TO A SMART METER AND THE MOP HAS REFUSED TO DO THE WORKS BECAUSE HE HAS SAID THE METAL CLAD CUT OUT IS OUTDATED AND NEEDS UPDATING AND THERE IS SIGNS OF ASPESTOS IN CUT OUT - CUSTOMERS FATHER H | Smart meter fitted later that month | B11 code received 24-10-17
2017-06-07 11:37 | **** CAME OUT LATE LAST NIGHT AND TOLD CUSTOMER TO CALL US OUT FOR AN EMERGENCY APPOINTMENT HE GAVE NO INFORMATION OTHER THAN THAT HE COULD NOT REMOVE THE FUSE TO CHANGE THE METER | Smart meter fitted later that month | No flow received
2017-05-12 08:25 | DOM PROP - MOP FROM **** BEEN OUT AND INFORMED MAIN FUSE WELDED TO CUSTOMER NOT CALLED IN VIA MOP - HE INFORMED CUSTOMER TO CALL INTO US | Smart meter fitted later that month | No flow received
2017-06-27 19:27 | **** FROM **** REPORTS ONE OF THEIR MOPS ATTENDED THIS AFTERNOON TO DO A METER EXCHANGE - COULDN'T DO IT BECAUSE THE FUSE WAS WELDED IN & WIRES WERE MELTED - HAS NOT RANG IT THROUGH AS A JOB - CUSTOMERS CONCERNED AS HUSBAND USES OXYGEN CYLINDER | Smart meter fitted early July | No flow received
2017-09-27 18:12 | CONS ADV THERE IS ASBESTOS IN THE FUSE CARRIER AS **** HAD BEEN TO THE PROP IN JAN AND CONFIRMED | Smart meter fitted early October | No flow received
2017-07-19 14:43 | **** MOP BEEN TO PROP TO INSTALL SMART METER BUT SAYS C/O IS LOOSE | Smart meter fitted later that month | Flow received 19-7-17
2017-08-20 18:41 | COMM PROP - CUST REPORTS RECENTLY TAKEN OVER PROPERTY AND HAS HAD SUPPLIER OUT DUE TO NO METER - SUPPLIER FOUND WET BITUMEN LEAK FROM MAINS INCOMING - WIRES HANGING OUT - UNSAFE - BACKBOARD IS HANGING OFF - 3 PHASE SUPPLY TO BE INSTALLED - SLIGHT BURN SME | Smart meter fitted later that month | No flow received
2017-07-14 17:25 | CUSTOMER REPORTING BITUMEN LEAK **** MOP ENGINEER TOLD HER COULD NOT FIT SM METER DUE TO THIS BLACK STUFF.. BEEN LEFT WITH NO FURTHER INFO.. | Smart meter fitted following month | B01 received 6-7-17
2017-08-30 14:06 | CUSTOMER HAS HAD THE SUPPLIER OUT WHO ADVISED THAT MAIN FUSE NEEDS CHANGING REALLY OLD METAL ONE | Smart meter fitted following month | C code received 10-7-17
2017-07-27 10:36 | **** HAVE BEEN OUT TO FIT SMART METER UNABLE TO FIT AS MAIN FUSE AND CUT OUT ARE REALLY OLD AND NEED UPGRADING BEFORE THEY CAN FIT THE NEW METER ADVISED THE CUSTOMER TO CALL OURSELVES TO GET SOMEONE OUT | Smart meter fitted following month | No flow received
2017-08-03 14:52 | DOM PROP VOID OUTSIDE VIEWER **** MOP REPORTS CUT OUT LOOSE ON BACK BOARD ALL EQUIPMENT FOR FLAT AND NEWSAGENT ALL SAFE CAN WE CHECK | Smart meter fitted later that month | No flow received
2017-05-03 14:06 | AS PER **** MOP CUST REPORTING THAT SMART METERS COULDN'T BE FITTED AS HE COULDN'T TOUCH THE FUSE-CUST UNSURE WHAT PROBLEM IS | Smart meter fitted later that month | B11 received 3-5-17
2017-07-15 15:43 | CUST CALLING AS SUPPLIER HAS BEEN OUT TO FIT SMART METERS BUT COULD NOT REMOVE NEUTRAL COVER - NOTE LEFT FOR CUST SO HE HAS NO FURTHER INFORMATION | Smart meter fitted following month | C flow received 14-7
2017-09-20 11:41 | CUST HAD **** TO FIT SMART METER BUT COULDN'T COMPLETE IT DUE TO ASBESTOS IN THE CUT OUT | Smart meter fitted following month | C received 30-5-17
2017-09-07 19:43 | DOM PROP - CUSTOMER CALLED STATING SHE HAD MOP OUT TO FIT SMART METER WHO STATED THAT HE COULD NOT FIT DUE TO PORCELAIN FUSE CARRIER HAVING HAIR LINE CRACK - UNABLE TO REMOVE FUSE | Smart meter fitted later that month | No flow received
2017-06-08 11:44 | CUST - REQ CHECK FOR SAFETY AS PER **** ENGINEER. ENGINEER HAS LEFT BUT SAID IT WASN'T SAFE TO WORK ON BACKBOARD HANGING OFF THE WALL | Smart meter fitted later that month | No flow received
2017-06-27 07:21 | SUPPLIER ATTENDED PROPERTY TO CHANGE METER BUT REFUSED TO DO WORK AS THEY SAID C/OUT WAS IN A DANGEROUS STATE | Smart meter fitted following month | C code received March 17
2017-08-24 10:49 | CUST BEEN ADVISED BY SUPPLIER VERY OLD C/O AND THEY CAN NOT FIT NEW METER UNTIL ENW ATTENDED | Smart meter fitted following month | C code received Nov 16
2017-07-11 19:09 | CUST BEEN ADVISED BY **** WHO WERE DUETO INSTALL SMART METER ISSUE WITH MAIN FUSE SO CAN NOT BE COMPLETED - ENWL engineer reported fuse welded in | Smart meter fitted following month | No flow received
2017-06-19 16:15 | BACK BOARD IS ROTTING AWAY AND CUSTOMER HAS HAD MOP ROUND AND THE MOP SAID THE METER IS READY FOR FALLING OFF//DOM PROP//NO SOB//NO ARC OR SPARK//METER WAS REPLACED A YEAR AGO DUE TO WATER DAMAGE | Smart meter fitted following month | B02 flow received 22-6-17
2017-05-21 09:02 | **** REPORTING ON BEHALF OF THE CUSTOMER THAT BACK BOARD IS LOOSE AND METER IS HANGING OFF THE WALL HE SAYS IT APPEARS TO HAVE PERISHED NOT SEEN ANY SPARKING OR SMELT ANY BURNS TOLD CUSTOMER TO STAY AWAY FROM THE AREA | Smart meter fitted following month | No flow received
2017-04-24 18:30 | DOM PROP -*** FROM **** WITH REGARDS TO A CODE - UNABLE TO GIVE A CODE BUT STATES THIS IS A FUSED NEUTRAL - SMART METER WORKS - NOT FITTED | Smart meter fitted following month | No flow received
2017-08-14 09:33 | **** METER OP TOLD CUSTOMER COULD NOT FIT METER AS IT IS UNSAFE AND HE WOULD GET AN ELECTRIC SHOCK.. CUSTOMER UNAWARE WHAT THE ACTUAL PROBLEM IS AS HE NEVER STATED ANY FURTHER DETAILS. | Smart meter fitted following month | No flow received
2017-06-06 11:11 | DOM: NO VUN:CONS ADVISED **** GOING TO CHANGE SMART METER BUT COULD NOT: SCREWS ON THE CUT/OUT: ARE SHREDDED IN THE CUT/OUT UNABLE TO REMOVE: | Smart meter fitted following month | No flow received
2017-08-17 15:47 | CUSTOMER REPORTING BITUMEN LEAK DOM PROP - NO SOB - ADVISE TO TURN SUPPLY OFF - SMART METER WAS BEING FITTED BUT THE ENGINEER SAID HE CANT DO IT WITH THE WAY IT WAS IN | Smart meter fitted Oct 2017 | C02 received 19-7-17
2017-05-09 19:00 | AS PER CUSTOMERS FATHER THERE IS A VERY BAD BITUMEN LEAK-DOM-CUST SAYS IT IS LEAKING A LOT-**** HAVE BEEN AND TOLD CUST ITS A FIRE RISK | Smart meter fitted July 2017 | No flow received
2017-05-04 17:00 | *DOM PROP* CHECK FOR SAFETY AS **** HAVE ATTENDED AND ADVISED SOMETHING IS WRONG WITH A NEUTRAL PART AND DIDN'T PROVIDE ANY FURTHER EXPLANATION | Smart meter fitted August 2017 | B11 and B07 received 28-4-17