| Title: | Deliverable 5. Second Year Final Report Stage 2 - REACT Project |  |
| --- | --- | --- |
| Synopsis: | This document is the final report on the REACT project. A framework is proposed to assess future reactive demand at any GSP and future trends in reactive demand are presented for GSPs across all DNOs. An initial techno-economical assessment using shunt reactors is also presented and the considerations for future studies are discussed. |  |
| Document ID: | UoM-REACT_Project_Deliverable5_v04 |  |
| Date: | 11th August 2015 |  |
| Prepared For: | REACT Project Members National Grid, ENWL, NP, UKPN, WPD, SSE, and SPEN |  |
| Prepared By: | Dr Christos Kaloudas The University of Manchester Sackville Street, Manchester M13 9PL, UK |  |
| Revised By: | Dr Luis (Nando) Ochoa, The University of Manchester Shanti Majithia, Energy and Climate Advisory Services Benjamin Marshall, National Grid |  |
| Contacts: | Dr Luis(Nando) Ochoa +44 (0)161 306 4819 luis.ochoa@manchester.ac.uk Dr Christos Kaloudas +44 (0)161 306 4767 christos.kaloudas@manchester.ac.uk |  |

# Executive Summary

This report corresponds to Deliverable 5 “Second Year Final Report Stage 2” part of the “Reactive Power Exchange Assessment and Characterisation (REACT)” Project funded by National Grid and the six Distribution Network Operators (DNOs) in Great Britain: Electricity North West Limited (ENWL), Northern Powergrid (NP), Scottish Power Energy Networks (SPEN), Scottish and Southern Energy (SSE), UK Power Networks (UKPN) and Western Power Distribution (WPD). This project is financially managed by Energy Networks Association (ENA).

The REACT Project has been established to understand the reasons behind the decline in reactive power demand as seen by National Grid during minimum load. This will allow DNOs and National Grid establishing future trends in the reactive power exchanges at Grid Supply Points (GSPs) and adopt the most cost-effective actions as well as responsibilities for ongoing data provision, planning, design, and operational management in this area.

In particular, this report presents:

- the proposed framework and the corresponding methodology that can be used by any DNO to assess future Q demand at any of their GSPs;

- the results of the scenario-based assessment of future Q demand at GSPs across all DNOs for previously examined (ENWL, NP, SPEN, WPD) and new (SSE and UKPN) cases;

- an initial techno-economical assessment using the installation of shunt reactors at GSPs and primary substations; and,

- considerations for future studies aimed at enhancing the trends in Q demand as well as investigating distribution-based solutions.

In this final report of the REACT project a framework that consists of 4 stages is proposed to DNOs to allow a scenario-based assessment of future Q demand at any of their GSPs. The proposed approach and the corresponding methodologies are described in this report and can be followed by any DNO using their available network and monitoring data, from the GSP to primary substations.

The assessment of future Q demand for the different scenarios of the proposed framework is presented for GSPs across all DNOs. More specifically, results are presented for previously examined cases (GSPs of ENWL, NP, SPEN, WPD) and new cases (GSPs of SSE and UKPN) covering all DNOs. Results, although limited to seven GSPs, show that the declining demand trends at primary substations is the major contributor to the overall decline of Q demand during minimum load. The nationwide trends in reactive demand (analysis on 5 GSPs with available 2013 data) show that in a 5 years horizon the Q exports to transmission are expected to increase, depending on the scenario, by 55 to 120% with respect to their 2013 level.

An initial techno-economical assessment using shunt reactors is also presented. The investigation considers aspects regarding the sizing of shunt reactors at primary substations and the corresponding effects on energy losses. It also focuses on the amount and total cost of shunt reactors needed to be installed at GSPs to meet the requirements of the European Demand Connection Code (EDCC). Results using the improved network models (2 GSPs with Q exports in 2013) show that if shunt reactors are installed at primary substations instead of GSPs, slightly less VArs would be required (up to 3%). This, however, would also result in a small increase in daily energy losses: up to 4% with constant use of reactors and up to 0.9% if operated only during the critical hours. In terms of cost, an initial estimation (assuming £45k/MVAr) to tackle the VAr exports of each of the top 60 critical GSPs in Great Britain in a 5 year horizon suggests £213 to £295 millions, depending on the nationwide trend.

Finally, considerations for future work are presented. These include the enhancement of the assessment of trends in Q demand by analysing more networks and extending the analyses downstream primary substations. It is also highlighted that future work should focus on distribution-based solutions if DNOs are to meet the requirements of the EDCC (or agreed specifications with National Grid) to limit VAr exports to transmission.

Table of Contents

Executive Summary	2

1	Introduction	4

1.1	Deliverable 5 “Second Year Final Report Stage 2”	4

1.2	Literature Review Update: Recent Studies in Europe	5

2	Framework for the Assessment of Future Trends	6

2.1	Proposed Framework	6

2.2	Methodology	7

2.2.1	Stage 1: Historic Demand Trends	7

2.2.2	Stage 2: Improved/Validated Network Modelling	8

2.2.3	Stage 3: Network Planning	8

2.2.4	Stage 4: Future Reactive Power Demand	9

2.3	Summary	10

3	Future Reactive Power Demand	11

3.1	Summary of Previously Presented Cases	11

3.2	New Cases	13

3.2.1	City Road GSP (UKPN)	13

3.2.2	Lovedean GSP (SSE)	14

3.3	Nationwide Trends in Q Demand	15

3.4	Summary	17

4	Techno-Economical Assessment Using Shunt Reactors	18

4.1	Installation of Shunt Reactors at Primary Substations	18

4.1.1	Relationship of VArs at the GSP and Primary Substations	18

4.1.2	Sizing of Shunt Reactors	19

4.1.3	Effects on Energy Losses	20

4.2	Cost Estimation for the Top 60 Critical GSPs in Great Britain	22

4.3	Summary	23

5	Considerations for Future Work	24

6	Conclusions	25

7	References	27

8	Appendices	28

8.1	Appendix A – Production of improved and semi-improved network models	28

8.1.1	City Road GSP (UKPN)	28

8.1.2	Lovedean GSP (SSE)	29

8.2	Appendix B: Line Parameters of the Improved Network Models	31

# Introduction

This report corresponds to Deliverable 5 “Second Year Final Report Stage 2” part of the “Reactive Power Exchange Assessment and Characterisation (REACT)” Project funded by National Grid and the six Distribution Network Operators (DNOs) in Great Britain: Electricity North West Limited (ENWL), Northern Powergrid (NP), Scottish Power Energy Networks (SPEN), Scottish and Southern Energy (SSE), UK Power Networks (UKPN) and Western Power Distribution (WPD). This project is financially managed by Energy Networks Association (ENA).

The REACT Project has been established to understand the reasons behind the decline in reactive power demand as seen by National Grid during minimum load. This will allow DNOs and National Grid establishing future trends in the reactive power exchanges at Grid Supply Points (GSPs) and adopt the most cost-effective actions as well as responsibilities for ongoing data provision, planning, design, and operational management in this area.

The understanding of these trends is also of importance to Distribution Network Operators (DNOs) as they also are seeing real voltage containment challenges within their networks with the additional technical challenges of complying with the forthcoming European Demand Connection Code [1] which limits the exchanges of reactive power between transmission and distribution operationally and requires new distribution networks to be designed to not export reactive power at the transmission/distribution interface for loadings up to the 25% of the peak MW load at that interface.

## Deliverable 5 “Second Year Final Report Stage 2”

Deliverable 5 “Second Year Six Final Report Stage 2” presents:

- A literature update regarding recent research work in European countries that focus on transmission-distribution interactions deriving from Q demand during periods of minimum load;

- the proposed framework and the corresponding methodology that can be used by any DNO to assess future Q demand at any of their GSPs;

- the results of the scenario-based assessment of future Q demand at GSPs across all DNOs for previously examined (ENWL, NP, SPEN, WPD) and new (SSE and UKPN) cases;

- an initial techno-economical assessment using the installation of shunt reactors at GSPs and primary substations; and,

- considerations for future studies aimed at enhancing the trends in Q demand as well as investigating distribution-based solutions.

In this final report of the REACT project, an update on the literature review from the first report of Deliverable 1 (March 2014) [2] is presented in subsection 1.2. Although most of the work still focuses on the operational and market perspectives, there are some initial studies within 2015 in other European countries regarding transmission-distribution Q exchanges during periods of minimum load.

Section 2 proposes a framework that can be used by DNOs to assess future Q demand at any of their GSPs during periods of minimum load. The described approach consists of 4 stages and can be carried out using original DNO network and monitoring data (from GSPs to primary substations) together with information related to future demand/generation scenarios and network changes from National Grid and DNO network planners.

In Section 3 all results of the scenario-based assessment of future Q demand are presented for the seven GSPs analysed. Apart from the previously examined cases (GSPs of ENWL, NP, SPEN, WPD [3]), future Q demand during periods of minimum load has been also assessed for new cases (GSPs of SSE and UKPN). The new cases include the improved model (validated for multiple days) of City Road (UKPN) and the semi-improved (mimicking GSP behaviour for a single day) network model of Lovedean (SSE). Using the results of the scenario-based assessment of future Q demand on 5 GSPs with available 2013 data (GSPs of ENWL, NP, SSE, WPD, UKPN) the nationwide trends are assessed. The corresponding limitations are also discussed.

In Section 4 an initial investigation on technical and economic aspects using the installation of shunt reactors is carried out to limit Q exports to transmission during periods of minimum load. First, the analysis on 2 critical GSPs (Norton-NP and Kearsley-ENWL) focuses on the sizing of shunt reactors at primary substations and the corresponding effects on energy losses so as to compare the benefits from GSP installations. Next, using the derived nationwide trends in Q demand (Section 3), an initial cost estimation of the required volume of shunt reactors to tackle the VAr exports of each of the 336 GSPs in Great Britain in a 5 year horizon is carried out.

In Section 5 considerations for future work are presented. The suggested studies include the enhancement of the assessment of trends in Q demand by analysing more networks but also extending analysis downstream primary substations, i.e., modelling –to some extent– HV and LV networks. Additionally, it is suggested that future work should focus on distribution-based solution (e.g., investigating alternatives that do not require the installation of new assets) if DNOs are to meet the requirements of the EDCC (or agreed specifications with National Grid) to limit VAr exports to transmission.

Finally, conclusions are drawn in Section 6.

## Literature Review Update: Recent Studies in Europe

The literature review in the first report of REACT project (Deliverable 1 - March 2014) [2] revealed that most of the studies until 2014 had focused on the operational and market perspectives (e.g., control of distribution voltages [4]-[6], provision of services from distribution to transmission [7]), rather than on transmission-distribution interactions during periods of minimum load. There was very limited documentation investigating the decline in reactive power demand of distribution networks, i.e., at the transmission-distribution interfaces.

More recently, mainly in 2015, initial studies have emerged in other European countries regarding transmission-distribution interactions during periods of minimum load. A research work carried out for ERDF in France [8] highlights that reactive power demand in French primary substations has been declining during periods of minimum load. However, there are no historic trends presented in this work. Other works from Germany [9]-[10] focus on distribution-based solutions to absorb VArs during periods of minimum load. It is noteworthy that the German Transmission System Operator aims at limiting reactive power imports and exports at the interfaces with distribution during minimum demand. A work from Italy [11] also highlights forthcoming limitations to DNOs regarding VAr exports to transmission and the need to consider this objective in operational planning of distribution networks.

It should be also noted that in major conferences in the USA, such as the IEEE Power & Energy Society General Meeting 2015 (where [12] was presented to disseminate the studies of the REACT project), most studies from outside Europe do not investigate the transmission-distribution reactive exchanges during periods of minimum load.

# Framework for the Assessment of Future Trends

National Grid (and TSOs in general) traditionally consider the historic and future trends of P and Q demand at GSPs without modelling the actual distribution networks. Although declining trends in Q demand have been identified in different GSPs of all DNOs, the extraction of empirical rules that could allow DNOs and National Grid to assess future Q demand at GSPs without modelling the actual networks could lead to results that do not take into account the effects from:

- the differences in topologies (e.g., SPEN networks are meshed);

- the differences from the total line lengths per voltage level from 132 to 33kV;

- the different loadings per line that determine the corresponding Q gains;

- the differences in the types of lines (e.g., City Road - UKPN is 100% cables whereas other networks have 50+% of overhead lines); and,

- the interactions of demand characteristics with the networks (e.g., from North to South, urban and rural networks).

This section first proposes a framework that consists of 4 stages and can be used by any DNO to assess the future Q demand at any of their GSPs during periods of minimum load. Next, the methodology for each of these 4 stages is described. Processes presented in the previous reports of Deliverables 1 to 4 have been embedded in the proposed approach, allowing DNOs to use their original historic monitoring and network data (from GSP to primary substations) together with TSO/DNO network planning information to assess future Q demand at GSPs.

## Proposed Framework

The proposed 4-stage framework is shown in Fig. 1. Monitoring data (e.g., half-hourly) for the aggregated P and Q demand of primary substations are seasonally analysed in Stage 1 to assess daily minimum P and corresponding Q/P ratios during minimum load and extract the corresponding trends.

In Stage 2, network and monitoring data are used to improve the original DNO network models. As mentioned in the report of Deliverable 3 [13], original DNO models traditionally focus on periods of peak demand, and hence do not cater for the Q gains from cables and overhead lines. Thus, improved network models are needed to mimic the actual behaviour of transmission-distribution interfaces in time-series simulations during periods of minimum load.

In Stage 3, information from TSO and DNO network planners regarding scheduled/future network, distributed generation (DG) and demand changes are gathered and considered to cater for their effects on the overall Q demand of the examined distribution networks.

The assessment of future Q demand during minimum load at the examined GSPs is carried out in Stage 4 using multiple scenarios. These scenarios are defined taking into account future uncertainties regarding financial affordability and policies supporting sustainability.

The following subsection describes the methodology for each of the 4 stages of the proposed framework to assess future Q demand at GSPs during periods of minimum load.

The proposed framework to assess future Q demand at GSPs during periods of minimum load.

## Methodology

The methodology that needs to be followed for each of the 4 stages of the proposed framework of Fig. 1 is presented in this subsection. It should be noted that the proposed approach is flexible and can be adapted to cater for the analysis of other factors that have not been considered in the REACT project (e.g., significant penetrations of wind generation or CHPs).

### Stage 1: Historic Demand Trends

Primary substations are typically the last points of real-time monitoring of demand in distribution networks, and hence of time-series historic data (although stored with longer sampling intervals). This data is crucial in the proposed framework as it allows validating upstream network models and capturing the aggregated demand behaviour downstream primary substations, i.e., residential, commercial and industrial loads, DG, and network changes.

To extract the historic demand trend for a given GSP, the daily minimum aggregated P demand, as well as the corresponding Q demand and Q/P ratios of the primary substations are calculated per season. Once these trends are identified using an adequate fitting approximation (e.g., linear, exponential – see Deliverables 3 [13] and 4 [3]), they can be applied to impact analyses of the different scenarios (Stage 4).

In cases where time-series monitoring data (e.g., half-hourly P and Q) are available, downstream primary substations, the corresponding models can be extended to lower voltage levels. However, it should be highlighted that the successful use of the proposed approach depends on the identification of representative historic demand trends during long time intervals.

### Stage 2: Improved/Validated Network Modelling

In order to carry out a thorough analysis of the main factors affecting Q demand, the corresponding distribution network models have to be produced. For this purpose, the available DNO network and monitoring data is used to create improved or semi-improved models (see Deliverable 3 [13]) that mimic the behaviour of the corresponding transmission-distribution interfaces.

Network data, such as line susceptances, that are crucial for the assessment of Q demand during periods of minimum load (due to the Q gains) might not be considered adequately by DNOs, which traditionally focus on periods of peak demand.

In terms of monitoring data, in practice, not all BSPs and/or primary substations have available P and Q monitoring data. More specifically, there have been cases where only apparent power (MVA) data are available, no monitoring devices are available, erroneous data have been recorded, or confidentiality issues exist (e.g., generation profiles).

Based on the above, Stage 2 proposes the production of improved network models (presented in detail in Deliverable 3 [13] for Norton GSP –NP). This process can be summarized with the following four steps:

Step 1: Perform daily simulations using the available DNO network and monitoring data (e.g., half-hourly) to identify the mismatch in P profiles (Pmismatch) between simulations and monitoring data at the GSP and intermediate substations (BSPs and primary substations).

Step 2: Minimize the Pmismatch by allocating P and Q profiles for loads and DG. This is done by adopting an approach that allocates load and generation profiles proportionally to the size of the corresponding BSPs and/or primary substations (see Appendix C of Deliverable 3 [13]).

Step 3: Match Q profiles at the GSP by updating line susceptances across all voltage levels. In the case that the type of lines is not available, this can be achieved iteratively starting from the assumption that all lines are overhead and then different cable penetrations are adopted progressively (see Deliverable 3 [13] for details).

Step 4: To confirm the adequacy of the updated line susceptances repeat steps 1 and 2 for different days.

### Stage 3: Network Planning

Scheduled network and demand changes, as well as DG penetrations can affect the future Q demand of the examined GSPs and therefore should be considered in the scenario-based assessment of future Q demand during minimum load.

In the report of Deliverable 4 [3] the scenario-based assessment of future Q demand at the examined GSPs (seven in total) takes into account future PV penetrations according to the Future Energy Scenarios (FES) of National Grid [14]. Apart from the FES, any available information from National Grid or DNO network planners regarding scheduled/future network, generation and demand changes need to be considered in the assessment of future reactive demand.

More specifically, the following information from National Grid and DNO network planners should be taken into account:

- installation of new power cables (particularly upstream 33kV);

- replacements of overhead lines with power cables;

- network reconfigurations that affect the loadings of circuits (particularly upstream 33kV);

- installation of capacitor banks;

- penetration of small and medium-size renewables (e.g., PV and wind generation); and,

- connection of other DG plants (e.g. CHP units).

### Stage 4: Future Reactive Power Demand

Having accomplished the processes of Stages 1 to 3, the scenario-based assessment of the future Q demand at GSPs during minimum load can be carried out in Stage 4. First, the different scenarios need to be defined, as described in the report of Deliverable 4 [3]. In a similar approach with that of the European Network of Transmission System Operators for Electricity (ENTSO-E) [15] and the National Grid’s FES [14], the uncertainties regarding economic growth conditions and support on policies and regulations towards more sustainable energy systems are considered.

Both ENTSO-E and National Grid carry out impact analyses using four future scenarios. Three of these scenarios that consider slow progression, fast progression and significant DG penetration are also included in the proposed methodology. Two extra scenarios are defined in order to have a final set of scenarios that also incorporate current trends and practices (“Existing Trends” scenario) and the effects from loads becoming even less inductive (or even capacitive) downstream primary substations due to energy efficiency measures (“Effective Loads” scenario).

In the REACT project the five trend-based scenarios have been defined in the report of Deliverable 4 [3]. The scenarios that have been used to assess future Q demand at GSPs across all DNOs during minimum load are:

- “Existing Trends”: This is what can be considered as the business as usual scenario taking into account the continuation of the identified historic trends (Stage 1) in the P and Q demands of primary substations. The future trend in PV penetrations is considered to be in the middle of the expected range according to National Grid FES [14]. No future network changes are considered from GSPs (132kV) downstream to primary substations.

- “Go Green Scenario”: Policies and regulations towards more sustainable energy systems are taken into account in this scenario. This scenario is different from the “Existing Trends” scenario in the sense of considering higher future PV penetrations (maximum PV penetration trend according to FES).

- “Effective Loads”: High future economic growth trends are taken into account in this scenario. This scenario is different from the “Existing Trends” scenario in the sense of considering less inductive or even capacitive future loadings of primary substations due to energy efficiency measures. Therefore, a more acute future Q/P ratio decline in primary demand during minimum load is considered.

- “Slow Progression”: Slow future economic growth trends together with weak policies towards more sustainable energy systems are taken into account in this scenario. Therefore, less declining Q/P ratios in future P and Q demand of primary substations during minimum load and slower PV penetration trends (minimum future PV penetration trend according to FES) from the “Existing Trends” scenario are considered.

- “Fast Progression”: High future economic growth trends together with strong policies and regulations towards more sustainable energy systems are considered in this scenario. The significant PV penetration trends of “Go Green” scenario and the Q/P ratio declining trends of primary demand in “Effective Loads” are considered. Since this corresponds to the worst case scenario, it is the only scenario considering replacements of 33kV overhead lines with cables.

Having defined the scenarios, the improved or semi-improved network models (Stage 2) can be used in daily time-series simulations to assess future Q demand at GSPs.

## Summary

In summary, the proposed framework to assess future reactive power demand at GSPs during periods of minimum load has the following characteristics:

- unlike traditional approaches followed by National Grid and, in general, transmission operators around the world, the proposed framework uses distribution network models (from GSPs to primary substations) and takes into account the effects of the actual networks, such as the type and length of circuits as well as the interactions of demand and generation;

- the proposed framework can be directly used by DNOs for any of their GSPs using their network and monitoring data;

- DNOs can use the framework to investigate and plan distribution-based solutions if they are to meet the EDDC requirement (or any agreed specifications with National Grid) to limit VArs to transmission during periods of minimum load;

- the framework consists of 4 stages that include the identification of historic demand trends, the production of improved/validated network models, the incorporation of network planning information and the scenario-based assessment of future reactive demand; and,

- the proposed framework is flexible and can be adapted to cater for the analysis of other factors that have not been considered in the REACT project (e.g., significant penetrations of wind generation or CHPs).

# Future Reactive Power Demand

The future Q demand at GSPs during periods of minimum load can be assessed for different scenarios following the proposed framework of the previous section (Section 2) of this report. The future trends in Q demand have been assessed following this framework for ENWL, NP, SPEN and WPD GSPs (5 GSPs) in the report of Deliverable 4 [3]. In the present final report the future trends in Q demand for the same scenarios are presented in detail for new cases of UKPN and SSE GSPs.

In the following subsections the final results for future trends in Q demand are first presented for the previously examined cases (ENWL, NP, SPEN and WPD). Next, the corresponding results are presented for the new cases (SSE and UKPN).

## Summary of Previously Presented Cases

In the report of Deliverable 4 [3] the future trends in Q demand at Kearsley (critical-ENWL), Norton (critical-NP), Chesterfield (critical-WPD) and the interconnected Fiddler’s Ferry (critical-SPEN) and Carrington (control-SPEN) GSPs were assessed for the different scenarios (see Table 2 of Deliverable 4 [3]). The network models corresponding to 18th June 2013 (year 0) were used in time-series simulations for ENWL, NP and WPD GSPs. Due to the availability of monitoring data, the network model corresponding to 18th June 2010 was considered for the interconnected SPEN GSPs.

The results of the 5 scenarios using the improved networks of Norton (NP) and Kearsley (ENWL) GSPs in Fig. 2 and Fig. 3 indicate that the continuation of the declining trends in the demand of primary substations is the main factor that can lead to significant VAr exports towards transmission in the mid-term. The increased VAr exports in a 2 to 5 year horizon at both GSPs highlight the fact that, if a similar behaviour is to be found in other GSPs in the North of England, this could deteriorate National Grid’s ability to maintain statutory voltage levels in the region but also the challenge to be faced by DNOs to comply with the EDCC requirements.

Future Q demand at Norton (NP) GSP for different scenarios.

Future Q demand at Kearsley (ENWL) GSP for different scenarios.

Unlike the analysis for ENWL and NP GSPs, the implementation of the scenario-based assessment of future Q demand at the WPD and SPEN GSPs in Fig. 4 and Fig. 5, respectively, exhibited significant drawbacks. Although the semi-improved network models for the examined WPD and SPEN GSP groups matched in daily time-series simulations the P and Q demand at GSPs, there are two major issues deriving from practical modelling challenges:

•	the historic trends in P and Q demand at primary substations could not be identified; and,

•	the cable penetration has not been estimated.

Consequently, the original DNO data for line parameters was not updated in the examined WPD and SPEN networks and the primary demand trends in the corresponding scenarios were considered as equal to the 2009-2013 historic Q/P ratio trends at these GSPs using National Grid half-hourly data.

Future Q demand at Chesterfield (WPD) GSP for different scenarios.

Future aggregated Q demand of Fiddler’s Ferry and Carrington (SPEN) GSPs for different scenarios.

The findings regarding the previously examined cases of ENWL, NP, SPEN and WPD networks can be summarized as follows:

- Future Q demand at GSPs are mainly affected by the future trends in P and Q demand at primary substations and any possible cable penetration, even in 33kV circuits;

- the expected future trends in PV penetrations do not significantly affect Q demand at GSPs;

- using improved network models the VAr exports to transmission for the ENWL and NP networks are expected to be increased by 30 to 175% until 2018;

- using semi-improved network models the VAr exports to transmission for the WPD and SPEN networks are expected to be many times higher than the corresponding for ENWL and NP networks; and,

- results using semi-improved network models for the WPD and SPEN networks might not be representative because of the use of original DNO (not updated and validated) line parameters for 132 to 33kV circuits and Q/P ratio trends at primary substations using GSP monitoring data.

## New Cases

Two new cases have been examined in this final report of the REACT project considering the proposed framework of Fig. 1: City Road GSP (critical-UKPN) and Lovedean GSP (critical-SSE). Unlike the previously presented cases, the new cases are in the South of Great Britain.

### City Road GSP (UKPN)

The future Q demand during minimum load is assessed in this subsection for the City Road GSP (critical-UKPN) using different scenarios according to the proposed framework of Fig. 1. City Road is a large distribution network with 812MW peak load in 2013. The minimum Q demand at this GSP in 2013 was inductive at 7MVAr (336MW minimum load in 2013). In fact, this is the only GSP out of the top 2 critical and top 2 control GSPs per DNO (28 GSPs in total) that exhibited inductive minimum annual Q demand during 2013 (see Deliverable 3 [13]).

To assess the future Q demand at City Road GSP, the improved network model of 18th June 2013 (year 0) is considered in time-series simulations (see Appendix 8.1.1). The minimum daily Q demand at the GSP (maximum VAr exports to transmission) is assessed for every scenario (see Stage 4 in Section 2 of this report) in year 0. Fig. 6 shows the normalized Q demand (Q/Q2013) at City Road GSP in a 5-year horizon. The Q demand at the GSP is the same for all scenarios in year 0 (Q/Q2013=1). Specifically, the Q demand in year 0 (18th June 2013) is 40MVAr (inductive).

It is noteworthy that City Road is a large urban network with 100% cable penetration in 132 to 33kV circuits. Nonetheless, the total length of 132kV circuits is considerably lower (circa 45km) compared to other networks (e.g., Lovedean GSP of SSE with approximately 50km total length of cables and 300km of overhead lines in 132kV – next subsection).

Since there is 100% cable penetration in 33kV circuits, the “Fast Progression” and “Effective Loads” scenarios do not exhibit any difference. Results show that future Q demand at GSP is reduced for all scenarios, but demand remains inductive for all scenarios until year 4. It is noteworthy that a 80% decrease in Q demand at City Road GSP is expected according to the “Existing Trends” scenario in a 5 years horizon. Only in year 5 there are Q exports during minimum load according to the “Fast Progression/Effective Loads” scenario (Q=-8.7MVAr).

Emphasis should be given to the fact that City Road is the network that exhibits the most acute decline in P demand at primary substations during periods of minimum load (-2.6% per year – see seasonal analysis in Deliverable 4 [3]) among all analysed GSPs with available P and Q monitoring data at primary substations. The corresponding decline in Q demand at primary substations (-8.7% per year) is very similar to other GSPs (e.g., Norton-NP, Kearsley and South Manchester-ENWL).

It should be noted that although City Road was inductive in 2013, the other critical and control GSPs were capacitive. Taking this into account, if similar acute declining trends in the P demand of primary substations is identified in future studies in other UKPN networks that are currently capacitive, they will lead to lower loadings of 132 to 33kV lines and therefore significant Q gains.

Future Q demand at City Road (UKPN) GSP for different scenarios.

### Lovedean GSP (SSE)

The future Q demand during minimum load is assessed in this subsection for the Lovedean GSP (critical-SSE) using the different scenarios (see Deliverable 4 [3]). Lovedean GSP group is a large distribution network with 592MW peak load in 2013. The minimum Q demand at this GSP in 2013 was -186MVAr (161MW minimum load in 2013).

It is noteworthy that Lovedean, together with Fleet (SSE) GSP, are the 2 GSPs that exhibited the lowest Q demand in 2013 during minimum load across all critical and control GSPs (28 GSPs) selected across all DNOs. It is also noteworthy that both networks are in the same license area of SSE in the South of Great Britain.

To assess the future Q demand at Lovedean GSP, the semi-improved network model of 18th June 2013 (year 0) is considered using time-series simulations (see Appendix 8.1.2). Since the cable penetration could not be estimated in 33kV circuits, the “Fast Progression” and “Effective Loads” scenarios are the same for this GSP. The minimum daily Q demand at GSP (maximum VAr exports to transmission) is assessed for every scenario from year 0 (2013) to year 5 (2018). Fig. 7 shows the normalized Q demand (Q/Q2013) at Lovedean GSP in a 5-year horizon. The Q demand at the GSP is the same and equal to -174MVAr for all scenarios in year 0 (Q/Q2013=1).

Results show that at least 15% increase in VAr exports to transmission is expected at Lovedean GSP after 5 years according to the “Slow Progression” scenario. The corresponding increase in VAr exports is 30% according to “Fast Progression”/”Effective Load” scenarios. Results for the “Existing Trends” and “Go Green” scenarios show that the higher PV penetrations of the “Go Green” scenario are not expected to affect Q demand at the examined GSP.

The significant increase of Q exports found in Lovedean (15 to 30% in a 5 year horizon) combined with the significant decrease of Q imports found in City Road (62 to 121%) highlight that the South of Great Britain might pose challenges to National Grid. In fact, if similar behaviours are to be found in other GSPs in the South of England, this could deteriorate National Grid’s ability to maintain statutory voltage levels in the region. In addition, tackling the effects of these trends will also be challenging to DNOs if they are to comply with the EDCC requirements (particularly for SSE).

.

- Future Q demand at Lovedean (SSE) GSP for different scenarios.

## Nationwide Trends in Q Demand

Using the proposed framework of Fig. 1, the future Q demand during minimum load has been assessed at 7 GSPs (5 GSPs in Deliverable 4 [3] and 2 GSPs in subsection 3.2 of this report) out of the 336 GSPs across Great Britain. Although the examined GSPs had an aggregated peak demand of approximately 6% of the 2013 peak demand across Great Britain, the corresponding trends can be used to understand the potential behaviour of all GSPs nationwide.

For consistency, the GSPs from which the nationwide trends will be extract should consider the same day of analysis. This applies to 5 GSPs out of 7: Kearsley - ENWL, Norton - NP, Lovedean - SSE, City Road - UKPN and Chesterfield - WPD (18th June 2013)

The aggregated Q demand of the 5 GSPs in year 0 (18/6/2013) for all scenarios is the same and equal to -193MVAr. The nationwide trends are derived taking into account the aggregated future Q demand for these GSPs (see subsection 3.2) in its normalised form (Q/Q2013), as shown in Fig. 8. The aggregated future Q demand in actual MVAr values are presented in Table 1. Results are not presented for the “Fast Progression” scenario, since cable estimation in 33kV circuits was not possible in semi-improved network models.

Results show that at least 55% increased VAr exports to transmission are expected for the aggregated demand of these 5 GSPs after 5 years according to the “Slow Progression” scenario (Q=-307MVAr). The corresponding increase in VAr exports is approximately 75 and 120% according to the “Existing Trends” and “Effective Loads” scenarios. Results for the “Existing Trends” and “Go Green” scenarios show that the higher PV penetrations of the “Go Green” scenario are not expected to affect Q demand at the examined GSPs.

Nationwide trends in reactive demand during periods of minimum load. Results for the aggregated Q demand of 5 GSPs corresponding to circa 5.5% of GB peak MW in 2013.

Future aggregated Q demand at 5 examined GSPs

| Scenario | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 |
| --- | --- | --- | --- | --- | --- |
| Existing Trends | -223.647 | -254.609 | -285.003 | -313.598 | -341.086 |
| Go Green | -223.675 | -254.663 | -285.083 | -313.702 | -341.214 |
| Effective Loads | -238.915 | -284.95 | -327.278 | -367.61 | -425.587 |
| Slow Progression | -216.166 | -238.943 | -262.206 | -285.003 | -306.683 |

Although the studied GSPs cover all DNOs, it is important to highlight that the adequacy of the derived nationwide trends has the following limitations:

- The studied GSPs correspond to an aggregated peak demand of only circa 6% (3.4GW) of the nationwide peak demand in 2013;

- 4 GSPs have been modelled with semi-improved network models that match P and Q profiles in time-series simulations for a specific day and are not validated in multiple days;

- the historic primary demand trends are an important component in the proposed framework to assess future Q demand (see section 3) and available P and Q monitoring data for over 5 years have been made available and used in analyses only for 2 of these GSPs; and,

- future Q demand has not been assessed for any network in Scotland.

Emphasis should be given in future studies not only to the enhancement of analyses (e.g., with modelling networks downstream primary substations), but also to expand the analyses to more GSPs that will update and/or improve the derived nationwide trends.

## Summary

The future trends in reactive Q demand during periods of minimum load can be summarized as follows:

- In all examined cases (7 GSPs – previously presented and new cases) across all DNOs the continuation of identified historic trends in the demand of primary substations can result in significant decline of Q demand during periods of minimum load;

- to analyse the future trends in UKPN and SSE GSPs, the improved network model of City Road (UKPN) and the semi-improved model of Lovedean (SSE) have been used in analyses;

- 62 to 121% reduction in Q demand during minimum load (still inductive with 61% decrease, but getting capacitive at 121%) is expected in a 5 years horizon at the UKPN GSP;

- extra 15 to 30% Q exports are expected in a 5 year horizon at the SSE GSP; and,

- nationwide trends in reactive demand (analysis on 5 GSPs with available 2013 data) show that in a 5 years horizon the Q exports to transmission are expected to increase, depending on the scenario, by 55 to 120% with respect to their 2013 level.

# Techno-Economical Assessment Using Shunt Reactors

The adoption of shunt reactors in distribution networks could be a potential solution that will help National Grid maintain statutory transmission voltage levels. It will also allow the DNOs to limit their Q exports to transmission, particularly if they are to meet the EDCC [1] requirements (i.e., no VAr exports to transmission for loadings below the 25% of the transmission-distribution interface capacity [1]).

In the following subsection the potential advantages and disadvantages from the installation of shunt reactors at primary substations instead of GSPs are first investigated. The analysis is carried out using the available 2013 improved network models. It is noted that improved network models have been produced for Kearsley (ENWL), Norton (NP) and City Road (UKPN) GSPs. Unlike Kearsley (ENWL) and Norton (NP) GSPs that exhibited Q exports to transmission within 2013, City Road (UKPN) was inductive in 2013 and therefore is not considered in the investigations. The analysis focuses on:

- the potential ability to size shunt reactors with less aggregated VArs when installed at primary substations instead of at the corresponding GSP; and,

- the effects on energy losses resulting from installing shunt reactors at primary substations with and without time control strategies.

Next, the identified nationwide trends (see Fig. 8 in Section 3) in Q demand are considered in a 5 years horizon to produce an initial cost estimation of shunt reactors required to tackle the VAr exports of each of the top 60 critical GSPs in Great Britain (top 10 per DNO).

## Installation of Shunt Reactors at Primary Substations

Shunt reactors can be installed by DNOs at the GSPs or any other network point downstream (e.g., BSPs or primary substations). A potential benefit from using shunt reactors at primary substations could be the sizing of shunt reactors with less aggregated VArs at primary substations compared to the corresponding amount of VArs needed to be installed at the GSPs.

In the following subsections the sizing of shunt reactors is first investigated using the improved network models of Kearsley (ENWL) and Norton (NP). Next, the corresponding effects on energy losses from the installation of shunt reactors at primary substations are presented for these two networks. The analysis also focuses on the reduction of energy losses that can be achieved when time control strategies are adopted.

### Relationship of VArs at the GSP and Primary Substations

Focusing on potential solutions that could tackle the effects from the declining Q demand at GSPs, it was highlighted in the report of Deliverable 4 [3] that any solution at primary substations (e.g., installation of shunt reactors) could potentially have a larger positive effect at GSPs. This point for further investigation derived from the observation of future trends in 2 different GSPS (Kearsley - ENWL and Norton - NP (Norton), where 1MVAr less in the minimum daily aggregated Q demand at primary substations corresponded in simulation results by ~1.5MVAr decline in the minimum daily Q demand at GSPs. This relationship, however, is not appropriate as it considered different (uncorrelated) time instants throughout the day.

Here, the relationship of Q demand at the GSP (QGSP) and that of primary substations (Qprimaries) is investigated again considering the same (correlated) time instant in the studied day. Fig. 9a and Fig. 9b show the QGSP/Qprimaries ratios for the daily time window that Q exports to transmission (i.e., 0 am to 7 am) during 18th June 2013 take place in Norton and Kearsley GSPs, respectively. The mean value of the QGSP/Qpimaries ratio is –0.44 and -0.8029 for Norton and Kearsley GSPs, respectively.

- Standard deviations (red lines) of the ratios of Q at GSP to the aggregated Q demand of primaries for a) Norton (NP); and, b) Kearsley (ENWL) GSPs.

The standard deviation in Fig. 9 (red lines showing the variation from the mean value) is 0.075 and 0.434 for Norton and Kearsley GSPs, respectively. The calculated standard deviations, particularly for Kearsley GSP, give a first indication that the relationship between QGSP and Qpimaries is highly dependent on the time of the day, and therefore a single value would not be realistic.

### Sizing of Shunt Reactors

To investigate if shunt reactors with less aggregated VArs can be sized at primary substations instead of GSPs, the following cases are presented for Norton (NP) and Kearsley (ENWL) GSPs:

- Case #1: no shunt reactors are installed;

- Case #2: installation of 1MVAr shunt reactors at primary substations for every 1MVAr exports at the GSP, i.e., direct sizing of VArs as seen at the GSP; and,

- Case #3: installation of minimum amount of VArs of shunt reactors at primary substations that can lead to zero MVAr exports to transmission, i.e., fine-tuned sizing of VArs as actually required by the GSP.

The analysis for both GSPs is carried out using the corresponding improved network models of the 18th June 2013. During this day the maximum Q exports at Norton and Kearsley GSPs are 20 and 32.4MVAr, respectively. Norton and Kearsley GSP groups have 39 and 37 primary substations, respectively. It is important to highlight that, for simplicity, in both networks the size of shunt reactors in each of the primary substations is the same, i.e., VArs are evenly distributed. In addition, shunt reactors are continuously switched on (no time control).

The simulated Q profiles at Norton and Kearsley GSP for Cases #1 to #3 are shown in Fig. 10a and Fig. 10b, respectively. For Case #2 the size of shunt reactors per primary substation are 513 (20MVar / 39) and 876kVAr (32.4MVar / 37) for Norton and Kearsley GSPs, respectively. The resulting reactive power seen at the GSPs are 0.58 and 0.39MVar, respectively. This highlights that the siting of shunt reactors at primary substations have a slightly extra benefit when the effect is seen at the GSP.

- Daily Q profiles at a) Norton (NP) and b) Kearsley ENWL GSP. Results from 0 am to 10 am using the improved network models of 18th June 2013.

Case #3 is used to determine the right amount of VArs needed by each GSP by iteratively fine tuning the sizes of shunt reactors at the primary substations and quantifying the effect at the GSP. It was found that to achieve zero reactive power exchanges at the GSPs during the critical instant, shunt reactors at primary substations should only not exceed 499 and 867kVAr in Norton and Kearsley GSPs, respectively.

Based on the above results, it can be concluded that 1MVAr from shunt reactors installed at primary substations can reduce the Q exports to transmission by 1.03 and 1.01MVAr in Norton and Kearsley GSPs, respectively, which in turn can lower the corresponding capital cost.

The cases presented in this analysis do not investigate the optimal siting, sizing and control of shunt reactors and therefore this should be addressed in future work to understand the cost-effectiveness of different approaches.

### Effects on Energy Losses

The adoption of shunt reactors at primary substations can increase the complex power flows through lines and transformers and therefore result in higher losses. The effects on energy losses are investigated in this subsection with and without time control strategies.

The analysis is carried out using the improved network models (18th June 2013) of Kearsley (ENWL) and Norton (NP) GSPs. The shunt reactors identified in Case #3 (subsection 4.1.1) are considered in the quantification.

The cases examined to investigate the corresponding effects on energy losses are:

- Case A: no shunt reactors are installed;

- Case B: shunt reactors absorb VArs constantly (no time control); and,

- Case C: shunt reactors absorb VArs from 0 am to 7.30 am (time controlled).

Daily Q profiles at a) Norton (NP) and b) Kearsley (ENWL) GSP using the improved network models of 18th June 2013.

Fig. 11a and Fig. 11b show the daily Q profiles for all three cases for Norton and Kearsley GSPs, respectively. Although with and without any time control strategy there are no Q exports to transmission, the corresponding energy losses for Cases B and C are different. The latter is shown in Tables 2 and 3 for Cases A, B and C considering the whole 24-hour daily time window for Norton and Kearsley GSP groups, respectively.

Energy Losses at Norton GSP Group Using Shunt Reactors at Primaries

| Case | Energy Losses |  |  |
| --- | --- | --- | --- |
|  | MWh | % | Increase (%) |
| A: no shunt reactors | 64.1 | 1.036 | -- |
| B: shunt reactors without time control | 65.6 | 1.062 | 2.5 |
| C: shunt reactors with time control | 64.6 | 1.046 | 0.9 |

Energy Losses at Kearsley GSP Group Using Shunt Reactors at Primaries

| Case | Energy Losses |  |  |
| --- | --- | --- | --- |
|  | MWh | % | Increase (%) |
| A: no shunt reactors | 88.8 | 1.253 | -- |
| B: shunt reactors without time control | 92.4 | 1.304 | 4.1 |
| C: shunt reactors with time control | 89.5 | 1.262 | 0.7 |

The installation and operation of shunt reactors without any time control (Case B) increases the energy losses by 2.5 and 4.1% with respect to the original case (Case A) for Norton and Kearsley GSPs, respectively. The corresponding increase using the time control operation (Case C) is much lower, i.e., 0.9 and 0.7% of the original level (Case) for Norton and Kearsley GSPs, respectively.

It can be concluded that the time window that the shunt reactors will absorb VArs has a significant effect on the corresponding increase in energy losses and, therefore, the adoption of time-based control strategies can bring significant benefits. Nonetheless, it is important to highlight that ultimately the impacts on energy losses should be assessed considering a yearly analysis. Depending on the reactive power exchange behavior of a GSP, the use of shunt reactors can be necessary only on a few days or weeks in a year and, consequently, the impact on energy losses could be considered negligible.

## Cost Estimation for the Top 60 Critical GSPs in Great Britain

This subsection presents an initial estimation of the total cost of adopting shunt reactors for the top 10 critical GSPs per DNO, i.e., a total of 60 critical GSPs in Great Britain [2]. For simplicity, the shunt reactors are sized equally to the VAr exports of each GSP. The analysis considers the nationwide trends (see Fig. 8) in a 5 year horizon and assumes a total cost of £45k per MVAr of shunt reactors (capital and installation cost).

This process allows DNOs and National Grid to have a first insight into the total cost of a solution based on shunt reactors; traditionally used in transmission networks to absorb VArs. Table 4 shows the amount of VArs and the corresponding total cost of shunt reactors per DNO for the different scenarios that define the derived nationwide trend. It is important to highlight that for each of the studied GSPs the Q demand considered for year 0 corresponds to the minimum found in 2013.

Economic Assessment Using Shunt Reactors at top 10 critical GSPs per DNO

| DNO (2013 aggregated peak demand) | Shunt Reactors | Existing Trends | Go Green | Effective Loads | Slow Progression |
| --- | --- | --- | --- | --- | --- |
| ENWL (2.87 GW) | Rating (MVAr) | 650 | 651 | 811 | 585 |
|  | Cost (million £) | 29.27 | 29.28 | 36.52 | 26.31 |
| NP (2.40 GW) | Rating (MVAr) | 491 | 491 | 613 | 442 |
|  | Cost (million £) | 22.11 | 22.12 | 27.59 | 19.88 |
| SPEN (1.61 GW) | Rating (MVAr) | 382 | 382 | 476 | 343 |
|  | Cost (million £) | 17.18 | 17.18 | 21.43 | 15.45 |
| SSE (2.87 GW) | Rating (MVAr) | 1211 | 1211 | 1511 | 1088 |
|  | Cost (million £) | 54.48 | 54.50 | 67.97 | 48.98 |
| UKPN (5.81 GW) | Rating (MVAr) | 1324 | 1324 | 1652 | 1190 |
|  | Cost (million £) | 59.57 | 59.59 | 74.32 | 53.56 |
| WPD (4.85 GW) | Rating (MVAr) | 1196 | 1197 | 1493 | 1076 |
|  | Cost (million £) | 53.84 | 53.86 | 67.18 | 48.41 |

The range of investment for the top 60 critical GSPs is from £213 million for the most optimistic scenario (“Slow Progression”) to £295 million for the worst case (“Effective Loads”). The amount of investment, however, is not evenly distributed across DNOs. This is due to both the size of each GSP (e.g., in terms of peak P demand) and the corresponding reactive power exchange behaviour.

DNOs that operate in the South of Great Britain (i.e., SSE and UKPN) would require the highest investments according to the results of Table 4, a combined total of £103 to £142 million depending on the scenario. The aggregated peak demand for the 20 GSPs of these two DNOs account for 8.68 GW (43% of the top 60 critical GSPs in 2013). In particular, the highest investment appears for UKPN (from £54 to £74 million). On the other hand, the top 10 critical SPEN GSPs would require the lowest investment (from £15.45 to £21.43 million depending on the scenario). A significant component in this large difference between UKPN and SPEN is due to the relative sizes of the GSPs. Indeed, the aggregated peak demand of the top 10 critical SPEN GSPs account only for 8% (of the 60 GSPs analysed) whereas for UKPN this figure is 28%.

Although Q/P ratio trends are very similar across Great Britain, there are also other aspects that should be taken into account to explain the different levels of investment. In particular, the interactions between minimum P demand and network characteristics can play a significant role when comparing networks of the same size in terms of peak demand. For instance, City Road GSP (UKPN) presents a declining Q demand trend but has not exported VArs in 2013 (see subsection 3.2.1). On the other hand, Lovedean GSP (SSE), with smaller peak demand, has significant VAr exports in 2013 (see subsection 3.2.2).

## Summary

The findings from the sizing of shunt reactors and the techno-economic assessment can be summarized as follows:

- based on the studies carried out on Norton and Kearsley GSPs, it was found that 1 to 3% less VArs of shunt reactors would be needed if installed at primary substations instead of at the GSP;

- the installation of shunt reactors at the primary substations do increase energy losses but this is only by 4% (Kearsley GSP). This effect can be significantly curbed by adopting time-based control strategies, i.e., switching on shunt reactors during the critical hours;

- the range of investment needed to install shunt reactors considering the top 60 critical GSPs in Great Britain and a 5 year horizon is from £213 to £295 million, depending on the nationwide trend;

- DNOs in the South of Great Britain (i.e., SSE and UKPN) would require higher investment for their top 10 critical GSPs (a combined total of £103 to £142 million depending on the scenario);

- SPEN would require the lowest investment across all DNOs (from £15.45 to £21.43 million); and,

- to explain the different levels of investment is important to consider not only the Q/P ratio trends (similar across Great Britain) but also the interactions between minimum P demand and network characteristics.

# Considerations for Future Work

Future work should aim not only to enhance the outcomes of the current project but also to investigate potential DNO-led solutions that can tackle the effects of the decline in reactive power demand. This is needed if DNOs are to meet the requirements of the EDCC (or agreed specifications with National Grid) to limit VAr exports to transmission.

The key objectives of future work should be to:

- Produce improved network models for more critical and control GSP groups for all DNOs (note that currently original models of 19 GSPs have been produced but improved and semi-improved models for only 7 GSPs have been completed by the current REACT project). The new models will be used to enhance trend-based scenarios to assess the mid and long-term reactive power exchanges at the GSPs. Future trends in electrification of heat and transport should be also included in the enhanced scenarios. The analyses should also consider more recent monitoring and network data (after 2014).

- Use available historic statistics for network and demand changes downstream primary substations to assess corresponding trends and investigate potential correlations with the identified by the current REACT project declining Q/P ratios trends in primary demand during periods of minimum load.

- Investigate potential solutions that do not require the installation of new assets in distribution networks and the extent of their benefits. This includes, tap staggering of primary substations, the adequate settings for DG power factor (e.g., fixed, time based, scheduled), and the adoption of different voltage targets at GSPs and BSPs during minimum load so as to reduce gains on the corresponding circuits. Different deployment scenarios across GSPs could be considered so as to quantify the overall benefit to National Grid in terms of reactive power demand.

- Investigate the adoption of VAr sources, in particular shunt reactors, in distribution networks considering optimal sizing (i.e., minimum cost) and siting of the corresponding devices across voltage levels. Different deployment scenarios across GSPs could be considered so as to quantify the overall benefit to National Grid in terms of reactive power demand.

- Investigate the potential benefits to DNOs and National Grid from large-scale demand side management strategies that could in the future be made available by aggregators (e.g., smart appliance aggregators, commercial load aggregators, electric vehicle aggregators, etc.). In particular, the extra demand required to reduce GSP exports of reactive power during periods of minimum load could be quantified. This could allow understanding the availability of demand side management services needed to make this a future alternative.

# Conclusions

The REACT project has been funded by National Grid and the six Distribution Network Operators (DNOs) in Great Britain: Electricity North West Limited (ENWL), Northern Powergrid (NP), Scottish Power Energy Networks (SPEN), Scottish and Southern Energy (SSE), UK Power Networks (UKPN) and Western Power Distribution (WPD). This project has been financially managed by Energy Networks Association (ENA).

The REACT project has been established to understand the reasons behind the decline in reactive power demand as seen by National Grid during minimum load. This will allow DNOs and National Grid establishing future trends in the reactive power exchanges at GSPs and adopt the most cost-effective actions as well as responsibilities for ongoing data provision, planning, design, and operational management in this area.

This final report of REACT project includes:

- the proposed framework and the corresponding methodology that can be used by any DNO to assess future Q demand at any of their GSPs;

- the scenario-based assessment of future trends in Q demand at GSPs across all DNOs for previously examined (ENWL, NP, SPEN, WPD) and new (SSE and UKPN) cases;

- an initial techno-economical assessment using the installation of shunt reactors at GSPs and primary substations; and,

- considerations for future studies aimed at enhancing the trends in Q demand as well as investigating distribution-based solutions.

Proposed Framework

A framework that consists of 4 stages is proposed to DNOs to assess future trends in Q demand at any of their GSPs during periods of minimum load. The proposed framework has the following characteristics:

- unlike traditional approaches followed by National Grid and, in general, transmission operators around the world, the proposed framework uses distribution network models (from GSPs to primary substations) and takes into account the effects of the actual networks, such as the type and length of circuits as well as the interactions of demand and generation;

- the proposed framework can be directly used by DNOs for any of their GSPs using their network and monitoring data;

- DNOs can use the framework to investigate and plan distribution-based solutions if they are to meet the EDDC requirement (or any agreed specifications with National Grid) to limit VArs to transmission during periods of minimum load;

- the framework consists of 4 stages that include the identification of historic demand trends, the production of improved/validated network models, the incorporation of network planning information and the scenario-based assessment of future reactive demand; and,

- the proposed framework is flexible and can be adapted to cater for the analysis of other factors that have not been considered in the REACT project (e.g., significant penetrations of wind generation or CHPs).

Future Reactive Power Demand

Following the proposed framework, the scenario-based assessment of future trends in Q demand during minimum load is presented in this final report for GSPs across all DNOs. More specifically, results are presented for previously examined cases (GSPs of ENWL, NP, SPEN, WPD) and new cases (GSPs of SSE and UKPN) covering all DNOs. Results, although limited to seven GSPs, demonstrate that:

- the declining demand trends at primary substations is the major contributor to the overall decline of Q demand during minimum load;

- future Q demand at GSPs can be significantly affected by any possible cable penetration, even in 33kV circuits;

- the expected future trends in PV penetrations do not significantly affect Q demand at GSPs;

- using improved network models the VAr exports at the ENWL and NP GSPs are expected to be increased by 30 to 175% until 2018;

- using improved network models the VAr imports for the UKPN GSP are expected to be decreased by 62 to 121% until 2018; and,

- results using semi-improved network models for the SPEN, SSE and WPD networks might not be representative because of the use of original DNO (not updated and validated) line parameters for 132 to 33kV circuits and Q/P ratio trends at primary substations using GSP monitoring data or data for short time intervals; and,

- in a 5 years horizon the Q exports to transmission are expected to increase, depending on the scenario, by 55 to 120% with respect to their 2013 level.

Techno-Economic Assessment Using Shunt-Reactors

An initial techno-economical assessment using shunt reactors is also presented in this final report. The investigation considers aspects regarding the sizing of shunt reactors at primary substations and the corresponding effects on energy losses. It also focuses on the amount of investment needed to be installed at GSPs to meet the requirements of the European Demand Connection Code (EDCC). The findings from the sizing of shunt reactors and the techno-economic assessment can be summarized as follows:

- based on the studies carried out on Norton and Kearsley GSPs, it was found that 1 to 3% less VArs of shunt reactors would be needed if installed at primary substations instead of at the GSP;

- the installation of shunt reactors at the primary substations do increase energy losses but this is only by 4% (Kearsley GSP). This effect can be significantly curbed by adopting time-based control strategies, i.e., switching on shunt reactors during the critical hours;

- the range of investment needed to install shunt reactors considering the top 60 critical GSPs in Great Britain and a 5 year horizon is from £213 to £295 million, depending on the nationwide trend;

- DNOs in the South of Great Britain (i.e., SSE and UKPN) would require higher investment for their top 10 critical GSPs (a combined total of £103 to £142 million depending on the scenario);

- SPEN would require the lowest investment across all DNOs (from £15.45 to £21.43 million); and,

- to explain the different levels of investment is important to consider not only the Q/P ratio trends (similar across Great Britain) but also the interactions between minimum P demand and network characteristics.

It is important to highlight that although the REACT project has been completed as scheduled, due to the delays in the collection of data and the fact that original DNO models needed to be improved, the studies have not been carried out in all the critical and control GSPs as initially expected. Therefore, the conclusions presented in this work might not be representative across Great Britain but indicative of the trends found in critical GSPs.

Future Work

Considerations for future work are also presented in this final report of REACT project. These include:

- the enhancement of the assessment of trends in Q demand by analysing more networks and extending the analyses downstream primary substations; and,

- the investigation of distribution-based solutions (e.g., alternatives that do not require the installation of new assets) if DNOs are to meet the requirements of the EDCC (or agreed specifications with National Grid) to limit VAr exports to transmission.

# References

- ENTSO-E., "Draft Demand Connection Code", 2012. [Online]. Available: https://www.entsoe.eu/resources/network-codes/demand-connection/

- REACT project, “Deliverable 1. Fourth Month Report - REACT project”, Mar. 2014.

- REACT project, “Deliverable 4. Second Year Six Month Report - REACT project”, Apr. 2015.

- P. M. S. Carvalho, F. Correia Pedro, L. F. Ferreira, “Distributed Reactive Power Generation Control for Voltage Rise Mitigation in Distribution Networks” IEEE Trans. on Power Systems, vol. 23, no. 2, pp. 766-772, May 2008.

- P. N. Vovos, A. E. Kiprakis, A. R. Wallace, G. P. Harrison, “Centralized and Distributed Voltage Control: Impact on Distributed Generation Penetration”, IEEE Trans. on Power Systems, vol. 22, no. 1, pp. 476-483, Feb. 2007.

- L. F. Ochoa, A. Keane, G. P. Harrison, “Minimizing the Reactive Support for Distributed Generation: Enhanced Passive Operation and Smart Distribution Networks”, IEEE Trans. on Power Systems, vol. 26, no. 4, pp. 2134-2142, Nov. 2011.

- K. L. Lo, Y. A. Alturki, "Towards reactive power markets. Part 1: reactive power allocation," IEE Proc. - Generation, Transmission and Distribution, vol.153, no.1, pp.59,70, 12 Jan. 2006.

- J. Morin, F. Colas, X. Guillaud, S. Grenard, "Determination and Origins of Reactive Power Flows in HV/MV Substations", Proc. CIRED 2015, paper 0414, Lyon, 15-18 Jun., 2015.

- P. Schafer, H. Vennegeerts, S. Krahl, A. Moser, "Derivation of Recommendations for the Future Reactive Power Exchange at the Interface between Distribution and Transmission Grid", Proc. CIRED 2015, paper 0760, Lyon, 15-18 Jun., 2015.

- I. Talavera, P. Franz, S. Weck, J. Hanson, S. Stepanescu, R. Huber, H. Abele, "Flexible Reactive Power Exchange Between Medium and High Voltage Networks: case Study", Proc. CIRED 2015, paper 0964, Lyon, 15-18 Jun., 2015.

- L. Cocchi, A. Cerretti, E. Deberardinis, F. Bignucolo, A. Savio, R. Sgarbossa, "Influence of Average Power Factor Management on Active Distribution Networks", Proc. CIRED 2015, paper 0634, Lyon, 15-18 Jun., 2015.

- C. G. Kaloudas, L. F. Ochoa, I. Fletcher, B. Marshall, S. Majithia, "Investigating the Declining Reactive Power Demand of UK Distribution Networks", Proc. IEEE PES General Meeting 2015, Denver, Jul. 2015.

- REACT project, “Deliverable 3. First Year Report Stage 1 - REACT project”, Nov. 2014.

- National Grid, "UK Future Energy Scenarios", 2014. [Online]. Available: http://www2.nationalgrid.com/uk/industry-information/future-of-energy/future-energy-scenarios/

- ENTSO-E (2012 Dec.). ENTSO-E Network Code on Demand Connection. [Online]. Available: https://www.entsoe.eu/major-projects/network-code-development/demand-connection/Pages/default.aspx

- REACT project, “Deliverable 2. Eighth Month Report REACT project”, Jun. 2014.

# Appendices

## Appendix A – Production of improved and semi-improved network models

### City Road GSP (UKPN)

Fig. 12 shows the single line diagrams from the original UKPN digital file (DIgSILENT file) for the 132 and 33kV circuits. It is noteworthy that there is a significant interconnection in City Road network with an adjacent GSP at 132kV (Bankside F – 132kV).

City Road GSP group has been modelled from the low voltage side of the GSP transformers (132kV) downstream to primary substations. The proposed methodology to produce improved network models in Deliverable 3 (Section 2) does not need to be followed for City Road group. More specifically, since half-hourly P and Q monitoring data have been provided by UKPN for years 2009 to 2014, only the load profiles of Paternoster-11kV primary substation has been allocated.

Additionally, since the type of lines (e.g., XLPE insulated cables, oil insulated cables etc) have been provided for all 132 to 33kV circuits, there is no need to estimate the corresponding cable penetrations. For limited number of power cables (oil insulated) there has been an update in their line susceptances using typical values.

Fig. 13 and Fig. 14 show the daily simulation results and monitoring data for P and Q demand at City Road GSP during 18th June 2013 (1st day of critical week 25 [16]) and 28th May 2013 (1st day of critical week 22 [16]).

Single line diagram of City Road GSP group.

Simulation results and monitoring data for City Road GSP for a) P profile and b) Q profile. Analysis for 18th June 2013.

Simulation results and monitoring data for City Road GSP for a) P profile and b) Q profile. Analysis for 28th May 2013.

### Lovedean GSP (SSE)

Fig. 15 shows the single line diagrams from the original SSE digital file (PSS/E file) for the Lovedean GSP group. Although only MVA data have been provided for this network, the types of lines (e.g., cable or overhead line) have been provided by SSE for the 132kV circuits of this network. More specifically, circa 50km of the aggregated 350km of 132kV circuits correspond to cables (circa 15% of 132kV circuits are cables).

The most challenging task in the modelling of Lovedean GSP group has been the availability of only half-hourly apparent power (MVA) data for the vast majority of BSPs and primary substations. Since P and Q monitoring data are not available for most primary substations, an improved network model with realistic Q demand at primary substations cannot be produced for Lovedean GSP. Nonetheless, the produced semi-improved network model of Lovedean network can match in daily simulation the P and Q monitoring data at GSP.

Fig. 16 shows the simulation results and monitoring data for P and Q demand at Lovedean GSP during the 18th June 2013. After the load and DG allocation (see Section 2 / Deliverable 3 [13]), a uniform power factor across all primary substations without available Q data was considered and Q was allocated accordingly so as to approximate the Q demand at GSP.

Single line diagram of Lovedean GSP group.

Simulation results and monitoring data for Lovedean GSP for a) P profile and b) Q profile. Analysis for 18th June 2013.

## Appendix B: Line Parameters of the Improved Network Models

The most important difference between an improved and a semi-improved model is the fact that line susceptances from 132 to 33kV have been updated from their original values and they have been validated in time-series simulations for multiple days.

Emphasis should be given to the fact that these line parameters could be much different from the actual line susceptance values. However, these line susceptances can provide realistic Q gains that allow the improved network models mimic the GSP behaviour during periods of minimum load. Table 5 to Table 7 show the line parameters that have been used in the improved network models of Norton (NP), Kearsley (ENWL) and City Road (UKPN) GSPs.

Line Parameters of the Improved Network Model of Norton GSP

Line Parameters of the Improved Network Model of Kearsley GSP

Line Parameters of The Improved Network Model of City Road (GSP)