# Table 2 – P2/7

| Type of Distributed Generation | Contribution (see Note 1 below) |
| --- | --- |
| Generation as listed in Tables 2-1A and 2-1B | F % of DNC |
| Generation as listed in Tables 2-2A and 2-2B | F % of DNC (see Note 2 below) |
| Plant operating for 8 hours (see Note 3 below) | Smaller of value derived from relevant row above; or 11 % of Group Demand |
| Plant operating for 12 hours (see Note 3 below) | Smaller of value derived from relevant row above; or 12 % of Group Demand |

NOTE 1:	The contributions derived from this table apply from the point of time when the DG is connected or reconnected to the demand group following the commencement of an outage. This may be immediately if the DG does not trip, otherwise it will be from the point of time when the DG is reconnected.

NOTE 2:	The value derived applies to the complete DG plant irrespective of the number of units.

NOTE 3:	The values in these two rows assume that the operating period is such that operation spans the peak demand, and the demand at start-up is the same as the demand at shut-down, ie operation is symmetrically placed on the daily load curve. If these conditions do not apply, the contribution could be optimistic (eg at one extreme, the contribution would be zero if the operating period did not span the peak demand at all), in which case the generation ought to be treated as a special case and therefore subject to detailed studies to assess the expected level of contribution – See ETR 130 [Ref 1].

# Table 2-1 F factors in % for Non-intermittent Generation

The F factors for non-intermittent generation are related directly to the number of units in the generating station. It is assumed that the energy source for the prime mover is available on demand so that Persistence does not need to be considered.

Table 2-1A High confidence data

| Type of generation | Number of units |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10+ |
| Landfill gas | 63 | 69 | 73 | 75 | 77 | 78 | 79 | 79 | 80 | 80 |
| CHP sewage treatment using a spark ignition engine | 40 | 48 | 51 | 52 | 53 | 54 | 55 | 55 | 56 | 56 |

Table 2-1B Sparse data

| Type of generation | Number of units |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10+ |
| Waste to energy | 58 | 64 | 69 | 71 | 73 | 74 | 75 | 75 | 76 | 77 |
| CCGT | 63 | 69 | 73 | 75 | 77 | 78 | 79 | 79 | 80 | 80 |
| CHP sewage treatment using a Gas Turbine | 53 | 61 | 65 | 67 | 69 | 70 | 71 | 71 | 72 | 73 |

NOTE:	This table is provided for guidance, however the data sets used to create this table have limited statistical robustness and the DNO should take care when using these F factors for these types of generation. It is preferable to seek site specific data when looking to assess the contribution to System Security from the types of DG listed in this table.

# Table 2-2 F factors in % for Intermittent Generation

The F factors for Intermittent Generation are related directly to the period of continuous generation (ie Persistence) and are not affected by the number of units at an individual site.

NOTE:   Recommended values of Tm are shown in Table 2-4.

Table 2-2A High confidence data

| Type of generation | Persistence, Tm (hours) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ½ | 2 | 3 | 18 | 24 | 120 | 360 | >360 |
| Wind farm | 28 | 25 | 24 | 14 | 11 | 0 | 0 | 0 |

Table 2-2B Sparse data

| Type of generation | Persistence, Tm (hours) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ½ | 2 | 3 | 18 | 24 | 120 | 360 | >360 |
| Small hydro | 37 | 36 | 36 | 34 | 34 | 25 | 13 | 0 |

NOTE 1:	The “small hydro” DG plants used to produce Table 2-2B were all rated below 1MW with water storage.

NOTE 2:	This table is provided for guidance, however the data sets used to create this it have limited statistical robustness and the DNO should take care in establishing appropriate F factors for this type of generation. It is preferable to seek site specific data when looking to assess the contribution

# Table 2-3 Number of DG units (N) contributing to FCO

| Type of generation | Number of units |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10+ |
| Landfill gas | 1 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 |
| CCGT | 1 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 |
| CHP sewage treatment, using a spark ignition engine | 1 | 2 | 3 | 4 | 4 | 5 | 5 | 6 | 6 | 7 |
| CHP sewage treatment using a Gas Turbine | 1 | 2 | 2 | 3 | 3 | 3 | 4 | 4 | 4 | 4 |
| Waste to energy | 1 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 4 | 4 |
| Wind farm | 1 (see Note below) |  |  |  |  |  |  |  |  |  |
| Small hydro | 1 (see Note below) |  |  |  |  |  |  |  |  |  |

NOTE:	For Intermittent Generation N is assumed to be 1 in all cases because the DNC used to determine the contribution to System Security is the DNC of the complete plant.

# Table 2-4 Recommended values for Tm

This table provides recommended values for Tm for three system conditions that may apply at the time that an infeed is lost.  For example, “Switching” values apply where the DG contribution is only required for the time necessary to reconfigure the system by switching operations.

| P2/6 demand class | Switching |  | (see Note 2 below) |
| --- | --- | --- | --- |
| A (FCO) | N/A | N/A | N/A |
| B (FCO) | 3 hours | 2 hours | 24 hours |
| C (FCO) | 3 hours | 18 hours | 15 days |
| D (FCO and SCO) (see Note 3 below) | 3 hours (see Note 4 below) | 24 hours | 90 days |
| E (FCO and SCO) (see Note 3 below) | N/A | 24 hours | 90 days |

NOTE 1:	Switching values for Tm are only appropriate where sufficient Transfer Capacity exists within the times specified in ER P2/6 Table 1.

NOTE 2:	Examples of “other outage” are an unplanned outage or an outage as part of a major project.

NOTE 3:	SCO only applies for demands greater than 100MW.

NOTE 4:	FCO only applies where compliance is achieved by automatic demand disconnection of 20MW or less.

# ENA Engineering Report 130 Issue 3 2019 Page 76

G.2  Derivation of F Factors in Table D.2.1 for non-intermittent renewable DG types

| Technology Type | Winter |  |  |  |  |  | Summer |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Number | Average | Min | Max | St Dev | Ave-1 St Dev | Number | Average | Min | Max | St Dev | Ave-1 St Dev |
| Biomass | 76 | 52% | 4% | 86% | 22% | 30% | 75 | 46% | 4% | 83% | 21% | 25% |
| CHP | 13 | 29% | 4% | 60% | 22% |  | 14 | 25% | 6% | 55% | 16% |  |
| Fossil Gas | 31 | 17% | 2% | 70% | 20% |  | 19 | 25% | 2% | 82% | 29% |  |
| Fossil Oil | 8 | 33% | 5% | 56% | 22% |  | 6 | 44% | 5% | 83% | 25% |  |
| Gas | 11 | 24% | 3% | 49% | 19% |  | 9 | 25% | 7% | 39% | 13% |  |
| Geothermal | 2 | 4% | 3% | 4% | 1% |  |  |  |  |  |  |  |
| Marine - Tidal | 3 | 16% | 8% | 29% | 11% |  | 2 | 15% | 7% | 23% | 11% |  |
| Mixed | 27 | 38% | 5% | 79% | 26% |  | 26 | 42% | 2% | 81% | 22% |  |
| Other Generation | 17 | 9% | 2% | 18% | 6% |  | 12 | 10% | 4% | 17% | 5% |  |
| Other, CHP | 62 | 27% | 2% | 80% | 24% |  | 63 | 26% | 3% | 75% | 23% |  |
| Landfill Gas | 74 | 51% | 3% | 83% | 23% | 28% | 73 | 50% | 4% | 100% | 23% | 27% |
| Waste | 71 | 54% | 2% | 82% | 19% | 35% | 69 | 48% | 5% | 78% | 16% | 32% |
| NOTE 1: Replicated from Table 5. Seasonal statistical parameters of F Factors for non-intermittent DG in the Imperial College London Report [N9] |  |  |  |  |  |  |  |  |  |  |  |  |
| NOTE 2: Data items in red font are used in EREP 130 Table D.2.1 |  |  |  |  |  |  |  |  |  |  |  |  |

NOTE 3: Other technology types are considered to either insufficiently w ell-defined or too small sample size for inclusion in EREP 130

G.3  Derivation of F Factors in Table D.2.2 for intermittent renewable DG types

| Technology Type | Season | Values | Persistence, h |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 0.5 | 2 | 3 | 6 | 12 | 18 | 24 | 48 | 120 | 360 | 480 | Comments |
| Onshore wind | Winter | Average (%) | 26 | 24 | 24 | 22 | 19 | 16 | 14 | 9 | 4 | 3 | 3 |  |
|  |  | Min (%) | 6 | 6 | 5 | 5 | 4 | 3 | 2 | 1 | 1 | 1 | 1 |  |
|  |  | Max (%) | 59 | 58 | 57 | 56 | 54 | 52 | 48 | 38 | 18 | 16 | 16 |  |
|  |  | St Dev (%) | 9 | 9 | 8 | 8 | 8 | 7 | 7 | 5 | 2 | 2 | 2 |  |
|  |  | Ave - 1 St Dev | 17 | 15 | 15 | 14 | 11 | 9 | 7 | 4 | 2 | 1 | 1 | Value for Tm 3 amended to 15% in Table D.2.2 as F Factors can't increase |
|  | Summer | Average (%) | 19 | 18 | 17 | 15 | 13 | 11 | 9 | 6 | 3 | 3 | 3 |  |
|  |  | Min (%) | 5 | 5 | 4 | 4 | 3 | 2 | 2 | 1 | 1 | 1 | 1 |  |
|  |  | Max (%) | 40 | 38 | 37 | 35 | 31 | 28 | 27 | 26 | 22 | 18 | 14 |  |
|  |  | St Dev (%) | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 4 | 3 | 2 | 1 |  |
|  |  | Ave - 1 St Dev | 13 | 12 | 11 | 9 | 8 | 6 | 4 | 2 | 0 | 0 | 0 | Values for Tm 360, 480 set to zero as F Factors can't increase |
| Offshore wind | Winter | Average (%) | 32 | 31 | 30 | 29 | 26 | 23 | 20 | 13 | 6 | 4 | 4 |  |
|  |  | Min (%) | 6 | 5 | 5 | 4 | 4 | 3 | 2 | 1 | 1 | 1 | 1 |  |
|  |  | Max (%) | 51 | 49 | 48 | 46 | 43 | 40 | 37 | 26 | 19 | 19 | 18 |  |
|  |  | St Dev (%) | 10 | 10 | 10 | 10 | 9 | 8 | 8 | 6 | 4 | 3 | 3 |  |
|  |  | Ave - 1 St Dev | 22 | 21 | 20 | 19 | 17 | 15 | 12 | 7 | 2 | 1 | 1 |  |
|  | Summer | Average (%) | 24 | 23 | 22 | 20 | 17 | 15 | 13 | 8 | 4 | 3 | 3 |  |
|  |  | Min (%) | 3 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |
|  |  | Max (%) | 35 | 34 | 33 | 31 | 30 | 30 | 29 | 28 | 25 | 20 | 12 |  |
|  |  | St Dev (%) | 8 | 7 | 7 | 7 | 6 | 6 | 6 | 5 | 4 | 3 | 2 |  |
|  |  | Ave - 1 St Dev | 16 | 16 | 15 | 13 | 11 | 9 | 7 | 3 | 0 | 0 | 0 | Values for Tm 480 set to zero as F Factors can't increase. |

(continued)

| Technology Type | Season | Values | Persistence, h |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 0.5 | 2 | 3 | 6 | 12 | 18 | 24 | 48 | 120 | 360 | 480 | Comments |
| Solar | Winter | Average (%) | 6 | 6 | 5 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |
|  |  | Min (%) | 3 | 3 | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |
|  |  | Max (%) | 13 | 12 | 12 | 10 | 5 | 5 | 5 | 4 | 4 | 4 | 4 |  |
|  |  | St Dev (%) | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 |  |
|  |  | Ave - 1 St Dev | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Values set to zero as Solar can't contribute to security if demand peak is after dusk |
|  | Summer | Average (%) | 16 | 15 | 14 | 12 | 5 | 2 | 2 | 2 | 2 | 2 | 2 |  |
|  |  | Min (%) | 3 | 3 | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |
|  |  | Max (%) | 22 | 22 | 21 | 20 | 9 | 3 | 3 | 3 | 3 | 3 | 3 |  |
|  |  | St Dev (%) | 4 | 4 | 4 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 |  |
|  |  | Ave - 1 St Dev | 12 | 11 | 10 | 9 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | Values for Tm >18 set to zero as Solar can't contribute to security overnight |
| NOTE 1: Replicated from Table 9. F Factors for intermittent renew ables DG types in the Imperial College London Report [N9] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NOTE 2: Data items in red font are used in EREP 130 Table D.2.2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NOTE 3: Where F Factors are adjusted from the (Ave - 1St Dev) formulae, justification is provided in the comments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

G.4  Derivation of F Factors in Table D.2.2 for intermittent hydro DG types

| Technology Type | Season | Values | Persistence, h |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 0.5 | 2 | 3 | 6 | 12 | 18 | 24 | 48 | 120 | 360 | 480 | Comments |
| Hydro run-of-river and poundage | Winter | Average (%) | 36 | 36 | 35 | 35 | 34 | 33 | 31 | 28 | 21 | 10 | 9 |  |
|  |  | Min (%) | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 4 | 2 | 1 | 1 |  |
|  |  | Max (%) | 74 | 74 | 74 | 74 | 74 | 74 | 73 | 73 | 69 | 56 | 52 |  |
|  |  | St Dev (%) | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 13 | 12 |  |
|  |  | Ave - 1 St Dev | 19 | 19 | 18 | 18 | 17 | 16 | 15 | 12 | 5 | 0 | 0 |  |
|  | Summer | Average (%) | 17 | 17 | 16 | 16 | 15 | 14 | 13 | 11 | 8 | 3 | 3 |  |
|  |  | Min (%) | 3 | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |
|  |  | Max (%) | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 39 | 33 | 12 | 8 |  |
|  |  | St Dev (%) | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 3 | 2 |  |
|  |  | Ave - 1 St Dev | 7 | 7 | 7 | 7 | 6 | 5 | 4 | 2 | 1 | 0 | 0 |  |
| Hydro water reservoir | Winter | Average (%) | 29 | 29 | 28 | 27 | 26 | 23 | 22 | 21 | 18 | 12 | 10 |  |
|  |  | Min (%) | 4 | 4 | 4 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |
|  |  | Max (%) | 76 | 76 | 76 | 75 | 74 | 72 | 70 | 70 | 68 | 60 | 56 |  |
|  |  | St Dev (%) | 17 | 17 | 18 | 18 | 19 | 19 | 19 | 18 | 16 | 13 | 12 |  |
|  |  | Ave - 1 St Dev | 12 | 12 | 10 | 9 | 7 | 4 | 3 | 3 | 2 | 0 | 0 |  |
|  | Summer | Average (%) | 16 | 16 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 6 | 5 |  |
|  |  | Min (%) | 3 | 3 | 3 | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 |  |
|  |  | Max (%) | 70 | 70 | 70 | 70 | 70 | 69 | 69 | 67 | 61 | 52 | 52 |  |
|  |  | St Dev (%) | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 11 | 8 | 7 |  |
|  |  | Ave - 1 St Dev | 5 | 5 | 4 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Values for Tm >18 set to zero as F Factors can't increase |

NOTE 1: Replicated from Table 10. F Factors for intermittent hydro DG types in the Imperial College London Report [N9]

NOTE 2: Data items in red font are used in EREP 130 Table D.2.2

NOTE 3: Where F Factors are adjusted from the (Ave - 1St Dev) formulae, justification is provided in the comments

G.5  Derivation of F Factors in Table D.3 for non-intermittent renewable DG types

| Capacity Factor | Winter |  |  |  |  | Summer |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Number | Average | Min | Max | St Dev | Ave - 1St Dev | Number | Average | Min | Max | St Dev | Ave - 1St Dev |
| Biomass |  |  |  |  |  |  |  |  |  |  |  |  |
| 90% | 22 | 76% | 64% | 86% | 6% | 49% | 15 | 72% | 61% | 83% | 7% | 46% |
| 70% | 20 | 60% | 42% | 78% | 11% | 36% | 18 | 58% | 30% | 77% | 12% | 35% |
| 50% | 11 | 45% | 32% | 57% | 9% | 26% | 19 | 42% | 30% | 55% | 7% | 29% |
| 30% | 18 | 30% | 23% | 37% | 4% | 3% | 12 | 32% | 28% | 36% | 3% | 6% |
| 10% | 5 | 7% | 4% | 14% | 4% | 0% | 11 | 13% | 4% | 20% | 7% | 0% |
| Other, Landfill Gas |  |  |  |  |  |  |  |  |  |  |  |  |
| 90% | 22 | 74% | 50% | 83% | 7% | 67% | 21 | 72% | 53% | 100% | 10% | 62% |
| 70% | 14 | 65% | 41% | 75% | 9% | 56% | 14 | 66% | 43% | 78% | 9% | 57% |
| 50% | 15 | 51% | 43% | 57% | 4% | 47% | 13 | 54% | 42% | 58% | 4% | 50% |
| 30% | 12 | 29% | 20% | 36% | 6% | 23% | 14 | 29% | 11% | 40% | 8% | 21% |
| 10% | 11 | 13% | 3% | 19% | 5% | 8% | 11 | 13% | 4% | 19% | 4% | 9% |
| Waste |  |  |  |  |  |  |  |  |  |  |  |  |
| 90% | 7 | 73% | 64% | 82% | 6% | 67% | 4 | 71% | 60% | 78% | 8% | 63% |
| 70% | 39 | 64% | 40% | 75% | 7% | 57% | 26 | 59% | 44% | 72% | 8% | 51% |
| 50% | 14 | 50% | 37% | 58% | 7% | 43% | 26 | 45% | 36% | 54% | 5% | 40% |
| 30% | 5 | 26% | 22% | 28% | 3% | 23% | 8 | 31% | 22% | 36% | 4% | 27% |
| 10% | 6 | 7% | 2% | 15% | 5% | 2% | 5 | 14% | 5% | 20% | 6% | 8% |

(continued)

NOTE 1: Replicated from Table 6. F Factors of non-intermittent generation for different capacity factors and seasons in the Imperial College London Report [N9]

NOTE 2: Data items in red font are used in EREP 130 Table D.3

NOTE 3: The data analysis for biomass generators show ed that capacity factors may vary more than 20% year to year, for more than 50% of the population. To accommodate this to some extent the F factors have been reduced by applying that of the next low est capacity factor value. For example rather than use a 70% F Factor (76-6) for a biomass plant w ith a 90% capacity factor, a 49% F Factor (60-11) is used