## Methodology
2 SETTING THE CURTAILMENT LIMIT
2.1 Unless otherwise directed by the Authority, the Import Curtailment Limit and Export Curtailment Limit will be determined by assessing the parts of the existing Distribution System that require reinforcement under the Minimum Scheme, in accordance with Paragraphs 2.2 to 2.7. If the Authority directs the Company to use an alternative approach to determine either the Import Curtailment Limit and/or the Export Curtailment Limit, the Company shall provide to the Customer details of the methodology and data used in the calculation.
Input data
2.2 The following data shall be used for the calculation of the Curtailment Limit.
(a) Profile data (in/converted to kVA based on an assumed 0.95 power factor) relating to the most recent 12 months of available data including:
(i) annual half-hourly observed/measured data from the asset to be reinforced; | This data is input in columns J, K, L and M. The spreadsheet contains sample data to populate columns J and K with England and Wales data derived from columns AI and AJ. Cell B11 allows the level of generation to be flexed to show the effect of more generation. In the example the storage profile in column M is set to zero.Column L contains a representative daylight profile.
(ii) half-hourly metered data from generation connected to the asset to be reinforced;
(iii) half-hourly representative daylight profile (1 to signify day, 0 to signify night) for the asset to be reinforced; and
(iv) half-hourly data from battery storage connected to the asset to be reinforced,
or equivalent data from other sources. The Company shall correct for missing data, erroneously shown negative values and abnormal running arrangements and/or similar anomalies. Where data for the asset is not available, data from (i) the feeding primary substation would be used for HV and LV assets, (ii) the relevant bulk supply point for 33kV and 66kV assets, and (iii) the relevant grid supply point data for 132kV assets.
(b) for a Demand Connection, the following data (in kVA unless otherwise stated) shall also be used for the calculation of the Import Curtailment Limit:
(i) Network Asset Demand Capacity, being the capacity based on the Company’s assessment of the thermal ratings, voltage change and upstream restrictions and compliance with its relevant design, planning and security of supply policies | Network Asset Demand Capacity is input in B22
(ii) Inflight Demand Acceptances, being the aggregated Maximum Import Capacity of all connection offers that utilise the asset being assessed but have yet to be connected/energised and hence are not included in the current maximum demand; | Inflight Demand Acceptances is input in B24
(iii) Largest Inflight Demand Offers, being the aggregate Maximum Import Capacity of the two largest connection offers that utilise the asset being assessed that have been issued to a Customer but have yet to be accepted; | Largest Inflight Demand Offers is input in B25
(iv) Other Inflight Demand Offers, being the aggregated Maximum Import Capacity of all other connection offers that utilise the asset being assessed that have been issued to a Customer but have yet to be accepted; | Other Inflight Demand Offers is input in B26
(v) Demand Confidence Factor, being a confidence factor representing the likelihood of the Other Inflight Demand Offers being accepted by Customers, and has the value 50%; and | Demand Confidence Factor is input in B27
(vi) New Demand Connection Capacity, being the requested Maximum Import Capacity of the connection for which the Curtailment Limit is being calculated. | New Demand Connection Capacity is input in B30
Note that for meshed networks, (ii), (iii), (iv) and (vi) may be adjusted by a factor determined through power flow analysis to reflect the extent the asset being assessed is utilised by these connections. | These are input in cells E24-E26 and cell E30. These will be derived from power systems analysis. Where there are a number of offfers using the same asset, this figure will be a weighted average.
(c) for a Generation Connection, the following data (in kVA unless otherwise stated) shall also be used for the calculation of the Export Curtailment Limit:
(i) Network Asset Generation Capacity, being the capacity based on the Company’s assessment of the thermal ratings, voltage change and upstream restrictions and compliance with its relevant design, planning and security of supply policies; | Network Asset Generation Capacity is input in B41
(ii) Inflight Generation Acceptances, being the aggregated Maximum Export Capacity of all connections offers that utilise the asset being assessed but have yet to be connected/energised and hence are not included in the current maximum generation/minimum demand. The aggregated values shall be categorised as either PV Generation or Non-PV Generation; | Inflight Generation Acceptances is input in B43 for Non-PV Generation and C43 for PV Generation
(iii) Largest Inflight Generation Offers, being the aggregate Maximum Export Capacity of the two largest connection offers that utilise the asset being assessed that have been issued to a Customer but not have to be accepted. The aggregated values shall be categorised as either PV Generation or Non-PV Generation; | Largest Inflight Generation Offer is input in B44 for Non-PV Generation and C44 for PV Generation
(iv) Other Inflight Generation Offers, being the aggregated Maximum Export Capacity of all other connection offers that utilise the asset being assessed that have been issued to a Customer but have yet to be accepted. The aggregated values shall be categorised as either PV Generation or Non-PV Generation; | Other Inflight Generation Offers is input in B45 for Non-PV Generation and C45 for PV Generation
(v) Generation Confidence Factor, being a confidence factor representing the likelihood of the Other Inflight Generation Offers being accepted by the Customers, and has the value 50%; and | Generation Confidence Factor is input in B46
(vi) New Generation Connection Capacity, being the requested Maximum Export Capacity of the connection for which the Curtailment Limit is being calculated. The aggregated values shall be categorised as either PV Generation or Non-PV Generation. | New Generation Connection Capacity is input in B49 for Non-PV Generation and C49 for PV Generation
Note that for meshed networks, (ii), (iii), (iv) and (vi) may be adjusted by a factor determined through power flow analysis to reflect the extent the asset being assessed is utilised by these connections. | These are input in cells E43-E45 and cell E49. These will be derived from power systems analysis. Where there are a number of offfers using the same asset, this figure will be a weighted average.
(d) Curtailment Threshold, being the percentage of the Network Asset Demand Capacity or Network Asset Generation Capacity, which, if exceeded by the Committed Demand Capacity or Committed Generation Capacity, will determine the number of hours where curtailment may be required, and is set at 95%. | The Curtailment Threshold for the demand calculation is input in B32 and copied into B51 for the generation calculation. It is set at 95%. This value is reflected in columns W and AF.
Calculating the Import Curtailment Limit
2.3 The following process shall be used for the calculation of the Import Curtailment Limit:
(a) The underlying true demand will be assessed as follows:
(i) Take annual half-hourly observed/measured data, from the asset as calculated in accordance with Paragraph 2.2(a)(i). | This data is in column J
(ii) Adjust for ‘latent demand’ by subtracting data from half-hourly metered generation (negative values) connected to the asset as provided in accordance with Paragraph 2.2(a)(ii). | This is calculated in column N.
(iii) This gives annual half-hourly true (gross) demand profile. For cases where this demand profile is not available at the asset in question, e.g. it is available at substation level and not at circuits supplied by that substation, the true (gross) demand profile can be scaled to the expected maximum and minimum true demand of the asset in question. | This profile is calculated in column O. Whether the data is scaled is selected in cell C16. The profile will be scaled to the selected values in cells with the profiles adjusted for the Maximum Demand (selected in C17) and the Minimum Demand (selcted in C18). If the profile is for the asset being analysed the profile maximum (B12) and profile minimum (B13) will be used. Otherwise the values input in cells B17 and B18 will be used.
(iv) Subtract from the annual half-hourly true (gross) demand profile (adjusted for the asset in question if required) calculated in accordance with Paragraph 2.3(a)(iii) the import data from half-hourly battery storage connected to the asset provided in accordance with Paragraph 2.2(a)(iv) to calculate the underlying true demand profile (baseline). | This is calculated in column P.
(v) Adjust for battery storage that currently utilise the asset to be reinforced by adding the maximum import from the import data from half-hourly battery storage connected to the asset provided in accordance with Paragraph 2.2(a)(iv). This is added to the underlying true demand profile (baseline) as a continuous constant profile. | This is calculated in column Q.
(b) Sort the underlying true demand profile calculated in Paragraph 2.3(a)(v) in descending order to produce the underlying true demand duration curve. | This is calculated in column R. Load duration curve indicates the variation of the load, but with the load arranged in descending order of magnitude. Load duration curve give the number of hours for which a particular load lasts during a day.
(c) Calculate the Committed Demand Capacity for each half-hour will be calculated as follows:
(i) Take the adjusted demand duration curve in Paragraph 2.3(b).
(ii) Add the Maximum Import Capacity of Inflight Demand Acceptances and the Largest Inflight Demand Offers, plus the Other Inflight Demand Offers multiplied by the Demand Confidence Factor. | These calculations are shown in cells B24 to B28. The result in B27 in each half-hour period in column S.
(iii) Add the Maximum Import Capacity of the new connection for which the Curtailment Limit is being calculated. | This value is input in B30 and then reflected in each half-hour period in column T. Columns R, S and T are summated with the result in column U.
(iv) The sum of (i) to (iii), above is then divided by the Network Asset Demand Capacity to represent it as a percentage of the firm capacity of the asset. | Each value in column U is then divided by the Network Asset Demand Capacity with the results in column V.
(d) The Import Curtailment Limit will be determined by assessing the number of hours for which demand exceeds the capacity threshold as follows:
(i) Quantify the number of hours that the Committed Demand Capacity relative to the Network Asset Demand Capacity exceeds the Curtailment Threshold.. | The Committed Demand Capacity is checked to see if it exceeds the Curtailment Threshold with the result shown in Column X. The number of times the threhold in exceeded is calculated and divided by 2 to give the Demand Curtailment Limit. This is determined in Cell B34.
(ii) If the true demand profile does not correspond to a whole year, the calculated hours from the previous step is divided by the number of hours in the true demand profile to determine the percentage curtailed. This is then multiplied by 8760 to determine an annual figure for the Import Curtailment Limit. | These calculations are shown in cells B36 to B38.
(e) Where multiple assets require reinforcement, the Import Curtailment Limit for each asset should will calculated and the largest value so calculated will be the Import Curtailment Limit.
Calculating the Export Curtailment Limit
2.4 The Export Curtailment Limit will be calculated as follows:
(a) Assessment of underlying generation:
(i) Take the underlying true demand profile (baseline) as calculated in accordance with Paragraph 2.3(a)(iv) and add in the annual half-hourly generation from assets (generation is treated as negative values) as provided in accordance with Paragraph 2.2(a)(ii). The generation data may need to be scaled to the expected output of the generation where this profile is not available at the asset in question, e.g. it is available at substation level and not at circuits supplied by that substation, the generation profile can be scaled to the expected maximum gross generation excluding battery charging of the asset in question. | This generation profile from column K adjusted where the profile is not for the assest being analysed. Whether the data is scaled is selected in cell C16. The profile will be scaled to the selected value in cells with the profiles adjusted for the Maximum Gross Generation for the assset (input in B19) and the Maximum Generation from the profile (determined in B15) with the result in Column Y.
(ii) This gives annual half-hourly generation profile without the effects of battery charging. | To this is added the data from column P. This is calculated in column Z.
(b) The Committed Generation Capacity will be calculated as follows:
(i) Take the generation profile determined in Paragraph 2.4(a)(ii).
(ii) Add the Maximum Export Capacity (expressed as a negative value) of Inflight Generation Acceptances and the Largest Inflight Generation Offers, plus the Other Inflight Generation Offers multiplied by the Generation Confidence Factor. PV Generation is only added to half-hourly periods where it is daylight by multiplying the PV Generation data by the representative daylight profile provided in Paragraph 2.2(a)(iii). | These calculations are shown in cells B43 to B47 for Non-PV Generation and in cells C43 to C47 for PV Generation. The result in C47 is multiplied by the appropriate daylight profile factor from column L and added to the result from B47 and the result included in each half-hour period in column AA.
(iii) Add the Maximum Export Capacity (expressed as a negative value) of the connection for which the Curtailment Limit is being calculated. PV Generation is only added to half-hourly periods where it is daylight by multiplying the PV Generation data by the representative daylight profile provided in Paragraph 2.2(a)(iii). | These values are input in cells B49 for Non-PV Generation and in cell C49 for PV Generation. The input in C49 is multiplied by the appropriate daylight profile factor from column L and added to the input from B49 and the result included in each half-hour period in column AB.
(iv) The sum of (i) to (iii) above is then divided by the Network Asset Generation Capacity to represent it as a percentage of the firm capacity of the asset. | Columns Z, AA and AB are summated with the result in column AC. Each value in column AC is then divided by the Network Asset Generation Capacity with the results in column AD.
(c) Sort the Committed Generation Capacity as a percentage of the Network Asset Generation Capacity calculated in Paragraph 2.4(b)(iv) in descending order to produce the committed generation duration curve. | This is calculated in column AE.
(d) The Export Curtailment Limit is determined by assessing the number of hours reverse power flows exceed the capacity threshold:
(i) Quantify the number of hours that the Committed Generation Capacity relative to the Network Asset Generation Capacity exceeds the Curtailment Threshold. | The Committed Generation Capacity is checked to see if it exceeds the Curtailment Threshold with the result shown in Column AD. The number of times the threhold in exceeded is calculated and divided by 2 to give the Generation Curtailment Limit. This is determined in Cell B48.
(ii) If the generation profile (excluding battery charging) does not correspond to a whole year, the calculated hours from the previous step is divided by the number of hours in the profile to determine the percentage curtailed. This is then multiplied by 8760 to determine an annual figure for the Export Curtailment Limit. | These calculations are shown in cells B55 to B57.
(e) Where multiple assets require reinforcement, the Export Curtailment Limit for each asset should be calculated and largest value used for the overall Export Curtailment Limit.
General
2.5 The Curtailment Limit(s) will not be recalculated once the connection offer has been issued to the Customer unless there has been material circumstances and both the Company and the Customer agree to the recalculation or the Authority directs that a different Curtailment Limit be used. Where the Company and Customer cannot agree, the matter should be resolved through the disputes process set out in the Curtailable Connection Agreement.
2.6 A worked example of a calculation modelling tool will be published and made available on the DCUSA website.
2.7 The Company may use whatever software tool it chooses providing it gives the same answer as the tool described in Paragraph 2.6. The Company should make available data used in its calculations when requested by the Customer.

## Calculation
CALCULATION OF IMPORT AND EXPORT CURTAILMENT LIMITS |  |  |  |  | SETTLEMENT_DATE | SETTLEMENT_PERIOD | HOURS | HH observed/ measured data Paragraph 2.2 (a)(i) | HH metered data from generation Paragraph 2.2 (a)(ii) | HH daylight profile Paragraph 2.2 (a)(iii) | HH data from battery storage Paragraph 2.2 (a)(iv) | Adjust for ‘latent demand’ Paragraph 2.3(a)(ii). | Asset Adjusted True Demand Profile Paragraph 2.3(a)(iii). | Underlying True Demand Profile (baseline) Paragraph 2.3(a)(iv). | Underlying True Demand Profile Paragraph 2.3(a)(v). | Underlying True Demand Duration Curve Paragraph 2.3(b) | Capacity of Inflight Demand Offers/ Connections Paragraph 2.3(c)(ii) | Capacity Of New Demand Connection Paragraph 2.3(c)(iii) | Committed Demand Capacity Paragraph 2.3(c)(iii) | Committed Demand Capacity relative to asset capacity Paragraph 2.3(c)(iv) | Curtailment Threshold for demand Paragraph 2.2(d) | Exceed Demand Threshold Paragraph 2.3(d) | Generation Profile (Asset adjusted where required) Paragraph 2.4(a)(i). | Generation Profile (baseline) Paragraph 2.4(a)(i)/ 2.4(a)(ii) | Capacity of Inflight Generation Offers/ Connections Paragraph 2.4(b)(ii) | Capacity Of New Generation Connection Paragraph 2.4(b)(iii) | Committed Generation Capacity Paragraph 2.4(b)(iii) | Committed Generation Capacity relative to asset capacity Paragraph 2.4(b)(iv) | Committed Generation Capacity duration curve Paragraph 2.4(c) | Generation Curtailment Threshold Paragraph 2.2(d) | Exceed Generation Threshold Paragraph 2.4(d) | EXAMPLE GROSS DEMAND | EXAMPLE GROSS GENERATION
[5 empty] | 2019-01-01 | 1 | 0.5 | 1682 | -160 | 0 | 0 | 1842 | 764.8805 | 764.8805 | 764.8805 | 3600 | 780 | 200 | 4580 | 114.5% | 95% | 100% | -183.0664 | 581.8141 | -2750 | -200 | -2368.1859 | 59.2% | 117.8% | 95% | 100% | 1842 | -160 | Yes
LOAD PROFILE INPUTS |  |  |  |  | 2019-01-01 | 2 | 1 | 1731 | -157 | 0 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 3592.1682 | 780 | 200 | 4572.1682 | 114.3% | 95% | 100% | -179.6339 | 657.2994 | -2750 | -200 | -2292.7006 | 57.32% | 117.4% | 95% | 100% | 1888 | -157 | No
LOAD PROFILE CALCULATION |  |  |  |  | 2019-01-01 | 3 | 1.5 | 1715 | -153 | 0 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 3576.5045 | 780 | 200 | 4556.5045 | 113.9% | 95% | 100% | -175.0572 | 630.5487 | -2750 | -200 | -2319.4513 | 57.99% | 117.3% | 95% | 100% | 1868 | -153
DEMAND INPUTS |  |  |  |  | 2019-01-01 | 4 | 2 | 1646 | -149 | 0 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 3574.9382 | 780 | 200 | 4554.9382 | 113.9% | 95% | 100% | -170.4805 | 520.7808 | -2750 | -200 | -2429.2192 | 60.73% | 116.3% | 95% | 100% | 1795 | -149
DEMAND CALCULATION |  |  |  |  | 2019-01-01 | 5 | 2.5 | 1582 | -145 | 0 | 0 | 1727 | 584.7486 | 584.7486 | 584.7486 | 3574.9382 | 780 | 200 | 4554.9382 | 113.9% | 95% | 100% | -165.9039 | 418.8447 | -2750 | -200 | -2531.1553 | 63.28% | 116% | 95% | 100% | 1727 | -145
GENERATION INPUTS |  |  |  |  | 2019-01-01 | 6 | 3 | 1560 | -141 | 0 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 3570.2391 | 780 | 200 | 4550.2391 | 113.8% | 95% | 100% | -161.3272 | 382.6959 | -2750 | -200 | -2567.3041 | 64.18% | 116% | 95% | 100% | 1701 | -141
GENERATION CALCULATION |  |  |  |  | 2019-01-01 | 7 | 3.5 | 1485 | -137 | 0 | 0 | 1622 | 420.2803 | 420.2803 | 420.2803 | 3559.2745 | 780 | 200 | 4539.2745 | 113.5% | 95% | 100% | -156.7506 | 263.5297 | -2750 | -200 | -2686.4703 | 67.16% | 115.7% | 95% | 100% | 1622 | -137
[5 empty] | 2019-01-01 | 8 | 4 | 1464 | -133 | 0 | 0 | 1597 | 381.1212 | 381.1212 | 381.1212 | 3554.5754 | 780 | 200 | 4534.5754 | 113.4% | 95% | 100% | -152.1739 | 228.9473 | -2750 | -200 | -2721.0527 | 68.03% | 115.7% | 95% | 100% | 1597 | -133
LOAD PROFILE DATA |  |  |  |  | 2019-01-01 | 9 | 4.5 | 1443 | -130 | 0 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 3553.0091 | 780 | 200 | 4533.0091 | 113.3% | 95% | 100% | -148.7414 | 194.787 | -2750 | -200 | -2755.213 | 68.88% | 115% | 95% | 100% | 1573 | -130
GENERATION FACTOR (FOR TEST DATA ONLY) | 1 |  |  |  | 2019-01-01 | 10 | 5 | 1427 | -128 | 0 | 0 | 1555 | 315.3339 | 315.3339 | 315.3339 | 3543.6109 | 780 | 200 | 4523.6109 | 113.1% | 95% | 100% | -146.4531 | 168.8808 | -2750 | -200 | -2781.1192 | 69.53% | 114.8% | 95% | 100% | 1555 | -128
DEMAND PROFILE MAXIMUM | 3652 |  |  |  | 2019-01-01 | 11 | 5.5 | 1433 | -125 | 0 | 0 | 1558 | 320.033 | 320.033 | 320.033 | 3542.0445 | 780 | 200 | 4522.0445 | 113.1% | 95% | 100% | -143.0206 | 177.0124 | -2750 | -200 | -2772.9876 | 69.32% | 114.6% | 95% | 100% | 1558 | -125
DEMAND PROFILE MINIMUM | 1226 |  |  |  | 2019-01-01 | 12 | 6 | 1457 | -122 | 0 | 0 | 1579 | 352.9266 | 352.9266 | 352.9266 | 3534.2127 | 780 | 200 | 4514.2127 | 112.9% | 95% | 100% | -139.5881 | 213.3385 | -2750 | -200 | -2736.6615 | 68.42% | 114.2% | 95% | 100% | 1579 | -122
DEMAND PROFILE RANGE | 2426 |  |  |  | 2019-01-01 | 13 | 6.5 | 1513 | -120 | 0 | 0 | 1633 | 437.5103 | 437.5103 | 437.5103 | 3531.08 | 780 | 200 | 4511.08 | 112.8% | 95% | 100% | -137.2998 | 300.2105 | -2750 | -200 | -2649.7895 | 66.24% | 113.9% | 95% | 100% | 1633 | -120
GENERATION PROFILE MAXIMUM GROSS GENERATION | -874 |  |  |  | 2019-01-01 | 14 | 7 | 1553 | -117 | 0 | 0 | 1670 | 495.4658 | 495.4658 | 495.4658 | 3521.6818 | 780 | 200 | 4501.6818 | 112.5% | 95% | 100% | -133.8673 | 361.5985 | -2750 | -200 | -2588.4015 | 64.71% | 113.6% | 95% | 100% | 1670 | -117
Scaling Parameters | Scaling | Yes | kVA |  | 2019-01-01 | 15 | 7.5 | 1603 | -115 | 0 | 0 | 1718 | 570.6513 | 570.6513 | 570.6513 | 3513.85 | 780 | 200 | 4493.85 | 112.3% | 95% | 100% | -131.5789 | 439.0723 | -2750 | -200 | -2510.9277 | 62.77% | 113.4% | 95% | 100% | 1718 | -115
Asset Maximum Demand (Minimum Generation) | 3600 | 3600 | kVA |  | 2019-01-01 | 16 | 8 | 1639 | -112 | 0 | 0 | 1751 | 622.3413 | 622.3413 | 622.3413 | 3507.5845 | 780 | 200 | 4487.5845 | 112.2% | 95% | 100% | -128.1465 | 494.1948 | -2750 | -200 | -2455.8052 | 61.4% | 112.9% | 95% | 100% | 1751 | -112
Asset Minimum Demand (Maximum Generation) | -200 | -200 | kVA |  | 2019-01-01 | 17 | 8.5 | 1684 | -111 | 0 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 3506.0181 | 780 | 200 | 4486.0181 | 112.2% | 95% | 100% | -127.0023 | 564.259 | -2750 | -200 | -2385.741 | 59.64% | 112.9% | 95% | 100% | 1795 | -111
Asset Maximum Gross Generation | -1000 | -1000 | kVA |  | 2019-01-01 | 18 | 9 | 1735 | -118 | 0 | 0 | 1853 | 782.1105 | 782.1105 | 782.1105 | 3504.4518 | 780 | 200 | 4484.4518 | 112.1% | 95% | 100% | -135.0114 | 647.099 | -2750 | -200 | -2302.901 | 57.57% | 112.8% | 95% | 100% | 1853 | -118
[5 empty] | 2019-01-01 | 19 | 9.5 | 1805 | -137 | 0 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 3504.4518 | 780 | 200 | 4484.4518 | 112.1% | 95% | 100% | -156.7506 | 764.7663 | -2750 | -200 | -2185.2337 | 54.63% | 112.4% | 95% | 100% | 1942 | -137
DEMAND DATA |  |  |  |  | 2019-01-01 | 20 | 10 | 1868 | -161 | 1 | 0 | 2029 | 1057.7906 | 1057.7906 | 1057.7906 | 3504.4518 | 780 | 200 | 4484.4518 | 112.1% | 95% | 100% | -184.2105 | 873.5801 | -3550 | -400 | -3076.4199 | 76.91% | 112.3% | 95% | 100% | 2029 | -161
Network Asset Demand Capacity | 4000 |  | kVA |  | 2019-01-01 | 21 | 10.5 | 1912 | -195 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 3498.1863 | 780 | 200 | 4478.1863 | 112% | 95% | 100% | -223.1121 | 956.8549 | -3550 | -400 | -2993.1451 | 74.83% | 112.3% | 95% | 100% | 2107 | -195
|  |  |  | Usage Factor | 2019-01-01 | 22 | 11 | 1945 | -227 | 1 | 0 | 2172 | 1281.7807 | 1281.7807 | 1281.7807 | 3495.0536 | 780 | 200 | 4475.0536 | 111.9% | 95% | 100% | -259.7254 | 1022.0553 | -3550 | -400 | -2927.9447 | 73.2% | 112% | 95% | 100% | 2172 | -227
Inflight Demand Acceptances | 400 |  | kVA | 50% | 2019-01-01 | 23 | 11.5 | 1961 | -258 | 1 | 0 | 2219 | 1355.3998 | 1355.3998 | 1355.3998 | 3495.0536 | 780 | 200 | 4475.0536 | 111.9% | 95% | 100% | -295.1945 | 1060.2053 | -3550 | -400 | -2889.7947 | 72.24% | 111.8% | 95% | 100% | 2219 | -258
Largest Inflight Demand Offers | 400 |  | kVA | 70% | 2019-01-01 | 24 | 12 | 1988 | -272 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 3495.0536 | 780 | 200 | 4475.0536 | 111.9% | 95% | 100% | -311.2128 | 1108.408 | -3550 | -400 | -2841.592 | 71.04% | 111.7% | 95% | 100% | 2260 | -272
Other Inflight Demand Offers | 1000 |  | kVA | 60% | 2019-01-01 | 25 | 12.5 | 2041 | -267 | 1 | 0 | 2308 | 1494.8063 | 1494.8063 | 1494.8063 | 3491.9209 | 780 | 200 | 4471.9209 | 111.8% | 95% | 100% | -305.492 | 1189.3143 | -3550 | -400 | -2760.6857 | 69.02% | 111.5% | 95% | 100% | 2308 | -267
Demand Confidence Factor | 50% |  |  |  | 2019-01-01 | 26 | 13 | 2078 | -257 | 1 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 3490.3545 | 780 | 200 | 4470.3545 | 111.8% | 95% | 100% | -294.0503 | 1243.0478 | -3550 | -400 | -2706.9522 | 67.67% | 111.2% | 95% | 100% | 2335 | -257
Inflight Demand Connection Capacity | 780 |  | kVA |  | 2019-01-01 | 27 | 13.5 | 2127 | -231 | 1 | 0 | 2358 | 1573.1245 | 1573.1245 | 1573.1245 | 3485.6554 | 780 | 200 | 4465.6554 | 111.6% | 95% | 100% | -264.3021 | 1308.8224 | -3550 | -400 | -2641.1776 | 66.03% | 110.9% | 95% | 100% | 2358 | -231
[5 empty] | 2019-01-01 | 28 | 14 | 2152 | -203 | 1 | 0 | 2355 | 1568.4254 | 1568.4254 | 1568.4254 | 3479.3899 | 780 | 200 | 4459.3899 | 111.5% | 95% | 100% | -232.2654 | 1336.1599 | -3550 | -400 | -2613.8401 | 65.35% | 110.5% | 95% | 100% | 2355 | -203
New Demand Connection Capacity | 200 |  | kVA | 100% | 2019-01-01 | 29 | 14.5 | 2203 | -175 | 1 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 3477.8236 | 780 | 200 | 4457.8236 | 111.4% | 95% | 100% | -200.2288 | 1404.2229 | -3550 | -400 | -2545.7771 | 63.64% | 110.5% | 95% | 100% | 2378 | -175
[5 empty] | 2019-01-01 | 30 | 15 | 2260 | -145 | 1 | 0 | 2405 | 1646.7436 | 1646.7436 | 1646.7436 | 3476.2572 | 780 | 200 | 4456.2572 | 111.4% | 95% | 100% | -165.9039 | 1480.8397 | -3550 | -400 | -2469.1603 | 61.73% | 110.3% | 95% | 100% | 2405 | -145
Curtailment Threshold | 95% |  |  |  | 2019-01-01 | 31 | 15.5 | 2336 | -118 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 3476.2572 | 780 | 200 | 4456.2572 | 111.4% | 95% | 100% | -135.0114 | 1588.484 | -3550 | -400 | -2361.516 | 59.04% | 110.2% | 95% | 100% | 2454 | -118
[5 empty] | 2019-01-01 | 32 | 16 | 2415 | -101 | 1 | 0 | 2516 | 1820.6101 | 1820.6101 | 1820.6101 | 3471.5581 | 780 | 200 | 4451.5581 | 111.3% | 95% | 100% | -115.5606 | 1705.0494 | -3550 | -400 | -2244.9506 | 56.12% | 110.1% | 95% | 100% | 2516 | -101
Import Curtailment Limit | 543 |  | Hours |  | 2019-01-01 | 33 | 16.5 | 2554 | -96 | 1 | 0 | 2650 | 2030.5029 | 2030.5029 | 2030.5029 | 3463.7263 | 780 | 200 | 4443.7263 | 111.1% | 95% | 100% | -109.8398 | 1920.6631 | -3550 | -400 | -2029.3369 | 50.73% | 110.1% | 95% | 100% | 2650 | -96
Partial Profile |  |  |  |  | 2019-01-01 | 34 | 17 | 2716 | -94 | 0 | 0 | 2810 | 2281.1212 | 2281.1212 | 2281.1212 | 3462.1599 | 780 | 200 | 4442.1599 | 111.1% | 95% | 100% | -107.5515 | 2173.5697 | -2750 | -200 | -776.4303 | 19.41% | 110.1% | 95% | 100% | 2810 | -94
Hours in Profile | 8760 | Hours |  |  | 2019-01-01 | 35 | 17.5 | 2760 | -94 | 0 | 0 | 2854 | 2350.0412 | 2350.0412 | 2350.0412 | 3457.4608 | 780 | 200 | 4437.4608 | 110.9% | 95% | 100% | -107.5515 | 2242.4897 | -2750 | -200 | -707.5103 | 17.69% | 110% | 95% | 100% | 2854 | -94
Percentage Curtailed | 6.199% | Hours |  |  | 2019-01-01 | 36 | 18 | 2752 | -94 | 0 | 0 | 2846 | 2337.5103 | 2337.5103 | 2337.5103 | 3451.1954 | 780 | 200 | 4431.1954 | 110.8% | 95% | 100% | -107.5515 | 2229.9588 | -2750 | -200 | -720.0412 | 18% | 109.9% | 95% | 100% | 2846 | -94
Import Curtailment Limit (for partial profile) | 543 | Hours |  |  | 2019-01-01 | 37 | 18.5 | 2721 | -93 | 0 | 0 | 2814 | 2287.3866 | 2287.3866 | 2287.3866 | 3448.0627 | 780 | 200 | 4428.0627 | 110.7% | 95% | 100% | -106.4073 | 2180.9793 | -2750 | -200 | -769.0207 | 19.23% | 109.8% | 95% | 100% | 2814 | -93
[5 empty] | 2019-01-01 | 38 | 19 | 2667 | -93 | 0 | 0 | 2760 | 2202.803 | 2202.803 | 2202.803 | 3444.9299 | 780 | 200 | 4424.9299 | 110.6% | 95% | 100% | -106.4073 | 2096.3956 | -2750 | -200 | -853.6044 | 21.34% | 109.6% | 95% | 100% | 2760 | -93
GENERATION DATA |  |  |  |  | 2019-01-01 | 39 | 19.5 | 2623 | -92 | 0 | 0 | 2715 | 2132.3166 | 2132.3166 | 2132.3166 | 3443.3636 | 780 | 200 | 4423.3636 | 110.6% | 95% | 100% | -105.2632 | 2027.0534 | -2750 | -200 | -922.9466 | 23.07% | 109.5% | 95% | 100% | 2715 | -92
Network Asset Generation Capacity | -4000 |  | kVA |  | 2019-01-01 | 40 | 20 | 2552 | -91 | 0 | 0 | 2643 | 2019.5383 | 2019.5383 | 2019.5383 | 3440.2308 | 780 | 200 | 4420.2308 | 110.5% | 95% | 100% | -104.119 | 1915.4193 | -2750 | -200 | -1034.5807 | 25.86% | 109.4% | 95% | 100% | 2643 | -91
| Non-PV | PV |  | Usage Factor | 2019-01-01 | 41 | 20.5 | 2488 | -90 | 0 | 0 | 2578 | 1917.7246 | 1917.7246 | 1917.7246 | 3429.2663 | 780 | 200 | 4409.2663 | 110.2% | 95% | 100% | -102.9748 | 1814.7498 | -2750 | -200 | -1135.2502 | 28.38% | 109.2% | 95% | 100% | 2578 | -90
Inflight Generation Acceptances | -2000 | -500 | kVA | 100% | 2019-01-01 | 42 | 21 | 2402 | -89 | 0 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 3427.6999 | 780 | 200 | 4407.6999 | 110.2% | 95% | 100% | -101.8307 | 1679.6203 | -2750 | -200 | -1270.3797 | 31.76% | 109.1% | 95% | 100% | 2491 | -89
Largest Inflight Generation Offers | -500 | -200 | kVA | 100% | 2019-01-01 | 43 | 21.5 | 2328 | -86 | 0 | 0 | 2414 | 1660.8409 | 1660.8409 | 1660.8409 | 3427.6999 | 780 | 200 | 4407.6999 | 110.2% | 95% | 100% | -98.3982 | 1562.4427 | -2750 | -200 | -1387.5573 | 34.69% | 109.1% | 95% | 100% | 2414 | -86
Other Inflight Generation Offers | -500 | -200 | kVA | 100% | 2019-01-01 | 44 | 22 | 2222 | -84 | 0 | 0 | 2306 | 1491.6735 | 1491.6735 | 1491.6735 | 3426.1336 | 780 | 200 | 4406.1336 | 110.2% | 95% | 100% | -96.1098 | 1395.5637 | -2750 | -200 | -1554.4363 | 38.86% | 108.9% | 95% | 100% | 2306 | -84
Generation Confidence Factor | 50% |  |  |  | 2019-01-01 | 45 | 22.5 | 2120 | -81 | 0 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 3421.4345 | 780 | 200 | 4401.4345 | 110% | 95% | 100% | -92.6773 | 1234.5279 | -2750 | -200 | -1715.4721 | 42.89% | 108.9% | 95% | 100% | 2201 | -81
Inflight Generation Connection Capacity | -2750 | -800 | kVA |  | 2019-01-01 | 46 | 23 | 2027 | -78 | 0 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 3418.3017 | 780 | 200 | 4398.3017 | 110% | 95% | 100% | -89.2449 | 1087.5894 | -2750 | -200 | -1862.4106 | 46.56% | 108.9% | 95% | 100% | 2105 | -78
[5 empty] | 2019-01-01 | 47 | 23.5 | 1920 | -75 | 0 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 3418.3017 | 780 | 200 | 4398.3017 | 110% | 95% | 100% | -85.8124 | 918.7219 | -2750 | -200 | -2031.2781 | 50.78% | 108.9% | 95% | 100% | 1995 | -75
New Generation Connection Capacity | -200 | -200 | kVA | 100% | 2019-01-01 | 48 | 24 | 1846 | -71 | 0 | 0 | 1917 | 882.3578 | 882.3578 | 882.3578 | 3413.6026 | 780 | 200 | 4393.6026 | 109.8% | 95% | 100% | -81.2357 | 801.1221 | -2750 | -200 | -2148.8779 | 53.72% | 108.8% | 95% | 100% | 1917 | -71
[5 empty] | 2019-01-02 | 1 | 24.5 | 1846 | -69 | 0 | 0 | 1915 | 879.2251 | 879.2251 | 879.2251 | 3412.0363 | 780 | 200 | 4392.0363 | 109.8% | 95% | 100% | -78.9474 | 800.2777 | -2750 | -200 | -2149.7223 | 53.74% | 108.6% | 95% | 100% | 1915 | -69
Curtailment Threshold | 95% |  |  |  | 2019-01-02 | 2 | 25 | 1888 | -67 | 0 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 3410.4699 | 780 | 200 | 4390.4699 | 109.8% | 95% | 100% | -76.659 | 865.2206 | -2750 | -200 | -2084.7794 | 52.12% | 108.4% | 95% | 100% | 1955 | -67
[5 empty] | 2019-01-02 | 3 | 25.5 | 1877 | -65 | 0 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 3410.4699 | 780 | 200 | 4390.4699 | 109.8% | 95% | 100% | -74.3707 | 847.1462 | -2750 | -200 | -2102.8538 | 52.57% | 108.2% | 95% | 100% | 1942 | -65
Generation Curtailment Threshold | 384.5 |  | Hours |  | 2019-01-02 | 4 | 26 | 1837 | -62 | 0 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 3407.3372 | 780 | 200 | 4387.3372 | 109.7% | 95% | 100% | -70.9382 | 783.225 | -2750 | -200 | -2166.775 | 54.17% | 108.2% | 95% | 100% | 1899 | -62
Partial Profile |  |  |  |  | 2019-01-02 | 5 | 26.5 | 1808 | -61 | 0 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 3407.3372 | 780 | 200 | 4387.3372 | 109.7% | 95% | 100% | -69.7941 | 737.3782 | -2750 | -200 | -2212.6218 | 55.32% | 108.1% | 95% | 100% | 1869 | -61
Hours in Profile | 8760 | Hours |  |  | 2019-01-02 | 6 | 27 | 1800 | -59 | 0 | 0 | 1859 | 791.5087 | 791.5087 | 791.5087 | 3405.7708 | 780 | 200 | 4385.7708 | 109.6% | 95% | 100% | -67.5057 | 724.0029 | -2750 | -200 | -2225.9971 | 55.65% | 108% | 95% | 100% | 1859 | -59
Percentage Curtailed | 4.389% | Hours |  |  | 2019-01-02 | 7 | 27.5 | 1772 | -58 | 0 | 0 | 1830 | 746.0841 | 746.0841 | 746.0841 | 3404.2045 | 780 | 200 | 4384.2045 | 109.6% | 95% | 100% | -66.3616 | 679.7225 | -2750 | -200 | -2270.2775 | 56.76% | 107.9% | 95% | 100% | 1830 | -58
Import Curtailment Limit (for partial profile) | 384.5 | Hours |  |  | 2019-01-02 | 8 | 28 | 1748 | -58 | 0 | 0 | 1806 | 708.4913 | 708.4913 | 708.4913 | 3404.2045 | 780 | 200 | 4384.2045 | 109.6% | 95% | 100% | -66.3616 | 642.1298 | -2750 | -200 | -2307.8702 | 57.7% | 107.8% | 95% | 100% | 1806 | -58
[5 empty] | 2019-01-02 | 9 | 28.5 | 1730 | -57 | 0 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 3391.6735 | 780 | 200 | 4371.6735 | 109.3% | 95% | 100% | -65.2174 | 613.513 | -2750 | -200 | -2336.487 | 58.41% | 107.6% | 95% | 100% | 1787 | -57
[5 empty] | 2019-01-02 | 10 | 29 | 1742 | -56 | 0 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 3390.1072 | 780 | 200 | 4370.1072 | 109.3% | 95% | 100% | -64.0732 | 631.8872 | -2750 | -200 | -2318.1128 | 57.95% | 107.6% | 95% | 100% | 1798 | -56
[5 empty] | 2019-01-02 | 11 | 29.5 | 1788 | -55 | 0 | 0 | 1843 | 766.4468 | 766.4468 | 766.4468 | 3385.4081 | 780 | 200 | 4365.4081 | 109.1% | 95% | 100% | -62.9291 | 703.5178 | -2750 | -200 | -2246.4822 | 56.16% | 107.4% | 95% | 100% | 1843 | -55
[5 empty] | 2019-01-02 | 12 | 30 | 1884 | -55 | 0 | 0 | 1939 | 916.8178 | 916.8178 | 916.8178 | 3383.8417 | 780 | 200 | 4363.8417 | 109.1% | 95% | 100% | -62.9291 | 853.8887 | -2750 | -200 | -2096.1113 | 52.4% | 107.3% | 95% | 100% | 1939 | -55
[5 empty] | 2019-01-02 | 13 | 30.5 | 2095 | -53 | 0 | 0 | 2148 | 1244.188 | 1244.188 | 1244.188 | 3383.8417 | 780 | 200 | 4363.8417 | 109.1% | 95% | 100% | -60.6407 | 1183.5472 | -2750 | -200 | -1766.4528 | 44.16% | 107.3% | 95% | 100% | 2148 | -53
[5 empty] | 2019-01-02 | 14 | 31 | 2274 | -51 | 0 | 0 | 2325 | 1521.4345 | 1521.4345 | 1521.4345 | 3379.1426 | 780 | 200 | 4359.1426 | 109% | 95% | 100% | -58.3524 | 1463.0821 | -2750 | -200 | -1486.9179 | 37.17% | 107.1% | 95% | 100% | 2325 | -51
[5 empty] | 2019-01-02 | 15 | 31.5 | 2468 | -51 | 0 | 0 | 2519 | 1825.3092 | 1825.3092 | 1825.3092 | 3374.4435 | 780 | 200 | 4354.4435 | 108.9% | 95% | 100% | -58.3524 | 1766.9567 | -2750 | -200 | -1183.0433 | 29.58% | 107.1% | 95% | 100% | 2519 | -51
[5 empty] | 2019-01-02 | 16 | 32 | 2598 | -51 | 0 | 0 | 2649 | 2028.9365 | 2028.9365 | 2028.9365 | 3372.8772 | 780 | 200 | 4352.8772 | 108.8% | 95% | 100% | -58.3524 | 1970.5841 | -2750 | -200 | -979.4159 | 24.49% | 107% | 95% | 100% | 2649 | -51
[5 empty] | 2019-01-02 | 17 | 32.5 | 2743 | -50 | 0 | 0 | 2793 | 2254.493 | 2254.493 | 2254.493 | 3371.3108 | 780 | 200 | 4351.3108 | 108.8% | 95% | 100% | -57.2082 | 2197.2848 | -2750 | -200 | -752.7152 | 18.82% | 106.9% | 95% | 100% | 2793 | -50
[5 empty] | 2019-01-02 | 18 | 33 | 2844 | -60 | 0 | 0 | 2904 | 2428.3594 | 2428.3594 | 2428.3594 | 3371.3108 | 780 | 200 | 4351.3108 | 108.8% | 95% | 100% | -68.6499 | 2359.7096 | -2750 | -200 | -590.2904 | 14.76% | 106.9% | 95% | 100% | 2904 | -60
[5 empty] | 2019-01-02 | 19 | 33.5 | 2920 | -74 | 0 | 0 | 2994 | 2569.3322 | 2569.3322 | 2569.3322 | 3366.6117 | 780 | 200 | 4346.6117 | 108.7% | 95% | 100% | -84.6682 | 2484.664 | -2750 | -200 | -465.336 | 11.63% | 106.9% | 95% | 100% | 2994 | -74
[5 empty] | 2019-01-02 | 20 | 34 | 2913 | -112 | 1 | 0 | 3025 | 2617.8895 | 2617.8895 | 2617.8895 | 3363.479 | 780 | 200 | 4343.479 | 108.6% | 95% | 100% | -128.1465 | 2489.7431 | -3550 | -400 | -1460.2569 | 36.51% | 106.9% | 95% | 100% | 3025 | -112
[5 empty] | 2019-01-02 | 21 | 34.5 | 2883 | -154 | 1 | 0 | 3037 | 2636.6859 | 2636.6859 | 2636.6859 | 3363.479 | 780 | 200 | 4343.479 | 108.6% | 95% | 100% | -176.2014 | 2460.4845 | -3550 | -400 | -1489.5155 | 37.24% | 106.9% | 95% | 100% | 3037 | -154
[5 empty] | 2019-01-02 | 22 | 35 | 2858 | -179 | 1 | 0 | 3037 | 2636.6859 | 2636.6859 | 2636.6859 | 3361.9126 | 780 | 200 | 4341.9126 | 108.5% | 95% | 100% | -204.8055 | 2431.8804 | -3550 | -400 | -1518.1196 | 37.95% | 106.9% | 95% | 100% | 3037 | -179
[5 empty] | 2019-01-02 | 23 | 35.5 | 2852 | -188 | 1 | 0 | 3040 | 2641.385 | 2641.385 | 2641.385 | 3360.3462 | 780 | 200 | 4340.3462 | 108.5% | 95% | 100% | -215.103 | 2426.282 | -3550 | -400 | -1523.718 | 38.09% | 106.9% | 95% | 100% | 3040 | -188
[5 empty] | 2019-01-02 | 24 | 36 | 2843 | -186 | 1 | 0 | 3029 | 2624.155 | 2624.155 | 2624.155 | 3360.3462 | 780 | 200 | 4340.3462 | 108.5% | 95% | 100% | -212.8146 | 2411.3403 | -3550 | -400 | -1538.6597 | 38.47% | 106.8% | 95% | 100% | 3029 | -186
[5 empty] | 2019-01-02 | 25 | 36.5 | 2887 | -172 | 1 | 0 | 3059 | 2671.1459 | 2671.1459 | 2671.1459 | 3358.7799 | 780 | 200 | 4338.7799 | 108.5% | 95% | 100% | -196.7963 | 2474.3496 | -3550 | -400 | -1475.6504 | 36.89% | 106.8% | 95% | 100% | 3059 | -172
[5 empty] | 2019-01-02 | 26 | 37 | 2919 | -157 | 1 | 0 | 3076 | 2697.7741 | 2697.7741 | 2697.7741 | 3357.2135 | 780 | 200 | 4337.2135 | 108.4% | 95% | 100% | -179.6339 | 2518.1402 | -3550 | -400 | -1431.8598 | 35.8% | 106.8% | 95% | 100% | 3076 | -157
[5 empty] | 2019-01-02 | 27 | 37.5 | 2958 | -137 | 1 | 0 | 3095 | 2727.535 | 2727.535 | 2727.535 | 3357.2135 | 780 | 200 | 4337.2135 | 108.4% | 95% | 100% | -156.7506 | 2570.7845 | -3550 | -400 | -1379.2155 | 34.48% | 106.8% | 95% | 100% | 3095 | -137
[5 empty] | 2019-01-02 | 28 | 38 | 2995 | -117 | 1 | 0 | 3112 | 2754.1632 | 2754.1632 | 2754.1632 | 3355.6472 | 780 | 200 | 4335.6472 | 108.4% | 95% | 100% | -133.8673 | 2620.296 | -3550 | -400 | -1329.704 | 33.24% | 106.8% | 95% | 100% | 3112 | -117
[5 empty] | 2019-01-02 | 29 | 38.5 | 3047 | -95 | 1 | 0 | 3142 | 2801.1542 | 2801.1542 | 2801.1542 | 3355.6472 | 780 | 200 | 4335.6472 | 108.4% | 95% | 100% | -108.6957 | 2692.4585 | -3550 | -400 | -1257.5415 | 31.44% | 106.7% | 95% | 100% | 3142 | -95
[5 empty] | 2019-01-02 | 30 | 39 | 3107 | -71 | 1 | 0 | 3178 | 2857.5433 | 2857.5433 | 2857.5433 | 3355.6472 | 780 | 200 | 4335.6472 | 108.4% | 95% | 100% | -81.2357 | 2776.3076 | -3550 | -400 | -1173.6924 | 29.34% | 106.7% | 95% | 100% | 3178 | -71
[5 empty] | 2019-01-02 | 31 | 39.5 | 3144 | -52 | 1 | 0 | 3196 | 2885.7378 | 2885.7378 | 2885.7378 | 3354.0808 | 780 | 200 | 4334.0808 | 108.4% | 95% | 100% | -59.4966 | 2826.2413 | -3550 | -400 | -1123.7587 | 28.09% | 106.7% | 95% | 100% | 3196 | -52
[5 empty] | 2019-01-02 | 32 | 40 | 3229 | -41 | 1 | 0 | 3270 | 3001.6488 | 3001.6488 | 3001.6488 | 3354.0808 | 780 | 200 | 4334.0808 | 108.4% | 95% | 100% | -46.9108 | 2954.738 | -3550 | -400 | -995.262 | 24.88% | 106.6% | 95% | 100% | 3270 | -41
[5 empty] | 2019-01-02 | 33 | 40.5 | 3323 | -39 | 1 | 0 | 3362 | 3145.7543 | 3145.7543 | 3145.7543 | 3350.9481 | 780 | 200 | 4330.9481 | 108.3% | 95% | 100% | -44.6224 | 3101.1319 | -3550 | -400 | -848.8681 | 21.22% | 106.6% | 95% | 100% | 3362 | -39
[5 empty] | 2019-01-02 | 34 | 41 | 3401 | -39 | 1 | 0 | 3440 | 3267.9308 | 3267.9308 | 3267.9308 | 3350.9481 | 780 | 200 | 4330.9481 | 108.3% | 95% | 100% | -44.6224 | 3223.3083 | -3550 | -400 | -726.6917 | 18.17% | 106.6% | 95% | 100% | 3440 | -39
[5 empty] | 2019-01-02 | 35 | 41.5 | 3443 | -40 | 1 | 0 | 3483 | 3335.2844 | 3335.2844 | 3335.2844 | 3349.3817 | 780 | 200 | 4329.3817 | 108.2% | 95% | 100% | -45.7666 | 3289.5178 | -3550 | -400 | -660.4822 | 16.51% | 106.6% | 95% | 100% | 3483 | -40
[5 empty] | 2019-01-02 | 36 | 42 | 3434 | -41 | 0 | 0 | 3475 | 3322.7535 | 3322.7535 | 3322.7535 | 3346.249 | 780 | 200 | 4326.249 | 108.2% | 95% | 100% | -46.9108 | 3275.8427 | -2750 | -200 | 325.8427 | -8.146% | 106.4% | 95% | 100% | 3475 | -41
[5 empty] | 2019-01-02 | 37 | 42.5 | 3420 | -40 | 0 | 0 | 3460 | 3299.258 | 3299.258 | 3299.258 | 3343.1162 | 780 | 200 | 4323.1162 | 108.1% | 95% | 100% | -45.7666 | 3253.4914 | -2750 | -200 | 303.4914 | -7.587% | 106.3% | 95% | 100% | 3460 | -40
[5 empty] | 2019-01-02 | 38 | 43 | 3392 | -40 | 0 | 0 | 3432 | 3255.3998 | 3255.3998 | 3255.3998 | 3343.1162 | 780 | 200 | 4323.1162 | 108.1% | 95% | 100% | -45.7666 | 3209.6332 | -2750 | -200 | 259.6332 | -6.491% | 106.3% | 95% | 100% | 3432 | -40
[5 empty] | 2019-01-02 | 39 | 43.5 | 3343 | -40 | 0 | 0 | 3383 | 3178.648 | 3178.648 | 3178.648 | 3341.5499 | 780 | 200 | 4321.5499 | 108% | 95% | 100% | -45.7666 | 3132.8814 | -2750 | -200 | 182.8814 | -4.572% | 106.2% | 95% | 100% | 3383 | -40
[5 empty] | 2019-01-02 | 40 | 44 | 3247 | -41 | 0 | 0 | 3288 | 3029.8434 | 3029.8434 | 3029.8434 | 3341.5499 | 780 | 200 | 4321.5499 | 108% | 95% | 100% | -46.9108 | 2982.9326 | -2750 | -200 | 32.9326 | -0.8233% | 106.2% | 95% | 100% | 3288 | -41
[5 empty] | 2019-01-02 | 41 | 44.5 | 3153 | -41 | 0 | 0 | 3194 | 2882.6051 | 2882.6051 | 2882.6051 | 3339.9835 | 780 | 200 | 4319.9835 | 108% | 95% | 100% | -46.9108 | 2835.6944 | -2750 | -200 | -114.3056 | 2.858% | 106.1% | 95% | 100% | 3194 | -41
[5 empty] | 2019-01-02 | 42 | 45 | 3026 | -41 | 0 | 0 | 3067 | 2683.6768 | 2683.6768 | 2683.6768 | 3339.9835 | 780 | 200 | 4319.9835 | 108% | 95% | 100% | -46.9108 | 2636.7661 | -2750 | -200 | -313.2339 | 7.831% | 106.1% | 95% | 100% | 3067 | -41
[5 empty] | 2019-01-02 | 43 | 45.5 | 2903 | -42 | 0 | 0 | 2945 | 2492.5804 | 2492.5804 | 2492.5804 | 3338.4171 | 780 | 200 | 4318.4171 | 108% | 95% | 100% | -48.0549 | 2444.5255 | -2750 | -200 | -505.4745 | 12.64% | 106% | 95% | 100% | 2945 | -42
[5 empty] | 2019-01-02 | 44 | 46 | 2754 | -42 | 0 | 0 | 2796 | 2259.1921 | 2259.1921 | 2259.1921 | 3336.8508 | 780 | 200 | 4316.8508 | 107.9% | 95% | 100% | -48.0549 | 2211.1372 | -2750 | -200 | -738.8628 | 18.47% | 105.9% | 95% | 100% | 2796 | -42
[5 empty] | 2019-01-02 | 45 | 46.5 | 2608 | -42 | 0 | 0 | 2650 | 2030.5029 | 2030.5029 | 2030.5029 | 3336.8508 | 780 | 200 | 4316.8508 | 107.9% | 95% | 100% | -48.0549 | 1982.448 | -2750 | -200 | -967.552 | 24.19% | 105.9% | 95% | 100% | 2650 | -42
[5 empty] | 2019-01-02 | 46 | 47 | 2463 | -42 | 0 | 0 | 2505 | 1803.38 | 1803.38 | 1803.38 | 3336.8508 | 780 | 200 | 4316.8508 | 107.9% | 95% | 100% | -48.0549 | 1755.3251 | -2750 | -200 | -1194.6749 | 29.87% | 105.9% | 95% | 100% | 2505 | -42
[5 empty] | 2019-01-02 | 47 | 47.5 | 2301 | -41 | 0 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 3336.8508 | 780 | 200 | 4316.8508 | 107.9% | 95% | 100% | -46.9108 | 1501.1519 | -2750 | -200 | -1448.8481 | 36.22% | 105.8% | 95% | 100% | 2342 | -41
[5 empty] | 2019-01-02 | 48 | 48 | 2209 | -41 | 0 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 3336.8508 | 780 | 200 | 4316.8508 | 107.9% | 95% | 100% | -46.9108 | 1357.0464 | -2750 | -200 | -1592.9536 | 39.82% | 105.8% | 95% | 100% | 2250 | -41
[5 empty] | 2019-01-03 | 1 | 48.5 | 2182 | -40 | 0 | 0 | 2222 | 1360.0989 | 1360.0989 | 1360.0989 | 3336.8508 | 780 | 200 | 4316.8508 | 107.9% | 95% | 100% | -45.7666 | 1314.3323 | -2750 | -200 | -1635.6677 | 40.89% | 105.7% | 95% | 100% | 2222 | -40
[5 empty] | 2019-01-03 | 2 | 49 | 2201 | -39 | 0 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 3335.2844 | 780 | 200 | 4315.2844 | 107.9% | 95% | 100% | -44.6224 | 1343.6711 | -2750 | -200 | -1606.3289 | 40.16% | 105.6% | 95% | 100% | 2240 | -39
[5 empty] | 2019-01-03 | 3 | 49.5 | 2175 | -39 | 0 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 3333.7181 | 780 | 200 | 4313.7181 | 107.8% | 95% | 100% | -44.6224 | 1302.9456 | -2750 | -200 | -1647.0544 | 41.18% | 105.6% | 95% | 100% | 2214 | -39
[5 empty] | 2019-01-03 | 4 | 50 | 2128 | -39 | 0 | 0 | 2167 | 1273.9489 | 1273.9489 | 1273.9489 | 3332.1517 | 780 | 200 | 4312.1517 | 107.8% | 95% | 100% | -44.6224 | 1229.3265 | -2750 | -200 | -1720.6735 | 43.02% | 105.6% | 95% | 100% | 2167 | -39
[5 empty] | 2019-01-03 | 5 | 50.5 | 2092 | -38 | 0 | 0 | 2130 | 1215.9934 | 1215.9934 | 1215.9934 | 3332.1517 | 780 | 200 | 4312.1517 | 107.8% | 95% | 100% | -43.4783 | 1172.5151 | -2750 | -200 | -1777.4849 | 44.44% | 105.6% | 95% | 100% | 2130 | -38
[5 empty] | 2019-01-03 | 6 | 51 | 2077 | -37 | 0 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 3332.1517 | 780 | 200 | 4312.1517 | 107.8% | 95% | 100% | -42.3341 | 1148.5975 | -2750 | -200 | -1801.4025 | 45.04% | 105.5% | 95% | 100% | 2114 | -37
[5 empty] | 2019-01-03 | 7 | 51.5 | 2048 | -38 | 0 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 3330.5853 | 780 | 200 | 4310.5853 | 107.8% | 95% | 100% | -43.4783 | 1103.5951 | -2750 | -200 | -1846.4049 | 46.16% | 105.5% | 95% | 100% | 2086 | -38
[5 empty] | 2019-01-03 | 8 | 52 | 2011 | -38 | 0 | 0 | 2049 | 1089.1179 | 1089.1179 | 1089.1179 | 3330.5853 | 780 | 200 | 4310.5853 | 107.8% | 95% | 100% | -43.4783 | 1045.6396 | -2750 | -200 | -1904.3604 | 47.61% | 105.5% | 95% | 100% | 2049 | -38
[5 empty] | 2019-01-03 | 9 | 52.5 | 1997 | -37 | 0 | 0 | 2034 | 1065.6224 | 1065.6224 | 1065.6224 | 3330.5853 | 780 | 200 | 4310.5853 | 107.8% | 95% | 100% | -42.3341 | 1023.2883 | -2750 | -200 | -1926.7117 | 48.17% | 105.4% | 95% | 100% | 2034 | -37
[5 empty] | 2019-01-03 | 10 | 53 | 2003 | -37 | 0 | 0 | 2040 | 1075.0206 | 1075.0206 | 1075.0206 | 3329.019 | 780 | 200 | 4309.019 | 107.7% | 95% | 100% | -42.3341 | 1032.6865 | -2750 | -200 | -1917.3135 | 47.93% | 105.4% | 95% | 100% | 2040 | -37
[5 empty] | 2019-01-03 | 11 | 53.5 | 2053 | -38 | 0 | 0 | 2091 | 1154.9052 | 1154.9052 | 1154.9052 | 3329.019 | 780 | 200 | 4309.019 | 107.7% | 95% | 100% | -43.4783 | 1111.4269 | -2750 | -200 | -1838.5731 | 45.96% | 105.3% | 95% | 100% | 2091 | -38
[5 empty] | 2019-01-03 | 12 | 54 | 2139 | -39 | 0 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 3329.019 | 780 | 200 | 4309.019 | 107.7% | 95% | 100% | -44.6224 | 1246.5565 | -2750 | -200 | -1703.4435 | 42.59% | 105.3% | 95% | 100% | 2178 | -39
[5 empty] | 2019-01-03 | 13 | 54.5 | 2343 | -37 | 0 | 0 | 2380 | 1607.5845 | 1607.5845 | 1607.5845 | 3327.4526 | 780 | 200 | 4307.4526 | 107.7% | 95% | 100% | -42.3341 | 1565.2504 | -2750 | -200 | -1384.7496 | 34.62% | 105.3% | 95% | 100% | 2380 | -37
[5 empty] | 2019-01-03 | 14 | 55 | 2531 | -36 | 0 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 3325.8862 | 780 | 200 | 4305.8862 | 107.6% | 95% | 100% | -41.1899 | 1859.3047 | -2750 | -200 | -1090.6953 | 27.27% | 105.3% | 95% | 100% | 2567 | -36
[5 empty] | 2019-01-03 | 15 | 55.5 | 2739 | -37 | 0 | 0 | 2776 | 2227.8648 | 2227.8648 | 2227.8648 | 3325.8862 | 780 | 200 | 4305.8862 | 107.6% | 95% | 100% | -42.3341 | 2185.5307 | -2750 | -200 | -764.4693 | 19.11% | 105.3% | 95% | 100% | 2776 | -37
[5 empty] | 2019-01-03 | 16 | 56 | 2879 | -38 | 0 | 0 | 2917 | 2448.7222 | 2448.7222 | 2448.7222 | 3325.8862 | 780 | 200 | 4305.8862 | 107.6% | 95% | 100% | -43.4783 | 2405.2439 | -2750 | -200 | -544.7561 | 13.62% | 105.2% | 95% | 100% | 2917 | -38
[5 empty] | 2019-01-03 | 17 | 56.5 | 3008 | -38 | 0 | 0 | 3046 | 2650.7832 | 2650.7832 | 2650.7832 | 3324.3199 | 780 | 200 | 4304.3199 | 107.6% | 95% | 100% | -43.4783 | 2607.3049 | -2750 | -200 | -342.6951 | 8.567% | 105.2% | 95% | 100% | 3046 | -38
[5 empty] | 2019-01-03 | 18 | 57 | 3105 | -42 | 0 | 0 | 3147 | 2808.986 | 2808.986 | 2808.986 | 3324.3199 | 780 | 200 | 4304.3199 | 107.6% | 95% | 100% | -48.0549 | 2760.9311 | -2750 | -200 | -189.0689 | 4.727% | 105.2% | 95% | 100% | 3147 | -42
[5 empty] | 2019-01-03 | 19 | 57.5 | 3177 | -49 | 0 | 0 | 3226 | 2932.7288 | 2932.7288 | 2932.7288 | 3322.7535 | 780 | 200 | 4302.7535 | 107.6% | 95% | 100% | -56.0641 | 2876.6647 | -2750 | -200 | -73.3353 | 1.833% | 105.2% | 95% | 100% | 3226 | -49
[5 empty] | 2019-01-03 | 20 | 58 | 3176 | -69 | 1 | 0 | 3245 | 2962.4897 | 2962.4897 | 2962.4897 | 3322.7535 | 780 | 200 | 4302.7535 | 107.6% | 95% | 100% | -78.9474 | 2883.5423 | -3550 | -400 | -1066.4577 | 26.66% | 105.1% | 95% | 100% | 3245 | -69
[5 empty] | 2019-01-03 | 21 | 58.5 | 3169 | -86 | 1 | 0 | 3255 | 2978.1533 | 2978.1533 | 2978.1533 | 3321.1871 | 780 | 200 | 4301.1871 | 107.5% | 95% | 100% | -98.3982 | 2879.7552 | -3550 | -400 | -1070.2448 | 26.76% | 105.1% | 95% | 100% | 3255 | -86
[5 empty] | 2019-01-03 | 22 | 59 | 3163 | -103 | 1 | 0 | 3266 | 2995.3833 | 2995.3833 | 2995.3833 | 3319.6208 | 780 | 200 | 4299.6208 | 107.5% | 95% | 100% | -117.849 | 2877.5344 | -3550 | -400 | -1072.4656 | 26.81% | 105.1% | 95% | 100% | 3266 | -103
[5 empty] | 2019-01-03 | 23 | 59.5 | 3140 | -111 | 1 | 0 | 3251 | 2971.8879 | 2971.8879 | 2971.8879 | 3319.6208 | 780 | 200 | 4299.6208 | 107.5% | 95% | 100% | -127.0023 | 2844.8856 | -3550 | -400 | -1105.1144 | 27.63% | 105% | 95% | 100% | 3251 | -111
[5 empty] | 2019-01-03 | 24 | 60 | 3138 | -116 | 1 | 0 | 3254 | 2976.587 | 2976.587 | 2976.587 | 3319.6208 | 780 | 200 | 4299.6208 | 107.5% | 95% | 100% | -132.7231 | 2843.8639 | -3550 | -400 | -1106.1361 | 27.65% | 105% | 95% | 100% | 3254 | -116
[5 empty] | 2019-01-03 | 25 | 60.5 | 3159 | -116 | 1 | 0 | 3275 | 3009.4806 | 3009.4806 | 3009.4806 | 3314.9217 | 780 | 200 | 4294.9217 | 107.4% | 95% | 100% | -132.7231 | 2876.7575 | -3550 | -400 | -1073.2425 | 26.83% | 104.9% | 95% | 100% | 3275 | -116
[5 empty] | 2019-01-03 | 26 | 61 | 3148 | -110 | 1 | 0 | 3258 | 2982.8524 | 2982.8524 | 2982.8524 | 3313.3553 | 780 | 200 | 4293.3553 | 107.3% | 95% | 100% | -125.8581 | 2856.9943 | -3550 | -400 | -1093.0057 | 27.33% | 104.9% | 95% | 100% | 3258 | -110
[5 empty] | 2019-01-03 | 27 | 61.5 | 3167 | -104 | 1 | 0 | 3271 | 3003.2152 | 3003.2152 | 3003.2152 | 3313.3553 | 780 | 200 | 4293.3553 | 107.3% | 95% | 100% | -118.9931 | 2884.222 | -3550 | -400 | -1065.778 | 26.64% | 104.8% | 95% | 100% | 3271 | -104
[5 empty] | 2019-01-03 | 28 | 62 | 3228 | -92 | 1 | 0 | 3320 | 3079.967 | 3079.967 | 3079.967 | 3313.3553 | 780 | 200 | 4293.3553 | 107.3% | 95% | 100% | -105.2632 | 2974.7039 | -3550 | -400 | -975.2961 | 24.38% | 104.7% | 95% | 100% | 3320 | -92
[5 empty] | 2019-01-03 | 29 | 62.5 | 3272 | -77 | 1 | 0 | 3349 | 3125.3916 | 3125.3916 | 3125.3916 | 3311.789 | 780 | 200 | 4291.789 | 107.3% | 95% | 100% | -88.1007 | 3037.2909 | -3550 | -400 | -912.7091 | 22.82% | 104.6% | 95% | 100% | 3349 | -77
[5 empty] | 2019-01-03 | 30 | 63 | 3299 | -60 | 1 | 0 | 3359 | 3141.0552 | 3141.0552 | 3141.0552 | 3311.789 | 780 | 200 | 4291.789 | 107.3% | 95% | 100% | -68.6499 | 3072.4053 | -3550 | -400 | -877.5947 | 21.94% | 104.6% | 95% | 100% | 3359 | -60
[5 empty] | 2019-01-03 | 31 | 63.5 | 3327 | -49 | 1 | 0 | 3376 | 3167.6834 | 3167.6834 | 3167.6834 | 3311.789 | 780 | 200 | 4291.789 | 107.3% | 95% | 100% | -56.0641 | 3111.6194 | -3550 | -400 | -838.3806 | 20.96% | 104.5% | 95% | 100% | 3376 | -49
[5 empty] | 2019-01-03 | 32 | 64 | 3372 | -42 | 1 | 0 | 3414 | 3227.2053 | 3227.2053 | 3227.2053 | 3310.2226 | 780 | 200 | 4290.2226 | 107.3% | 95% | 100% | -48.0549 | 3179.1504 | -3550 | -400 | -770.8496 | 19.27% | 104.5% | 95% | 100% | 3414 | -42
[5 empty] | 2019-01-03 | 33 | 64.5 | 3425 | -40 | 1 | 0 | 3465 | 3307.0899 | 3307.0899 | 3307.0899 | 3310.2226 | 780 | 200 | 4290.2226 | 107.3% | 95% | 100% | -45.7666 | 3261.3233 | -3550 | -400 | -688.6767 | 17.22% | 104.5% | 95% | 100% | 3465 | -40
[5 empty] | 2019-01-03 | 34 | 65 | 3415 | -40 | 1 | 0 | 3455 | 3291.4262 | 3291.4262 | 3291.4262 | 3310.2226 | 780 | 200 | 4290.2226 | 107.3% | 95% | 100% | -45.7666 | 3245.6596 | -3550 | -400 | -704.3404 | 17.61% | 104.5% | 95% | 100% | 3455 | -40
[5 empty] | 2019-01-03 | 35 | 65.5 | 3422 | -41 | 0 | 0 | 3463 | 3303.9571 | 3303.9571 | 3303.9571 | 3308.6562 | 780 | 200 | 4288.6562 | 107.2% | 95% | 100% | -46.9108 | 3257.0464 | -2750 | -200 | 307.0464 | -7.676% | 104.5% | 95% | 100% | 3463 | -41
[5 empty] | 2019-01-03 | 36 | 66 | 3413 | -42 | 0 | 0 | 3455 | 3291.4262 | 3291.4262 | 3291.4262 | 3307.0899 | 780 | 200 | 4287.0899 | 107.2% | 95% | 100% | -48.0549 | 3243.3713 | -2750 | -200 | 293.3713 | -7.334% | 104.5% | 95% | 100% | 3455 | -42
[5 empty] | 2019-01-03 | 37 | 66.5 | 3394 | -42 | 0 | 0 | 3436 | 3261.6653 | 3261.6653 | 3261.6653 | 3307.0899 | 780 | 200 | 4287.0899 | 107.2% | 95% | 100% | -48.0549 | 3213.6104 | -2750 | -200 | 263.6104 | -6.59% | 104.4% | 95% | 100% | 3436 | -42
[5 empty] | 2019-01-03 | 38 | 67 | 3404 | -41 | 0 | 0 | 3445 | 3275.7626 | 3275.7626 | 3275.7626 | 3307.0899 | 780 | 200 | 4287.0899 | 107.2% | 95% | 100% | -46.9108 | 3228.8518 | -2750 | -200 | 278.8518 | -6.971% | 104.4% | 95% | 100% | 3445 | -41
[5 empty] | 2019-01-03 | 39 | 67.5 | 3412 | -41 | 0 | 0 | 3453 | 3288.2935 | 3288.2935 | 3288.2935 | 3307.0899 | 780 | 200 | 4287.0899 | 107.2% | 95% | 100% | -46.9108 | 3241.3827 | -2750 | -200 | 291.3827 | -7.285% | 104.4% | 95% | 100% | 3453 | -41
[5 empty] | 2019-01-03 | 40 | 68 | 3354 | -40 | 0 | 0 | 3394 | 3195.878 | 3195.878 | 3195.878 | 3305.5235 | 780 | 200 | 4285.5235 | 107.1% | 95% | 100% | -45.7666 | 3150.1114 | -2750 | -200 | 200.1114 | -5.003% | 104.4% | 95% | 100% | 3394 | -40
[5 empty] | 2019-01-03 | 41 | 68.5 | 3249 | -41 | 0 | 0 | 3290 | 3032.9761 | 3032.9761 | 3032.9761 | 3303.9571 | 780 | 200 | 4283.9571 | 107.1% | 95% | 100% | -46.9108 | 2986.0653 | -2750 | -200 | 36.0653 | -0.9016% | 104.4% | 95% | 100% | 3290 | -41
[5 empty] | 2019-01-03 | 42 | 69 | 3138 | -41 | 0 | 0 | 3179 | 2859.1096 | 2859.1096 | 2859.1096 | 3302.3908 | 780 | 200 | 4282.3908 | 107.1% | 95% | 100% | -46.9108 | 2812.1989 | -2750 | -200 | -137.8011 | 3.445% | 104.4% | 95% | 100% | 3179 | -41
[5 empty] | 2019-01-03 | 43 | 69.5 | 3000 | -42 | 0 | 0 | 3042 | 2644.5177 | 2644.5177 | 2644.5177 | 3300.8244 | 780 | 200 | 4280.8244 | 107% | 95% | 100% | -48.0549 | 2596.4628 | -2750 | -200 | -353.5372 | 8.838% | 104.3% | 95% | 100% | 3042 | -42
[5 empty] | 2019-01-03 | 44 | 70 | 2841 | -42 | 0 | 0 | 2883 | 2395.4658 | 2395.4658 | 2395.4658 | 3300.8244 | 780 | 200 | 4280.8244 | 107% | 95% | 100% | -48.0549 | 2347.4109 | -2750 | -200 | -602.5891 | 15.06% | 104.3% | 95% | 100% | 2883 | -42
[5 empty] | 2019-01-03 | 45 | 70.5 | 2685 | -44 | 0 | 0 | 2729 | 2154.2457 | 2154.2457 | 2154.2457 | 3300.8244 | 780 | 200 | 4280.8244 | 107% | 95% | 100% | -50.3432 | 2103.9024 | -2750 | -200 | -846.0976 | 21.15% | 104.2% | 95% | 100% | 2729 | -44
[5 empty] | 2019-01-03 | 46 | 71 | 2527 | -46 | 0 | 0 | 2573 | 1909.8928 | 1909.8928 | 1909.8928 | 3300.8244 | 780 | 200 | 4280.8244 | 107% | 95% | 100% | -52.6316 | 1857.2612 | -2750 | -200 | -1092.7388 | 27.32% | 104.2% | 95% | 100% | 2573 | -46
[5 empty] | 2019-01-03 | 47 | 71.5 | 2367 | -46 | 0 | 0 | 2413 | 1659.2745 | 1659.2745 | 1659.2745 | 3299.258 | 780 | 200 | 4279.258 | 107% | 95% | 100% | -52.6316 | 1606.6429 | -2750 | -200 | -1343.3571 | 33.58% | 104.2% | 95% | 100% | 2413 | -46
[5 empty] | 2019-01-03 | 48 | 72 | 2260 | -47 | 0 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 3299.258 | 780 | 200 | 4279.258 | 107% | 95% | 100% | -53.7757 | 1439.4642 | -2750 | -200 | -1510.5358 | 37.76% | 104.1% | 95% | 100% | 2307 | -47
[5 empty] | 2019-01-04 | 1 | 72.5 | 2231 | -47 | 0 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 3297.6917 | 780 | 200 | 4277.6917 | 106.9% | 95% | 100% | -53.7757 | 1394.0396 | -2750 | -200 | -1555.9604 | 38.9% | 104.1% | 95% | 100% | 2278 | -47
[5 empty] | 2019-01-04 | 2 | 73 | 2253 | -48 | 0 | 0 | 2301 | 1483.8417 | 1483.8417 | 1483.8417 | 3296.1253 | 780 | 200 | 4276.1253 | 106.9% | 95% | 100% | -54.9199 | 1428.9218 | -2750 | -200 | -1521.0782 | 38.03% | 104.1% | 95% | 100% | 2301 | -48
[5 empty] | 2019-01-04 | 3 | 73.5 | 2219 | -49 | 0 | 0 | 2268 | 1432.1517 | 1432.1517 | 1432.1517 | 3296.1253 | 780 | 200 | 4276.1253 | 106.9% | 95% | 100% | -56.0641 | 1376.0876 | -2750 | -200 | -1573.9124 | 39.35% | 104.1% | 95% | 100% | 2268 | -49
[5 empty] | 2019-01-04 | 4 | 74 | 2163 | -50 | 0 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 3294.5589 | 780 | 200 | 4274.5589 | 106.9% | 95% | 100% | -57.2082 | 1288.7934 | -2750 | -200 | -1661.2066 | 41.53% | 104% | 95% | 100% | 2213 | -50
[5 empty] | 2019-01-04 | 5 | 74.5 | 2122 | -50 | 0 | 0 | 2172 | 1281.7807 | 1281.7807 | 1281.7807 | 3294.5589 | 780 | 200 | 4274.5589 | 106.9% | 95% | 100% | -57.2082 | 1224.5725 | -2750 | -200 | -1725.4275 | 43.14% | 104% | 95% | 100% | 2172 | -50
[5 empty] | 2019-01-04 | 6 | 75 | 2112 | -49 | 0 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 3294.5589 | 780 | 200 | 4274.5589 | 106.9% | 95% | 100% | -56.0641 | 1208.4866 | -2750 | -200 | -1741.5134 | 43.54% | 104% | 95% | 100% | 2161 | -49
[5 empty] | 2019-01-04 | 7 | 75.5 | 2078 | -50 | 0 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 3294.5589 | 780 | 200 | 4274.5589 | 106.9% | 95% | 100% | -57.2082 | 1155.6524 | -2750 | -200 | -1794.3476 | 44.86% | 104% | 95% | 100% | 2128 | -50
[5 empty] | 2019-01-04 | 8 | 76 | 2047 | -50 | 0 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 3292.9926 | 780 | 200 | 4272.9926 | 106.8% | 95% | 100% | -57.2082 | 1107.0951 | -2750 | -200 | -1842.9049 | 46.07% | 104% | 95% | 100% | 2097 | -50
[5 empty] | 2019-01-04 | 9 | 76.5 | 2026 | -50 | 0 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 3292.9926 | 780 | 200 | 4272.9926 | 106.8% | 95% | 100% | -57.2082 | 1074.2015 | -2750 | -200 | -1875.7985 | 46.89% | 103.8% | 95% | 100% | 2076 | -50
[5 empty] | 2019-01-04 | 10 | 77 | 2036 | -51 | 0 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 3291.4262 | 780 | 200 | 4271.4262 | 106.8% | 95% | 100% | -58.3524 | 1090.2873 | -2750 | -200 | -1859.7127 | 46.49% | 103.8% | 95% | 100% | 2087 | -51
[5 empty] | 2019-01-04 | 11 | 77.5 | 2087 | -51 | 0 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 3291.4262 | 780 | 200 | 4271.4262 | 106.8% | 95% | 100% | -58.3524 | 1170.1719 | -2750 | -200 | -1779.8281 | 44.5% | 103.7% | 95% | 100% | 2138 | -51
[5 empty] | 2019-01-04 | 12 | 78 | 2169 | -52 | 0 | 0 | 2221 | 1358.5326 | 1358.5326 | 1358.5326 | 3291.4262 | 780 | 200 | 4271.4262 | 106.8% | 95% | 100% | -59.4966 | 1299.036 | -2750 | -200 | -1650.964 | 41.27% | 103.7% | 95% | 100% | 2221 | -52
[5 empty] | 2019-01-04 | 13 | 78.5 | 2364 | -50 | 0 | 0 | 2414 | 1660.8409 | 1660.8409 | 1660.8409 | 3291.4262 | 780 | 200 | 4271.4262 | 106.8% | 95% | 100% | -57.2082 | 1603.6327 | -2750 | -200 | -1346.3673 | 33.66% | 103.6% | 95% | 100% | 2414 | -50
[5 empty] | 2019-01-04 | 14 | 79 | 2567 | -48 | 0 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 3289.8599 | 780 | 200 | 4269.8599 | 106.7% | 95% | 100% | -54.9199 | 1920.7602 | -2750 | -200 | -1029.2398 | 25.73% | 103.6% | 95% | 100% | 2615 | -48
[5 empty] | 2019-01-04 | 15 | 79.5 | 2784 | -48 | 0 | 0 | 2832 | 2315.5812 | 2315.5812 | 2315.5812 | 3288.2935 | 780 | 200 | 4268.2935 | 106.7% | 95% | 100% | -54.9199 | 2260.6613 | -2750 | -200 | -689.3387 | 17.23% | 103.6% | 95% | 100% | 2832 | -48
[5 empty] | 2019-01-04 | 16 | 80 | 2939 | -49 | 0 | 0 | 2988 | 2559.934 | 2559.934 | 2559.934 | 3288.2935 | 780 | 200 | 4268.2935 | 106.7% | 95% | 100% | -56.0641 | 2503.87 | -2750 | -200 | -446.13 | 11.15% | 103.5% | 95% | 100% | 2988 | -49
[5 empty] | 2019-01-04 | 17 | 80.5 | 3064 | -50 | 0 | 0 | 3114 | 2757.296 | 2757.296 | 2757.296 | 3286.7271 | 780 | 200 | 4266.7271 | 106.7% | 95% | 100% | -57.2082 | 2700.0877 | -2750 | -200 | -249.9123 | 6.248% | 103.5% | 95% | 100% | 3114 | -50
[5 empty] | 2019-01-04 | 18 | 81 | 3146 | -63 | 0 | 0 | 3209 | 2906.1006 | 2906.1006 | 2906.1006 | 3286.7271 | 780 | 200 | 4266.7271 | 106.7% | 95% | 100% | -72.0824 | 2834.0182 | -2750 | -200 | -115.9818 | 2.9% | 103.5% | 95% | 100% | 3209 | -63
[5 empty] | 2019-01-04 | 19 | 81.5 | 3207 | -78 | 0 | 0 | 3285 | 3025.1443 | 3025.1443 | 3025.1443 | 3286.7271 | 780 | 200 | 4266.7271 | 106.7% | 95% | 100% | -89.2449 | 2935.8994 | -2750 | -200 | -14.1006 | 0.3525% | 103.5% | 95% | 100% | 3285 | -78
[5 empty] | 2019-01-04 | 20 | 82 | 3179 | -128 | 0 | 0 | 3307 | 3059.6043 | 3059.6043 | 3059.6043 | 3285.1608 | 780 | 200 | 4265.1608 | 106.6% | 95% | 100% | -146.4531 | 2913.1512 | -2750 | -200 | -36.8488 | 0.9212% | 103.5% | 95% | 100% | 3307 | -128
[5 empty] | 2019-01-04 | 21 | 82.5 | 3146 | -159 | 1 | 0 | 3305 | 3056.4716 | 3056.4716 | 3056.4716 | 3285.1608 | 780 | 200 | 4265.1608 | 106.6% | 95% | 100% | -181.9222 | 2874.5494 | -3550 | -400 | -1075.4506 | 26.89% | 103.4% | 95% | 100% | 3305 | -159
[5 empty] | 2019-01-04 | 22 | 83 | 3105 | -190 | 1 | 0 | 3295 | 3040.8079 | 3040.8079 | 3040.8079 | 3285.1608 | 780 | 200 | 4265.1608 | 106.6% | 95% | 100% | -217.3913 | 2823.4166 | -3550 | -400 | -1126.5834 | 28.16% | 103.4% | 95% | 100% | 3295 | -190
[5 empty] | 2019-01-04 | 23 | 83.5 | 3084 | -205 | 1 | 0 | 3289 | 3031.4097 | 3031.4097 | 3031.4097 | 3285.1608 | 780 | 200 | 4265.1608 | 106.6% | 95% | 100% | -234.5538 | 2796.856 | -3550 | -400 | -1153.144 | 28.83% | 103.4% | 95% | 100% | 3289 | -205
[5 empty] | 2019-01-04 | 24 | 84 | 3073 | -218 | 1 | 0 | 3291 | 3034.5425 | 3034.5425 | 3034.5425 | 3283.5944 | 780 | 200 | 4263.5944 | 106.6% | 95% | 100% | -249.4279 | 2785.1145 | -3550 | -400 | -1164.8855 | 29.12% | 103.4% | 95% | 100% | 3291 | -218
[5 empty] | 2019-01-04 | 25 | 84.5 | 3089 | -206 | 1 | 0 | 3295 | 3040.8079 | 3040.8079 | 3040.8079 | 3283.5944 | 780 | 200 | 4263.5944 | 106.6% | 95% | 100% | -235.6979 | 2805.11 | -3550 | -400 | -1144.89 | 28.62% | 103.3% | 95% | 100% | 3295 | -206
[5 empty] | 2019-01-04 | 26 | 85 | 3070 | -218 | 1 | 0 | 3288 | 3029.8434 | 3029.8434 | 3029.8434 | 3283.5944 | 780 | 200 | 4263.5944 | 106.6% | 95% | 100% | -249.4279 | 2780.4154 | -3550 | -400 | -1169.5846 | 29.24% | 103.3% | 95% | 100% | 3288 | -218
[5 empty] | 2019-01-04 | 27 | 85.5 | 3061 | -213 | 1 | 0 | 3274 | 3007.9143 | 3007.9143 | 3007.9143 | 3280.4617 | 780 | 200 | 4260.4617 | 106.5% | 95% | 100% | -243.7071 | 2764.2072 | -3550 | -400 | -1185.7928 | 29.64% | 103.3% | 95% | 100% | 3274 | -213
[5 empty] | 2019-01-04 | 28 | 86 | 3101 | -169 | 1 | 0 | 3270 | 3001.6488 | 3001.6488 | 3001.6488 | 3278.8953 | 780 | 200 | 4258.8953 | 106.5% | 95% | 100% | -193.3638 | 2808.285 | -3550 | -400 | -1141.715 | 28.54% | 103.3% | 95% | 100% | 3270 | -169
[5 empty] | 2019-01-04 | 29 | 86.5 | 3149 | -139 | 1 | 0 | 3288 | 3029.8434 | 3029.8434 | 3029.8434 | 3277.3289 | 780 | 200 | 4257.3289 | 106.4% | 95% | 100% | -159.0389 | 2870.8045 | -3550 | -400 | -1079.1955 | 26.98% | 103.2% | 95% | 100% | 3288 | -139
[5 empty] | 2019-01-04 | 30 | 87 | 3179 | -110 | 1 | 0 | 3289 | 3031.4097 | 3031.4097 | 3031.4097 | 3275.7626 | 780 | 200 | 4255.7626 | 106.4% | 95% | 100% | -125.8581 | 2905.5516 | -3550 | -400 | -1044.4484 | 26.11% | 103.1% | 95% | 100% | 3289 | -110
[5 empty] | 2019-01-04 | 31 | 87.5 | 3237 | -85 | 1 | 0 | 3322 | 3083.0998 | 3083.0998 | 3083.0998 | 3275.7626 | 780 | 200 | 4255.7626 | 106.4% | 95% | 100% | -97.254 | 2985.8457 | -3550 | -400 | -964.1543 | 24.1% | 103.1% | 95% | 100% | 3322 | -85
[5 empty] | 2019-01-04 | 32 | 88 | 3294 | -69 | 1 | 0 | 3363 | 3147.3207 | 3147.3207 | 3147.3207 | 3275.7626 | 780 | 200 | 4255.7626 | 106.4% | 95% | 100% | -78.9474 | 3068.3733 | -3550 | -400 | -881.6267 | 22.04% | 103.1% | 95% | 100% | 3363 | -69
[5 empty] | 2019-01-04 | 33 | 88.5 | 3297 | -64 | 1 | 0 | 3361 | 3144.188 | 3144.188 | 3144.188 | 3275.7626 | 780 | 200 | 4255.7626 | 106.4% | 95% | 100% | -73.2265 | 3070.9614 | -3550 | -400 | -879.0386 | 21.98% | 103% | 95% | 100% | 3361 | -64
[5 empty] | 2019-01-04 | 34 | 89 | 3377 | -65 | 1 | 0 | 3442 | 3271.0635 | 3271.0635 | 3271.0635 | 3274.1962 | 780 | 200 | 4254.1962 | 106.4% | 95% | 100% | -74.3707 | 3196.6928 | -3550 | -400 | -753.3072 | 18.83% | 103% | 95% | 100% | 3442 | -65
[5 empty] | 2019-01-04 | 35 | 89.5 | 3389 | -65 | 0 | 0 | 3454 | 3289.8599 | 3289.8599 | 3289.8599 | 3274.1962 | 780 | 200 | 4254.1962 | 106.4% | 95% | 100% | -74.3707 | 3215.4891 | -2750 | -200 | 265.4891 | -6.637% | 103% | 95% | 100% | 3454 | -65
[5 empty] | 2019-01-04 | 36 | 90 | 3388 | -65 | 0 | 0 | 3453 | 3288.2935 | 3288.2935 | 3288.2935 | 3274.1962 | 780 | 200 | 4254.1962 | 106.4% | 95% | 100% | -74.3707 | 3213.9228 | -2750 | -200 | 263.9228 | -6.598% | 103% | 95% | 100% | 3453 | -65
[5 empty] | 2019-01-04 | 37 | 90.5 | 3400 | -64 | 0 | 0 | 3464 | 3305.5235 | 3305.5235 | 3305.5235 | 3272.6298 | 780 | 200 | 4252.6298 | 106.3% | 95% | 100% | -73.2265 | 3232.297 | -2750 | -200 | 282.297 | -7.057% | 103% | 95% | 100% | 3464 | -64
[5 empty] | 2019-01-04 | 38 | 91 | 3377 | -63 | 0 | 0 | 3440 | 3267.9308 | 3267.9308 | 3267.9308 | 3272.6298 | 780 | 200 | 4252.6298 | 106.3% | 95% | 100% | -72.0824 | 3195.8484 | -2750 | -200 | 245.8484 | -6.146% | 103% | 95% | 100% | 3440 | -63
[5 empty] | 2019-01-04 | 39 | 91.5 | 3355 | -63 | 0 | 0 | 3418 | 3233.4707 | 3233.4707 | 3233.4707 | 3272.6298 | 780 | 200 | 4252.6298 | 106.3% | 95% | 100% | -72.0824 | 3161.3884 | -2750 | -200 | 211.3884 | -5.285% | 102.9% | 95% | 100% | 3418 | -63
[5 empty] | 2019-01-04 | 40 | 92 | 3271 | -62 | 0 | 0 | 3333 | 3100.3298 | 3100.3298 | 3100.3298 | 3271.0635 | 780 | 200 | 4251.0635 | 106.3% | 95% | 100% | -70.9382 | 3029.3915 | -2750 | -200 | 79.3915 | -1.985% | 102.9% | 95% | 100% | 3333 | -62
[5 empty] | 2019-01-04 | 41 | 92.5 | 3140 | -62 | 0 | 0 | 3202 | 2895.136 | 2895.136 | 2895.136 | 3271.0635 | 780 | 200 | 4251.0635 | 106.3% | 95% | 100% | -70.9382 | 2824.1978 | -2750 | -200 | -125.8022 | 3.145% | 102.9% | 95% | 100% | 3202 | -62
[5 empty] | 2019-01-04 | 42 | 93 | 3030 | -62 | 0 | 0 | 3092 | 2722.8359 | 2722.8359 | 2722.8359 | 3271.0635 | 780 | 200 | 4251.0635 | 106.3% | 95% | 100% | -70.9382 | 2651.8977 | -2750 | -200 | -298.1023 | 7.453% | 102.9% | 95% | 100% | 3092 | -62
[5 empty] | 2019-01-04 | 43 | 93.5 | 2897 | -62 | 0 | 0 | 2959 | 2514.5095 | 2514.5095 | 2514.5095 | 3271.0635 | 780 | 200 | 4251.0635 | 106.3% | 95% | 100% | -70.9382 | 2443.5713 | -2750 | -200 | -506.4287 | 12.66% | 102.9% | 95% | 100% | 2959 | -62
[5 empty] | 2019-01-04 | 44 | 94 | 2749 | -62 | 0 | 0 | 2811 | 2282.6876 | 2282.6876 | 2282.6876 | 3271.0635 | 780 | 200 | 4251.0635 | 106.3% | 95% | 100% | -70.9382 | 2211.7493 | -2750 | -200 | -738.2507 | 18.46% | 102.8% | 95% | 100% | 2811 | -62
[5 empty] | 2019-01-04 | 45 | 94.5 | 2604 | -61 | 0 | 0 | 2665 | 2053.9984 | 2053.9984 | 2053.9984 | 3269.4971 | 780 | 200 | 4249.4971 | 106.2% | 95% | 100% | -69.7941 | 1984.2043 | -2750 | -200 | -965.7957 | 24.14% | 102.7% | 95% | 100% | 2665 | -61
[5 empty] | 2019-01-04 | 46 | 95 | 2472 | -61 | 0 | 0 | 2533 | 1847.2383 | 1847.2383 | 1847.2383 | 3269.4971 | 780 | 200 | 4249.4971 | 106.2% | 95% | 100% | -69.7941 | 1777.4442 | -2750 | -200 | -1172.5558 | 29.31% | 102.6% | 95% | 100% | 2533 | -61
[5 empty] | 2019-01-04 | 47 | 95.5 | 2328 | -63 | 0 | 0 | 2391 | 1624.8145 | 1624.8145 | 1624.8145 | 3267.9308 | 780 | 200 | 4247.9308 | 106.2% | 95% | 100% | -72.0824 | 1552.7321 | -2750 | -200 | -1397.2679 | 34.93% | 102.6% | 95% | 100% | 2391 | -63
[5 empty] | 2019-01-04 | 48 | 96 | 2243 | -64 | 0 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 3267.9308 | 780 | 200 | 4247.9308 | 106.2% | 95% | 100% | -73.2265 | 1420.0134 | -2750 | -200 | -1529.9866 | 38.25% | 102.6% | 95% | 100% | 2307 | -64
[5 empty] | 2019-01-05 | 1 | 96.5 | 2202 | -64 | 0 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 3267.9308 | 780 | 200 | 4247.9308 | 106.2% | 95% | 100% | -73.2265 | 1355.7924 | -2750 | -200 | -1594.2076 | 39.86% | 102.6% | 95% | 100% | 2266 | -64
[5 empty] | 2019-01-05 | 2 | 97 | 2223 | -64 | 0 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 3267.9308 | 780 | 200 | 4247.9308 | 106.2% | 95% | 100% | -73.2265 | 1388.6861 | -2750 | -200 | -1561.3139 | 39.03% | 102.6% | 95% | 100% | 2287 | -64
[5 empty] | 2019-01-05 | 3 | 97.5 | 2185 | -63 | 0 | 0 | 2248 | 1400.8244 | 1400.8244 | 1400.8244 | 3267.9308 | 780 | 200 | 4247.9308 | 106.2% | 95% | 100% | -72.0824 | 1328.742 | -2750 | -200 | -1621.258 | 40.53% | 102.5% | 95% | 100% | 2248 | -63
[5 empty] | 2019-01-05 | 4 | 98 | 2116 | -63 | 0 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 3267.9308 | 780 | 200 | 4247.9308 | 106.2% | 95% | 100% | -72.0824 | 1220.6629 | -2750 | -200 | -1729.3371 | 43.23% | 102.5% | 95% | 100% | 2179 | -63
[5 empty] | 2019-01-05 | 5 | 98.5 | 2072 | -63 | 0 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 3267.9308 | 780 | 200 | 4247.9308 | 106.2% | 95% | 100% | -72.0824 | 1151.7428 | -2750 | -200 | -1798.2572 | 44.96% | 102.5% | 95% | 100% | 2135 | -63
[5 empty] | 2019-01-05 | 6 | 99 | 2057 | -62 | 0 | 0 | 2119 | 1198.7634 | 1198.7634 | 1198.7634 | 3266.3644 | 780 | 200 | 4246.3644 | 106.2% | 95% | 100% | -70.9382 | 1127.8252 | -2750 | -200 | -1822.1748 | 45.55% | 102.5% | 95% | 100% | 2119 | -62
[5 empty] | 2019-01-05 | 7 | 99.5 | 2013 | -63 | 0 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 3266.3644 | 780 | 200 | 4246.3644 | 106.2% | 95% | 100% | -72.0824 | 1059.3273 | -2750 | -200 | -1890.6727 | 47.27% | 102.4% | 95% | 100% | 2076 | -63
[5 empty] | 2019-01-05 | 8 | 100 | 1970 | -63 | 0 | 0 | 2033 | 1064.0561 | 1064.0561 | 1064.0561 | 3266.3644 | 780 | 200 | 4246.3644 | 106.2% | 95% | 100% | -72.0824 | 991.9737 | -2750 | -200 | -1958.0263 | 48.95% | 102.4% | 95% | 100% | 2033 | -63
[5 empty] | 2019-01-05 | 9 | 100.5 | 1952 | -63 | 0 | 0 | 2015 | 1035.8615 | 1035.8615 | 1035.8615 | 3266.3644 | 780 | 200 | 4246.3644 | 106.2% | 95% | 100% | -72.0824 | 963.7791 | -2750 | -200 | -1986.2209 | 49.66% | 102.4% | 95% | 100% | 2015 | -63
[5 empty] | 2019-01-05 | 10 | 101 | 1942 | -62 | 0 | 0 | 2004 | 1018.6315 | 1018.6315 | 1018.6315 | 3266.3644 | 780 | 200 | 4246.3644 | 106.2% | 95% | 100% | -70.9382 | 947.6933 | -2750 | -200 | -2002.3067 | 50.06% | 102.4% | 95% | 100% | 2004 | -62
[5 empty] | 2019-01-05 | 11 | 101.5 | 1956 | -62 | 0 | 0 | 2018 | 1040.5606 | 1040.5606 | 1040.5606 | 3264.798 | 780 | 200 | 4244.798 | 106.1% | 95% | 100% | -70.9382 | 969.6224 | -2750 | -200 | -1980.3776 | 49.51% | 102.4% | 95% | 100% | 2018 | -62
[5 empty] | 2019-01-05 | 12 | 102 | 1981 | -62 | 0 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 3264.798 | 780 | 200 | 4244.798 | 106.1% | 95% | 100% | -70.9382 | 1008.7815 | -2750 | -200 | -1941.2185 | 48.53% | 102.3% | 95% | 100% | 2043 | -62
[5 empty] | 2019-01-05 | 13 | 102.5 | 2084 | -61 | 0 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 3261.6653 | 780 | 200 | 4241.6653 | 106% | 95% | 100% | -69.7941 | 1169.6948 | -2750 | -200 | -1780.3052 | 44.51% | 102.2% | 95% | 100% | 2145 | -61
[5 empty] | 2019-01-05 | 14 | 103 | 2151 | -60 | 0 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 3261.6653 | 780 | 200 | 4241.6653 | 106% | 95% | 100% | -68.6499 | 1274.219 | -2750 | -200 | -1675.781 | 41.89% | 102.2% | 95% | 100% | 2211 | -60
[5 empty] | 2019-01-05 | 15 | 103.5 | 2256 | -62 | 0 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 3260.0989 | 780 | 200 | 4240.0989 | 106% | 95% | 100% | -70.9382 | 1439.5317 | -2750 | -200 | -1510.4683 | 37.76% | 102.2% | 95% | 100% | 2318 | -62
[5 empty] | 2019-01-05 | 16 | 104 | 2348 | -63 | 0 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 3260.0989 | 780 | 200 | 4240.0989 | 106% | 95% | 100% | -72.0824 | 1584.0594 | -2750 | -200 | -1365.9406 | 34.15% | 102.2% | 95% | 100% | 2411 | -63
[5 empty] | 2019-01-05 | 17 | 104.5 | 2486 | -64 | 0 | 0 | 2550 | 1873.8664 | 1873.8664 | 1873.8664 | 3260.0989 | 780 | 200 | 4240.0989 | 106% | 95% | 100% | -73.2265 | 1800.6399 | -2750 | -200 | -1149.3601 | 28.73% | 102.1% | 95% | 100% | 2550 | -64
[5 empty] | 2019-01-05 | 18 | 105 | 2611 | -66 | 0 | 0 | 2677 | 2072.7947 | 2072.7947 | 2072.7947 | 3260.0989 | 780 | 200 | 4240.0989 | 106% | 95% | 100% | -75.5149 | 1997.2798 | -2750 | -200 | -952.7202 | 23.82% | 102.1% | 95% | 100% | 2677 | -66
[5 empty] | 2019-01-05 | 19 | 105.5 | 2748 | -71 | 1 | 0 | 2819 | 2295.2185 | 2295.2185 | 2295.2185 | 3260.0989 | 780 | 200 | 4240.0989 | 106% | 95% | 100% | -81.2357 | 2213.9828 | -3550 | -400 | -1736.0172 | 43.4% | 102% | 95% | 100% | 2819 | -71
[5 empty] | 2019-01-05 | 20 | 106 | 2805 | -79 | 1 | 0 | 2884 | 2397.0322 | 2397.0322 | 2397.0322 | 3258.5326 | 780 | 200 | 4238.5326 | 106% | 95% | 100% | -90.389 | 2306.6431 | -3550 | -400 | -1643.3569 | 41.08% | 102% | 95% | 100% | 2884 | -79
[5 empty] | 2019-01-05 | 21 | 106.5 | 2831 | -86 | 1 | 0 | 2917 | 2448.7222 | 2448.7222 | 2448.7222 | 3256.9662 | 780 | 200 | 4236.9662 | 105.9% | 95% | 100% | -98.3982 | 2350.324 | -3550 | -400 | -1599.676 | 39.99% | 102% | 95% | 100% | 2917 | -86
[5 empty] | 2019-01-05 | 22 | 107 | 2840 | -93 | 1 | 0 | 2933 | 2473.784 | 2473.784 | 2473.784 | 3255.3998 | 780 | 200 | 4235.3998 | 105.9% | 95% | 100% | -106.4073 | 2367.3767 | -3550 | -400 | -1582.6233 | 39.57% | 102% | 95% | 100% | 2933 | -93
[5 empty] | 2019-01-05 | 23 | 107.5 | 2856 | -100 | 1 | 0 | 2956 | 2509.8104 | 2509.8104 | 2509.8104 | 3255.3998 | 780 | 200 | 4235.3998 | 105.9% | 95% | 100% | -114.4165 | 2395.3939 | -3550 | -400 | -1554.6061 | 38.87% | 101.9% | 95% | 100% | 2956 | -100
[5 empty] | 2019-01-05 | 24 | 108 | 2866 | -105 | 1 | 0 | 2971 | 2533.3059 | 2533.3059 | 2533.3059 | 3253.8335 | 780 | 200 | 4233.8335 | 105.8% | 95% | 100% | -120.1373 | 2413.1686 | -3550 | -400 | -1536.8314 | 38.42% | 101.9% | 95% | 100% | 2971 | -105
[5 empty] | 2019-01-05 | 25 | 108.5 | 2877 | -106 | 1 | 0 | 2983 | 2552.1022 | 2552.1022 | 2552.1022 | 3253.8335 | 780 | 200 | 4233.8335 | 105.8% | 95% | 100% | -121.2815 | 2430.8208 | -3550 | -400 | -1519.1792 | 37.98% | 101.9% | 95% | 100% | 2983 | -106
[5 empty] | 2019-01-05 | 26 | 109 | 2891 | -106 | 1 | 0 | 2997 | 2574.0313 | 2574.0313 | 2574.0313 | 3253.8335 | 780 | 200 | 4233.8335 | 105.8% | 95% | 100% | -121.2815 | 2452.7499 | -3550 | -400 | -1497.2501 | 37.43% | 101.9% | 95% | 100% | 2997 | -106
[5 empty] | 2019-01-05 | 27 | 109.5 | 2916 | -101 | 1 | 0 | 3017 | 2605.3586 | 2605.3586 | 2605.3586 | 3253.8335 | 780 | 200 | 4233.8335 | 105.8% | 95% | 100% | -115.5606 | 2489.798 | -3550 | -400 | -1460.202 | 36.51% | 101.9% | 95% | 100% | 3017 | -101
[5 empty] | 2019-01-05 | 28 | 110 | 2925 | -95 | 1 | 0 | 3020 | 2610.0577 | 2610.0577 | 2610.0577 | 3252.2671 | 780 | 200 | 4232.2671 | 105.8% | 95% | 100% | -108.6957 | 2501.3621 | -3550 | -400 | -1448.6379 | 36.22% | 101.9% | 95% | 100% | 3020 | -95
[5 empty] | 2019-01-05 | 29 | 110.5 | 2927 | -89 | 1 | 0 | 3016 | 2603.7923 | 2603.7923 | 2603.7923 | 3250.7007 | 780 | 200 | 4230.7007 | 105.8% | 95% | 100% | -101.8307 | 2501.9616 | -3550 | -400 | -1448.0384 | 36.2% | 101.9% | 95% | 100% | 3016 | -89
[5 empty] | 2019-01-05 | 30 | 111 | 2933 | -81 | 1 | 0 | 3014 | 2600.6595 | 2600.6595 | 2600.6595 | 3249.1344 | 780 | 200 | 4229.1344 | 105.7% | 95% | 100% | -92.6773 | 2507.9822 | -3550 | -400 | -1442.0178 | 36.05% | 101.8% | 95% | 100% | 3014 | -81
[5 empty] | 2019-01-05 | 31 | 111.5 | 2956 | -74 | 1 | 0 | 3030 | 2625.7214 | 2625.7214 | 2625.7214 | 3247.568 | 780 | 200 | 4227.568 | 105.7% | 95% | 100% | -84.6682 | 2541.0532 | -3550 | -400 | -1408.9468 | 35.22% | 101.8% | 95% | 100% | 3030 | -74
[5 empty] | 2019-01-05 | 32 | 112 | 2999 | -71 | 1 | 0 | 3070 | 2688.3759 | 2688.3759 | 2688.3759 | 3247.568 | 780 | 200 | 4227.568 | 105.7% | 95% | 100% | -81.2357 | 2607.1402 | -3550 | -400 | -1342.8598 | 33.57% | 101.8% | 95% | 100% | 3070 | -71
[5 empty] | 2019-01-05 | 33 | 112.5 | 3092 | -71 | 1 | 0 | 3163 | 2834.0478 | 2834.0478 | 2834.0478 | 3247.568 | 780 | 200 | 4227.568 | 105.7% | 95% | 100% | -81.2357 | 2752.8121 | -3550 | -400 | -1197.1879 | 29.93% | 101.8% | 95% | 100% | 3163 | -71
[5 empty] | 2019-01-05 | 34 | 113 | 3210 | -71 | 1 | 0 | 3281 | 3018.8788 | 3018.8788 | 3018.8788 | 3246.0016 | 780 | 200 | 4226.0016 | 105.7% | 95% | 100% | -81.2357 | 2937.6431 | -3550 | -400 | -1012.3569 | 25.31% | 101.8% | 95% | 100% | 3281 | -71
[5 empty] | 2019-01-05 | 35 | 113.5 | 3256 | -71 | 1 | 0 | 3327 | 3090.9316 | 3090.9316 | 3090.9316 | 3246.0016 | 780 | 200 | 4226.0016 | 105.7% | 95% | 100% | -81.2357 | 3009.6959 | -3550 | -400 | -940.3041 | 23.51% | 101.8% | 95% | 100% | 3327 | -71
[5 empty] | 2019-01-05 | 36 | 114 | 3246 | -70 | 0 | 0 | 3316 | 3073.7016 | 3073.7016 | 3073.7016 | 3246.0016 | 780 | 200 | 4226.0016 | 105.7% | 95% | 100% | -80.0915 | 2993.61 | -2750 | -200 | 43.61 | -1.09% | 101.7% | 95% | 100% | 3316 | -70
[5 empty] | 2019-01-05 | 37 | 114.5 | 3212 | -70 | 0 | 0 | 3282 | 3020.4452 | 3020.4452 | 3020.4452 | 3244.4353 | 780 | 200 | 4224.4353 | 105.6% | 95% | 100% | -80.0915 | 2940.3536 | -2750 | -200 | -9.6464 | 0.2412% | 101.7% | 95% | 100% | 3282 | -70
[5 empty] | 2019-01-05 | 38 | 115 | 3154 | -70 | 0 | 0 | 3224 | 2929.596 | 2929.596 | 2929.596 | 3244.4353 | 780 | 200 | 4224.4353 | 105.6% | 95% | 100% | -80.0915 | 2849.5045 | -2750 | -200 | -100.4955 | 2.512% | 101.6% | 95% | 100% | 3224 | -70
[5 empty] | 2019-01-05 | 39 | 115.5 | 3071 | -70 | 0 | 0 | 3141 | 2799.5878 | 2799.5878 | 2799.5878 | 3244.4353 | 780 | 200 | 4224.4353 | 105.6% | 95% | 100% | -80.0915 | 2719.4963 | -2750 | -200 | -230.5037 | 5.763% | 101.6% | 95% | 100% | 3141 | -70
[5 empty] | 2019-01-05 | 40 | 116 | 2958 | -71 | 0 | 0 | 3029 | 2624.155 | 2624.155 | 2624.155 | 3242.8689 | 780 | 200 | 4222.8689 | 105.6% | 95% | 100% | -81.2357 | 2542.9193 | -2750 | -200 | -407.0807 | 10.18% | 101.6% | 95% | 100% | 3029 | -71
[5 empty] | 2019-01-05 | 41 | 116.5 | 2872 | -71 | 0 | 0 | 2943 | 2489.4477 | 2489.4477 | 2489.4477 | 3242.8689 | 780 | 200 | 4222.8689 | 105.6% | 95% | 100% | -81.2357 | 2408.212 | -2750 | -200 | -541.788 | 13.54% | 101.6% | 95% | 100% | 2943 | -71
[5 empty] | 2019-01-05 | 42 | 117 | 2746 | -72 | 0 | 0 | 2818 | 2293.6521 | 2293.6521 | 2293.6521 | 3242.8689 | 780 | 200 | 4222.8689 | 105.6% | 95% | 100% | -82.3799 | 2211.2722 | -2750 | -200 | -738.7278 | 18.47% | 101.6% | 95% | 100% | 2818 | -72
[5 empty] | 2019-01-05 | 43 | 117.5 | 2658 | -72 | 0 | 0 | 2730 | 2155.812 | 2155.812 | 2155.812 | 3242.8689 | 780 | 200 | 4222.8689 | 105.6% | 95% | 100% | -82.3799 | 2073.4322 | -2750 | -200 | -876.5678 | 21.91% | 101.5% | 95% | 100% | 2730 | -72
[5 empty] | 2019-01-05 | 44 | 118 | 2540 | -72 | 0 | 0 | 2612 | 1970.981 | 1970.981 | 1970.981 | 3242.8689 | 780 | 200 | 4222.8689 | 105.6% | 95% | 100% | -82.3799 | 1888.6012 | -2750 | -200 | -1061.3988 | 26.53% | 101.5% | 95% | 100% | 2612 | -72
[5 empty] | 2019-01-05 | 45 | 118.5 | 2420 | -71 | 0 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 3242.8689 | 780 | 200 | 4222.8689 | 105.6% | 95% | 100% | -81.2357 | 1700.2153 | -2750 | -200 | -1249.7847 | 31.24% | 101.5% | 95% | 100% | 2491 | -71
[5 empty] | 2019-01-05 | 46 | 119 | 2329 | -70 | 0 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 3242.8689 | 780 | 200 | 4222.8689 | 105.6% | 95% | 100% | -80.0915 | 1557.2539 | -2750 | -200 | -1392.7461 | 34.82% | 101.5% | 95% | 100% | 2399 | -70
[5 empty] | 2019-01-05 | 47 | 119.5 | 2205 | -69 | 0 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 3241.3026 | 780 | 200 | 4221.3026 | 105.5% | 95% | 100% | -78.9474 | 1362.6025 | -2750 | -200 | -1587.3975 | 39.68% | 101.5% | 95% | 100% | 2274 | -69
[5 empty] | 2019-01-05 | 48 | 120 | 2126 | -67 | 0 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 3239.7362 | 780 | 200 | 4219.7362 | 105.5% | 95% | 100% | -76.659 | 1238.0153 | -2750 | -200 | -1711.9847 | 42.8% | 101.5% | 95% | 100% | 2193 | -67
[5 empty] | 2019-01-06 | 1 | 120.5 | 2098 | -66 | 0 | 0 | 2164 | 1269.2498 | 1269.2498 | 1269.2498 | 3239.7362 | 780 | 200 | 4219.7362 | 105.5% | 95% | 100% | -75.5149 | 1193.7349 | -2750 | -200 | -1756.2651 | 43.91% | 101.5% | 95% | 100% | 2164 | -66
[5 empty] | 2019-01-06 | 2 | 121 | 2116 | -65 | 0 | 0 | 2181 | 1295.878 | 1295.878 | 1295.878 | 3238.1698 | 780 | 200 | 4218.1698 | 105.5% | 95% | 100% | -74.3707 | 1221.5073 | -2750 | -200 | -1728.4927 | 43.21% | 101.4% | 95% | 100% | 2181 | -65
[5 empty] | 2019-01-06 | 3 | 121.5 | 2059 | -64 | 0 | 0 | 2123 | 1205.0289 | 1205.0289 | 1205.0289 | 3236.6035 | 780 | 200 | 4216.6035 | 105.4% | 95% | 100% | -73.2265 | 1131.8023 | -2750 | -200 | -1818.1977 | 45.45% | 101.4% | 95% | 100% | 2123 | -64
[5 empty] | 2019-01-06 | 4 | 122 | 1990 | -62 | 0 | 0 | 2052 | 1093.817 | 1093.817 | 1093.817 | 3236.6035 | 780 | 200 | 4216.6035 | 105.4% | 95% | 100% | -70.9382 | 1022.8788 | -2750 | -200 | -1927.1212 | 48.18% | 101.4% | 95% | 100% | 2052 | -62
[5 empty] | 2019-01-06 | 5 | 122.5 | 1940 | -63 | 0 | 0 | 2003 | 1017.0651 | 1017.0651 | 1017.0651 | 3236.6035 | 780 | 200 | 4216.6035 | 105.4% | 95% | 100% | -72.0824 | 944.9827 | -2750 | -200 | -2005.0173 | 50.13% | 101.4% | 95% | 100% | 2003 | -63
[5 empty] | 2019-01-06 | 6 | 123 | 1925 | -64 | 0 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 3235.0371 | 780 | 200 | 4215.0371 | 105.4% | 95% | 100% | -73.2265 | 921.9095 | -2750 | -200 | -2028.0905 | 50.7% | 101.4% | 95% | 100% | 1989 | -64
[5 empty] | 2019-01-06 | 7 | 123.5 | 1899 | -64 | 0 | 0 | 1963 | 954.4106 | 954.4106 | 954.4106 | 3235.0371 | 780 | 200 | 4215.0371 | 105.4% | 95% | 100% | -73.2265 | 881.184 | -2750 | -200 | -2068.816 | 51.72% | 101.4% | 95% | 100% | 1963 | -64
[5 empty] | 2019-01-06 | 8 | 124 | 1854 | -65 | 0 | 0 | 1919 | 885.4905 | 885.4905 | 885.4905 | 3235.0371 | 780 | 200 | 4215.0371 | 105.4% | 95% | 100% | -74.3707 | 811.1198 | -2750 | -200 | -2138.8802 | 53.47% | 101.4% | 95% | 100% | 1919 | -65
[5 empty] | 2019-01-06 | 9 | 124.5 | 1820 | -65 | 0 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 3235.0371 | 780 | 200 | 4215.0371 | 105.4% | 95% | 100% | -74.3707 | 757.8634 | -2750 | -200 | -2192.1366 | 54.8% | 101.4% | 95% | 100% | 1885 | -65
[5 empty] | 2019-01-06 | 10 | 125 | 1804 | -64 | 0 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 3235.0371 | 780 | 200 | 4215.0371 | 105.4% | 95% | 100% | -73.2265 | 732.3794 | -2750 | -200 | -2217.6206 | 55.44% | 101.3% | 95% | 100% | 1868 | -64
[5 empty] | 2019-01-06 | 11 | 125.5 | 1808 | -63 | 0 | 0 | 1871 | 810.305 | 810.305 | 810.305 | 3233.4707 | 780 | 200 | 4213.4707 | 105.3% | 95% | 100% | -72.0824 | 738.2226 | -2750 | -200 | -2211.7774 | 55.29% | 101.3% | 95% | 100% | 1871 | -63
[5 empty] | 2019-01-06 | 12 | 126 | 1835 | -61 | 0 | 0 | 1896 | 849.4641 | 849.4641 | 849.4641 | 3233.4707 | 780 | 200 | 4213.4707 | 105.3% | 95% | 100% | -69.7941 | 779.6701 | -2750 | -200 | -2170.3299 | 54.26% | 101.3% | 95% | 100% | 1896 | -61
[5 empty] | 2019-01-06 | 13 | 126.5 | 1894 | -58 | 0 | 0 | 1952 | 937.1805 | 937.1805 | 937.1805 | 3233.4707 | 780 | 200 | 4213.4707 | 105.3% | 95% | 100% | -66.3616 | 870.819 | -2750 | -200 | -2079.181 | 51.98% | 101.2% | 95% | 100% | 1952 | -58
[5 empty] | 2019-01-06 | 14 | 127 | 1945 | -54 | 0 | 0 | 1999 | 1010.7997 | 1010.7997 | 1010.7997 | 3231.9044 | 780 | 200 | 4211.9044 | 105.3% | 95% | 100% | -61.7849 | 949.0148 | -2750 | -200 | -2000.9852 | 50.02% | 101.2% | 95% | 100% | 1999 | -54
[5 empty] | 2019-01-06 | 15 | 127.5 | 2023 | -51 | 0 | 0 | 2074 | 1128.277 | 1128.277 | 1128.277 | 3231.9044 | 780 | 200 | 4211.9044 | 105.3% | 95% | 100% | -58.3524 | 1069.9246 | -2750 | -200 | -1880.0754 | 47% | 101.2% | 95% | 100% | 2074 | -51
[5 empty] | 2019-01-06 | 16 | 128 | 2087 | -48 | 0 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 3231.9044 | 780 | 200 | 4211.9044 | 105.3% | 95% | 100% | -54.9199 | 1168.9053 | -2750 | -200 | -1781.0947 | 44.53% | 101.2% | 95% | 100% | 2135 | -48
[5 empty] | 2019-01-06 | 17 | 128.5 | 2201 | -45 | 0 | 0 | 2246 | 1397.6917 | 1397.6917 | 1397.6917 | 3231.9044 | 780 | 200 | 4211.9044 | 105.3% | 95% | 100% | -51.4874 | 1346.2043 | -2750 | -200 | -1603.7957 | 40.09% | 101.2% | 95% | 100% | 2246 | -45
[5 empty] | 2019-01-06 | 18 | 129 | 2317 | -44 | 0 | 0 | 2361 | 1577.8236 | 1577.8236 | 1577.8236 | 3231.9044 | 780 | 200 | 4211.9044 | 105.3% | 95% | 100% | -50.3432 | 1527.4803 | -2750 | -200 | -1422.5197 | 35.56% | 101.1% | 95% | 100% | 2361 | -44
[5 empty] | 2019-01-06 | 19 | 129.5 | 2448 | -50 | 0 | 0 | 2498 | 1792.4155 | 1792.4155 | 1792.4155 | 3230.338 | 780 | 200 | 4210.338 | 105.3% | 95% | 100% | -57.2082 | 1735.2073 | -2750 | -200 | -1214.7927 | 30.37% | 101.1% | 95% | 100% | 2498 | -50
[5 empty] | 2019-01-06 | 20 | 130 | 2560 | -60 | 1 | 0 | 2620 | 1983.512 | 1983.512 | 1983.512 | 3230.338 | 780 | 200 | 4210.338 | 105.3% | 95% | 100% | -68.6499 | 1914.8621 | -3550 | -400 | -2035.1379 | 50.88% | 101.1% | 95% | 100% | 2620 | -60
[5 empty] | 2019-01-06 | 21 | 130.5 | 2639 | -74 | 1 | 0 | 2713 | 2129.1838 | 2129.1838 | 2129.1838 | 3230.338 | 780 | 200 | 4210.338 | 105.3% | 95% | 100% | -84.6682 | 2044.5156 | -3550 | -400 | -1905.4844 | 47.64% | 101.1% | 95% | 100% | 2713 | -74
[5 empty] | 2019-01-06 | 22 | 131 | 2679 | -84 | 1 | 0 | 2763 | 2207.5021 | 2207.5021 | 2207.5021 | 3230.338 | 780 | 200 | 4210.338 | 105.3% | 95% | 100% | -96.1098 | 2111.3922 | -3550 | -400 | -1838.6078 | 45.97% | 101.1% | 95% | 100% | 2763 | -84
[5 empty] | 2019-01-06 | 23 | 131.5 | 2692 | -96 | 1 | 0 | 2788 | 2246.6612 | 2246.6612 | 2246.6612 | 3230.338 | 780 | 200 | 4210.338 | 105.3% | 95% | 100% | -109.8398 | 2136.8214 | -3550 | -400 | -1813.1786 | 45.33% | 101.1% | 95% | 100% | 2788 | -96
[5 empty] | 2019-01-06 | 24 | 132 | 2722 | -111 | 1 | 0 | 2833 | 2317.1476 | 2317.1476 | 2317.1476 | 3228.7716 | 780 | 200 | 4208.7716 | 105.2% | 95% | 100% | -127.0023 | 2190.1453 | -3550 | -400 | -1759.8547 | 44% | 101.1% | 95% | 100% | 2833 | -111
[5 empty] | 2019-01-06 | 25 | 132.5 | 2753 | -116 | 1 | 0 | 2869 | 2373.5367 | 2373.5367 | 2373.5367 | 3227.2053 | 780 | 200 | 4207.2053 | 105.2% | 95% | 100% | -132.7231 | 2240.8136 | -3550 | -400 | -1709.1864 | 42.73% | 101% | 95% | 100% | 2869 | -116
[5 empty] | 2019-01-06 | 26 | 133 | 2771 | -110 | 1 | 0 | 2881 | 2392.3331 | 2392.3331 | 2392.3331 | 3227.2053 | 780 | 200 | 4207.2053 | 105.2% | 95% | 100% | -125.8581 | 2266.4749 | -3550 | -400 | -1683.5251 | 42.09% | 101% | 95% | 100% | 2881 | -110
[5 empty] | 2019-01-06 | 27 | 133.5 | 2794 | -100 | 1 | 0 | 2894 | 2412.6958 | 2412.6958 | 2412.6958 | 3227.2053 | 780 | 200 | 4207.2053 | 105.2% | 95% | 100% | -114.4165 | 2298.2793 | -3550 | -400 | -1651.7207 | 41.29% | 101% | 95% | 100% | 2894 | -100
[5 empty] | 2019-01-06 | 28 | 134 | 2811 | -84 | 1 | 0 | 2895 | 2414.2622 | 2414.2622 | 2414.2622 | 3225.6389 | 780 | 200 | 4205.6389 | 105.1% | 95% | 100% | -96.1098 | 2318.1523 | -3550 | -400 | -1631.8477 | 40.8% | 100.9% | 95% | 100% | 2895 | -84
[5 empty] | 2019-01-06 | 29 | 134.5 | 2848 | -67 | 1 | 0 | 2915 | 2445.5894 | 2445.5894 | 2445.5894 | 3224.0725 | 780 | 200 | 4204.0725 | 105.1% | 95% | 100% | -76.659 | 2368.9304 | -3550 | -400 | -1581.0696 | 39.53% | 100.9% | 95% | 100% | 2915 | -67
[5 empty] | 2019-01-06 | 30 | 135 | 2873 | -51 | 1 | 0 | 2924 | 2459.6867 | 2459.6867 | 2459.6867 | 3222.5062 | 780 | 200 | 4202.5062 | 105.1% | 95% | 100% | -58.3524 | 2401.3343 | -3550 | -400 | -1548.6657 | 38.72% | 100.9% | 95% | 100% | 2924 | -51
[5 empty] | 2019-01-06 | 31 | 135.5 | 2932 | -40 | 1 | 0 | 2972 | 2534.8722 | 2534.8722 | 2534.8722 | 3222.5062 | 780 | 200 | 4202.5062 | 105.1% | 95% | 100% | -45.7666 | 2489.1056 | -3550 | -400 | -1460.8944 | 36.52% | 100.9% | 95% | 100% | 2972 | -40
[5 empty] | 2019-01-06 | 32 | 136 | 3006 | -33 | 1 | 0 | 3039 | 2639.8186 | 2639.8186 | 2639.8186 | 3222.5062 | 780 | 200 | 4202.5062 | 105.1% | 95% | 100% | -37.7574 | 2602.0612 | -3550 | -400 | -1347.9388 | 33.7% | 100.8% | 95% | 100% | 3039 | -33
[5 empty] | 2019-01-06 | 33 | 136.5 | 3114 | -33 | 1 | 0 | 3147 | 2808.986 | 2808.986 | 2808.986 | 3222.5062 | 780 | 200 | 4202.5062 | 105.1% | 95% | 100% | -37.7574 | 2771.2285 | -3550 | -400 | -1178.7715 | 29.47% | 100.8% | 95% | 100% | 3147 | -33
[5 empty] | 2019-01-06 | 34 | 137 | 3222 | -34 | 1 | 0 | 3256 | 2979.7197 | 2979.7197 | 2979.7197 | 3222.5062 | 780 | 200 | 4202.5062 | 105.1% | 95% | 100% | -38.9016 | 2940.8181 | -3550 | -400 | -1009.1819 | 25.23% | 100.8% | 95% | 100% | 3256 | -34
[5 empty] | 2019-01-06 | 35 | 137.5 | 3260 | -35 | 0 | 0 | 3295 | 3040.8079 | 3040.8079 | 3040.8079 | 3220.9398 | 780 | 200 | 4200.9398 | 105% | 95% | 100% | -40.0458 | 3000.7621 | -2750 | -200 | 50.7621 | -1.269% | 100.8% | 95% | 100% | 3295 | -35
[5 empty] | 2019-01-06 | 36 | 138 | 3234 | -36 | 0 | 0 | 3270 | 3001.6488 | 3001.6488 | 3001.6488 | 3220.9398 | 780 | 200 | 4200.9398 | 105% | 95% | 100% | -41.1899 | 2960.4589 | -2750 | -200 | 10.4589 | -0.2615% | 100.8% | 95% | 100% | 3270 | -36
[5 empty] | 2019-01-06 | 37 | 138.5 | 3204 | -38 | 0 | 0 | 3242 | 2957.7906 | 2957.7906 | 2957.7906 | 3219.3735 | 780 | 200 | 4199.3735 | 105% | 95% | 100% | -43.4783 | 2914.3123 | -2750 | -200 | -35.6877 | 0.8922% | 100.8% | 95% | 100% | 3242 | -38
[5 empty] | 2019-01-06 | 38 | 139 | 3169 | -40 | 0 | 0 | 3209 | 2906.1006 | 2906.1006 | 2906.1006 | 3219.3735 | 780 | 200 | 4199.3735 | 105% | 95% | 100% | -45.7666 | 2860.334 | -2750 | -200 | -89.666 | 2.242% | 100.7% | 95% | 100% | 3209 | -40
[5 empty] | 2019-01-06 | 39 | 139.5 | 3075 | -43 | 0 | 0 | 3118 | 2763.5614 | 2763.5614 | 2763.5614 | 3219.3735 | 780 | 200 | 4199.3735 | 105% | 95% | 100% | -49.1991 | 2714.3623 | -2750 | -200 | -235.6377 | 5.891% | 100.7% | 95% | 100% | 3118 | -43
[5 empty] | 2019-01-06 | 40 | 140 | 2964 | -46 | 0 | 0 | 3010 | 2594.3941 | 2594.3941 | 2594.3941 | 3219.3735 | 780 | 200 | 4199.3735 | 105% | 95% | 100% | -52.6316 | 2541.7625 | -2750 | -200 | -408.2375 | 10.21% | 100.7% | 95% | 100% | 3010 | -46
[5 empty] | 2019-01-06 | 41 | 140.5 | 2871 | -50 | 0 | 0 | 2921 | 2454.9876 | 2454.9876 | 2454.9876 | 3219.3735 | 780 | 200 | 4199.3735 | 105% | 95% | 100% | -57.2082 | 2397.7794 | -2750 | -200 | -552.2206 | 13.81% | 100.7% | 95% | 100% | 2921 | -50
[5 empty] | 2019-01-06 | 42 | 141 | 2760 | -54 | 0 | 0 | 2814 | 2287.3866 | 2287.3866 | 2287.3866 | 3217.8071 | 780 | 200 | 4197.8071 | 104.9% | 95% | 100% | -61.7849 | 2225.6017 | -2750 | -200 | -724.3983 | 18.11% | 100.7% | 95% | 100% | 2814 | -54
[5 empty] | 2019-01-06 | 43 | 141.5 | 2624 | -59 | 0 | 0 | 2683 | 2082.1929 | 2082.1929 | 2082.1929 | 3217.8071 | 780 | 200 | 4197.8071 | 104.9% | 95% | 100% | -67.5057 | 2014.6872 | -2750 | -200 | -935.3128 | 23.38% | 100.7% | 95% | 100% | 2683 | -59
[5 empty] | 2019-01-06 | 44 | 142 | 2477 | -64 | 0 | 0 | 2541 | 1859.7692 | 1859.7692 | 1859.7692 | 3217.8071 | 780 | 200 | 4197.8071 | 104.9% | 95% | 100% | -73.2265 | 1786.5426 | -2750 | -200 | -1163.4574 | 29.09% | 100.7% | 95% | 100% | 2541 | -64
[5 empty] | 2019-01-06 | 45 | 142.5 | 2342 | -68 | 0 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 3216.2407 | 780 | 200 | 4196.2407 | 104.9% | 95% | 100% | -77.8032 | 1576.7722 | -2750 | -200 | -1373.2278 | 34.33% | 100.7% | 95% | 100% | 2410 | -68
[5 empty] | 2019-01-06 | 46 | 143 | 2188 | -73 | 0 | 0 | 2261 | 1421.1871 | 1421.1871 | 1421.1871 | 3216.2407 | 780 | 200 | 4196.2407 | 104.9% | 95% | 100% | -83.524 | 1337.6631 | -2750 | -200 | -1612.3369 | 40.31% | 100.7% | 95% | 100% | 2261 | -73
[5 empty] | 2019-01-06 | 47 | 143.5 | 2032 | -80 | 0 | 0 | 2112 | 1187.7988 | 1187.7988 | 1187.7988 | 3214.6744 | 780 | 200 | 4194.6744 | 104.9% | 95% | 100% | -91.5332 | 1096.2657 | -2750 | -200 | -1853.7343 | 46.34% | 100.7% | 95% | 100% | 2112 | -80
[5 empty] | 2019-01-06 | 48 | 144 | 1937 | -86 | 0 | 0 | 2023 | 1048.3924 | 1048.3924 | 1048.3924 | 3214.6744 | 780 | 200 | 4194.6744 | 104.9% | 95% | 100% | -98.3982 | 949.9942 | -2750 | -200 | -2000.0058 | 50% | 100.7% | 95% | 100% | 2023 | -86
[5 empty] | 2019-01-07 | 1 | 144.5 | 1912 | -92 | 0 | 0 | 2004 | 1018.6315 | 1018.6315 | 1018.6315 | 3213.108 | 780 | 200 | 4193.108 | 104.8% | 95% | 100% | -105.2632 | 913.3683 | -2750 | -200 | -2036.6317 | 50.92% | 100.6% | 95% | 100% | 2004 | -92
[5 empty] | 2019-01-07 | 2 | 145 | 1928 | -98 | 0 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 3211.5416 | 780 | 200 | 4191.5416 | 104.8% | 95% | 100% | -112.1281 | 940.9634 | -2750 | -200 | -2009.0366 | 50.23% | 100.6% | 95% | 100% | 2026 | -98
[5 empty] | 2019-01-07 | 3 | 145.5 | 1909 | -101 | 0 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 3209.9753 | 780 | 200 | 4189.9753 | 104.7% | 95% | 100% | -115.5606 | 912.469 | -2750 | -200 | -2037.531 | 50.94% | 100.6% | 95% | 100% | 2010 | -101
[5 empty] | 2019-01-07 | 4 | 146 | 1859 | -105 | 0 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 3209.9753 | 780 | 200 | 4189.9753 | 104.7% | 95% | 100% | -120.1373 | 835.8396 | -2750 | -200 | -2114.1604 | 52.85% | 100.6% | 95% | 100% | 1964 | -105
[5 empty] | 2019-01-07 | 5 | 146.5 | 1804 | -109 | 0 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 3208.4089 | 780 | 200 | 4188.4089 | 104.7% | 95% | 100% | -124.714 | 751.3784 | -2750 | -200 | -2198.6216 | 54.97% | 100.6% | 95% | 100% | 1913 | -109
[5 empty] | 2019-01-07 | 6 | 147 | 1782 | -113 | 0 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 3208.4089 | 780 | 200 | 4188.4089 | 104.7% | 95% | 100% | -129.2906 | 718.6072 | -2750 | -200 | -2231.3928 | 55.78% | 100.6% | 95% | 100% | 1895 | -113
[5 empty] | 2019-01-07 | 7 | 147.5 | 1748 | -116 | 0 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 3206.8425 | 780 | 200 | 4186.8425 | 104.7% | 95% | 100% | -132.7231 | 666.6174 | -2750 | -200 | -2283.3826 | 57.08% | 100.5% | 95% | 100% | 1864 | -116
[5 empty] | 2019-01-07 | 8 | 148 | 1695 | -119 | 0 | 0 | 1814 | 721.0223 | 721.0223 | 721.0223 | 3206.8425 | 780 | 200 | 4186.8425 | 104.7% | 95% | 100% | -136.1556 | 584.8667 | -2750 | -200 | -2365.1333 | 59.13% | 100.5% | 95% | 100% | 1814 | -119
[5 empty] | 2019-01-07 | 9 | 148.5 | 1665 | -124 | 0 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 3200.5771 | 780 | 200 | 4180.5771 | 104.5% | 95% | 100% | -141.8764 | 539.9867 | -2750 | -200 | -2410.0133 | 60.25% | 100.5% | 95% | 100% | 1789 | -124
[5 empty] | 2019-01-07 | 10 | 149 | 1664 | -129 | 0 | 0 | 1793 | 688.1286 | 688.1286 | 688.1286 | 3200.5771 | 780 | 200 | 4180.5771 | 104.5% | 95% | 100% | -147.5973 | 540.5314 | -2750 | -200 | -2409.4686 | 60.24% | 100.5% | 95% | 100% | 1793 | -129
[5 empty] | 2019-01-07 | 11 | 149.5 | 1710 | -135 | 0 | 0 | 1845 | 769.5796 | 769.5796 | 769.5796 | 3199.0107 | 780 | 200 | 4179.0107 | 104.5% | 95% | 100% | -154.4622 | 615.1173 | -2750 | -200 | -2334.8827 | 58.37% | 100.5% | 95% | 100% | 1845 | -135
[5 empty] | 2019-01-07 | 12 | 150 | 1794 | -142 | 0 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 3199.0107 | 780 | 200 | 4179.0107 | 104.5% | 95% | 100% | -162.4714 | 749.6473 | -2750 | -200 | -2200.3527 | 55.01% | 100.5% | 95% | 100% | 1936 | -142
[5 empty] | 2019-01-07 | 13 | 150.5 | 2050 | -150 | 0 | 0 | 2200 | 1325.6389 | 1325.6389 | 1325.6389 | 3197.4444 | 780 | 200 | 4177.4444 | 104.4% | 95% | 100% | -171.6247 | 1154.0142 | -2750 | -200 | -1795.9858 | 44.9% | 100.5% | 95% | 100% | 2200 | -150
[5 empty] | 2019-01-07 | 14 | 151 | 2285 | -157 | 0 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 3195.878 | 780 | 200 | 4175.878 | 104.4% | 95% | 100% | -179.6339 | 1525.0652 | -2750 | -200 | -1424.9348 | 35.62% | 100.4% | 95% | 100% | 2442 | -157
[5 empty] | 2019-01-07 | 15 | 151.5 | 2538 | -164 | 0 | 0 | 2702 | 2111.9538 | 2111.9538 | 2111.9538 | 3195.878 | 780 | 200 | 4175.878 | 104.4% | 95% | 100% | -187.643 | 1924.3108 | -2750 | -200 | -1025.6892 | 25.64% | 100.4% | 95% | 100% | 2702 | -164
[5 empty] | 2019-01-07 | 16 | 152 | 2679 | -171 | 0 | 0 | 2850 | 2343.7758 | 2343.7758 | 2343.7758 | 3195.878 | 780 | 200 | 4175.878 | 104.4% | 95% | 100% | -195.6522 | 2148.1236 | -2750 | -200 | -801.8764 | 20.05% | 100.4% | 95% | 100% | 2850 | -171
[5 empty] | 2019-01-07 | 17 | 152.5 | 2766 | -177 | 0 | 0 | 2943 | 2489.4477 | 2489.4477 | 2489.4477 | 3195.878 | 780 | 200 | 4175.878 | 104.4% | 95% | 100% | -202.5172 | 2286.9305 | -2750 | -200 | -663.0695 | 16.58% | 100.4% | 95% | 100% | 2943 | -177
[5 empty] | 2019-01-07 | 18 | 153 | 2788 | -185 | 0 | 0 | 2973 | 2536.4386 | 2536.4386 | 2536.4386 | 3195.878 | 780 | 200 | 4175.878 | 104.4% | 95% | 100% | -211.6705 | 2324.7681 | -2750 | -200 | -625.2319 | 15.63% | 100.4% | 95% | 100% | 2973 | -185
[5 empty] | 2019-01-07 | 19 | 153.5 | 2826 | -195 | 0 | 0 | 3021 | 2611.6241 | 2611.6241 | 2611.6241 | 3195.878 | 780 | 200 | 4175.878 | 104.4% | 95% | 100% | -223.1121 | 2388.5119 | -2750 | -200 | -561.4881 | 14.04% | 100.3% | 95% | 100% | 3021 | -195
[5 empty] | 2019-01-07 | 20 | 154 | 2820 | -218 | 1 | 0 | 3038 | 2638.2523 | 2638.2523 | 2638.2523 | 3194.3116 | 780 | 200 | 4174.3116 | 104.4% | 95% | 100% | -249.4279 | 2388.8243 | -3550 | -400 | -1561.1757 | 39.03% | 100.3% | 95% | 100% | 3038 | -218
[5 empty] | 2019-01-07 | 21 | 154.5 | 2783 | -238 | 1 | 0 | 3021 | 2611.6241 | 2611.6241 | 2611.6241 | 3194.3116 | 780 | 200 | 4174.3116 | 104.4% | 95% | 100% | -272.3112 | 2339.3129 | -3550 | -400 | -1610.6871 | 40.27% | 100.3% | 95% | 100% | 3021 | -238
[5 empty] | 2019-01-07 | 22 | 155 | 2769 | -253 | 1 | 0 | 3022 | 2613.1904 | 2613.1904 | 2613.1904 | 3194.3116 | 780 | 200 | 4174.3116 | 104.4% | 95% | 100% | -289.4737 | 2323.7168 | -3550 | -400 | -1626.2832 | 40.66% | 100.3% | 95% | 100% | 3022 | -253
[5 empty] | 2019-01-07 | 23 | 155.5 | 2752 | -268 | 1 | 0 | 3020 | 2610.0577 | 2610.0577 | 2610.0577 | 3191.1789 | 780 | 200 | 4171.1789 | 104.3% | 95% | 100% | -306.6362 | 2303.4216 | -3550 | -400 | -1646.5784 | 41.16% | 100.3% | 95% | 100% | 3020 | -268
[5 empty] | 2019-01-07 | 24 | 156 | 2733 | -275 | 1 | 0 | 3008 | 2591.2613 | 2591.2613 | 2591.2613 | 3191.1789 | 780 | 200 | 4171.1789 | 104.3% | 95% | 100% | -314.6453 | 2276.616 | -3550 | -400 | -1673.384 | 41.83% | 100.3% | 95% | 100% | 3008 | -275
[5 empty] | 2019-01-07 | 25 | 156.5 | 2747 | -269 | 1 | 0 | 3016 | 2603.7923 | 2603.7923 | 2603.7923 | 3189.6125 | 780 | 200 | 4169.6125 | 104.2% | 95% | 100% | -307.7803 | 2296.0119 | -3550 | -400 | -1653.9881 | 41.35% | 100.3% | 95% | 100% | 3016 | -269
[5 empty] | 2019-01-07 | 26 | 157 | 2752 | -261 | 1 | 0 | 3013 | 2599.0932 | 2599.0932 | 2599.0932 | 3189.6125 | 780 | 200 | 4169.6125 | 104.2% | 95% | 100% | -298.627 | 2300.4662 | -3550 | -400 | -1649.5338 | 41.24% | 100.3% | 95% | 100% | 3013 | -261
[5 empty] | 2019-01-07 | 27 | 157.5 | 2762 | -253 | 1 | 0 | 3015 | 2602.2259 | 2602.2259 | 2602.2259 | 3189.6125 | 780 | 200 | 4169.6125 | 104.2% | 95% | 100% | -289.4737 | 2312.7522 | -3550 | -400 | -1637.2478 | 40.93% | 100.2% | 95% | 100% | 3015 | -253
[5 empty] | 2019-01-07 | 28 | 158 | 2764 | -246 | 1 | 0 | 3010 | 2594.3941 | 2594.3941 | 2594.3941 | 3188.0462 | 780 | 200 | 4168.0462 | 104.2% | 95% | 100% | -281.4645 | 2312.9295 | -3550 | -400 | -1637.0705 | 40.93% | 100.2% | 95% | 100% | 3010 | -246
[5 empty] | 2019-01-07 | 29 | 158.5 | 2782 | -230 | 1 | 0 | 3012 | 2597.5268 | 2597.5268 | 2597.5268 | 3188.0462 | 780 | 200 | 4168.0462 | 104.2% | 95% | 100% | -263.1579 | 2334.3689 | -3550 | -400 | -1615.6311 | 40.39% | 100.1% | 95% | 100% | 3012 | -230
[5 empty] | 2019-01-07 | 30 | 159 | 2772 | -215 | 1 | 0 | 2987 | 2558.3677 | 2558.3677 | 2558.3677 | 3186.4798 | 780 | 200 | 4166.4798 | 104.2% | 95% | 100% | -245.9954 | 2312.3723 | -3550 | -400 | -1637.6277 | 40.94% | 100.1% | 95% | 100% | 2987 | -215
[5 empty] | 2019-01-07 | 31 | 159.5 | 2798 | -203 | 1 | 0 | 3001 | 2580.2968 | 2580.2968 | 2580.2968 | 3186.4798 | 780 | 200 | 4166.4798 | 104.2% | 95% | 100% | -232.2654 | 2348.0313 | -3550 | -400 | -1601.9687 | 40.05% | 100.1% | 95% | 100% | 3001 | -203
[5 empty] | 2019-01-07 | 32 | 160 | 2877 | -195 | 1 | 0 | 3072 | 2691.5087 | 2691.5087 | 2691.5087 | 3184.9134 | 780 | 200 | 4164.9134 | 104.1% | 95% | 100% | -223.1121 | 2468.3965 | -3550 | -400 | -1481.6035 | 37.04% | 100.1% | 95% | 100% | 3072 | -195
[5 empty] | 2019-01-07 | 33 | 160.5 | 2994 | -195 | 1 | 0 | 3189 | 2874.7733 | 2874.7733 | 2874.7733 | 3183.3471 | 780 | 200 | 4163.3471 | 104.1% | 95% | 100% | -223.1121 | 2651.6612 | -3550 | -400 | -1298.3388 | 32.46% | 100.1% | 95% | 100% | 3189 | -195
[5 empty] | 2019-01-07 | 34 | 161 | 3105 | -195 | 0 | 0 | 3300 | 3048.6397 | 3048.6397 | 3048.6397 | 3181.7807 | 780 | 200 | 4161.7807 | 104% | 95% | 100% | -223.1121 | 2825.5276 | -2750 | -200 | -124.4724 | 3.112% | 100.1% | 95% | 100% | 3300 | -195
[5 empty] | 2019-01-07 | 35 | 161.5 | 3135 | -193 | 0 | 0 | 3328 | 3092.4979 | 3092.4979 | 3092.4979 | 3180.2143 | 780 | 200 | 4160.2143 | 104% | 95% | 100% | -220.8238 | 2871.6741 | -2750 | -200 | -78.3259 | 1.958% | 100.1% | 95% | 100% | 3328 | -193
[5 empty] | 2019-01-07 | 36 | 162 | 3119 | -190 | 0 | 0 | 3309 | 3062.737 | 3062.737 | 3062.737 | 3180.2143 | 780 | 200 | 4160.2143 | 104% | 95% | 100% | -217.3913 | 2845.3457 | -2750 | -200 | -104.6543 | 2.616% | 100.1% | 95% | 100% | 3309 | -190
[5 empty] | 2019-01-07 | 37 | 162.5 | 3082 | -190 | 0 | 0 | 3272 | 3004.7815 | 3004.7815 | 3004.7815 | 3180.2143 | 780 | 200 | 4160.2143 | 104% | 95% | 100% | -217.3913 | 2787.3902 | -2750 | -200 | -162.6098 | 4.065% | 100% | 95% | 100% | 3272 | -190
[5 empty] | 2019-01-07 | 38 | 163 | 3029 | -189 | 0 | 0 | 3218 | 2920.1979 | 2920.1979 | 2920.1979 | 3180.2143 | 780 | 200 | 4160.2143 | 104% | 95% | 100% | -216.2471 | 2703.9507 | -2750 | -200 | -246.0493 | 6.151% | 99.98% | 95% | 100% | 3218 | -189
[5 empty] | 2019-01-07 | 39 | 163.5 | 2953 | -189 | 0 | 0 | 3142 | 2801.1542 | 2801.1542 | 2801.1542 | 3180.2143 | 780 | 200 | 4160.2143 | 104% | 95% | 100% | -216.2471 | 2584.907 | -2750 | -200 | -365.093 | 9.127% | 99.95% | 95% | 100% | 3142 | -189
[5 empty] | 2019-01-07 | 40 | 164 | 2854 | -190 | 0 | 0 | 3044 | 2647.6505 | 2647.6505 | 2647.6505 | 3178.648 | 780 | 200 | 4158.648 | 104% | 95% | 100% | -217.3913 | 2430.2591 | -2750 | -200 | -519.7409 | 12.99% | 99.95% | 95% | 100% | 3044 | -190
[5 empty] | 2019-01-07 | 41 | 164.5 | 2746 | -191 | 0 | 0 | 2937 | 2480.0495 | 2480.0495 | 2480.0495 | 3178.648 | 780 | 200 | 4158.648 | 104% | 95% | 100% | -218.5355 | 2261.514 | -2750 | -200 | -688.486 | 17.21% | 99.92% | 95% | 100% | 2937 | -191
[5 empty] | 2019-01-07 | 42 | 165 | 2610 | -193 | 0 | 0 | 2803 | 2270.1566 | 2270.1566 | 2270.1566 | 3178.648 | 780 | 200 | 4158.648 | 104% | 95% | 100% | -220.8238 | 2049.3328 | -2750 | -200 | -900.6672 | 22.52% | 99.92% | 95% | 100% | 2803 | -193
[5 empty] | 2019-01-07 | 43 | 165.5 | 2450 | -193 | 0 | 0 | 2643 | 2019.5383 | 2019.5383 | 2019.5383 | 3177.0816 | 780 | 200 | 4157.0816 | 103.9% | 95% | 100% | -220.8238 | 1798.7145 | -2750 | -200 | -1151.2855 | 28.78% | 99.91% | 95% | 100% | 2643 | -193
[5 empty] | 2019-01-07 | 44 | 166 | 2293 | -193 | 0 | 0 | 2486 | 1773.6191 | 1773.6191 | 1773.6191 | 3177.0816 | 780 | 200 | 4157.0816 | 103.9% | 95% | 100% | -220.8238 | 1552.7953 | -2750 | -200 | -1397.2047 | 34.93% | 99.91% | 95% | 100% | 2486 | -193
[5 empty] | 2019-01-07 | 45 | 166.5 | 2126 | -191 | 0 | 0 | 2317 | 1508.9035 | 1508.9035 | 1508.9035 | 3177.0816 | 780 | 200 | 4157.0816 | 103.9% | 95% | 100% | -218.5355 | 1290.3681 | -2750 | -200 | -1659.6319 | 41.49% | 99.91% | 95% | 100% | 2317 | -191
[5 empty] | 2019-01-07 | 46 | 167 | 1979 | -190 | 0 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 3177.0816 | 780 | 200 | 4157.0816 | 103.9% | 95% | 100% | -217.3913 | 1059.6903 | -2750 | -200 | -1890.3097 | 47.26% | 99.91% | 95% | 100% | 2169 | -190
[5 empty] | 2019-01-07 | 47 | 167.5 | 1825 | -192 | 0 | 0 | 2017 | 1038.9942 | 1038.9942 | 1038.9942 | 3175.5153 | 780 | 200 | 4155.5153 | 103.9% | 95% | 100% | -219.6796 | 819.3146 | -2750 | -200 | -2130.6854 | 53.27% | 99.9% | 95% | 100% | 2017 | -192
[5 empty] | 2019-01-07 | 48 | 168 | 1729 | -194 | 0 | 0 | 1923 | 891.756 | 891.756 | 891.756 | 3175.5153 | 780 | 200 | 4155.5153 | 103.9% | 95% | 100% | -221.968 | 669.788 | -2750 | -200 | -2280.212 | 57.01% | 99.89% | 95% | 100% | 1923 | -194
[5 empty] | 2019-01-08 | 1 | 168.5 | 1707 | -195 | 0 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 3175.5153 | 780 | 200 | 4155.5153 | 103.9% | 95% | 100% | -223.1121 | 635.7502 | -2750 | -200 | -2314.2498 | 57.86% | 99.86% | 95% | 100% | 1902 | -195
[5 empty] | 2019-01-08 | 2 | 169 | 1743 | -196 | 0 | 0 | 1939 | 916.8178 | 916.8178 | 916.8178 | 3173.9489 | 780 | 200 | 4153.9489 | 103.8% | 95% | 100% | -224.2563 | 692.5615 | -2750 | -200 | -2257.4385 | 56.44% | 99.85% | 95% | 100% | 1939 | -196
[5 empty] | 2019-01-08 | 3 | 169.5 | 1726 | -196 | 0 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 3173.9489 | 780 | 200 | 4153.9489 | 103.8% | 95% | 100% | -224.2563 | 665.9333 | -2750 | -200 | -2284.0667 | 57.1% | 99.84% | 95% | 100% | 1922 | -196
[5 empty] | 2019-01-08 | 4 | 170 | 1676 | -196 | 0 | 0 | 1872 | 811.8714 | 811.8714 | 811.8714 | 3173.9489 | 780 | 200 | 4153.9489 | 103.8% | 95% | 100% | -224.2563 | 587.6151 | -2750 | -200 | -2362.3849 | 59.06% | 99.8% | 95% | 100% | 1872 | -196
[5 empty] | 2019-01-08 | 5 | 170.5 | 1646 | -195 | 0 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 3172.3825 | 780 | 200 | 4152.3825 | 103.8% | 95% | 100% | -223.1121 | 540.202 | -2750 | -200 | -2409.798 | 60.24% | 99.8% | 95% | 100% | 1841 | -195
[5 empty] | 2019-01-08 | 6 | 171 | 1629 | -195 | 0 | 0 | 1824 | 736.6859 | 736.6859 | 736.6859 | 3172.3825 | 780 | 200 | 4152.3825 | 103.8% | 95% | 100% | -223.1121 | 513.5738 | -2750 | -200 | -2436.4262 | 60.91% | 99.76% | 95% | 100% | 1824 | -195
[5 empty] | 2019-01-08 | 7 | 171.5 | 1600 | -191 | 0 | 0 | 1791 | 684.9959 | 684.9959 | 684.9959 | 3170.8162 | 780 | 200 | 4150.8162 | 103.8% | 95% | 100% | -218.5355 | 466.4604 | -2750 | -200 | -2483.5396 | 62.09% | 99.76% | 95% | 100% | 1791 | -191
[5 empty] | 2019-01-08 | 8 | 172 | 1586 | -188 | 0 | 0 | 1774 | 658.3677 | 658.3677 | 658.3677 | 3170.8162 | 780 | 200 | 4150.8162 | 103.8% | 95% | 100% | -215.103 | 443.2647 | -2750 | -200 | -2506.7353 | 62.67% | 99.74% | 95% | 100% | 1774 | -188
[5 empty] | 2019-01-08 | 9 | 172.5 | 1575 | -185 | 0 | 0 | 1760 | 636.4386 | 636.4386 | 636.4386 | 3170.8162 | 780 | 200 | 4150.8162 | 103.8% | 95% | 100% | -211.6705 | 424.7681 | -2750 | -200 | -2525.2319 | 63.13% | 99.74% | 95% | 100% | 1760 | -185
[5 empty] | 2019-01-08 | 10 | 173 | 1590 | -182 | 0 | 0 | 1772 | 655.235 | 655.235 | 655.235 | 3170.8162 | 780 | 200 | 4150.8162 | 103.8% | 95% | 100% | -208.238 | 446.997 | -2750 | -200 | -2503.003 | 62.58% | 99.72% | 95% | 100% | 1772 | -182
[5 empty] | 2019-01-08 | 11 | 173.5 | 1662 | -178 | 0 | 0 | 1840 | 761.7477 | 761.7477 | 761.7477 | 3169.2498 | 780 | 200 | 4149.2498 | 103.7% | 95% | 100% | -203.6613 | 558.0864 | -2750 | -200 | -2391.9136 | 59.8% | 99.71% | 95% | 100% | 1840 | -178
[5 empty] | 2019-01-08 | 12 | 174 | 1768 | -174 | 0 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 3169.2498 | 780 | 200 | 4149.2498 | 103.7% | 95% | 100% | -199.0847 | 722.4322 | -2750 | -200 | -2227.5678 | 55.69% | 99.7% | 95% | 100% | 1942 | -174
[5 empty] | 2019-01-08 | 13 | 174.5 | 2039 | -172 | 0 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 3169.2498 | 780 | 200 | 4149.2498 | 103.7% | 95% | 100% | -196.7963 | 1146.0726 | -2750 | -200 | -1803.9274 | 45.1% | 99.65% | 95% | 100% | 2211 | -172
[5 empty] | 2019-01-08 | 14 | 175 | 2296 | -169 | 0 | 0 | 2465 | 1740.7255 | 1740.7255 | 1740.7255 | 3167.6834 | 780 | 200 | 4147.6834 | 103.7% | 95% | 100% | -193.3638 | 1547.3616 | -2750 | -200 | -1402.6384 | 35.07% | 99.59% | 95% | 100% | 2465 | -169
[5 empty] | 2019-01-08 | 15 | 175.5 | 2606 | -165 | 0 | 0 | 2771 | 2220.033 | 2220.033 | 2220.033 | 3167.6834 | 780 | 200 | 4147.6834 | 103.7% | 95% | 100% | -188.7872 | 2031.2458 | -2750 | -200 | -918.7542 | 22.97% | 99.59% | 95% | 100% | 2771 | -165
[5 empty] | 2019-01-08 | 16 | 176 | 2736 | -162 | 0 | 0 | 2898 | 2418.9613 | 2418.9613 | 2418.9613 | 3167.6834 | 780 | 200 | 4147.6834 | 103.7% | 95% | 100% | -185.3547 | 2233.6066 | -2750 | -200 | -716.3934 | 17.91% | 99.59% | 95% | 100% | 2898 | -162
[5 empty] | 2019-01-08 | 17 | 176.5 | 2789 | -160 | 0 | 0 | 2949 | 2498.8458 | 2498.8458 | 2498.8458 | 3167.6834 | 780 | 200 | 4147.6834 | 103.7% | 95% | 100% | -183.0664 | 2315.7795 | -2750 | -200 | -634.2205 | 15.86% | 99.57% | 95% | 100% | 2949 | -160
[5 empty] | 2019-01-08 | 18 | 177 | 2790 | -171 | 0 | 0 | 2961 | 2517.6422 | 2517.6422 | 2517.6422 | 3166.1171 | 780 | 200 | 4146.1171 | 103.7% | 95% | 100% | -195.6522 | 2321.99 | -2750 | -200 | -628.01 | 15.7% | 99.56% | 95% | 100% | 2961 | -171
[5 empty] | 2019-01-08 | 19 | 177.5 | 2789 | -207 | 0 | 0 | 2996 | 2572.465 | 2572.465 | 2572.465 | 3166.1171 | 780 | 200 | 4146.1171 | 103.7% | 95% | 100% | -236.8421 | 2335.6229 | -2750 | -200 | -614.3771 | 15.36% | 99.56% | 95% | 100% | 2996 | -207
[5 empty] | 2019-01-08 | 20 | 178 | 2720 | -262 | 0 | 0 | 2982 | 2550.5359 | 2550.5359 | 2550.5359 | 3166.1171 | 780 | 200 | 4146.1171 | 103.7% | 95% | 100% | -299.7712 | 2250.7647 | -2750 | -200 | -699.2353 | 17.48% | 99.55% | 95% | 100% | 2982 | -262
[5 empty] | 2019-01-08 | 21 | 178.5 | 2642 | -323 | 1 | 0 | 2965 | 2523.9077 | 2523.9077 | 2523.9077 | 3166.1171 | 780 | 200 | 4146.1171 | 103.7% | 95% | 100% | -369.5652 | 2154.3424 | -3550 | -400 | -1795.6576 | 44.89% | 99.55% | 95% | 100% | 2965 | -323
[5 empty] | 2019-01-08 | 22 | 179 | 2577 | -368 | 1 | 0 | 2945 | 2492.5804 | 2492.5804 | 2492.5804 | 3164.5507 | 780 | 200 | 4144.5507 | 103.6% | 95% | 100% | -421.0526 | 2071.5277 | -3550 | -400 | -1878.4723 | 46.96% | 99.53% | 95% | 100% | 2945 | -368
[5 empty] | 2019-01-08 | 23 | 179.5 | 2506 | -402 | 1 | 0 | 2908 | 2434.6249 | 2434.6249 | 2434.6249 | 3164.5507 | 780 | 200 | 4144.5507 | 103.6% | 95% | 100% | -459.9542 | 1974.6707 | -3550 | -400 | -1975.3293 | 49.38% | 99.51% | 95% | 100% | 2908 | -402
[5 empty] | 2019-01-08 | 24 | 180 | 2455 | -422 | 1 | 0 | 2877 | 2386.0676 | 2386.0676 | 2386.0676 | 3164.5507 | 780 | 200 | 4144.5507 | 103.6% | 95% | 100% | -482.8375 | 1903.2301 | -3550 | -400 | -2046.7699 | 51.17% | 99.51% | 95% | 100% | 2877 | -422
[5 empty] | 2019-01-08 | 25 | 180.5 | 2432 | -429 | 1 | 0 | 2861 | 2361.0058 | 2361.0058 | 2361.0058 | 3164.5507 | 780 | 200 | 4144.5507 | 103.6% | 95% | 100% | -490.8467 | 1870.1591 | -3550 | -400 | -2079.8409 | 52% | 99.51% | 95% | 100% | 2861 | -429
[5 empty] | 2019-01-08 | 26 | 181 | 2416 | -419 | 1 | 0 | 2835 | 2320.2803 | 2320.2803 | 2320.2803 | 3162.9843 | 780 | 200 | 4142.9843 | 103.6% | 95% | 100% | -479.405 | 1840.8753 | -3550 | -400 | -2109.1247 | 52.73% | 99.51% | 95% | 100% | 2835 | -419
[5 empty] | 2019-01-08 | 27 | 181.5 | 2455 | -392 | 1 | 0 | 2847 | 2339.0767 | 2339.0767 | 2339.0767 | 3161.418 | 780 | 200 | 4141.418 | 103.5% | 95% | 100% | -448.5126 | 1890.5641 | -3550 | -400 | -2059.4359 | 51.49% | 99.5% | 95% | 100% | 2847 | -392
[5 empty] | 2019-01-08 | 28 | 182 | 2503 | -353 | 1 | 0 | 2856 | 2353.1739 | 2353.1739 | 2353.1739 | 3161.418 | 780 | 200 | 4141.418 | 103.5% | 95% | 100% | -403.8902 | 1949.2838 | -3550 | -400 | -2000.7162 | 50.02% | 99.49% | 95% | 100% | 2856 | -353
[5 empty] | 2019-01-08 | 29 | 182.5 | 2602 | -304 | 1 | 0 | 2906 | 2431.4922 | 2431.4922 | 2431.4922 | 3161.418 | 780 | 200 | 4141.418 | 103.5% | 95% | 100% | -347.8261 | 2083.6661 | -3550 | -400 | -1866.3339 | 46.66% | 99.47% | 95% | 100% | 2906 | -304
[5 empty] | 2019-01-08 | 30 | 183 | 2696 | -248 | 1 | 0 | 2944 | 2491.014 | 2491.014 | 2491.014 | 3159.8516 | 780 | 200 | 4139.8516 | 103.5% | 95% | 100% | -283.7529 | 2207.2612 | -3550 | -400 | -1742.7388 | 43.57% | 99.46% | 95% | 100% | 2944 | -248
[5 empty] | 2019-01-08 | 31 | 183.5 | 2806 | -194 | 1 | 0 | 3000 | 2578.7304 | 2578.7304 | 2578.7304 | 3158.2852 | 780 | 200 | 4138.2852 | 103.5% | 95% | 100% | -221.968 | 2356.7625 | -3550 | -400 | -1593.2375 | 39.83% | 99.45% | 95% | 100% | 3000 | -194
[5 empty] | 2019-01-08 | 32 | 184 | 2947 | -153 | 1 | 0 | 3100 | 2735.3669 | 2735.3669 | 2735.3669 | 3158.2852 | 780 | 200 | 4138.2852 | 103.5% | 95% | 100% | -175.0572 | 2560.3097 | -3550 | -400 | -1389.6903 | 34.74% | 99.44% | 95% | 100% | 3100 | -153
[5 empty] | 2019-01-08 | 33 | 184.5 | 3107 | -138 | 1 | 0 | 3245 | 2962.4897 | 2962.4897 | 2962.4897 | 3158.2852 | 780 | 200 | 4138.2852 | 103.5% | 95% | 100% | -157.8947 | 2804.595 | -3550 | -400 | -1145.405 | 28.64% | 99.42% | 95% | 100% | 3245 | -138
[5 empty] | 2019-01-08 | 34 | 185 | 3291 | -136 | 1 | 0 | 3427 | 3247.568 | 3247.568 | 3247.568 | 3156.7189 | 780 | 200 | 4136.7189 | 103.4% | 95% | 100% | -155.6064 | 3091.9616 | -3550 | -400 | -858.0384 | 21.45% | 99.4% | 95% | 100% | 3427 | -136
[5 empty] | 2019-01-08 | 35 | 185.5 | 3344 | -135 | 0 | 0 | 3479 | 3329.019 | 3329.019 | 3329.019 | 3156.7189 | 780 | 200 | 4136.7189 | 103.4% | 95% | 100% | -154.4622 | 3174.5567 | -2750 | -200 | 224.5567 | -5.614% | 99.39% | 95% | 100% | 3479 | -135
[5 empty] | 2019-01-08 | 36 | 186 | 3340 | -134 | 0 | 0 | 3474 | 3321.1871 | 3321.1871 | 3321.1871 | 3155.1525 | 780 | 200 | 4135.1525 | 103.4% | 95% | 100% | -153.3181 | 3167.8691 | -2750 | -200 | 217.8691 | -5.447% | 99.37% | 95% | 100% | 3474 | -134
[5 empty] | 2019-01-08 | 37 | 186.5 | 3309 | -133 | 0 | 0 | 3442 | 3271.0635 | 3271.0635 | 3271.0635 | 3153.5862 | 780 | 200 | 4133.5862 | 103.3% | 95% | 100% | -152.1739 | 3118.8896 | -2750 | -200 | 168.8896 | -4.222% | 99.37% | 95% | 100% | 3442 | -133
[5 empty] | 2019-01-08 | 38 | 187 | 3286 | -131 | 0 | 0 | 3417 | 3231.9044 | 3231.9044 | 3231.9044 | 3153.5862 | 780 | 200 | 4133.5862 | 103.3% | 95% | 100% | -149.8856 | 3082.0188 | -2750 | -200 | 132.0188 | -3.3% | 99.36% | 95% | 100% | 3417 | -131
[5 empty] | 2019-01-08 | 39 | 187.5 | 3230 | -129 | 0 | 0 | 3359 | 3141.0552 | 3141.0552 | 3141.0552 | 3153.5862 | 780 | 200 | 4133.5862 | 103.3% | 95% | 100% | -147.5973 | 2993.458 | -2750 | -200 | 43.458 | -1.086% | 99.36% | 95% | 100% | 3359 | -129
[5 empty] | 2019-01-08 | 40 | 188 | 3122 | -126 | 0 | 0 | 3248 | 2967.1888 | 2967.1888 | 2967.1888 | 3153.5862 | 780 | 200 | 4133.5862 | 103.3% | 95% | 100% | -144.1648 | 2823.024 | -2750 | -200 | -126.976 | 3.174% | 99.35% | 95% | 100% | 3248 | -126
[5 empty] | 2019-01-08 | 41 | 188.5 | 3060 | -124 | 0 | 0 | 3184 | 2866.9415 | 2866.9415 | 2866.9415 | 3153.5862 | 780 | 200 | 4133.5862 | 103.3% | 95% | 100% | -141.8764 | 2725.065 | -2750 | -200 | -224.935 | 5.623% | 99.33% | 95% | 100% | 3184 | -124
[5 empty] | 2019-01-08 | 42 | 189 | 2944 | -122 | 0 | 0 | 3066 | 2682.1105 | 2682.1105 | 2682.1105 | 3152.0198 | 780 | 200 | 4132.0198 | 103.3% | 95% | 100% | -139.5881 | 2542.5224 | -2750 | -200 | -407.4776 | 10.19% | 99.33% | 95% | 100% | 3066 | -122
[5 empty] | 2019-01-08 | 43 | 189.5 | 2787 | -121 | 0 | 0 | 2908 | 2434.6249 | 2434.6249 | 2434.6249 | 3152.0198 | 780 | 200 | 4132.0198 | 103.3% | 95% | 100% | -138.4439 | 2296.181 | -2750 | -200 | -653.819 | 16.35% | 99.27% | 95% | 100% | 2908 | -121
[5 empty] | 2019-01-08 | 44 | 190 | 2608 | -120 | 0 | 0 | 2728 | 2152.6793 | 2152.6793 | 2152.6793 | 3150.4534 | 780 | 200 | 4130.4534 | 103.3% | 95% | 100% | -137.2998 | 2015.3795 | -2750 | -200 | -934.6205 | 23.37% | 99.26% | 95% | 100% | 2728 | -120
[5 empty] | 2019-01-08 | 45 | 190.5 | 2459 | -118 | 0 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 3150.4534 | 780 | 200 | 4130.4534 | 103.3% | 95% | 100% | -135.0114 | 1781.1468 | -2750 | -200 | -1168.8532 | 29.22% | 99.21% | 95% | 100% | 2577 | -118
[5 empty] | 2019-01-08 | 46 | 191 | 2298 | -117 | 0 | 0 | 2415 | 1662.4073 | 1662.4073 | 1662.4073 | 3150.4534 | 780 | 200 | 4130.4534 | 103.3% | 95% | 100% | -133.8673 | 1528.54 | -2750 | -200 | -1421.46 | 35.54% | 99.2% | 95% | 100% | 2415 | -117
[5 empty] | 2019-01-08 | 47 | 191.5 | 2148 | -111 | 0 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 3148.8871 | 780 | 200 | 4128.8871 | 103.2% | 95% | 100% | -127.0023 | 1291.0521 | -2750 | -200 | -1658.9479 | 41.47% | 99.2% | 95% | 100% | 2259 | -111
[5 empty] | 2019-01-08 | 48 | 192 | 2059 | -105 | 0 | 0 | 2164 | 1269.2498 | 1269.2498 | 1269.2498 | 3147.3207 | 780 | 200 | 4127.3207 | 103.2% | 95% | 100% | -120.1373 | 1149.1125 | -2750 | -200 | -1800.8875 | 45.02% | 99.19% | 95% | 100% | 2164 | -105
[5 empty] | 2019-01-09 | 1 | 192.5 | 2028 | -104 | 0 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 3147.3207 | 780 | 200 | 4127.3207 | 103.2% | 95% | 100% | -118.9931 | 1100.133 | -2750 | -200 | -1849.867 | 46.25% | 99.17% | 95% | 100% | 2132 | -104
[5 empty] | 2019-01-09 | 2 | 193 | 2063 | -103 | 0 | 0 | 2166 | 1272.3825 | 1272.3825 | 1272.3825 | 3145.7543 | 780 | 200 | 4125.7543 | 103.1% | 95% | 100% | -117.849 | 1154.5336 | -2750 | -200 | -1795.4664 | 44.89% | 99.17% | 95% | 100% | 2166 | -103
[5 empty] | 2019-01-09 | 3 | 193.5 | 2037 | -101 | 0 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 3145.7543 | 780 | 200 | 4125.7543 | 103.1% | 95% | 100% | -115.5606 | 1112.9637 | -2750 | -200 | -1837.0363 | 45.93% | 99.16% | 95% | 100% | 2138 | -101
[5 empty] | 2019-01-09 | 4 | 194 | 1991 | -99 | 0 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 3145.7543 | 780 | 200 | 4125.7543 | 103.1% | 95% | 100% | -113.2723 | 1040.0665 | -2750 | -200 | -1909.9335 | 47.75% | 99.15% | 95% | 100% | 2090 | -99
[5 empty] | 2019-01-09 | 5 | 194.5 | 1951 | -99 | 0 | 0 | 2050 | 1090.6843 | 1090.6843 | 1090.6843 | 3145.7543 | 780 | 200 | 4125.7543 | 103.1% | 95% | 100% | -113.2723 | 977.4119 | -2750 | -200 | -1972.5881 | 49.31% | 99.11% | 95% | 100% | 2050 | -99
[5 empty] | 2019-01-09 | 6 | 195 | 1955 | -99 | 0 | 0 | 2054 | 1096.9497 | 1096.9497 | 1096.9497 | 3145.7543 | 780 | 200 | 4125.7543 | 103.1% | 95% | 100% | -113.2723 | 983.6774 | -2750 | -200 | -1966.3226 | 49.16% | 99.08% | 95% | 100% | 2054 | -99
[5 empty] | 2019-01-09 | 7 | 195.5 | 1922 | -95 | 0 | 0 | 2017 | 1038.9942 | 1038.9942 | 1038.9942 | 3145.7543 | 780 | 200 | 4125.7543 | 103.1% | 95% | 100% | -108.6957 | 930.2986 | -2750 | -200 | -2019.7014 | 50.49% | 99.08% | 95% | 100% | 2017 | -95
[5 empty] | 2019-01-09 | 8 | 196 | 1890 | -91 | 0 | 0 | 1981 | 982.6051 | 982.6051 | 982.6051 | 3144.188 | 780 | 200 | 4124.188 | 103.1% | 95% | 100% | -104.119 | 878.4861 | -2750 | -200 | -2071.5139 | 51.79% | 99.08% | 95% | 100% | 1981 | -91
[5 empty] | 2019-01-09 | 9 | 196.5 | 1880 | -89 | 0 | 0 | 1969 | 963.8087 | 963.8087 | 963.8087 | 3142.6216 | 780 | 200 | 4122.6216 | 103.1% | 95% | 100% | -101.8307 | 861.9781 | -2750 | -200 | -2088.0219 | 52.2% | 99.06% | 95% | 100% | 1969 | -89
[5 empty] | 2019-01-09 | 10 | 197 | 1905 | -86 | 0 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 3141.0552 | 780 | 200 | 4121.0552 | 103% | 95% | 100% | -98.3982 | 899.8706 | -2750 | -200 | -2050.1294 | 51.25% | 99.05% | 95% | 100% | 1991 | -86
[5 empty] | 2019-01-09 | 11 | 197.5 | 1976 | -84 | 0 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 3141.0552 | 780 | 200 | 4121.0552 | 103% | 95% | 100% | -96.1098 | 1010.2381 | -2750 | -200 | -1939.7619 | 48.49% | 99% | 95% | 100% | 2060 | -84
[5 empty] | 2019-01-09 | 12 | 198 | 2096 | -82 | 0 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 3141.0552 | 780 | 200 | 4121.0552 | 103% | 95% | 100% | -93.8215 | 1197.3574 | -2750 | -200 | -1752.6426 | 43.82% | 98.98% | 95% | 100% | 2178 | -82
[5 empty] | 2019-01-09 | 13 | 198.5 | 2360 | -79 | 0 | 0 | 2439 | 1700 | 1700 | 1700 | 3137.9225 | 780 | 200 | 4117.9225 | 102.9% | 95% | 100% | -90.389 | 1609.611 | -2750 | -200 | -1340.389 | 33.51% | 98.97% | 95% | 100% | 2439 | -79
[5 empty] | 2019-01-09 | 14 | 199 | 2628 | -77 | 0 | 0 | 2705 | 2116.6529 | 2116.6529 | 2116.6529 | 3137.9225 | 780 | 200 | 4117.9225 | 102.9% | 95% | 100% | -88.1007 | 2028.5522 | -2750 | -200 | -921.4478 | 23.04% | 98.95% | 95% | 100% | 2705 | -77
[5 empty] | 2019-01-09 | 15 | 199.5 | 2939 | -76 | 0 | 0 | 3015 | 2602.2259 | 2602.2259 | 2602.2259 | 3137.9225 | 780 | 200 | 4117.9225 | 102.9% | 95% | 100% | -86.9565 | 2515.2694 | -2750 | -200 | -434.7306 | 10.87% | 98.95% | 95% | 100% | 3015 | -76
[5 empty] | 2019-01-09 | 16 | 200 | 3101 | -75 | 0 | 0 | 3176 | 2854.4106 | 2854.4106 | 2854.4106 | 3137.9225 | 780 | 200 | 4117.9225 | 102.9% | 95% | 100% | -85.8124 | 2768.5982 | -2750 | -200 | -181.4018 | 4.535% | 98.93% | 95% | 100% | 3176 | -75
[5 empty] | 2019-01-09 | 17 | 200.5 | 3177 | -75 | 0 | 0 | 3252 | 2973.4542 | 2973.4542 | 2973.4542 | 3136.3561 | 780 | 200 | 4116.3561 | 102.9% | 95% | 100% | -85.8124 | 2887.6419 | -2750 | -200 | -62.3581 | 1.559% | 98.93% | 95% | 100% | 3252 | -75
[5 empty] | 2019-01-09 | 18 | 201 | 3159 | -94 | 0 | 0 | 3253 | 2975.0206 | 2975.0206 | 2975.0206 | 3136.3561 | 780 | 200 | 4116.3561 | 102.9% | 95% | 100% | -107.5515 | 2867.4691 | -2750 | -200 | -82.5309 | 2.063% | 98.92% | 95% | 100% | 3253 | -94
[5 empty] | 2019-01-09 | 19 | 201.5 | 3168 | -128 | 0 | 0 | 3296 | 3042.3743 | 3042.3743 | 3042.3743 | 3136.3561 | 780 | 200 | 4116.3561 | 102.9% | 95% | 100% | -146.4531 | 2895.9212 | -2750 | -200 | -54.0788 | 1.352% | 98.89% | 95% | 100% | 3296 | -128
[5 empty] | 2019-01-09 | 20 | 202 | 3098 | -191 | 1 | 0 | 3289 | 3031.4097 | 3031.4097 | 3031.4097 | 3136.3561 | 780 | 200 | 4116.3561 | 102.9% | 95% | 100% | -218.5355 | 2812.8743 | -3550 | -400 | -1137.1257 | 28.43% | 98.88% | 95% | 100% | 3289 | -191
[5 empty] | 2019-01-09 | 21 | 202.5 | 2984 | -247 | 1 | 0 | 3231 | 2940.5606 | 2940.5606 | 2940.5606 | 3134.7898 | 780 | 200 | 4114.7898 | 102.9% | 95% | 100% | -282.6087 | 2657.9519 | -3550 | -400 | -1292.0481 | 32.3% | 98.88% | 95% | 100% | 3231 | -247
[5 empty] | 2019-01-09 | 22 | 203 | 2893 | -293 | 1 | 0 | 3186 | 2870.0742 | 2870.0742 | 2870.0742 | 3134.7898 | 780 | 200 | 4114.7898 | 102.9% | 95% | 100% | -335.2403 | 2534.8339 | -3550 | -400 | -1415.1661 | 35.38% | 98.84% | 95% | 100% | 3186 | -293
[5 empty] | 2019-01-09 | 23 | 203.5 | 2844 | -316 | 1 | 0 | 3160 | 2829.3487 | 2829.3487 | 2829.3487 | 3134.7898 | 780 | 200 | 4114.7898 | 102.9% | 95% | 100% | -361.5561 | 2467.7927 | -3550 | -400 | -1482.2073 | 37.06% | 98.81% | 95% | 100% | 3160 | -316
[5 empty] | 2019-01-09 | 24 | 204 | 2785 | -354 | 1 | 0 | 3139 | 2796.4551 | 2796.4551 | 2796.4551 | 3134.7898 | 780 | 200 | 4114.7898 | 102.9% | 95% | 100% | -405.0343 | 2391.4207 | -3550 | -400 | -1558.5793 | 38.96% | 98.76% | 95% | 100% | 3139 | -354
[5 empty] | 2019-01-09 | 25 | 204.5 | 2806 | -330 | 1 | 0 | 3136 | 2791.756 | 2791.756 | 2791.756 | 3133.2234 | 780 | 200 | 4113.2234 | 102.8% | 95% | 100% | -377.5744 | 2414.1816 | -3550 | -400 | -1535.8184 | 38.4% | 98.73% | 95% | 100% | 3136 | -330
[5 empty] | 2019-01-09 | 26 | 205 | 2817 | -318 | 1 | 0 | 3135 | 2790.1896 | 2790.1896 | 2790.1896 | 3133.2234 | 780 | 200 | 4113.2234 | 102.8% | 95% | 100% | -363.8444 | 2426.3452 | -3550 | -400 | -1523.6548 | 38.09% | 98.73% | 95% | 100% | 3135 | -318
[5 empty] | 2019-01-09 | 27 | 205.5 | 2871 | -285 | 1 | 0 | 3156 | 2823.0833 | 2823.0833 | 2823.0833 | 3133.2234 | 780 | 200 | 4113.2234 | 102.8% | 95% | 100% | -326.087 | 2496.9963 | -3550 | -400 | -1453.0037 | 36.33% | 98.73% | 95% | 100% | 3156 | -285
[5 empty] | 2019-01-09 | 28 | 206 | 2917 | -248 | 1 | 0 | 3165 | 2837.1805 | 2837.1805 | 2837.1805 | 3133.2234 | 780 | 200 | 4113.2234 | 102.8% | 95% | 100% | -283.7529 | 2553.4277 | -3550 | -400 | -1396.5723 | 34.91% | 98.71% | 95% | 100% | 3165 | -248
[5 empty] | 2019-01-09 | 29 | 206.5 | 3002 | -203 | 1 | 0 | 3205 | 2899.8351 | 2899.8351 | 2899.8351 | 3131.657 | 780 | 200 | 4111.657 | 102.8% | 95% | 100% | -232.2654 | 2667.5697 | -3550 | -400 | -1282.4303 | 32.06% | 98.71% | 95% | 100% | 3205 | -203
[5 empty] | 2019-01-09 | 30 | 207 | 3084 | -154 | 1 | 0 | 3238 | 2951.5251 | 2951.5251 | 2951.5251 | 3128.5243 | 780 | 200 | 4108.5243 | 102.7% | 95% | 100% | -176.2014 | 2775.3238 | -3550 | -400 | -1174.6762 | 29.37% | 98.71% | 95% | 100% | 3238 | -154
[5 empty] | 2019-01-09 | 31 | 207.5 | 3167 | -111 | 0 | 0 | 3278 | 3014.1797 | 3014.1797 | 3014.1797 | 3128.5243 | 780 | 200 | 4108.5243 | 102.7% | 95% | 100% | -127.0023 | 2887.1774 | -2750 | -200 | -62.8226 | 1.571% | 98.69% | 95% | 100% | 3278 | -111
[5 empty] | 2019-01-09 | 32 | 208 | 3296 | -77 | 1 | 0 | 3373 | 3162.9843 | 3162.9843 | 3162.9843 | 3128.5243 | 780 | 200 | 4108.5243 | 102.7% | 95% | 100% | -88.1007 | 3074.8836 | -3550 | -400 | -875.1164 | 21.88% | 98.68% | 95% | 100% | 3373 | -77
[5 empty] | 2019-01-09 | 33 | 208.5 | 3407 | -62 | 1 | 0 | 3469 | 3313.3553 | 3313.3553 | 3313.3553 | 3128.5243 | 780 | 200 | 4108.5243 | 102.7% | 95% | 100% | -70.9382 | 3242.4171 | -3550 | -400 | -707.5829 | 17.69% | 98.67% | 95% | 100% | 3469 | -62
[5 empty] | 2019-01-09 | 34 | 209 | 3438 | -59 | 0 | 0 | 3497 | 3357.2135 | 3357.2135 | 3357.2135 | 3126.958 | 780 | 200 | 4106.958 | 102.7% | 95% | 100% | -67.5057 | 3289.7078 | -2750 | -200 | 339.7078 | -8.493% | 98.65% | 95% | 100% | 3497 | -59
[5 empty] | 2019-01-09 | 35 | 209.5 | 3456 | -58 | 0 | 0 | 3514 | 3383.8417 | 3383.8417 | 3383.8417 | 3126.958 | 780 | 200 | 4106.958 | 102.7% | 95% | 100% | -66.3616 | 3317.4802 | -2750 | -200 | 367.4802 | -9.187% | 98.64% | 95% | 100% | 3514 | -58
[5 empty] | 2019-01-09 | 36 | 210 | 3448 | -58 | 0 | 0 | 3506 | 3371.3108 | 3371.3108 | 3371.3108 | 3126.958 | 780 | 200 | 4106.958 | 102.7% | 95% | 100% | -66.3616 | 3304.9492 | -2750 | -200 | 354.9492 | -8.874% | 98.64% | 95% | 100% | 3506 | -58
[5 empty] | 2019-01-09 | 37 | 210.5 | 3442 | -59 | 0 | 0 | 3501 | 3363.479 | 3363.479 | 3363.479 | 3125.3916 | 780 | 200 | 4105.3916 | 102.6% | 95% | 100% | -67.5057 | 3295.9733 | -2750 | -200 | 345.9733 | -8.649% | 98.59% | 95% | 100% | 3501 | -59
[5 empty] | 2019-01-09 | 38 | 211 | 3416 | -59 | 0 | 0 | 3475 | 3322.7535 | 3322.7535 | 3322.7535 | 3125.3916 | 780 | 200 | 4105.3916 | 102.6% | 95% | 100% | -67.5057 | 3255.2478 | -2750 | -200 | 305.2478 | -7.631% | 98.58% | 95% | 100% | 3475 | -59
[5 empty] | 2019-01-09 | 39 | 211.5 | 3427 | -59 | 0 | 0 | 3486 | 3339.9835 | 3339.9835 | 3339.9835 | 3125.3916 | 780 | 200 | 4105.3916 | 102.6% | 95% | 100% | -67.5057 | 3272.4778 | -2750 | -200 | 322.4778 | -8.062% | 98.56% | 95% | 100% | 3486 | -59
[5 empty] | 2019-01-09 | 40 | 212 | 3401 | -59 | 0 | 0 | 3460 | 3299.258 | 3299.258 | 3299.258 | 3125.3916 | 780 | 200 | 4105.3916 | 102.6% | 95% | 100% | -67.5057 | 3231.7523 | -2750 | -200 | 281.7523 | -7.044% | 98.56% | 95% | 100% | 3460 | -59
[5 empty] | 2019-01-09 | 41 | 212.5 | 3315 | -60 | 0 | 0 | 3375 | 3166.1171 | 3166.1171 | 3166.1171 | 3125.3916 | 780 | 200 | 4105.3916 | 102.6% | 95% | 100% | -68.6499 | 3097.4672 | -2750 | -200 | 147.4672 | -3.687% | 98.49% | 95% | 100% | 3375 | -60
[5 empty] | 2019-01-09 | 42 | 213 | 3187 | -60 | 0 | 0 | 3247 | 2965.6224 | 2965.6224 | 2965.6224 | 3125.3916 | 780 | 200 | 4105.3916 | 102.6% | 95% | 100% | -68.6499 | 2896.9725 | -2750 | -200 | -53.0275 | 1.326% | 98.47% | 95% | 100% | 3247 | -60
[5 empty] | 2019-01-09 | 43 | 213.5 | 3038 | -60 | 0 | 0 | 3098 | 2732.2341 | 2732.2341 | 2732.2341 | 3123.8252 | 780 | 200 | 4103.8252 | 102.6% | 95% | 100% | -68.6499 | 2663.5842 | -2750 | -200 | -286.4158 | 7.16% | 98.45% | 95% | 100% | 3098 | -60
[5 empty] | 2019-01-09 | 44 | 214 | 2851 | -61 | 0 | 0 | 2912 | 2440.8904 | 2440.8904 | 2440.8904 | 3123.8252 | 780 | 200 | 4103.8252 | 102.6% | 95% | 100% | -69.7941 | 2371.0963 | -2750 | -200 | -578.9037 | 14.47% | 98.45% | 95% | 100% | 2912 | -61
[5 empty] | 2019-01-09 | 45 | 214.5 | 2672 | -62 | 0 | 0 | 2734 | 2162.0775 | 2162.0775 | 2162.0775 | 3123.8252 | 780 | 200 | 4103.8252 | 102.6% | 95% | 100% | -70.9382 | 2091.1393 | -2750 | -200 | -858.8607 | 21.47% | 98.44% | 95% | 100% | 2734 | -62
[5 empty] | 2019-01-09 | 46 | 215 | 2512 | -64 | 0 | 0 | 2576 | 1914.5919 | 1914.5919 | 1914.5919 | 3123.8252 | 780 | 200 | 4103.8252 | 102.6% | 95% | 100% | -73.2265 | 1841.3654 | -2750 | -200 | -1108.6346 | 27.72% | 98.41% | 95% | 100% | 2576 | -64
[5 empty] | 2019-01-09 | 47 | 215.5 | 2344 | -66 | 0 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 3122.2589 | 780 | 200 | 4102.2589 | 102.6% | 95% | 100% | -75.5149 | 1579.0606 | -2750 | -200 | -1370.9394 | 34.27% | 98.39% | 95% | 100% | 2410 | -66
[5 empty] | 2019-01-09 | 48 | 216 | 2238 | -68 | 0 | 0 | 2306 | 1491.6735 | 1491.6735 | 1491.6735 | 3122.2589 | 780 | 200 | 4102.2589 | 102.6% | 95% | 100% | -77.8032 | 1413.8703 | -2750 | -200 | -1536.1297 | 38.4% | 98.33% | 95% | 100% | 2306 | -68
[5 empty] | 2019-01-10 | 1 | 216.5 | 2211 | -67 | 0 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 3122.2589 | 780 | 200 | 4102.2589 | 102.6% | 95% | 100% | -76.659 | 1371.1563 | -2750 | -200 | -1578.8437 | 39.47% | 98.32% | 95% | 100% | 2278 | -67
[5 empty] | 2019-01-10 | 2 | 217 | 2243 | -66 | 0 | 0 | 2309 | 1496.3726 | 1496.3726 | 1496.3726 | 3120.6925 | 780 | 200 | 4100.6925 | 102.5% | 95% | 100% | -75.5149 | 1420.8578 | -2750 | -200 | -1529.1422 | 38.23% | 98.28% | 95% | 100% | 2309 | -66
[5 empty] | 2019-01-10 | 3 | 217.5 | 2222 | -66 | 0 | 0 | 2288 | 1463.479 | 1463.479 | 1463.479 | 3120.6925 | 780 | 200 | 4100.6925 | 102.5% | 95% | 100% | -75.5149 | 1387.9641 | -2750 | -200 | -1562.0359 | 39.05% | 98.26% | 95% | 100% | 2288 | -66
[5 empty] | 2019-01-10 | 4 | 218 | 2181 | -66 | 0 | 0 | 2247 | 1399.258 | 1399.258 | 1399.258 | 3119.1261 | 780 | 200 | 4099.1261 | 102.5% | 95% | 100% | -75.5149 | 1323.7432 | -2750 | -200 | -1626.2568 | 40.66% | 98.23% | 95% | 100% | 2247 | -66
[5 empty] | 2019-01-10 | 5 | 218.5 | 2142 | -65 | 0 | 0 | 2207 | 1336.6035 | 1336.6035 | 1336.6035 | 3119.1261 | 780 | 200 | 4099.1261 | 102.5% | 95% | 100% | -74.3707 | 1262.2328 | -2750 | -200 | -1687.7672 | 42.19% | 98.22% | 95% | 100% | 2207 | -65
[5 empty] | 2019-01-10 | 6 | 219 | 2135 | -64 | 0 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 3119.1261 | 780 | 200 | 4099.1261 | 102.5% | 95% | 100% | -73.2265 | 1250.846 | -2750 | -200 | -1699.154 | 42.48% | 98.21% | 95% | 100% | 2199 | -64
[5 empty] | 2019-01-10 | 7 | 219.5 | 2106 | -67 | 0 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 3117.5598 | 780 | 200 | 4097.5598 | 102.4% | 95% | 100% | -76.659 | 1206.688 | -2750 | -200 | -1743.312 | 43.58% | 98.21% | 95% | 100% | 2173 | -67
[5 empty] | 2019-01-10 | 8 | 220 | 2075 | -69 | 0 | 0 | 2144 | 1237.9225 | 1237.9225 | 1237.9225 | 3115.9934 | 780 | 200 | 4095.9934 | 102.4% | 95% | 100% | -78.9474 | 1158.9751 | -2750 | -200 | -1791.0249 | 44.78% | 98.2% | 95% | 100% | 2144 | -69
[5 empty] | 2019-01-10 | 9 | 220.5 | 2061 | -68 | 0 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 3115.9934 | 780 | 200 | 4095.9934 | 102.4% | 95% | 100% | -77.8032 | 1136.6238 | -2750 | -200 | -1813.3762 | 45.33% | 98.19% | 95% | 100% | 2129 | -68
[5 empty] | 2019-01-10 | 10 | 221 | 2066 | -67 | 0 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 3114.427 | 780 | 200 | 4094.427 | 102.4% | 95% | 100% | -76.659 | 1144.0335 | -2750 | -200 | -1805.9665 | 45.15% | 98.19% | 95% | 100% | 2133 | -67
[5 empty] | 2019-01-10 | 11 | 221.5 | 2127 | -68 | 0 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 3114.427 | 780 | 200 | 4094.427 | 102.4% | 95% | 100% | -77.8032 | 1240.0039 | -2750 | -200 | -1709.9961 | 42.75% | 98.18% | 95% | 100% | 2195 | -68
[5 empty] | 2019-01-10 | 12 | 222 | 2232 | -68 | 0 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 3114.427 | 780 | 200 | 4094.427 | 102.4% | 95% | 100% | -77.8032 | 1404.4721 | -2750 | -200 | -1545.5279 | 38.64% | 98.18% | 95% | 100% | 2300 | -68
[5 empty] | 2019-01-10 | 13 | 222.5 | 2495 | -67 | 0 | 0 | 2562 | 1892.6628 | 1892.6628 | 1892.6628 | 3114.427 | 780 | 200 | 4094.427 | 102.4% | 95% | 100% | -76.659 | 1816.0038 | -2750 | -200 | -1133.9962 | 28.35% | 98.16% | 95% | 100% | 2562 | -67
[5 empty] | 2019-01-10 | 14 | 223 | 2733 | -65 | 0 | 0 | 2798 | 2262.3248 | 2262.3248 | 2262.3248 | 3112.8607 | 780 | 200 | 4092.8607 | 102.3% | 95% | 100% | -74.3707 | 2187.9541 | -2750 | -200 | -762.0459 | 19.05% | 98.15% | 95% | 100% | 2798 | -65
[5 empty] | 2019-01-10 | 15 | 223.5 | 3016 | -66 | 0 | 0 | 3082 | 2707.1723 | 2707.1723 | 2707.1723 | 3112.8607 | 780 | 200 | 4092.8607 | 102.3% | 95% | 100% | -75.5149 | 2631.6574 | -2750 | -200 | -318.3426 | 7.959% | 98.13% | 95% | 100% | 3082 | -66
[5 empty] | 2019-01-10 | 16 | 224 | 3177 | -66 | 0 | 0 | 3243 | 2959.357 | 2959.357 | 2959.357 | 3112.8607 | 780 | 200 | 4092.8607 | 102.3% | 95% | 100% | -75.5149 | 2883.8421 | -2750 | -200 | -66.1579 | 1.654% | 98.12% | 95% | 100% | 3243 | -66
[5 empty] | 2019-01-10 | 17 | 224.5 | 3262 | -68 | 0 | 0 | 3330 | 3095.6307 | 3095.6307 | 3095.6307 | 3112.8607 | 780 | 200 | 4092.8607 | 102.3% | 95% | 100% | -77.8032 | 3017.8275 | -2750 | -200 | 67.8275 | -1.696% | 98.1% | 95% | 100% | 3330 | -68
[5 empty] | 2019-01-10 | 18 | 225 | 3256 | -74 | 0 | 0 | 3330 | 3095.6307 | 3095.6307 | 3095.6307 | 3111.2943 | 780 | 200 | 4091.2943 | 102.3% | 95% | 100% | -84.6682 | 3010.9625 | -2750 | -200 | 60.9625 | -1.524% | 98.09% | 95% | 100% | 3330 | -74
[5 empty] | 2019-01-10 | 19 | 225.5 | 3290 | -79 | 0 | 0 | 3369 | 3156.7189 | 3156.7189 | 3156.7189 | 3111.2943 | 780 | 200 | 4091.2943 | 102.3% | 95% | 100% | -90.389 | 3066.3299 | -2750 | -200 | 116.3299 | -2.908% | 98.07% | 95% | 100% | 3369 | -79
[5 empty] | 2019-01-10 | 20 | 226 | 3271 | -106 | 1 | 0 | 3377 | 3169.2498 | 3169.2498 | 3169.2498 | 3111.2943 | 780 | 200 | 4091.2943 | 102.3% | 95% | 100% | -121.2815 | 3047.9683 | -3550 | -400 | -902.0317 | 22.55% | 98.05% | 95% | 100% | 3377 | -106
[5 empty] | 2019-01-10 | 21 | 226.5 | 3220 | -131 | 1 | 0 | 3351 | 3128.5243 | 3128.5243 | 3128.5243 | 3111.2943 | 780 | 200 | 4091.2943 | 102.3% | 95% | 100% | -149.8856 | 2978.6387 | -3550 | -400 | -971.3613 | 24.28% | 98.05% | 95% | 100% | 3351 | -131
[5 empty] | 2019-01-10 | 22 | 227 | 3217 | -142 | 1 | 0 | 3359 | 3141.0552 | 3141.0552 | 3141.0552 | 3109.7279 | 780 | 200 | 4089.7279 | 102.2% | 95% | 100% | -162.4714 | 2978.5838 | -3550 | -400 | -971.4162 | 24.29% | 98.04% | 95% | 100% | 3359 | -142
[5 empty] | 2019-01-10 | 23 | 227.5 | 3190 | -152 | 1 | 0 | 3342 | 3114.427 | 3114.427 | 3114.427 | 3109.7279 | 780 | 200 | 4089.7279 | 102.2% | 95% | 100% | -173.913 | 2940.514 | -3550 | -400 | -1009.486 | 25.24% | 98.02% | 95% | 100% | 3342 | -152
[5 empty] | 2019-01-10 | 24 | 228 | 3153 | -164 | 1 | 0 | 3317 | 3075.2679 | 3075.2679 | 3075.2679 | 3109.7279 | 780 | 200 | 4089.7279 | 102.2% | 95% | 100% | -187.643 | 2887.6249 | -3550 | -400 | -1062.3751 | 26.56% | 98.01% | 95% | 100% | 3317 | -164
[5 empty] | 2019-01-10 | 25 | 228.5 | 3178 | -171 | 1 | 0 | 3349 | 3125.3916 | 3125.3916 | 3125.3916 | 3109.7279 | 780 | 200 | 4089.7279 | 102.2% | 95% | 100% | -195.6522 | 2929.7394 | -3550 | -400 | -1020.2606 | 25.51% | 97.96% | 95% | 100% | 3349 | -171
[5 empty] | 2019-01-10 | 26 | 229 | 3196 | -167 | 1 | 0 | 3363 | 3147.3207 | 3147.3207 | 3147.3207 | 3108.1616 | 780 | 200 | 4088.1616 | 102.2% | 95% | 100% | -191.0755 | 2956.2452 | -3550 | -400 | -993.7548 | 24.84% | 97.94% | 95% | 100% | 3363 | -167
[5 empty] | 2019-01-10 | 27 | 229.5 | 3208 | -157 | 1 | 0 | 3365 | 3150.4534 | 3150.4534 | 3150.4534 | 3108.1616 | 780 | 200 | 4088.1616 | 102.2% | 95% | 100% | -179.6339 | 2970.8196 | -3550 | -400 | -979.1804 | 24.48% | 97.92% | 95% | 100% | 3365 | -157
[5 empty] | 2019-01-10 | 28 | 230 | 3205 | -143 | 1 | 0 | 3348 | 3123.8252 | 3123.8252 | 3123.8252 | 3108.1616 | 780 | 200 | 4088.1616 | 102.2% | 95% | 100% | -163.6156 | 2960.2097 | -3550 | -400 | -989.7903 | 24.74% | 97.91% | 95% | 100% | 3348 | -143
[5 empty] | 2019-01-10 | 29 | 230.5 | 3230 | -124 | 1 | 0 | 3354 | 3133.2234 | 3133.2234 | 3133.2234 | 3106.5952 | 780 | 200 | 4086.5952 | 102.2% | 95% | 100% | -141.8764 | 2991.347 | -3550 | -400 | -958.653 | 23.97% | 97.91% | 95% | 100% | 3354 | -124
[5 empty] | 2019-01-10 | 30 | 231 | 3240 | -109 | 1 | 0 | 3349 | 3125.3916 | 3125.3916 | 3125.3916 | 3106.5952 | 780 | 200 | 4086.5952 | 102.2% | 95% | 100% | -124.714 | 3000.6776 | -3550 | -400 | -949.3224 | 23.73% | 97.91% | 95% | 100% | 3349 | -109
[5 empty] | 2019-01-10 | 31 | 231.5 | 3285 | -94 | 1 | 0 | 3379 | 3172.3825 | 3172.3825 | 3172.3825 | 3106.5952 | 780 | 200 | 4086.5952 | 102.2% | 95% | 100% | -107.5515 | 3064.831 | -3550 | -400 | -885.169 | 22.13% | 97.9% | 95% | 100% | 3379 | -94
[5 empty] | 2019-01-10 | 32 | 232 | 3362 | -83 | 1 | 0 | 3445 | 3275.7626 | 3275.7626 | 3275.7626 | 3106.5952 | 780 | 200 | 4086.5952 | 102.2% | 95% | 100% | -94.9657 | 3180.7969 | -3550 | -400 | -769.2031 | 19.23% | 97.87% | 95% | 100% | 3445 | -83
[5 empty] | 2019-01-10 | 33 | 232.5 | 3417 | -80 | 1 | 0 | 3497 | 3357.2135 | 3357.2135 | 3357.2135 | 3106.5952 | 780 | 200 | 4086.5952 | 102.2% | 95% | 100% | -91.5332 | 3265.6803 | -3550 | -400 | -684.3197 | 17.11% | 97.87% | 95% | 100% | 3497 | -80
[5 empty] | 2019-01-10 | 34 | 233 | 3428 | -80 | 1 | 0 | 3508 | 3374.4435 | 3374.4435 | 3374.4435 | 3105.0289 | 780 | 200 | 4085.0289 | 102.1% | 95% | 100% | -91.5332 | 3282.9103 | -3550 | -400 | -667.0897 | 16.68% | 97.86% | 95% | 100% | 3508 | -80
[5 empty] | 2019-01-10 | 35 | 233.5 | 3446 | -82 | 0 | 0 | 3528 | 3405.7708 | 3405.7708 | 3405.7708 | 3105.0289 | 780 | 200 | 4085.0289 | 102.1% | 95% | 100% | -93.8215 | 3311.9493 | -2750 | -200 | 361.9493 | -9.049% | 97.85% | 95% | 100% | 3528 | -82
[5 empty] | 2019-01-10 | 36 | 234 | 3414 | -84 | 0 | 0 | 3498 | 3358.7799 | 3358.7799 | 3358.7799 | 3103.4625 | 780 | 200 | 4083.4625 | 102.1% | 95% | 100% | -96.1098 | 3262.67 | -2750 | -200 | 312.67 | -7.817% | 97.85% | 95% | 100% | 3498 | -84
[5 empty] | 2019-01-10 | 37 | 234.5 | 3408 | -87 | 0 | 0 | 3495 | 3354.0808 | 3354.0808 | 3354.0808 | 3101.8961 | 780 | 200 | 4081.8961 | 102% | 95% | 100% | -99.5423 | 3254.5385 | -2750 | -200 | 304.5385 | -7.613% | 97.84% | 95% | 100% | 3495 | -87
[5 empty] | 2019-01-10 | 38 | 235 | 3410 | -89 | 0 | 0 | 3499 | 3360.3462 | 3360.3462 | 3360.3462 | 3101.8961 | 780 | 200 | 4081.8961 | 102% | 95% | 100% | -101.8307 | 3258.5156 | -2750 | -200 | 308.5156 | -7.713% | 97.84% | 95% | 100% | 3499 | -89
[5 empty] | 2019-01-10 | 39 | 235.5 | 3394 | -90 | 0 | 0 | 3484 | 3336.8508 | 3336.8508 | 3336.8508 | 3100.3298 | 780 | 200 | 4080.3298 | 102% | 95% | 100% | -102.9748 | 3233.876 | -2750 | -200 | 283.876 | -7.097% | 97.83% | 95% | 100% | 3484 | -90
[5 empty] | 2019-01-10 | 40 | 236 | 3340 | -91 | 0 | 0 | 3431 | 3253.8335 | 3253.8335 | 3253.8335 | 3100.3298 | 780 | 200 | 4080.3298 | 102% | 95% | 100% | -104.119 | 3149.7145 | -2750 | -200 | 199.7145 | -4.993% | 97.81% | 95% | 100% | 3431 | -91
[5 empty] | 2019-01-10 | 41 | 236.5 | 3227 | -92 | 0 | 0 | 3319 | 3078.4007 | 3078.4007 | 3078.4007 | 3100.3298 | 780 | 200 | 4080.3298 | 102% | 95% | 100% | -105.2632 | 2973.1375 | -2750 | -200 | 23.1375 | -0.5784% | 97.81% | 95% | 100% | 3319 | -92
[5 empty] | 2019-01-10 | 42 | 237 | 3101 | -93 | 0 | 0 | 3194 | 2882.6051 | 2882.6051 | 2882.6051 | 3100.3298 | 780 | 200 | 4080.3298 | 102% | 95% | 100% | -106.4073 | 2776.1978 | -2750 | -200 | -173.8022 | 4.345% | 97.77% | 95% | 100% | 3194 | -93
[5 empty] | 2019-01-10 | 43 | 237.5 | 2932 | -95 | 0 | 0 | 3027 | 2621.0223 | 2621.0223 | 2621.0223 | 3100.3298 | 780 | 200 | 4080.3298 | 102% | 95% | 100% | -108.6957 | 2512.3266 | -2750 | -200 | -437.6734 | 10.94% | 97.74% | 95% | 100% | 3027 | -95
[5 empty] | 2019-01-10 | 44 | 238 | 2753 | -97 | 0 | 0 | 2850 | 2343.7758 | 2343.7758 | 2343.7758 | 3100.3298 | 780 | 200 | 4080.3298 | 102% | 95% | 100% | -110.984 | 2232.7918 | -2750 | -200 | -717.2082 | 17.93% | 97.74% | 95% | 100% | 2850 | -97
[5 empty] | 2019-01-10 | 45 | 238.5 | 2568 | -99 | 0 | 0 | 2667 | 2057.1311 | 2057.1311 | 2057.1311 | 3098.7634 | 780 | 200 | 4078.7634 | 102% | 95% | 100% | -113.2723 | 1943.8588 | -2750 | -200 | -1006.1412 | 25.15% | 97.73% | 95% | 100% | 2667 | -99
[5 empty] | 2019-01-10 | 46 | 239 | 2409 | -101 | 0 | 0 | 2510 | 1811.2119 | 1811.2119 | 1811.2119 | 3098.7634 | 780 | 200 | 4078.7634 | 102% | 95% | 100% | -115.5606 | 1695.6512 | -2750 | -200 | -1254.3488 | 31.36% | 97.73% | 95% | 100% | 2510 | -101
[5 empty] | 2019-01-10 | 47 | 239.5 | 2248 | -98 | 0 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 3095.6307 | 780 | 200 | 4075.6307 | 101.9% | 95% | 100% | -112.1281 | 1442.2 | -2750 | -200 | -1507.8 | 37.7% | 97.71% | 95% | 100% | 2346 | -98
[5 empty] | 2019-01-10 | 48 | 240 | 2132 | -96 | 0 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 3095.6307 | 780 | 200 | 4075.6307 | 101.9% | 95% | 100% | -109.8398 | 1259.6573 | -2750 | -200 | -1690.3427 | 42.26% | 97.71% | 95% | 100% | 2228 | -96
[5 empty] | 2019-01-11 | 1 | 240.5 | 2118 | -97 | 0 | 0 | 2215 | 1349.1344 | 1349.1344 | 1349.1344 | 3095.6307 | 780 | 200 | 4075.6307 | 101.9% | 95% | 100% | -110.984 | 1238.1504 | -2750 | -200 | -1711.8496 | 42.8% | 97.7% | 95% | 100% | 2215 | -97
[5 empty] | 2019-01-11 | 2 | 241 | 2156 | -98 | 0 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 3095.6307 | 780 | 200 | 4075.6307 | 101.9% | 95% | 100% | -112.1281 | 1298.0944 | -2750 | -200 | -1651.9056 | 41.3% | 97.69% | 95% | 100% | 2254 | -98
[5 empty] | 2019-01-11 | 3 | 241.5 | 2126 | -98 | 0 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 3095.6307 | 780 | 200 | 4075.6307 | 101.9% | 95% | 100% | -112.1281 | 1251.1035 | -2750 | -200 | -1698.8965 | 42.47% | 97.66% | 95% | 100% | 2224 | -98
[5 empty] | 2019-01-11 | 4 | 242 | 2069 | -98 | 0 | 0 | 2167 | 1273.9489 | 1273.9489 | 1273.9489 | 3095.6307 | 780 | 200 | 4075.6307 | 101.9% | 95% | 100% | -112.1281 | 1161.8207 | -2750 | -200 | -1788.1793 | 44.7% | 97.64% | 95% | 100% | 2167 | -98
[5 empty] | 2019-01-11 | 5 | 242.5 | 2035 | -99 | 0 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 3095.6307 | 780 | 200 | 4075.6307 | 101.9% | 95% | 100% | -113.2723 | 1108.9866 | -2750 | -200 | -1841.0134 | 46.03% | 97.63% | 95% | 100% | 2134 | -99
[5 empty] | 2019-01-11 | 6 | 243 | 2024 | -101 | 0 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 3094.0643 | 780 | 200 | 4074.0643 | 101.9% | 95% | 100% | -115.5606 | 1092.6009 | -2750 | -200 | -1857.3991 | 46.43% | 97.62% | 95% | 100% | 2125 | -101
[5 empty] | 2019-01-11 | 7 | 243.5 | 1982 | -100 | 0 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 3092.4979 | 780 | 200 | 4072.4979 | 101.8% | 95% | 100% | -114.4165 | 1026.3914 | -2750 | -200 | -1923.6086 | 48.09% | 97.61% | 95% | 100% | 2082 | -100
[5 empty] | 2019-01-11 | 8 | 244 | 1959 | -100 | 0 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 3092.4979 | 780 | 200 | 4072.4979 | 101.8% | 95% | 100% | -114.4165 | 990.3651 | -2750 | -200 | -1959.6349 | 48.99% | 97.6% | 95% | 100% | 2059 | -100
[5 empty] | 2019-01-11 | 9 | 244.5 | 1935 | -100 | 0 | 0 | 2035 | 1067.1888 | 1067.1888 | 1067.1888 | 3090.9316 | 780 | 200 | 4070.9316 | 101.8% | 95% | 100% | -114.4165 | 952.7723 | -2750 | -200 | -1997.2277 | 49.93% | 97.6% | 95% | 100% | 2035 | -100
[5 empty] | 2019-01-11 | 10 | 245 | 1938 | -100 | 0 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 3090.9316 | 780 | 200 | 4070.9316 | 101.8% | 95% | 100% | -114.4165 | 957.4714 | -2750 | -200 | -1992.5286 | 49.81% | 97.57% | 95% | 100% | 2038 | -100
[5 empty] | 2019-01-11 | 11 | 245.5 | 2004 | -99 | 0 | 0 | 2103 | 1173.7016 | 1173.7016 | 1173.7016 | 3089.3652 | 780 | 200 | 4069.3652 | 101.7% | 95% | 100% | -113.2723 | 1060.4293 | -2750 | -200 | -1889.5707 | 47.24% | 97.57% | 95% | 100% | 2103 | -99
[5 empty] | 2019-01-11 | 12 | 246 | 2105 | -98 | 0 | 0 | 2203 | 1330.338 | 1330.338 | 1330.338 | 3089.3652 | 780 | 200 | 4069.3652 | 101.7% | 95% | 100% | -112.1281 | 1218.2099 | -2750 | -200 | -1731.7901 | 43.29% | 97.57% | 95% | 100% | 2203 | -98
[5 empty] | 2019-01-11 | 13 | 246.5 | 2339 | -95 | 0 | 0 | 2434 | 1692.1682 | 1692.1682 | 1692.1682 | 3087.7988 | 780 | 200 | 4067.7988 | 101.7% | 95% | 100% | -108.6957 | 1583.4725 | -2750 | -200 | -1366.5275 | 34.16% | 97.55% | 95% | 100% | 2434 | -95
[5 empty] | 2019-01-11 | 14 | 247 | 2609 | -93 | 0 | 0 | 2702 | 2111.9538 | 2111.9538 | 2111.9538 | 3086.2325 | 780 | 200 | 4066.2325 | 101.7% | 95% | 100% | -106.4073 | 2005.5465 | -2750 | -200 | -944.4535 | 23.61% | 97.53% | 95% | 100% | 2702 | -93
[5 empty] | 2019-01-11 | 15 | 247.5 | 2913 | -91 | 0 | 0 | 3004 | 2584.9959 | 2584.9959 | 2584.9959 | 3086.2325 | 780 | 200 | 4066.2325 | 101.7% | 95% | 100% | -104.119 | 2480.8769 | -2750 | -200 | -469.1231 | 11.73% | 97.52% | 95% | 100% | 3004 | -91
[5 empty] | 2019-01-11 | 16 | 248 | 3090 | -88 | 0 | 0 | 3178 | 2857.5433 | 2857.5433 | 2857.5433 | 3086.2325 | 780 | 200 | 4066.2325 | 101.7% | 95% | 100% | -100.6865 | 2756.8568 | -2750 | -200 | -193.1432 | 4.829% | 97.5% | 95% | 100% | 3178 | -88
[5 empty] | 2019-01-11 | 17 | 248.5 | 3171 | -88 | 0 | 0 | 3259 | 2984.4188 | 2984.4188 | 2984.4188 | 3084.6661 | 780 | 200 | 4064.6661 | 101.6% | 95% | 100% | -100.6865 | 2883.7323 | -2750 | -200 | -66.2677 | 1.657% | 97.46% | 95% | 100% | 3259 | -88
[5 empty] | 2019-01-11 | 18 | 249 | 3167 | -92 | 1 | 0 | 3259 | 2984.4188 | 2984.4188 | 2984.4188 | 3083.0998 | 780 | 200 | 4063.0998 | 101.6% | 95% | 100% | -105.2632 | 2879.1556 | -3550 | -400 | -1070.8444 | 26.77% | 97.45% | 95% | 100% | 3259 | -92
[5 empty] | 2019-01-11 | 19 | 249.5 | 3186 | -98 | 1 | 0 | 3284 | 3023.5779 | 3023.5779 | 3023.5779 | 3083.0998 | 780 | 200 | 4063.0998 | 101.6% | 95% | 100% | -112.1281 | 2911.4498 | -3550 | -400 | -1038.5502 | 25.96% | 97.44% | 95% | 100% | 3284 | -98
[5 empty] | 2019-01-11 | 20 | 250 | 3136 | -120 | 1 | 0 | 3256 | 2979.7197 | 2979.7197 | 2979.7197 | 3083.0998 | 780 | 200 | 4063.0998 | 101.6% | 95% | 100% | -137.2998 | 2842.4199 | -3550 | -400 | -1107.5801 | 27.69% | 97.44% | 95% | 100% | 3256 | -120
[5 empty] | 2019-01-11 | 21 | 250.5 | 3081 | -143 | 1 | 0 | 3224 | 2929.596 | 2929.596 | 2929.596 | 3083.0998 | 780 | 200 | 4063.0998 | 101.6% | 95% | 100% | -163.6156 | 2765.9805 | -3550 | -400 | -1184.0195 | 29.6% | 97.42% | 95% | 100% | 3224 | -143
[5 empty] | 2019-01-11 | 22 | 251 | 3039 | -163 | 1 | 0 | 3202 | 2895.136 | 2895.136 | 2895.136 | 3081.5334 | 780 | 200 | 4061.5334 | 101.5% | 95% | 100% | -186.4989 | 2708.6372 | -3550 | -400 | -1241.3628 | 31.03% | 97.4% | 95% | 100% | 3202 | -163
[5 empty] | 2019-01-11 | 23 | 251.5 | 3032 | -180 | 1 | 0 | 3212 | 2910.7997 | 2910.7997 | 2910.7997 | 3081.5334 | 780 | 200 | 4061.5334 | 101.5% | 95% | 100% | -205.9497 | 2704.85 | -3550 | -400 | -1245.15 | 31.13% | 97.4% | 95% | 100% | 3212 | -180
[5 empty] | 2019-01-11 | 24 | 252 | 3008 | -196 | 1 | 0 | 3204 | 2898.2688 | 2898.2688 | 2898.2688 | 3081.5334 | 780 | 200 | 4061.5334 | 101.5% | 95% | 100% | -224.2563 | 2674.0125 | -3550 | -400 | -1275.9875 | 31.9% | 97.39% | 95% | 100% | 3204 | -196
[5 empty] | 2019-01-11 | 25 | 252.5 | 3030 | -199 | 1 | 0 | 3229 | 2937.4279 | 2937.4279 | 2937.4279 | 3081.5334 | 780 | 200 | 4061.5334 | 101.5% | 95% | 100% | -227.6888 | 2709.7391 | -3550 | -400 | -1240.2609 | 31.01% | 97.37% | 95% | 100% | 3229 | -199
[5 empty] | 2019-01-11 | 26 | 253 | 3011 | -197 | 1 | 0 | 3208 | 2904.5342 | 2904.5342 | 2904.5342 | 3079.967 | 780 | 200 | 4059.967 | 101.5% | 95% | 100% | -225.4005 | 2679.1338 | -3550 | -400 | -1270.8662 | 31.77% | 97.37% | 95% | 100% | 3208 | -197
[5 empty] | 2019-01-11 | 27 | 253.5 | 3030 | -181 | 1 | 0 | 3211 | 2909.2333 | 2909.2333 | 2909.2333 | 3079.967 | 780 | 200 | 4059.967 | 101.5% | 95% | 100% | -207.0938 | 2702.1395 | -3550 | -400 | -1247.8605 | 31.2% | 97.36% | 95% | 100% | 3211 | -181
[5 empty] | 2019-01-11 | 28 | 254 | 3038 | -160 | 1 | 0 | 3198 | 2888.8706 | 2888.8706 | 2888.8706 | 3079.967 | 780 | 200 | 4059.967 | 101.5% | 95% | 100% | -183.0664 | 2705.8042 | -3550 | -400 | -1244.1958 | 31.1% | 97.34% | 95% | 100% | 3198 | -160
[5 empty] | 2019-01-11 | 29 | 254.5 | 3063 | -140 | 1 | 0 | 3203 | 2896.7024 | 2896.7024 | 2896.7024 | 3079.967 | 780 | 200 | 4059.967 | 101.5% | 95% | 100% | -160.1831 | 2736.5193 | -3550 | -400 | -1213.4807 | 30.34% | 97.32% | 95% | 100% | 3203 | -140
[5 empty] | 2019-01-11 | 30 | 255 | 3048 | -127 | 1 | 0 | 3175 | 2852.8442 | 2852.8442 | 2852.8442 | 3079.967 | 780 | 200 | 4059.967 | 101.5% | 95% | 100% | -145.3089 | 2707.5353 | -3550 | -400 | -1242.4647 | 31.06% | 97.31% | 95% | 100% | 3175 | -127
[5 empty] | 2019-01-11 | 31 | 255.5 | 3073 | -111 | 1 | 0 | 3184 | 2866.9415 | 2866.9415 | 2866.9415 | 3079.967 | 780 | 200 | 4059.967 | 101.5% | 95% | 100% | -127.0023 | 2739.9392 | -3550 | -400 | -1210.0608 | 30.25% | 97.26% | 95% | 100% | 3184 | -111
[5 empty] | 2019-01-11 | 32 | 256 | 3126 | -99 | 1 | 0 | 3225 | 2931.1624 | 2931.1624 | 2931.1624 | 3079.967 | 780 | 200 | 4059.967 | 101.5% | 95% | 100% | -113.2723 | 2817.8901 | -3550 | -400 | -1132.1099 | 28.3% | 97.25% | 95% | 100% | 3225 | -99
[5 empty] | 2019-01-11 | 33 | 256.5 | 3244 | -95 | 1 | 0 | 3339 | 3109.7279 | 3109.7279 | 3109.7279 | 3078.4007 | 780 | 200 | 4058.4007 | 101.5% | 95% | 100% | -108.6957 | 3001.0323 | -3550 | -400 | -948.9677 | 23.72% | 97.24% | 95% | 100% | 3339 | -95
[5 empty] | 2019-01-11 | 34 | 257 | 3365 | -96 | 1 | 0 | 3461 | 3300.8244 | 3300.8244 | 3300.8244 | 3078.4007 | 780 | 200 | 4058.4007 | 101.5% | 95% | 100% | -109.8398 | 3190.9846 | -3550 | -400 | -759.0154 | 18.98% | 97.23% | 95% | 100% | 3461 | -96
[5 empty] | 2019-01-11 | 35 | 257.5 | 3405 | -98 | 1 | 0 | 3503 | 3366.6117 | 3366.6117 | 3366.6117 | 3076.8343 | 780 | 200 | 4056.8343 | 101.4% | 95% | 100% | -112.1281 | 3254.4836 | -3550 | -400 | -695.5164 | 17.39% | 97.21% | 95% | 100% | 3503 | -98
[5 empty] | 2019-01-11 | 36 | 258 | 3358 | -100 | 0 | 0 | 3458 | 3296.1253 | 3296.1253 | 3296.1253 | 3076.8343 | 780 | 200 | 4056.8343 | 101.4% | 95% | 100% | -114.4165 | 3181.7088 | -2750 | -200 | 231.7088 | -5.793% | 97.19% | 95% | 100% | 3458 | -100
[5 empty] | 2019-01-11 | 37 | 258.5 | 3329 | -103 | 0 | 0 | 3432 | 3255.3998 | 3255.3998 | 3255.3998 | 3076.8343 | 780 | 200 | 4056.8343 | 101.4% | 95% | 100% | -117.849 | 3137.5509 | -2750 | -200 | 187.5509 | -4.689% | 97.17% | 95% | 100% | 3432 | -103
[5 empty] | 2019-01-11 | 38 | 259 | 3291 | -105 | 0 | 0 | 3396 | 3199.0107 | 3199.0107 | 3199.0107 | 3075.2679 | 780 | 200 | 4055.2679 | 101.4% | 95% | 100% | -120.1373 | 3078.8734 | -2750 | -200 | 128.8734 | -3.222% | 97.17% | 95% | 100% | 3396 | -105
[5 empty] | 2019-01-11 | 39 | 259.5 | 3191 | -107 | 0 | 0 | 3298 | 3045.507 | 3045.507 | 3045.507 | 3075.2679 | 780 | 200 | 4055.2679 | 101.4% | 95% | 100% | -122.4256 | 2923.0814 | -2750 | -200 | -26.9186 | 0.673% | 97.16% | 95% | 100% | 3298 | -107
[5 empty] | 2019-01-11 | 40 | 260 | 3071 | -109 | 0 | 0 | 3180 | 2860.676 | 2860.676 | 2860.676 | 3075.2679 | 780 | 200 | 4055.2679 | 101.4% | 95% | 100% | -124.714 | 2735.9621 | -2750 | -200 | -214.0379 | 5.351% | 97.16% | 95% | 100% | 3180 | -109
[5 empty] | 2019-01-11 | 41 | 260.5 | 2955 | -114 | 0 | 0 | 3069 | 2686.8096 | 2686.8096 | 2686.8096 | 3073.7016 | 780 | 200 | 4053.7016 | 101.3% | 95% | 100% | -130.4348 | 2556.3748 | -2750 | -200 | -393.6252 | 9.841% | 97.16% | 95% | 100% | 3069 | -114
[5 empty] | 2019-01-11 | 42 | 261 | 2824 | -120 | 0 | 0 | 2944 | 2491.014 | 2491.014 | 2491.014 | 3073.7016 | 780 | 200 | 4053.7016 | 101.3% | 95% | 100% | -137.2998 | 2353.7142 | -2750 | -200 | -596.2858 | 14.91% | 97.16% | 95% | 100% | 2944 | -120
[5 empty] | 2019-01-11 | 43 | 261.5 | 2671 | -126 | 0 | 0 | 2797 | 2260.7585 | 2260.7585 | 2260.7585 | 3073.7016 | 780 | 200 | 4053.7016 | 101.3% | 95% | 100% | -144.1648 | 2116.5937 | -2750 | -200 | -833.4063 | 20.84% | 97.13% | 95% | 100% | 2797 | -126
[5 empty] | 2019-01-11 | 44 | 262 | 2512 | -132 | 0 | 0 | 2644 | 2021.1047 | 2021.1047 | 2021.1047 | 3072.1352 | 780 | 200 | 4052.1352 | 101.3% | 95% | 100% | -151.0297 | 1870.075 | -2750 | -200 | -1079.925 | 27% | 97.12% | 95% | 100% | 2644 | -132
[5 empty] | 2019-01-11 | 45 | 262.5 | 2339 | -139 | 0 | 0 | 2478 | 1761.0882 | 1761.0882 | 1761.0882 | 3072.1352 | 780 | 200 | 4052.1352 | 101.3% | 95% | 100% | -159.0389 | 1602.0493 | -2750 | -200 | -1347.9507 | 33.7% | 97.1% | 95% | 100% | 2478 | -139
[5 empty] | 2019-01-11 | 46 | 263 | 2208 | -146 | 0 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 3072.1352 | 780 | 200 | 4052.1352 | 101.3% | 95% | 100% | -167.0481 | 1399.811 | -2750 | -200 | -1550.189 | 38.75% | 97.1% | 95% | 100% | 2354 | -146
[5 empty] | 2019-01-11 | 47 | 263.5 | 2038 | -148 | 0 | 0 | 2186 | 1303.7098 | 1303.7098 | 1303.7098 | 3072.1352 | 780 | 200 | 4052.1352 | 101.3% | 95% | 100% | -169.3364 | 1134.3734 | -2750 | -200 | -1815.6266 | 45.39% | 97.08% | 95% | 100% | 2186 | -148
[5 empty] | 2019-01-11 | 48 | 264 | 1932 | -151 | 0 | 0 | 2083 | 1142.3743 | 1142.3743 | 1142.3743 | 3070.5688 | 780 | 200 | 4050.5688 | 101.3% | 95% | 100% | -172.7689 | 969.6054 | -2750 | -200 | -1980.3946 | 49.51% | 97.07% | 95% | 100% | 2083 | -151
[5 empty] | 2019-01-12 | 1 | 264.5 | 1888 | -155 | 0 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 3070.5688 | 780 | 200 | 4050.5688 | 101.3% | 95% | 100% | -177.3455 | 902.3742 | -2750 | -200 | -2047.6258 | 51.19% | 97.06% | 95% | 100% | 2043 | -155
[5 empty] | 2019-01-12 | 2 | 265 | 1868 | -159 | 0 | 0 | 2027 | 1054.6579 | 1054.6579 | 1054.6579 | 3070.5688 | 780 | 200 | 4050.5688 | 101.3% | 95% | 100% | -181.9222 | 872.7357 | -2750 | -200 | -2077.2643 | 51.93% | 97.06% | 95% | 100% | 2027 | -159
[5 empty] | 2019-01-12 | 3 | 265.5 | 1830 | -163 | 0 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 3070.5688 | 780 | 200 | 4050.5688 | 101.3% | 95% | 100% | -186.4989 | 814.9026 | -2750 | -200 | -2135.0974 | 53.38% | 97.05% | 95% | 100% | 1993 | -163
[5 empty] | 2019-01-12 | 4 | 266 | 1762 | -167 | 0 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 3070.5688 | 780 | 200 | 4050.5688 | 101.3% | 95% | 100% | -191.0755 | 710.0786 | -2750 | -200 | -2239.9214 | 56% | 97.04% | 95% | 100% | 1929 | -167
[5 empty] | 2019-01-12 | 5 | 266.5 | 1705 | -171 | 0 | 0 | 1876 | 818.1369 | 818.1369 | 818.1369 | 3070.5688 | 780 | 200 | 4050.5688 | 101.3% | 95% | 100% | -195.6522 | 622.4847 | -2750 | -200 | -2327.5153 | 58.19% | 97.02% | 95% | 100% | 1876 | -171
[5 empty] | 2019-01-12 | 6 | 267 | 1664 | -176 | 0 | 0 | 1840 | 761.7477 | 761.7477 | 761.7477 | 3070.5688 | 780 | 200 | 4050.5688 | 101.3% | 95% | 100% | -201.373 | 560.3747 | -2750 | -200 | -2389.6253 | 59.74% | 97.01% | 95% | 100% | 1840 | -176
[5 empty] | 2019-01-12 | 7 | 267.5 | 1605 | -177 | 0 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 3070.5688 | 780 | 200 | 4050.5688 | 101.3% | 95% | 100% | -202.5172 | 468.3814 | -2750 | -200 | -2481.6186 | 62.04% | 97.01% | 95% | 100% | 1782 | -177
[5 empty] | 2019-01-12 | 8 | 268 | 1553 | -179 | 0 | 0 | 1732 | 592.5804 | 592.5804 | 592.5804 | 3069.0025 | 780 | 200 | 4049.0025 | 101.2% | 95% | 100% | -204.8055 | 387.7749 | -2750 | -200 | -2562.2251 | 64.06% | 97.01% | 95% | 100% | 1732 | -179
[5 empty] | 2019-01-12 | 9 | 268.5 | 1522 | -182 | 0 | 0 | 1704 | 548.7222 | 548.7222 | 548.7222 | 3067.4361 | 780 | 200 | 4047.4361 | 101.2% | 95% | 100% | -208.238 | 340.4842 | -2750 | -200 | -2609.5158 | 65.24% | 97.01% | 95% | 100% | 1704 | -182
[5 empty] | 2019-01-12 | 10 | 269 | 1507 | -184 | 0 | 0 | 1691 | 528.3594 | 528.3594 | 528.3594 | 3067.4361 | 780 | 200 | 4047.4361 | 101.2% | 95% | 100% | -210.5263 | 317.8331 | -2750 | -200 | -2632.1669 | 65.8% | 97% | 95% | 100% | 1691 | -184
[5 empty] | 2019-01-12 | 11 | 269.5 | 1519 | -185 | 0 | 0 | 1704 | 548.7222 | 548.7222 | 548.7222 | 3067.4361 | 780 | 200 | 4047.4361 | 101.2% | 95% | 100% | -211.6705 | 337.0517 | -2750 | -200 | -2612.9483 | 65.32% | 96.99% | 95% | 100% | 1704 | -185
[5 empty] | 2019-01-12 | 12 | 270 | 1541 | -187 | 0 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 3067.4361 | 780 | 200 | 4047.4361 | 101.2% | 95% | 100% | -213.9588 | 372.3561 | -2750 | -200 | -2577.6439 | 64.44% | 96.99% | 95% | 100% | 1728 | -187
[5 empty] | 2019-01-12 | 13 | 270.5 | 1653 | -187 | 0 | 0 | 1840 | 761.7477 | 761.7477 | 761.7477 | 3065.8697 | 780 | 200 | 4045.8697 | 101.1% | 95% | 100% | -213.9588 | 547.7889 | -2750 | -200 | -2402.2111 | 60.06% | 96.98% | 95% | 100% | 1840 | -187
[5 empty] | 2019-01-12 | 14 | 271 | 1740 | -187 | 0 | 0 | 1927 | 898.0214 | 898.0214 | 898.0214 | 3065.8697 | 780 | 200 | 4045.8697 | 101.1% | 95% | 100% | -213.9588 | 684.0626 | -2750 | -200 | -2265.9374 | 56.65% | 96.97% | 95% | 100% | 1927 | -187
[5 empty] | 2019-01-12 | 15 | 271.5 | 1860 | -187 | 0 | 0 | 2047 | 1085.9852 | 1085.9852 | 1085.9852 | 3065.8697 | 780 | 200 | 4045.8697 | 101.1% | 95% | 100% | -213.9588 | 872.0264 | -2750 | -200 | -2077.9736 | 51.95% | 96.95% | 95% | 100% | 2047 | -187
[5 empty] | 2019-01-12 | 16 | 272 | 1964 | -188 | 0 | 0 | 2152 | 1250.4534 | 1250.4534 | 1250.4534 | 3065.8697 | 780 | 200 | 4045.8697 | 101.1% | 95% | 100% | -215.103 | 1035.3504 | -2750 | -200 | -1914.6496 | 47.87% | 96.94% | 95% | 100% | 2152 | -188
[5 empty] | 2019-01-12 | 17 | 272.5 | 2108 | -189 | 0 | 0 | 2297 | 1477.5763 | 1477.5763 | 1477.5763 | 3062.737 | 780 | 200 | 4042.737 | 101.1% | 95% | 100% | -216.2471 | 1261.3291 | -2750 | -200 | -1688.6709 | 42.22% | 96.93% | 95% | 100% | 2297 | -189
[5 empty] | 2019-01-12 | 18 | 273 | 2236 | -194 | 0 | 0 | 2430 | 1685.9027 | 1685.9027 | 1685.9027 | 3062.737 | 780 | 200 | 4042.737 | 101.1% | 95% | 100% | -221.968 | 1463.9348 | -2750 | -200 | -1486.0652 | 37.15% | 96.93% | 95% | 100% | 2430 | -194
[5 empty] | 2019-01-12 | 19 | 273.5 | 2360 | -198 | 0 | 0 | 2558 | 1886.3974 | 1886.3974 | 1886.3974 | 3062.737 | 780 | 200 | 4042.737 | 101.1% | 95% | 100% | -226.5446 | 1659.8527 | -2750 | -200 | -1290.1473 | 32.25% | 96.93% | 95% | 100% | 2558 | -198
[5 empty] | 2019-01-12 | 20 | 274 | 2422 | -203 | 0 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 3062.737 | 780 | 200 | 4042.737 | 101.1% | 95% | 100% | -232.2654 | 1759.0783 | -2750 | -200 | -1190.9217 | 29.77% | 96.93% | 95% | 100% | 2625 | -203
[5 empty] | 2019-01-12 | 21 | 274.5 | 2472 | -212 | 1 | 0 | 2684 | 2083.7593 | 2083.7593 | 2083.7593 | 3062.737 | 780 | 200 | 4042.737 | 101.1% | 95% | 100% | -242.5629 | 1841.1963 | -3550 | -400 | -2108.8037 | 52.72% | 96.93% | 95% | 100% | 2684 | -212
[5 empty] | 2019-01-12 | 22 | 275 | 2479 | -222 | 1 | 0 | 2701 | 2110.3875 | 2110.3875 | 2110.3875 | 3061.1707 | 780 | 200 | 4041.1707 | 101% | 95% | 100% | -254.0046 | 1856.3829 | -3550 | -400 | -2093.6171 | 52.34% | 96.92% | 95% | 100% | 2701 | -222
[5 empty] | 2019-01-12 | 23 | 275.5 | 2483 | -234 | 1 | 0 | 2717 | 2135.4493 | 2135.4493 | 2135.4493 | 3059.6043 | 780 | 200 | 4039.6043 | 101% | 95% | 100% | -267.7346 | 1867.7147 | -3550 | -400 | -2082.2853 | 52.06% | 96.91% | 95% | 100% | 2717 | -234
[5 empty] | 2019-01-12 | 24 | 276 | 2480 | -243 | 1 | 0 | 2723 | 2144.8475 | 2144.8475 | 2144.8475 | 3059.6043 | 780 | 200 | 4039.6043 | 101% | 95% | 100% | -278.032 | 1866.8154 | -3550 | -400 | -2083.1846 | 52.08% | 96.91% | 95% | 100% | 2723 | -243
[5 empty] | 2019-01-12 | 25 | 276.5 | 2477 | -253 | 1 | 0 | 2730 | 2155.812 | 2155.812 | 2155.812 | 3058.0379 | 780 | 200 | 4038.0379 | 101% | 95% | 100% | -289.4737 | 1866.3384 | -3550 | -400 | -2083.6616 | 52.09% | 96.88% | 95% | 100% | 2730 | -253
[5 empty] | 2019-01-12 | 26 | 277 | 2456 | -257 | 1 | 0 | 2713 | 2129.1838 | 2129.1838 | 2129.1838 | 3058.0379 | 780 | 200 | 4038.0379 | 101% | 95% | 100% | -294.0503 | 1835.1335 | -3550 | -400 | -2114.8665 | 52.87% | 96.87% | 95% | 100% | 2713 | -257
[5 empty] | 2019-01-12 | 27 | 277.5 | 2435 | -255 | 1 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 3058.0379 | 780 | 200 | 4038.0379 | 101% | 95% | 100% | -291.762 | 1801.3954 | -3550 | -400 | -2148.6046 | 53.72% | 96.86% | 95% | 100% | 2690 | -255
[5 empty] | 2019-01-12 | 28 | 278 | 2408 | -251 | 1 | 0 | 2659 | 2044.6002 | 2044.6002 | 2044.6002 | 3058.0379 | 780 | 200 | 4038.0379 | 101% | 95% | 100% | -287.1854 | 1757.4148 | -3550 | -400 | -2192.5852 | 54.81% | 96.84% | 95% | 100% | 2659 | -251
[5 empty] | 2019-01-12 | 29 | 278.5 | 2390 | -248 | 1 | 0 | 2638 | 2011.7065 | 2011.7065 | 2011.7065 | 3058.0379 | 780 | 200 | 4038.0379 | 101% | 95% | 100% | -283.7529 | 1727.9537 | -3550 | -400 | -2222.0463 | 55.55% | 96.84% | 95% | 100% | 2638 | -248
[5 empty] | 2019-01-12 | 30 | 279 | 2382 | -238 | 1 | 0 | 2620 | 1983.512 | 1983.512 | 1983.512 | 3056.4716 | 780 | 200 | 4036.4716 | 100.9% | 95% | 100% | -272.3112 | 1711.2007 | -3550 | -400 | -2238.7993 | 55.97% | 96.83% | 95% | 100% | 2620 | -238
[5 empty] | 2019-01-12 | 31 | 279.5 | 2424 | -224 | 1 | 0 | 2648 | 2027.3702 | 2027.3702 | 2027.3702 | 3056.4716 | 780 | 200 | 4036.4716 | 100.9% | 95% | 100% | -256.2929 | 1771.0773 | -3550 | -400 | -2178.9227 | 54.47% | 96.83% | 95% | 100% | 2648 | -224
[5 empty] | 2019-01-12 | 32 | 280 | 2474 | -212 | 1 | 0 | 2686 | 2086.892 | 2086.892 | 2086.892 | 3056.4716 | 780 | 200 | 4036.4716 | 100.9% | 95% | 100% | -242.5629 | 1844.3291 | -3550 | -400 | -2105.6709 | 52.64% | 96.83% | 95% | 100% | 2686 | -212
[5 empty] | 2019-01-12 | 33 | 280.5 | 2578 | -207 | 1 | 0 | 2785 | 2241.9621 | 2241.9621 | 2241.9621 | 3056.4716 | 780 | 200 | 4036.4716 | 100.9% | 95% | 100% | -236.8421 | 2005.12 | -3550 | -400 | -1944.88 | 48.62% | 96.83% | 95% | 100% | 2785 | -207
[5 empty] | 2019-01-12 | 34 | 281 | 2696 | -207 | 0 | 0 | 2903 | 2426.7931 | 2426.7931 | 2426.7931 | 3054.9052 | 780 | 200 | 4034.9052 | 100.9% | 95% | 100% | -236.8421 | 2189.951 | -2750 | -200 | -760.049 | 19% | 96.82% | 95% | 100% | 2903 | -207
[5 empty] | 2019-01-12 | 35 | 281.5 | 2764 | -208 | 0 | 0 | 2972 | 2534.8722 | 2534.8722 | 2534.8722 | 3054.9052 | 780 | 200 | 4034.9052 | 100.9% | 95% | 100% | -237.9863 | 2296.8859 | -2750 | -200 | -653.1141 | 16.33% | 96.8% | 95% | 100% | 2972 | -208
[5 empty] | 2019-01-12 | 36 | 282 | 2786 | -210 | 0 | 0 | 2996 | 2572.465 | 2572.465 | 2572.465 | 3054.9052 | 780 | 200 | 4034.9052 | 100.9% | 95% | 100% | -240.2746 | 2332.1904 | -2750 | -200 | -617.8096 | 15.45% | 96.8% | 95% | 100% | 2996 | -210
[5 empty] | 2019-01-12 | 37 | 282.5 | 2771 | -212 | 0 | 0 | 2983 | 2552.1022 | 2552.1022 | 2552.1022 | 3054.9052 | 780 | 200 | 4034.9052 | 100.9% | 95% | 100% | -242.5629 | 2309.5393 | -2750 | -200 | -640.4607 | 16.01% | 96.8% | 95% | 100% | 2983 | -212
[5 empty] | 2019-01-12 | 38 | 283 | 2722 | -215 | 0 | 0 | 2937 | 2480.0495 | 2480.0495 | 2480.0495 | 3053.3388 | 780 | 200 | 4033.3388 | 100.8% | 95% | 100% | -245.9954 | 2234.054 | -2750 | -200 | -715.946 | 17.9% | 96.79% | 95% | 100% | 2937 | -215
[5 empty] | 2019-01-12 | 39 | 283.5 | 2621 | -216 | 0 | 0 | 2837 | 2323.413 | 2323.413 | 2323.413 | 3053.3388 | 780 | 200 | 4033.3388 | 100.8% | 95% | 100% | -247.1396 | 2076.2734 | -2750 | -200 | -873.7266 | 21.84% | 96.79% | 95% | 100% | 2837 | -216
[5 empty] | 2019-01-12 | 40 | 284 | 2503 | -218 | 0 | 0 | 2721 | 2141.7148 | 2141.7148 | 2141.7148 | 3051.7725 | 780 | 200 | 4031.7725 | 100.8% | 95% | 100% | -249.4279 | 1892.2868 | -2750 | -200 | -1057.7132 | 26.44% | 96.78% | 95% | 100% | 2721 | -218
[5 empty] | 2019-01-12 | 41 | 284.5 | 2401 | -219 | 0 | 0 | 2620 | 1983.512 | 1983.512 | 1983.512 | 3051.7725 | 780 | 200 | 4031.7725 | 100.8% | 95% | 100% | -250.5721 | 1732.9399 | -2750 | -200 | -1217.0601 | 30.43% | 96.78% | 95% | 100% | 2620 | -219
[5 empty] | 2019-01-12 | 42 | 285 | 2294 | -219 | 0 | 0 | 2513 | 1815.911 | 1815.911 | 1815.911 | 3050.2061 | 780 | 200 | 4030.2061 | 100.8% | 95% | 100% | -250.5721 | 1565.3389 | -2750 | -200 | -1384.6611 | 34.62% | 96.77% | 95% | 100% | 2513 | -219
[5 empty] | 2019-01-12 | 43 | 285.5 | 2184 | -220 | 0 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 3050.2061 | 780 | 200 | 4030.2061 | 100.8% | 95% | 100% | -251.7162 | 1393.461 | -2750 | -200 | -1556.539 | 38.91% | 96.77% | 95% | 100% | 2404 | -220
[5 empty] | 2019-01-12 | 44 | 286 | 2079 | -220 | 0 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 3050.2061 | 780 | 200 | 4030.2061 | 100.8% | 95% | 100% | -251.7162 | 1228.9927 | -2750 | -200 | -1721.0073 | 43.03% | 96.77% | 95% | 100% | 2299 | -220
[5 empty] | 2019-01-12 | 45 | 286.5 | 1947 | -223 | 0 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 3048.6397 | 780 | 200 | 4028.6397 | 100.7% | 95% | 100% | -255.1487 | 1023.4992 | -2750 | -200 | -1926.5008 | 48.16% | 96.77% | 95% | 100% | 2170 | -223
[5 empty] | 2019-01-12 | 46 | 287 | 1855 | -225 | 0 | 0 | 2080 | 1137.6752 | 1137.6752 | 1137.6752 | 3048.6397 | 780 | 200 | 4028.6397 | 100.7% | 95% | 100% | -257.4371 | 880.2381 | -2750 | -200 | -2069.7619 | 51.74% | 96.74% | 95% | 100% | 2080 | -225
[5 empty] | 2019-01-12 | 47 | 287.5 | 1723 | -229 | 0 | 0 | 1952 | 937.1805 | 937.1805 | 937.1805 | 3048.6397 | 780 | 200 | 4028.6397 | 100.7% | 95% | 100% | -262.0137 | 675.1668 | -2750 | -200 | -2274.8332 | 56.87% | 96.7% | 95% | 100% | 1952 | -229
[5 empty] | 2019-01-12 | 48 | 288 | 1638 | -233 | 0 | 0 | 1871 | 810.305 | 810.305 | 810.305 | 3047.0734 | 780 | 200 | 4027.0734 | 100.7% | 95% | 100% | -266.5904 | 543.7146 | -2750 | -200 | -2406.2854 | 60.16% | 96.7% | 95% | 100% | 1871 | -233
[5 empty] | 2019-01-13 | 1 | 288.5 | 1601 | -236 | 0 | 0 | 1837 | 757.0486 | 757.0486 | 757.0486 | 3047.0734 | 780 | 200 | 4027.0734 | 100.7% | 95% | 100% | -270.0229 | 487.0258 | -2750 | -200 | -2462.9742 | 61.57% | 96.7% | 95% | 100% | 1837 | -236
[5 empty] | 2019-01-13 | 2 | 289 | 1613 | -239 | 0 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 3047.0734 | 780 | 200 | 4027.0734 | 100.7% | 95% | 100% | -273.4554 | 507.0887 | -2750 | -200 | -2442.9113 | 61.07% | 96.69% | 95% | 100% | 1852 | -239
[5 empty] | 2019-01-13 | 3 | 289.5 | 1568 | -242 | 0 | 0 | 1810 | 714.7568 | 714.7568 | 714.7568 | 3047.0734 | 780 | 200 | 4027.0734 | 100.7% | 95% | 100% | -276.8879 | 437.8689 | -2750 | -200 | -2512.1311 | 62.8% | 96.67% | 95% | 100% | 1810 | -242
[5 empty] | 2019-01-13 | 4 | 290 | 1491 | -244 | 0 | 0 | 1735 | 597.2795 | 597.2795 | 597.2795 | 3045.507 | 780 | 200 | 4025.507 | 100.6% | 95% | 100% | -279.1762 | 318.1033 | -2750 | -200 | -2631.8967 | 65.8% | 96.67% | 95% | 100% | 1735 | -244
[5 empty] | 2019-01-13 | 5 | 290.5 | 1435 | -245 | 0 | 0 | 1680 | 511.1294 | 511.1294 | 511.1294 | 3045.507 | 780 | 200 | 4025.507 | 100.6% | 95% | 100% | -280.3204 | 230.8091 | -2750 | -200 | -2719.1909 | 67.98% | 96.66% | 95% | 100% | 1680 | -245
[5 empty] | 2019-01-13 | 6 | 291 | 1401 | -245 | 0 | 0 | 1646 | 457.873 | 457.873 | 457.873 | 3045.507 | 780 | 200 | 4025.507 | 100.6% | 95% | 100% | -280.3204 | 177.5527 | -2750 | -200 | -2772.4473 | 69.31% | 96.66% | 95% | 100% | 1646 | -245
[5 empty] | 2019-01-13 | 7 | 291.5 | 1362 | -246 | 0 | 0 | 1608 | 398.3512 | 398.3512 | 398.3512 | 3043.9406 | 780 | 200 | 4023.9406 | 100.6% | 95% | 100% | -281.4645 | 116.8867 | -2750 | -200 | -2833.1133 | 70.83% | 96.64% | 95% | 100% | 1608 | -246
[5 empty] | 2019-01-13 | 8 | 292 | 1325 | -247 | 0 | 0 | 1572 | 341.9621 | 341.9621 | 341.9621 | 3043.9406 | 780 | 200 | 4023.9406 | 100.6% | 95% | 100% | -282.6087 | 59.3534 | -2750 | -200 | -2890.6466 | 72.27% | 96.64% | 95% | 100% | 1572 | -247
[5 empty] | 2019-01-13 | 9 | 292.5 | 1294 | -245 | 0 | 0 | 1539 | 290.2721 | 290.2721 | 290.2721 | 3043.9406 | 780 | 200 | 4023.9406 | 100.6% | 95% | 100% | -280.3204 | 9.9517 | -2750 | -200 | -2940.0483 | 73.5% | 96.63% | 95% | 100% | 1539 | -245
[5 empty] | 2019-01-13 | 10 | 293 | 1277 | -244 | 0 | 0 | 1521 | 262.0775 | 262.0775 | 262.0775 | 3043.9406 | 780 | 200 | 4023.9406 | 100.6% | 95% | 100% | -279.1762 | -17.0987 | -2750 | -200 | -2967.0987 | 74.18% | 96.62% | 95% | 100% | 1521 | -244
[5 empty] | 2019-01-13 | 11 | 293.5 | 1278 | -244 | 0 | 0 | 1522 | 263.6439 | 263.6439 | 263.6439 | 3042.3743 | 780 | 200 | 4022.3743 | 100.6% | 95% | 100% | -279.1762 | -15.5323 | -2750 | -200 | -2965.5323 | 74.14% | 96.61% | 95% | 100% | 1522 | -244
[5 empty] | 2019-01-13 | 12 | 294 | 1295 | -243 | 0 | 0 | 1538 | 288.7057 | 288.7057 | 288.7057 | 3042.3743 | 780 | 200 | 4022.3743 | 100.6% | 95% | 100% | -278.032 | 10.6737 | -2750 | -200 | -2939.3263 | 73.48% | 96.6% | 95% | 100% | 1538 | -243
[5 empty] | 2019-01-13 | 13 | 294.5 | 1361 | -243 | 0 | 0 | 1604 | 392.0857 | 392.0857 | 392.0857 | 3042.3743 | 780 | 200 | 4022.3743 | 100.6% | 95% | 100% | -278.032 | 114.0537 | -2750 | -200 | -2835.9463 | 70.9% | 96.6% | 95% | 100% | 1604 | -243
[5 empty] | 2019-01-13 | 14 | 295 | 1408 | -244 | 0 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 3040.8079 | 780 | 200 | 4020.8079 | 100.5% | 95% | 100% | -279.1762 | 188.095 | -2750 | -200 | -2761.905 | 69.05% | 96.57% | 95% | 100% | 1652 | -244
[5 empty] | 2019-01-13 | 15 | 295.5 | 1498 | -243 | 0 | 0 | 1741 | 606.6777 | 606.6777 | 606.6777 | 3040.8079 | 780 | 200 | 4020.8079 | 100.5% | 95% | 100% | -278.032 | 328.6456 | -2750 | -200 | -2621.3544 | 65.53% | 96.56% | 95% | 100% | 1741 | -243
[5 empty] | 2019-01-13 | 16 | 296 | 1565 | -242 | 0 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 3040.8079 | 780 | 200 | 4020.8079 | 100.5% | 95% | 100% | -276.8879 | 433.1698 | -2750 | -200 | -2516.8302 | 62.92% | 96.53% | 95% | 100% | 1807 | -242
[5 empty] | 2019-01-13 | 17 | 296.5 | 1691 | -239 | 0 | 0 | 1930 | 902.7205 | 902.7205 | 902.7205 | 3040.8079 | 780 | 200 | 4020.8079 | 100.5% | 95% | 100% | -273.4554 | 629.2652 | -2750 | -200 | -2320.7348 | 58.02% | 96.53% | 95% | 100% | 1930 | -239
[5 empty] | 2019-01-13 | 18 | 297 | 1825 | -238 | 0 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 3040.8079 | 780 | 200 | 4020.8079 | 100.5% | 95% | 100% | -272.3112 | 838.7358 | -2750 | -200 | -2111.2642 | 52.78% | 96.53% | 95% | 100% | 2063 | -238
[5 empty] | 2019-01-13 | 19 | 297.5 | 1952 | -254 | 0 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 3040.8079 | 780 | 200 | 4020.8079 | 100.5% | 95% | 100% | -290.6178 | 1044.4192 | -2750 | -200 | -1905.5808 | 47.64% | 96.51% | 95% | 100% | 2206 | -254
[5 empty] | 2019-01-13 | 20 | 298 | 2023 | -273 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 3040.8079 | 780 | 200 | 4020.8079 | 100.5% | 95% | 100% | -312.357 | 1163.6529 | -3550 | -400 | -2786.3471 | 69.66% | 96.51% | 95% | 100% | 2296 | -273
[5 empty] | 2019-01-13 | 21 | 298.5 | 2095 | -292 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 3039.2415 | 780 | 200 | 4019.2415 | 100.5% | 95% | 100% | -334.0961 | 1284.4529 | -3550 | -400 | -2665.5471 | 66.64% | 96.5% | 95% | 100% | 2387 | -292
[5 empty] | 2019-01-13 | 22 | 299 | 2100 | -318 | 1 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 3039.2415 | 780 | 200 | 4019.2415 | 100.5% | 95% | 100% | -363.8444 | 1303.262 | -3550 | -400 | -2646.738 | 66.17% | 96.5% | 95% | 100% | 2418 | -318
[5 empty] | 2019-01-13 | 23 | 299.5 | 2107 | -340 | 1 | 0 | 2447 | 1712.5309 | 1712.5309 | 1712.5309 | 3039.2415 | 780 | 200 | 4019.2415 | 100.5% | 95% | 100% | -389.016 | 1323.5149 | -3550 | -400 | -2626.4851 | 65.66% | 96.49% | 95% | 100% | 2447 | -340
[5 empty] | 2019-01-13 | 24 | 300 | 2116 | -358 | 1 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 3036.1088 | 780 | 200 | 4016.1088 | 100.4% | 95% | 100% | -409.611 | 1345.2118 | -3550 | -400 | -2604.7882 | 65.12% | 96.49% | 95% | 100% | 2474 | -358
[5 empty] | 2019-01-13 | 25 | 300.5 | 2132 | -366 | 1 | 0 | 2498 | 1792.4155 | 1792.4155 | 1792.4155 | 3036.1088 | 780 | 200 | 4016.1088 | 100.4% | 95% | 100% | -418.7643 | 1373.6512 | -3550 | -400 | -2576.3488 | 64.41% | 96.49% | 95% | 100% | 2498 | -366
[5 empty] | 2019-01-13 | 26 | 301 | 2153 | -360 | 1 | 0 | 2513 | 1815.911 | 1815.911 | 1815.911 | 3036.1088 | 780 | 200 | 4016.1088 | 100.4% | 95% | 100% | -411.8993 | 1404.0117 | -3550 | -400 | -2545.9883 | 63.65% | 96.49% | 95% | 100% | 2513 | -360
[5 empty] | 2019-01-13 | 27 | 301.5 | 2172 | -346 | 1 | 0 | 2518 | 1823.7428 | 1823.7428 | 1823.7428 | 3034.5425 | 780 | 200 | 4014.5425 | 100.4% | 95% | 100% | -395.881 | 1427.8618 | -3550 | -400 | -2522.1382 | 63.05% | 96.48% | 95% | 100% | 2518 | -346
[5 empty] | 2019-01-13 | 28 | 302 | 2173 | -331 | 1 | 0 | 2504 | 1801.8137 | 1801.8137 | 1801.8137 | 3034.5425 | 780 | 200 | 4014.5425 | 100.4% | 95% | 100% | -378.7185 | 1423.0951 | -3550 | -400 | -2526.9049 | 63.17% | 96.48% | 95% | 100% | 2504 | -331
[5 empty] | 2019-01-13 | 29 | 302.5 | 2229 | -301 | 1 | 0 | 2530 | 1842.5392 | 1842.5392 | 1842.5392 | 3034.5425 | 780 | 200 | 4014.5425 | 100.4% | 95% | 100% | -344.3936 | 1498.1456 | -3550 | -400 | -2451.8544 | 61.3% | 96.48% | 95% | 100% | 2530 | -301
[5 empty] | 2019-01-13 | 30 | 303 | 2267 | -273 | 1 | 0 | 2540 | 1858.2028 | 1858.2028 | 1858.2028 | 3032.9761 | 780 | 200 | 4012.9761 | 100.3% | 95% | 100% | -312.357 | 1545.8458 | -3550 | -400 | -2404.1542 | 60.1% | 96.47% | 95% | 100% | 2540 | -273
[5 empty] | 2019-01-13 | 31 | 303.5 | 2320 | -257 | 1 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 3032.9761 | 780 | 200 | 4012.9761 | 100.3% | 95% | 100% | -294.0503 | 1622.1079 | -3550 | -400 | -2327.8921 | 58.2% | 96.47% | 95% | 100% | 2577 | -257
[5 empty] | 2019-01-13 | 32 | 304 | 2394 | -245 | 1 | 0 | 2639 | 2013.2729 | 2013.2729 | 2013.2729 | 3031.4097 | 780 | 200 | 4011.4097 | 100.3% | 95% | 100% | -280.3204 | 1732.9525 | -3550 | -400 | -2217.0475 | 55.43% | 96.47% | 95% | 100% | 2639 | -245
[5 empty] | 2019-01-13 | 33 | 304.5 | 2509 | -241 | 1 | 0 | 2750 | 2187.1393 | 2187.1393 | 2187.1393 | 3031.4097 | 780 | 200 | 4011.4097 | 100.3% | 95% | 100% | -275.7437 | 1911.3956 | -3550 | -400 | -2038.6044 | 50.97% | 96.46% | 95% | 100% | 2750 | -241
[5 empty] | 2019-01-13 | 34 | 305 | 2690 | -240 | 1 | 0 | 2930 | 2469.0849 | 2469.0849 | 2469.0849 | 3031.4097 | 780 | 200 | 4011.4097 | 100.3% | 95% | 100% | -274.5995 | 2194.4854 | -3550 | -400 | -1755.5146 | 43.89% | 96.45% | 95% | 100% | 2930 | -240
[5 empty] | 2019-01-13 | 35 | 305.5 | 2739 | -238 | 0 | 0 | 2977 | 2542.704 | 2542.704 | 2542.704 | 3031.4097 | 780 | 200 | 4011.4097 | 100.3% | 95% | 100% | -272.3112 | 2270.3928 | -2750 | -200 | -679.6072 | 16.99% | 96.44% | 95% | 100% | 2977 | -238
[5 empty] | 2019-01-13 | 36 | 306 | 2749 | -235 | 0 | 0 | 2984 | 2553.6686 | 2553.6686 | 2553.6686 | 3031.4097 | 780 | 200 | 4011.4097 | 100.3% | 95% | 100% | -268.8787 | 2284.7899 | -2750 | -200 | -665.2101 | 16.63% | 96.43% | 95% | 100% | 2984 | -235
[5 empty] | 2019-01-13 | 37 | 306.5 | 2696 | -230 | 0 | 0 | 2926 | 2462.8195 | 2462.8195 | 2462.8195 | 3031.4097 | 780 | 200 | 4011.4097 | 100.3% | 95% | 100% | -263.1579 | 2199.6616 | -2750 | -200 | -750.3384 | 18.76% | 96.42% | 95% | 100% | 2926 | -230
[5 empty] | 2019-01-13 | 38 | 307 | 2635 | -225 | 0 | 0 | 2860 | 2359.4394 | 2359.4394 | 2359.4394 | 3029.8434 | 780 | 200 | 4009.8434 | 100.2% | 95% | 100% | -257.4371 | 2102.0023 | -2750 | -200 | -847.9977 | 21.2% | 96.42% | 95% | 100% | 2860 | -225
[5 empty] | 2019-01-13 | 39 | 307.5 | 2581 | -221 | 0 | 0 | 2802 | 2268.5903 | 2268.5903 | 2268.5903 | 3029.8434 | 780 | 200 | 4009.8434 | 100.2% | 95% | 100% | -252.8604 | 2015.7299 | -2750 | -200 | -934.2701 | 23.36% | 96.42% | 95% | 100% | 2802 | -221
[5 empty] | 2019-01-13 | 40 | 308 | 2505 | -218 | 0 | 0 | 2723 | 2144.8475 | 2144.8475 | 2144.8475 | 3029.8434 | 780 | 200 | 4009.8434 | 100.2% | 95% | 100% | -249.4279 | 1895.4196 | -2750 | -200 | -1054.5804 | 26.36% | 96.39% | 95% | 100% | 2723 | -218
[5 empty] | 2019-01-13 | 41 | 308.5 | 2422 | -215 | 0 | 0 | 2637 | 2010.1401 | 2010.1401 | 2010.1401 | 3029.8434 | 780 | 200 | 4009.8434 | 100.2% | 95% | 100% | -245.9954 | 1764.1447 | -2750 | -200 | -1185.8553 | 29.65% | 96.39% | 95% | 100% | 2637 | -215
[5 empty] | 2019-01-13 | 42 | 309 | 2312 | -211 | 0 | 0 | 2523 | 1831.5746 | 1831.5746 | 1831.5746 | 3028.277 | 780 | 200 | 4008.277 | 100.2% | 95% | 100% | -241.4188 | 1590.1558 | -2750 | -200 | -1359.8442 | 34% | 96.37% | 95% | 100% | 2523 | -211
[5 empty] | 2019-01-13 | 43 | 309.5 | 2218 | -206 | 0 | 0 | 2424 | 1676.5045 | 1676.5045 | 1676.5045 | 3028.277 | 780 | 200 | 4008.277 | 100.2% | 95% | 100% | -235.6979 | 1440.8066 | -2750 | -200 | -1509.1934 | 37.73% | 96.36% | 95% | 100% | 2424 | -206
[5 empty] | 2019-01-13 | 44 | 310 | 2092 | -200 | 0 | 0 | 2292 | 1469.7444 | 1469.7444 | 1469.7444 | 3028.277 | 780 | 200 | 4008.277 | 100.2% | 95% | 100% | -228.833 | 1240.9115 | -2750 | -200 | -1709.0885 | 42.73% | 96.35% | 95% | 100% | 2292 | -200
[5 empty] | 2019-01-13 | 45 | 310.5 | 1964 | -193 | 1 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 3026.7106 | 780 | 200 | 4006.7106 | 100.2% | 95% | 100% | -220.8238 | 1037.4614 | -3550 | -400 | -2912.5386 | 72.81% | 96.32% | 95% | 100% | 2157 | -193
[5 empty] | 2019-01-13 | 46 | 311 | 1856 | -187 | 1 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 3025.1443 | 780 | 200 | 4005.1443 | 100.1% | 95% | 100% | -213.9588 | 865.7609 | -3550 | -400 | -3084.2391 | 77.11% | 96.28% | 95% | 100% | 2043 | -187
[5 empty] | 2019-01-13 | 47 | 311.5 | 1757 | -177 | 1 | 0 | 1934 | 908.986 | 908.986 | 908.986 | 3025.1443 | 780 | 200 | 4005.1443 | 100.1% | 95% | 100% | -202.5172 | 706.4688 | -3550 | -400 | -3243.5312 | 81.09% | 96.25% | 95% | 100% | 1934 | -177
[5 empty] | 2019-01-13 | 48 | 312 | 1692 | -167 | 1 | 0 | 1859 | 791.5087 | 791.5087 | 791.5087 | 3025.1443 | 780 | 200 | 4005.1443 | 100.1% | 95% | 100% | -191.0755 | 600.4331 | -3550 | -400 | -3349.5669 | 83.74% | 96.25% | 95% | 100% | 1859 | -167
[5 empty] | 2019-01-14 | 1 | 312.5 | 1688 | -162 | 1 | 0 | 1850 | 777.4114 | 777.4114 | 777.4114 | 3023.5779 | 780 | 200 | 4003.5779 | 100.1% | 95% | 100% | -185.3547 | 592.0567 | -3550 | -400 | -3357.9433 | 83.95% | 96.24% | 95% | 100% | 1850 | -162
[5 empty] | 2019-01-14 | 2 | 313 | 1744 | -157 | 1 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 3023.5779 | 780 | 200 | 4003.5779 | 100.1% | 95% | 100% | -179.6339 | 677.6621 | -3550 | -400 | -3272.3379 | 81.81% | 96.24% | 95% | 100% | 1901 | -157
[5 empty] | 2019-01-14 | 3 | 313.5 | 1741 | -153 | 1 | 0 | 1894 | 846.3314 | 846.3314 | 846.3314 | 3023.5779 | 780 | 200 | 4003.5779 | 100.1% | 95% | 100% | -175.0572 | 671.2742 | -3550 | -400 | -3278.7258 | 81.97% | 96.24% | 95% | 100% | 1894 | -153
[5 empty] | 2019-01-14 | 4 | 314 | 1714 | -149 | 1 | 0 | 1863 | 797.7741 | 797.7741 | 797.7741 | 3023.5779 | 780 | 200 | 4003.5779 | 100.1% | 95% | 100% | -170.4805 | 627.2936 | -3550 | -400 | -3322.7064 | 83.07% | 96.23% | 95% | 100% | 1863 | -149
[5 empty] | 2019-01-14 | 5 | 314.5 | 1693 | -145 | 1 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 3023.5779 | 780 | 200 | 4003.5779 | 100.1% | 95% | 100% | -165.9039 | 592.7111 | -3550 | -400 | -3357.2889 | 83.93% | 96.22% | 95% | 100% | 1838 | -145
[5 empty] | 2019-01-14 | 6 | 315 | 1680 | -142 | 1 | 0 | 1822 | 733.5532 | 733.5532 | 733.5532 | 3022.0115 | 780 | 200 | 4002.0115 | 100.1% | 95% | 100% | -162.4714 | 571.0818 | -3550 | -400 | -3378.9182 | 84.47% | 96.2% | 95% | 100% | 1822 | -142
[5 empty] | 2019-01-14 | 7 | 315.5 | 1664 | -137 | 1 | 0 | 1801 | 700.6595 | 700.6595 | 700.6595 | 3022.0115 | 780 | 200 | 4002.0115 | 100.1% | 95% | 100% | -156.7506 | 543.9089 | -3550 | -400 | -3406.0911 | 85.15% | 96.17% | 95% | 100% | 1801 | -137
[5 empty] | 2019-01-14 | 8 | 316 | 1653 | -132 | 1 | 0 | 1785 | 675.5977 | 675.5977 | 675.5977 | 3022.0115 | 780 | 200 | 4002.0115 | 100.1% | 95% | 100% | -151.0297 | 524.5679 | -3550 | -400 | -3425.4321 | 85.64% | 96.17% | 95% | 100% | 1785 | -132
[5 empty] | 2019-01-14 | 9 | 316.5 | 1654 | -126 | 1 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 3022.0115 | 780 | 200 | 4002.0115 | 100.1% | 95% | 100% | -144.1648 | 523.6011 | -3550 | -400 | -3426.3989 | 85.66% | 96.14% | 95% | 100% | 1780 | -126
[5 empty] | 2019-01-14 | 10 | 317 | 1684 | -120 | 1 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 3020.4452 | 780 | 200 | 4000.4452 | 100% | 95% | 100% | -137.2998 | 568.0588 | -3550 | -400 | -3381.9412 | 84.55% | 96.14% | 95% | 100% | 1804 | -120
[5 empty] | 2019-01-14 | 11 | 317.5 | 1771 | -114 | 1 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 3020.4452 | 780 | 200 | 4000.4452 | 100% | 95% | 100% | -130.4348 | 701.7993 | -3550 | -400 | -3248.2007 | 81.21% | 96.14% | 95% | 100% | 1885 | -114
[5 empty] | 2019-01-14 | 12 | 318 | 1899 | -108 | 1 | 0 | 2007 | 1023.3306 | 1023.3306 | 1023.3306 | 3020.4452 | 780 | 200 | 4000.4452 | 100% | 95% | 100% | -123.5698 | 899.7608 | -3550 | -400 | -3050.2392 | 76.26% | 96.14% | 95% | 100% | 2007 | -108
[5 empty] | 2019-01-14 | 13 | 318.5 | 2167 | -104 | 1 | 0 | 2271 | 1436.8508 | 1436.8508 | 1436.8508 | 3018.8788 | 780 | 200 | 3998.8788 | 99.97% | 95% | 100% | -118.9931 | 1317.8576 | -3550 | -400 | -2632.1424 | 65.8% | 96.13% | 95% | 100% | 2271 | -104
[5 empty] | 2019-01-14 | 14 | 319 | 2457 | -101 | 1 | 0 | 2558 | 1886.3974 | 1886.3974 | 1886.3974 | 3018.8788 | 780 | 200 | 3998.8788 | 99.97% | 95% | 100% | -115.5606 | 1770.8367 | -3550 | -400 | -2179.1633 | 54.48% | 96.12% | 95% | 100% | 2558 | -101
[5 empty] | 2019-01-14 | 15 | 319.5 | 2783 | -97 | 1 | 0 | 2880 | 2390.7667 | 2390.7667 | 2390.7667 | 3018.8788 | 780 | 200 | 3998.8788 | 99.97% | 95% | 100% | -110.984 | 2279.7827 | -3550 | -400 | -1670.2173 | 41.76% | 96.12% | 95% | 100% | 2880 | -97
[5 empty] | 2019-01-14 | 16 | 320 | 2955 | -94 | 1 | 0 | 3049 | 2655.4823 | 2655.4823 | 2655.4823 | 3018.8788 | 780 | 200 | 3998.8788 | 99.97% | 95% | 100% | -107.5515 | 2547.9308 | -3550 | -400 | -1402.0692 | 35.05% | 96.1% | 95% | 100% | 3049 | -94
[5 empty] | 2019-01-14 | 17 | 320.5 | 3043 | -92 | 1 | 0 | 3135 | 2790.1896 | 2790.1896 | 2790.1896 | 3015.7461 | 780 | 200 | 3995.7461 | 99.89% | 95% | 100% | -105.2632 | 2684.9265 | -3550 | -400 | -1265.0735 | 31.63% | 96.1% | 95% | 100% | 3135 | -92
[5 empty] | 2019-01-14 | 18 | 321 | 3033 | -105 | 1 | 0 | 3138 | 2794.8887 | 2794.8887 | 2794.8887 | 3015.7461 | 780 | 200 | 3995.7461 | 99.89% | 95% | 100% | -120.1373 | 2674.7514 | -3550 | -400 | -1275.2486 | 31.88% | 96.1% | 95% | 100% | 3138 | -105
[5 empty] | 2019-01-14 | 19 | 321.5 | 3033 | -137 | 1 | 0 | 3170 | 2845.0124 | 2845.0124 | 2845.0124 | 3015.7461 | 780 | 200 | 3995.7461 | 99.89% | 95% | 100% | -156.7506 | 2688.2618 | -3550 | -400 | -1261.7382 | 31.54% | 96.08% | 95% | 100% | 3170 | -137
[5 empty] | 2019-01-14 | 20 | 322 | 2968 | -172 | 1 | 0 | 3140 | 2798.0214 | 2798.0214 | 2798.0214 | 3015.7461 | 780 | 200 | 3995.7461 | 99.89% | 95% | 100% | -196.7963 | 2601.2251 | -3550 | -400 | -1348.7749 | 33.72% | 96.07% | 95% | 100% | 3140 | -172
[5 empty] | 2019-01-14 | 21 | 322.5 | 2944 | -195 | 1 | 0 | 3139 | 2796.4551 | 2796.4551 | 2796.4551 | 3015.7461 | 780 | 200 | 3995.7461 | 99.89% | 95% | 100% | -223.1121 | 2573.3429 | -3550 | -400 | -1376.6571 | 34.42% | 96.06% | 95% | 100% | 3139 | -195
[5 empty] | 2019-01-14 | 22 | 323 | 2898 | -212 | 1 | 0 | 3110 | 2751.0305 | 2751.0305 | 2751.0305 | 3015.7461 | 780 | 200 | 3995.7461 | 99.89% | 95% | 100% | -242.5629 | 2508.4676 | -3550 | -400 | -1441.5324 | 36.04% | 96.01% | 95% | 100% | 3110 | -212
[5 empty] | 2019-01-14 | 23 | 323.5 | 2884 | -213 | 1 | 0 | 3097 | 2730.6678 | 2730.6678 | 2730.6678 | 3014.1797 | 780 | 200 | 3994.1797 | 99.85% | 95% | 100% | -243.7071 | 2486.9607 | -3550 | -400 | -1463.0393 | 36.58% | 96% | 95% | 100% | 3097 | -213
[5 empty] | 2019-01-14 | 24 | 324 | 2897 | -211 | 1 | 0 | 3108 | 2747.8978 | 2747.8978 | 2747.8978 | 3014.1797 | 780 | 200 | 3994.1797 | 99.85% | 95% | 100% | -241.4188 | 2506.479 | -3550 | -400 | -1443.521 | 36.09% | 96% | 95% | 100% | 3108 | -211
[5 empty] | 2019-01-14 | 25 | 324.5 | 2911 | -215 | 1 | 0 | 3126 | 2776.0923 | 2776.0923 | 2776.0923 | 3014.1797 | 780 | 200 | 3994.1797 | 99.85% | 95% | 100% | -245.9954 | 2530.0969 | -3550 | -400 | -1419.9031 | 35.5% | 95.97% | 95% | 100% | 3126 | -215
[5 empty] | 2019-01-14 | 26 | 325 | 2916 | -213 | 1 | 0 | 3129 | 2780.7914 | 2780.7914 | 2780.7914 | 3012.6134 | 780 | 200 | 3992.6134 | 99.82% | 95% | 100% | -243.7071 | 2537.0843 | -3550 | -400 | -1412.9157 | 35.32% | 95.96% | 95% | 100% | 3129 | -213
[5 empty] | 2019-01-14 | 27 | 325.5 | 2932 | -203 | 1 | 0 | 3135 | 2790.1896 | 2790.1896 | 2790.1896 | 3011.047 | 780 | 200 | 3991.047 | 99.78% | 95% | 100% | -232.2654 | 2557.9242 | -3550 | -400 | -1392.0758 | 34.8% | 95.96% | 95% | 100% | 3135 | -203
[5 empty] | 2019-01-14 | 28 | 326 | 2960 | -183 | 1 | 0 | 3143 | 2802.7205 | 2802.7205 | 2802.7205 | 3011.047 | 780 | 200 | 3991.047 | 99.78% | 95% | 100% | -209.3822 | 2593.3384 | -3550 | -400 | -1356.6616 | 33.92% | 95.96% | 95% | 100% | 3143 | -183
[5 empty] | 2019-01-14 | 29 | 326.5 | 2997 | -158 | 1 | 0 | 3155 | 2821.5169 | 2821.5169 | 2821.5169 | 3011.047 | 780 | 200 | 3991.047 | 99.78% | 95% | 100% | -180.778 | 2640.7389 | -3550 | -400 | -1309.2611 | 32.73% | 95.96% | 95% | 100% | 3155 | -158
[5 empty] | 2019-01-14 | 30 | 327 | 3034 | -135 | 1 | 0 | 3169 | 2843.446 | 2843.446 | 2843.446 | 3009.4806 | 780 | 200 | 3989.4806 | 99.74% | 95% | 100% | -154.4622 | 2688.9838 | -3550 | -400 | -1261.0162 | 31.53% | 95.96% | 95% | 100% | 3169 | -135
[5 empty] | 2019-01-14 | 31 | 327.5 | 3076 | -114 | 1 | 0 | 3190 | 2876.3397 | 2876.3397 | 2876.3397 | 3009.4806 | 780 | 200 | 3989.4806 | 99.74% | 95% | 100% | -130.4348 | 2745.9049 | -3550 | -400 | -1204.0951 | 30.1% | 95.95% | 95% | 100% | 3190 | -114
[5 empty] | 2019-01-14 | 32 | 328 | 3123 | -97 | 1 | 0 | 3220 | 2923.3306 | 2923.3306 | 2923.3306 | 3009.4806 | 780 | 200 | 3989.4806 | 99.74% | 95% | 100% | -110.984 | 2812.3466 | -3550 | -400 | -1137.6534 | 28.44% | 95.95% | 95% | 100% | 3220 | -97
[5 empty] | 2019-01-14 | 33 | 328.5 | 3230 | -91 | 1 | 0 | 3321 | 3081.5334 | 3081.5334 | 3081.5334 | 3007.9143 | 780 | 200 | 3987.9143 | 99.7% | 95% | 100% | -104.119 | 2977.4144 | -3550 | -400 | -972.5856 | 24.31% | 95.95% | 95% | 100% | 3321 | -91
[5 empty] | 2019-01-14 | 34 | 329 | 3355 | -90 | 1 | 0 | 3445 | 3275.7626 | 3275.7626 | 3275.7626 | 3006.3479 | 780 | 200 | 3986.3479 | 99.66% | 95% | 100% | -102.9748 | 3172.7877 | -3550 | -400 | -777.2123 | 19.43% | 95.95% | 95% | 100% | 3445 | -90
[5 empty] | 2019-01-14 | 35 | 329.5 | 3386 | -91 | 1 | 0 | 3477 | 3325.8862 | 3325.8862 | 3325.8862 | 3006.3479 | 780 | 200 | 3986.3479 | 99.66% | 95% | 100% | -104.119 | 3221.7672 | -3550 | -400 | -728.2328 | 18.21% | 95.94% | 95% | 100% | 3477 | -91
[5 empty] | 2019-01-14 | 36 | 330 | 3368 | -91 | 0 | 0 | 3459 | 3297.6917 | 3297.6917 | 3297.6917 | 3006.3479 | 780 | 200 | 3986.3479 | 99.66% | 95% | 100% | -104.119 | 3193.5727 | -2750 | -200 | 243.5727 | -6.089% | 95.93% | 95% | 100% | 3459 | -91
[5 empty] | 2019-01-14 | 37 | 330.5 | 3348 | -95 | 0 | 0 | 3443 | 3272.6298 | 3272.6298 | 3272.6298 | 3006.3479 | 780 | 200 | 3986.3479 | 99.66% | 95% | 100% | -108.6957 | 3163.9342 | -2750 | -200 | 213.9342 | -5.348% | 95.92% | 95% | 100% | 3443 | -95
[5 empty] | 2019-01-14 | 38 | 331 | 3324 | -99 | 0 | 0 | 3423 | 3241.3026 | 3241.3026 | 3241.3026 | 3004.7815 | 780 | 200 | 3984.7815 | 99.62% | 95% | 100% | -113.2723 | 3128.0302 | -2750 | -200 | 178.0302 | -4.451% | 95.91% | 95% | 100% | 3423 | -99
[5 empty] | 2019-01-14 | 39 | 331.5 | 3243 | -104 | 0 | 0 | 3347 | 3122.2589 | 3122.2589 | 3122.2589 | 3004.7815 | 780 | 200 | 3984.7815 | 99.62% | 95% | 100% | -118.9931 | 3003.2657 | -2750 | -200 | 53.2657 | -1.332% | 95.91% | 95% | 100% | 3347 | -104
[5 empty] | 2019-01-14 | 40 | 332 | 3139 | -108 | 0 | 0 | 3247 | 2965.6224 | 2965.6224 | 2965.6224 | 3004.7815 | 780 | 200 | 3984.7815 | 99.62% | 95% | 100% | -123.5698 | 2842.0526 | -2750 | -200 | -107.9474 | 2.699% | 95.91% | 95% | 100% | 3247 | -108
[5 empty] | 2019-01-14 | 41 | 332.5 | 3049 | -114 | 0 | 0 | 3163 | 2834.0478 | 2834.0478 | 2834.0478 | 3004.7815 | 780 | 200 | 3984.7815 | 99.62% | 95% | 100% | -130.4348 | 2703.613 | -2750 | -200 | -246.387 | 6.16% | 95.9% | 95% | 100% | 3163 | -114
[5 empty] | 2019-01-14 | 42 | 333 | 2910 | -120 | 0 | 0 | 3030 | 2625.7214 | 2625.7214 | 2625.7214 | 3004.7815 | 780 | 200 | 3984.7815 | 99.62% | 95% | 100% | -137.2998 | 2488.4216 | -2750 | -200 | -461.5784 | 11.54% | 95.9% | 95% | 100% | 3030 | -120
[5 empty] | 2019-01-14 | 43 | 333.5 | 2729 | -127 | 0 | 0 | 2856 | 2353.1739 | 2353.1739 | 2353.1739 | 3003.2152 | 780 | 200 | 3983.2152 | 99.58% | 95% | 100% | -145.3089 | 2207.865 | -2750 | -200 | -742.135 | 18.55% | 95.89% | 95% | 100% | 2856 | -127
[5 empty] | 2019-01-14 | 44 | 334 | 2530 | -133 | 0 | 0 | 2663 | 2050.8656 | 2050.8656 | 2050.8656 | 3003.2152 | 780 | 200 | 3983.2152 | 99.58% | 95% | 100% | -152.1739 | 1898.6917 | -2750 | -200 | -1051.3083 | 26.28% | 95.88% | 95% | 100% | 2663 | -133
[5 empty] | 2019-01-14 | 45 | 334.5 | 2345 | -138 | 0 | 0 | 2483 | 1768.92 | 1768.92 | 1768.92 | 3003.2152 | 780 | 200 | 3983.2152 | 99.58% | 95% | 100% | -157.8947 | 1611.0253 | -2750 | -200 | -1338.9747 | 33.47% | 95.87% | 95% | 100% | 2483 | -138
[5 empty] | 2019-01-14 | 46 | 335 | 2177 | -142 | 0 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 3003.2152 | 780 | 200 | 3983.2152 | 99.58% | 95% | 100% | -162.4714 | 1349.5649 | -2750 | -200 | -1600.4351 | 40.01% | 95.86% | 95% | 100% | 2319 | -142
[5 empty] | 2019-01-14 | 47 | 335.5 | 2010 | -144 | 0 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 3003.2152 | 780 | 200 | 3983.2152 | 99.58% | 95% | 100% | -164.7597 | 1088.8264 | -2750 | -200 | -1861.1736 | 46.53% | 95.84% | 95% | 100% | 2154 | -144
[5 empty] | 2019-01-14 | 48 | 336 | 1896 | -145 | 0 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 3001.6488 | 780 | 200 | 3981.6488 | 99.54% | 95% | 100% | -165.9039 | 910.6831 | -2750 | -200 | -2039.3169 | 50.98% | 95.84% | 95% | 100% | 2041 | -145
[5 empty] | 2019-01-15 | 1 | 336.5 | 1857 | -150 | 0 | 0 | 2007 | 1023.3306 | 1023.3306 | 1023.3306 | 3001.6488 | 780 | 200 | 3981.6488 | 99.54% | 95% | 100% | -171.6247 | 851.7059 | -2750 | -200 | -2098.2941 | 52.46% | 95.83% | 95% | 100% | 2007 | -150
[5 empty] | 2019-01-15 | 2 | 337 | 1883 | -155 | 0 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 3001.6488 | 780 | 200 | 3981.6488 | 99.54% | 95% | 100% | -177.3455 | 894.5423 | -2750 | -200 | -2055.4577 | 51.39% | 95.82% | 95% | 100% | 2038 | -155
[5 empty] | 2019-01-15 | 3 | 337.5 | 1851 | -158 | 0 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 3001.6488 | 780 | 200 | 3981.6488 | 99.54% | 95% | 100% | -180.778 | 845.6853 | -2750 | -200 | -2104.3147 | 52.61% | 95.8% | 95% | 100% | 2009 | -158
[5 empty] | 2019-01-15 | 4 | 338 | 1794 | -161 | 0 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 3000.0824 | 780 | 200 | 3980.0824 | 99.5% | 95% | 100% | -184.2105 | 757.6691 | -2750 | -200 | -2192.3309 | 54.81% | 95.8% | 95% | 100% | 1955 | -161
[5 empty] | 2019-01-15 | 5 | 338.5 | 1761 | -163 | 0 | 0 | 1924 | 893.3223 | 893.3223 | 893.3223 | 3000.0824 | 780 | 200 | 3980.0824 | 99.5% | 95% | 100% | -186.4989 | 706.8235 | -2750 | -200 | -2243.1765 | 56.08% | 95.79% | 95% | 100% | 1924 | -163
[5 empty] | 2019-01-15 | 6 | 339 | 1736 | -166 | 0 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 2998.5161 | 780 | 200 | 3978.5161 | 99.46% | 95% | 100% | -189.9314 | 668.931 | -2750 | -200 | -2281.069 | 57.03% | 95.79% | 95% | 100% | 1902 | -166
[5 empty] | 2019-01-15 | 7 | 339.5 | 1704 | -165 | 0 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 2998.5161 | 780 | 200 | 3978.5161 | 99.46% | 95% | 100% | -188.7872 | 618.3851 | -2750 | -200 | -2331.6149 | 58.29% | 95.78% | 95% | 100% | 1869 | -165
[5 empty] | 2019-01-15 | 8 | 340 | 1666 | -164 | 0 | 0 | 1830 | 746.0841 | 746.0841 | 746.0841 | 2996.9497 | 780 | 200 | 3976.9497 | 99.42% | 95% | 100% | -187.643 | 558.4411 | -2750 | -200 | -2391.5589 | 59.79% | 95.77% | 95% | 100% | 1830 | -164
[5 empty] | 2019-01-15 | 9 | 340.5 | 1653 | -166 | 0 | 0 | 1819 | 728.8541 | 728.8541 | 728.8541 | 2995.3833 | 780 | 200 | 3975.3833 | 99.38% | 95% | 100% | -189.9314 | 538.9227 | -2750 | -200 | -2411.0773 | 60.28% | 95.76% | 95% | 100% | 1819 | -166
[5 empty] | 2019-01-15 | 10 | 341 | 1668 | -167 | 0 | 0 | 1835 | 753.9159 | 753.9159 | 753.9159 | 2995.3833 | 780 | 200 | 3975.3833 | 99.38% | 95% | 100% | -191.0755 | 562.8404 | -2750 | -200 | -2387.1596 | 59.68% | 95.76% | 95% | 100% | 1835 | -167
[5 empty] | 2019-01-15 | 11 | 341.5 | 1729 | -166 | 0 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 2995.3833 | 780 | 200 | 3975.3833 | 99.38% | 95% | 100% | -189.9314 | 657.9664 | -2750 | -200 | -2292.0336 | 57.3% | 95.76% | 95% | 100% | 1895 | -166
[5 empty] | 2019-01-15 | 12 | 342 | 1845 | -165 | 0 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 2995.3833 | 780 | 200 | 3975.3833 | 99.38% | 95% | 100% | -188.7872 | 839.2425 | -2750 | -200 | -2110.7575 | 52.77% | 95.75% | 95% | 100% | 2010 | -165
[5 empty] | 2019-01-15 | 13 | 342.5 | 2110 | -164 | 0 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 2995.3833 | 780 | 200 | 3975.3833 | 99.38% | 95% | 100% | -187.643 | 1253.9069 | -2750 | -200 | -1696.0931 | 42.4% | 95.74% | 95% | 100% | 2274 | -164
[5 empty] | 2019-01-15 | 14 | 343 | 2364 | -162 | 0 | 0 | 2526 | 1836.2737 | 1836.2737 | 1836.2737 | 2993.817 | 780 | 200 | 3973.817 | 99.35% | 95% | 100% | -185.3547 | 1650.919 | -2750 | -200 | -1299.081 | 32.48% | 95.74% | 95% | 100% | 2526 | -162
[5 empty] | 2019-01-15 | 15 | 343.5 | 2658 | -162 | 0 | 0 | 2820 | 2296.7848 | 2296.7848 | 2296.7848 | 2993.817 | 780 | 200 | 3973.817 | 99.35% | 95% | 100% | -185.3547 | 2111.4301 | -2750 | -200 | -838.5699 | 20.96% | 95.74% | 95% | 100% | 2820 | -162
[5 empty] | 2019-01-15 | 16 | 344 | 2810 | -162 | 0 | 0 | 2972 | 2534.8722 | 2534.8722 | 2534.8722 | 2992.2506 | 780 | 200 | 3972.2506 | 99.31% | 95% | 100% | -185.3547 | 2349.5175 | -2750 | -200 | -600.4825 | 15.01% | 95.74% | 95% | 100% | 2972 | -162
[5 empty] | 2019-01-15 | 17 | 344.5 | 2884 | -161 | 0 | 0 | 3045 | 2649.2168 | 2649.2168 | 2649.2168 | 2992.2506 | 780 | 200 | 3972.2506 | 99.31% | 95% | 100% | -184.2105 | 2465.0063 | -2750 | -200 | -484.9937 | 12.12% | 95.74% | 95% | 100% | 3045 | -161
[5 empty] | 2019-01-15 | 18 | 345 | 2877 | -167 | 0 | 0 | 3044 | 2647.6505 | 2647.6505 | 2647.6505 | 2990.6843 | 780 | 200 | 3970.6843 | 99.27% | 95% | 100% | -191.0755 | 2456.5749 | -2750 | -200 | -493.4251 | 12.34% | 95.73% | 95% | 100% | 3044 | -167
[5 empty] | 2019-01-15 | 19 | 345.5 | 2890 | -187 | 0 | 0 | 3077 | 2699.3405 | 2699.3405 | 2699.3405 | 2990.6843 | 780 | 200 | 3970.6843 | 99.27% | 95% | 100% | -213.9588 | 2485.3817 | -2750 | -200 | -464.6183 | 11.62% | 95.73% | 95% | 100% | 3077 | -187
[5 empty] | 2019-01-15 | 20 | 346 | 2859 | -211 | 1 | 0 | 3070 | 2688.3759 | 2688.3759 | 2688.3759 | 2990.6843 | 780 | 200 | 3970.6843 | 99.27% | 95% | 100% | -241.4188 | 2446.9572 | -3550 | -400 | -1503.0428 | 37.58% | 95.73% | 95% | 100% | 3070 | -211
[5 empty] | 2019-01-15 | 21 | 346.5 | 2800 | -236 | 1 | 0 | 3036 | 2635.1195 | 2635.1195 | 2635.1195 | 2990.6843 | 780 | 200 | 3970.6843 | 99.27% | 95% | 100% | -270.0229 | 2365.0967 | -3550 | -400 | -1584.9033 | 39.62% | 95.72% | 95% | 100% | 3036 | -236
[5 empty] | 2019-01-15 | 22 | 347 | 2751 | -259 | 1 | 0 | 3010 | 2594.3941 | 2594.3941 | 2594.3941 | 2990.6843 | 780 | 200 | 3970.6843 | 99.27% | 95% | 100% | -296.3387 | 2298.0554 | -3550 | -400 | -1651.9446 | 41.3% | 95.69% | 95% | 100% | 3010 | -259
[5 empty] | 2019-01-15 | 23 | 347.5 | 2708 | -270 | 1 | 0 | 2978 | 2544.2704 | 2544.2704 | 2544.2704 | 2989.1179 | 780 | 200 | 3969.1179 | 99.23% | 95% | 100% | -308.9245 | 2235.3459 | -3550 | -400 | -1714.6541 | 42.87% | 95.68% | 95% | 100% | 2978 | -270
[5 empty] | 2019-01-15 | 24 | 348 | 2706 | -277 | 1 | 0 | 2983 | 2552.1022 | 2552.1022 | 2552.1022 | 2989.1179 | 780 | 200 | 3969.1179 | 99.23% | 95% | 100% | -316.9336 | 2235.1686 | -3550 | -400 | -1714.8314 | 42.87% | 95.68% | 95% | 100% | 2983 | -277
[5 empty] | 2019-01-15 | 25 | 348.5 | 2727 | -275 | 1 | 0 | 3002 | 2581.8631 | 2581.8631 | 2581.8631 | 2987.5515 | 780 | 200 | 3967.5515 | 99.19% | 95% | 100% | -314.6453 | 2267.2178 | -3550 | -400 | -1682.7822 | 42.07% | 95.68% | 95% | 100% | 3002 | -275
[5 empty] | 2019-01-15 | 26 | 349 | 2738 | -267 | 1 | 0 | 3005 | 2586.5622 | 2586.5622 | 2586.5622 | 2987.5515 | 780 | 200 | 3967.5515 | 99.19% | 95% | 100% | -305.492 | 2281.0703 | -3550 | -400 | -1668.9297 | 41.72% | 95.67% | 95% | 100% | 3005 | -267
[5 empty] | 2019-01-15 | 27 | 349.5 | 2758 | -246 | 1 | 0 | 3004 | 2584.9959 | 2584.9959 | 2584.9959 | 2985.9852 | 780 | 200 | 3965.9852 | 99.15% | 95% | 100% | -281.4645 | 2303.5313 | -3550 | -400 | -1646.4687 | 41.16% | 95.67% | 95% | 100% | 3004 | -246
[5 empty] | 2019-01-15 | 28 | 350 | 2768 | -233 | 1 | 0 | 3001 | 2580.2968 | 2580.2968 | 2580.2968 | 2985.9852 | 780 | 200 | 3965.9852 | 99.15% | 95% | 100% | -266.5904 | 2313.7064 | -3550 | -400 | -1636.2936 | 40.91% | 95.66% | 95% | 100% | 3001 | -233
[5 empty] | 2019-01-15 | 29 | 350.5 | 2800 | -217 | 1 | 0 | 3017 | 2605.3586 | 2605.3586 | 2605.3586 | 2985.9852 | 780 | 200 | 3965.9852 | 99.15% | 95% | 100% | -248.2838 | 2357.0749 | -3550 | -400 | -1592.9251 | 39.82% | 95.65% | 95% | 100% | 3017 | -217
[5 empty] | 2019-01-15 | 30 | 351 | 2831 | -200 | 1 | 0 | 3031 | 2627.2877 | 2627.2877 | 2627.2877 | 2985.9852 | 780 | 200 | 3965.9852 | 99.15% | 95% | 100% | -228.833 | 2398.4548 | -3550 | -400 | -1551.5452 | 38.79% | 95.61% | 95% | 100% | 3031 | -200
[5 empty] | 2019-01-15 | 31 | 351.5 | 2878 | -179 | 1 | 0 | 3057 | 2668.0132 | 2668.0132 | 2668.0132 | 2985.9852 | 780 | 200 | 3965.9852 | 99.15% | 95% | 100% | -204.8055 | 2463.2077 | -3550 | -400 | -1486.7923 | 37.17% | 95.6% | 95% | 100% | 3057 | -179
[5 empty] | 2019-01-15 | 32 | 352 | 2960 | -161 | 1 | 0 | 3121 | 2768.2605 | 2768.2605 | 2768.2605 | 2985.9852 | 780 | 200 | 3965.9852 | 99.15% | 95% | 100% | -184.2105 | 2584.05 | -3550 | -400 | -1365.95 | 34.15% | 95.59% | 95% | 100% | 3121 | -161
[5 empty] | 2019-01-15 | 33 | 352.5 | 3104 | -155 | 1 | 0 | 3259 | 2984.4188 | 2984.4188 | 2984.4188 | 2985.9852 | 780 | 200 | 3965.9852 | 99.15% | 95% | 100% | -177.3455 | 2807.0733 | -3550 | -400 | -1142.9267 | 28.57% | 95.57% | 95% | 100% | 3259 | -155
[5 empty] | 2019-01-15 | 34 | 353 | 3216 | -156 | 1 | 0 | 3372 | 3161.418 | 3161.418 | 3161.418 | 2984.4188 | 780 | 200 | 3964.4188 | 99.11% | 95% | 100% | -178.4897 | 2982.9283 | -3550 | -400 | -967.0717 | 24.18% | 95.57% | 95% | 100% | 3372 | -156
[5 empty] | 2019-01-15 | 35 | 353.5 | 3269 | -156 | 0 | 0 | 3425 | 3244.4353 | 3244.4353 | 3244.4353 | 2984.4188 | 780 | 200 | 3964.4188 | 99.11% | 95% | 100% | -178.4897 | 3065.9456 | -2750 | -200 | 115.9456 | -2.899% | 95.56% | 95% | 100% | 3425 | -156
[5 empty] | 2019-01-15 | 36 | 354 | 3261 | -157 | 0 | 0 | 3418 | 3233.4707 | 3233.4707 | 3233.4707 | 2984.4188 | 780 | 200 | 3964.4188 | 99.11% | 95% | 100% | -179.6339 | 3053.8369 | -2750 | -200 | 103.8369 | -2.596% | 95.56% | 95% | 100% | 3418 | -157
[5 empty] | 2019-01-15 | 37 | 354.5 | 3243 | -158 | 0 | 0 | 3401 | 3206.8425 | 3206.8425 | 3206.8425 | 2984.4188 | 780 | 200 | 3964.4188 | 99.11% | 95% | 100% | -180.778 | 3026.0645 | -2750 | -200 | 76.0645 | -1.902% | 95.56% | 95% | 100% | 3401 | -158
[5 empty] | 2019-01-15 | 38 | 355 | 3190 | -160 | 0 | 0 | 3350 | 3126.958 | 3126.958 | 3126.958 | 2984.4188 | 780 | 200 | 3964.4188 | 99.11% | 95% | 100% | -183.0664 | 2943.8916 | -2750 | -200 | -6.1084 | 0.1527% | 95.55% | 95% | 100% | 3350 | -160
[5 empty] | 2019-01-15 | 39 | 355.5 | 3113 | -160 | 0 | 0 | 3273 | 3006.3479 | 3006.3479 | 3006.3479 | 2984.4188 | 780 | 200 | 3964.4188 | 99.11% | 95% | 100% | -183.0664 | 2823.2815 | -2750 | -200 | -126.7185 | 3.168% | 95.55% | 95% | 100% | 3273 | -160
[5 empty] | 2019-01-15 | 40 | 356 | 2996 | -161 | 0 | 0 | 3157 | 2824.6496 | 2824.6496 | 2824.6496 | 2984.4188 | 780 | 200 | 3964.4188 | 99.11% | 95% | 100% | -184.2105 | 2640.4391 | -2750 | -200 | -309.5609 | 7.739% | 95.53% | 95% | 100% | 3157 | -161
[5 empty] | 2019-01-15 | 41 | 356.5 | 2886 | -163 | 0 | 0 | 3049 | 2655.4823 | 2655.4823 | 2655.4823 | 2982.8524 | 780 | 200 | 3962.8524 | 99.07% | 95% | 100% | -186.4989 | 2468.9834 | -2750 | -200 | -481.0166 | 12.03% | 95.52% | 95% | 100% | 3049 | -163
[5 empty] | 2019-01-15 | 42 | 357 | 2760 | -166 | 0 | 0 | 2926 | 2462.8195 | 2462.8195 | 2462.8195 | 2982.8524 | 780 | 200 | 3962.8524 | 99.07% | 95% | 100% | -189.9314 | 2272.8881 | -2750 | -200 | -677.1119 | 16.93% | 95.5% | 95% | 100% | 2926 | -166
[5 empty] | 2019-01-15 | 43 | 357.5 | 2594 | -169 | 0 | 0 | 2763 | 2207.5021 | 2207.5021 | 2207.5021 | 2982.8524 | 780 | 200 | 3962.8524 | 99.07% | 95% | 100% | -193.3638 | 2014.1382 | -2750 | -200 | -935.8618 | 23.4% | 95.5% | 95% | 100% | 2763 | -169
[5 empty] | 2019-01-15 | 44 | 358 | 2399 | -171 | 0 | 0 | 2570 | 1905.1937 | 1905.1937 | 1905.1937 | 2981.2861 | 780 | 200 | 3961.2861 | 99.03% | 95% | 100% | -195.6522 | 1709.5416 | -2750 | -200 | -1240.4584 | 31.01% | 95.49% | 95% | 100% | 2570 | -171
[5 empty] | 2019-01-15 | 45 | 358.5 | 2228 | -173 | 0 | 0 | 2401 | 1640.4782 | 1640.4782 | 1640.4782 | 2981.2861 | 780 | 200 | 3961.2861 | 99.03% | 95% | 100% | -197.9405 | 1442.5376 | -2750 | -200 | -1507.4624 | 37.69% | 95.48% | 95% | 100% | 2401 | -173
[5 empty] | 2019-01-15 | 46 | 359 | 2052 | -174 | 0 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 2979.7197 | 780 | 200 | 3959.7197 | 98.99% | 95% | 100% | -199.0847 | 1167.2797 | -2750 | -200 | -1782.7203 | 44.57% | 95.46% | 95% | 100% | 2226 | -174
[5 empty] | 2019-01-15 | 47 | 359.5 | 1899 | -179 | 0 | 0 | 2078 | 1134.5425 | 1134.5425 | 1134.5425 | 2979.7197 | 780 | 200 | 3959.7197 | 98.99% | 95% | 100% | -204.8055 | 929.737 | -2750 | -200 | -2020.263 | 50.51% | 95.45% | 95% | 100% | 2078 | -179
[5 empty] | 2019-01-15 | 48 | 360 | 1768 | -184 | 0 | 0 | 1952 | 937.1805 | 937.1805 | 937.1805 | 2979.7197 | 780 | 200 | 3959.7197 | 98.99% | 95% | 100% | -210.5263 | 726.6542 | -2750 | -200 | -2223.3458 | 55.58% | 95.45% | 95% | 100% | 1952 | -184
[5 empty] | 2019-01-16 | 1 | 360.5 | 1746 | -185 | 0 | 0 | 1931 | 904.2869 | 904.2869 | 904.2869 | 2979.7197 | 780 | 200 | 3959.7197 | 98.99% | 95% | 100% | -211.6705 | 692.6164 | -2750 | -200 | -2257.3836 | 56.43% | 95.45% | 95% | 100% | 1931 | -185
[5 empty] | 2019-01-16 | 2 | 361 | 1768 | -187 | 0 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 2979.7197 | 780 | 200 | 3959.7197 | 98.99% | 95% | 100% | -213.9588 | 727.9208 | -2750 | -200 | -2222.0792 | 55.55% | 95.44% | 95% | 100% | 1955 | -187
[5 empty] | 2019-01-16 | 3 | 361.5 | 1753 | -186 | 0 | 0 | 1939 | 916.8178 | 916.8178 | 916.8178 | 2978.1533 | 780 | 200 | 3958.1533 | 98.95% | 95% | 100% | -212.8146 | 704.0032 | -2750 | -200 | -2245.9968 | 56.15% | 95.43% | 95% | 100% | 1939 | -186
[5 empty] | 2019-01-16 | 4 | 362 | 1708 | -186 | 0 | 0 | 1894 | 846.3314 | 846.3314 | 846.3314 | 2978.1533 | 780 | 200 | 3958.1533 | 98.95% | 95% | 100% | -212.8146 | 633.5168 | -2750 | -200 | -2316.4832 | 57.91% | 95.43% | 95% | 100% | 1894 | -186
[5 empty] | 2019-01-16 | 5 | 362.5 | 1668 | -185 | 0 | 0 | 1853 | 782.1105 | 782.1105 | 782.1105 | 2978.1533 | 780 | 200 | 3958.1533 | 98.95% | 95% | 100% | -211.6705 | 570.44 | -2750 | -200 | -2379.56 | 59.49% | 95.42% | 95% | 100% | 1853 | -185
[5 empty] | 2019-01-16 | 6 | 363 | 1653 | -184 | 0 | 0 | 1837 | 757.0486 | 757.0486 | 757.0486 | 2978.1533 | 780 | 200 | 3958.1533 | 98.95% | 95% | 100% | -210.5263 | 546.5223 | -2750 | -200 | -2403.4777 | 60.09% | 95.4% | 95% | 100% | 1837 | -184
[5 empty] | 2019-01-16 | 7 | 363.5 | 1620 | -182 | 0 | 0 | 1802 | 702.2259 | 702.2259 | 702.2259 | 2978.1533 | 780 | 200 | 3958.1533 | 98.95% | 95% | 100% | -208.238 | 493.9879 | -2750 | -200 | -2456.0121 | 61.4% | 95.38% | 95% | 100% | 1802 | -182
[5 empty] | 2019-01-16 | 8 | 364 | 1592 | -179 | 0 | 0 | 1771 | 653.6686 | 653.6686 | 653.6686 | 2978.1533 | 780 | 200 | 3958.1533 | 98.95% | 95% | 100% | -204.8055 | 448.8631 | -2750 | -200 | -2501.1369 | 62.53% | 95.38% | 95% | 100% | 1771 | -179
[5 empty] | 2019-01-16 | 9 | 364.5 | 1580 | -178 | 0 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 2978.1533 | 780 | 200 | 3958.1533 | 98.95% | 95% | 100% | -203.6613 | 429.6445 | -2750 | -200 | -2520.3555 | 63.01% | 95.38% | 95% | 100% | 1758 | -178
[5 empty] | 2019-01-16 | 10 | 365 | 1600 | -176 | 0 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 2976.587 | 780 | 200 | 3956.587 | 98.91% | 95% | 100% | -201.373 | 460.1274 | -2750 | -200 | -2489.8726 | 62.25% | 95.37% | 95% | 100% | 1776 | -176
[5 empty] | 2019-01-16 | 11 | 365.5 | 1659 | -173 | 0 | 0 | 1832 | 749.2168 | 749.2168 | 749.2168 | 2976.587 | 780 | 200 | 3956.587 | 98.91% | 95% | 100% | -197.9405 | 551.2763 | -2750 | -200 | -2398.7237 | 59.97% | 95.37% | 95% | 100% | 1832 | -173
[5 empty] | 2019-01-16 | 12 | 366 | 1777 | -169 | 0 | 0 | 1946 | 927.7824 | 927.7824 | 927.7824 | 2976.587 | 780 | 200 | 3956.587 | 98.91% | 95% | 100% | -193.3638 | 734.4185 | -2750 | -200 | -2215.5815 | 55.39% | 95.36% | 95% | 100% | 1946 | -169
[5 empty] | 2019-01-16 | 13 | 366.5 | 2043 | -166 | 0 | 0 | 2209 | 1339.7362 | 1339.7362 | 1339.7362 | 2976.587 | 780 | 200 | 3956.587 | 98.91% | 95% | 100% | -189.9314 | 1149.8048 | -2750 | -200 | -1800.1952 | 45% | 95.36% | 95% | 100% | 2209 | -166
[5 empty] | 2019-01-16 | 14 | 367 | 2303 | -163 | 0 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 2976.587 | 780 | 200 | 3956.587 | 98.91% | 95% | 100% | -186.4989 | 1555.793 | -2750 | -200 | -1394.207 | 34.86% | 95.34% | 95% | 100% | 2466 | -163
[5 empty] | 2019-01-16 | 15 | 367.5 | 2600 | -163 | 0 | 0 | 2763 | 2207.5021 | 2207.5021 | 2207.5021 | 2976.587 | 780 | 200 | 3956.587 | 98.91% | 95% | 100% | -186.4989 | 2021.0032 | -2750 | -200 | -928.9968 | 23.22% | 95.33% | 95% | 100% | 2763 | -163
[5 empty] | 2019-01-16 | 16 | 368 | 2766 | -162 | 0 | 0 | 2928 | 2465.9522 | 2465.9522 | 2465.9522 | 2975.0206 | 780 | 200 | 3955.0206 | 98.88% | 95% | 100% | -185.3547 | 2280.5975 | -2750 | -200 | -669.4025 | 16.74% | 95.31% | 95% | 100% | 2928 | -162
[5 empty] | 2019-01-16 | 17 | 368.5 | 2833 | -162 | 0 | 0 | 2995 | 2570.8986 | 2570.8986 | 2570.8986 | 2975.0206 | 780 | 200 | 3955.0206 | 98.88% | 95% | 100% | -185.3547 | 2385.5439 | -2750 | -200 | -564.4561 | 14.11% | 95.3% | 95% | 100% | 2995 | -162
[5 empty] | 2019-01-16 | 18 | 369 | 2835 | -163 | 0 | 0 | 2998 | 2575.5977 | 2575.5977 | 2575.5977 | 2973.4542 | 780 | 200 | 3953.4542 | 98.84% | 95% | 100% | -186.4989 | 2389.0988 | -2750 | -200 | -560.9012 | 14.02% | 95.29% | 95% | 100% | 2998 | -163
[5 empty] | 2019-01-16 | 19 | 369.5 | 2865 | -170 | 0 | 0 | 3035 | 2633.5532 | 2633.5532 | 2633.5532 | 2973.4542 | 780 | 200 | 3953.4542 | 98.84% | 95% | 100% | -194.508 | 2439.0452 | -2750 | -200 | -510.9548 | 12.77% | 95.29% | 95% | 100% | 3035 | -170
[5 empty] | 2019-01-16 | 20 | 370 | 2853 | -185 | 1 | 0 | 3038 | 2638.2523 | 2638.2523 | 2638.2523 | 2973.4542 | 780 | 200 | 3953.4542 | 98.84% | 95% | 100% | -211.6705 | 2426.5818 | -3550 | -400 | -1523.4182 | 38.09% | 95.27% | 95% | 100% | 3038 | -185
[5 empty] | 2019-01-16 | 21 | 370.5 | 2823 | -205 | 1 | 0 | 3028 | 2622.5886 | 2622.5886 | 2622.5886 | 2973.4542 | 780 | 200 | 3953.4542 | 98.84% | 95% | 100% | -234.5538 | 2388.0348 | -3550 | -400 | -1561.9652 | 39.05% | 95.27% | 95% | 100% | 3028 | -205
[5 empty] | 2019-01-16 | 22 | 371 | 2813 | -217 | 1 | 0 | 3030 | 2625.7214 | 2625.7214 | 2625.7214 | 2971.8879 | 780 | 200 | 3951.8879 | 98.8% | 95% | 100% | -248.2838 | 2377.4376 | -3550 | -400 | -1572.5624 | 39.31% | 95.25% | 95% | 100% | 3030 | -217
[5 empty] | 2019-01-16 | 23 | 371.5 | 2832 | -240 | 1 | 0 | 3072 | 2691.5087 | 2691.5087 | 2691.5087 | 2971.8879 | 780 | 200 | 3951.8879 | 98.8% | 95% | 100% | -274.5995 | 2416.9091 | -3550 | -400 | -1533.0909 | 38.33% | 95.24% | 95% | 100% | 3072 | -240
[5 empty] | 2019-01-16 | 24 | 372 | 2852 | -238 | 1 | 0 | 3090 | 2719.7032 | 2719.7032 | 2719.7032 | 2970.3215 | 780 | 200 | 3950.3215 | 98.76% | 95% | 100% | -272.3112 | 2447.392 | -3550 | -400 | -1502.608 | 37.57% | 95.24% | 95% | 100% | 3090 | -238
[5 empty] | 2019-01-16 | 25 | 372.5 | 2879 | -231 | 1 | 0 | 3110 | 2751.0305 | 2751.0305 | 2751.0305 | 2970.3215 | 780 | 200 | 3950.3215 | 98.76% | 95% | 100% | -264.3021 | 2486.7284 | -3550 | -400 | -1463.2716 | 36.58% | 95.23% | 95% | 100% | 3110 | -231
[5 empty] | 2019-01-16 | 26 | 373 | 2884 | -228 | 1 | 0 | 3112 | 2754.1632 | 2754.1632 | 2754.1632 | 2970.3215 | 780 | 200 | 3950.3215 | 98.76% | 95% | 100% | -260.8696 | 2493.2937 | -3550 | -400 | -1456.7063 | 36.42% | 95.23% | 95% | 100% | 3112 | -228
[5 empty] | 2019-01-16 | 27 | 373.5 | 2891 | -224 | 1 | 0 | 3115 | 2758.8623 | 2758.8623 | 2758.8623 | 2970.3215 | 780 | 200 | 3950.3215 | 98.76% | 95% | 100% | -256.2929 | 2502.5694 | -3550 | -400 | -1447.4306 | 36.19% | 95.23% | 95% | 100% | 3115 | -224
[5 empty] | 2019-01-16 | 28 | 374 | 2872 | -222 | 1 | 0 | 3094 | 2725.9687 | 2725.9687 | 2725.9687 | 2968.7552 | 780 | 200 | 3948.7552 | 98.72% | 95% | 100% | -254.0046 | 2471.9641 | -3550 | -400 | -1478.0359 | 36.95% | 95.22% | 95% | 100% | 3094 | -222
[5 empty] | 2019-01-16 | 29 | 374.5 | 2886 | -217 | 1 | 0 | 3103 | 2740.066 | 2740.066 | 2740.066 | 2968.7552 | 780 | 200 | 3948.7552 | 98.72% | 95% | 100% | -248.2838 | 2491.7822 | -3550 | -400 | -1458.2178 | 36.46% | 95.22% | 95% | 100% | 3103 | -217
[5 empty] | 2019-01-16 | 30 | 375 | 2881 | -207 | 1 | 0 | 3088 | 2716.5705 | 2716.5705 | 2716.5705 | 2968.7552 | 780 | 200 | 3948.7552 | 98.72% | 95% | 100% | -236.8421 | 2479.7284 | -3550 | -400 | -1470.2716 | 36.76% | 95.19% | 95% | 100% | 3088 | -207
[5 empty] | 2019-01-16 | 31 | 375.5 | 2899 | -184 | 1 | 0 | 3083 | 2708.7387 | 2708.7387 | 2708.7387 | 2967.1888 | 780 | 200 | 3947.1888 | 98.68% | 95% | 100% | -210.5263 | 2498.2123 | -3550 | -400 | -1451.7877 | 36.29% | 95.19% | 95% | 100% | 3083 | -184
[5 empty] | 2019-01-16 | 32 | 376 | 3029 | -159 | 1 | 0 | 3188 | 2873.2069 | 2873.2069 | 2873.2069 | 2967.1888 | 780 | 200 | 3947.1888 | 98.68% | 95% | 100% | -181.9222 | 2691.2847 | -3550 | -400 | -1258.7153 | 31.47% | 95.18% | 95% | 100% | 3188 | -159
[5 empty] | 2019-01-16 | 33 | 376.5 | 3156 | -143 | 1 | 0 | 3299 | 3047.0734 | 3047.0734 | 3047.0734 | 2967.1888 | 780 | 200 | 3947.1888 | 98.68% | 95% | 100% | -163.6156 | 2883.4578 | -3550 | -400 | -1066.5422 | 26.66% | 95.18% | 95% | 100% | 3299 | -143
[5 empty] | 2019-01-16 | 34 | 377 | 3290 | -136 | 1 | 0 | 3426 | 3246.0016 | 3246.0016 | 3246.0016 | 2967.1888 | 780 | 200 | 3947.1888 | 98.68% | 95% | 100% | -155.6064 | 3090.3952 | -3550 | -400 | -859.6048 | 21.49% | 95.17% | 95% | 100% | 3426 | -136
[5 empty] | 2019-01-16 | 35 | 377.5 | 3343 | -135 | 1 | 0 | 3478 | 3327.4526 | 3327.4526 | 3327.4526 | 2967.1888 | 780 | 200 | 3947.1888 | 98.68% | 95% | 100% | -154.4622 | 3172.9904 | -3550 | -400 | -777.0096 | 19.43% | 95.16% | 95% | 100% | 3478 | -135
[5 empty] | 2019-01-16 | 36 | 378 | 3328 | -134 | 0 | 0 | 3462 | 3302.3908 | 3302.3908 | 3302.3908 | 2965.6224 | 780 | 200 | 3945.6224 | 98.64% | 95% | 100% | -153.3181 | 3149.0727 | -2750 | -200 | 199.0727 | -4.977% | 95.15% | 95% | 100% | 3462 | -134
[5 empty] | 2019-01-16 | 37 | 378.5 | 3317 | -133 | 0 | 0 | 3450 | 3283.5944 | 3283.5944 | 3283.5944 | 2965.6224 | 780 | 200 | 3945.6224 | 98.64% | 95% | 100% | -152.1739 | 3131.4205 | -2750 | -200 | 181.4205 | -4.536% | 95.14% | 95% | 100% | 3450 | -133
[5 empty] | 2019-01-16 | 38 | 379 | 3265 | -132 | 0 | 0 | 3397 | 3200.5771 | 3200.5771 | 3200.5771 | 2965.6224 | 780 | 200 | 3945.6224 | 98.64% | 95% | 100% | -151.0297 | 3049.5473 | -2750 | -200 | 99.5473 | -2.489% | 95.14% | 95% | 100% | 3397 | -132
[5 empty] | 2019-01-16 | 39 | 379.5 | 3186 | -133 | 0 | 0 | 3319 | 3078.4007 | 3078.4007 | 3078.4007 | 2965.6224 | 780 | 200 | 3945.6224 | 98.64% | 95% | 100% | -152.1739 | 2926.2267 | -2750 | -200 | -23.7733 | 0.5943% | 95.13% | 95% | 100% | 3319 | -133
[5 empty] | 2019-01-16 | 40 | 380 | 3107 | -134 | 0 | 0 | 3241 | 2956.2242 | 2956.2242 | 2956.2242 | 2964.0561 | 780 | 200 | 3944.0561 | 98.6% | 95% | 100% | -153.3181 | 2802.9062 | -2750 | -200 | -147.0938 | 3.677% | 95.13% | 95% | 100% | 3241 | -134
[5 empty] | 2019-01-16 | 41 | 380.5 | 3024 | -135 | 0 | 0 | 3159 | 2827.7824 | 2827.7824 | 2827.7824 | 2964.0561 | 780 | 200 | 3944.0561 | 98.6% | 95% | 100% | -154.4622 | 2673.3201 | -2750 | -200 | -276.6799 | 6.917% | 95.12% | 95% | 100% | 3159 | -135
[5 empty] | 2019-01-16 | 42 | 381 | 2906 | -137 | 0 | 0 | 3043 | 2646.0841 | 2646.0841 | 2646.0841 | 2964.0561 | 780 | 200 | 3944.0561 | 98.6% | 95% | 100% | -156.7506 | 2489.3335 | -2750 | -200 | -460.6665 | 11.52% | 95.09% | 95% | 100% | 3043 | -137
[5 empty] | 2019-01-16 | 43 | 381.5 | 2761 | -141 | 0 | 0 | 2902 | 2425.2267 | 2425.2267 | 2425.2267 | 2964.0561 | 780 | 200 | 3944.0561 | 98.6% | 95% | 100% | -161.3272 | 2263.8995 | -2750 | -200 | -686.1005 | 17.15% | 95.06% | 95% | 100% | 2902 | -141
[5 empty] | 2019-01-16 | 44 | 382 | 2586 | -144 | 0 | 0 | 2730 | 2155.812 | 2155.812 | 2155.812 | 2964.0561 | 780 | 200 | 3944.0561 | 98.6% | 95% | 100% | -164.7597 | 1991.0523 | -2750 | -200 | -958.9477 | 23.97% | 95.06% | 95% | 100% | 2730 | -144
[5 empty] | 2019-01-16 | 45 | 382.5 | 2402 | -148 | 0 | 0 | 2550 | 1873.8664 | 1873.8664 | 1873.8664 | 2962.4897 | 780 | 200 | 3942.4897 | 98.56% | 95% | 100% | -169.3364 | 1704.5301 | -2750 | -200 | -1245.4699 | 31.14% | 95.06% | 95% | 100% | 2550 | -148
[5 empty] | 2019-01-16 | 46 | 383 | 2240 | -152 | 0 | 0 | 2392 | 1626.3809 | 1626.3809 | 1626.3809 | 2962.4897 | 780 | 200 | 3942.4897 | 98.56% | 95% | 100% | -173.913 | 1452.4678 | -2750 | -200 | -1497.5322 | 37.44% | 95.05% | 95% | 100% | 2392 | -152
[5 empty] | 2019-01-16 | 47 | 383.5 | 2076 | -155 | 0 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 2962.4897 | 780 | 200 | 3942.4897 | 98.56% | 95% | 100% | -177.3455 | 1196.8507 | -2750 | -200 | -1753.1493 | 43.83% | 95.04% | 95% | 100% | 2231 | -155
[5 empty] | 2019-01-16 | 48 | 384 | 1960 | -157 | 0 | 0 | 2117 | 1195.6307 | 1195.6307 | 1195.6307 | 2962.4897 | 780 | 200 | 3942.4897 | 98.56% | 95% | 100% | -179.6339 | 1015.9968 | -2750 | -200 | -1934.0032 | 48.35% | 95.03% | 95% | 100% | 2117 | -157
[5 empty] | 2019-01-17 | 1 | 384.5 | 1943 | -158 | 0 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 2962.4897 | 780 | 200 | 3942.4897 | 98.56% | 95% | 100% | -180.778 | 989.7908 | -2750 | -200 | -1960.2092 | 49.01% | 95.01% | 95% | 100% | 2101 | -158
[5 empty] | 2019-01-17 | 2 | 385 | 1961 | -159 | 0 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 2960.9233 | 780 | 200 | 3940.9233 | 98.52% | 95% | 100% | -181.9222 | 1018.4076 | -2750 | -200 | -1931.5924 | 48.29% | 94.99% | 95% | 0% | 2120 | -159
[5 empty] | 2019-01-17 | 3 | 385.5 | 1934 | -159 | 0 | 0 | 2093 | 1158.0379 | 1158.0379 | 1158.0379 | 2960.9233 | 780 | 200 | 3940.9233 | 98.52% | 95% | 100% | -181.9222 | 976.1157 | -2750 | -200 | -1973.8843 | 49.35% | 94.98% | 95% | 0% | 2093 | -159
[5 empty] | 2019-01-17 | 4 | 386 | 1893 | -158 | 0 | 0 | 2051 | 1092.2506 | 1092.2506 | 1092.2506 | 2959.357 | 780 | 200 | 3939.357 | 98.48% | 95% | 100% | -180.778 | 911.4726 | -2750 | -200 | -2038.5274 | 50.96% | 94.98% | 95% | 0% | 2051 | -158
[5 empty] | 2019-01-17 | 5 | 386.5 | 1867 | -161 | 0 | 0 | 2028 | 1056.2242 | 1056.2242 | 1056.2242 | 2959.357 | 780 | 200 | 3939.357 | 98.48% | 95% | 100% | -184.2105 | 872.0137 | -2750 | -200 | -2077.9863 | 51.95% | 94.98% | 95% | 0% | 2028 | -161
[5 empty] | 2019-01-17 | 6 | 387 | 1840 | -163 | 0 | 0 | 2003 | 1017.0651 | 1017.0651 | 1017.0651 | 2957.7906 | 780 | 200 | 3937.7906 | 98.44% | 95% | 100% | -186.4989 | 830.5663 | -2750 | -200 | -2119.4337 | 52.99% | 94.97% | 95% | 0% | 2003 | -163
[5 empty] | 2019-01-17 | 7 | 387.5 | 1814 | -162 | 0 | 0 | 1976 | 974.7733 | 974.7733 | 974.7733 | 2957.7906 | 780 | 200 | 3937.7906 | 98.44% | 95% | 100% | -185.3547 | 789.4186 | -2750 | -200 | -2160.5814 | 54.01% | 94.97% | 95% | 0% | 1976 | -162
[5 empty] | 2019-01-17 | 8 | 388 | 1765 | -160 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 2957.7906 | 780 | 200 | 3937.7906 | 98.44% | 95% | 100% | -183.0664 | 711.8223 | -2750 | -200 | -2238.1777 | 55.95% | 94.96% | 95% | 0% | 1925 | -160
[5 empty] | 2019-01-17 | 9 | 388.5 | 1747 | -164 | 0 | 0 | 1911 | 872.9596 | 872.9596 | 872.9596 | 2957.7906 | 780 | 200 | 3937.7906 | 98.44% | 95% | 100% | -187.643 | 685.3166 | -2750 | -200 | -2264.6834 | 56.62% | 94.94% | 95% | 0% | 1911 | -164
[5 empty] | 2019-01-17 | 10 | 389 | 1757 | -167 | 0 | 0 | 1924 | 893.3223 | 893.3223 | 893.3223 | 2956.2242 | 780 | 200 | 3936.2242 | 98.41% | 95% | 100% | -191.0755 | 702.2468 | -2750 | -200 | -2247.7532 | 56.19% | 94.93% | 95% | 0% | 1924 | -167
[5 empty] | 2019-01-17 | 11 | 389.5 | 1799 | -169 | 0 | 0 | 1968 | 962.2424 | 962.2424 | 962.2424 | 2956.2242 | 780 | 200 | 3936.2242 | 98.41% | 95% | 100% | -193.3638 | 768.8785 | -2750 | -200 | -2181.1215 | 54.53% | 94.93% | 95% | 0% | 1968 | -169
[5 empty] | 2019-01-17 | 12 | 390 | 1896 | -171 | 0 | 0 | 2067 | 1117.3124 | 1117.3124 | 1117.3124 | 2954.6579 | 780 | 200 | 3934.6579 | 98.37% | 95% | 100% | -195.6522 | 921.6603 | -2750 | -200 | -2028.3397 | 50.71% | 94.9% | 95% | 0% | 2067 | -171
[5 empty] | 2019-01-17 | 13 | 390.5 | 2142 | -172 | 0 | 0 | 2314 | 1504.2045 | 1504.2045 | 1504.2045 | 2954.6579 | 780 | 200 | 3934.6579 | 98.37% | 95% | 100% | -196.7963 | 1307.4081 | -2750 | -200 | -1642.5919 | 41.06% | 94.9% | 95% | 0% | 2314 | -172
[5 empty] | 2019-01-17 | 14 | 391 | 2407 | -174 | 0 | 0 | 2581 | 1922.4237 | 1922.4237 | 1922.4237 | 2953.0915 | 780 | 200 | 3933.0915 | 98.33% | 95% | 100% | -199.0847 | 1723.3391 | -2750 | -200 | -1226.6609 | 30.67% | 94.9% | 95% | 0% | 2581 | -174
[5 empty] | 2019-01-17 | 15 | 391.5 | 2718 | -173 | 0 | 0 | 2891 | 2407.9967 | 2407.9967 | 2407.9967 | 2953.0915 | 780 | 200 | 3933.0915 | 98.33% | 95% | 100% | -197.9405 | 2210.0562 | -2750 | -200 | -739.9438 | 18.5% | 94.9% | 95% | 0% | 2891 | -173
[5 empty] | 2019-01-17 | 16 | 392 | 2891 | -173 | 0 | 0 | 3064 | 2678.9777 | 2678.9777 | 2678.9777 | 2951.5251 | 780 | 200 | 3931.5251 | 98.29% | 95% | 100% | -197.9405 | 2481.0372 | -2750 | -200 | -468.9628 | 11.72% | 94.9% | 95% | 0% | 3064 | -173
[5 empty] | 2019-01-17 | 17 | 392.5 | 2974 | -172 | 0 | 0 | 3146 | 2807.4196 | 2807.4196 | 2807.4196 | 2951.5251 | 780 | 200 | 3931.5251 | 98.29% | 95% | 100% | -196.7963 | 2610.6233 | -2750 | -200 | -339.3767 | 8.484% | 94.89% | 95% | 0% | 3146 | -172
[5 empty] | 2019-01-17 | 18 | 393 | 2957 | -197 | 0 | 0 | 3154 | 2819.9505 | 2819.9505 | 2819.9505 | 2951.5251 | 780 | 200 | 3931.5251 | 98.29% | 95% | 100% | -225.4005 | 2594.5501 | -2750 | -200 | -355.4499 | 8.886% | 94.88% | 95% | 0% | 3154 | -197
[5 empty] | 2019-01-17 | 19 | 393.5 | 2926 | -235 | 0 | 0 | 3161 | 2830.9151 | 2830.9151 | 2830.9151 | 2951.5251 | 780 | 200 | 3931.5251 | 98.29% | 95% | 100% | -268.8787 | 2562.0364 | -2750 | -200 | -387.9636 | 9.699% | 94.87% | 95% | 0% | 3161 | -235
[5 empty] | 2019-01-17 | 20 | 394 | 2788 | -329 | 1 | 0 | 3117 | 2761.9951 | 2761.9951 | 2761.9951 | 2951.5251 | 780 | 200 | 3931.5251 | 98.29% | 95% | 100% | -376.4302 | 2385.5648 | -3550 | -400 | -1564.4352 | 39.11% | 94.87% | 95% | 0% | 3117 | -329
[5 empty] | 2019-01-17 | 21 | 394.5 | 2655 | -392 | 1 | 0 | 3047 | 2652.3495 | 2652.3495 | 2652.3495 | 2951.5251 | 780 | 200 | 3931.5251 | 98.29% | 95% | 100% | -448.5126 | 2203.837 | -3550 | -400 | -1746.163 | 43.65% | 94.86% | 95% | 0% | 3047 | -392
[5 empty] | 2019-01-17 | 22 | 395 | 2552 | -441 | 1 | 0 | 2993 | 2567.7659 | 2567.7659 | 2567.7659 | 2948.3924 | 780 | 200 | 3928.3924 | 98.21% | 95% | 100% | -504.5767 | 2063.1892 | -3550 | -400 | -1886.8108 | 47.17% | 94.84% | 95% | 0% | 2993 | -441
[5 empty] | 2019-01-17 | 23 | 395.5 | 2474 | -481 | 1 | 0 | 2955 | 2508.244 | 2508.244 | 2508.244 | 2948.3924 | 780 | 200 | 3928.3924 | 98.21% | 95% | 100% | -550.3432 | 1957.9008 | -3550 | -400 | -1992.0992 | 49.8% | 94.84% | 95% | 0% | 2955 | -481
[5 empty] | 2019-01-17 | 24 | 396 | 2405 | -505 | 1 | 0 | 2910 | 2437.7576 | 2437.7576 | 2437.7576 | 2948.3924 | 780 | 200 | 3928.3924 | 98.21% | 95% | 100% | -577.8032 | 1859.9544 | -3550 | -400 | -2090.0456 | 52.25% | 94.83% | 95% | 0% | 2910 | -505
[5 empty] | 2019-01-17 | 25 | 396.5 | 2399 | -510 | 1 | 0 | 2909 | 2436.1913 | 2436.1913 | 2436.1913 | 2946.8261 | 780 | 200 | 3926.8261 | 98.17% | 95% | 100% | -583.524 | 1852.6672 | -3550 | -400 | -2097.3328 | 52.43% | 94.83% | 95% | 0% | 2909 | -510
[5 empty] | 2019-01-17 | 26 | 397 | 2401 | -503 | 1 | 0 | 2904 | 2428.3594 | 2428.3594 | 2428.3594 | 2946.8261 | 780 | 200 | 3926.8261 | 98.17% | 95% | 100% | -575.5149 | 1852.8446 | -3550 | -400 | -2097.1554 | 52.43% | 94.8% | 95% | 0% | 2904 | -503
[5 empty] | 2019-01-17 | 27 | 397.5 | 2442 | -470 | 1 | 0 | 2912 | 2440.8904 | 2440.8904 | 2440.8904 | 2946.8261 | 780 | 200 | 3926.8261 | 98.17% | 95% | 100% | -537.7574 | 1903.1329 | -3550 | -400 | -2046.8671 | 51.17% | 94.8% | 95% | 0% | 2912 | -470
[5 empty] | 2019-01-17 | 28 | 398 | 2520 | -420 | 1 | 0 | 2940 | 2484.7486 | 2484.7486 | 2484.7486 | 2945.2597 | 780 | 200 | 3925.2597 | 98.13% | 95% | 100% | -480.5492 | 2004.1994 | -3550 | -400 | -1945.8006 | 48.65% | 94.79% | 95% | 0% | 2940 | -420
[5 empty] | 2019-01-17 | 29 | 398.5 | 2635 | -357 | 1 | 0 | 2992 | 2566.1995 | 2566.1995 | 2566.1995 | 2945.2597 | 780 | 200 | 3925.2597 | 98.13% | 95% | 100% | -408.4668 | 2157.7327 | -3550 | -400 | -1792.2673 | 44.81% | 94.79% | 95% | 0% | 2992 | -357
[5 empty] | 2019-01-17 | 30 | 399 | 2787 | -275 | 1 | 0 | 3062 | 2675.845 | 2675.845 | 2675.845 | 2943.6933 | 780 | 200 | 3923.6933 | 98.09% | 95% | 100% | -314.6453 | 2361.1997 | -3550 | -400 | -1588.8003 | 39.72% | 94.78% | 95% | 0% | 3062 | -275
[5 empty] | 2019-01-17 | 31 | 399.5 | 2953 | -188 | 1 | 0 | 3141 | 2799.5878 | 2799.5878 | 2799.5878 | 2943.6933 | 780 | 200 | 3923.6933 | 98.09% | 95% | 100% | -215.103 | 2584.4848 | -3550 | -400 | -1365.5152 | 34.14% | 94.76% | 95% | 0% | 3141 | -188
[5 empty] | 2019-01-17 | 32 | 400 | 3159 | -112 | 1 | 0 | 3271 | 3003.2152 | 3003.2152 | 3003.2152 | 2943.6933 | 780 | 200 | 3923.6933 | 98.09% | 95% | 100% | -128.1465 | 2875.0687 | -3550 | -400 | -1074.9313 | 26.87% | 94.76% | 95% | 0% | 3271 | -112
[5 empty] | 2019-01-17 | 33 | 400.5 | 3306 | -78 | 1 | 0 | 3384 | 3180.2143 | 3180.2143 | 3180.2143 | 2943.6933 | 780 | 200 | 3923.6933 | 98.09% | 95% | 100% | -89.2449 | 3090.9695 | -3550 | -400 | -859.0305 | 21.48% | 94.75% | 95% | 0% | 3384 | -78
[5 empty] | 2019-01-17 | 34 | 401 | 3390 | -71 | 1 | 0 | 3461 | 3300.8244 | 3300.8244 | 3300.8244 | 2943.6933 | 780 | 200 | 3923.6933 | 98.09% | 95% | 100% | -81.2357 | 3219.5887 | -3550 | -400 | -730.4113 | 18.26% | 94.75% | 95% | 0% | 3461 | -71
[5 empty] | 2019-01-17 | 35 | 401.5 | 3426 | -67 | 1 | 0 | 3493 | 3350.9481 | 3350.9481 | 3350.9481 | 2943.6933 | 780 | 200 | 3923.6933 | 98.09% | 95% | 100% | -76.659 | 3274.289 | -3550 | -400 | -675.711 | 16.89% | 94.75% | 95% | 0% | 3493 | -67
[5 empty] | 2019-01-17 | 36 | 402 | 3443 | -64 | 0 | 0 | 3507 | 3372.8772 | 3372.8772 | 3372.8772 | 2942.127 | 780 | 200 | 3922.127 | 98.05% | 95% | 100% | -73.2265 | 3299.6506 | -2750 | -200 | 349.6506 | -8.741% | 94.74% | 95% | 0% | 3507 | -64
[5 empty] | 2019-01-17 | 37 | 402.5 | 3453 | -61 | 0 | 0 | 3514 | 3383.8417 | 3383.8417 | 3383.8417 | 2942.127 | 780 | 200 | 3922.127 | 98.05% | 95% | 100% | -69.7941 | 3314.0477 | -2750 | -200 | 364.0477 | -9.101% | 94.74% | 95% | 0% | 3514 | -61
[5 empty] | 2019-01-17 | 38 | 403 | 3448 | -58 | 0 | 0 | 3506 | 3371.3108 | 3371.3108 | 3371.3108 | 2940.5606 | 780 | 200 | 3920.5606 | 98.01% | 95% | 100% | -66.3616 | 3304.9492 | -2750 | -200 | 354.9492 | -8.874% | 94.74% | 95% | 0% | 3506 | -58
[5 empty] | 2019-01-17 | 39 | 403.5 | 3463 | -55 | 0 | 0 | 3518 | 3390.1072 | 3390.1072 | 3390.1072 | 2940.5606 | 780 | 200 | 3920.5606 | 98.01% | 95% | 100% | -62.9291 | 3327.1781 | -2750 | -200 | 377.1781 | -9.429% | 94.73% | 95% | 0% | 3518 | -55
[5 empty] | 2019-01-17 | 40 | 404 | 3425 | -52 | 0 | 0 | 3477 | 3325.8862 | 3325.8862 | 3325.8862 | 2940.5606 | 780 | 200 | 3920.5606 | 98.01% | 95% | 100% | -59.4966 | 3266.3897 | -2750 | -200 | 316.3897 | -7.91% | 94.72% | 95% | 0% | 3477 | -52
[5 empty] | 2019-01-17 | 41 | 404.5 | 3371 | -50 | 0 | 0 | 3421 | 3238.1698 | 3238.1698 | 3238.1698 | 2940.5606 | 780 | 200 | 3920.5606 | 98.01% | 95% | 100% | -57.2082 | 3180.9616 | -2750 | -200 | 230.9616 | -5.774% | 94.72% | 95% | 0% | 3421 | -50
[5 empty] | 2019-01-17 | 42 | 405 | 3267 | -48 | 0 | 0 | 3315 | 3072.1352 | 3072.1352 | 3072.1352 | 2940.5606 | 780 | 200 | 3920.5606 | 98.01% | 95% | 100% | -54.9199 | 3017.2153 | -2750 | -200 | 67.2153 | -1.68% | 94.71% | 95% | 0% | 3315 | -48
[5 empty] | 2019-01-17 | 43 | 405.5 | 3119 | -48 | 0 | 0 | 3167 | 2840.3133 | 2840.3133 | 2840.3133 | 2938.9942 | 780 | 200 | 3918.9942 | 97.97% | 95% | 100% | -54.9199 | 2785.3934 | -2750 | -200 | -164.6066 | 4.115% | 94.69% | 95% | 0% | 3167 | -48
[5 empty] | 2019-01-17 | 44 | 406 | 2928 | -48 | 0 | 0 | 2976 | 2541.1377 | 2541.1377 | 2541.1377 | 2938.9942 | 780 | 200 | 3918.9942 | 97.97% | 95% | 100% | -54.9199 | 2486.2178 | -2750 | -200 | -463.7822 | 11.59% | 94.69% | 95% | 0% | 2976 | -48
[5 empty] | 2019-01-17 | 45 | 406.5 | 2750 | -48 | 0 | 0 | 2798 | 2262.3248 | 2262.3248 | 2262.3248 | 2937.4279 | 780 | 200 | 3917.4279 | 97.94% | 95% | 100% | -54.9199 | 2207.4049 | -2750 | -200 | -742.5951 | 18.56% | 94.68% | 95% | 0% | 2798 | -48
[5 empty] | 2019-01-17 | 46 | 407 | 2587 | -49 | 0 | 0 | 2636 | 2008.5738 | 2008.5738 | 2008.5738 | 2937.4279 | 780 | 200 | 3917.4279 | 97.94% | 95% | 100% | -56.0641 | 1952.5097 | -2750 | -200 | -997.4903 | 24.94% | 94.66% | 95% | 0% | 2636 | -49
[5 empty] | 2019-01-17 | 47 | 407.5 | 2428 | -50 | 0 | 0 | 2478 | 1761.0882 | 1761.0882 | 1761.0882 | 2935.8615 | 780 | 200 | 3915.8615 | 97.9% | 95% | 100% | -57.2082 | 1703.88 | -2750 | -200 | -1246.12 | 31.15% | 94.66% | 95% | 0% | 2478 | -50
[5 empty] | 2019-01-17 | 48 | 408 | 2313 | -51 | 0 | 0 | 2364 | 1582.5227 | 1582.5227 | 1582.5227 | 2935.8615 | 780 | 200 | 3915.8615 | 97.9% | 95% | 100% | -58.3524 | 1524.1703 | -2750 | -200 | -1425.8297 | 35.65% | 94.65% | 95% | 0% | 2364 | -51
[5 empty] | 2019-01-18 | 1 | 408.5 | 2280 | -53 | 0 | 0 | 2333 | 1533.9654 | 1533.9654 | 1533.9654 | 2934.2951 | 780 | 200 | 3914.2951 | 97.86% | 95% | 100% | -60.6407 | 1473.3246 | -2750 | -200 | -1476.6754 | 36.92% | 94.64% | 95% | 0% | 2333 | -53
[5 empty] | 2019-01-18 | 2 | 409 | 2303 | -55 | 0 | 0 | 2358 | 1573.1245 | 1573.1245 | 1573.1245 | 2934.2951 | 780 | 200 | 3914.2951 | 97.86% | 95% | 100% | -62.9291 | 1510.1954 | -2750 | -200 | -1439.8046 | 36% | 94.64% | 95% | 0% | 2358 | -55
[5 empty] | 2019-01-18 | 3 | 409.5 | 2282 | -57 | 0 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 2934.2951 | 780 | 200 | 3914.2951 | 97.86% | 95% | 100% | -65.2174 | 1478.1462 | -2750 | -200 | -1471.8538 | 36.8% | 94.62% | 95% | 0% | 2339 | -57
[5 empty] | 2019-01-18 | 4 | 410 | 2227 | -59 | 0 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 2932.7288 | 780 | 200 | 3912.7288 | 97.82% | 95% | 100% | -67.5057 | 1392.8405 | -2750 | -200 | -1557.1595 | 38.93% | 94.61% | 95% | 0% | 2286 | -59
[5 empty] | 2019-01-18 | 5 | 410.5 | 2194 | -61 | 0 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 2932.7288 | 780 | 200 | 3912.7288 | 97.82% | 95% | 100% | -69.7941 | 1341.9949 | -2750 | -200 | -1608.0051 | 40.2% | 94.61% | 95% | 0% | 2255 | -61
[5 empty] | 2019-01-18 | 6 | 411 | 2173 | -63 | 0 | 0 | 2236 | 1382.028 | 1382.028 | 1382.028 | 2932.7288 | 780 | 200 | 3912.7288 | 97.82% | 95% | 100% | -72.0824 | 1309.9456 | -2750 | -200 | -1640.0544 | 41% | 94.6% | 95% | 0% | 2236 | -63
[5 empty] | 2019-01-18 | 7 | 411.5 | 2137 | -66 | 0 | 0 | 2203 | 1330.338 | 1330.338 | 1330.338 | 2932.7288 | 780 | 200 | 3912.7288 | 97.82% | 95% | 100% | -75.5149 | 1254.8231 | -2750 | -200 | -1695.1769 | 42.38% | 94.6% | 95% | 0% | 2203 | -66
[5 empty] | 2019-01-18 | 8 | 412 | 2097 | -70 | 0 | 0 | 2167 | 1273.9489 | 1273.9489 | 1273.9489 | 2932.7288 | 780 | 200 | 3912.7288 | 97.82% | 95% | 100% | -80.0915 | 1193.8574 | -2750 | -200 | -1756.1426 | 43.9% | 94.59% | 95% | 0% | 2167 | -70
[5 empty] | 2019-01-18 | 9 | 412.5 | 2079 | -73 | 0 | 0 | 2152 | 1250.4534 | 1250.4534 | 1250.4534 | 2931.1624 | 780 | 200 | 3911.1624 | 97.78% | 95% | 100% | -83.524 | 1166.9294 | -2750 | -200 | -1783.0706 | 44.58% | 94.58% | 95% | 0% | 2152 | -73
[5 empty] | 2019-01-18 | 10 | 413 | 2083 | -76 | 0 | 0 | 2159 | 1261.418 | 1261.418 | 1261.418 | 2931.1624 | 780 | 200 | 3911.1624 | 97.78% | 95% | 100% | -86.9565 | 1174.4615 | -2750 | -200 | -1775.5385 | 44.39% | 94.57% | 95% | 0% | 2159 | -76
[5 empty] | 2019-01-18 | 11 | 413.5 | 2131 | -79 | 0 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 2931.1624 | 780 | 200 | 3911.1624 | 97.78% | 95% | 100% | -90.389 | 1250.9135 | -2750 | -200 | -1699.0865 | 42.48% | 94.57% | 95% | 0% | 2210 | -79
[5 empty] | 2019-01-18 | 12 | 414 | 2239 | -81 | 0 | 0 | 2320 | 1513.6026 | 1513.6026 | 1513.6026 | 2931.1624 | 780 | 200 | 3911.1624 | 97.78% | 95% | 100% | -92.6773 | 1420.9253 | -2750 | -200 | -1529.0747 | 38.23% | 94.56% | 95% | 0% | 2320 | -81
[5 empty] | 2019-01-18 | 13 | 414.5 | 2486 | -84 | 0 | 0 | 2570 | 1905.1937 | 1905.1937 | 1905.1937 | 2931.1624 | 780 | 200 | 3911.1624 | 97.78% | 95% | 100% | -96.1098 | 1809.0839 | -2750 | -200 | -1140.9161 | 28.52% | 94.56% | 95% | 0% | 2570 | -84
[5 empty] | 2019-01-18 | 14 | 415 | 2738 | -86 | 0 | 0 | 2824 | 2303.0503 | 2303.0503 | 2303.0503 | 2931.1624 | 780 | 200 | 3911.1624 | 97.78% | 95% | 100% | -98.3982 | 2204.6521 | -2750 | -200 | -745.3479 | 18.63% | 94.53% | 95% | 0% | 2824 | -86
[5 empty] | 2019-01-18 | 15 | 415.5 | 3038 | -90 | 0 | 0 | 3128 | 2779.2251 | 2779.2251 | 2779.2251 | 2929.596 | 780 | 200 | 3909.596 | 97.74% | 95% | 100% | -102.9748 | 2676.2502 | -2750 | -200 | -273.7498 | 6.844% | 94.53% | 95% | 0% | 3128 | -90
[5 empty] | 2019-01-18 | 16 | 416 | 3204 | -93 | 0 | 0 | 3297 | 3043.9406 | 3043.9406 | 3043.9406 | 2929.596 | 780 | 200 | 3909.596 | 97.74% | 95% | 100% | -106.4073 | 2937.5333 | -2750 | -200 | -12.4667 | 0.3117% | 94.53% | 95% | 0% | 3297 | -93
[5 empty] | 2019-01-18 | 17 | 416.5 | 3268 | -98 | 0 | 0 | 3366 | 3152.0198 | 3152.0198 | 3152.0198 | 2929.596 | 780 | 200 | 3909.596 | 97.74% | 95% | 100% | -112.1281 | 3039.8916 | -2750 | -200 | 89.8916 | -2.247% | 94.53% | 95% | 0% | 3366 | -98
[5 empty] | 2019-01-18 | 18 | 417 | 3255 | -114 | 0 | 0 | 3369 | 3156.7189 | 3156.7189 | 3156.7189 | 2929.596 | 780 | 200 | 3909.596 | 97.74% | 95% | 100% | -130.4348 | 3026.2841 | -2750 | -200 | 76.2841 | -1.907% | 94.52% | 95% | 0% | 3369 | -114
[5 empty] | 2019-01-18 | 19 | 417.5 | 3284 | -142 | 0 | 0 | 3426 | 3246.0016 | 3246.0016 | 3246.0016 | 2929.596 | 780 | 200 | 3909.596 | 97.74% | 95% | 100% | -162.4714 | 3083.5303 | -2750 | -200 | 133.5303 | -3.338% | 94.51% | 95% | 0% | 3426 | -142
[5 empty] | 2019-01-18 | 20 | 418 | 3238 | -182 | 1 | 0 | 3420 | 3236.6035 | 3236.6035 | 3236.6035 | 2928.0297 | 780 | 200 | 3908.0297 | 97.7% | 95% | 100% | -208.238 | 3028.3655 | -3550 | -400 | -921.6345 | 23.04% | 94.51% | 95% | 0% | 3420 | -182
[5 empty] | 2019-01-18 | 21 | 418.5 | 3172 | -213 | 1 | 0 | 3385 | 3181.7807 | 3181.7807 | 3181.7807 | 2928.0297 | 780 | 200 | 3908.0297 | 97.7% | 95% | 100% | -243.7071 | 2938.0736 | -3550 | -400 | -1011.9264 | 25.3% | 94.5% | 95% | 0% | 3385 | -213
[5 empty] | 2019-01-18 | 22 | 419 | 3118 | -237 | 1 | 0 | 3355 | 3134.7898 | 3134.7898 | 3134.7898 | 2926.4633 | 780 | 200 | 3906.4633 | 97.66% | 95% | 100% | -271.167 | 2863.6227 | -3550 | -400 | -1086.3773 | 27.16% | 94.5% | 95% | 0% | 3355 | -237
[5 empty] | 2019-01-18 | 23 | 419.5 | 3084 | -259 | 1 | 0 | 3343 | 3115.9934 | 3115.9934 | 3115.9934 | 2924.8969 | 780 | 200 | 3904.8969 | 97.62% | 95% | 100% | -296.3387 | 2819.6547 | -3550 | -400 | -1130.3453 | 28.26% | 94.49% | 95% | 0% | 3343 | -259
[5 empty] | 2019-01-18 | 24 | 420 | 3047 | -265 | 1 | 0 | 3312 | 3067.4361 | 3067.4361 | 3067.4361 | 2924.8969 | 780 | 200 | 3904.8969 | 97.62% | 95% | 100% | -303.2037 | 2764.2324 | -3550 | -400 | -1185.7676 | 29.64% | 94.47% | 95% | 0% | 3312 | -265
[5 empty] | 2019-01-18 | 25 | 420.5 | 3033 | -268 | 1 | 0 | 3301 | 3050.2061 | 3050.2061 | 3050.2061 | 2924.8969 | 780 | 200 | 3904.8969 | 97.62% | 95% | 100% | -306.6362 | 2743.5699 | -3550 | -400 | -1206.4301 | 30.16% | 94.47% | 95% | 0% | 3301 | -268
[5 empty] | 2019-01-18 | 26 | 421 | 3017 | -264 | 1 | 0 | 3281 | 3018.8788 | 3018.8788 | 3018.8788 | 2924.8969 | 780 | 200 | 3904.8969 | 97.62% | 95% | 100% | -302.0595 | 2716.8193 | -3550 | -400 | -1233.1807 | 30.83% | 94.46% | 95% | 0% | 3281 | -264
[5 empty] | 2019-01-18 | 27 | 421.5 | 3006 | -254 | 1 | 0 | 3260 | 2985.9852 | 2985.9852 | 2985.9852 | 2924.8969 | 780 | 200 | 3904.8969 | 97.62% | 95% | 100% | -290.6178 | 2695.3673 | -3550 | -400 | -1254.6327 | 31.37% | 94.45% | 95% | 0% | 3260 | -254
[5 empty] | 2019-01-18 | 28 | 422 | 3000 | -234 | 1 | 0 | 3234 | 2945.2597 | 2945.2597 | 2945.2597 | 2923.3306 | 780 | 200 | 3903.3306 | 97.58% | 95% | 100% | -267.7346 | 2677.5251 | -3550 | -400 | -1272.4749 | 31.81% | 94.45% | 95% | 0% | 3234 | -234
[5 empty] | 2019-01-18 | 29 | 422.5 | 3023 | -215 | 1 | 0 | 3238 | 2951.5251 | 2951.5251 | 2951.5251 | 2923.3306 | 780 | 200 | 3903.3306 | 97.58% | 95% | 100% | -245.9954 | 2705.5297 | -3550 | -400 | -1244.4703 | 31.11% | 94.45% | 95% | 0% | 3238 | -215
[5 empty] | 2019-01-18 | 30 | 423 | 3044 | -194 | 1 | 0 | 3238 | 2951.5251 | 2951.5251 | 2951.5251 | 2923.3306 | 780 | 200 | 3903.3306 | 97.58% | 95% | 100% | -221.968 | 2729.5572 | -3550 | -400 | -1220.4428 | 30.51% | 94.43% | 95% | 0% | 3238 | -194
[5 empty] | 2019-01-18 | 31 | 423.5 | 3054 | -173 | 1 | 0 | 3227 | 2934.2951 | 2934.2951 | 2934.2951 | 2921.7642 | 780 | 200 | 3901.7642 | 97.54% | 95% | 100% | -197.9405 | 2736.3546 | -3550 | -400 | -1213.6454 | 30.34% | 94.43% | 95% | 0% | 3227 | -173
[5 empty] | 2019-01-18 | 32 | 424 | 3129 | -156 | 1 | 0 | 3285 | 3025.1443 | 3025.1443 | 3025.1443 | 2921.7642 | 780 | 200 | 3901.7642 | 97.54% | 95% | 100% | -178.4897 | 2846.6546 | -3550 | -400 | -1103.3454 | 27.58% | 94.43% | 95% | 0% | 3285 | -156
[5 empty] | 2019-01-18 | 33 | 424.5 | 3210 | -144 | 1 | 0 | 3354 | 3133.2234 | 3133.2234 | 3133.2234 | 2920.1979 | 780 | 200 | 3900.1979 | 97.5% | 95% | 100% | -164.7597 | 2968.4637 | -3550 | -400 | -981.5363 | 24.54% | 94.4% | 95% | 0% | 3354 | -144
[5 empty] | 2019-01-18 | 34 | 425 | 3297 | -143 | 1 | 0 | 3440 | 3267.9308 | 3267.9308 | 3267.9308 | 2920.1979 | 780 | 200 | 3900.1979 | 97.5% | 95% | 100% | -163.6156 | 3104.3152 | -3550 | -400 | -845.6848 | 21.14% | 94.39% | 95% | 0% | 3440 | -143
[5 empty] | 2019-01-18 | 35 | 425.5 | 3340 | -144 | 1 | 0 | 3484 | 3336.8508 | 3336.8508 | 3336.8508 | 2920.1979 | 780 | 200 | 3900.1979 | 97.5% | 95% | 100% | -164.7597 | 3172.0911 | -3550 | -400 | -777.9089 | 19.45% | 94.39% | 95% | 0% | 3484 | -144
[5 empty] | 2019-01-18 | 36 | 426 | 3324 | -144 | 0 | 0 | 3468 | 3311.789 | 3311.789 | 3311.789 | 2920.1979 | 780 | 200 | 3900.1979 | 97.5% | 95% | 100% | -164.7597 | 3147.0292 | -2750 | -200 | 197.0292 | -4.926% | 94.39% | 95% | 0% | 3468 | -144
[5 empty] | 2019-01-18 | 37 | 426.5 | 3313 | -144 | 0 | 0 | 3457 | 3294.5589 | 3294.5589 | 3294.5589 | 2920.1979 | 780 | 200 | 3900.1979 | 97.5% | 95% | 100% | -164.7597 | 3129.7992 | -2750 | -200 | 179.7992 | -4.495% | 94.38% | 95% | 0% | 3457 | -144
[5 empty] | 2019-01-18 | 38 | 427 | 3312 | -144 | 0 | 0 | 3456 | 3292.9926 | 3292.9926 | 3292.9926 | 2918.6315 | 780 | 200 | 3898.6315 | 97.47% | 95% | 100% | -164.7597 | 3128.2329 | -2750 | -200 | 178.2329 | -4.456% | 94.37% | 95% | 0% | 3456 | -144
[5 empty] | 2019-01-18 | 39 | 427.5 | 3268 | -144 | 0 | 0 | 3412 | 3224.0725 | 3224.0725 | 3224.0725 | 2918.6315 | 780 | 200 | 3898.6315 | 97.47% | 95% | 100% | -164.7597 | 3059.3128 | -2750 | -200 | 109.3128 | -2.733% | 94.37% | 95% | 0% | 3412 | -144
[5 empty] | 2019-01-18 | 40 | 428 | 3170 | -144 | 0 | 0 | 3314 | 3070.5688 | 3070.5688 | 3070.5688 | 2918.6315 | 780 | 200 | 3898.6315 | 97.47% | 95% | 100% | -164.7597 | 2905.8091 | -2750 | -200 | -44.1909 | 1.105% | 94.37% | 95% | 0% | 3314 | -144
[5 empty] | 2019-01-18 | 41 | 428.5 | 3054 | -143 | 0 | 0 | 3197 | 2887.3042 | 2887.3042 | 2887.3042 | 2917.0651 | 780 | 200 | 3897.0651 | 97.43% | 95% | 100% | -163.6156 | 2723.6886 | -2750 | -200 | -226.3114 | 5.658% | 94.36% | 95% | 0% | 3197 | -143
[5 empty] | 2019-01-18 | 42 | 429 | 2921 | -142 | 0 | 0 | 3063 | 2677.4114 | 2677.4114 | 2677.4114 | 2917.0651 | 780 | 200 | 3897.0651 | 97.43% | 95% | 100% | -162.4714 | 2514.94 | -2750 | -200 | -435.06 | 10.88% | 94.35% | 95% | 0% | 3063 | -142
[5 empty] | 2019-01-18 | 43 | 429.5 | 2780 | -140 | 0 | 0 | 2920 | 2453.4213 | 2453.4213 | 2453.4213 | 2917.0651 | 780 | 200 | 3897.0651 | 97.43% | 95% | 100% | -160.1831 | 2293.2382 | -2750 | -200 | -656.7618 | 16.42% | 94.34% | 95% | 0% | 2920 | -140
[5 empty] | 2019-01-18 | 44 | 430 | 2640 | -138 | 0 | 0 | 2778 | 2230.9975 | 2230.9975 | 2230.9975 | 2917.0651 | 780 | 200 | 3897.0651 | 97.43% | 95% | 100% | -157.8947 | 2073.1028 | -2750 | -200 | -876.8972 | 21.92% | 94.33% | 95% | 0% | 2778 | -138
[5 empty] | 2019-01-18 | 45 | 430.5 | 2492 | -137 | 0 | 0 | 2629 | 1997.6092 | 1997.6092 | 1997.6092 | 2915.4988 | 780 | 200 | 3895.4988 | 97.39% | 95% | 100% | -156.7506 | 1840.8587 | -2750 | -200 | -1109.1413 | 27.73% | 94.33% | 95% | 0% | 2629 | -137
[5 empty] | 2019-01-18 | 46 | 431 | 2360 | -135 | 0 | 0 | 2495 | 1787.7164 | 1787.7164 | 1787.7164 | 2915.4988 | 780 | 200 | 3895.4988 | 97.39% | 95% | 100% | -154.4622 | 1633.2542 | -2750 | -200 | -1316.7458 | 32.92% | 94.32% | 95% | 0% | 2495 | -135
[5 empty] | 2019-01-18 | 47 | 431.5 | 2230 | -131 | 0 | 0 | 2361 | 1577.8236 | 1577.8236 | 1577.8236 | 2915.4988 | 780 | 200 | 3895.4988 | 97.39% | 95% | 100% | -149.8856 | 1427.938 | -2750 | -200 | -1522.062 | 38.05% | 94.32% | 95% | 0% | 2361 | -131
[5 empty] | 2019-01-18 | 48 | 432 | 2132 | -126 | 0 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 2915.4988 | 780 | 200 | 3895.4988 | 97.39% | 95% | 100% | -144.1648 | 1272.3233 | -2750 | -200 | -1677.6767 | 41.94% | 94.32% | 95% | 0% | 2258 | -126
[5 empty] | 2019-01-19 | 1 | 432.5 | 2116 | -122 | 0 | 0 | 2238 | 1385.1608 | 1385.1608 | 1385.1608 | 2913.9324 | 780 | 200 | 3893.9324 | 97.35% | 95% | 100% | -139.5881 | 1245.5727 | -2750 | -200 | -1704.4273 | 42.61% | 94.31% | 95% | 0% | 2238 | -122
[5 empty] | 2019-01-19 | 2 | 433 | 2148 | -118 | 0 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 2913.9324 | 780 | 200 | 3893.9324 | 97.35% | 95% | 100% | -135.0114 | 1294.0075 | -2750 | -200 | -1655.9925 | 41.4% | 94.3% | 95% | 0% | 2266 | -118
[5 empty] | 2019-01-19 | 3 | 433.5 | 2120 | -114 | 0 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 2913.9324 | 780 | 200 | 3893.9324 | 97.35% | 95% | 100% | -130.4348 | 1248.4605 | -2750 | -200 | -1701.5395 | 42.54% | 94.3% | 95% | 0% | 2234 | -114
[5 empty] | 2019-01-19 | 4 | 434 | 2059 | -111 | 0 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 2912.366 | 780 | 200 | 3892.366 | 97.31% | 95% | 100% | -127.0023 | 1151.6457 | -2750 | -200 | -1798.3543 | 44.96% | 94.3% | 95% | 0% | 2170 | -111
[5 empty] | 2019-01-19 | 5 | 434.5 | 2023 | -107 | 0 | 0 | 2130 | 1215.9934 | 1215.9934 | 1215.9934 | 2912.366 | 780 | 200 | 3892.366 | 97.31% | 95% | 100% | -122.4256 | 1093.5678 | -2750 | -200 | -1856.4322 | 46.41% | 94.3% | 95% | 0% | 2130 | -107
[5 empty] | 2019-01-19 | 6 | 435 | 2013 | -104 | 0 | 0 | 2117 | 1195.6307 | 1195.6307 | 1195.6307 | 2912.366 | 780 | 200 | 3892.366 | 97.31% | 95% | 100% | -118.9931 | 1076.6375 | -2750 | -200 | -1873.3625 | 46.83% | 94.29% | 95% | 0% | 2117 | -104
[5 empty] | 2019-01-19 | 7 | 435.5 | 1978 | -100 | 0 | 0 | 2078 | 1134.5425 | 1134.5425 | 1134.5425 | 2910.7997 | 780 | 200 | 3890.7997 | 97.27% | 95% | 100% | -114.4165 | 1020.126 | -2750 | -200 | -1929.874 | 48.25% | 94.29% | 95% | 0% | 2078 | -100
[5 empty] | 2019-01-19 | 8 | 436 | 1942 | -96 | 0 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 2910.7997 | 780 | 200 | 3890.7997 | 97.27% | 95% | 100% | -109.8398 | 962.0481 | -2750 | -200 | -1987.9519 | 49.7% | 94.29% | 95% | 0% | 2038 | -96
[5 empty] | 2019-01-19 | 9 | 436.5 | 1915 | -93 | 0 | 0 | 2008 | 1024.8969 | 1024.8969 | 1024.8969 | 2910.7997 | 780 | 200 | 3890.7997 | 97.27% | 95% | 100% | -106.4073 | 918.4896 | -2750 | -200 | -2031.5104 | 50.79% | 94.28% | 95% | 0% | 2008 | -93
[5 empty] | 2019-01-19 | 10 | 437 | 1915 | -90 | 0 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 2910.7997 | 780 | 200 | 3890.7997 | 97.27% | 95% | 100% | -102.9748 | 917.223 | -2750 | -200 | -2032.777 | 50.82% | 94.27% | 95% | 0% | 2005 | -90
[5 empty] | 2019-01-19 | 11 | 437.5 | 1943 | -89 | 0 | 0 | 2032 | 1062.4897 | 1062.4897 | 1062.4897 | 2909.2333 | 780 | 200 | 3889.2333 | 97.23% | 95% | 100% | -101.8307 | 960.659 | -2750 | -200 | -1989.341 | 49.73% | 94.26% | 95% | 0% | 2032 | -89
[5 empty] | 2019-01-19 | 12 | 438 | 1980 | -87 | 0 | 0 | 2067 | 1117.3124 | 1117.3124 | 1117.3124 | 2909.2333 | 780 | 200 | 3889.2333 | 97.23% | 95% | 100% | -99.5423 | 1017.7701 | -2750 | -200 | -1932.2299 | 48.31% | 94.21% | 95% | 0% | 2067 | -87
[5 empty] | 2019-01-19 | 13 | 438.5 | 2076 | -84 | 0 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 2909.2333 | 780 | 200 | 3889.2333 | 97.23% | 95% | 100% | -96.1098 | 1166.8745 | -2750 | -200 | -1783.1255 | 44.58% | 94.21% | 95% | 0% | 2160 | -84
[5 empty] | 2019-01-19 | 14 | 439 | 2176 | -82 | 0 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 2909.2333 | 780 | 200 | 3889.2333 | 97.23% | 95% | 100% | -93.8215 | 1322.6665 | -2750 | -200 | -1627.3335 | 40.68% | 94.19% | 95% | 0% | 2258 | -82
[5 empty] | 2019-01-19 | 15 | 439.5 | 2314 | -81 | 0 | 0 | 2395 | 1631.08 | 1631.08 | 1631.08 | 2909.2333 | 780 | 200 | 3889.2333 | 97.23% | 95% | 100% | -92.6773 | 1538.4026 | -2750 | -200 | -1411.5974 | 35.29% | 94.18% | 95% | 0% | 2395 | -81
[5 empty] | 2019-01-19 | 16 | 440 | 2434 | -80 | 0 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 2909.2333 | 780 | 200 | 3889.2333 | 97.23% | 95% | 100% | -91.5332 | 1725.9441 | -2750 | -200 | -1224.0559 | 30.6% | 94.17% | 95% | 0% | 2514 | -80
[5 empty] | 2019-01-19 | 17 | 440.5 | 2595 | -79 | 0 | 0 | 2674 | 2068.0956 | 2068.0956 | 2068.0956 | 2907.6669 | 780 | 200 | 3887.6669 | 97.19% | 95% | 100% | -90.389 | 1977.7066 | -2750 | -200 | -972.2934 | 24.31% | 94.17% | 95% | 0% | 2674 | -79
[5 empty] | 2019-01-19 | 18 | 441 | 2739 | -82 | 0 | 0 | 2821 | 2298.3512 | 2298.3512 | 2298.3512 | 2907.6669 | 780 | 200 | 3887.6669 | 97.19% | 95% | 100% | -93.8215 | 2204.5297 | -2750 | -200 | -745.4703 | 18.64% | 94.17% | 95% | 0% | 2821 | -82
[5 empty] | 2019-01-19 | 19 | 441.5 | 2870 | -92 | 1 | 0 | 2962 | 2519.2086 | 2519.2086 | 2519.2086 | 2907.6669 | 780 | 200 | 3887.6669 | 97.19% | 95% | 100% | -105.2632 | 2413.9454 | -3550 | -400 | -1536.0546 | 38.4% | 94.17% | 95% | 0% | 2962 | -92
[5 empty] | 2019-01-19 | 20 | 442 | 2923 | -102 | 1 | 0 | 3025 | 2617.8895 | 2617.8895 | 2617.8895 | 2907.6669 | 780 | 200 | 3887.6669 | 97.19% | 95% | 100% | -116.7048 | 2501.1847 | -3550 | -400 | -1448.8153 | 36.22% | 94.16% | 95% | 0% | 3025 | -102
[5 empty] | 2019-01-19 | 21 | 442.5 | 2960 | -121 | 1 | 0 | 3081 | 2705.6059 | 2705.6059 | 2705.6059 | 2906.1006 | 780 | 200 | 3886.1006 | 97.15% | 95% | 100% | -138.4439 | 2567.162 | -3550 | -400 | -1382.838 | 34.57% | 94.16% | 95% | 0% | 3081 | -121
[5 empty] | 2019-01-19 | 22 | 443 | 2954 | -138 | 1 | 0 | 3092 | 2722.8359 | 2722.8359 | 2722.8359 | 2906.1006 | 780 | 200 | 3886.1006 | 97.15% | 95% | 100% | -157.8947 | 2564.9412 | -3550 | -400 | -1385.0588 | 34.63% | 94.16% | 95% | 0% | 3092 | -138
[5 empty] | 2019-01-19 | 23 | 443.5 | 2956 | -150 | 1 | 0 | 3106 | 2744.765 | 2744.765 | 2744.765 | 2906.1006 | 780 | 200 | 3886.1006 | 97.15% | 95% | 100% | -171.6247 | 2573.1403 | -3550 | -400 | -1376.8597 | 34.42% | 94.15% | 95% | 0% | 3106 | -150
[5 empty] | 2019-01-19 | 24 | 444 | 2956 | -153 | 1 | 0 | 3109 | 2749.4641 | 2749.4641 | 2749.4641 | 2906.1006 | 780 | 200 | 3886.1006 | 97.15% | 95% | 100% | -175.0572 | 2574.4069 | -3550 | -400 | -1375.5931 | 34.39% | 94.15% | 95% | 0% | 3109 | -153
[5 empty] | 2019-01-19 | 25 | 444.5 | 2968 | -145 | 1 | 0 | 3113 | 2755.7296 | 2755.7296 | 2755.7296 | 2904.5342 | 780 | 200 | 3884.5342 | 97.11% | 95% | 100% | -165.9039 | 2589.8257 | -3550 | -400 | -1360.1743 | 34% | 94.14% | 95% | 0% | 3113 | -145
[5 empty] | 2019-01-19 | 26 | 445 | 2961 | -143 | 1 | 0 | 3104 | 2741.6323 | 2741.6323 | 2741.6323 | 2904.5342 | 780 | 200 | 3884.5342 | 97.11% | 95% | 100% | -163.6156 | 2578.0168 | -3550 | -400 | -1371.9832 | 34.3% | 94.14% | 95% | 0% | 3104 | -143
[5 empty] | 2019-01-19 | 27 | 445.5 | 2950 | -134 | 1 | 0 | 3084 | 2710.305 | 2710.305 | 2710.305 | 2904.5342 | 780 | 200 | 3884.5342 | 97.11% | 95% | 100% | -153.3181 | 2556.987 | -3550 | -400 | -1393.013 | 34.83% | 94.14% | 95% | 0% | 3084 | -134
[5 empty] | 2019-01-19 | 28 | 446 | 2938 | -122 | 1 | 0 | 3060 | 2672.7123 | 2672.7123 | 2672.7123 | 2904.5342 | 780 | 200 | 3884.5342 | 97.11% | 95% | 100% | -139.5881 | 2533.1242 | -3550 | -400 | -1416.8758 | 35.42% | 94.14% | 95% | 0% | 3060 | -122
[5 empty] | 2019-01-19 | 29 | 446.5 | 2938 | -105 | 1 | 0 | 3043 | 2646.0841 | 2646.0841 | 2646.0841 | 2904.5342 | 780 | 200 | 3884.5342 | 97.11% | 95% | 100% | -120.1373 | 2525.9468 | -3550 | -400 | -1424.0532 | 35.6% | 94.14% | 95% | 0% | 3043 | -105
[5 empty] | 2019-01-19 | 30 | 447 | 2950 | -86 | 1 | 0 | 3036 | 2635.1195 | 2635.1195 | 2635.1195 | 2904.5342 | 780 | 200 | 3884.5342 | 97.11% | 95% | 100% | -98.3982 | 2536.7214 | -3550 | -400 | -1413.2786 | 35.33% | 94.13% | 95% | 0% | 3036 | -86
[5 empty] | 2019-01-19 | 31 | 447.5 | 2974 | -68 | 1 | 0 | 3042 | 2644.5177 | 2644.5177 | 2644.5177 | 2904.5342 | 780 | 200 | 3884.5342 | 97.11% | 95% | 100% | -77.8032 | 2566.7145 | -3550 | -400 | -1383.2855 | 34.58% | 94.1% | 95% | 0% | 3042 | -68
[5 empty] | 2019-01-19 | 32 | 448 | 2998 | -53 | 1 | 0 | 3051 | 2658.615 | 2658.615 | 2658.615 | 2904.5342 | 780 | 200 | 3884.5342 | 97.11% | 95% | 100% | -60.6407 | 2597.9743 | -3550 | -400 | -1352.0257 | 33.8% | 94.09% | 95% | 0% | 3051 | -53
[5 empty] | 2019-01-19 | 33 | 448.5 | 3094 | -45 | 1 | 0 | 3139 | 2796.4551 | 2796.4551 | 2796.4551 | 2902.9678 | 780 | 200 | 3882.9678 | 97.07% | 95% | 100% | -51.4874 | 2744.9677 | -3550 | -400 | -1205.0323 | 30.13% | 94.09% | 95% | 0% | 3139 | -45
[5 empty] | 2019-01-19 | 34 | 449 | 3217 | -43 | 1 | 0 | 3260 | 2985.9852 | 2985.9852 | 2985.9852 | 2901.4015 | 780 | 200 | 3881.4015 | 97.04% | 95% | 100% | -49.1991 | 2936.7861 | -3550 | -400 | -1013.2139 | 25.33% | 94.09% | 95% | 0% | 3260 | -43
[5 empty] | 2019-01-19 | 35 | 449.5 | 3313 | -42 | 1 | 0 | 3355 | 3134.7898 | 3134.7898 | 3134.7898 | 2901.4015 | 780 | 200 | 3881.4015 | 97.04% | 95% | 100% | -48.0549 | 3086.7349 | -3550 | -400 | -863.2651 | 21.58% | 94.07% | 95% | 0% | 3355 | -42
[5 empty] | 2019-01-19 | 36 | 450 | 3308 | -42 | 0 | 0 | 3350 | 3126.958 | 3126.958 | 3126.958 | 2899.8351 | 780 | 200 | 3879.8351 | 97% | 95% | 100% | -48.0549 | 3078.903 | -2750 | -200 | 128.903 | -3.223% | 94.07% | 95% | 0% | 3350 | -42
[5 empty] | 2019-01-19 | 37 | 450.5 | 3262 | -41 | 0 | 0 | 3303 | 3053.3388 | 3053.3388 | 3053.3388 | 2899.8351 | 780 | 200 | 3879.8351 | 97% | 95% | 100% | -46.9108 | 3006.4281 | -2750 | -200 | 56.4281 | -1.411% | 94.07% | 95% | 0% | 3303 | -41
[5 empty] | 2019-01-19 | 38 | 451 | 3244 | -39 | 0 | 0 | 3283 | 3022.0115 | 3022.0115 | 3022.0115 | 2898.2688 | 780 | 200 | 3878.2688 | 96.96% | 95% | 100% | -44.6224 | 2977.3891 | -2750 | -200 | 27.3891 | -0.6847% | 94.07% | 95% | 0% | 3283 | -39
[5 empty] | 2019-01-19 | 39 | 451.5 | 3173 | -38 | 0 | 0 | 3211 | 2909.2333 | 2909.2333 | 2909.2333 | 2898.2688 | 780 | 200 | 3878.2688 | 96.96% | 95% | 100% | -43.4783 | 2865.755 | -2750 | -200 | -84.245 | 2.106% | 94.07% | 95% | 0% | 3211 | -38
[5 empty] | 2019-01-19 | 40 | 452 | 3058 | -37 | 0 | 0 | 3095 | 2727.535 | 2727.535 | 2727.535 | 2898.2688 | 780 | 200 | 3878.2688 | 96.96% | 95% | 100% | -42.3341 | 2685.2009 | -2750 | -200 | -264.7991 | 6.62% | 94.07% | 95% | 0% | 3095 | -37
[5 empty] | 2019-01-19 | 41 | 452.5 | 3007 | -35 | 0 | 0 | 3042 | 2644.5177 | 2644.5177 | 2644.5177 | 2898.2688 | 780 | 200 | 3878.2688 | 96.96% | 95% | 100% | -40.0458 | 2604.472 | -2750 | -200 | -345.528 | 8.638% | 94.05% | 95% | 0% | 3042 | -35
[5 empty] | 2019-01-19 | 42 | 453 | 2903 | -34 | 0 | 0 | 2937 | 2480.0495 | 2480.0495 | 2480.0495 | 2898.2688 | 780 | 200 | 3878.2688 | 96.96% | 95% | 100% | -38.9016 | 2441.1479 | -2750 | -200 | -508.8521 | 12.72% | 94.05% | 95% | 0% | 2937 | -34
[5 empty] | 2019-01-19 | 43 | 453.5 | 2802 | -32 | 0 | 0 | 2834 | 2318.7139 | 2318.7139 | 2318.7139 | 2898.2688 | 780 | 200 | 3878.2688 | 96.96% | 95% | 100% | -36.6133 | 2282.1007 | -2750 | -200 | -667.8993 | 16.7% | 94.03% | 95% | 0% | 2834 | -32
[5 empty] | 2019-01-19 | 44 | 454 | 2700 | -31 | 0 | 0 | 2731 | 2157.3784 | 2157.3784 | 2157.3784 | 2898.2688 | 780 | 200 | 3878.2688 | 96.96% | 95% | 100% | -35.4691 | 2121.9093 | -2750 | -200 | -828.0907 | 20.7% | 94.02% | 95% | 0% | 2731 | -31
[5 empty] | 2019-01-19 | 45 | 454.5 | 2581 | -30 | 0 | 0 | 2611 | 1969.4147 | 1969.4147 | 1969.4147 | 2896.7024 | 780 | 200 | 3876.7024 | 96.92% | 95% | 100% | -34.3249 | 1935.0897 | -2750 | -200 | -1014.9103 | 25.37% | 94.01% | 95% | 0% | 2611 | -30
[5 empty] | 2019-01-19 | 46 | 455 | 2485 | -29 | 0 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 2896.7024 | 780 | 200 | 3876.7024 | 96.92% | 95% | 100% | -33.1808 | 1784.2966 | -2750 | -200 | -1165.7034 | 29.14% | 94.01% | 95% | 0% | 2514 | -29
[5 empty] | 2019-01-19 | 47 | 455.5 | 2362 | -27 | 0 | 0 | 2389 | 1621.6818 | 1621.6818 | 1621.6818 | 2896.7024 | 780 | 200 | 3876.7024 | 96.92% | 95% | 100% | -30.8924 | 1590.7893 | -2750 | -200 | -1359.2107 | 33.98% | 94% | 95% | 0% | 2389 | -27
[5 empty] | 2019-01-19 | 48 | 456 | 2281 | -25 | 0 | 0 | 2306 | 1491.6735 | 1491.6735 | 1491.6735 | 2896.7024 | 780 | 200 | 3876.7024 | 96.92% | 95% | 100% | -28.6041 | 1463.0694 | -2750 | -200 | -1486.9306 | 37.17% | 93.99% | 95% | 0% | 2306 | -25
[5 empty] | 2019-01-20 | 1 | 456.5 | 2260 | -24 | 0 | 0 | 2284 | 1457.2135 | 1457.2135 | 1457.2135 | 2895.136 | 780 | 200 | 3875.136 | 96.88% | 95% | 100% | -27.46 | 1429.7536 | -2750 | -200 | -1520.2464 | 38.01% | 93.99% | 95% | 0% | 2284 | -24
[5 empty] | 2019-01-20 | 2 | 457 | 2283 | -24 | 0 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 2895.136 | 780 | 200 | 3875.136 | 96.88% | 95% | 100% | -27.46 | 1465.7799 | -2750 | -200 | -1484.2201 | 37.11% | 93.98% | 95% | 0% | 2307 | -24
[5 empty] | 2019-01-20 | 3 | 457.5 | 2246 | -24 | 0 | 0 | 2270 | 1435.2844 | 1435.2844 | 1435.2844 | 2895.136 | 780 | 200 | 3875.136 | 96.88% | 95% | 100% | -27.46 | 1407.8245 | -2750 | -200 | -1542.1755 | 38.55% | 93.96% | 95% | 0% | 2270 | -24
[5 empty] | 2019-01-20 | 4 | 458 | 2173 | -24 | 0 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 2893.5697 | 780 | 200 | 3873.5697 | 96.84% | 95% | 100% | -27.46 | 1293.4799 | -2750 | -200 | -1656.5201 | 41.41% | 93.94% | 95% | 0% | 2197 | -24
[5 empty] | 2019-01-20 | 5 | 458.5 | 2140 | -24 | 0 | 0 | 2164 | 1269.2498 | 1269.2498 | 1269.2498 | 2892.0033 | 780 | 200 | 3872.0033 | 96.8% | 95% | 100% | -27.46 | 1241.7898 | -2750 | -200 | -1708.2102 | 42.71% | 93.92% | 95% | 0% | 2164 | -24
[5 empty] | 2019-01-20 | 6 | 459 | 2120 | -24 | 0 | 0 | 2144 | 1237.9225 | 1237.9225 | 1237.9225 | 2892.0033 | 780 | 200 | 3872.0033 | 96.8% | 95% | 100% | -27.46 | 1210.4626 | -2750 | -200 | -1739.5374 | 43.49% | 93.92% | 95% | 0% | 2144 | -24
[5 empty] | 2019-01-20 | 7 | 459.5 | 2073 | -24 | 0 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 2890.4369 | 780 | 200 | 3870.4369 | 96.76% | 95% | 100% | -27.46 | 1136.8434 | -2750 | -200 | -1813.1566 | 45.33% | 93.91% | 95% | 0% | 2097 | -24
[5 empty] | 2019-01-20 | 8 | 460 | 2042 | -24 | 0 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 2890.4369 | 780 | 200 | 3870.4369 | 96.76% | 95% | 100% | -27.46 | 1088.2861 | -2750 | -200 | -1861.7139 | 46.54% | 93.89% | 95% | 0% | 2066 | -24
[5 empty] | 2019-01-20 | 9 | 460.5 | 1995 | -24 | 0 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 2890.4369 | 780 | 200 | 3870.4369 | 96.76% | 95% | 100% | -27.46 | 1014.667 | -2750 | -200 | -1935.333 | 48.38% | 93.89% | 95% | 0% | 2019 | -24
[5 empty] | 2019-01-20 | 10 | 461 | 1988 | -25 | 0 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 2890.4369 | 780 | 200 | 3870.4369 | 96.76% | 95% | 100% | -28.6041 | 1004.1247 | -2750 | -200 | -1945.8753 | 48.65% | 93.87% | 95% | 0% | 2013 | -25
[5 empty] | 2019-01-20 | 11 | 461.5 | 1997 | -26 | 0 | 0 | 2023 | 1048.3924 | 1048.3924 | 1048.3924 | 2888.8706 | 780 | 200 | 3868.8706 | 96.72% | 95% | 100% | -29.7483 | 1018.6441 | -2750 | -200 | -1931.3559 | 48.28% | 93.86% | 95% | 0% | 2023 | -26
[5 empty] | 2019-01-20 | 12 | 462 | 2014 | -26 | 0 | 0 | 2040 | 1075.0206 | 1075.0206 | 1075.0206 | 2888.8706 | 780 | 200 | 3868.8706 | 96.72% | 95% | 100% | -29.7483 | 1045.2723 | -2750 | -200 | -1904.7277 | 47.62% | 93.86% | 95% | 0% | 2040 | -26
[5 empty] | 2019-01-20 | 13 | 462.5 | 2079 | -26 | 0 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 2888.8706 | 780 | 200 | 3868.8706 | 96.72% | 95% | 100% | -29.7483 | 1147.086 | -2750 | -200 | -1802.914 | 45.07% | 93.85% | 95% | 0% | 2105 | -26
[5 empty] | 2019-01-20 | 14 | 463 | 2137 | -25 | 0 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 2888.8706 | 780 | 200 | 3868.8706 | 96.72% | 95% | 100% | -28.6041 | 1237.5129 | -2750 | -200 | -1712.4871 | 42.81% | 93.85% | 95% | 0% | 2162 | -25
[5 empty] | 2019-01-20 | 15 | 463.5 | 2213 | -27 | 0 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 2888.8706 | 780 | 200 | 3868.8706 | 96.72% | 95% | 100% | -30.8924 | 1357.401 | -2750 | -200 | -1592.599 | 39.81% | 93.85% | 95% | 0% | 2240 | -27
[5 empty] | 2019-01-20 | 16 | 464 | 2281 | -29 | 0 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 2887.3042 | 780 | 200 | 3867.3042 | 96.68% | 95% | 100% | -33.1808 | 1464.7582 | -2750 | -200 | -1485.2418 | 37.13% | 93.84% | 95% | 0% | 2310 | -29
[5 empty] | 2019-01-20 | 17 | 464.5 | 2407 | -33 | 0 | 0 | 2440 | 1701.5664 | 1701.5664 | 1701.5664 | 2885.7378 | 780 | 200 | 3865.7378 | 96.64% | 95% | 100% | -37.7574 | 1663.8089 | -2750 | -200 | -1286.1911 | 32.15% | 93.81% | 95% | 0% | 2440 | -33
[5 empty] | 2019-01-20 | 18 | 465 | 2524 | -49 | 1 | 0 | 2573 | 1909.8928 | 1909.8928 | 1909.8928 | 2885.7378 | 780 | 200 | 3865.7378 | 96.64% | 95% | 100% | -56.0641 | 1853.8288 | -3550 | -400 | -2096.1712 | 52.4% | 93.81% | 95% | 0% | 2573 | -49
[5 empty] | 2019-01-20 | 19 | 465.5 | 2633 | -78 | 1 | 0 | 2711 | 2126.0511 | 2126.0511 | 2126.0511 | 2884.1715 | 780 | 200 | 3864.1715 | 96.6% | 95% | 100% | -89.2449 | 2036.8063 | -3550 | -400 | -1913.1937 | 47.83% | 93.81% | 95% | 0% | 2711 | -78
[5 empty] | 2019-01-20 | 20 | 466 | 2672 | -115 | 1 | 0 | 2787 | 2245.0948 | 2245.0948 | 2245.0948 | 2882.6051 | 780 | 200 | 3862.6051 | 96.57% | 95% | 100% | -131.5789 | 2113.5159 | -3550 | -400 | -1836.4841 | 45.91% | 93.81% | 95% | 0% | 2787 | -115
[5 empty] | 2019-01-20 | 21 | 466.5 | 2690 | -157 | 1 | 0 | 2847 | 2339.0767 | 2339.0767 | 2339.0767 | 2882.6051 | 780 | 200 | 3862.6051 | 96.57% | 95% | 100% | -179.6339 | 2159.4428 | -3550 | -400 | -1790.5572 | 44.76% | 93.81% | 95% | 0% | 2847 | -157
[5 empty] | 2019-01-20 | 22 | 467 | 2668 | -196 | 1 | 0 | 2864 | 2365.7049 | 2365.7049 | 2365.7049 | 2882.6051 | 780 | 200 | 3862.6051 | 96.57% | 95% | 100% | -224.2563 | 2141.4486 | -3550 | -400 | -1808.5514 | 45.21% | 93.8% | 95% | 0% | 2864 | -196
[5 empty] | 2019-01-20 | 23 | 467.5 | 2647 | -222 | 1 | 0 | 2869 | 2373.5367 | 2373.5367 | 2373.5367 | 2882.6051 | 780 | 200 | 3862.6051 | 96.57% | 95% | 100% | -254.0046 | 2119.5321 | -3550 | -400 | -1830.4679 | 45.76% | 93.8% | 95% | 0% | 2869 | -222
[5 empty] | 2019-01-20 | 24 | 468 | 2627 | -247 | 1 | 0 | 2874 | 2381.3685 | 2381.3685 | 2381.3685 | 2882.6051 | 780 | 200 | 3862.6051 | 96.57% | 95% | 100% | -282.6087 | 2098.7598 | -3550 | -400 | -1851.2402 | 46.28% | 93.8% | 95% | 0% | 2874 | -247
[5 empty] | 2019-01-20 | 25 | 468.5 | 2629 | -252 | 1 | 0 | 2881 | 2392.3331 | 2392.3331 | 2392.3331 | 2881.0387 | 780 | 200 | 3861.0387 | 96.53% | 95% | 100% | -288.3295 | 2104.0035 | -3550 | -400 | -1845.9965 | 46.15% | 93.8% | 95% | 0% | 2881 | -252
[5 empty] | 2019-01-20 | 26 | 469 | 2632 | -247 | 1 | 0 | 2879 | 2389.2003 | 2389.2003 | 2389.2003 | 2881.0387 | 780 | 200 | 3861.0387 | 96.53% | 95% | 100% | -282.6087 | 2106.5916 | -3550 | -400 | -1843.4084 | 46.09% | 93.8% | 95% | 0% | 2879 | -247
[5 empty] | 2019-01-20 | 27 | 469.5 | 2638 | -239 | 1 | 0 | 2877 | 2386.0676 | 2386.0676 | 2386.0676 | 2881.0387 | 780 | 200 | 3861.0387 | 96.53% | 95% | 100% | -273.4554 | 2112.6122 | -3550 | -400 | -1837.3878 | 45.93% | 93.79% | 95% | 0% | 2877 | -239
[5 empty] | 2019-01-20 | 28 | 470 | 2640 | -224 | 1 | 0 | 2864 | 2365.7049 | 2365.7049 | 2365.7049 | 2881.0387 | 780 | 200 | 3861.0387 | 96.53% | 95% | 100% | -256.2929 | 2109.412 | -3550 | -400 | -1840.588 | 46.01% | 93.79% | 95% | 0% | 2864 | -224
[5 empty] | 2019-01-20 | 29 | 470.5 | 2683 | -197 | 1 | 0 | 2880 | 2390.7667 | 2390.7667 | 2390.7667 | 2881.0387 | 780 | 200 | 3861.0387 | 96.53% | 95% | 100% | -225.4005 | 2165.3662 | -3550 | -400 | -1784.6338 | 44.62% | 93.78% | 95% | 0% | 2880 | -197
[5 empty] | 2019-01-20 | 30 | 471 | 2741 | -168 | 1 | 0 | 2909 | 2436.1913 | 2436.1913 | 2436.1913 | 2881.0387 | 780 | 200 | 3861.0387 | 96.53% | 95% | 100% | -192.2197 | 2243.9716 | -3550 | -400 | -1706.0284 | 42.65% | 93.77% | 95% | 0% | 2909 | -168
[5 empty] | 2019-01-20 | 31 | 471.5 | 2829 | -131 | 1 | 0 | 2960 | 2516.0758 | 2516.0758 | 2516.0758 | 2879.4724 | 780 | 200 | 3859.4724 | 96.49% | 95% | 100% | -149.8856 | 2366.1903 | -3550 | -400 | -1583.8097 | 39.6% | 93.76% | 95% | 0% | 2960 | -131
[5 empty] | 2019-01-20 | 32 | 472 | 2953 | -92 | 1 | 0 | 3045 | 2649.2168 | 2649.2168 | 2649.2168 | 2877.906 | 780 | 200 | 3857.906 | 96.45% | 95% | 100% | -105.2632 | 2543.9537 | -3550 | -400 | -1406.0463 | 35.15% | 93.76% | 95% | 0% | 3045 | -92
[5 empty] | 2019-01-20 | 33 | 472.5 | 3095 | -71 | 1 | 0 | 3166 | 2838.7469 | 2838.7469 | 2838.7469 | 2877.906 | 780 | 200 | 3857.906 | 96.45% | 95% | 100% | -81.2357 | 2757.5112 | -3550 | -400 | -1192.4888 | 29.81% | 93.76% | 95% | 0% | 3166 | -71
[5 empty] | 2019-01-20 | 34 | 473 | 3280 | -68 | 1 | 0 | 3348 | 3123.8252 | 3123.8252 | 3123.8252 | 2877.906 | 780 | 200 | 3857.906 | 96.45% | 95% | 100% | -77.8032 | 3046.022 | -3550 | -400 | -903.978 | 22.6% | 93.76% | 95% | 0% | 3348 | -68
[5 empty] | 2019-01-20 | 35 | 473.5 | 3393 | -68 | 1 | 0 | 3461 | 3300.8244 | 3300.8244 | 3300.8244 | 2877.906 | 780 | 200 | 3857.906 | 96.45% | 95% | 100% | -77.8032 | 3223.0212 | -3550 | -400 | -726.9788 | 18.17% | 93.76% | 95% | 0% | 3461 | -68
[5 empty] | 2019-01-20 | 36 | 474 | 3373 | -67 | 0 | 0 | 3440 | 3267.9308 | 3267.9308 | 3267.9308 | 2876.3397 | 780 | 200 | 3856.3397 | 96.41% | 95% | 100% | -76.659 | 3191.2717 | -2750 | -200 | 241.2717 | -6.032% | 93.76% | 95% | 0% | 3440 | -67
[5 empty] | 2019-01-20 | 37 | 474.5 | 3322 | -67 | 0 | 0 | 3389 | 3188.0462 | 3188.0462 | 3188.0462 | 2876.3397 | 780 | 200 | 3856.3397 | 96.41% | 95% | 100% | -76.659 | 3111.3871 | -2750 | -200 | 161.3871 | -4.035% | 93.74% | 95% | 0% | 3389 | -67
[5 empty] | 2019-01-20 | 38 | 475 | 3291 | -66 | 0 | 0 | 3357 | 3137.9225 | 3137.9225 | 3137.9225 | 2876.3397 | 780 | 200 | 3856.3397 | 96.41% | 95% | 100% | -75.5149 | 3062.4076 | -2750 | -200 | 112.4076 | -2.81% | 93.74% | 95% | 0% | 3357 | -66
[5 empty] | 2019-01-20 | 39 | 475.5 | 3224 | -64 | 0 | 0 | 3288 | 3029.8434 | 3029.8434 | 3029.8434 | 2874.7733 | 780 | 200 | 3854.7733 | 96.37% | 95% | 100% | -73.2265 | 2956.6168 | -2750 | -200 | 6.6168 | -0.1654% | 93.73% | 95% | 0% | 3288 | -64
[5 empty] | 2019-01-20 | 40 | 476 | 3120 | -63 | 0 | 0 | 3183 | 2865.3751 | 2865.3751 | 2865.3751 | 2874.7733 | 780 | 200 | 3854.7733 | 96.37% | 95% | 100% | -72.0824 | 2793.2927 | -2750 | -200 | -156.7073 | 3.918% | 93.73% | 95% | 0% | 3183 | -63
[5 empty] | 2019-01-20 | 41 | 476.5 | 3035 | -60 | 0 | 0 | 3095 | 2727.535 | 2727.535 | 2727.535 | 2874.7733 | 780 | 200 | 3854.7733 | 96.37% | 95% | 100% | -68.6499 | 2658.8852 | -2750 | -200 | -291.1148 | 7.278% | 93.72% | 95% | 0% | 3095 | -60
[5 empty] | 2019-01-20 | 42 | 477 | 2937 | -58 | 0 | 0 | 2995 | 2570.8986 | 2570.8986 | 2570.8986 | 2874.7733 | 780 | 200 | 3854.7733 | 96.37% | 95% | 100% | -66.3616 | 2504.537 | -2750 | -200 | -445.463 | 11.14% | 93.71% | 95% | 0% | 2995 | -58
[5 empty] | 2019-01-20 | 43 | 477.5 | 2822 | -56 | 0 | 0 | 2878 | 2387.634 | 2387.634 | 2387.634 | 2873.2069 | 780 | 200 | 3853.2069 | 96.33% | 95% | 100% | -64.0732 | 2323.5607 | -2750 | -200 | -626.4393 | 15.66% | 93.7% | 95% | 0% | 2878 | -56
[5 empty] | 2019-01-20 | 44 | 478 | 2684 | -54 | 0 | 0 | 2738 | 2168.343 | 2168.343 | 2168.343 | 2873.2069 | 780 | 200 | 3853.2069 | 96.33% | 95% | 100% | -61.7849 | 2106.5581 | -2750 | -200 | -843.4419 | 21.09% | 93.68% | 95% | 0% | 2738 | -54
[5 empty] | 2019-01-20 | 45 | 478.5 | 2544 | -53 | 0 | 0 | 2597 | 1947.4856 | 1947.4856 | 1947.4856 | 2873.2069 | 780 | 200 | 3853.2069 | 96.33% | 95% | 100% | -60.6407 | 1886.8448 | -2750 | -200 | -1063.1552 | 26.58% | 93.67% | 95% | 0% | 2597 | -53
[5 empty] | 2019-01-20 | 46 | 479 | 2410 | -52 | 0 | 0 | 2462 | 1736.0264 | 1736.0264 | 1736.0264 | 2873.2069 | 780 | 200 | 3853.2069 | 96.33% | 95% | 100% | -59.4966 | 1676.5298 | -2750 | -200 | -1273.4702 | 31.84% | 93.67% | 95% | 0% | 2462 | -52
[5 empty] | 2019-01-20 | 47 | 479.5 | 2265 | -48 | 0 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 2873.2069 | 780 | 200 | 3853.2069 | 96.33% | 95% | 100% | -54.9199 | 1447.7182 | -2750 | -200 | -1502.2818 | 37.56% | 93.65% | 95% | 0% | 2313 | -48
[5 empty] | 2019-01-20 | 48 | 480 | 2181 | -45 | 0 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 2873.2069 | 780 | 200 | 3853.2069 | 96.33% | 95% | 100% | -51.4874 | 1314.877 | -2750 | -200 | -1635.123 | 40.88% | 93.65% | 95% | 0% | 2226 | -45
[5 empty] | 2019-01-21 | 1 | 480.5 | 2170 | -44 | 0 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 2873.2069 | 780 | 200 | 3853.2069 | 96.33% | 95% | 100% | -50.3432 | 1297.2248 | -2750 | -200 | -1652.7752 | 41.32% | 93.64% | 95% | 0% | 2214 | -44
[5 empty] | 2019-01-21 | 2 | 481 | 2205 | -44 | 0 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 2871.6406 | 780 | 200 | 3851.6406 | 96.29% | 95% | 100% | -50.3432 | 1352.0475 | -2750 | -200 | -1597.9525 | 39.95% | 93.63% | 95% | 0% | 2249 | -44
[5 empty] | 2019-01-21 | 3 | 481.5 | 2202 | -43 | 0 | 0 | 2245 | 1396.1253 | 1396.1253 | 1396.1253 | 2871.6406 | 780 | 200 | 3851.6406 | 96.29% | 95% | 100% | -49.1991 | 1346.9262 | -2750 | -200 | -1603.0738 | 40.08% | 93.62% | 95% | 0% | 2245 | -43
[5 empty] | 2019-01-21 | 4 | 482 | 2165 | -43 | 0 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 2871.6406 | 780 | 200 | 3851.6406 | 96.29% | 95% | 100% | -49.1991 | 1288.9707 | -2750 | -200 | -1661.0293 | 41.53% | 93.6% | 95% | 0% | 2208 | -43
[5 empty] | 2019-01-21 | 5 | 482.5 | 2135 | -42 | 0 | 0 | 2177 | 1289.6125 | 1289.6125 | 1289.6125 | 2871.6406 | 780 | 200 | 3851.6406 | 96.29% | 95% | 100% | -48.0549 | 1241.5576 | -2750 | -200 | -1708.4424 | 42.71% | 93.6% | 95% | 0% | 2177 | -42
[5 empty] | 2019-01-21 | 6 | 483 | 2129 | -42 | 0 | 0 | 2171 | 1280.2143 | 1280.2143 | 1280.2143 | 2871.6406 | 780 | 200 | 3851.6406 | 96.29% | 95% | 100% | -48.0549 | 1232.1594 | -2750 | -200 | -1717.8406 | 42.95% | 93.59% | 95% | 0% | 2171 | -42
[5 empty] | 2019-01-21 | 7 | 483.5 | 2103 | -43 | 0 | 0 | 2146 | 1241.0552 | 1241.0552 | 1241.0552 | 2871.6406 | 780 | 200 | 3851.6406 | 96.29% | 95% | 100% | -49.1991 | 1191.8562 | -2750 | -200 | -1758.1438 | 43.95% | 93.59% | 95% | 0% | 2146 | -43
[5 empty] | 2019-01-21 | 8 | 484 | 2076 | -44 | 0 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 2871.6406 | 780 | 200 | 3851.6406 | 96.29% | 95% | 100% | -50.3432 | 1149.9865 | -2750 | -200 | -1800.0135 | 45% | 93.59% | 95% | 0% | 2120 | -44
[5 empty] | 2019-01-21 | 9 | 484.5 | 2071 | -45 | 0 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 2870.0742 | 780 | 200 | 3850.0742 | 96.25% | 95% | 100% | -51.4874 | 1142.5769 | -2750 | -200 | -1807.4231 | 45.19% | 93.55% | 95% | 0% | 2116 | -45
[5 empty] | 2019-01-21 | 10 | 485 | 2088 | -45 | 0 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 2870.0742 | 780 | 200 | 3850.0742 | 96.25% | 95% | 100% | -51.4874 | 1169.2051 | -2750 | -200 | -1780.7949 | 44.52% | 93.54% | 95% | 0% | 2133 | -45
[5 empty] | 2019-01-21 | 11 | 485.5 | 2148 | -47 | 0 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 2870.0742 | 780 | 200 | 3850.0742 | 96.25% | 95% | 100% | -53.7757 | 1264.0313 | -2750 | -200 | -1685.9687 | 42.15% | 93.54% | 95% | 0% | 2195 | -47
[5 empty] | 2019-01-21 | 12 | 486 | 2261 | -49 | 0 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 2870.0742 | 780 | 200 | 3850.0742 | 96.25% | 95% | 100% | -56.0641 | 1441.8749 | -2750 | -200 | -1508.1251 | 37.7% | 93.51% | 95% | 0% | 2310 | -49
[5 empty] | 2019-01-21 | 13 | 486.5 | 2530 | -50 | 0 | 0 | 2580 | 1920.8574 | 1920.8574 | 1920.8574 | 2870.0742 | 780 | 200 | 3850.0742 | 96.25% | 95% | 100% | -57.2082 | 1863.6491 | -2750 | -200 | -1086.3509 | 27.16% | 93.5% | 95% | 0% | 2580 | -50
[5 empty] | 2019-01-21 | 14 | 487 | 2786 | -51 | 0 | 0 | 2837 | 2323.413 | 2323.413 | 2323.413 | 2868.5078 | 780 | 200 | 3848.5078 | 96.21% | 95% | 100% | -58.3524 | 2265.0606 | -2750 | -200 | -684.9394 | 17.12% | 93.49% | 95% | 0% | 2837 | -51
[5 empty] | 2019-01-21 | 15 | 487.5 | 3056 | -55 | 0 | 0 | 3111 | 2752.5969 | 2752.5969 | 2752.5969 | 2866.9415 | 780 | 200 | 3846.9415 | 96.17% | 95% | 100% | -62.9291 | 2689.6678 | -2750 | -200 | -260.3322 | 6.508% | 93.48% | 95% | 0% | 3111 | -55
[5 empty] | 2019-01-21 | 16 | 488 | 3204 | -59 | 0 | 0 | 3263 | 2990.6843 | 2990.6843 | 2990.6843 | 2866.9415 | 780 | 200 | 3846.9415 | 96.17% | 95% | 100% | -67.5057 | 2923.1785 | -2750 | -200 | -26.8215 | 0.6705% | 93.48% | 95% | 0% | 3263 | -59
[5 empty] | 2019-01-21 | 17 | 488.5 | 3296 | -64 | 0 | 0 | 3360 | 3142.6216 | 3142.6216 | 3142.6216 | 2866.9415 | 780 | 200 | 3846.9415 | 96.17% | 95% | 100% | -73.2265 | 3069.3951 | -2750 | -200 | 119.3951 | -2.985% | 93.46% | 95% | 0% | 3360 | -64
[5 empty] | 2019-01-21 | 18 | 489 | 3292 | -83 | 0 | 0 | 3375 | 3166.1171 | 3166.1171 | 3166.1171 | 2866.9415 | 780 | 200 | 3846.9415 | 96.17% | 95% | 100% | -94.9657 | 3071.1514 | -2750 | -200 | 121.1514 | -3.029% | 93.45% | 95% | 0% | 3375 | -83
[5 empty] | 2019-01-21 | 19 | 489.5 | 3321 | -103 | 0 | 0 | 3424 | 3242.8689 | 3242.8689 | 3242.8689 | 2866.9415 | 780 | 200 | 3846.9415 | 96.17% | 95% | 100% | -117.849 | 3125.0199 | -2750 | -200 | 175.0199 | -4.375% | 93.43% | 95% | 0% | 3424 | -103
[5 empty] | 2019-01-21 | 20 | 490 | 3272 | -146 | 1 | 0 | 3418 | 3233.4707 | 3233.4707 | 3233.4707 | 2866.9415 | 780 | 200 | 3846.9415 | 96.17% | 95% | 100% | -167.0481 | 3066.4227 | -3550 | -400 | -883.5773 | 22.09% | 93.42% | 95% | 0% | 3418 | -146
[5 empty] | 2019-01-21 | 21 | 490.5 | 3191 | -185 | 1 | 0 | 3376 | 3167.6834 | 3167.6834 | 3167.6834 | 2865.3751 | 780 | 200 | 3845.3751 | 96.13% | 95% | 100% | -211.6705 | 2956.0129 | -3550 | -400 | -993.9871 | 24.85% | 93.41% | 95% | 0% | 3376 | -185
[5 empty] | 2019-01-21 | 22 | 491 | 3143 | -229 | 1 | 0 | 3372 | 3161.418 | 3161.418 | 3161.418 | 2865.3751 | 780 | 200 | 3845.3751 | 96.13% | 95% | 100% | -262.0137 | 2899.4042 | -3550 | -400 | -1050.5958 | 26.26% | 93.41% | 95% | 0% | 3372 | -229
[5 empty] | 2019-01-21 | 23 | 491.5 | 3060 | -258 | 1 | 0 | 3318 | 3076.8343 | 3076.8343 | 3076.8343 | 2865.3751 | 780 | 200 | 3845.3751 | 96.13% | 95% | 100% | -295.1945 | 2781.6398 | -3550 | -400 | -1168.3602 | 29.21% | 93.4% | 95% | 0% | 3318 | -258
[5 empty] | 2019-01-21 | 24 | 492 | 3032 | -282 | 1 | 0 | 3314 | 3070.5688 | 3070.5688 | 3070.5688 | 2863.8087 | 780 | 200 | 3843.8087 | 96.1% | 95% | 100% | -322.6545 | 2747.9144 | -3550 | -400 | -1202.0856 | 30.05% | 93.37% | 95% | 0% | 3314 | -282
[5 empty] | 2019-01-21 | 25 | 492.5 | 3012 | -292 | 1 | 0 | 3304 | 3054.9052 | 3054.9052 | 3054.9052 | 2863.8087 | 780 | 200 | 3843.8087 | 96.1% | 95% | 100% | -334.0961 | 2720.8091 | -3550 | -400 | -1229.1909 | 30.73% | 93.36% | 95% | 0% | 3304 | -292
[5 empty] | 2019-01-21 | 26 | 493 | 2977 | -296 | 1 | 0 | 3273 | 3006.3479 | 3006.3479 | 3006.3479 | 2862.2424 | 780 | 200 | 3842.2424 | 96.06% | 95% | 100% | -338.6728 | 2667.6751 | -3550 | -400 | -1282.3249 | 32.06% | 93.36% | 95% | 0% | 3273 | -296
[5 empty] | 2019-01-21 | 27 | 493.5 | 2991 | -281 | 1 | 0 | 3272 | 3004.7815 | 3004.7815 | 3004.7815 | 2862.2424 | 780 | 200 | 3842.2424 | 96.06% | 95% | 100% | -321.5103 | 2683.2712 | -3550 | -400 | -1266.7288 | 31.67% | 93.36% | 95% | 0% | 3272 | -281
[5 empty] | 2019-01-21 | 28 | 494 | 3002 | -259 | 1 | 0 | 3261 | 2987.5515 | 2987.5515 | 2987.5515 | 2862.2424 | 780 | 200 | 3842.2424 | 96.06% | 95% | 100% | -296.3387 | 2691.2129 | -3550 | -400 | -1258.7871 | 31.47% | 93.35% | 95% | 0% | 3261 | -259
[5 empty] | 2019-01-21 | 29 | 494.5 | 3031 | -237 | 1 | 0 | 3268 | 2998.5161 | 2998.5161 | 2998.5161 | 2862.2424 | 780 | 200 | 3842.2424 | 96.06% | 95% | 100% | -271.167 | 2727.349 | -3550 | -400 | -1222.651 | 30.57% | 93.34% | 95% | 0% | 3268 | -237
[5 empty] | 2019-01-21 | 30 | 495 | 3063 | -210 | 1 | 0 | 3273 | 3006.3479 | 3006.3479 | 3006.3479 | 2860.676 | 780 | 200 | 3840.676 | 96.02% | 95% | 100% | -240.2746 | 2766.0733 | -3550 | -400 | -1183.9267 | 29.6% | 93.31% | 95% | 0% | 3273 | -210
[5 empty] | 2019-01-21 | 31 | 495.5 | 3107 | -185 | 1 | 0 | 3292 | 3036.1088 | 3036.1088 | 3036.1088 | 2860.676 | 780 | 200 | 3840.676 | 96.02% | 95% | 100% | -211.6705 | 2824.4383 | -3550 | -400 | -1125.5617 | 28.14% | 93.3% | 95% | 0% | 3292 | -185
[5 empty] | 2019-01-21 | 32 | 496 | 3179 | -167 | 1 | 0 | 3346 | 3120.6925 | 3120.6925 | 3120.6925 | 2860.676 | 780 | 200 | 3840.676 | 96.02% | 95% | 100% | -191.0755 | 2929.617 | -3550 | -400 | -1020.383 | 25.51% | 93.3% | 95% | 0% | 3346 | -167
[5 empty] | 2019-01-21 | 33 | 496.5 | 3252 | -159 | 1 | 0 | 3411 | 3222.5062 | 3222.5062 | 3222.5062 | 2859.1096 | 780 | 200 | 3839.1096 | 95.98% | 95% | 100% | -181.9222 | 3040.584 | -3550 | -400 | -909.416 | 22.74% | 93.29% | 95% | 0% | 3411 | -159
[5 empty] | 2019-01-21 | 34 | 497 | 3311 | -162 | 1 | 0 | 3473 | 3319.6208 | 3319.6208 | 3319.6208 | 2859.1096 | 780 | 200 | 3839.1096 | 95.98% | 95% | 100% | -185.3547 | 3134.2661 | -3550 | -400 | -815.7339 | 20.39% | 93.26% | 95% | 0% | 3473 | -162
[5 empty] | 2019-01-21 | 35 | 497.5 | 3333 | -166 | 1 | 0 | 3499 | 3360.3462 | 3360.3462 | 3360.3462 | 2859.1096 | 780 | 200 | 3839.1096 | 95.98% | 95% | 100% | -189.9314 | 3170.4149 | -3550 | -400 | -779.5851 | 19.49% | 93.25% | 95% | 0% | 3499 | -166
[5 empty] | 2019-01-21 | 36 | 498 | 3300 | -170 | 1 | 0 | 3470 | 3314.9217 | 3314.9217 | 3314.9217 | 2859.1096 | 780 | 200 | 3839.1096 | 95.98% | 95% | 100% | -194.508 | 3120.4137 | -3550 | -400 | -829.5863 | 20.74% | 93.24% | 95% | 0% | 3470 | -170
[5 empty] | 2019-01-21 | 37 | 498.5 | 3275 | -171 | 0 | 0 | 3446 | 3277.3289 | 3277.3289 | 3277.3289 | 2857.5433 | 780 | 200 | 3837.5433 | 95.94% | 95% | 100% | -195.6522 | 3081.6768 | -2750 | -200 | 131.6768 | -3.292% | 93.24% | 95% | 0% | 3446 | -171
[5 empty] | 2019-01-21 | 38 | 499 | 3277 | -173 | 0 | 0 | 3450 | 3283.5944 | 3283.5944 | 3283.5944 | 2857.5433 | 780 | 200 | 3837.5433 | 95.94% | 95% | 100% | -197.9405 | 3085.6539 | -2750 | -200 | 135.6539 | -3.391% | 93.24% | 95% | 0% | 3450 | -173
[5 empty] | 2019-01-21 | 39 | 499.5 | 3256 | -171 | 0 | 0 | 3427 | 3247.568 | 3247.568 | 3247.568 | 2855.9769 | 780 | 200 | 3835.9769 | 95.9% | 95% | 100% | -195.6522 | 3051.9158 | -2750 | -200 | 101.9158 | -2.548% | 93.23% | 95% | 0% | 3427 | -171
[5 empty] | 2019-01-21 | 40 | 500 | 3184 | -169 | 0 | 0 | 3353 | 3131.657 | 3131.657 | 3131.657 | 2855.9769 | 780 | 200 | 3835.9769 | 95.9% | 95% | 100% | -193.3638 | 2938.2932 | -2750 | -200 | -11.7068 | 0.2927% | 93.23% | 95% | 0% | 3353 | -169
[5 empty] | 2019-01-21 | 41 | 500.5 | 3066 | -165 | 0 | 0 | 3231 | 2940.5606 | 2940.5606 | 2940.5606 | 2855.9769 | 780 | 200 | 3835.9769 | 95.9% | 95% | 100% | -188.7872 | 2751.7734 | -2750 | -200 | -198.2266 | 4.956% | 93.22% | 95% | 0% | 3231 | -165
[5 empty] | 2019-01-21 | 42 | 501 | 2917 | -162 | 0 | 0 | 3079 | 2702.4732 | 2702.4732 | 2702.4732 | 2855.9769 | 780 | 200 | 3835.9769 | 95.9% | 95% | 100% | -185.3547 | 2517.1185 | -2750 | -200 | -432.8815 | 10.82% | 93.22% | 95% | 0% | 3079 | -162
[5 empty] | 2019-01-21 | 43 | 501.5 | 2763 | -161 | 0 | 0 | 2924 | 2459.6867 | 2459.6867 | 2459.6867 | 2854.4106 | 780 | 200 | 3834.4106 | 95.86% | 95% | 100% | -184.2105 | 2275.4762 | -2750 | -200 | -674.5238 | 16.86% | 93.21% | 95% | 0% | 2924 | -161
[5 empty] | 2019-01-21 | 44 | 502 | 2594 | -161 | 0 | 0 | 2755 | 2194.9711 | 2194.9711 | 2194.9711 | 2854.4106 | 780 | 200 | 3834.4106 | 95.86% | 95% | 100% | -184.2105 | 2010.7606 | -2750 | -200 | -939.2394 | 23.48% | 93.2% | 95% | 0% | 2755 | -161
[5 empty] | 2019-01-21 | 45 | 502.5 | 2440 | -153 | 0 | 0 | 2593 | 1941.2201 | 1941.2201 | 1941.2201 | 2852.8442 | 780 | 200 | 3832.8442 | 95.82% | 95% | 100% | -175.0572 | 1766.1629 | -2750 | -200 | -1183.8371 | 29.6% | 93.18% | 95% | 0% | 2593 | -153
[5 empty] | 2019-01-21 | 46 | 503 | 2305 | -145 | 0 | 0 | 2450 | 1717.23 | 1717.23 | 1717.23 | 2852.8442 | 780 | 200 | 3832.8442 | 95.82% | 95% | 100% | -165.9039 | 1551.3261 | -2750 | -200 | -1398.6739 | 34.97% | 93.18% | 95% | 0% | 2450 | -145
[5 empty] | 2019-01-21 | 47 | 503.5 | 2140 | -143 | 0 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 2852.8442 | 780 | 200 | 3832.8442 | 95.82% | 95% | 100% | -163.6156 | 1292.0316 | -2750 | -200 | -1657.9684 | 41.45% | 93.17% | 95% | 0% | 2283 | -143
[5 empty] | 2019-01-21 | 48 | 504 | 2059 | -141 | 0 | 0 | 2200 | 1325.6389 | 1325.6389 | 1325.6389 | 2852.8442 | 780 | 200 | 3832.8442 | 95.82% | 95% | 100% | -161.3272 | 1164.3117 | -2750 | -200 | -1785.6883 | 44.64% | 93.17% | 95% | 0% | 2200 | -141
[5 empty] | 2019-01-22 | 1 | 504.5 | 2044 | -139 | 0 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 2851.2778 | 780 | 200 | 3831.2778 | 95.78% | 95% | 100% | -159.0389 | 1139.9718 | -2750 | -200 | -1810.0282 | 45.25% | 93.17% | 95% | 0% | 2183 | -139
[5 empty] | 2019-01-22 | 2 | 505 | 2079 | -137 | 0 | 0 | 2216 | 1350.7007 | 1350.7007 | 1350.7007 | 2851.2778 | 780 | 200 | 3831.2778 | 95.78% | 95% | 100% | -156.7506 | 1193.9502 | -2750 | -200 | -1756.0498 | 43.9% | 93.15% | 95% | 0% | 2216 | -137
[5 empty] | 2019-01-22 | 3 | 505.5 | 2067 | -135 | 0 | 0 | 2202 | 1328.7716 | 1328.7716 | 1328.7716 | 2851.2778 | 780 | 200 | 3831.2778 | 95.78% | 95% | 100% | -154.4622 | 1174.3094 | -2750 | -200 | -1775.6906 | 44.39% | 93.15% | 95% | 0% | 2202 | -135
[5 empty] | 2019-01-22 | 4 | 506 | 2013 | -134 | 0 | 0 | 2147 | 1242.6216 | 1242.6216 | 1242.6216 | 2849.7115 | 780 | 200 | 3829.7115 | 95.74% | 95% | 100% | -153.3181 | 1089.3035 | -2750 | -200 | -1860.6965 | 46.52% | 93.14% | 95% | 0% | 2147 | -134
[5 empty] | 2019-01-22 | 5 | 506.5 | 2004 | -132 | 0 | 0 | 2136 | 1225.3916 | 1225.3916 | 1225.3916 | 2849.7115 | 780 | 200 | 3829.7115 | 95.74% | 95% | 100% | -151.0297 | 1074.3618 | -2750 | -200 | -1875.6382 | 46.89% | 93.14% | 95% | 0% | 2136 | -132
[5 empty] | 2019-01-22 | 6 | 507 | 2007 | -130 | 0 | 0 | 2137 | 1226.958 | 1226.958 | 1226.958 | 2849.7115 | 780 | 200 | 3829.7115 | 95.74% | 95% | 100% | -148.7414 | 1078.2165 | -2750 | -200 | -1871.7835 | 46.79% | 93.13% | 95% | 0% | 2137 | -130
[5 empty] | 2019-01-22 | 7 | 507.5 | 1970 | -127 | 0 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 2849.7115 | 780 | 200 | 3829.7115 | 95.74% | 95% | 100% | -145.3089 | 1018.9945 | -2750 | -200 | -1931.0055 | 48.28% | 93.12% | 95% | 0% | 2097 | -127
[5 empty] | 2019-01-22 | 8 | 508 | 1945 | -123 | 0 | 0 | 2068 | 1118.8788 | 1118.8788 | 1118.8788 | 2849.7115 | 780 | 200 | 3829.7115 | 95.74% | 95% | 100% | -140.7323 | 978.1465 | -2750 | -200 | -1971.8535 | 49.3% | 93.12% | 95% | 0% | 2068 | -123
[5 empty] | 2019-01-22 | 9 | 508.5 | 1923 | -121 | 0 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 2849.7115 | 780 | 200 | 3829.7115 | 95.74% | 95% | 100% | -138.4439 | 942.8421 | -2750 | -200 | -2007.1579 | 50.18% | 93.12% | 95% | 0% | 2044 | -121
[5 empty] | 2019-01-22 | 10 | 509 | 1957 | -119 | 0 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 2849.7115 | 780 | 200 | 3829.7115 | 95.74% | 95% | 100% | -136.1556 | 995.2541 | -2750 | -200 | -1954.7459 | 48.87% | 93.12% | 95% | 0% | 2076 | -119
[5 empty] | 2019-01-22 | 11 | 509.5 | 2038 | -115 | 0 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 2849.7115 | 780 | 200 | 3829.7115 | 95.74% | 95% | 100% | -131.5789 | 1120.4408 | -2750 | -200 | -1829.5592 | 45.74% | 93.1% | 95% | 0% | 2153 | -115
[5 empty] | 2019-01-22 | 12 | 510 | 2163 | -111 | 0 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 2849.7115 | 780 | 200 | 3829.7115 | 95.74% | 95% | 100% | -127.0023 | 1314.5476 | -2750 | -200 | -1635.4524 | 40.89% | 93.1% | 95% | 0% | 2274 | -111
[5 empty] | 2019-01-22 | 13 | 510.5 | 2438 | -108 | 0 | 0 | 2546 | 1867.601 | 1867.601 | 1867.601 | 2849.7115 | 780 | 200 | 3829.7115 | 95.74% | 95% | 100% | -123.5698 | 1744.0312 | -2750 | -200 | -1205.9688 | 30.15% | 93.1% | 95% | 0% | 2546 | -108
[5 empty] | 2019-01-22 | 14 | 511 | 2697 | -105 | 0 | 0 | 2802 | 2268.5903 | 2268.5903 | 2268.5903 | 2849.7115 | 780 | 200 | 3829.7115 | 95.74% | 95% | 100% | -120.1373 | 2148.453 | -2750 | -200 | -801.547 | 20.04% | 93.09% | 95% | 0% | 2802 | -105
[5 empty] | 2019-01-22 | 15 | 511.5 | 3002 | -106 | 0 | 0 | 3108 | 2747.8978 | 2747.8978 | 2747.8978 | 2848.1451 | 780 | 200 | 3828.1451 | 95.7% | 95% | 100% | -121.2815 | 2626.6163 | -2750 | -200 | -323.3837 | 8.085% | 93.08% | 95% | 0% | 3108 | -106
[5 empty] | 2019-01-22 | 16 | 512 | 3171 | -106 | 0 | 0 | 3277 | 3012.6134 | 3012.6134 | 3012.6134 | 2848.1451 | 780 | 200 | 3828.1451 | 95.7% | 95% | 100% | -121.2815 | 2891.3319 | -2750 | -200 | -58.6681 | 1.467% | 93.06% | 95% | 0% | 3277 | -106
[5 empty] | 2019-01-22 | 17 | 512.5 | 3239 | -107 | 1 | 0 | 3346 | 3120.6925 | 3120.6925 | 3120.6925 | 2848.1451 | 780 | 200 | 3828.1451 | 95.7% | 95% | 100% | -122.4256 | 2998.2669 | -3550 | -400 | -951.7331 | 23.79% | 93.06% | 95% | 0% | 3346 | -107
[5 empty] | 2019-01-22 | 18 | 513 | 3203 | -138 | 1 | 0 | 3341 | 3112.8607 | 3112.8607 | 3112.8607 | 2845.0124 | 780 | 200 | 3825.0124 | 95.63% | 95% | 100% | -157.8947 | 2954.9659 | -3550 | -400 | -995.0341 | 24.88% | 93.06% | 95% | 0% | 3341 | -138
[5 empty] | 2019-01-22 | 19 | 513.5 | 3164 | -192 | 1 | 0 | 3356 | 3136.3561 | 3136.3561 | 3136.3561 | 2845.0124 | 780 | 200 | 3825.0124 | 95.63% | 95% | 100% | -219.6796 | 2916.6765 | -3550 | -400 | -1033.3235 | 25.83% | 93.06% | 95% | 0% | 3356 | -192
[5 empty] | 2019-01-22 | 20 | 514 | 3096 | -234 | 1 | 0 | 3330 | 3095.6307 | 3095.6307 | 3095.6307 | 2845.0124 | 780 | 200 | 3825.0124 | 95.63% | 95% | 100% | -267.7346 | 2827.8961 | -3550 | -400 | -1122.1039 | 28.05% | 93.05% | 95% | 0% | 3330 | -234
[5 empty] | 2019-01-22 | 21 | 514.5 | 3027 | -268 | 1 | 0 | 3295 | 3040.8079 | 3040.8079 | 3040.8079 | 2843.446 | 780 | 200 | 3823.446 | 95.59% | 95% | 100% | -306.6362 | 2734.1718 | -3550 | -400 | -1215.8282 | 30.4% | 93.04% | 95% | 0% | 3295 | -268
[5 empty] | 2019-01-22 | 22 | 515 | 2983 | -295 | 1 | 0 | 3278 | 3014.1797 | 3014.1797 | 3014.1797 | 2843.446 | 780 | 200 | 3823.446 | 95.59% | 95% | 100% | -337.5286 | 2676.6511 | -3550 | -400 | -1273.3489 | 31.83% | 93.03% | 95% | 0% | 3278 | -295
[5 empty] | 2019-01-22 | 23 | 515.5 | 2940 | -311 | 1 | 0 | 3251 | 2971.8879 | 2971.8879 | 2971.8879 | 2843.446 | 780 | 200 | 3823.446 | 95.59% | 95% | 100% | -355.8352 | 2616.0526 | -3550 | -400 | -1333.9474 | 33.35% | 93.01% | 95% | 0% | 3251 | -311
[5 empty] | 2019-01-22 | 24 | 516 | 2945 | -301 | 1 | 0 | 3246 | 2964.0561 | 2964.0561 | 2964.0561 | 2843.446 | 780 | 200 | 3823.446 | 95.59% | 95% | 100% | -344.3936 | 2619.6625 | -3550 | -400 | -1330.3375 | 33.26% | 93% | 95% | 0% | 3246 | -301
[5 empty] | 2019-01-22 | 25 | 516.5 | 2943 | -287 | 1 | 0 | 3230 | 2938.9942 | 2938.9942 | 2938.9942 | 2841.8796 | 780 | 200 | 3821.8796 | 95.55% | 95% | 100% | -328.3753 | 2610.6189 | -3550 | -400 | -1339.3811 | 33.48% | 93% | 95% | 0% | 3230 | -287
[5 empty] | 2019-01-22 | 26 | 517 | 2969 | -264 | 1 | 0 | 3233 | 2943.6933 | 2943.6933 | 2943.6933 | 2841.8796 | 780 | 200 | 3821.8796 | 95.55% | 95% | 100% | -302.0595 | 2641.6338 | -3550 | -400 | -1308.3662 | 32.71% | 93% | 95% | 0% | 3233 | -264
[5 empty] | 2019-01-22 | 27 | 517.5 | 3067 | -232 | 1 | 0 | 3299 | 3047.0734 | 3047.0734 | 3047.0734 | 2841.8796 | 780 | 200 | 3821.8796 | 95.55% | 95% | 100% | -265.4462 | 2781.6271 | -3550 | -400 | -1168.3729 | 29.21% | 93% | 95% | 0% | 3299 | -232
[5 empty] | 2019-01-22 | 28 | 518 | 3122 | -204 | 1 | 0 | 3326 | 3089.3652 | 3089.3652 | 3089.3652 | 2841.8796 | 780 | 200 | 3821.8796 | 95.55% | 95% | 100% | -233.4096 | 2855.9556 | -3550 | -400 | -1094.0444 | 27.35% | 92.98% | 95% | 0% | 3326 | -204
[5 empty] | 2019-01-22 | 29 | 518.5 | 3166 | -174 | 1 | 0 | 3340 | 3111.2943 | 3111.2943 | 3111.2943 | 2841.8796 | 780 | 200 | 3821.8796 | 95.55% | 95% | 100% | -199.0847 | 2912.2096 | -3550 | -400 | -1037.7904 | 25.94% | 92.98% | 95% | 0% | 3340 | -174
[5 empty] | 2019-01-22 | 30 | 519 | 3204 | -143 | 1 | 0 | 3347 | 3122.2589 | 3122.2589 | 3122.2589 | 2841.8796 | 780 | 200 | 3821.8796 | 95.55% | 95% | 100% | -163.6156 | 2958.6433 | -3550 | -400 | -991.3567 | 24.78% | 92.97% | 95% | 0% | 3347 | -143
[5 empty] | 2019-01-22 | 31 | 519.5 | 3267 | -111 | 1 | 0 | 3378 | 3170.8162 | 3170.8162 | 3170.8162 | 2841.8796 | 780 | 200 | 3821.8796 | 95.55% | 95% | 100% | -127.0023 | 3043.8139 | -3550 | -400 | -906.1861 | 22.65% | 92.97% | 95% | 0% | 3378 | -111
[5 empty] | 2019-01-22 | 32 | 520 | 3341 | -92 | 1 | 0 | 3433 | 3256.9662 | 3256.9662 | 3256.9662 | 2840.3133 | 780 | 200 | 3820.3133 | 95.51% | 95% | 100% | -105.2632 | 3151.703 | -3550 | -400 | -798.297 | 19.96% | 92.97% | 95% | 0% | 3433 | -92
[5 empty] | 2019-01-22 | 33 | 520.5 | 3423 | -78 | 1 | 0 | 3501 | 3363.479 | 3363.479 | 3363.479 | 2840.3133 | 780 | 200 | 3820.3133 | 95.51% | 95% | 100% | -89.2449 | 3274.2341 | -3550 | -400 | -675.7659 | 16.89% | 92.97% | 95% | 0% | 3501 | -78
[5 empty] | 2019-01-22 | 34 | 521 | 3470 | -72 | 1 | 0 | 3542 | 3427.6999 | 3427.6999 | 3427.6999 | 2840.3133 | 780 | 200 | 3820.3133 | 95.51% | 95% | 100% | -82.3799 | 3345.3201 | -3550 | -400 | -604.6799 | 15.12% | 92.96% | 95% | 0% | 3542 | -72
[5 empty] | 2019-01-22 | 35 | 521.5 | 3521 | -70 | 1 | 0 | 3591 | 3504.4518 | 3504.4518 | 3504.4518 | 2838.7469 | 780 | 200 | 3818.7469 | 95.47% | 95% | 100% | -80.0915 | 3424.3602 | -3550 | -400 | -525.6398 | 13.14% | 92.95% | 95% | 0% | 3591 | -70
[5 empty] | 2019-01-22 | 36 | 522 | 3528 | -69 | 0 | 0 | 3597 | 3513.85 | 3513.85 | 3513.85 | 2838.7469 | 780 | 200 | 3818.7469 | 95.47% | 95% | 100% | -78.9474 | 3434.9026 | -2750 | -200 | 484.9026 | -12.12% | 92.95% | 95% | 0% | 3597 | -69
[5 empty] | 2019-01-22 | 37 | 522.5 | 3520 | -67 | 0 | 0 | 3587 | 3498.1863 | 3498.1863 | 3498.1863 | 2838.7469 | 780 | 200 | 3818.7469 | 95.47% | 95% | 100% | -76.659 | 3421.5273 | -2750 | -200 | 471.5273 | -11.79% | 92.94% | 95% | 0% | 3587 | -67
[5 empty] | 2019-01-22 | 38 | 523 | 3518 | -65 | 0 | 0 | 3583 | 3491.9209 | 3491.9209 | 3491.9209 | 2838.7469 | 780 | 200 | 3818.7469 | 95.47% | 95% | 100% | -74.3707 | 3417.5501 | -2750 | -200 | 467.5501 | -11.69% | 92.94% | 95% | 0% | 3583 | -65
[5 empty] | 2019-01-22 | 39 | 523.5 | 3474 | -62 | 0 | 0 | 3536 | 3418.3017 | 3418.3017 | 3418.3017 | 2838.7469 | 780 | 200 | 3818.7469 | 95.47% | 95% | 100% | -70.9382 | 3347.3635 | -2750 | -200 | 397.3635 | -9.934% | 92.92% | 95% | 0% | 3536 | -62
[5 empty] | 2019-01-22 | 40 | 524 | 3473 | -60 | 0 | 0 | 3533 | 3413.6026 | 3413.6026 | 3413.6026 | 2837.1805 | 780 | 200 | 3817.1805 | 95.43% | 95% | 100% | -68.6499 | 3344.9528 | -2750 | -200 | 394.9528 | -9.874% | 92.92% | 95% | 0% | 3533 | -60
[5 empty] | 2019-01-22 | 41 | 524.5 | 3379 | -59 | 0 | 0 | 3438 | 3264.798 | 3264.798 | 3264.798 | 2837.1805 | 780 | 200 | 3817.1805 | 95.43% | 95% | 100% | -67.5057 | 3197.2923 | -2750 | -200 | 247.2923 | -6.182% | 92.91% | 95% | 0% | 3438 | -59
[5 empty] | 2019-01-22 | 42 | 525 | 3278 | -58 | 0 | 0 | 3336 | 3105.0289 | 3105.0289 | 3105.0289 | 2837.1805 | 780 | 200 | 3817.1805 | 95.43% | 95% | 100% | -66.3616 | 3038.6673 | -2750 | -200 | 88.6673 | -2.217% | 92.9% | 95% | 0% | 3336 | -58
[5 empty] | 2019-01-22 | 43 | 525.5 | 3131 | -58 | 0 | 0 | 3189 | 2874.7733 | 2874.7733 | 2874.7733 | 2835.6142 | 780 | 200 | 3815.6142 | 95.39% | 95% | 100% | -66.3616 | 2808.4117 | -2750 | -200 | -141.5883 | 3.54% | 92.9% | 95% | 0% | 3189 | -58
[5 empty] | 2019-01-22 | 44 | 526 | 2946 | -59 | 0 | 0 | 3005 | 2586.5622 | 2586.5622 | 2586.5622 | 2835.6142 | 780 | 200 | 3815.6142 | 95.39% | 95% | 100% | -67.5057 | 2519.0565 | -2750 | -200 | -430.9435 | 10.77% | 92.9% | 95% | 0% | 3005 | -59
[5 empty] | 2019-01-22 | 45 | 526.5 | 2773 | -60 | 0 | 0 | 2833 | 2317.1476 | 2317.1476 | 2317.1476 | 2834.0478 | 780 | 200 | 3814.0478 | 95.35% | 95% | 100% | -68.6499 | 2248.4977 | -2750 | -200 | -701.5023 | 17.54% | 92.9% | 95% | 0% | 2833 | -60
[5 empty] | 2019-01-22 | 46 | 527 | 2600 | -62 | 0 | 0 | 2662 | 2049.2993 | 2049.2993 | 2049.2993 | 2834.0478 | 780 | 200 | 3814.0478 | 95.35% | 95% | 100% | -70.9382 | 1978.361 | -2750 | -200 | -971.639 | 24.29% | 92.89% | 95% | 0% | 2662 | -62
[5 empty] | 2019-01-22 | 47 | 527.5 | 2423 | -61 | 0 | 0 | 2484 | 1770.4864 | 1770.4864 | 1770.4864 | 2832.4815 | 780 | 200 | 3812.4815 | 95.31% | 95% | 100% | -69.7941 | 1700.6923 | -2750 | -200 | -1249.3077 | 31.23% | 92.89% | 95% | 0% | 2484 | -61
[5 empty] | 2019-01-22 | 48 | 528 | 2310 | -59 | 0 | 0 | 2369 | 1590.3545 | 1590.3545 | 1590.3545 | 2832.4815 | 780 | 200 | 3812.4815 | 95.31% | 95% | 100% | -67.5057 | 1522.8488 | -2750 | -200 | -1427.1512 | 35.68% | 92.87% | 95% | 0% | 2369 | -59
[5 empty] | 2019-01-23 | 1 | 528.5 | 2283 | -61 | 0 | 0 | 2344 | 1551.1954 | 1551.1954 | 1551.1954 | 2832.4815 | 780 | 200 | 3812.4815 | 95.31% | 95% | 100% | -69.7941 | 1481.4013 | -2750 | -200 | -1468.5987 | 36.71% | 92.86% | 95% | 0% | 2344 | -61
[5 empty] | 2019-01-23 | 2 | 529 | 2311 | -63 | 0 | 0 | 2374 | 1598.1863 | 1598.1863 | 1598.1863 | 2832.4815 | 780 | 200 | 3812.4815 | 95.31% | 95% | 100% | -72.0824 | 1526.1039 | -2750 | -200 | -1423.8961 | 35.6% | 92.83% | 95% | 0% | 2374 | -63
[5 empty] | 2019-01-23 | 3 | 529.5 | 2288 | -66 | 0 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 2830.9151 | 780 | 200 | 3810.9151 | 95.27% | 95% | 100% | -75.5149 | 1491.3442 | -2750 | -200 | -1458.6558 | 36.47% | 92.82% | 95% | 0% | 2354 | -66
[5 empty] | 2019-01-23 | 4 | 530 | 2244 | -68 | 0 | 0 | 2312 | 1501.0717 | 1501.0717 | 1501.0717 | 2830.9151 | 780 | 200 | 3810.9151 | 95.27% | 95% | 100% | -77.8032 | 1423.2685 | -2750 | -200 | -1526.7315 | 38.17% | 92.81% | 95% | 0% | 2312 | -68
[5 empty] | 2019-01-23 | 5 | 530.5 | 2219 | -70 | 0 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 2830.9151 | 780 | 200 | 3810.9151 | 95.27% | 95% | 100% | -80.0915 | 1384.9538 | -2750 | -200 | -1565.0462 | 39.13% | 92.8% | 95% | 0% | 2289 | -70
[5 empty] | 2019-01-23 | 6 | 531 | 2206 | -71 | 0 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 2830.9151 | 780 | 200 | 3810.9151 | 95.27% | 95% | 100% | -81.2357 | 1365.0133 | -2750 | -200 | -1584.9867 | 39.62% | 92.79% | 95% | 0% | 2277 | -71
[5 empty] | 2019-01-23 | 7 | 531.5 | 2170 | -72 | 0 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 2830.9151 | 780 | 200 | 3810.9151 | 95.27% | 95% | 100% | -82.3799 | 1309.0464 | -2750 | -200 | -1640.9536 | 41.02% | 92.79% | 95% | 0% | 2242 | -72
[5 empty] | 2019-01-23 | 8 | 532 | 2131 | -73 | 0 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 2830.9151 | 780 | 200 | 3810.9151 | 95.27% | 95% | 100% | -83.524 | 1248.3803 | -2750 | -200 | -1701.6197 | 42.54% | 92.79% | 95% | 0% | 2204 | -73
[5 empty] | 2019-01-23 | 9 | 532.5 | 2115 | -73 | 0 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 2830.9151 | 780 | 200 | 3810.9151 | 95.27% | 95% | 100% | -83.524 | 1223.3185 | -2750 | -200 | -1726.6815 | 43.17% | 92.79% | 95% | 0% | 2188 | -73
[5 empty] | 2019-01-23 | 10 | 533 | 2133 | -73 | 0 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 2829.3487 | 780 | 200 | 3809.3487 | 95.23% | 95% | 100% | -83.524 | 1251.5131 | -2750 | -200 | -1698.4869 | 42.46% | 92.78% | 95% | 0% | 2206 | -73
[5 empty] | 2019-01-23 | 11 | 533.5 | 2193 | -74 | 0 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 2829.3487 | 780 | 200 | 3809.3487 | 95.23% | 95% | 100% | -84.6682 | 1345.9171 | -2750 | -200 | -1604.0829 | 40.1% | 92.76% | 95% | 0% | 2267 | -74
[5 empty] | 2019-01-23 | 12 | 534 | 2307 | -74 | 0 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 2829.3487 | 780 | 200 | 3809.3487 | 95.23% | 95% | 100% | -84.6682 | 1524.4827 | -2750 | -200 | -1425.5173 | 35.64% | 92.76% | 95% | 0% | 2381 | -74
[5 empty] | 2019-01-23 | 13 | 534.5 | 2557 | -71 | 0 | 0 | 2628 | 1996.0429 | 1996.0429 | 1996.0429 | 2829.3487 | 780 | 200 | 3809.3487 | 95.23% | 95% | 100% | -81.2357 | 1914.8072 | -2750 | -200 | -1035.1928 | 25.88% | 92.76% | 95% | 0% | 2628 | -71
[5 empty] | 2019-01-23 | 14 | 535 | 2835 | -68 | 0 | 0 | 2903 | 2426.7931 | 2426.7931 | 2426.7931 | 2829.3487 | 780 | 200 | 3809.3487 | 95.23% | 95% | 100% | -77.8032 | 2348.9899 | -2750 | -200 | -601.0101 | 15.03% | 92.76% | 95% | 0% | 2903 | -68
[5 empty] | 2019-01-23 | 15 | 535.5 | 3108 | -67 | 0 | 0 | 3175 | 2852.8442 | 2852.8442 | 2852.8442 | 2829.3487 | 780 | 200 | 3809.3487 | 95.23% | 95% | 100% | -76.659 | 2776.1851 | -2750 | -200 | -173.8149 | 4.345% | 92.76% | 95% | 0% | 3175 | -67
[5 empty] | 2019-01-23 | 16 | 536 | 3258 | -66 | 0 | 0 | 3324 | 3086.2325 | 3086.2325 | 3086.2325 | 2827.7824 | 780 | 200 | 3807.7824 | 95.19% | 95% | 100% | -75.5149 | 3010.7176 | -2750 | -200 | 60.7176 | -1.518% | 92.74% | 95% | 0% | 3324 | -66
[5 empty] | 2019-01-23 | 17 | 536.5 | 3321 | -67 | 0 | 0 | 3388 | 3186.4798 | 3186.4798 | 3186.4798 | 2827.7824 | 780 | 200 | 3807.7824 | 95.19% | 95% | 100% | -76.659 | 3109.8208 | -2750 | -200 | 159.8208 | -3.996% | 92.74% | 95% | 0% | 3388 | -67
[5 empty] | 2019-01-23 | 18 | 537 | 3300 | -89 | 0 | 0 | 3389 | 3188.0462 | 3188.0462 | 3188.0462 | 2827.7824 | 780 | 200 | 3807.7824 | 95.19% | 95% | 100% | -101.8307 | 3086.2155 | -2750 | -200 | 136.2155 | -3.405% | 92.73% | 95% | 0% | 3389 | -89
[5 empty] | 2019-01-23 | 19 | 537.5 | 3331 | -93 | 0 | 0 | 3424 | 3242.8689 | 3242.8689 | 3242.8689 | 2826.216 | 780 | 200 | 3806.216 | 95.16% | 95% | 100% | -106.4073 | 3136.4616 | -2750 | -200 | 186.4616 | -4.662% | 92.72% | 95% | 0% | 3424 | -93
[5 empty] | 2019-01-23 | 20 | 538 | 3233 | -175 | 1 | 0 | 3408 | 3217.8071 | 3217.8071 | 3217.8071 | 2824.6496 | 780 | 200 | 3804.6496 | 95.12% | 95% | 100% | -200.2288 | 3017.5783 | -3550 | -400 | -932.4217 | 23.31% | 92.72% | 95% | 0% | 3408 | -175
[5 empty] | 2019-01-23 | 21 | 538.5 | 3124 | -218 | 1 | 0 | 3342 | 3114.427 | 3114.427 | 3114.427 | 2824.6496 | 780 | 200 | 3804.6496 | 95.12% | 95% | 100% | -249.4279 | 2864.9991 | -3550 | -400 | -1085.0009 | 27.13% | 92.71% | 95% | 0% | 3342 | -218
[5 empty] | 2019-01-23 | 22 | 539 | 3039 | -264 | 1 | 0 | 3303 | 3053.3388 | 3053.3388 | 3053.3388 | 2824.6496 | 780 | 200 | 3804.6496 | 95.12% | 95% | 100% | -302.0595 | 2751.2793 | -3550 | -400 | -1198.7207 | 29.97% | 92.71% | 95% | 0% | 3303 | -264
[5 empty] | 2019-01-23 | 23 | 539.5 | 3000 | -294 | 1 | 0 | 3294 | 3039.2415 | 3039.2415 | 3039.2415 | 2823.0833 | 780 | 200 | 3803.0833 | 95.08% | 95% | 100% | -336.3844 | 2702.8571 | -3550 | -400 | -1247.1429 | 31.18% | 92.69% | 95% | 0% | 3294 | -294
[5 empty] | 2019-01-23 | 24 | 540 | 2962 | -310 | 1 | 0 | 3272 | 3004.7815 | 3004.7815 | 3004.7815 | 2823.0833 | 780 | 200 | 3803.0833 | 95.08% | 95% | 100% | -354.6911 | 2650.0905 | -3550 | -400 | -1299.9095 | 32.5% | 92.68% | 95% | 0% | 3272 | -310
[5 empty] | 2019-01-23 | 25 | 540.5 | 2948 | -317 | 1 | 0 | 3265 | 2993.817 | 2993.817 | 2993.817 | 2823.0833 | 780 | 200 | 3803.0833 | 95.08% | 95% | 100% | -362.7002 | 2631.1168 | -3550 | -400 | -1318.8832 | 32.97% | 92.66% | 95% | 0% | 3265 | -317
[5 empty] | 2019-01-23 | 26 | 541 | 2949 | -301 | 1 | 0 | 3250 | 2970.3215 | 2970.3215 | 2970.3215 | 2823.0833 | 780 | 200 | 3803.0833 | 95.08% | 95% | 100% | -344.3936 | 2625.9279 | -3550 | -400 | -1324.0721 | 33.1% | 92.66% | 95% | 0% | 3250 | -301
[5 empty] | 2019-01-23 | 27 | 541.5 | 2937 | -281 | 1 | 0 | 3218 | 2920.1979 | 2920.1979 | 2920.1979 | 2823.0833 | 780 | 200 | 3803.0833 | 95.08% | 95% | 100% | -321.5103 | 2598.6876 | -3550 | -400 | -1351.3124 | 33.78% | 92.65% | 95% | 0% | 3218 | -281
[5 empty] | 2019-01-23 | 28 | 542 | 2962 | -254 | 1 | 0 | 3216 | 2917.0651 | 2917.0651 | 2917.0651 | 2823.0833 | 780 | 200 | 3803.0833 | 95.08% | 95% | 100% | -290.6178 | 2626.4473 | -3550 | -400 | -1323.5527 | 33.09% | 92.64% | 95% | 0% | 3216 | -254
[5 empty] | 2019-01-23 | 29 | 542.5 | 3023 | -218 | 1 | 0 | 3241 | 2956.2242 | 2956.2242 | 2956.2242 | 2821.5169 | 780 | 200 | 3801.5169 | 95.04% | 95% | 100% | -249.4279 | 2706.7963 | -3550 | -400 | -1243.2037 | 31.08% | 92.64% | 95% | 0% | 3241 | -218
[5 empty] | 2019-01-23 | 30 | 543 | 3085 | -174 | 1 | 0 | 3259 | 2984.4188 | 2984.4188 | 2984.4188 | 2821.5169 | 780 | 200 | 3801.5169 | 95.04% | 95% | 100% | -199.0847 | 2785.3341 | -3550 | -400 | -1164.6659 | 29.12% | 92.63% | 95% | 0% | 3259 | -174
[5 empty] | 2019-01-23 | 31 | 543.5 | 3213 | -120 | 1 | 0 | 3333 | 3100.3298 | 3100.3298 | 3100.3298 | 2819.9505 | 780 | 200 | 3799.9505 | 95% | 95% | 0% | -137.2998 | 2963.03 | -3550 | -400 | -986.97 | 24.67% | 92.63% | 95% | 0% | 3333 | -120
[5 empty] | 2019-01-23 | 32 | 544 | 3335 | -76 | 1 | 0 | 3411 | 3222.5062 | 3222.5062 | 3222.5062 | 2819.9505 | 780 | 200 | 3799.9505 | 95% | 95% | 0% | -86.9565 | 3135.5497 | -3550 | -400 | -814.4503 | 20.36% | 92.63% | 95% | 0% | 3411 | -76
[5 empty] | 2019-01-23 | 33 | 544.5 | 3430 | -54 | 1 | 0 | 3484 | 3336.8508 | 3336.8508 | 3336.8508 | 2819.9505 | 780 | 200 | 3799.9505 | 95% | 95% | 0% | -61.7849 | 3275.0659 | -3550 | -400 | -674.9341 | 16.87% | 92.63% | 95% | 0% | 3484 | -54
[5 empty] | 2019-01-23 | 34 | 545 | 3489 | -52 | 1 | 0 | 3541 | 3426.1336 | 3426.1336 | 3426.1336 | 2818.3842 | 780 | 200 | 3798.3842 | 94.96% | 95% | 0% | -59.4966 | 3366.637 | -3550 | -400 | -583.363 | 14.58% | 92.63% | 95% | 0% | 3541 | -52
[5 empty] | 2019-01-23 | 35 | 545.5 | 3595 | -52 | 1 | 0 | 3647 | 3592.1682 | 3592.1682 | 3592.1682 | 2818.3842 | 780 | 200 | 3798.3842 | 94.96% | 95% | 0% | -59.4966 | 3532.6716 | -3550 | -400 | -417.3284 | 10.43% | 92.62% | 95% | 0% | 3647 | -52
[5 empty] | 2019-01-23 | 36 | 546 | 3600 | -52 | 0 | 0 | 3652 | 3600 | 3600 | 3600 | 2816.8178 | 780 | 200 | 3796.8178 | 94.92% | 95% | 0% | -59.4966 | 3540.5034 | -2750 | -200 | 590.5034 | -14.76% | 92.61% | 95% | 0% | 3652 | -52
[5 empty] | 2019-01-23 | 37 | 546.5 | 3585 | -52 | 0 | 0 | 3637 | 3576.5045 | 3576.5045 | 3576.5045 | 2816.8178 | 780 | 200 | 3796.8178 | 94.92% | 95% | 0% | -59.4966 | 3517.008 | -2750 | -200 | 567.008 | -14.18% | 92.61% | 95% | 0% | 3637 | -52
[5 empty] | 2019-01-23 | 38 | 547 | 3571 | -51 | 0 | 0 | 3622 | 3553.0091 | 3553.0091 | 3553.0091 | 2816.8178 | 780 | 200 | 3796.8178 | 94.92% | 95% | 0% | -58.3524 | 3494.6567 | -2750 | -200 | 544.6567 | -13.62% | 92.6% | 95% | 0% | 3622 | -51
[5 empty] | 2019-01-23 | 39 | 547.5 | 3522 | -51 | 0 | 0 | 3573 | 3476.2572 | 3476.2572 | 3476.2572 | 2816.8178 | 780 | 200 | 3796.8178 | 94.92% | 95% | 0% | -58.3524 | 3417.9048 | -2750 | -200 | 467.9048 | -11.7% | 92.59% | 95% | 0% | 3573 | -51
[5 empty] | 2019-01-23 | 40 | 548 | 3514 | -50 | 0 | 0 | 3564 | 3462.1599 | 3462.1599 | 3462.1599 | 2815.2514 | 780 | 200 | 3795.2514 | 94.88% | 95% | 0% | -57.2082 | 3404.9517 | -2750 | -200 | 454.9517 | -11.37% | 92.58% | 95% | 0% | 3564 | -50
[5 empty] | 2019-01-23 | 41 | 548.5 | 3477 | -50 | 0 | 0 | 3527 | 3404.2045 | 3404.2045 | 3404.2045 | 2815.2514 | 780 | 200 | 3795.2514 | 94.88% | 95% | 0% | -57.2082 | 3346.9962 | -2750 | -200 | 396.9962 | -9.925% | 92.55% | 95% | 0% | 3527 | -50
[5 empty] | 2019-01-23 | 42 | 549 | 3360 | -49 | 0 | 0 | 3409 | 3219.3735 | 3219.3735 | 3219.3735 | 2815.2514 | 780 | 200 | 3795.2514 | 94.88% | 95% | 0% | -56.0641 | 3163.3094 | -2750 | -200 | 213.3094 | -5.333% | 92.55% | 95% | 0% | 3409 | -49
[5 empty] | 2019-01-23 | 43 | 549.5 | 3205 | -49 | 0 | 0 | 3254 | 2976.587 | 2976.587 | 2976.587 | 2813.6851 | 780 | 200 | 3793.6851 | 94.84% | 95% | 0% | -56.0641 | 2920.5229 | -2750 | -200 | -29.4771 | 0.7369% | 92.54% | 95% | 0% | 3254 | -49
[5 empty] | 2019-01-23 | 44 | 550 | 3025 | -49 | 0 | 0 | 3074 | 2694.6414 | 2694.6414 | 2694.6414 | 2813.6851 | 780 | 200 | 3793.6851 | 94.84% | 95% | 0% | -56.0641 | 2638.5773 | -2750 | -200 | -311.4227 | 7.786% | 92.54% | 95% | 0% | 3074 | -49
[5 empty] | 2019-01-23 | 45 | 550.5 | 2832 | -50 | 0 | 0 | 2882 | 2393.8994 | 2393.8994 | 2393.8994 | 2813.6851 | 780 | 200 | 3793.6851 | 94.84% | 95% | 0% | -57.2082 | 2336.6912 | -2750 | -200 | -613.3088 | 15.33% | 92.54% | 95% | 0% | 2882 | -50
[5 empty] | 2019-01-23 | 46 | 551 | 2664 | -50 | 0 | 0 | 2714 | 2130.7502 | 2130.7502 | 2130.7502 | 2813.6851 | 780 | 200 | 3793.6851 | 94.84% | 95% | 0% | -57.2082 | 2073.542 | -2750 | -200 | -876.458 | 21.91% | 92.54% | 95% | 0% | 2714 | -50
[5 empty] | 2019-01-23 | 47 | 551.5 | 2484 | -47 | 0 | 0 | 2531 | 1844.1055 | 1844.1055 | 1844.1055 | 2813.6851 | 780 | 200 | 3793.6851 | 94.84% | 95% | 0% | -53.7757 | 1790.3298 | -2750 | -200 | -1159.6702 | 28.99% | 92.53% | 95% | 0% | 2531 | -47
[5 empty] | 2019-01-23 | 48 | 552 | 2384 | -44 | 0 | 0 | 2428 | 1682.77 | 1682.77 | 1682.77 | 2812.1187 | 780 | 200 | 3792.1187 | 94.8% | 95% | 0% | -50.3432 | 1632.4267 | -2750 | -200 | -1317.5733 | 32.94% | 92.52% | 95% | 0% | 2428 | -44
[5 empty] | 2019-01-24 | 1 | 552.5 | 2352 | -44 | 0 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 2812.1187 | 780 | 200 | 3792.1187 | 94.8% | 95% | 0% | -50.3432 | 1582.3031 | -2750 | -200 | -1367.6969 | 34.19% | 92.51% | 95% | 0% | 2396 | -44
[5 empty] | 2019-01-24 | 2 | 553 | 2383 | -44 | 0 | 0 | 2427 | 1681.2036 | 1681.2036 | 1681.2036 | 2810.5523 | 780 | 200 | 3790.5523 | 94.76% | 95% | 0% | -50.3432 | 1630.8604 | -2750 | -200 | -1319.1396 | 32.98% | 92.51% | 95% | 0% | 2427 | -44
[5 empty] | 2019-01-24 | 3 | 553.5 | 2362 | -45 | 0 | 0 | 2407 | 1649.8763 | 1649.8763 | 1649.8763 | 2810.5523 | 780 | 200 | 3790.5523 | 94.76% | 95% | 0% | -51.4874 | 1598.3889 | -2750 | -200 | -1351.6111 | 33.79% | 92.5% | 95% | 0% | 2407 | -45
[5 empty] | 2019-01-24 | 4 | 554 | 2313 | -45 | 0 | 0 | 2358 | 1573.1245 | 1573.1245 | 1573.1245 | 2808.986 | 780 | 200 | 3788.986 | 94.72% | 95% | 0% | -51.4874 | 1521.6371 | -2750 | -200 | -1428.3629 | 35.71% | 92.49% | 95% | 0% | 2358 | -45
[5 empty] | 2019-01-24 | 5 | 554.5 | 2280 | -45 | 0 | 0 | 2325 | 1521.4345 | 1521.4345 | 1521.4345 | 2808.986 | 780 | 200 | 3788.986 | 94.72% | 95% | 0% | -51.4874 | 1469.947 | -2750 | -200 | -1480.053 | 37% | 92.49% | 95% | 0% | 2325 | -45
[5 empty] | 2019-01-24 | 6 | 555 | 2272 | -45 | 0 | 0 | 2317 | 1508.9035 | 1508.9035 | 1508.9035 | 2808.986 | 780 | 200 | 3788.986 | 94.72% | 95% | 0% | -51.4874 | 1457.4161 | -2750 | -200 | -1492.5839 | 37.31% | 92.48% | 95% | 0% | 2317 | -45
[5 empty] | 2019-01-24 | 7 | 555.5 | 2248 | -43 | 0 | 0 | 2291 | 1468.1781 | 1468.1781 | 1468.1781 | 2808.986 | 780 | 200 | 3788.986 | 94.72% | 95% | 0% | -49.1991 | 1418.979 | -2750 | -200 | -1531.021 | 38.28% | 92.48% | 95% | 0% | 2291 | -43
[5 empty] | 2019-01-24 | 8 | 556 | 2219 | -42 | 0 | 0 | 2261 | 1421.1871 | 1421.1871 | 1421.1871 | 2808.986 | 780 | 200 | 3788.986 | 94.72% | 95% | 0% | -48.0549 | 1373.1322 | -2750 | -200 | -1576.8678 | 39.42% | 92.46% | 95% | 0% | 2261 | -42
[5 empty] | 2019-01-24 | 9 | 556.5 | 2195 | -41 | 0 | 0 | 2236 | 1382.028 | 1382.028 | 1382.028 | 2808.986 | 780 | 200 | 3788.986 | 94.72% | 95% | 0% | -46.9108 | 1335.1173 | -2750 | -200 | -1614.8827 | 40.37% | 92.43% | 95% | 0% | 2236 | -41
[5 empty] | 2019-01-24 | 10 | 557 | 2212 | -41 | 0 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 2807.4196 | 780 | 200 | 3787.4196 | 94.69% | 95% | 0% | -46.9108 | 1361.7455 | -2750 | -200 | -1588.2545 | 39.71% | 92.43% | 95% | 0% | 2253 | -41
[5 empty] | 2019-01-24 | 11 | 557.5 | 2275 | -40 | 0 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 2807.4196 | 780 | 200 | 3787.4196 | 94.69% | 95% | 0% | -45.7666 | 1460.0042 | -2750 | -200 | -1489.9958 | 37.25% | 92.43% | 95% | 0% | 2315 | -40
[5 empty] | 2019-01-24 | 12 | 558 | 2380 | -40 | 0 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 2807.4196 | 780 | 200 | 3787.4196 | 94.69% | 95% | 0% | -45.7666 | 1624.4725 | -2750 | -200 | -1325.5275 | 33.14% | 92.43% | 95% | 0% | 2420 | -40
[5 empty] | 2019-01-24 | 13 | 558.5 | 2623 | -38 | 0 | 0 | 2661 | 2047.7329 | 2047.7329 | 2047.7329 | 2807.4196 | 780 | 200 | 3787.4196 | 94.69% | 95% | 0% | -43.4783 | 2004.2546 | -2750 | -200 | -945.7454 | 23.64% | 92.43% | 95% | 0% | 2661 | -38
[5 empty] | 2019-01-24 | 14 | 559 | 2885 | -36 | 0 | 0 | 2921 | 2454.9876 | 2454.9876 | 2454.9876 | 2805.8533 | 780 | 200 | 3785.8533 | 94.65% | 95% | 0% | -41.1899 | 2413.7977 | -2750 | -200 | -536.2023 | 13.41% | 92.42% | 95% | 0% | 2921 | -36
[5 empty] | 2019-01-24 | 15 | 559.5 | 3164 | -36 | 0 | 0 | 3200 | 2892.0033 | 2892.0033 | 2892.0033 | 2805.8533 | 780 | 200 | 3785.8533 | 94.65% | 95% | 0% | -41.1899 | 2850.8134 | -2750 | -200 | -99.1866 | 2.48% | 92.42% | 95% | 0% | 3200 | -36
[5 empty] | 2019-01-24 | 16 | 560 | 3302 | -35 | 0 | 0 | 3337 | 3106.5952 | 3106.5952 | 3106.5952 | 2805.8533 | 780 | 200 | 3785.8533 | 94.65% | 95% | 0% | -40.0458 | 3066.5495 | -2750 | -200 | 116.5495 | -2.914% | 92.4% | 95% | 0% | 3337 | -35
[5 empty] | 2019-01-24 | 17 | 560.5 | 3370 | -36 | 0 | 0 | 3406 | 3214.6744 | 3214.6744 | 3214.6744 | 2804.2869 | 780 | 200 | 3784.2869 | 94.61% | 95% | 0% | -41.1899 | 3173.4844 | -2750 | -200 | 223.4844 | -5.587% | 92.4% | 95% | 0% | 3406 | -36
[5 empty] | 2019-01-24 | 18 | 561 | 3378 | -44 | 0 | 0 | 3422 | 3239.7362 | 3239.7362 | 3239.7362 | 2804.2869 | 780 | 200 | 3784.2869 | 94.61% | 95% | 0% | -50.3432 | 3189.3929 | -2750 | -200 | 239.3929 | -5.985% | 92.4% | 95% | 0% | 3422 | -44
[5 empty] | 2019-01-24 | 19 | 561.5 | 3425 | -55 | 1 | 0 | 3480 | 3330.5853 | 3330.5853 | 3330.5853 | 2804.2869 | 780 | 200 | 3784.2869 | 94.61% | 95% | 0% | -62.9291 | 3267.6563 | -3550 | -400 | -682.3437 | 17.06% | 92.39% | 95% | 0% | 3480 | -55
[5 empty] | 2019-01-24 | 20 | 562 | 3431 | -64 | 1 | 0 | 3495 | 3354.0808 | 3354.0808 | 3354.0808 | 2802.7205 | 780 | 200 | 3782.7205 | 94.57% | 95% | 0% | -73.2265 | 3280.8542 | -3550 | -400 | -669.1458 | 16.73% | 92.38% | 95% | 0% | 3495 | -64
[5 empty] | 2019-01-24 | 21 | 562.5 | 3412 | -76 | 1 | 0 | 3488 | 3343.1162 | 3343.1162 | 3343.1162 | 2802.7205 | 780 | 200 | 3782.7205 | 94.57% | 95% | 0% | -86.9565 | 3256.1597 | -3550 | -400 | -693.8403 | 17.35% | 92.38% | 95% | 0% | 3488 | -76
[5 empty] | 2019-01-24 | 22 | 563 | 3408 | -84 | 1 | 0 | 3492 | 3349.3817 | 3349.3817 | 3349.3817 | 2802.7205 | 780 | 200 | 3782.7205 | 94.57% | 95% | 0% | -96.1098 | 3253.2719 | -3550 | -400 | -696.7281 | 17.42% | 92.37% | 95% | 0% | 3492 | -84
[5 empty] | 2019-01-24 | 23 | 563.5 | 3386 | -95 | 1 | 0 | 3481 | 3332.1517 | 3332.1517 | 3332.1517 | 2801.1542 | 780 | 200 | 3781.1542 | 94.53% | 95% | 0% | -108.6957 | 3223.456 | -3550 | -400 | -726.544 | 18.16% | 92.36% | 95% | 0% | 3481 | -95
[5 empty] | 2019-01-24 | 24 | 564 | 3348 | -107 | 1 | 0 | 3455 | 3291.4262 | 3291.4262 | 3291.4262 | 2801.1542 | 780 | 200 | 3781.1542 | 94.53% | 95% | 0% | -122.4256 | 3169.0006 | -3550 | -400 | -780.9994 | 19.52% | 92.36% | 95% | 0% | 3455 | -107
[5 empty] | 2019-01-24 | 25 | 564.5 | 3352 | -117 | 1 | 0 | 3469 | 3313.3553 | 3313.3553 | 3313.3553 | 2801.1542 | 780 | 200 | 3781.1542 | 94.53% | 95% | 0% | -133.8673 | 3179.488 | -3550 | -400 | -770.512 | 19.26% | 92.36% | 95% | 0% | 3469 | -117
[5 empty] | 2019-01-24 | 26 | 565 | 3315 | -129 | 1 | 0 | 3444 | 3274.1962 | 3274.1962 | 3274.1962 | 2801.1542 | 780 | 200 | 3781.1542 | 94.53% | 95% | 0% | -147.5973 | 3126.599 | -3550 | -400 | -823.401 | 20.59% | 92.35% | 95% | 0% | 3444 | -129
[5 empty] | 2019-01-24 | 27 | 565.5 | 3272 | -135 | 1 | 0 | 3407 | 3216.2407 | 3216.2407 | 3216.2407 | 2801.1542 | 780 | 200 | 3781.1542 | 94.53% | 95% | 0% | -154.4622 | 3061.7785 | -3550 | -400 | -888.2215 | 22.21% | 92.34% | 95% | 0% | 3407 | -135
[5 empty] | 2019-01-24 | 28 | 566 | 3253 | -131 | 1 | 0 | 3384 | 3180.2143 | 3180.2143 | 3180.2143 | 2801.1542 | 780 | 200 | 3781.1542 | 94.53% | 95% | 0% | -149.8856 | 3030.3288 | -3550 | -400 | -919.6712 | 22.99% | 92.33% | 95% | 0% | 3384 | -131
[5 empty] | 2019-01-24 | 29 | 566.5 | 3258 | -119 | 1 | 0 | 3377 | 3169.2498 | 3169.2498 | 3169.2498 | 2799.5878 | 780 | 200 | 3779.5878 | 94.49% | 95% | 0% | -136.1556 | 3033.0942 | -3550 | -400 | -916.9058 | 22.92% | 92.33% | 95% | 0% | 3377 | -119
[5 empty] | 2019-01-24 | 30 | 567 | 3279 | -96 | 1 | 0 | 3375 | 3166.1171 | 3166.1171 | 3166.1171 | 2799.5878 | 780 | 200 | 3779.5878 | 94.49% | 95% | 0% | -109.8398 | 3056.2772 | -3550 | -400 | -893.7228 | 22.34% | 92.33% | 95% | 0% | 3375 | -96
[5 empty] | 2019-01-24 | 31 | 567.5 | 3320 | -74 | 1 | 0 | 3394 | 3195.878 | 3195.878 | 3195.878 | 2799.5878 | 780 | 200 | 3779.5878 | 94.49% | 95% | 0% | -84.6682 | 3111.2098 | -3550 | -400 | -838.7902 | 20.97% | 92.32% | 95% | 0% | 3394 | -74
[5 empty] | 2019-01-24 | 32 | 568 | 3388 | -52 | 1 | 0 | 3440 | 3267.9308 | 3267.9308 | 3267.9308 | 2799.5878 | 780 | 200 | 3779.5878 | 94.49% | 95% | 0% | -59.4966 | 3208.4342 | -3550 | -400 | -741.5658 | 18.54% | 92.31% | 95% | 0% | 3440 | -52
[5 empty] | 2019-01-24 | 33 | 568.5 | 3457 | -39 | 1 | 0 | 3496 | 3355.6472 | 3355.6472 | 3355.6472 | 2799.5878 | 780 | 200 | 3779.5878 | 94.49% | 95% | 0% | -44.6224 | 3311.0247 | -3550 | -400 | -638.9753 | 15.97% | 92.29% | 95% | 0% | 3496 | -39
[5 empty] | 2019-01-24 | 34 | 569 | 3519 | -36 | 1 | 0 | 3555 | 3448.0627 | 3448.0627 | 3448.0627 | 2799.5878 | 780 | 200 | 3779.5878 | 94.49% | 95% | 0% | -41.1899 | 3406.8727 | -3550 | -400 | -543.1273 | 13.58% | 92.28% | 95% | 0% | 3555 | -36
[5 empty] | 2019-01-24 | 35 | 569.5 | 3554 | -37 | 1 | 0 | 3591 | 3504.4518 | 3504.4518 | 3504.4518 | 2798.0214 | 780 | 200 | 3778.0214 | 94.45% | 95% | 0% | -42.3341 | 3462.1177 | -3550 | -400 | -487.8823 | 12.2% | 92.28% | 95% | 0% | 3591 | -37
[5 empty] | 2019-01-24 | 36 | 570 | 3544 | -38 | 0 | 0 | 3582 | 3490.3545 | 3490.3545 | 3490.3545 | 2798.0214 | 780 | 200 | 3778.0214 | 94.45% | 95% | 0% | -43.4783 | 3446.8762 | -2750 | -200 | 496.8762 | -12.42% | 92.26% | 95% | 0% | 3582 | -38
[5 empty] | 2019-01-24 | 37 | 570.5 | 3545 | -40 | 0 | 0 | 3585 | 3495.0536 | 3495.0536 | 3495.0536 | 2796.4551 | 780 | 200 | 3776.4551 | 94.41% | 95% | 0% | -45.7666 | 3449.287 | -2750 | -200 | 499.287 | -12.48% | 92.24% | 95% | 0% | 3585 | -40
[5 empty] | 2019-01-24 | 38 | 571 | 3530 | -43 | 0 | 0 | 3573 | 3476.2572 | 3476.2572 | 3476.2572 | 2796.4551 | 780 | 200 | 3776.4551 | 94.41% | 95% | 0% | -49.1991 | 3427.0581 | -2750 | -200 | 477.0581 | -11.93% | 92.23% | 95% | 0% | 3573 | -43
[5 empty] | 2019-01-24 | 39 | 571.5 | 3485 | -46 | 0 | 0 | 3531 | 3410.4699 | 3410.4699 | 3410.4699 | 2796.4551 | 780 | 200 | 3776.4551 | 94.41% | 95% | 0% | -52.6316 | 3357.8383 | -2750 | -200 | 407.8383 | -10.2% | 92.23% | 95% | 0% | 3531 | -46
[5 empty] | 2019-01-24 | 40 | 572 | 3462 | -49 | 0 | 0 | 3511 | 3379.1426 | 3379.1426 | 3379.1426 | 2796.4551 | 780 | 200 | 3776.4551 | 94.41% | 95% | 0% | -56.0641 | 3323.0785 | -2750 | -200 | 373.0785 | -9.327% | 92.23% | 95% | 0% | 3511 | -49
[5 empty] | 2019-01-24 | 41 | 572.5 | 3365 | -52 | 0 | 0 | 3417 | 3231.9044 | 3231.9044 | 3231.9044 | 2796.4551 | 780 | 200 | 3776.4551 | 94.41% | 95% | 0% | -59.4966 | 3172.4078 | -2750 | -200 | 222.4078 | -5.56% | 92.21% | 95% | 0% | 3417 | -52
[5 empty] | 2019-01-24 | 42 | 573 | 3243 | -56 | 0 | 0 | 3299 | 3047.0734 | 3047.0734 | 3047.0734 | 2796.4551 | 780 | 200 | 3776.4551 | 94.41% | 95% | 0% | -64.0732 | 2983.0001 | -2750 | -200 | 33.0001 | -0.825% | 92.21% | 95% | 0% | 3299 | -56
[5 empty] | 2019-01-24 | 43 | 573.5 | 3080 | -61 | 0 | 0 | 3141 | 2799.5878 | 2799.5878 | 2799.5878 | 2796.4551 | 780 | 200 | 3776.4551 | 94.41% | 95% | 0% | -69.7941 | 2729.7937 | -2750 | -200 | -220.2063 | 5.505% | 92.19% | 95% | 0% | 3141 | -61
[5 empty] | 2019-01-24 | 44 | 574 | 2881 | -66 | 0 | 0 | 2947 | 2495.7131 | 2495.7131 | 2495.7131 | 2794.8887 | 780 | 200 | 3774.8887 | 94.37% | 95% | 0% | -75.5149 | 2420.1982 | -2750 | -200 | -529.8018 | 13.25% | 92.19% | 95% | 0% | 2947 | -66
[5 empty] | 2019-01-24 | 45 | 574.5 | 2684 | -73 | 0 | 0 | 2757 | 2198.1039 | 2198.1039 | 2198.1039 | 2794.8887 | 780 | 200 | 3774.8887 | 94.37% | 95% | 0% | -83.524 | 2114.5798 | -2750 | -200 | -835.4202 | 20.89% | 92.18% | 95% | 0% | 2757 | -73
[5 empty] | 2019-01-24 | 46 | 575 | 2513 | -80 | 0 | 0 | 2593 | 1941.2201 | 1941.2201 | 1941.2201 | 2794.8887 | 780 | 200 | 3774.8887 | 94.37% | 95% | 0% | -91.5332 | 1849.6869 | -2750 | -200 | -1100.3131 | 27.51% | 92.17% | 95% | 0% | 2593 | -80
[5 empty] | 2019-01-24 | 47 | 575.5 | 2331 | -81 | 0 | 0 | 2412 | 1657.7082 | 1657.7082 | 1657.7082 | 2793.3223 | 780 | 200 | 3773.3223 | 94.33% | 95% | 0% | -92.6773 | 1565.0308 | -2750 | -200 | -1384.9692 | 34.62% | 92.17% | 95% | 0% | 2412 | -81
[5 empty] | 2019-01-24 | 48 | 576 | 2223 | -83 | 0 | 0 | 2306 | 1491.6735 | 1491.6735 | 1491.6735 | 2793.3223 | 780 | 200 | 3773.3223 | 94.33% | 95% | 0% | -94.9657 | 1396.7079 | -2750 | -200 | -1553.2921 | 38.83% | 92.15% | 95% | 0% | 2306 | -83
[5 empty] | 2019-01-25 | 1 | 576.5 | 2185 | -89 | 0 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 2791.756 | 780 | 200 | 3771.756 | 94.29% | 95% | 0% | -101.8307 | 1339.7192 | -2750 | -200 | -1610.2808 | 40.26% | 92.15% | 95% | 0% | 2274 | -89
[5 empty] | 2019-01-25 | 2 | 577 | 2204 | -95 | 0 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 2791.756 | 780 | 200 | 3771.756 | 94.29% | 95% | 0% | -108.6957 | 1372.0133 | -2750 | -200 | -1577.9867 | 39.45% | 92.14% | 95% | 0% | 2299 | -95
[5 empty] | 2019-01-25 | 3 | 577.5 | 2170 | -101 | 0 | 0 | 2271 | 1436.8508 | 1436.8508 | 1436.8508 | 2791.756 | 780 | 200 | 3771.756 | 94.29% | 95% | 0% | -115.5606 | 1321.2901 | -2750 | -200 | -1628.7099 | 40.72% | 92.14% | 95% | 0% | 2271 | -101
[5 empty] | 2019-01-25 | 4 | 578 | 2108 | -106 | 0 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 2790.1896 | 780 | 200 | 3770.1896 | 94.25% | 95% | 0% | -121.2815 | 1226.2865 | -2750 | -200 | -1723.7135 | 43.09% | 92.14% | 95% | 0% | 2214 | -106
[5 empty] | 2019-01-25 | 5 | 578.5 | 2058 | -112 | 0 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 2790.1896 | 780 | 200 | 3770.1896 | 94.25% | 95% | 0% | -128.1465 | 1150.5015 | -2750 | -200 | -1799.4985 | 44.99% | 92.13% | 95% | 0% | 2170 | -112
[5 empty] | 2019-01-25 | 6 | 579 | 2026 | -118 | 0 | 0 | 2144 | 1237.9225 | 1237.9225 | 1237.9225 | 2790.1896 | 780 | 200 | 3770.1896 | 94.25% | 95% | 0% | -135.0114 | 1102.9111 | -2750 | -200 | -1847.0889 | 46.18% | 92.13% | 95% | 0% | 2144 | -118
[5 empty] | 2019-01-25 | 7 | 579.5 | 1984 | -120 | 0 | 0 | 2104 | 1175.2679 | 1175.2679 | 1175.2679 | 2788.6232 | 780 | 200 | 3768.6232 | 94.22% | 95% | 0% | -137.2998 | 1037.9682 | -2750 | -200 | -1912.0318 | 47.8% | 92.12% | 95% | 0% | 2104 | -120
[5 empty] | 2019-01-25 | 8 | 580 | 1948 | -123 | 0 | 0 | 2071 | 1123.5779 | 1123.5779 | 1123.5779 | 2788.6232 | 780 | 200 | 3768.6232 | 94.22% | 95% | 0% | -140.7323 | 982.8456 | -2750 | -200 | -1967.1544 | 49.18% | 92.12% | 95% | 0% | 2071 | -123
[5 empty] | 2019-01-25 | 9 | 580.5 | 1924 | -126 | 0 | 0 | 2050 | 1090.6843 | 1090.6843 | 1090.6843 | 2788.6232 | 780 | 200 | 3768.6232 | 94.22% | 95% | 0% | -144.1648 | 946.5195 | -2750 | -200 | -2003.4805 | 50.09% | 92.12% | 95% | 0% | 2050 | -126
[5 empty] | 2019-01-25 | 10 | 581 | 1914 | -130 | 0 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 2788.6232 | 780 | 200 | 3768.6232 | 94.22% | 95% | 0% | -148.7414 | 932.5446 | -2750 | -200 | -2017.4554 | 50.44% | 92.12% | 95% | 0% | 2044 | -130
[5 empty] | 2019-01-25 | 11 | 581.5 | 1967 | -132 | 0 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 2788.6232 | 780 | 200 | 3768.6232 | 94.22% | 95% | 0% | -151.0297 | 1016.4064 | -2750 | -200 | -1933.5936 | 48.34% | 92.11% | 95% | 0% | 2099 | -132
[5 empty] | 2019-01-25 | 12 | 582 | 2065 | -134 | 0 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 2787.0569 | 780 | 200 | 3767.0569 | 94.18% | 95% | 0% | -153.3181 | 1170.7545 | -2750 | -200 | -1779.2455 | 44.48% | 92.1% | 95% | 0% | 2199 | -134
[5 empty] | 2019-01-25 | 13 | 582.5 | 2320 | -137 | 0 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 2787.0569 | 780 | 200 | 3767.0569 | 94.18% | 95% | 0% | -156.7506 | 1571.444 | -2750 | -200 | -1378.556 | 34.46% | 92.06% | 95% | 0% | 2457 | -137
[5 empty] | 2019-01-25 | 14 | 583 | 2550 | -140 | 0 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 2787.0569 | 780 | 200 | 3767.0569 | 94.18% | 95% | 0% | -160.1831 | 1932.9744 | -2750 | -200 | -1017.0256 | 25.43% | 92.06% | 95% | 0% | 2690 | -140
[5 empty] | 2019-01-25 | 15 | 583.5 | 2827 | -142 | 0 | 0 | 2969 | 2530.1731 | 2530.1731 | 2530.1731 | 2785.4905 | 780 | 200 | 3765.4905 | 94.14% | 95% | 0% | -162.4714 | 2367.7017 | -2750 | -200 | -582.2983 | 14.56% | 92.05% | 95% | 0% | 2969 | -142
[5 empty] | 2019-01-25 | 16 | 584 | 2971 | -145 | 0 | 0 | 3116 | 2760.4287 | 2760.4287 | 2760.4287 | 2785.4905 | 780 | 200 | 3765.4905 | 94.14% | 95% | 0% | -165.9039 | 2594.5248 | -2750 | -200 | -355.4752 | 8.887% | 92.05% | 95% | 0% | 3116 | -145
[5 empty] | 2019-01-25 | 17 | 584.5 | 3020 | -148 | 1 | 0 | 3168 | 2841.8796 | 2841.8796 | 2841.8796 | 2785.4905 | 780 | 200 | 3765.4905 | 94.14% | 95% | 0% | -169.3364 | 2672.5433 | -3550 | -400 | -1277.4567 | 31.94% | 92.04% | 95% | 0% | 3168 | -148
[5 empty] | 2019-01-25 | 18 | 585 | 3029 | -157 | 1 | 0 | 3186 | 2870.0742 | 2870.0742 | 2870.0742 | 2783.9242 | 780 | 200 | 3763.9242 | 94.1% | 95% | 0% | -179.6339 | 2690.4403 | -3550 | -400 | -1259.5597 | 31.49% | 92.04% | 95% | 0% | 3186 | -157
[5 empty] | 2019-01-25 | 19 | 585.5 | 3051 | -161 | 1 | 0 | 3212 | 2910.7997 | 2910.7997 | 2910.7997 | 2783.9242 | 780 | 200 | 3763.9242 | 94.1% | 95% | 0% | -184.2105 | 2726.5891 | -3550 | -400 | -1223.4109 | 30.59% | 92.04% | 95% | 0% | 3212 | -161
[5 empty] | 2019-01-25 | 20 | 586 | 2992 | -196 | 1 | 0 | 3188 | 2873.2069 | 2873.2069 | 2873.2069 | 2783.9242 | 780 | 200 | 3763.9242 | 94.1% | 95% | 0% | -224.2563 | 2648.9506 | -3550 | -400 | -1301.0494 | 32.53% | 92.04% | 95% | 0% | 3188 | -196
[5 empty] | 2019-01-25 | 21 | 586.5 | 2919 | -233 | 1 | 0 | 3152 | 2816.8178 | 2816.8178 | 2816.8178 | 2782.3578 | 780 | 200 | 3762.3578 | 94.06% | 95% | 0% | -266.5904 | 2550.2274 | -3550 | -400 | -1399.7726 | 34.99% | 92.03% | 95% | 0% | 3152 | -233
[5 empty] | 2019-01-25 | 22 | 587 | 2848 | -268 | 1 | 0 | 3116 | 2760.4287 | 2760.4287 | 2760.4287 | 2782.3578 | 780 | 200 | 3762.3578 | 94.06% | 95% | 0% | -306.6362 | 2453.7925 | -3550 | -400 | -1496.2075 | 37.41% | 92.03% | 95% | 0% | 3116 | -268
[5 empty] | 2019-01-25 | 23 | 587.5 | 2799 | -292 | 1 | 0 | 3091 | 2721.2696 | 2721.2696 | 2721.2696 | 2782.3578 | 780 | 200 | 3762.3578 | 94.06% | 95% | 0% | -334.0961 | 2387.1735 | -3550 | -400 | -1562.8265 | 39.07% | 92.02% | 95% | 0% | 3091 | -292
[5 empty] | 2019-01-25 | 24 | 588 | 2757 | -308 | 1 | 0 | 3065 | 2680.5441 | 2680.5441 | 2680.5441 | 2780.7914 | 780 | 200 | 3760.7914 | 94.02% | 95% | 0% | -352.4027 | 2328.1414 | -3550 | -400 | -1621.8586 | 40.55% | 92.01% | 95% | 0% | 3065 | -308
[5 empty] | 2019-01-25 | 25 | 588.5 | 2723 | -319 | 1 | 0 | 3042 | 2644.5177 | 2644.5177 | 2644.5177 | 2780.7914 | 780 | 200 | 3760.7914 | 94.02% | 95% | 0% | -364.9886 | 2279.5292 | -3550 | -400 | -1670.4708 | 41.76% | 92% | 95% | 0% | 3042 | -319
[5 empty] | 2019-01-25 | 26 | 589 | 2679 | -315 | 1 | 0 | 2994 | 2569.3322 | 2569.3322 | 2569.3322 | 2780.7914 | 780 | 200 | 3760.7914 | 94.02% | 95% | 0% | -360.4119 | 2208.9203 | -3550 | -400 | -1741.0797 | 43.53% | 92% | 95% | 0% | 2994 | -315
[5 empty] | 2019-01-25 | 27 | 589.5 | 2666 | -310 | 1 | 0 | 2976 | 2541.1377 | 2541.1377 | 2541.1377 | 2780.7914 | 780 | 200 | 3760.7914 | 94.02% | 95% | 0% | -354.6911 | 2186.4466 | -3550 | -400 | -1763.5534 | 44.09% | 91.99% | 95% | 0% | 2976 | -310
[5 empty] | 2019-01-25 | 28 | 590 | 2648 | -288 | 1 | 0 | 2936 | 2478.4831 | 2478.4831 | 2478.4831 | 2779.2251 | 780 | 200 | 3759.2251 | 93.98% | 95% | 0% | -329.5195 | 2148.9636 | -3550 | -400 | -1801.0364 | 45.03% | 91.99% | 95% | 0% | 2936 | -288
[5 empty] | 2019-01-25 | 29 | 590.5 | 2680 | -266 | 1 | 0 | 2946 | 2494.1467 | 2494.1467 | 2494.1467 | 2779.2251 | 780 | 200 | 3759.2251 | 93.98% | 95% | 0% | -304.3478 | 2189.7989 | -3550 | -400 | -1760.2011 | 44.01% | 91.98% | 95% | 0% | 2946 | -266
[5 empty] | 2019-01-25 | 30 | 591 | 2711 | -238 | 1 | 0 | 2949 | 2498.8458 | 2498.8458 | 2498.8458 | 2779.2251 | 780 | 200 | 3759.2251 | 93.98% | 95% | 0% | -272.3112 | 2226.5346 | -3550 | -400 | -1723.4654 | 43.09% | 91.98% | 95% | 0% | 2949 | -238
[5 empty] | 2019-01-25 | 31 | 591.5 | 2747 | -211 | 1 | 0 | 2958 | 2512.9431 | 2512.9431 | 2512.9431 | 2777.6587 | 780 | 200 | 3757.6587 | 93.94% | 95% | 0% | -241.4188 | 2271.5244 | -3550 | -400 | -1678.4756 | 41.96% | 91.97% | 95% | 0% | 2958 | -211
[5 empty] | 2019-01-25 | 32 | 592 | 2841 | -186 | 1 | 0 | 3027 | 2621.0223 | 2621.0223 | 2621.0223 | 2777.6587 | 780 | 200 | 3757.6587 | 93.94% | 95% | 0% | -212.8146 | 2408.2076 | -3550 | -400 | -1541.7924 | 38.54% | 91.96% | 95% | 0% | 3027 | -186
[5 empty] | 2019-01-25 | 33 | 592.5 | 2945 | -165 | 1 | 0 | 3110 | 2751.0305 | 2751.0305 | 2751.0305 | 2777.6587 | 780 | 200 | 3757.6587 | 93.94% | 95% | 0% | -188.7872 | 2562.2433 | -3550 | -400 | -1387.7567 | 34.69% | 91.96% | 95% | 0% | 3110 | -165
[5 empty] | 2019-01-25 | 34 | 593 | 3070 | -154 | 1 | 0 | 3224 | 2929.596 | 2929.596 | 2929.596 | 2776.0923 | 780 | 200 | 3756.0923 | 93.9% | 95% | 0% | -176.2014 | 2753.3947 | -3550 | -400 | -1196.6053 | 29.92% | 91.96% | 95% | 0% | 3224 | -154
[5 empty] | 2019-01-25 | 35 | 593.5 | 3224 | -152 | 1 | 0 | 3376 | 3167.6834 | 3167.6834 | 3167.6834 | 2776.0923 | 780 | 200 | 3756.0923 | 93.9% | 95% | 0% | -173.913 | 2993.7704 | -3550 | -400 | -956.2296 | 23.91% | 91.96% | 95% | 0% | 3376 | -152
[5 empty] | 2019-01-25 | 36 | 594 | 3230 | -150 | 0 | 0 | 3380 | 3173.9489 | 3173.9489 | 3173.9489 | 2776.0923 | 780 | 200 | 3756.0923 | 93.9% | 95% | 0% | -171.6247 | 3002.3242 | -2750 | -200 | 52.3242 | -1.308% | 91.96% | 95% | 0% | 3380 | -150
[5 empty] | 2019-01-25 | 37 | 594.5 | 3190 | -151 | 0 | 0 | 3341 | 3112.8607 | 3112.8607 | 3112.8607 | 2776.0923 | 780 | 200 | 3756.0923 | 93.9% | 95% | 0% | -172.7689 | 2940.0918 | -2750 | -200 | -9.9082 | 0.2477% | 91.95% | 95% | 0% | 3341 | -151
[5 empty] | 2019-01-25 | 38 | 595 | 3126 | -152 | 0 | 0 | 3278 | 3014.1797 | 3014.1797 | 3014.1797 | 2776.0923 | 780 | 200 | 3756.0923 | 93.9% | 95% | 0% | -173.913 | 2840.2667 | -2750 | -200 | -109.7333 | 2.743% | 91.95% | 95% | 0% | 3278 | -152
[5 empty] | 2019-01-25 | 39 | 595.5 | 3031 | -154 | 0 | 0 | 3185 | 2868.5078 | 2868.5078 | 2868.5078 | 2776.0923 | 780 | 200 | 3756.0923 | 93.9% | 95% | 0% | -176.2014 | 2692.3065 | -2750 | -200 | -257.6935 | 6.442% | 91.94% | 95% | 0% | 3185 | -154
[5 empty] | 2019-01-25 | 40 | 596 | 2936 | -155 | 0 | 0 | 3091 | 2721.2696 | 2721.2696 | 2721.2696 | 2774.526 | 780 | 200 | 3754.526 | 93.86% | 95% | 0% | -177.3455 | 2543.924 | -2750 | -200 | -406.076 | 10.15% | 91.94% | 95% | 0% | 3091 | -155
[5 empty] | 2019-01-25 | 41 | 596.5 | 2823 | -158 | 0 | 0 | 2981 | 2548.9695 | 2548.9695 | 2548.9695 | 2772.9596 | 780 | 200 | 3752.9596 | 93.82% | 95% | 0% | -180.778 | 2368.1915 | -2750 | -200 | -581.8085 | 14.55% | 91.93% | 95% | 0% | 2981 | -158
[5 empty] | 2019-01-25 | 42 | 597 | 2685 | -160 | 0 | 0 | 2845 | 2335.9439 | 2335.9439 | 2335.9439 | 2772.9596 | 780 | 200 | 3752.9596 | 93.82% | 95% | 0% | -183.0664 | 2152.8776 | -2750 | -200 | -797.1224 | 19.93% | 91.91% | 95% | 0% | 2845 | -160
[5 empty] | 2019-01-25 | 43 | 597.5 | 2535 | -162 | 0 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 2772.9596 | 780 | 200 | 3752.9596 | 93.82% | 95% | 0% | -185.3547 | 1918.7673 | -2750 | -200 | -1031.2327 | 25.78% | 91.89% | 95% | 0% | 2697 | -162
[5 empty] | 2019-01-25 | 44 | 598 | 2387 | -164 | 0 | 0 | 2551 | 1875.4328 | 1875.4328 | 1875.4328 | 2772.9596 | 780 | 200 | 3752.9596 | 93.82% | 95% | 0% | -187.643 | 1687.7898 | -2750 | -200 | -1262.2102 | 31.56% | 91.88% | 95% | 0% | 2551 | -164
[5 empty] | 2019-01-25 | 45 | 598.5 | 2245 | -166 | 0 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 2771.3932 | 780 | 200 | 3751.3932 | 93.78% | 95% | 0% | -189.9314 | 1466.2104 | -2750 | -200 | -1483.7896 | 37.09% | 91.87% | 95% | 0% | 2411 | -166
[5 empty] | 2019-01-25 | 46 | 599 | 2109 | -168 | 0 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 2771.3932 | 780 | 200 | 3751.3932 | 93.78% | 95% | 0% | -192.2197 | 1254.0293 | -2750 | -200 | -1695.9707 | 42.4% | 91.86% | 95% | 0% | 2277 | -168
[5 empty] | 2019-01-25 | 47 | 599.5 | 1967 | -171 | 0 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 2771.3932 | 780 | 200 | 3751.3932 | 93.78% | 95% | 0% | -195.6522 | 1032.8721 | -2750 | -200 | -1917.1279 | 47.93% | 91.86% | 95% | 0% | 2138 | -171
[5 empty] | 2019-01-25 | 48 | 600 | 1889 | -174 | 0 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 2771.3932 | 780 | 200 | 3751.3932 | 93.78% | 95% | 0% | -199.0847 | 911.9623 | -2750 | -200 | -2038.0377 | 50.95% | 91.86% | 95% | 0% | 2063 | -174
[5 empty] | 2019-01-26 | 1 | 600.5 | 1863 | -173 | 0 | 0 | 2036 | 1068.7552 | 1068.7552 | 1068.7552 | 2769.8269 | 780 | 200 | 3749.8269 | 93.75% | 95% | 0% | -197.9405 | 870.8146 | -2750 | -200 | -2079.1854 | 51.98% | 91.85% | 95% | 0% | 2036 | -173
[5 empty] | 2019-01-26 | 2 | 601 | 1880 | -172 | 0 | 0 | 2052 | 1093.817 | 1093.817 | 1093.817 | 2769.8269 | 780 | 200 | 3749.8269 | 93.75% | 95% | 0% | -196.7963 | 897.0206 | -2750 | -200 | -2052.9794 | 51.32% | 91.85% | 95% | 0% | 2052 | -172
[5 empty] | 2019-01-26 | 3 | 601.5 | 1850 | -170 | 0 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 2769.8269 | 780 | 200 | 3749.8269 | 93.75% | 95% | 0% | -194.508 | 849.1853 | -2750 | -200 | -2100.8147 | 52.52% | 91.84% | 95% | 0% | 2020 | -170
[5 empty] | 2019-01-26 | 4 | 602 | 1788 | -169 | 0 | 0 | 1957 | 945.0124 | 945.0124 | 945.0124 | 2769.8269 | 780 | 200 | 3749.8269 | 93.75% | 95% | 0% | -193.3638 | 751.6485 | -2750 | -200 | -2198.3515 | 54.96% | 91.83% | 95% | 0% | 1957 | -169
[5 empty] | 2019-01-26 | 5 | 602.5 | 1746 | -167 | 0 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 2769.8269 | 780 | 200 | 3749.8269 | 93.75% | 95% | 0% | -191.0755 | 685.0168 | -2750 | -200 | -2264.9832 | 56.62% | 91.82% | 95% | 0% | 1913 | -167
[5 empty] | 2019-01-26 | 6 | 603 | 1717 | -165 | 0 | 0 | 1882 | 827.535 | 827.535 | 827.535 | 2768.2605 | 780 | 200 | 3748.2605 | 93.71% | 95% | 0% | -188.7872 | 638.7479 | -2750 | -200 | -2311.2521 | 57.78% | 91.82% | 95% | 0% | 1882 | -165
[5 empty] | 2019-01-26 | 7 | 603.5 | 1677 | -161 | 0 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 2768.2605 | 780 | 200 | 3748.2605 | 93.71% | 95% | 0% | -184.2105 | 574.4045 | -2750 | -200 | -2375.5955 | 59.39% | 91.81% | 95% | 0% | 1838 | -161
[5 empty] | 2019-01-26 | 8 | 604 | 1638 | -158 | 0 | 0 | 1796 | 692.8277 | 692.8277 | 692.8277 | 2768.2605 | 780 | 200 | 3748.2605 | 93.71% | 95% | 0% | -180.778 | 512.0497 | -2750 | -200 | -2437.9503 | 60.95% | 91.81% | 95% | 0% | 1796 | -158
[5 empty] | 2019-01-26 | 9 | 604.5 | 1616 | -156 | 0 | 0 | 1772 | 655.235 | 655.235 | 655.235 | 2768.2605 | 780 | 200 | 3748.2605 | 93.71% | 95% | 0% | -178.4897 | 476.7453 | -2750 | -200 | -2473.2547 | 61.83% | 91.78% | 95% | 0% | 1772 | -156
[5 empty] | 2019-01-26 | 10 | 605 | 1615 | -155 | 0 | 0 | 1770 | 652.1022 | 652.1022 | 652.1022 | 2766.6941 | 780 | 200 | 3746.6941 | 93.67% | 95% | 0% | -177.3455 | 474.7567 | -2750 | -200 | -2475.2433 | 61.88% | 91.78% | 95% | 0% | 1770 | -155
[5 empty] | 2019-01-26 | 11 | 605.5 | 1643 | -152 | 0 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 2766.6941 | 780 | 200 | 3746.6941 | 93.67% | 95% | 0% | -173.913 | 517.3483 | -2750 | -200 | -2432.6517 | 60.82% | 91.77% | 95% | 0% | 1795 | -152
[5 empty] | 2019-01-26 | 12 | 606 | 1672 | -149 | 0 | 0 | 1821 | 731.9868 | 731.9868 | 731.9868 | 2766.6941 | 780 | 200 | 3746.6941 | 93.67% | 95% | 0% | -170.4805 | 561.5063 | -2750 | -200 | -2388.4937 | 59.71% | 91.77% | 95% | 0% | 1821 | -149
[5 empty] | 2019-01-26 | 13 | 606.5 | 1794 | -149 | 0 | 0 | 1943 | 923.0833 | 923.0833 | 923.0833 | 2766.6941 | 780 | 200 | 3746.6941 | 93.67% | 95% | 0% | -170.4805 | 752.6027 | -2750 | -200 | -2197.3973 | 54.93% | 91.76% | 95% | 0% | 1943 | -149
[5 empty] | 2019-01-26 | 14 | 607 | 1885 | -149 | 0 | 0 | 2034 | 1065.6224 | 1065.6224 | 1065.6224 | 2765.1278 | 780 | 200 | 3745.1278 | 93.63% | 95% | 0% | -170.4805 | 895.1419 | -2750 | -200 | -2054.8581 | 51.37% | 91.75% | 95% | 0% | 2034 | -149
[5 empty] | 2019-01-26 | 15 | 607.5 | 2007 | -152 | 0 | 0 | 2159 | 1261.418 | 1261.418 | 1261.418 | 2765.1278 | 780 | 200 | 3745.1278 | 93.63% | 95% | 0% | -173.913 | 1087.5049 | -2750 | -200 | -1862.4951 | 46.56% | 91.74% | 95% | 0% | 2159 | -152
[5 empty] | 2019-01-26 | 16 | 608 | 2042 | -155 | 0 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 2765.1278 | 780 | 200 | 3745.1278 | 93.63% | 95% | 0% | -177.3455 | 1143.5943 | -2750 | -200 | -1806.4057 | 45.16% | 91.73% | 95% | 0% | 2197 | -155
[5 empty] | 2019-01-26 | 17 | 608.5 | 2218 | -160 | 0 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 2765.1278 | 780 | 200 | 3745.1278 | 93.63% | 95% | 0% | -183.0664 | 1421.3854 | -2750 | -200 | -1528.6146 | 38.22% | 91.71% | 95% | 0% | 2378 | -160
[5 empty] | 2019-01-26 | 18 | 609 | 2337 | -175 | 0 | 0 | 2512 | 1814.3446 | 1814.3446 | 1814.3446 | 2763.5614 | 780 | 200 | 3743.5614 | 93.59% | 95% | 0% | -200.2288 | 1614.1158 | -2750 | -200 | -1335.8842 | 33.4% | 91.71% | 95% | 0% | 2512 | -175
[5 empty] | 2019-01-26 | 19 | 609.5 | 2407 | -198 | 0 | 0 | 2605 | 1960.0165 | 1960.0165 | 1960.0165 | 2763.5614 | 780 | 200 | 3743.5614 | 93.59% | 95% | 0% | -226.5446 | 1733.4719 | -2750 | -200 | -1216.5281 | 30.41% | 91.7% | 95% | 0% | 2605 | -198
[5 empty] | 2019-01-26 | 20 | 610 | 2427 | -219 | 1 | 0 | 2646 | 2024.2374 | 2024.2374 | 2024.2374 | 2763.5614 | 780 | 200 | 3743.5614 | 93.59% | 95% | 0% | -250.5721 | 1773.6653 | -3550 | -400 | -2176.3347 | 54.41% | 91.7% | 95% | 0% | 2646 | -219
[5 empty] | 2019-01-26 | 21 | 610.5 | 2447 | -241 | 1 | 0 | 2688 | 2090.0247 | 2090.0247 | 2090.0247 | 2761.9951 | 780 | 200 | 3741.9951 | 93.55% | 95% | 0% | -275.7437 | 1814.281 | -3550 | -400 | -2135.719 | 53.39% | 91.69% | 95% | 0% | 2688 | -241
[5 empty] | 2019-01-26 | 22 | 611 | 2412 | -260 | 1 | 0 | 2672 | 2064.9629 | 2064.9629 | 2064.9629 | 2760.4287 | 780 | 200 | 3740.4287 | 93.51% | 95% | 0% | -297.4828 | 1767.4801 | -3550 | -400 | -2182.5199 | 54.56% | 91.68% | 95% | 0% | 2672 | -260
[5 empty] | 2019-01-26 | 23 | 611.5 | 2396 | -273 | 1 | 0 | 2669 | 2060.2638 | 2060.2638 | 2060.2638 | 2760.4287 | 780 | 200 | 3740.4287 | 93.51% | 95% | 0% | -312.357 | 1747.9068 | -3550 | -400 | -2202.0932 | 55.05% | 91.68% | 95% | 0% | 2669 | -273
[5 empty] | 2019-01-26 | 24 | 612 | 2387 | -278 | 1 | 0 | 2665 | 2053.9984 | 2053.9984 | 2053.9984 | 2760.4287 | 780 | 200 | 3740.4287 | 93.51% | 95% | 0% | -318.0778 | 1735.9205 | -3550 | -400 | -2214.0795 | 55.35% | 91.67% | 95% | 0% | 2665 | -278
[5 empty] | 2019-01-26 | 25 | 612.5 | 2363 | -295 | 1 | 0 | 2658 | 2043.0338 | 2043.0338 | 2043.0338 | 2758.8623 | 780 | 200 | 3738.8623 | 93.47% | 95% | 0% | -337.5286 | 1705.5052 | -3550 | -400 | -2244.4948 | 56.11% | 91.67% | 95% | 0% | 2658 | -295
[5 empty] | 2019-01-26 | 26 | 613 | 2357 | -289 | 1 | 0 | 2646 | 2024.2374 | 2024.2374 | 2024.2374 | 2758.8623 | 780 | 200 | 3738.8623 | 93.47% | 95% | 0% | -330.6636 | 1693.5738 | -3550 | -400 | -2256.4262 | 56.41% | 91.66% | 95% | 0% | 2646 | -289
[5 empty] | 2019-01-26 | 27 | 613.5 | 2355 | -270 | 1 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 2757.296 | 780 | 200 | 3737.296 | 93.43% | 95% | 0% | -308.9245 | 1682.4193 | -3550 | -400 | -2267.5807 | 56.69% | 91.66% | 95% | 0% | 2625 | -270
[5 empty] | 2019-01-26 | 28 | 614 | 2352 | -253 | 1 | 0 | 2605 | 1960.0165 | 1960.0165 | 1960.0165 | 2757.296 | 780 | 200 | 3737.296 | 93.43% | 95% | 0% | -289.4737 | 1670.5428 | -3550 | -400 | -2279.4572 | 56.99% | 91.66% | 95% | 0% | 2605 | -253
[5 empty] | 2019-01-26 | 29 | 614.5 | 2372 | -233 | 1 | 0 | 2605 | 1960.0165 | 1960.0165 | 1960.0165 | 2757.296 | 780 | 200 | 3737.296 | 93.43% | 95% | 0% | -266.5904 | 1693.4261 | -3550 | -400 | -2256.5739 | 56.41% | 91.65% | 95% | 0% | 2605 | -233
[5 empty] | 2019-01-26 | 30 | 615 | 2416 | -208 | 1 | 0 | 2624 | 1989.7774 | 1989.7774 | 1989.7774 | 2757.296 | 780 | 200 | 3737.296 | 93.43% | 95% | 0% | -237.9863 | 1751.7911 | -3550 | -400 | -2198.2089 | 54.96% | 91.64% | 95% | 0% | 2624 | -208
[5 empty] | 2019-01-26 | 31 | 615.5 | 2453 | -186 | 1 | 0 | 2639 | 2013.2729 | 2013.2729 | 2013.2729 | 2757.296 | 780 | 200 | 3737.296 | 93.43% | 95% | 0% | -212.8146 | 1800.4582 | -3550 | -400 | -2149.5418 | 53.74% | 91.64% | 95% | 0% | 2639 | -186
[5 empty] | 2019-01-26 | 32 | 616 | 2512 | -169 | 1 | 0 | 2681 | 2079.0602 | 2079.0602 | 2079.0602 | 2757.296 | 780 | 200 | 3737.296 | 93.43% | 95% | 0% | -193.3638 | 1885.6963 | -3550 | -400 | -2064.3037 | 51.61% | 91.62% | 95% | 0% | 2681 | -169
[5 empty] | 2019-01-26 | 33 | 616.5 | 2601 | -159 | 1 | 0 | 2760 | 2202.803 | 2202.803 | 2202.803 | 2755.7296 | 780 | 200 | 3735.7296 | 93.39% | 95% | 0% | -181.9222 | 2020.8808 | -3550 | -400 | -1929.1192 | 48.23% | 91.62% | 95% | 0% | 2760 | -159
[5 empty] | 2019-01-26 | 34 | 617 | 2741 | -152 | 1 | 0 | 2893 | 2411.1294 | 2411.1294 | 2411.1294 | 2755.7296 | 780 | 200 | 3735.7296 | 93.39% | 95% | 0% | -173.913 | 2237.2164 | -3550 | -400 | -1712.7836 | 42.82% | 91.62% | 95% | 0% | 2893 | -152
[5 empty] | 2019-01-26 | 35 | 617.5 | 2882 | -151 | 1 | 0 | 3033 | 2630.4204 | 2630.4204 | 2630.4204 | 2755.7296 | 780 | 200 | 3735.7296 | 93.39% | 95% | 0% | -172.7689 | 2457.6516 | -3550 | -400 | -1492.3484 | 37.31% | 91.62% | 95% | 0% | 3033 | -151
[5 empty] | 2019-01-26 | 36 | 618 | 2913 | -150 | 0 | 0 | 3063 | 2677.4114 | 2677.4114 | 2677.4114 | 2755.7296 | 780 | 200 | 3735.7296 | 93.39% | 95% | 0% | -171.6247 | 2505.7867 | -2750 | -200 | -444.2133 | 11.11% | 91.61% | 95% | 0% | 3063 | -150
[5 empty] | 2019-01-26 | 37 | 618.5 | 2875 | -152 | 0 | 0 | 3027 | 2621.0223 | 2621.0223 | 2621.0223 | 2755.7296 | 780 | 200 | 3735.7296 | 93.39% | 95% | 0% | -173.913 | 2447.1092 | -2750 | -200 | -502.8908 | 12.57% | 91.61% | 95% | 0% | 3027 | -152
[5 empty] | 2019-01-26 | 38 | 619 | 2819 | -154 | 0 | 0 | 2973 | 2536.4386 | 2536.4386 | 2536.4386 | 2755.7296 | 780 | 200 | 3735.7296 | 93.39% | 95% | 0% | -176.2014 | 2360.2372 | -2750 | -200 | -589.7628 | 14.74% | 91.6% | 95% | 0% | 2973 | -154
[5 empty] | 2019-01-26 | 39 | 619.5 | 2748 | -155 | 0 | 0 | 2903 | 2426.7931 | 2426.7931 | 2426.7931 | 2754.1632 | 780 | 200 | 3734.1632 | 93.35% | 95% | 0% | -177.3455 | 2249.4475 | -2750 | -200 | -700.5525 | 17.51% | 91.6% | 95% | 0% | 2903 | -155
[5 empty] | 2019-01-26 | 40 | 620 | 2639 | -156 | 0 | 0 | 2795 | 2257.6257 | 2257.6257 | 2257.6257 | 2754.1632 | 780 | 200 | 3734.1632 | 93.35% | 95% | 0% | -178.4897 | 2079.136 | -2750 | -200 | -870.864 | 21.77% | 91.6% | 95% | 0% | 2795 | -156
[5 empty] | 2019-01-26 | 41 | 620.5 | 2541 | -162 | 0 | 0 | 2703 | 2113.5202 | 2113.5202 | 2113.5202 | 2754.1632 | 780 | 200 | 3734.1632 | 93.35% | 95% | 0% | -185.3547 | 1928.1655 | -2750 | -200 | -1021.8345 | 25.55% | 91.58% | 95% | 0% | 2703 | -162
[5 empty] | 2019-01-26 | 42 | 621 | 2430 | -168 | 0 | 0 | 2598 | 1949.0519 | 1949.0519 | 1949.0519 | 2754.1632 | 780 | 200 | 3734.1632 | 93.35% | 95% | 0% | -192.2197 | 1756.8323 | -2750 | -200 | -1193.1677 | 29.83% | 91.57% | 95% | 0% | 2598 | -168
[5 empty] | 2019-01-26 | 43 | 621.5 | 2303 | -172 | 0 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 2754.1632 | 780 | 200 | 3734.1632 | 93.35% | 95% | 0% | -196.7963 | 1559.5928 | -2750 | -200 | -1390.4072 | 34.76% | 91.54% | 95% | 0% | 2475 | -172
[5 empty] | 2019-01-26 | 44 | 622 | 2217 | -176 | 0 | 0 | 2393 | 1627.9472 | 1627.9472 | 1627.9472 | 2754.1632 | 780 | 200 | 3734.1632 | 93.35% | 95% | 0% | -201.373 | 1426.5742 | -2750 | -200 | -1523.4258 | 38.09% | 91.54% | 95% | 0% | 2393 | -176
[5 empty] | 2019-01-26 | 45 | 622.5 | 2083 | -178 | 0 | 0 | 2261 | 1421.1871 | 1421.1871 | 1421.1871 | 2754.1632 | 780 | 200 | 3734.1632 | 93.35% | 95% | 0% | -203.6613 | 1217.5258 | -2750 | -200 | -1732.4742 | 43.31% | 91.52% | 95% | 0% | 2261 | -178
[5 empty] | 2019-01-26 | 46 | 623 | 1977 | -180 | 0 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 2752.5969 | 780 | 200 | 3732.5969 | 93.31% | 95% | 0% | -205.9497 | 1052.3356 | -2750 | -200 | -1897.6644 | 47.44% | 91.51% | 95% | 0% | 2157 | -180
[5 empty] | 2019-01-26 | 47 | 623.5 | 1872 | -184 | 0 | 0 | 2056 | 1100.0824 | 1100.0824 | 1100.0824 | 2752.5969 | 780 | 200 | 3732.5969 | 93.31% | 95% | 0% | -210.5263 | 889.5561 | -2750 | -200 | -2060.4439 | 51.51% | 91.5% | 95% | 0% | 2056 | -184
[5 empty] | 2019-01-26 | 48 | 624 | 1802 | -188 | 0 | 0 | 1990 | 996.7024 | 996.7024 | 996.7024 | 2752.5969 | 780 | 200 | 3732.5969 | 93.31% | 95% | 0% | -215.103 | 781.5994 | -2750 | -200 | -2168.4006 | 54.21% | 91.49% | 95% | 0% | 1990 | -188
[5 empty] | 2019-01-27 | 1 | 624.5 | 1774 | -191 | 0 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 2752.5969 | 780 | 200 | 3732.5969 | 93.31% | 95% | 0% | -218.5355 | 739.0078 | -2750 | -200 | -2210.9922 | 55.27% | 91.48% | 95% | 0% | 1965 | -191
[5 empty] | 2019-01-27 | 2 | 625 | 1797 | -194 | 0 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 2752.5969 | 780 | 200 | 3732.5969 | 93.31% | 95% | 0% | -221.968 | 776.3008 | -2750 | -200 | -2173.6992 | 54.34% | 91.48% | 95% | 0% | 1991 | -194
[5 empty] | 2019-01-27 | 3 | 625.5 | 1744 | -197 | 0 | 0 | 1941 | 919.9505 | 919.9505 | 919.9505 | 2752.5969 | 780 | 200 | 3732.5969 | 93.31% | 95% | 0% | -225.4005 | 694.5501 | -2750 | -200 | -2255.4499 | 56.39% | 91.46% | 95% | 0% | 1941 | -197
[5 empty] | 2019-01-27 | 4 | 626 | 1656 | -201 | 0 | 0 | 1857 | 788.3759 | 788.3759 | 788.3759 | 2751.0305 | 780 | 200 | 3731.0305 | 93.28% | 95% | 0% | -229.9771 | 558.3988 | -2750 | -200 | -2391.6012 | 59.79% | 91.46% | 95% | 0% | 1857 | -201
[5 empty] | 2019-01-27 | 5 | 626.5 | 1605 | -197 | 0 | 0 | 1802 | 702.2259 | 702.2259 | 702.2259 | 2751.0305 | 780 | 200 | 3731.0305 | 93.28% | 95% | 0% | -225.4005 | 476.8254 | -2750 | -200 | -2473.1746 | 61.83% | 91.45% | 95% | 0% | 1802 | -197
[5 empty] | 2019-01-27 | 6 | 627 | 1588 | -193 | 0 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 2751.0305 | 780 | 200 | 3731.0305 | 93.28% | 95% | 0% | -220.8238 | 448.5084 | -2750 | -200 | -2501.4916 | 62.54% | 91.44% | 95% | 0% | 1781 | -193
[5 empty] | 2019-01-27 | 7 | 627.5 | 1536 | -204 | 0 | 0 | 1740 | 605.1113 | 605.1113 | 605.1113 | 2751.0305 | 780 | 200 | 3731.0305 | 93.28% | 95% | 0% | -233.4096 | 371.7017 | -2750 | -200 | -2578.2983 | 64.46% | 91.44% | 95% | 0% | 1740 | -204
[5 empty] | 2019-01-27 | 8 | 628 | 1465 | -216 | 0 | 0 | 1681 | 512.6958 | 512.6958 | 512.6958 | 2751.0305 | 780 | 200 | 3731.0305 | 93.28% | 95% | 0% | -247.1396 | 265.5562 | -2750 | -200 | -2684.4438 | 67.11% | 91.43% | 95% | 0% | 1681 | -216
[5 empty] | 2019-01-27 | 9 | 628.5 | 1423 | -220 | 0 | 0 | 1643 | 453.1739 | 453.1739 | 453.1739 | 2751.0305 | 780 | 200 | 3731.0305 | 93.28% | 95% | 0% | -251.7162 | 201.4577 | -2750 | -200 | -2748.5423 | 68.71% | 91.43% | 95% | 0% | 1643 | -220
[5 empty] | 2019-01-27 | 10 | 629 | 1396 | -225 | 0 | 0 | 1621 | 418.7139 | 418.7139 | 418.7139 | 2751.0305 | 780 | 200 | 3731.0305 | 93.28% | 95% | 0% | -257.4371 | 161.2769 | -2750 | -200 | -2788.7231 | 69.72% | 91.42% | 95% | 0% | 1621 | -225
[5 empty] | 2019-01-27 | 11 | 629.5 | 1393 | -222 | 0 | 0 | 1615 | 409.3157 | 409.3157 | 409.3157 | 2749.4641 | 780 | 200 | 3729.4641 | 93.24% | 95% | 0% | -254.0046 | 155.3112 | -2750 | -200 | -2794.6888 | 69.87% | 91.42% | 95% | 0% | 1615 | -222
[5 empty] | 2019-01-27 | 12 | 630 | 1408 | -220 | 0 | 0 | 1628 | 429.6785 | 429.6785 | 429.6785 | 2749.4641 | 780 | 200 | 3729.4641 | 93.24% | 95% | 0% | -251.7162 | 177.9622 | -2750 | -200 | -2772.0378 | 69.3% | 91.41% | 95% | 0% | 1628 | -220
[5 empty] | 2019-01-27 | 13 | 630.5 | 1487 | -219 | 0 | 0 | 1706 | 551.8549 | 551.8549 | 551.8549 | 2749.4641 | 780 | 200 | 3729.4641 | 93.24% | 95% | 0% | -250.5721 | 301.2828 | -2750 | -200 | -2648.7172 | 66.22% | 91.41% | 95% | 0% | 1706 | -219
[5 empty] | 2019-01-27 | 14 | 631 | 1547 | -218 | 0 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 2749.4641 | 780 | 200 | 3729.4641 | 93.24% | 95% | 0% | -249.4279 | 394.8425 | -2750 | -200 | -2555.1575 | 63.88% | 91.41% | 95% | 0% | 1765 | -218
[5 empty] | 2019-01-27 | 15 | 631.5 | 1635 | -220 | 0 | 0 | 1855 | 785.2432 | 785.2432 | 785.2432 | 2749.4641 | 780 | 200 | 3729.4641 | 93.24% | 95% | 0% | -251.7162 | 533.527 | -2750 | -200 | -2416.473 | 60.41% | 91.4% | 95% | 0% | 1855 | -220
[5 empty] | 2019-01-27 | 16 | 632 | 1688 | -221 | 0 | 0 | 1909 | 869.8269 | 869.8269 | 869.8269 | 2749.4641 | 780 | 200 | 3729.4641 | 93.24% | 95% | 0% | -252.8604 | 616.9665 | -2750 | -200 | -2333.0335 | 58.33% | 91.4% | 95% | 0% | 1909 | -221
[5 empty] | 2019-01-27 | 17 | 632.5 | 1804 | -223 | 0 | 0 | 2027 | 1054.6579 | 1054.6579 | 1054.6579 | 2747.8978 | 780 | 200 | 3727.8978 | 93.2% | 95% | 0% | -255.1487 | 799.5091 | -2750 | -200 | -2150.4909 | 53.76% | 91.4% | 95% | 0% | 2027 | -223
[5 empty] | 2019-01-27 | 18 | 633 | 1903 | -252 | 0 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 2747.8978 | 780 | 200 | 3727.8978 | 93.2% | 95% | 0% | -288.3295 | 966.823 | -2750 | -200 | -1983.177 | 49.58% | 91.39% | 95% | 0% | 2155 | -252
[5 empty] | 2019-01-27 | 19 | 633.5 | 1937 | -320 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 2747.8978 | 780 | 200 | 3727.8978 | 93.2% | 95% | 0% | -366.1327 | 1048.789 | -3550 | -400 | -2901.211 | 72.53% | 91.39% | 95% | 0% | 2257 | -320
[5 empty] | 2019-01-27 | 20 | 634 | 1920 | -382 | 1 | 0 | 2302 | 1485.4081 | 1485.4081 | 1485.4081 | 2746.3314 | 780 | 200 | 3726.3314 | 93.16% | 95% | 0% | -437.0709 | 1048.3371 | -3550 | -400 | -2901.6629 | 72.54% | 91.39% | 95% | 0% | 2302 | -382
[5 empty] | 2019-01-27 | 21 | 634.5 | 1923 | -430 | 1 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 2746.3314 | 780 | 200 | 3726.3314 | 93.16% | 95% | 0% | -491.9908 | 1073.3018 | -3550 | -400 | -2876.6982 | 71.92% | 91.38% | 95% | 0% | 2353 | -430
[5 empty] | 2019-01-27 | 22 | 635 | 1928 | -447 | 1 | 0 | 2375 | 1599.7527 | 1599.7527 | 1599.7527 | 2746.3314 | 780 | 200 | 3726.3314 | 93.16% | 95% | 0% | -511.4416 | 1088.311 | -3550 | -400 | -2861.689 | 71.54% | 91.38% | 95% | 0% | 2375 | -447
[5 empty] | 2019-01-27 | 23 | 635.5 | 1941 | -469 | 1 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 2744.765 | 780 | 200 | 3724.765 | 93.12% | 95% | 0% | -536.6133 | 1117.9622 | -3550 | -400 | -2832.0378 | 70.8% | 91.37% | 95% | 0% | 2410 | -469
[5 empty] | 2019-01-27 | 24 | 636 | 1965 | -482 | 1 | 0 | 2447 | 1712.5309 | 1712.5309 | 1712.5309 | 2744.765 | 780 | 200 | 3724.765 | 93.12% | 95% | 0% | -551.4874 | 1161.0435 | -3550 | -400 | -2788.9565 | 69.72% | 91.37% | 95% | 0% | 2447 | -482
[5 empty] | 2019-01-27 | 25 | 636.5 | 2025 | -468 | 1 | 0 | 2493 | 1784.5837 | 1784.5837 | 1784.5837 | 2744.765 | 780 | 200 | 3724.765 | 93.12% | 95% | 0% | -535.4691 | 1249.1146 | -3550 | -400 | -2700.8854 | 67.52% | 91.36% | 95% | 0% | 2493 | -468
[5 empty] | 2019-01-27 | 26 | 637 | 2063 | -460 | 1 | 0 | 2523 | 1831.5746 | 1831.5746 | 1831.5746 | 2744.765 | 780 | 200 | 3724.765 | 93.12% | 95% | 0% | -526.3158 | 1305.2588 | -3550 | -400 | -2644.7412 | 66.12% | 91.34% | 95% | 0% | 2523 | -460
[5 empty] | 2019-01-27 | 27 | 637.5 | 2110 | -439 | 1 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 2743.1987 | 780 | 200 | 3723.1987 | 93.08% | 95% | 0% | -502.2883 | 1370.0118 | -3550 | -400 | -2579.9882 | 64.5% | 91.33% | 95% | 0% | 2549 | -439
[5 empty] | 2019-01-27 | 28 | 638 | 2122 | -427 | 1 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 2743.1987 | 780 | 200 | 3723.1987 | 93.08% | 95% | 0% | -488.5584 | 1383.7417 | -3550 | -400 | -2566.2583 | 64.16% | 91.31% | 95% | 0% | 2549 | -427
[5 empty] | 2019-01-27 | 29 | 638.5 | 2179 | -397 | 1 | 0 | 2576 | 1914.5919 | 1914.5919 | 1914.5919 | 2743.1987 | 780 | 200 | 3723.1987 | 93.08% | 95% | 0% | -454.2334 | 1460.3585 | -3550 | -400 | -2489.6415 | 62.24% | 91.3% | 95% | 0% | 2576 | -397
[5 empty] | 2019-01-27 | 30 | 639 | 2252 | -356 | 1 | 0 | 2608 | 1964.7156 | 1964.7156 | 1964.7156 | 2741.6323 | 780 | 200 | 3721.6323 | 93.04% | 95% | 0% | -407.3227 | 1557.3929 | -3550 | -400 | -2392.6071 | 59.82% | 91.3% | 95% | 0% | 2608 | -356
[5 empty] | 2019-01-27 | 31 | 639.5 | 2338 | -322 | 1 | 0 | 2660 | 2046.1665 | 2046.1665 | 2046.1665 | 2741.6323 | 780 | 200 | 3721.6323 | 93.04% | 95% | 0% | -368.4211 | 1677.7455 | -3550 | -400 | -2272.2545 | 56.81% | 91.3% | 95% | 0% | 2660 | -322
[5 empty] | 2019-01-27 | 32 | 640 | 2448 | -289 | 1 | 0 | 2737 | 2166.7766 | 2166.7766 | 2166.7766 | 2741.6323 | 780 | 200 | 3721.6323 | 93.04% | 95% | 0% | -330.6636 | 1836.113 | -3550 | -400 | -2113.887 | 52.85% | 91.29% | 95% | 0% | 2737 | -289
[5 empty] | 2019-01-27 | 33 | 640.5 | 2569 | -259 | 1 | 0 | 2828 | 2309.3157 | 2309.3157 | 2309.3157 | 2740.066 | 780 | 200 | 3720.066 | 93% | 95% | 0% | -296.3387 | 2012.9771 | -3550 | -400 | -1937.0229 | 48.43% | 91.28% | 95% | 0% | 2828 | -259
[5 empty] | 2019-01-27 | 34 | 641 | 2749 | -244 | 1 | 0 | 2993 | 2567.7659 | 2567.7659 | 2567.7659 | 2740.066 | 780 | 200 | 3720.066 | 93% | 95% | 0% | -279.1762 | 2288.5897 | -3550 | -400 | -1661.4103 | 41.54% | 91.28% | 95% | 0% | 2993 | -244
[5 empty] | 2019-01-27 | 35 | 641.5 | 2896 | -238 | 1 | 0 | 3134 | 2788.6232 | 2788.6232 | 2788.6232 | 2738.4996 | 780 | 200 | 3718.4996 | 92.96% | 95% | 0% | -272.3112 | 2516.312 | -3550 | -400 | -1433.688 | 35.84% | 91.28% | 95% | 0% | 3134 | -238
[5 empty] | 2019-01-27 | 36 | 642 | 2917 | -233 | 0 | 0 | 3150 | 2813.6851 | 2813.6851 | 2813.6851 | 2738.4996 | 780 | 200 | 3718.4996 | 92.96% | 95% | 0% | -266.5904 | 2547.0947 | -2750 | -200 | -402.9053 | 10.07% | 91.27% | 95% | 0% | 3150 | -233
[5 empty] | 2019-01-27 | 37 | 642.5 | 2880 | -226 | 0 | 0 | 3106 | 2744.765 | 2744.765 | 2744.765 | 2738.4996 | 780 | 200 | 3718.4996 | 92.96% | 95% | 0% | -258.5812 | 2486.1838 | -2750 | -200 | -463.8162 | 11.6% | 91.26% | 95% | 0% | 3106 | -226
[5 empty] | 2019-01-27 | 38 | 643 | 2810 | -220 | 0 | 0 | 3030 | 2625.7214 | 2625.7214 | 2625.7214 | 2738.4996 | 780 | 200 | 3718.4996 | 92.96% | 95% | 0% | -251.7162 | 2374.0051 | -2750 | -200 | -575.9949 | 14.4% | 91.26% | 95% | 0% | 3030 | -220
[5 empty] | 2019-01-27 | 39 | 643.5 | 2765 | -213 | 0 | 0 | 2978 | 2544.2704 | 2544.2704 | 2544.2704 | 2738.4996 | 780 | 200 | 3718.4996 | 92.96% | 95% | 0% | -243.7071 | 2300.5633 | -2750 | -200 | -649.4367 | 16.24% | 91.24% | 95% | 0% | 2978 | -213
[5 empty] | 2019-01-27 | 40 | 644 | 2692 | -205 | 0 | 0 | 2897 | 2417.3949 | 2417.3949 | 2417.3949 | 2738.4996 | 780 | 200 | 3718.4996 | 92.96% | 95% | 0% | -234.5538 | 2182.8411 | -2750 | -200 | -767.1589 | 19.18% | 91.24% | 95% | 0% | 2897 | -205
[5 empty] | 2019-01-27 | 41 | 644.5 | 2628 | -198 | 0 | 0 | 2826 | 2306.183 | 2306.183 | 2306.183 | 2738.4996 | 780 | 200 | 3718.4996 | 92.96% | 95% | 0% | -226.5446 | 2079.6384 | -2750 | -200 | -870.3616 | 21.76% | 91.23% | 95% | 0% | 2826 | -198
[5 empty] | 2019-01-27 | 42 | 645 | 2530 | -191 | 0 | 0 | 2721 | 2141.7148 | 2141.7148 | 2141.7148 | 2736.9332 | 780 | 200 | 3716.9332 | 92.92% | 95% | 0% | -218.5355 | 1923.1793 | -2750 | -200 | -1026.8207 | 25.67% | 91.23% | 95% | 0% | 2721 | -191
[5 empty] | 2019-01-27 | 43 | 645.5 | 2430 | -190 | 0 | 0 | 2620 | 1983.512 | 1983.512 | 1983.512 | 2736.9332 | 780 | 200 | 3716.9332 | 92.92% | 95% | 0% | -217.3913 | 1766.1206 | -2750 | -200 | -1183.8794 | 29.6% | 91.23% | 95% | 0% | 2620 | -190
[5 empty] | 2019-01-27 | 44 | 646 | 2299 | -188 | 0 | 0 | 2487 | 1775.1855 | 1775.1855 | 1775.1855 | 2736.9332 | 780 | 200 | 3716.9332 | 92.92% | 95% | 0% | -215.103 | 1560.0825 | -2750 | -200 | -1389.9175 | 34.75% | 91.22% | 95% | 0% | 2487 | -188
[5 empty] | 2019-01-27 | 45 | 646.5 | 2173 | -186 | 0 | 0 | 2359 | 1574.6908 | 1574.6908 | 1574.6908 | 2735.3669 | 780 | 200 | 3715.3669 | 92.88% | 95% | 0% | -212.8146 | 1361.8762 | -2750 | -200 | -1588.1238 | 39.7% | 91.2% | 95% | 0% | 2359 | -186
[5 empty] | 2019-01-27 | 46 | 647 | 2053 | -183 | 0 | 0 | 2236 | 1382.028 | 1382.028 | 1382.028 | 2735.3669 | 780 | 200 | 3715.3669 | 92.88% | 95% | 0% | -209.3822 | 1172.6459 | -2750 | -200 | -1777.3541 | 44.43% | 91.18% | 95% | 0% | 2236 | -183
[5 empty] | 2019-01-27 | 47 | 647.5 | 1919 | -176 | 0 | 0 | 2095 | 1161.1707 | 1161.1707 | 1161.1707 | 2735.3669 | 780 | 200 | 3715.3669 | 92.88% | 95% | 0% | -201.373 | 959.7977 | -2750 | -200 | -1990.2023 | 49.76% | 91.18% | 95% | 0% | 2095 | -176
[5 empty] | 2019-01-27 | 48 | 648 | 1843 | -170 | 0 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 2735.3669 | 780 | 200 | 3715.3669 | 92.88% | 95% | 0% | -194.508 | 838.2208 | -2750 | -200 | -2111.7792 | 52.79% | 91.17% | 95% | 0% | 2013 | -170
[5 empty] | 2019-01-28 | 1 | 648.5 | 1842 | -168 | 0 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 2735.3669 | 780 | 200 | 3715.3669 | 92.88% | 95% | 0% | -192.2197 | 835.81 | -2750 | -200 | -2114.19 | 52.85% | 91.15% | 95% | 0% | 2010 | -168
[5 empty] | 2019-01-28 | 2 | 649 | 1880 | -167 | 0 | 0 | 2047 | 1085.9852 | 1085.9852 | 1085.9852 | 2733.8005 | 780 | 200 | 3713.8005 | 92.85% | 95% | 0% | -191.0755 | 894.9096 | -2750 | -200 | -2055.0904 | 51.38% | 91.15% | 95% | 0% | 2047 | -167
[5 empty] | 2019-01-28 | 3 | 649.5 | 1868 | -164 | 0 | 0 | 2032 | 1062.4897 | 1062.4897 | 1062.4897 | 2733.8005 | 780 | 200 | 3713.8005 | 92.85% | 95% | 0% | -187.643 | 874.8467 | -2750 | -200 | -2075.1533 | 51.88% | 91.14% | 95% | 0% | 2032 | -164
[5 empty] | 2019-01-28 | 4 | 650 | 1843 | -162 | 0 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 2733.8005 | 780 | 200 | 3713.8005 | 92.85% | 95% | 0% | -185.3547 | 834.8432 | -2750 | -200 | -2115.1568 | 52.88% | 91.13% | 95% | 0% | 2005 | -162
[5 empty] | 2019-01-28 | 5 | 650.5 | 1814 | -160 | 0 | 0 | 1974 | 971.6406 | 971.6406 | 971.6406 | 2733.8005 | 780 | 200 | 3713.8005 | 92.85% | 95% | 0% | -183.0664 | 788.5742 | -2750 | -200 | -2161.4258 | 54.04% | 91.13% | 95% | 0% | 1974 | -160
[5 empty] | 2019-01-28 | 6 | 651 | 1814 | -158 | 0 | 0 | 1972 | 968.5078 | 968.5078 | 968.5078 | 2733.8005 | 780 | 200 | 3713.8005 | 92.85% | 95% | 0% | -180.778 | 787.7298 | -2750 | -200 | -2162.2702 | 54.06% | 91.13% | 95% | 0% | 1972 | -158
[5 empty] | 2019-01-28 | 7 | 651.5 | 1806 | -152 | 0 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 2733.8005 | 780 | 200 | 3713.8005 | 92.85% | 95% | 0% | -173.913 | 772.6657 | -2750 | -200 | -2177.3343 | 54.43% | 91.13% | 95% | 0% | 1958 | -152
[5 empty] | 2019-01-28 | 8 | 652 | 1791 | -147 | 0 | 0 | 1938 | 915.2514 | 915.2514 | 915.2514 | 2733.8005 | 780 | 200 | 3713.8005 | 92.85% | 95% | 0% | -168.1922 | 747.0592 | -2750 | -200 | -2202.9408 | 55.07% | 91.12% | 95% | 0% | 1938 | -147
[5 empty] | 2019-01-28 | 9 | 652.5 | 1796 | -143 | 0 | 0 | 1939 | 916.8178 | 916.8178 | 916.8178 | 2732.2341 | 780 | 200 | 3712.2341 | 92.81% | 95% | 0% | -163.6156 | 753.2022 | -2750 | -200 | -2196.7978 | 54.92% | 91.12% | 95% | 0% | 1939 | -143
[5 empty] | 2019-01-28 | 10 | 653 | 1809 | -139 | 0 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 2732.2341 | 780 | 200 | 3712.2341 | 92.81% | 95% | 0% | -159.0389 | 771.8762 | -2750 | -200 | -2178.1238 | 54.45% | 91.11% | 95% | 0% | 1948 | -139
[5 empty] | 2019-01-28 | 11 | 653.5 | 1892 | -134 | 0 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 2732.2341 | 780 | 200 | 3712.2341 | 92.81% | 95% | 0% | -153.3181 | 899.7734 | -2750 | -200 | -2050.2266 | 51.26% | 91.11% | 95% | 0% | 2026 | -134
[5 empty] | 2019-01-28 | 12 | 654 | 2013 | -130 | 0 | 0 | 2143 | 1236.3561 | 1236.3561 | 1236.3561 | 2730.6678 | 780 | 200 | 3710.6678 | 92.77% | 95% | 0% | -148.7414 | 1087.6147 | -2750 | -200 | -1862.3853 | 46.56% | 91.1% | 95% | 0% | 2143 | -130
[5 empty] | 2019-01-28 | 13 | 654.5 | 2300 | -126 | 0 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 2730.6678 | 780 | 200 | 3710.6678 | 92.77% | 95% | 0% | -144.1648 | 1535.4725 | -2750 | -200 | -1414.5275 | 35.36% | 91.1% | 95% | 0% | 2426 | -126
[5 empty] | 2019-01-28 | 14 | 655 | 2568 | -122 | 0 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 2729.1014 | 780 | 200 | 3709.1014 | 92.73% | 95% | 0% | -139.5881 | 1953.5694 | -2750 | -200 | -996.4306 | 24.91% | 91.08% | 95% | 0% | 2690 | -122
[5 empty] | 2019-01-28 | 15 | 655.5 | 2878 | -120 | 0 | 0 | 2998 | 2575.5977 | 2575.5977 | 2575.5977 | 2729.1014 | 780 | 200 | 3709.1014 | 92.73% | 95% | 0% | -137.2998 | 2438.2979 | -2750 | -200 | -511.7021 | 12.79% | 91.08% | 95% | 0% | 2998 | -120
[5 empty] | 2019-01-28 | 16 | 656 | 2996 | -118 | 0 | 0 | 3114 | 2757.296 | 2757.296 | 2757.296 | 2729.1014 | 780 | 200 | 3709.1014 | 92.73% | 95% | 0% | -135.0114 | 2622.2845 | -2750 | -200 | -327.7155 | 8.193% | 91.08% | 95% | 0% | 3114 | -118
[5 empty] | 2019-01-28 | 17 | 656.5 | 3062 | -131 | 0 | 0 | 3193 | 2881.0387 | 2881.0387 | 2881.0387 | 2729.1014 | 780 | 200 | 3709.1014 | 92.73% | 95% | 0% | -149.8856 | 2731.1532 | -2750 | -200 | -218.8468 | 5.471% | 91.07% | 95% | 0% | 3193 | -131
[5 empty] | 2019-01-28 | 18 | 657 | 3021 | -188 | 0 | 0 | 3209 | 2906.1006 | 2906.1006 | 2906.1006 | 2729.1014 | 780 | 200 | 3709.1014 | 92.73% | 95% | 0% | -215.103 | 2690.9976 | -2750 | -200 | -259.0024 | 6.475% | 91.07% | 95% | 0% | 3209 | -188
[5 empty] | 2019-01-28 | 19 | 657.5 | 2991 | -263 | 0 | 0 | 3254 | 2976.587 | 2976.587 | 2976.587 | 2727.535 | 780 | 200 | 3707.535 | 92.69% | 95% | 0% | -300.9153 | 2675.6716 | -2750 | -200 | -274.3284 | 6.858% | 91.05% | 95% | 0% | 3254 | -263
[5 empty] | 2019-01-28 | 20 | 658 | 2898 | -333 | 1 | 0 | 3231 | 2940.5606 | 2940.5606 | 2940.5606 | 2727.535 | 780 | 200 | 3707.535 | 92.69% | 95% | 0% | -381.0069 | 2559.5537 | -3550 | -400 | -1390.4463 | 34.76% | 91.04% | 95% | 0% | 3231 | -333
[5 empty] | 2019-01-28 | 21 | 658.5 | 2764 | -387 | 1 | 0 | 3151 | 2815.2514 | 2815.2514 | 2815.2514 | 2727.535 | 780 | 200 | 3707.535 | 92.69% | 95% | 0% | -442.7918 | 2372.4597 | -3550 | -400 | -1577.5403 | 39.44% | 91.04% | 95% | 0% | 3151 | -387
[5 empty] | 2019-01-28 | 22 | 659 | 2650 | -432 | 1 | 0 | 3082 | 2707.1723 | 2707.1723 | 2707.1723 | 2727.535 | 780 | 200 | 3707.535 | 92.69% | 95% | 0% | -494.2792 | 2212.8931 | -3550 | -400 | -1737.1069 | 43.43% | 91.04% | 95% | 0% | 3082 | -432
[5 empty] | 2019-01-28 | 23 | 659.5 | 2579 | -463 | 1 | 0 | 3042 | 2644.5177 | 2644.5177 | 2644.5177 | 2727.535 | 780 | 200 | 3707.535 | 92.69% | 95% | 0% | -529.7483 | 2114.7694 | -3550 | -400 | -1835.2306 | 45.88% | 91.02% | 95% | 0% | 3042 | -463
[5 empty] | 2019-01-28 | 24 | 660 | 2542 | -477 | 1 | 0 | 3019 | 2608.4913 | 2608.4913 | 2608.4913 | 2725.9687 | 780 | 200 | 3705.9687 | 92.65% | 95% | 0% | -545.7666 | 2062.7248 | -3550 | -400 | -1887.2752 | 47.18% | 91% | 95% | 0% | 3019 | -477
[5 empty] | 2019-01-28 | 25 | 660.5 | 2545 | -475 | 1 | 0 | 3020 | 2610.0577 | 2610.0577 | 2610.0577 | 2725.9687 | 780 | 200 | 3705.9687 | 92.65% | 95% | 0% | -543.4783 | 2066.5794 | -3550 | -400 | -1883.4206 | 47.09% | 90.99% | 95% | 0% | 3020 | -475
[5 empty] | 2019-01-28 | 26 | 661 | 2558 | -458 | 1 | 0 | 3016 | 2603.7923 | 2603.7923 | 2603.7923 | 2724.4023 | 780 | 200 | 3704.4023 | 92.61% | 95% | 0% | -524.0275 | 2079.7648 | -3550 | -400 | -1870.2352 | 46.76% | 90.98% | 95% | 0% | 3016 | -458
[5 empty] | 2019-01-28 | 27 | 661.5 | 2581 | -437 | 1 | 0 | 3018 | 2606.925 | 2606.925 | 2606.925 | 2724.4023 | 780 | 200 | 3704.4023 | 92.61% | 95% | 0% | -500 | 2106.925 | -3550 | -400 | -1843.075 | 46.08% | 90.98% | 95% | 0% | 3018 | -437
[5 empty] | 2019-01-28 | 28 | 662 | 2621 | -412 | 1 | 0 | 3033 | 2630.4204 | 2630.4204 | 2630.4204 | 2724.4023 | 780 | 200 | 3704.4023 | 92.61% | 95% | 0% | -471.3959 | 2159.0246 | -3550 | -400 | -1790.9754 | 44.77% | 90.96% | 95% | 0% | 3033 | -412
[5 empty] | 2019-01-28 | 29 | 662.5 | 2677 | -374 | 1 | 0 | 3051 | 2658.615 | 2658.615 | 2658.615 | 2722.8359 | 780 | 200 | 3702.8359 | 92.57% | 95% | 0% | -427.9176 | 2230.6974 | -3550 | -400 | -1719.3026 | 42.98% | 90.95% | 95% | 0% | 3051 | -374
[5 empty] | 2019-01-28 | 30 | 663 | 2753 | -326 | 1 | 0 | 3079 | 2702.4732 | 2702.4732 | 2702.4732 | 2722.8359 | 780 | 200 | 3702.8359 | 92.57% | 95% | 0% | -372.9977 | 2329.4755 | -3550 | -400 | -1620.5245 | 40.51% | 90.93% | 95% | 0% | 3079 | -326
[5 empty] | 2019-01-28 | 31 | 663.5 | 2865 | -265 | 1 | 0 | 3130 | 2782.3578 | 2782.3578 | 2782.3578 | 2722.8359 | 780 | 200 | 3702.8359 | 92.57% | 95% | 0% | -303.2037 | 2479.1541 | -3550 | -400 | -1470.8459 | 36.77% | 90.93% | 95% | 0% | 3130 | -265
[5 empty] | 2019-01-28 | 32 | 664 | 3025 | -190 | 1 | 0 | 3215 | 2915.4988 | 2915.4988 | 2915.4988 | 2722.8359 | 780 | 200 | 3702.8359 | 92.57% | 95% | 0% | -217.3913 | 2698.1075 | -3550 | -400 | -1251.8925 | 31.3% | 90.92% | 95% | 0% | 3215 | -190
[5 empty] | 2019-01-28 | 33 | 664.5 | 3188 | -127 | 1 | 0 | 3315 | 3072.1352 | 3072.1352 | 3072.1352 | 2721.2696 | 780 | 200 | 3701.2696 | 92.53% | 95% | 0% | -145.3089 | 2926.8263 | -3550 | -400 | -1023.1737 | 25.58% | 90.91% | 95% | 0% | 3315 | -127
[5 empty] | 2019-01-28 | 34 | 665 | 3331 | -99 | 1 | 0 | 3430 | 3252.2671 | 3252.2671 | 3252.2671 | 2721.2696 | 780 | 200 | 3701.2696 | 92.53% | 95% | 0% | -113.2723 | 3138.9948 | -3550 | -400 | -811.0052 | 20.28% | 90.9% | 95% | 0% | 3430 | -99
[5 empty] | 2019-01-28 | 35 | 665.5 | 3453 | -99 | 1 | 0 | 3552 | 3443.3636 | 3443.3636 | 3443.3636 | 2721.2696 | 780 | 200 | 3701.2696 | 92.53% | 95% | 0% | -113.2723 | 3330.0913 | -3550 | -400 | -619.9087 | 15.5% | 90.9% | 95% | 0% | 3552 | -99
[5 empty] | 2019-01-28 | 36 | 666 | 3473 | -101 | 1 | 0 | 3574 | 3477.8236 | 3477.8236 | 3477.8236 | 2721.2696 | 780 | 200 | 3701.2696 | 92.53% | 95% | 0% | -115.5606 | 3362.2629 | -3550 | -400 | -587.7371 | 14.69% | 90.9% | 95% | 0% | 3574 | -101
[5 empty] | 2019-01-28 | 37 | 666.5 | 3468 | -102 | 0 | 0 | 3570 | 3471.5581 | 3471.5581 | 3471.5581 | 2721.2696 | 780 | 200 | 3701.2696 | 92.53% | 95% | 0% | -116.7048 | 3354.8533 | -2750 | -200 | 404.8533 | -10.12% | 90.89% | 95% | 0% | 3570 | -102
[5 empty] | 2019-01-28 | 38 | 667 | 3439 | -104 | 0 | 0 | 3543 | 3429.2663 | 3429.2663 | 3429.2663 | 2719.7032 | 780 | 200 | 3699.7032 | 92.49% | 95% | 0% | -118.9931 | 3310.2731 | -2750 | -200 | 360.2731 | -9.007% | 90.89% | 95% | 0% | 3543 | -104
[5 empty] | 2019-01-28 | 39 | 667.5 | 3372 | -104 | 0 | 0 | 3476 | 3324.3199 | 3324.3199 | 3324.3199 | 2719.7032 | 780 | 200 | 3699.7032 | 92.49% | 95% | 0% | -118.9931 | 3205.3267 | -2750 | -200 | 255.3267 | -6.383% | 90.88% | 95% | 0% | 3476 | -104
[5 empty] | 2019-01-28 | 40 | 668 | 3300 | -104 | 0 | 0 | 3404 | 3211.5416 | 3211.5416 | 3211.5416 | 2719.7032 | 780 | 200 | 3699.7032 | 92.49% | 95% | 0% | -118.9931 | 3092.5485 | -2750 | -200 | 142.5485 | -3.564% | 90.88% | 95% | 0% | 3404 | -104
[5 empty] | 2019-01-28 | 41 | 668.5 | 3264 | -104 | 0 | 0 | 3368 | 3155.1525 | 3155.1525 | 3155.1525 | 2719.7032 | 780 | 200 | 3699.7032 | 92.49% | 95% | 0% | -118.9931 | 3036.1594 | -2750 | -200 | 86.1594 | -2.154% | 90.87% | 95% | 0% | 3368 | -104
[5 empty] | 2019-01-28 | 42 | 669 | 3142 | -104 | 0 | 0 | 3246 | 2964.0561 | 2964.0561 | 2964.0561 | 2718.1369 | 780 | 200 | 3698.1369 | 92.45% | 95% | 0% | -118.9931 | 2845.0629 | -2750 | -200 | -104.9371 | 2.623% | 90.86% | 95% | 0% | 3246 | -104
[5 empty] | 2019-01-28 | 43 | 669.5 | 2972 | -104 | 0 | 0 | 3076 | 2697.7741 | 2697.7741 | 2697.7741 | 2718.1369 | 780 | 200 | 3698.1369 | 92.45% | 95% | 0% | -118.9931 | 2578.781 | -2750 | -200 | -371.219 | 9.28% | 90.86% | 95% | 0% | 3076 | -104
[5 empty] | 2019-01-28 | 44 | 670 | 2785 | -103 | 0 | 0 | 2888 | 2403.2976 | 2403.2976 | 2403.2976 | 2718.1369 | 780 | 200 | 3698.1369 | 92.45% | 95% | 0% | -117.849 | 2285.4486 | -2750 | -200 | -664.5514 | 16.61% | 90.86% | 95% | 0% | 2888 | -103
[5 empty] | 2019-01-28 | 45 | 670.5 | 2602 | -103 | 0 | 0 | 2705 | 2116.6529 | 2116.6529 | 2116.6529 | 2718.1369 | 780 | 200 | 3698.1369 | 92.45% | 95% | 0% | -117.849 | 1998.804 | -2750 | -200 | -951.196 | 23.78% | 90.86% | 95% | 0% | 2705 | -103
[5 empty] | 2019-01-28 | 46 | 671 | 2430 | -103 | 0 | 0 | 2533 | 1847.2383 | 1847.2383 | 1847.2383 | 2716.5705 | 780 | 200 | 3696.5705 | 92.41% | 95% | 0% | -117.849 | 1729.3893 | -2750 | -200 | -1220.6107 | 30.52% | 90.85% | 95% | 0% | 2533 | -103
[5 empty] | 2019-01-28 | 47 | 671.5 | 2261 | -101 | 0 | 0 | 2362 | 1579.3899 | 1579.3899 | 1579.3899 | 2716.5705 | 780 | 200 | 3696.5705 | 92.41% | 95% | 0% | -115.5606 | 1463.8293 | -2750 | -200 | -1486.1707 | 37.15% | 90.85% | 95% | 0% | 2362 | -101
[5 empty] | 2019-01-28 | 48 | 672 | 2176 | -99 | 0 | 0 | 2275 | 1443.1162 | 1443.1162 | 1443.1162 | 2716.5705 | 780 | 200 | 3696.5705 | 92.41% | 95% | 0% | -113.2723 | 1329.8439 | -2750 | -200 | -1620.1561 | 40.5% | 90.84% | 95% | 0% | 2275 | -99
[5 empty] | 2019-01-29 | 1 | 672.5 | 2146 | -101 | 0 | 0 | 2247 | 1399.258 | 1399.258 | 1399.258 | 2716.5705 | 780 | 200 | 3696.5705 | 92.41% | 95% | 0% | -115.5606 | 1283.6974 | -2750 | -200 | -1666.3026 | 41.66% | 90.83% | 95% | 0% | 2247 | -101
[5 empty] | 2019-01-29 | 2 | 673 | 2184 | -103 | 0 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 2715.0041 | 780 | 200 | 3695.0041 | 92.38% | 95% | 0% | -117.849 | 1344.0636 | -2750 | -200 | -1605.9364 | 40.15% | 90.82% | 95% | 0% | 2287 | -103
[5 empty] | 2019-01-29 | 3 | 673.5 | 2175 | -102 | 0 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 2715.0041 | 780 | 200 | 3695.0041 | 92.38% | 95% | 0% | -116.7048 | 1329.5442 | -2750 | -200 | -1620.4558 | 40.51% | 90.82% | 95% | 0% | 2277 | -102
[5 empty] | 2019-01-29 | 4 | 674 | 2130 | -102 | 0 | 0 | 2232 | 1375.7626 | 1375.7626 | 1375.7626 | 2715.0041 | 780 | 200 | 3695.0041 | 92.38% | 95% | 0% | -116.7048 | 1259.0578 | -2750 | -200 | -1690.9422 | 42.27% | 90.81% | 95% | 0% | 2232 | -102
[5 empty] | 2019-01-29 | 5 | 674.5 | 2106 | -101 | 0 | 0 | 2207 | 1336.6035 | 1336.6035 | 1336.6035 | 2715.0041 | 780 | 200 | 3695.0041 | 92.38% | 95% | 0% | -115.5606 | 1221.0428 | -2750 | -200 | -1728.9572 | 43.22% | 90.81% | 95% | 0% | 2207 | -101
[5 empty] | 2019-01-29 | 6 | 675 | 2112 | -100 | 0 | 0 | 2212 | 1344.4353 | 1344.4353 | 1344.4353 | 2715.0041 | 780 | 200 | 3695.0041 | 92.38% | 95% | 0% | -114.4165 | 1230.0188 | -2750 | -200 | -1719.9812 | 43% | 90.81% | 95% | 0% | 2212 | -100
[5 empty] | 2019-01-29 | 7 | 675.5 | 2082 | -96 | 0 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 2715.0041 | 780 | 200 | 3695.0041 | 92.38% | 95% | 0% | -109.8398 | 1181.3391 | -2750 | -200 | -1768.6609 | 44.22% | 90.8% | 95% | 0% | 2178 | -96
[5 empty] | 2019-01-29 | 8 | 676 | 2057 | -92 | 0 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 2715.0041 | 780 | 200 | 3695.0041 | 92.38% | 95% | 0% | -105.2632 | 1140.4912 | -2750 | -200 | -1809.5088 | 45.24% | 90.79% | 95% | 0% | 2149 | -92
[5 empty] | 2019-01-29 | 9 | 676.5 | 2046 | -90 | 0 | 0 | 2136 | 1225.3916 | 1225.3916 | 1225.3916 | 2715.0041 | 780 | 200 | 3695.0041 | 92.38% | 95% | 0% | -102.9748 | 1122.4168 | -2750 | -200 | -1827.5832 | 45.69% | 90.78% | 95% | 0% | 2136 | -90
[5 empty] | 2019-01-29 | 10 | 677 | 2065 | -89 | 0 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 2713.4378 | 780 | 200 | 3693.4378 | 92.34% | 95% | 0% | -101.8307 | 1151.7555 | -2750 | -200 | -1798.2445 | 44.96% | 90.78% | 95% | 0% | 2154 | -89
[5 empty] | 2019-01-29 | 11 | 677.5 | 2127 | -87 | 0 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 2713.4378 | 780 | 200 | 3693.4378 | 92.34% | 95% | 0% | -99.5423 | 1248.0257 | -2750 | -200 | -1701.9743 | 42.55% | 90.77% | 95% | 0% | 2214 | -87
[5 empty] | 2019-01-29 | 12 | 678 | 2235 | -86 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 2713.4378 | 780 | 200 | 3693.4378 | 92.34% | 95% | 0% | -98.3982 | 1416.7708 | -3550 | -400 | -2533.2292 | 63.33% | 90.77% | 95% | 0% | 2321 | -86
[5 empty] | 2019-01-29 | 13 | 678.5 | 2498 | -84 | 1 | 0 | 2582 | 1923.9901 | 1923.9901 | 1923.9901 | 2713.4378 | 780 | 200 | 3693.4378 | 92.34% | 95% | 0% | -96.1098 | 1827.8803 | -3550 | -400 | -2122.1197 | 53.05% | 90.77% | 95% | 0% | 2582 | -84
[5 empty] | 2019-01-29 | 14 | 679 | 2764 | -82 | 1 | 0 | 2846 | 2337.5103 | 2337.5103 | 2337.5103 | 2713.4378 | 780 | 200 | 3693.4378 | 92.34% | 95% | 0% | -93.8215 | 2243.6888 | -3550 | -400 | -1706.3112 | 42.66% | 90.77% | 95% | 0% | 2846 | -82
[5 empty] | 2019-01-29 | 15 | 679.5 | 3077 | -81 | 1 | 0 | 3158 | 2826.216 | 2826.216 | 2826.216 | 2713.4378 | 780 | 200 | 3693.4378 | 92.34% | 95% | 0% | -92.6773 | 2733.5386 | -3550 | -400 | -1216.4614 | 30.41% | 90.76% | 95% | 0% | 3158 | -81
[5 empty] | 2019-01-29 | 16 | 680 | 3225 | -81 | 1 | 0 | 3306 | 3058.0379 | 3058.0379 | 3058.0379 | 2711.8714 | 780 | 200 | 3691.8714 | 92.3% | 95% | 0% | -92.6773 | 2965.3606 | -3550 | -400 | -984.6394 | 24.62% | 90.75% | 95% | 0% | 3306 | -81
[5 empty] | 2019-01-29 | 17 | 680.5 | 3289 | -85 | 1 | 0 | 3374 | 3164.5507 | 3164.5507 | 3164.5507 | 2711.8714 | 780 | 200 | 3691.8714 | 92.3% | 95% | 0% | -97.254 | 3067.2967 | -3550 | -400 | -882.7033 | 22.07% | 90.75% | 95% | 0% | 3374 | -85
[5 empty] | 2019-01-29 | 18 | 681 | 3277 | -103 | 1 | 0 | 3380 | 3173.9489 | 3173.9489 | 3173.9489 | 2711.8714 | 780 | 200 | 3691.8714 | 92.3% | 95% | 0% | -117.849 | 3056.0999 | -3550 | -400 | -893.9001 | 22.35% | 90.75% | 95% | 0% | 3380 | -103
[5 empty] | 2019-01-29 | 19 | 681.5 | 3294 | -116 | 1 | 0 | 3410 | 3220.9398 | 3220.9398 | 3220.9398 | 2711.8714 | 780 | 200 | 3691.8714 | 92.3% | 95% | 0% | -132.7231 | 3088.2167 | -3550 | -400 | -861.7833 | 21.54% | 90.75% | 95% | 0% | 3410 | -116
[5 empty] | 2019-01-29 | 20 | 682 | 3265 | -145 | 1 | 0 | 3410 | 3220.9398 | 3220.9398 | 3220.9398 | 2711.8714 | 780 | 200 | 3691.8714 | 92.3% | 95% | 0% | -165.9039 | 3055.0359 | -3550 | -400 | -894.9641 | 22.37% | 90.75% | 95% | 0% | 3410 | -145
[5 empty] | 2019-01-29 | 21 | 682.5 | 3203 | -164 | 1 | 0 | 3367 | 3153.5862 | 3153.5862 | 3153.5862 | 2711.8714 | 780 | 200 | 3691.8714 | 92.3% | 95% | 0% | -187.643 | 2965.9431 | -3550 | -400 | -984.0569 | 24.6% | 90.74% | 95% | 0% | 3367 | -164
[5 empty] | 2019-01-29 | 22 | 683 | 3191 | -185 | 1 | 0 | 3376 | 3167.6834 | 3167.6834 | 3167.6834 | 2711.8714 | 780 | 200 | 3691.8714 | 92.3% | 95% | 0% | -211.6705 | 2956.0129 | -3550 | -400 | -993.9871 | 24.85% | 90.73% | 95% | 0% | 3376 | -185
[5 empty] | 2019-01-29 | 23 | 683.5 | 3206 | -201 | 1 | 0 | 3407 | 3216.2407 | 3216.2407 | 3216.2407 | 2710.305 | 780 | 200 | 3690.305 | 92.26% | 95% | 0% | -229.9771 | 2986.2636 | -3550 | -400 | -963.7364 | 24.09% | 90.72% | 95% | 0% | 3407 | -201
[5 empty] | 2019-01-29 | 24 | 684 | 3216 | -200 | 1 | 0 | 3416 | 3230.338 | 3230.338 | 3230.338 | 2710.305 | 780 | 200 | 3690.305 | 92.26% | 95% | 0% | -228.833 | 3001.5051 | -3550 | -400 | -948.4949 | 23.71% | 90.71% | 95% | 0% | 3416 | -200
[5 empty] | 2019-01-29 | 25 | 684.5 | 3255 | -192 | 1 | 0 | 3447 | 3278.8953 | 3278.8953 | 3278.8953 | 2710.305 | 780 | 200 | 3690.305 | 92.26% | 95% | 0% | -219.6796 | 3059.2157 | -3550 | -400 | -890.7843 | 22.27% | 90.7% | 95% | 0% | 3447 | -192
[5 empty] | 2019-01-29 | 26 | 685 | 3253 | -187 | 1 | 0 | 3440 | 3267.9308 | 3267.9308 | 3267.9308 | 2710.305 | 780 | 200 | 3690.305 | 92.26% | 95% | 0% | -213.9588 | 3053.9719 | -3550 | -400 | -896.0281 | 22.4% | 90.7% | 95% | 0% | 3440 | -187
[5 empty] | 2019-01-29 | 27 | 685.5 | 3240 | -184 | 1 | 0 | 3424 | 3242.8689 | 3242.8689 | 3242.8689 | 2710.305 | 780 | 200 | 3690.305 | 92.26% | 95% | 0% | -210.5263 | 3032.3426 | -3550 | -400 | -917.6574 | 22.94% | 90.69% | 95% | 0% | 3424 | -184
[5 empty] | 2019-01-29 | 28 | 686 | 3219 | -171 | 1 | 0 | 3390 | 3189.6125 | 3189.6125 | 3189.6125 | 2710.305 | 780 | 200 | 3690.305 | 92.26% | 95% | 0% | -195.6522 | 2993.9604 | -3550 | -400 | -956.0396 | 23.9% | 90.69% | 95% | 0% | 3390 | -171
[5 empty] | 2019-01-29 | 29 | 686.5 | 3242 | -155 | 1 | 0 | 3397 | 3200.5771 | 3200.5771 | 3200.5771 | 2708.7387 | 780 | 200 | 3688.7387 | 92.22% | 95% | 0% | -177.3455 | 3023.2315 | -3550 | -400 | -926.7685 | 23.17% | 90.69% | 95% | 0% | 3397 | -155
[5 empty] | 2019-01-29 | 30 | 687 | 3250 | -144 | 1 | 0 | 3394 | 3195.878 | 3195.878 | 3195.878 | 2708.7387 | 780 | 200 | 3688.7387 | 92.22% | 95% | 0% | -164.7597 | 3031.1183 | -3550 | -400 | -918.8817 | 22.97% | 90.68% | 95% | 0% | 3394 | -144
[5 empty] | 2019-01-29 | 31 | 687.5 | 3285 | -132 | 1 | 0 | 3417 | 3231.9044 | 3231.9044 | 3231.9044 | 2708.7387 | 780 | 200 | 3688.7387 | 92.22% | 95% | 0% | -151.0297 | 3080.8746 | -3550 | -400 | -869.1254 | 21.73% | 90.68% | 95% | 0% | 3417 | -132
[5 empty] | 2019-01-29 | 32 | 688 | 3355 | -118 | 1 | 0 | 3473 | 3319.6208 | 3319.6208 | 3319.6208 | 2708.7387 | 780 | 200 | 3688.7387 | 92.22% | 95% | 0% | -135.0114 | 3184.6093 | -3550 | -400 | -765.3907 | 19.13% | 90.68% | 95% | 0% | 3473 | -118
[5 empty] | 2019-01-29 | 33 | 688.5 | 3419 | -108 | 1 | 0 | 3527 | 3404.2045 | 3404.2045 | 3404.2045 | 2708.7387 | 780 | 200 | 3688.7387 | 92.22% | 95% | 0% | -123.5698 | 3280.6347 | -3550 | -400 | -669.3653 | 16.73% | 90.68% | 95% | 0% | 3527 | -108
[5 empty] | 2019-01-29 | 34 | 689 | 3481 | -104 | 1 | 0 | 3585 | 3495.0536 | 3495.0536 | 3495.0536 | 2708.7387 | 780 | 200 | 3688.7387 | 92.22% | 95% | 0% | -118.9931 | 3376.0605 | -3550 | -400 | -573.9395 | 14.35% | 90.67% | 95% | 0% | 3585 | -104
[5 empty] | 2019-01-29 | 35 | 689.5 | 3476 | -103 | 0 | 0 | 3579 | 3485.6554 | 3485.6554 | 3485.6554 | 2707.1723 | 780 | 200 | 3687.1723 | 92.18% | 95% | 0% | -117.849 | 3367.8064 | -2750 | -200 | 417.8064 | -10.45% | 90.67% | 95% | 0% | 3579 | -103
[5 empty] | 2019-01-29 | 36 | 690 | 3489 | -103 | 0 | 0 | 3592 | 3506.0181 | 3506.0181 | 3506.0181 | 2707.1723 | 780 | 200 | 3687.1723 | 92.18% | 95% | 0% | -117.849 | 3388.1692 | -2750 | -200 | 438.1692 | -10.95% | 90.67% | 95% | 0% | 3592 | -103
[5 empty] | 2019-01-29 | 37 | 690.5 | 3483 | -102 | 0 | 0 | 3585 | 3495.0536 | 3495.0536 | 3495.0536 | 2707.1723 | 780 | 200 | 3687.1723 | 92.18% | 95% | 0% | -116.7048 | 3378.3488 | -2750 | -200 | 428.3488 | -10.71% | 90.66% | 95% | 0% | 3585 | -102
[5 empty] | 2019-01-29 | 38 | 691 | 3463 | -102 | 0 | 0 | 3565 | 3463.7263 | 3463.7263 | 3463.7263 | 2707.1723 | 780 | 200 | 3687.1723 | 92.18% | 95% | 0% | -116.7048 | 3347.0215 | -2750 | -200 | 397.0215 | -9.926% | 90.65% | 95% | 0% | 3565 | -102
[5 empty] | 2019-01-29 | 39 | 691.5 | 3475 | -100 | 0 | 0 | 3575 | 3479.3899 | 3479.3899 | 3479.3899 | 2705.6059 | 780 | 200 | 3685.6059 | 92.14% | 95% | 0% | -114.4165 | 3364.9735 | -2750 | -200 | 414.9735 | -10.37% | 90.65% | 95% | 0% | 3575 | -100
[5 empty] | 2019-01-29 | 40 | 692 | 3439 | -97 | 0 | 0 | 3536 | 3418.3017 | 3418.3017 | 3418.3017 | 2705.6059 | 780 | 200 | 3685.6059 | 92.14% | 95% | 0% | -110.984 | 3307.3177 | -2750 | -200 | 357.3177 | -8.933% | 90.63% | 95% | 0% | 3536 | -97
[5 empty] | 2019-01-29 | 41 | 692.5 | 3344 | -95 | 0 | 0 | 3439 | 3266.3644 | 3266.3644 | 3266.3644 | 2705.6059 | 780 | 200 | 3685.6059 | 92.14% | 95% | 0% | -108.6957 | 3157.6687 | -2750 | -200 | 207.6687 | -5.192% | 90.62% | 95% | 0% | 3439 | -95
[5 empty] | 2019-01-29 | 42 | 693 | 3198 | -92 | 0 | 0 | 3290 | 3032.9761 | 3032.9761 | 3032.9761 | 2705.6059 | 780 | 200 | 3685.6059 | 92.14% | 95% | 0% | -105.2632 | 2927.7129 | -2750 | -200 | -22.2871 | 0.5572% | 90.61% | 95% | 0% | 3290 | -92
[5 empty] | 2019-01-29 | 43 | 693.5 | 3057 | -90 | 0 | 0 | 3147 | 2808.986 | 2808.986 | 2808.986 | 2705.6059 | 780 | 200 | 3685.6059 | 92.14% | 95% | 0% | -102.9748 | 2706.0112 | -2750 | -200 | -243.9888 | 6.1% | 90.6% | 95% | 0% | 3147 | -90
[5 empty] | 2019-01-29 | 44 | 694 | 2886 | -88 | 0 | 0 | 2974 | 2538.0049 | 2538.0049 | 2538.0049 | 2704.0396 | 780 | 200 | 3684.0396 | 92.1% | 95% | 0% | -100.6865 | 2437.3184 | -2750 | -200 | -512.6816 | 12.82% | 90.6% | 95% | 0% | 2974 | -88
[5 empty] | 2019-01-29 | 45 | 694.5 | 2692 | -86 | 0 | 0 | 2778 | 2230.9975 | 2230.9975 | 2230.9975 | 2704.0396 | 780 | 200 | 3684.0396 | 92.1% | 95% | 0% | -98.3982 | 2132.5994 | -2750 | -200 | -817.4006 | 20.44% | 90.59% | 95% | 0% | 2778 | -86
[5 empty] | 2019-01-29 | 46 | 695 | 2517 | -84 | 0 | 0 | 2601 | 1953.751 | 1953.751 | 1953.751 | 2702.4732 | 780 | 200 | 3682.4732 | 92.06% | 95% | 0% | -96.1098 | 1857.6412 | -2750 | -200 | -1092.3588 | 27.31% | 90.59% | 95% | 0% | 2601 | -84
[5 empty] | 2019-01-29 | 47 | 695.5 | 2356 | -81 | 0 | 0 | 2437 | 1696.8673 | 1696.8673 | 1696.8673 | 2702.4732 | 780 | 200 | 3682.4732 | 92.06% | 95% | 0% | -92.6773 | 1604.1899 | -2750 | -200 | -1345.8101 | 33.65% | 90.58% | 95% | 0% | 2437 | -81
[5 empty] | 2019-01-29 | 48 | 696 | 2252 | -78 | 0 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 2702.4732 | 780 | 200 | 3682.4732 | 92.06% | 95% | 0% | -89.2449 | 1440.0214 | -2750 | -200 | -1509.9786 | 37.75% | 90.55% | 95% | 0% | 2330 | -78
[5 empty] | 2019-01-30 | 1 | 696.5 | 2233 | -79 | 0 | 0 | 2312 | 1501.0717 | 1501.0717 | 1501.0717 | 2702.4732 | 780 | 200 | 3682.4732 | 92.06% | 95% | 0% | -90.389 | 1410.6827 | -2750 | -200 | -1539.3173 | 38.48% | 90.55% | 95% | 0% | 2312 | -79
[5 empty] | 2019-01-30 | 2 | 697 | 2258 | -80 | 0 | 0 | 2338 | 1541.7972 | 1541.7972 | 1541.7972 | 2700.9068 | 780 | 200 | 3680.9068 | 92.02% | 95% | 0% | -91.5332 | 1450.264 | -2750 | -200 | -1499.736 | 37.49% | 90.54% | 95% | 0% | 2338 | -80
[5 empty] | 2019-01-30 | 3 | 697.5 | 2247 | -81 | 0 | 0 | 2328 | 1526.1336 | 1526.1336 | 1526.1336 | 2700.9068 | 780 | 200 | 3680.9068 | 92.02% | 95% | 0% | -92.6773 | 1433.4562 | -2750 | -200 | -1516.5438 | 37.91% | 90.54% | 95% | 0% | 2328 | -81
[5 empty] | 2019-01-30 | 4 | 698 | 2205 | -82 | 0 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 2700.9068 | 780 | 200 | 3680.9068 | 92.02% | 95% | 0% | -93.8215 | 1368.0911 | -2750 | -200 | -1581.9089 | 39.55% | 90.53% | 95% | 0% | 2287 | -82
[5 empty] | 2019-01-30 | 5 | 698.5 | 2170 | -83 | 0 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 2700.9068 | 780 | 200 | 3680.9068 | 92.02% | 95% | 0% | -94.9657 | 1313.6905 | -2750 | -200 | -1636.3095 | 40.91% | 90.51% | 95% | 0% | 2253 | -83
[5 empty] | 2019-01-30 | 6 | 699 | 2167 | -83 | 0 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 2700.9068 | 780 | 200 | 3680.9068 | 92.02% | 95% | 0% | -94.9657 | 1308.9915 | -2750 | -200 | -1641.0085 | 41.03% | 90.51% | 95% | 0% | 2250 | -83
[5 empty] | 2019-01-30 | 7 | 699.5 | 2141 | -82 | 0 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 2699.3405 | 780 | 200 | 3679.3405 | 91.98% | 95% | 0% | -93.8215 | 1267.8438 | -2750 | -200 | -1682.1562 | 42.05% | 90.51% | 95% | 0% | 2223 | -82
[5 empty] | 2019-01-30 | 8 | 700 | 2117 | -82 | 0 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 2699.3405 | 780 | 200 | 3679.3405 | 91.98% | 95% | 0% | -93.8215 | 1230.251 | -2750 | -200 | -1719.749 | 42.99% | 90.5% | 95% | 0% | 2199 | -82
[5 empty] | 2019-01-30 | 9 | 700.5 | 2109 | -80 | 0 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 2697.7741 | 780 | 200 | 3677.7741 | 91.94% | 95% | 0% | -91.5332 | 1216.8757 | -2750 | -200 | -1733.1243 | 43.33% | 90.5% | 95% | 0% | 2189 | -80
[5 empty] | 2019-01-30 | 10 | 701 | 2123 | -79 | 0 | 0 | 2202 | 1328.7716 | 1328.7716 | 1328.7716 | 2697.7741 | 780 | 200 | 3677.7741 | 91.94% | 95% | 0% | -90.389 | 1238.3826 | -2750 | -200 | -1711.6174 | 42.79% | 90.5% | 95% | 0% | 2202 | -79
[5 empty] | 2019-01-30 | 11 | 701.5 | 2195 | -77 | 0 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 2697.7741 | 780 | 200 | 3677.7741 | 91.94% | 95% | 0% | -88.1007 | 1350.3165 | -2750 | -200 | -1599.6835 | 39.99% | 90.5% | 95% | 0% | 2272 | -77
[5 empty] | 2019-01-30 | 12 | 702 | 2313 | -75 | 0 | 0 | 2388 | 1620.1154 | 1620.1154 | 1620.1154 | 2697.7741 | 780 | 200 | 3677.7741 | 91.94% | 95% | 0% | -85.8124 | 1534.3031 | -2750 | -200 | -1415.6969 | 35.39% | 90.48% | 95% | 0% | 2388 | -75
[5 empty] | 2019-01-30 | 13 | 702.5 | 2583 | -71 | 0 | 0 | 2654 | 2036.7683 | 2036.7683 | 2036.7683 | 2697.7741 | 780 | 200 | 3677.7741 | 91.94% | 95% | 0% | -81.2357 | 1955.5326 | -2750 | -200 | -994.4674 | 24.86% | 90.48% | 95% | 0% | 2654 | -71
[5 empty] | 2019-01-30 | 14 | 703 | 2864 | -68 | 0 | 0 | 2932 | 2472.2176 | 2472.2176 | 2472.2176 | 2697.7741 | 780 | 200 | 3677.7741 | 91.94% | 95% | 0% | -77.8032 | 2394.4144 | -2750 | -200 | -555.5856 | 13.89% | 90.46% | 95% | 0% | 2932 | -68
[5 empty] | 2019-01-30 | 15 | 703.5 | 3182 | -66 | 0 | 0 | 3248 | 2967.1888 | 2967.1888 | 2967.1888 | 2697.7741 | 780 | 200 | 3677.7741 | 91.94% | 95% | 0% | -75.5149 | 2891.6739 | -2750 | -200 | -58.3261 | 1.458% | 90.45% | 95% | 0% | 3248 | -66
[5 empty] | 2019-01-30 | 16 | 704 | 3308 | -63 | 0 | 0 | 3371 | 3159.8516 | 3159.8516 | 3159.8516 | 2697.7741 | 780 | 200 | 3677.7741 | 91.94% | 95% | 0% | -72.0824 | 3087.7692 | -2750 | -200 | 137.7692 | -3.444% | 90.45% | 95% | 0% | 3371 | -63
[5 empty] | 2019-01-30 | 17 | 704.5 | 3361 | -70 | 0 | 0 | 3431 | 3253.8335 | 3253.8335 | 3253.8335 | 2697.7741 | 780 | 200 | 3677.7741 | 91.94% | 95% | 0% | -80.0915 | 3173.7419 | -2750 | -200 | 223.7419 | -5.594% | 90.43% | 95% | 0% | 3431 | -70
[5 empty] | 2019-01-30 | 18 | 705 | 3343 | -105 | 0 | 0 | 3448 | 3280.4617 | 3280.4617 | 3280.4617 | 2697.7741 | 780 | 200 | 3677.7741 | 91.94% | 95% | 0% | -120.1373 | 3160.3244 | -2750 | -200 | 210.3244 | -5.258% | 90.42% | 95% | 0% | 3448 | -105
[5 empty] | 2019-01-30 | 19 | 705.5 | 3364 | -104 | 0 | 0 | 3468 | 3311.789 | 3311.789 | 3311.789 | 2696.2077 | 780 | 200 | 3676.2077 | 91.91% | 95% | 0% | -118.9931 | 3192.7958 | -2750 | -200 | 242.7958 | -6.07% | 90.41% | 95% | 0% | 3468 | -104
[5 empty] | 2019-01-30 | 20 | 706 | 3239 | -211 | 1 | 0 | 3450 | 3283.5944 | 3283.5944 | 3283.5944 | 2696.2077 | 780 | 200 | 3676.2077 | 91.91% | 95% | 0% | -241.4188 | 3042.1756 | -3550 | -400 | -907.8244 | 22.7% | 90.4% | 95% | 0% | 3450 | -211
[5 empty] | 2019-01-30 | 21 | 706.5 | 3152 | -264 | 1 | 0 | 3416 | 3230.338 | 3230.338 | 3230.338 | 2696.2077 | 780 | 200 | 3676.2077 | 91.91% | 95% | 0% | -302.0595 | 2928.2785 | -3550 | -400 | -1021.7215 | 25.54% | 90.39% | 95% | 0% | 3416 | -264
[5 empty] | 2019-01-30 | 22 | 707 | 3037 | -317 | 1 | 0 | 3354 | 3133.2234 | 3133.2234 | 3133.2234 | 2696.2077 | 780 | 200 | 3676.2077 | 91.91% | 95% | 0% | -362.7002 | 2770.5232 | -3550 | -400 | -1179.4768 | 29.49% | 90.39% | 95% | 0% | 3354 | -317
[5 empty] | 2019-01-30 | 23 | 707.5 | 2933 | -365 | 1 | 0 | 3298 | 3045.507 | 3045.507 | 3045.507 | 2694.6414 | 780 | 200 | 3674.6414 | 91.87% | 95% | 0% | -417.6201 | 2627.8869 | -3550 | -400 | -1322.1131 | 33.05% | 90.39% | 95% | 0% | 3298 | -365
[5 empty] | 2019-01-30 | 24 | 708 | 2845 | -403 | 1 | 0 | 3248 | 2967.1888 | 2967.1888 | 2967.1888 | 2694.6414 | 780 | 200 | 3674.6414 | 91.87% | 95% | 0% | -461.0984 | 2506.0904 | -3550 | -400 | -1443.9096 | 36.1% | 90.39% | 95% | 0% | 3248 | -403
[5 empty] | 2019-01-30 | 25 | 708.5 | 2815 | -406 | 1 | 0 | 3221 | 2924.8969 | 2924.8969 | 2924.8969 | 2694.6414 | 780 | 200 | 3674.6414 | 91.87% | 95% | 0% | -464.5309 | 2460.3661 | -3550 | -400 | -1489.6339 | 37.24% | 90.38% | 95% | 0% | 3221 | -406
[5 empty] | 2019-01-30 | 26 | 709 | 2817 | -386 | 1 | 0 | 3203 | 2896.7024 | 2896.7024 | 2896.7024 | 2694.6414 | 780 | 200 | 3674.6414 | 91.87% | 95% | 0% | -441.6476 | 2455.0548 | -3550 | -400 | -1494.9452 | 37.37% | 90.36% | 95% | 0% | 3203 | -386
[5 empty] | 2019-01-30 | 27 | 709.5 | 2831 | -373 | 1 | 0 | 3204 | 2898.2688 | 2898.2688 | 2898.2688 | 2693.075 | 780 | 200 | 3673.075 | 91.83% | 95% | 0% | -426.7735 | 2471.4953 | -3550 | -400 | -1478.5047 | 36.96% | 90.35% | 95% | 0% | 3204 | -373
[5 empty] | 2019-01-30 | 28 | 710 | 2864 | -337 | 1 | 0 | 3201 | 2893.5697 | 2893.5697 | 2893.5697 | 2691.5087 | 780 | 200 | 3671.5087 | 91.79% | 95% | 0% | -385.5835 | 2507.9861 | -3550 | -400 | -1442.0139 | 36.05% | 90.35% | 95% | 0% | 3201 | -337
[5 empty] | 2019-01-30 | 29 | 710.5 | 2917 | -301 | 1 | 0 | 3218 | 2920.1979 | 2920.1979 | 2920.1979 | 2691.5087 | 780 | 200 | 3671.5087 | 91.79% | 95% | 0% | -344.3936 | 2575.8043 | -3550 | -400 | -1374.1957 | 34.35% | 90.35% | 95% | 0% | 3218 | -301
[5 empty] | 2019-01-30 | 30 | 711 | 2995 | -254 | 1 | 0 | 3249 | 2968.7552 | 2968.7552 | 2968.7552 | 2691.5087 | 780 | 200 | 3671.5087 | 91.79% | 95% | 0% | -290.6178 | 2678.1373 | -3550 | -400 | -1271.8627 | 31.8% | 90.35% | 95% | 0% | 3249 | -254
[5 empty] | 2019-01-30 | 31 | 711.5 | 3119 | -199 | 1 | 0 | 3318 | 3076.8343 | 3076.8343 | 3076.8343 | 2691.5087 | 780 | 200 | 3671.5087 | 91.79% | 95% | 0% | -227.6888 | 2849.1455 | -3550 | -400 | -1100.8545 | 27.52% | 90.34% | 95% | 0% | 3318 | -199
[5 empty] | 2019-01-30 | 32 | 712 | 3275 | -133 | 1 | 0 | 3408 | 3217.8071 | 3217.8071 | 3217.8071 | 2691.5087 | 780 | 200 | 3671.5087 | 91.79% | 95% | 0% | -152.1739 | 3065.6332 | -3550 | -400 | -884.3668 | 22.11% | 90.34% | 95% | 0% | 3408 | -133
[5 empty] | 2019-01-30 | 33 | 712.5 | 3408 | -78 | 1 | 0 | 3486 | 3339.9835 | 3339.9835 | 3339.9835 | 2691.5087 | 780 | 200 | 3671.5087 | 91.79% | 95% | 0% | -89.2449 | 3250.7387 | -3550 | -400 | -699.2613 | 17.48% | 90.32% | 95% | 0% | 3486 | -78
[5 empty] | 2019-01-30 | 34 | 713 | 3491 | -47 | 1 | 0 | 3538 | 3421.4345 | 3421.4345 | 3421.4345 | 2691.5087 | 780 | 200 | 3671.5087 | 91.79% | 95% | 0% | -53.7757 | 3367.6587 | -3550 | -400 | -582.3413 | 14.56% | 90.32% | 95% | 0% | 3538 | -47
[5 empty] | 2019-01-30 | 35 | 713.5 | 3548 | -43 | 0 | 0 | 3591 | 3504.4518 | 3504.4518 | 3504.4518 | 2691.5087 | 780 | 200 | 3671.5087 | 91.79% | 95% | 0% | -49.1991 | 3455.2527 | -2750 | -200 | 505.2527 | -12.63% | 90.32% | 95% | 0% | 3591 | -43
[5 empty] | 2019-01-30 | 36 | 714 | 3580 | -43 | 0 | 0 | 3623 | 3554.5754 | 3554.5754 | 3554.5754 | 2691.5087 | 780 | 200 | 3671.5087 | 91.79% | 95% | 0% | -49.1991 | 3505.3763 | -2750 | -200 | 555.3763 | -13.88% | 90.31% | 95% | 0% | 3623 | -43
[5 empty] | 2019-01-30 | 37 | 714.5 | 3592 | -41 | 0 | 0 | 3633 | 3570.2391 | 3570.2391 | 3570.2391 | 2689.9423 | 780 | 200 | 3669.9423 | 91.75% | 95% | 0% | -46.9108 | 3523.3283 | -2750 | -200 | 573.3283 | -14.33% | 90.29% | 95% | 0% | 3633 | -41
[5 empty] | 2019-01-30 | 38 | 715 | 3596 | -40 | 0 | 0 | 3636 | 3574.9382 | 3574.9382 | 3574.9382 | 2689.9423 | 780 | 200 | 3669.9423 | 91.75% | 95% | 0% | -45.7666 | 3529.1716 | -2750 | -200 | 579.1716 | -14.48% | 90.29% | 95% | 0% | 3636 | -40
[5 empty] | 2019-01-30 | 39 | 715.5 | 3563 | -39 | 0 | 0 | 3602 | 3521.6818 | 3521.6818 | 3521.6818 | 2689.9423 | 780 | 200 | 3669.9423 | 91.75% | 95% | 0% | -44.6224 | 3477.0594 | -2750 | -200 | 527.0594 | -13.18% | 90.28% | 95% | 0% | 3602 | -39
[5 empty] | 2019-01-30 | 40 | 716 | 3504 | -38 | 0 | 0 | 3542 | 3427.6999 | 3427.6999 | 3427.6999 | 2688.3759 | 780 | 200 | 3668.3759 | 91.71% | 95% | 0% | -43.4783 | 3384.2217 | -2750 | -200 | 434.2217 | -10.86% | 90.27% | 95% | 0% | 3542 | -38
[5 empty] | 2019-01-30 | 41 | 716.5 | 3456 | -37 | 0 | 0 | 3493 | 3350.9481 | 3350.9481 | 3350.9481 | 2688.3759 | 780 | 200 | 3668.3759 | 91.71% | 95% | 0% | -42.3341 | 3308.614 | -2750 | -200 | 358.614 | -8.965% | 90.26% | 95% | 0% | 3493 | -37
[5 empty] | 2019-01-30 | 42 | 717 | 3346 | -36 | 0 | 0 | 3382 | 3177.0816 | 3177.0816 | 3177.0816 | 2688.3759 | 780 | 200 | 3668.3759 | 91.71% | 95% | 0% | -41.1899 | 3135.8917 | -2750 | -200 | 185.8917 | -4.647% | 90.26% | 95% | 0% | 3382 | -36
[5 empty] | 2019-01-30 | 43 | 717.5 | 3225 | -35 | 0 | 0 | 3260 | 2985.9852 | 2985.9852 | 2985.9852 | 2688.3759 | 780 | 200 | 3668.3759 | 91.71% | 95% | 0% | -40.0458 | 2945.9394 | -2750 | -200 | -4.0606 | 0.1015% | 90.26% | 95% | 0% | 3260 | -35
[5 empty] | 2019-01-30 | 44 | 718 | 3052 | -35 | 0 | 0 | 3087 | 2715.0041 | 2715.0041 | 2715.0041 | 2688.3759 | 780 | 200 | 3668.3759 | 91.71% | 95% | 0% | -40.0458 | 2674.9584 | -2750 | -200 | -275.0416 | 6.876% | 90.26% | 95% | 0% | 3087 | -35
[5 empty] | 2019-01-30 | 45 | 718.5 | 2875 | -34 | 0 | 0 | 2909 | 2436.1913 | 2436.1913 | 2436.1913 | 2688.3759 | 780 | 200 | 3668.3759 | 91.71% | 95% | 0% | -38.9016 | 2397.2897 | -2750 | -200 | -552.7103 | 13.82% | 90.26% | 95% | 0% | 2909 | -34
[5 empty] | 2019-01-30 | 46 | 719 | 2718 | -33 | 0 | 0 | 2751 | 2188.7057 | 2188.7057 | 2188.7057 | 2686.8096 | 780 | 200 | 3666.8096 | 91.67% | 95% | 0% | -37.7574 | 2150.9483 | -2750 | -200 | -799.0517 | 19.98% | 90.26% | 95% | 0% | 2751 | -33
[5 empty] | 2019-01-30 | 47 | 719.5 | 2550 | -34 | 0 | 0 | 2584 | 1927.1228 | 1927.1228 | 1927.1228 | 2686.8096 | 780 | 200 | 3666.8096 | 91.67% | 95% | 0% | -38.9016 | 1888.2212 | -2750 | -200 | -1061.7788 | 26.54% | 90.25% | 95% | 0% | 2584 | -34
[5 empty] | 2019-01-30 | 48 | 720 | 2446 | -34 | 0 | 0 | 2480 | 1764.2209 | 1764.2209 | 1764.2209 | 2686.8096 | 780 | 200 | 3666.8096 | 91.67% | 95% | 0% | -38.9016 | 1725.3193 | -2750 | -200 | -1224.6807 | 30.62% | 90.25% | 95% | 0% | 2480 | -34
[5 empty] | 2019-01-31 | 1 | 720.5 | 2420 | -34 | 0 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 2685.2432 | 780 | 200 | 3665.2432 | 91.63% | 95% | 0% | -38.9016 | 1684.5939 | -2750 | -200 | -1265.4061 | 31.64% | 90.25% | 95% | 0% | 2454 | -34
[5 empty] | 2019-01-31 | 2 | 721 | 2437 | -34 | 0 | 0 | 2471 | 1750.1237 | 1750.1237 | 1750.1237 | 2685.2432 | 780 | 200 | 3665.2432 | 91.63% | 95% | 0% | -38.9016 | 1711.2221 | -2750 | -200 | -1238.7779 | 30.97% | 90.25% | 95% | 0% | 2471 | -34
[5 empty] | 2019-01-31 | 3 | 721.5 | 2404 | -34 | 0 | 0 | 2438 | 1698.4336 | 1698.4336 | 1698.4336 | 2685.2432 | 780 | 200 | 3665.2432 | 91.63% | 95% | 0% | -38.9016 | 1659.532 | -2750 | -200 | -1290.468 | 32.26% | 90.24% | 95% | 0% | 2438 | -34
[5 empty] | 2019-01-31 | 4 | 722 | 2375 | -35 | 0 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 2685.2432 | 780 | 200 | 3665.2432 | 91.63% | 95% | 0% | -40.0458 | 1614.5297 | -2750 | -200 | -1335.4703 | 33.39% | 90.24% | 95% | 0% | 2410 | -35
[5 empty] | 2019-01-31 | 5 | 722.5 | 2346 | -35 | 0 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 2685.2432 | 780 | 200 | 3665.2432 | 91.63% | 95% | 0% | -40.0458 | 1569.1051 | -2750 | -200 | -1380.8949 | 34.52% | 90.2% | 95% | 0% | 2381 | -35
[5 empty] | 2019-01-31 | 6 | 723 | 2340 | -34 | 0 | 0 | 2374 | 1598.1863 | 1598.1863 | 1598.1863 | 2683.6768 | 780 | 200 | 3663.6768 | 91.59% | 95% | 0% | -38.9016 | 1559.2847 | -2750 | -200 | -1390.7153 | 34.77% | 90.2% | 95% | 0% | 2374 | -34
[5 empty] | 2019-01-31 | 7 | 723.5 | 2320 | -37 | 0 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 2683.6768 | 780 | 200 | 3663.6768 | 91.59% | 95% | 0% | -42.3341 | 1529.224 | -2750 | -200 | -1420.776 | 35.52% | 90.2% | 95% | 0% | 2357 | -37
[5 empty] | 2019-01-31 | 8 | 724 | 2282 | -40 | 0 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 2683.6768 | 780 | 200 | 3663.6768 | 91.59% | 95% | 0% | -45.7666 | 1470.9688 | -2750 | -200 | -1479.0312 | 36.98% | 90.19% | 95% | 0% | 2322 | -40
[5 empty] | 2019-01-31 | 9 | 724.5 | 2270 | -41 | 0 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 2683.6768 | 780 | 200 | 3663.6768 | 91.59% | 95% | 0% | -46.9108 | 1452.5946 | -2750 | -200 | -1497.4054 | 37.44% | 90.18% | 95% | 0% | 2311 | -41
[5 empty] | 2019-01-31 | 10 | 725 | 2278 | -43 | 0 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 2683.6768 | 780 | 200 | 3663.6768 | 91.59% | 95% | 0% | -49.1991 | 1465.9699 | -2750 | -200 | -1484.0301 | 37.1% | 90.16% | 95% | 0% | 2321 | -43
[5 empty] | 2019-01-31 | 11 | 725.5 | 2332 | -45 | 0 | 0 | 2377 | 1602.8854 | 1602.8854 | 1602.8854 | 2682.1105 | 780 | 200 | 3662.1105 | 91.55% | 95% | 0% | -51.4874 | 1551.398 | -2750 | -200 | -1398.602 | 34.97% | 90.15% | 95% | 0% | 2377 | -45
[5 empty] | 2019-01-31 | 12 | 726 | 2434 | -47 | 0 | 0 | 2481 | 1765.7873 | 1765.7873 | 1765.7873 | 2682.1105 | 780 | 200 | 3662.1105 | 91.55% | 95% | 0% | -53.7757 | 1712.0116 | -2750 | -200 | -1237.9884 | 30.95% | 90.14% | 95% | 0% | 2481 | -47
[5 empty] | 2019-01-31 | 13 | 726.5 | 2696 | -46 | 0 | 0 | 2742 | 2174.6084 | 2174.6084 | 2174.6084 | 2682.1105 | 780 | 200 | 3662.1105 | 91.55% | 95% | 0% | -52.6316 | 2121.9768 | -2750 | -200 | -828.0232 | 20.7% | 90.13% | 95% | 0% | 2742 | -46
[5 empty] | 2019-01-31 | 14 | 727 | 2969 | -46 | 0 | 0 | 3015 | 2602.2259 | 2602.2259 | 2602.2259 | 2682.1105 | 780 | 200 | 3662.1105 | 91.55% | 95% | 0% | -52.6316 | 2549.5943 | -2750 | -200 | -400.4057 | 10.01% | 90.13% | 95% | 0% | 3015 | -46
[5 empty] | 2019-01-31 | 15 | 727.5 | 3288 | -48 | 0 | 0 | 3336 | 3105.0289 | 3105.0289 | 3105.0289 | 2682.1105 | 780 | 200 | 3662.1105 | 91.55% | 95% | 0% | -54.9199 | 3050.1089 | -2750 | -200 | 100.1089 | -2.503% | 90.13% | 95% | 0% | 3336 | -48
[5 empty] | 2019-01-31 | 16 | 728 | 3374 | -50 | 0 | 0 | 3424 | 3242.8689 | 3242.8689 | 3242.8689 | 2680.5441 | 780 | 200 | 3660.5441 | 91.51% | 95% | 0% | -57.2082 | 3185.6607 | -2750 | -200 | 235.6607 | -5.892% | 90.13% | 95% | 0% | 3424 | -50
[5 empty] | 2019-01-31 | 17 | 728.5 | 3429 | -67 | 0 | 0 | 3496 | 3355.6472 | 3355.6472 | 3355.6472 | 2680.5441 | 780 | 200 | 3660.5441 | 91.51% | 95% | 0% | -76.659 | 3278.9881 | -2750 | -200 | 328.9881 | -8.225% | 90.13% | 95% | 0% | 3496 | -67
[5 empty] | 2019-01-31 | 18 | 729 | 3410 | -109 | 0 | 0 | 3519 | 3391.6735 | 3391.6735 | 3391.6735 | 2680.5441 | 780 | 200 | 3660.5441 | 91.51% | 95% | 0% | -124.714 | 3266.9596 | -2750 | -200 | 316.9596 | -7.924% | 90.11% | 95% | 0% | 3519 | -109
[5 empty] | 2019-01-31 | 19 | 729.5 | 3395 | -162 | 1 | 0 | 3557 | 3451.1954 | 3451.1954 | 3451.1954 | 2678.9777 | 780 | 200 | 3658.9777 | 91.47% | 95% | 0% | -185.3547 | 3265.8407 | -3550 | -400 | -684.1593 | 17.1% | 90.11% | 95% | 0% | 3557 | -162
[5 empty] | 2019-01-31 | 20 | 730 | 3325 | -204 | 1 | 0 | 3529 | 3407.3372 | 3407.3372 | 3407.3372 | 2678.9777 | 780 | 200 | 3658.9777 | 91.47% | 95% | 0% | -233.4096 | 3173.9276 | -3550 | -400 | -776.0724 | 19.4% | 90.1% | 95% | 0% | 3529 | -204
[5 empty] | 2019-01-31 | 21 | 730.5 | 3246 | -235 | 1 | 0 | 3481 | 3332.1517 | 3332.1517 | 3332.1517 | 2678.9777 | 780 | 200 | 3658.9777 | 91.47% | 95% | 0% | -268.8787 | 3063.273 | -3550 | -400 | -886.727 | 22.17% | 90.1% | 95% | 0% | 3481 | -235
[5 empty] | 2019-01-31 | 22 | 731 | 3215 | -252 | 1 | 0 | 3467 | 3310.2226 | 3310.2226 | 3310.2226 | 2678.9777 | 780 | 200 | 3658.9777 | 91.47% | 95% | 0% | -288.3295 | 3021.8931 | -3550 | -400 | -928.1069 | 23.2% | 90.1% | 95% | 0% | 3467 | -252
[5 empty] | 2019-01-31 | 23 | 731.5 | 3163 | -273 | 1 | 0 | 3436 | 3261.6653 | 3261.6653 | 3261.6653 | 2678.9777 | 780 | 200 | 3658.9777 | 91.47% | 95% | 0% | -312.357 | 2949.3083 | -3550 | -400 | -1000.6917 | 25.02% | 90.09% | 95% | 0% | 3436 | -273
[5 empty] | 2019-01-31 | 24 | 732 | 3164 | -277 | 1 | 0 | 3441 | 3269.4971 | 3269.4971 | 3269.4971 | 2678.9777 | 780 | 200 | 3658.9777 | 91.47% | 95% | 0% | -316.9336 | 2952.5635 | -3550 | -400 | -997.4365 | 24.94% | 90.09% | 95% | 0% | 3441 | -277
[5 empty] | 2019-01-31 | 25 | 732.5 | 3196 | -270 | 1 | 0 | 3466 | 3308.6562 | 3308.6562 | 3308.6562 | 2677.4114 | 780 | 200 | 3657.4114 | 91.44% | 95% | 0% | -308.9245 | 2999.7317 | -3550 | -400 | -950.2683 | 23.76% | 90.09% | 95% | 0% | 3466 | -270
[5 empty] | 2019-01-31 | 26 | 733 | 3201 | -251 | 1 | 0 | 3452 | 3286.7271 | 3286.7271 | 3286.7271 | 2677.4114 | 780 | 200 | 3657.4114 | 91.44% | 95% | 0% | -287.1854 | 2999.5418 | -3550 | -400 | -950.4582 | 23.76% | 90.07% | 95% | 0% | 3452 | -251
[5 empty] | 2019-01-31 | 27 | 733.5 | 3211 | -234 | 1 | 0 | 3445 | 3275.7626 | 3275.7626 | 3275.7626 | 2677.4114 | 780 | 200 | 3657.4114 | 91.44% | 95% | 0% | -267.7346 | 3008.028 | -3550 | -400 | -941.972 | 23.55% | 90.06% | 95% | 0% | 3445 | -234
[5 empty] | 2019-01-31 | 28 | 734 | 3229 | -214 | 1 | 0 | 3443 | 3272.6298 | 3272.6298 | 3272.6298 | 2677.4114 | 780 | 200 | 3657.4114 | 91.44% | 95% | 0% | -244.8513 | 3027.7786 | -3550 | -400 | -922.2214 | 23.06% | 90.04% | 95% | 0% | 3443 | -214
[5 empty] | 2019-01-31 | 29 | 734.5 | 3265 | -191 | 1 | 0 | 3456 | 3292.9926 | 3292.9926 | 3292.9926 | 2677.4114 | 780 | 200 | 3657.4114 | 91.44% | 95% | 0% | -218.5355 | 3074.4571 | -3550 | -400 | -875.5429 | 21.89% | 90.04% | 95% | 0% | 3456 | -191
[5 empty] | 2019-01-31 | 30 | 735 | 3296 | -169 | 1 | 0 | 3465 | 3307.0899 | 3307.0899 | 3307.0899 | 2677.4114 | 780 | 200 | 3657.4114 | 91.44% | 95% | 0% | -193.3638 | 3113.726 | -3550 | -400 | -836.274 | 20.91% | 90.03% | 95% | 0% | 3465 | -169
[5 empty] | 2019-01-31 | 31 | 735.5 | 3334 | -146 | 1 | 0 | 3480 | 3330.5853 | 3330.5853 | 3330.5853 | 2677.4114 | 780 | 200 | 3657.4114 | 91.44% | 95% | 0% | -167.0481 | 3163.5373 | -3550 | -400 | -786.4627 | 19.66% | 90.03% | 95% | 0% | 3480 | -146
[5 empty] | 2019-01-31 | 32 | 736 | 3407 | -122 | 1 | 0 | 3529 | 3407.3372 | 3407.3372 | 3407.3372 | 2677.4114 | 780 | 200 | 3657.4114 | 91.44% | 95% | 0% | -139.5881 | 3267.7491 | -3550 | -400 | -682.2509 | 17.06% | 90.01% | 95% | 0% | 3529 | -122
[5 empty] | 2019-01-31 | 33 | 736.5 | 3486 | -107 | 1 | 0 | 3593 | 3507.5845 | 3507.5845 | 3507.5845 | 2677.4114 | 780 | 200 | 3657.4114 | 91.44% | 95% | 0% | -122.4256 | 3385.1589 | -3550 | -400 | -564.8411 | 14.12% | 90.01% | 95% | 0% | 3593 | -107
[5 empty] | 2019-01-31 | 34 | 737 | 3521 | -105 | 1 | 0 | 3626 | 3559.2745 | 3559.2745 | 3559.2745 | 2677.4114 | 780 | 200 | 3657.4114 | 91.44% | 95% | 0% | -120.1373 | 3439.1372 | -3550 | -400 | -510.8628 | 12.77% | 90% | 95% | 0% | 3626 | -105
[5 empty] | 2019-01-31 | 35 | 737.5 | 3530 | -106 | 1 | 0 | 3636 | 3574.9382 | 3574.9382 | 3574.9382 | 2677.4114 | 780 | 200 | 3657.4114 | 91.44% | 95% | 0% | -121.2815 | 3453.6567 | -3550 | -400 | -496.3433 | 12.41% | 90% | 95% | 0% | 3636 | -106
[5 empty] | 2019-01-31 | 36 | 738 | 3508 | -108 | 0 | 0 | 3616 | 3543.6109 | 3543.6109 | 3543.6109 | 2675.845 | 780 | 200 | 3655.845 | 91.4% | 95% | 0% | -123.5698 | 3420.0411 | -2750 | -200 | 470.0411 | -11.75% | 89.99% | 95% | 0% | 3616 | -108
[5 empty] | 2019-01-31 | 37 | 738.5 | 3501 | -107 | 0 | 0 | 3608 | 3531.08 | 3531.08 | 3531.08 | 2675.845 | 780 | 200 | 3655.845 | 91.4% | 95% | 0% | -122.4256 | 3408.6543 | -2750 | -200 | 458.6543 | -11.47% | 89.98% | 95% | 0% | 3608 | -107
[5 empty] | 2019-01-31 | 38 | 739 | 3503 | -107 | 0 | 0 | 3610 | 3534.2127 | 3534.2127 | 3534.2127 | 2675.845 | 780 | 200 | 3655.845 | 91.4% | 95% | 0% | -122.4256 | 3411.7871 | -2750 | -200 | 461.7871 | -11.54% | 89.98% | 95% | 0% | 3610 | -107
[5 empty] | 2019-01-31 | 39 | 739.5 | 3508 | -107 | 0 | 0 | 3615 | 3542.0445 | 3542.0445 | 3542.0445 | 2675.845 | 780 | 200 | 3655.845 | 91.4% | 95% | 0% | -122.4256 | 3419.6189 | -2750 | -200 | 469.6189 | -11.74% | 89.98% | 95% | 0% | 3615 | -107
[5 empty] | 2019-01-31 | 40 | 740 | 3454 | -107 | 0 | 0 | 3561 | 3457.4608 | 3457.4608 | 3457.4608 | 2674.2786 | 780 | 200 | 3654.2786 | 91.36% | 95% | 0% | -122.4256 | 3335.0352 | -2750 | -200 | 385.0352 | -9.626% | 89.97% | 95% | 0% | 3561 | -107
[5 empty] | 2019-01-31 | 41 | 740.5 | 3358 | -107 | 0 | 0 | 3465 | 3307.0899 | 3307.0899 | 3307.0899 | 2674.2786 | 780 | 200 | 3654.2786 | 91.36% | 95% | 0% | -122.4256 | 3184.6642 | -2750 | -200 | 234.6642 | -5.867% | 89.97% | 95% | 0% | 3465 | -107
[5 empty] | 2019-01-31 | 42 | 741 | 3208 | -107 | 0 | 0 | 3315 | 3072.1352 | 3072.1352 | 3072.1352 | 2674.2786 | 780 | 200 | 3654.2786 | 91.36% | 95% | 0% | -122.4256 | 2949.7096 | -2750 | -200 | -0.29043 | 0.007261% | 89.97% | 95% | 0% | 3315 | -107
[5 empty] | 2019-01-31 | 43 | 741.5 | 3053 | -107 | 0 | 0 | 3160 | 2829.3487 | 2829.3487 | 2829.3487 | 2674.2786 | 780 | 200 | 3654.2786 | 91.36% | 95% | 0% | -122.4256 | 2706.9231 | -2750 | -200 | -243.0769 | 6.077% | 89.97% | 95% | 0% | 3160 | -107
[5 empty] | 2019-01-31 | 44 | 742 | 2868 | -107 | 0 | 0 | 2975 | 2539.5713 | 2539.5713 | 2539.5713 | 2674.2786 | 780 | 200 | 3654.2786 | 91.36% | 95% | 0% | -122.4256 | 2417.1457 | -2750 | -200 | -532.8543 | 13.32% | 89.96% | 95% | 0% | 2975 | -107
[5 empty] | 2019-01-31 | 45 | 742.5 | 2681 | -106 | 0 | 0 | 2787 | 2245.0948 | 2245.0948 | 2245.0948 | 2674.2786 | 780 | 200 | 3654.2786 | 91.36% | 95% | 0% | -121.2815 | 2123.8133 | -2750 | -200 | -826.1867 | 20.65% | 89.95% | 95% | 0% | 2787 | -106
[5 empty] | 2019-01-31 | 46 | 743 | 2516 | -104 | 0 | 0 | 2620 | 1983.512 | 1983.512 | 1983.512 | 2674.2786 | 780 | 200 | 3654.2786 | 91.36% | 95% | 0% | -118.9931 | 1864.5188 | -2750 | -200 | -1085.4812 | 27.14% | 89.94% | 95% | 0% | 2620 | -104
[5 empty] | 2019-01-31 | 47 | 743.5 | 2344 | -107 | 0 | 0 | 2451 | 1718.7964 | 1718.7964 | 1718.7964 | 2672.7123 | 780 | 200 | 3652.7123 | 91.32% | 95% | 0% | -122.4256 | 1596.3707 | -2750 | -200 | -1353.6293 | 33.84% | 89.94% | 95% | 0% | 2451 | -107
[5 empty] | 2019-01-31 | 48 | 744 | 2244 | -110 | 0 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 2672.7123 | 780 | 200 | 3652.7123 | 91.32% | 95% | 0% | -125.8581 | 1441.0009 | -2750 | -200 | -1508.9991 | 37.72% | 89.93% | 95% | 0% | 2354 | -110
[5 empty] | 2019-02-01 | 1 | 744.5 | 2218 | -111 | 0 | 0 | 2329 | 1527.6999 | 1527.6999 | 1527.6999 | 2672.7123 | 780 | 200 | 3652.7123 | 91.32% | 95% | 0% | -127.0023 | 1400.6976 | -2750 | -200 | -1549.3024 | 38.73% | 89.92% | 95% | 0% | 2329 | -111
[5 empty] | 2019-02-01 | 2 | 745 | 2259 | -111 | 0 | 0 | 2370 | 1591.9209 | 1591.9209 | 1591.9209 | 2672.7123 | 780 | 200 | 3652.7123 | 91.32% | 95% | 0% | -127.0023 | 1464.9186 | -2750 | -200 | -1485.0814 | 37.13% | 89.92% | 95% | 0% | 2370 | -111
[5 empty] | 2019-02-01 | 3 | 745.5 | 2235 | -112 | 0 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 2672.7123 | 780 | 200 | 3652.7123 | 91.32% | 95% | 0% | -128.1465 | 1427.748 | -2750 | -200 | -1522.252 | 38.06% | 89.92% | 95% | 0% | 2347 | -112
[5 empty] | 2019-02-01 | 4 | 746 | 2180 | -113 | 0 | 0 | 2293 | 1471.3108 | 1471.3108 | 1471.3108 | 2671.1459 | 780 | 200 | 3651.1459 | 91.28% | 95% | 0% | -129.2906 | 1342.0202 | -2750 | -200 | -1607.9798 | 40.2% | 89.91% | 95% | 0% | 2293 | -113
[5 empty] | 2019-02-01 | 5 | 746.5 | 2142 | -113 | 0 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 2671.1459 | 780 | 200 | 3651.1459 | 91.28% | 95% | 0% | -129.2906 | 1282.4983 | -2750 | -200 | -1667.5017 | 41.69% | 89.91% | 95% | 0% | 2255 | -113
[5 empty] | 2019-02-01 | 6 | 747 | 2138 | -112 | 0 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 2671.1459 | 780 | 200 | 3651.1459 | 91.28% | 95% | 0% | -128.1465 | 1275.8107 | -2750 | -200 | -1674.1893 | 41.85% | 89.9% | 95% | 0% | 2250 | -112
[5 empty] | 2019-02-01 | 7 | 747.5 | 2114 | -114 | 0 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 2671.1459 | 780 | 200 | 3651.1459 | 91.28% | 95% | 0% | -130.4348 | 1239.0623 | -2750 | -200 | -1710.9377 | 42.77% | 89.9% | 95% | 0% | 2228 | -114
[5 empty] | 2019-02-01 | 8 | 748 | 2070 | -116 | 0 | 0 | 2186 | 1303.7098 | 1303.7098 | 1303.7098 | 2671.1459 | 780 | 200 | 3651.1459 | 91.28% | 95% | 0% | -132.7231 | 1170.9867 | -2750 | -200 | -1779.0133 | 44.48% | 89.9% | 95% | 0% | 2186 | -116
[5 empty] | 2019-02-01 | 9 | 748.5 | 2061 | -116 | 0 | 0 | 2177 | 1289.6125 | 1289.6125 | 1289.6125 | 2671.1459 | 780 | 200 | 3651.1459 | 91.28% | 95% | 0% | -132.7231 | 1156.8894 | -2750 | -200 | -1793.1106 | 44.83% | 89.89% | 95% | 0% | 2177 | -116
[5 empty] | 2019-02-01 | 10 | 749 | 2070 | -117 | 0 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 2671.1459 | 780 | 200 | 3651.1459 | 91.28% | 95% | 0% | -133.8673 | 1171.4089 | -2750 | -200 | -1778.5911 | 44.46% | 89.88% | 95% | 0% | 2187 | -117
[5 empty] | 2019-02-01 | 11 | 749.5 | 2123 | -116 | 0 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 2669.5796 | 780 | 200 | 3649.5796 | 91.24% | 95% | 0% | -132.7231 | 1254.004 | -2750 | -200 | -1695.996 | 42.4% | 89.87% | 95% | 0% | 2239 | -116
[5 empty] | 2019-02-01 | 12 | 750 | 2214 | -115 | 0 | 0 | 2329 | 1527.6999 | 1527.6999 | 1527.6999 | 2669.5796 | 780 | 200 | 3649.5796 | 91.24% | 95% | 0% | -131.5789 | 1396.121 | -2750 | -200 | -1553.879 | 38.85% | 89.87% | 95% | 0% | 2329 | -115
[5 empty] | 2019-02-01 | 13 | 750.5 | 2475 | -113 | 0 | 0 | 2588 | 1933.3883 | 1933.3883 | 1933.3883 | 2669.5796 | 780 | 200 | 3649.5796 | 91.24% | 95% | 0% | -129.2906 | 1804.0977 | -2750 | -200 | -1145.9023 | 28.65% | 89.87% | 95% | 0% | 2588 | -113
[5 empty] | 2019-02-01 | 14 | 751 | 2715 | -110 | 0 | 0 | 2825 | 2304.6167 | 2304.6167 | 2304.6167 | 2668.0132 | 780 | 200 | 3648.0132 | 91.2% | 95% | 0% | -125.8581 | 2178.7585 | -2750 | -200 | -771.2415 | 19.28% | 89.87% | 95% | 0% | 2825 | -110
[5 empty] | 2019-02-01 | 15 | 751.5 | 3002 | -109 | 0 | 0 | 3111 | 2752.5969 | 2752.5969 | 2752.5969 | 2668.0132 | 780 | 200 | 3648.0132 | 91.2% | 95% | 0% | -124.714 | 2627.8829 | -2750 | -200 | -322.1171 | 8.053% | 89.86% | 95% | 0% | 3111 | -109
[5 empty] | 2019-02-01 | 16 | 752 | 3139 | -109 | 0 | 0 | 3248 | 2967.1888 | 2967.1888 | 2967.1888 | 2668.0132 | 780 | 200 | 3648.0132 | 91.2% | 95% | 0% | -124.714 | 2842.4748 | -2750 | -200 | -107.5252 | 2.688% | 89.85% | 95% | 0% | 3248 | -109
[5 empty] | 2019-02-01 | 17 | 752.5 | 3253 | -109 | 0 | 0 | 3362 | 3145.7543 | 3145.7543 | 3145.7543 | 2668.0132 | 780 | 200 | 3648.0132 | 91.2% | 95% | 0% | -124.714 | 3021.0404 | -2750 | -200 | 71.0404 | -1.776% | 89.85% | 95% | 0% | 3362 | -109
[5 empty] | 2019-02-01 | 18 | 753 | 3283 | -119 | 0 | 0 | 3402 | 3208.4089 | 3208.4089 | 3208.4089 | 2668.0132 | 780 | 200 | 3648.0132 | 91.2% | 95% | 0% | -136.1556 | 3072.2533 | -2750 | -200 | 122.2533 | -3.056% | 89.84% | 95% | 0% | 3402 | -119
[5 empty] | 2019-02-01 | 19 | 753.5 | 3335 | -116 | 0 | 0 | 3451 | 3285.1608 | 3285.1608 | 3285.1608 | 2668.0132 | 780 | 200 | 3648.0132 | 91.2% | 95% | 0% | -132.7231 | 3152.4376 | -2750 | -200 | 202.4376 | -5.061% | 89.84% | 95% | 0% | 3451 | -116
[5 empty] | 2019-02-01 | 20 | 754 | 3339 | -148 | 1 | 0 | 3487 | 3341.5499 | 3341.5499 | 3341.5499 | 2666.4468 | 780 | 200 | 3646.4468 | 91.16% | 95% | 0% | -169.3364 | 3172.2135 | -3550 | -400 | -777.7865 | 19.44% | 89.84% | 95% | 0% | 3487 | -148
[5 empty] | 2019-02-01 | 21 | 754.5 | 3312 | -168 | 1 | 0 | 3480 | 3330.5853 | 3330.5853 | 3330.5853 | 2666.4468 | 780 | 200 | 3646.4468 | 91.16% | 95% | 0% | -192.2197 | 3138.3656 | -3550 | -400 | -811.6344 | 20.29% | 89.82% | 95% | 0% | 3480 | -168
[5 empty] | 2019-02-01 | 22 | 755 | 3274 | -193 | 1 | 0 | 3467 | 3310.2226 | 3310.2226 | 3310.2226 | 2666.4468 | 780 | 200 | 3646.4468 | 91.16% | 95% | 0% | -220.8238 | 3089.3988 | -3550 | -400 | -860.6012 | 21.52% | 89.82% | 95% | 0% | 3467 | -193
[5 empty] | 2019-02-01 | 23 | 755.5 | 3266 | -218 | 1 | 0 | 3484 | 3336.8508 | 3336.8508 | 3336.8508 | 2666.4468 | 780 | 200 | 3646.4468 | 91.16% | 95% | 0% | -249.4279 | 3087.4229 | -3550 | -400 | -862.5771 | 21.56% | 89.82% | 95% | 0% | 3484 | -218
[5 empty] | 2019-02-01 | 24 | 756 | 3245 | -228 | 1 | 0 | 3473 | 3319.6208 | 3319.6208 | 3319.6208 | 2664.8805 | 780 | 200 | 3644.8805 | 91.12% | 95% | 0% | -260.8696 | 3058.7512 | -3550 | -400 | -891.2488 | 22.28% | 89.82% | 95% | 0% | 3473 | -228
[5 empty] | 2019-02-01 | 25 | 756.5 | 3254 | -236 | 1 | 0 | 3490 | 3346.249 | 3346.249 | 3346.249 | 2664.8805 | 780 | 200 | 3644.8805 | 91.12% | 95% | 0% | -270.0229 | 3076.2261 | -3550 | -400 | -873.7739 | 21.84% | 89.81% | 95% | 0% | 3490 | -236
[5 empty] | 2019-02-01 | 26 | 757 | 3235 | -242 | 1 | 0 | 3477 | 3325.8862 | 3325.8862 | 3325.8862 | 2664.8805 | 780 | 200 | 3644.8805 | 91.12% | 95% | 0% | -276.8879 | 3048.9984 | -3550 | -400 | -901.0016 | 22.53% | 89.81% | 95% | 0% | 3477 | -242
[5 empty] | 2019-02-01 | 27 | 757.5 | 3211 | -241 | 1 | 0 | 3452 | 3286.7271 | 3286.7271 | 3286.7271 | 2664.8805 | 780 | 200 | 3644.8805 | 91.12% | 95% | 0% | -275.7437 | 3010.9834 | -3550 | -400 | -939.0166 | 23.48% | 89.79% | 95% | 0% | 3452 | -241
[5 empty] | 2019-02-01 | 28 | 758 | 3190 | -229 | 1 | 0 | 3419 | 3235.0371 | 3235.0371 | 3235.0371 | 2664.8805 | 780 | 200 | 3644.8805 | 91.12% | 95% | 0% | -262.0137 | 2973.0234 | -3550 | -400 | -976.9766 | 24.42% | 89.79% | 95% | 0% | 3419 | -229
[5 empty] | 2019-02-01 | 29 | 758.5 | 3206 | -205 | 1 | 0 | 3411 | 3222.5062 | 3222.5062 | 3222.5062 | 2663.3141 | 780 | 200 | 3643.3141 | 91.08% | 95% | 0% | -234.5538 | 2987.9524 | -3550 | -400 | -962.0476 | 24.05% | 89.79% | 95% | 0% | 3411 | -205
[5 empty] | 2019-02-01 | 30 | 759 | 3188 | -191 | 1 | 0 | 3379 | 3172.3825 | 3172.3825 | 3172.3825 | 2663.3141 | 780 | 200 | 3643.3141 | 91.08% | 95% | 0% | -218.5355 | 2953.8471 | -3550 | -400 | -996.1529 | 24.9% | 89.77% | 95% | 0% | 3379 | -191
[5 empty] | 2019-02-01 | 31 | 759.5 | 3212 | -165 | 1 | 0 | 3377 | 3169.2498 | 3169.2498 | 3169.2498 | 2661.7477 | 780 | 200 | 3641.7477 | 91.04% | 95% | 0% | -188.7872 | 2980.4626 | -3550 | -400 | -969.5374 | 24.24% | 89.76% | 95% | 0% | 3377 | -165
[5 empty] | 2019-02-01 | 32 | 760 | 3268 | -143 | 1 | 0 | 3411 | 3222.5062 | 3222.5062 | 3222.5062 | 2661.7477 | 780 | 200 | 3641.7477 | 91.04% | 95% | 0% | -163.6156 | 3058.8906 | -3550 | -400 | -891.1094 | 22.28% | 89.76% | 95% | 0% | 3411 | -143
[5 empty] | 2019-02-01 | 33 | 760.5 | 3339 | -118 | 1 | 0 | 3457 | 3294.5589 | 3294.5589 | 3294.5589 | 2661.7477 | 780 | 200 | 3641.7477 | 91.04% | 95% | 0% | -135.0114 | 3159.5475 | -3550 | -400 | -790.4525 | 19.76% | 89.76% | 95% | 0% | 3457 | -118
[5 empty] | 2019-02-01 | 34 | 761 | 3382 | -102 | 1 | 0 | 3484 | 3336.8508 | 3336.8508 | 3336.8508 | 2661.7477 | 780 | 200 | 3641.7477 | 91.04% | 95% | 0% | -116.7048 | 3220.146 | -3550 | -400 | -729.854 | 18.25% | 89.75% | 95% | 0% | 3484 | -102
[5 empty] | 2019-02-01 | 35 | 761.5 | 3432 | -100 | 1 | 0 | 3532 | 3412.0363 | 3412.0363 | 3412.0363 | 2661.7477 | 780 | 200 | 3641.7477 | 91.04% | 95% | 0% | -114.4165 | 3297.6198 | -3550 | -400 | -652.3802 | 16.31% | 89.75% | 95% | 0% | 3532 | -100
[5 empty] | 2019-02-01 | 36 | 762 | 3450 | -100 | 1 | 0 | 3550 | 3440.2308 | 3440.2308 | 3440.2308 | 2661.7477 | 780 | 200 | 3641.7477 | 91.04% | 95% | 0% | -114.4165 | 3325.8144 | -3550 | -400 | -624.1856 | 15.6% | 89.75% | 95% | 0% | 3550 | -100
[5 empty] | 2019-02-01 | 37 | 762.5 | 3453 | -100 | 0 | 0 | 3553 | 3444.9299 | 3444.9299 | 3444.9299 | 2660.1814 | 780 | 200 | 3640.1814 | 91% | 95% | 0% | -114.4165 | 3330.5134 | -2750 | -200 | 380.5134 | -9.513% | 89.74% | 95% | 0% | 3553 | -100
[5 empty] | 2019-02-01 | 38 | 763 | 3430 | -101 | 0 | 0 | 3531 | 3410.4699 | 3410.4699 | 3410.4699 | 2660.1814 | 780 | 200 | 3640.1814 | 91% | 95% | 0% | -115.5606 | 3294.9093 | -2750 | -200 | 344.9093 | -8.623% | 89.74% | 95% | 0% | 3531 | -101
[5 empty] | 2019-02-01 | 39 | 763.5 | 3398 | -102 | 0 | 0 | 3500 | 3361.9126 | 3361.9126 | 3361.9126 | 2660.1814 | 780 | 200 | 3640.1814 | 91% | 95% | 0% | -116.7048 | 3245.2078 | -2750 | -200 | 295.2078 | -7.38% | 89.72% | 95% | 0% | 3500 | -102
[5 empty] | 2019-02-01 | 40 | 764 | 3311 | -103 | 0 | 0 | 3414 | 3227.2053 | 3227.2053 | 3227.2053 | 2660.1814 | 780 | 200 | 3640.1814 | 91% | 95% | 0% | -117.849 | 3109.3563 | -2750 | -200 | 159.3563 | -3.984% | 89.71% | 95% | 0% | 3414 | -103
[5 empty] | 2019-02-01 | 41 | 764.5 | 3190 | -104 | 0 | 0 | 3294 | 3039.2415 | 3039.2415 | 3039.2415 | 2658.615 | 780 | 200 | 3638.615 | 90.97% | 95% | 0% | -118.9931 | 2920.2484 | -2750 | -200 | -29.7516 | 0.7438% | 89.71% | 95% | 0% | 3294 | -104
[5 empty] | 2019-02-01 | 42 | 765 | 3066 | -104 | 0 | 0 | 3170 | 2845.0124 | 2845.0124 | 2845.0124 | 2658.615 | 780 | 200 | 3638.615 | 90.97% | 95% | 0% | -118.9931 | 2726.0192 | -2750 | -200 | -223.9808 | 5.6% | 89.71% | 95% | 0% | 3170 | -104
[5 empty] | 2019-02-01 | 43 | 765.5 | 2922 | -105 | 0 | 0 | 3027 | 2621.0223 | 2621.0223 | 2621.0223 | 2658.615 | 780 | 200 | 3638.615 | 90.97% | 95% | 0% | -120.1373 | 2500.885 | -2750 | -200 | -449.115 | 11.23% | 89.7% | 95% | 0% | 3027 | -105
[5 empty] | 2019-02-01 | 44 | 766 | 2757 | -106 | 0 | 0 | 2863 | 2364.1385 | 2364.1385 | 2364.1385 | 2658.615 | 780 | 200 | 3638.615 | 90.97% | 95% | 0% | -121.2815 | 2242.857 | -2750 | -200 | -707.143 | 17.68% | 89.7% | 95% | 0% | 2863 | -106
[5 empty] | 2019-02-01 | 45 | 766.5 | 2615 | -107 | 0 | 0 | 2722 | 2143.2811 | 2143.2811 | 2143.2811 | 2658.615 | 780 | 200 | 3638.615 | 90.97% | 95% | 0% | -122.4256 | 2020.8555 | -2750 | -200 | -929.1445 | 23.23% | 89.7% | 95% | 0% | 2722 | -107
[5 empty] | 2019-02-01 | 46 | 767 | 2497 | -109 | 0 | 0 | 2606 | 1961.5829 | 1961.5829 | 1961.5829 | 2658.615 | 780 | 200 | 3638.615 | 90.97% | 95% | 0% | -124.714 | 1836.8689 | -2750 | -200 | -1113.1311 | 27.83% | 89.7% | 95% | 0% | 2606 | -109
[5 empty] | 2019-02-01 | 47 | 767.5 | 2336 | -107 | 0 | 0 | 2443 | 1706.2655 | 1706.2655 | 1706.2655 | 2657.0486 | 780 | 200 | 3637.0486 | 90.93% | 95% | 0% | -122.4256 | 1583.8398 | -2750 | -200 | -1366.1602 | 34.15% | 89.68% | 95% | 0% | 2443 | -107
[5 empty] | 2019-02-01 | 48 | 768 | 2240 | -106 | 0 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 2657.0486 | 780 | 200 | 3637.0486 | 90.93% | 95% | 0% | -121.2815 | 1433.0466 | -2750 | -200 | -1516.9534 | 37.92% | 89.68% | 95% | 0% | 2346 | -106
[5 empty] | 2019-02-02 | 1 | 768.5 | 2216 | -108 | 0 | 0 | 2324 | 1519.8681 | 1519.8681 | 1519.8681 | 2657.0486 | 780 | 200 | 3637.0486 | 90.93% | 95% | 0% | -123.5698 | 1396.2983 | -2750 | -200 | -1553.7017 | 38.84% | 89.68% | 95% | 0% | 2324 | -108
[5 empty] | 2019-02-02 | 2 | 769 | 2223 | -111 | 0 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 2657.0486 | 780 | 200 | 3637.0486 | 90.93% | 95% | 0% | -127.0023 | 1408.5295 | -2750 | -200 | -1541.4705 | 38.54% | 89.67% | 95% | 0% | 2334 | -111
[5 empty] | 2019-02-02 | 3 | 769.5 | 2196 | -112 | 0 | 0 | 2308 | 1494.8063 | 1494.8063 | 1494.8063 | 2657.0486 | 780 | 200 | 3637.0486 | 90.93% | 95% | 0% | -128.1465 | 1366.6598 | -2750 | -200 | -1583.3402 | 39.58% | 89.67% | 95% | 0% | 2308 | -112
[5 empty] | 2019-02-02 | 4 | 770 | 2129 | -114 | 0 | 0 | 2243 | 1392.9926 | 1392.9926 | 1392.9926 | 2657.0486 | 780 | 200 | 3637.0486 | 90.93% | 95% | 0% | -130.4348 | 1262.5578 | -2750 | -200 | -1687.4422 | 42.19% | 89.64% | 95% | 0% | 2243 | -114
[5 empty] | 2019-02-02 | 5 | 770.5 | 2086 | -116 | 0 | 0 | 2202 | 1328.7716 | 1328.7716 | 1328.7716 | 2655.4823 | 780 | 200 | 3635.4823 | 90.89% | 95% | 0% | -132.7231 | 1196.0485 | -2750 | -200 | -1753.9515 | 43.85% | 89.63% | 95% | 0% | 2202 | -116
[5 empty] | 2019-02-02 | 6 | 771 | 2070 | -118 | 0 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 2655.4823 | 780 | 200 | 3635.4823 | 90.89% | 95% | 0% | -135.0114 | 1171.8311 | -2750 | -200 | -1778.1689 | 44.45% | 89.63% | 95% | 0% | 2188 | -118
[5 empty] | 2019-02-02 | 7 | 771.5 | 2047 | -118 | 0 | 0 | 2165 | 1270.8162 | 1270.8162 | 1270.8162 | 2655.4823 | 780 | 200 | 3635.4823 | 90.89% | 95% | 0% | -135.0114 | 1135.8047 | -2750 | -200 | -1814.1953 | 45.35% | 89.62% | 95% | 0% | 2165 | -118
[5 empty] | 2019-02-02 | 8 | 772 | 1998 | -118 | 0 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 2655.4823 | 780 | 200 | 3635.4823 | 90.89% | 95% | 0% | -135.0114 | 1059.0529 | -2750 | -200 | -1890.9471 | 47.27% | 89.62% | 95% | 0% | 2116 | -118
[5 empty] | 2019-02-02 | 9 | 772.5 | 1974 | -118 | 0 | 0 | 2092 | 1156.4716 | 1156.4716 | 1156.4716 | 2653.9159 | 780 | 200 | 3633.9159 | 90.85% | 95% | 0% | -135.0114 | 1021.4601 | -2750 | -200 | -1928.5399 | 48.21% | 89.62% | 95% | 0% | 2092 | -118
[5 empty] | 2019-02-02 | 10 | 773 | 1962 | -119 | 0 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 2653.9159 | 780 | 200 | 3633.9159 | 90.85% | 95% | 0% | -136.1556 | 1003.0859 | -2750 | -200 | -1946.9141 | 48.67% | 89.62% | 95% | 0% | 2081 | -119
[5 empty] | 2019-02-02 | 11 | 773.5 | 1963 | -118 | 0 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 2653.9159 | 780 | 200 | 3633.9159 | 90.85% | 95% | 0% | -135.0114 | 1004.2301 | -2750 | -200 | -1945.7699 | 48.64% | 89.6% | 95% | 0% | 2081 | -118
[5 empty] | 2019-02-02 | 12 | 774 | 1997 | -117 | 0 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 2652.3495 | 780 | 200 | 3632.3495 | 90.81% | 95% | 0% | -133.8673 | 1057.0643 | -2750 | -200 | -1892.9357 | 47.32% | 89.6% | 95% | 0% | 2114 | -117
[5 empty] | 2019-02-02 | 13 | 774.5 | 2105 | -116 | 0 | 0 | 2221 | 1358.5326 | 1358.5326 | 1358.5326 | 2652.3495 | 780 | 200 | 3632.3495 | 90.81% | 95% | 0% | -132.7231 | 1225.8095 | -2750 | -200 | -1724.1905 | 43.1% | 89.6% | 95% | 0% | 2221 | -116
[5 empty] | 2019-02-02 | 14 | 775 | 2215 | -114 | 1 | 0 | 2329 | 1527.6999 | 1527.6999 | 1527.6999 | 2652.3495 | 780 | 200 | 3632.3495 | 90.81% | 95% | 0% | -130.4348 | 1397.2651 | -3550 | -400 | -2552.7349 | 63.82% | 89.59% | 95% | 0% | 2329 | -114
[5 empty] | 2019-02-02 | 15 | 775.5 | 2342 | -114 | 1 | 0 | 2456 | 1726.6282 | 1726.6282 | 1726.6282 | 2652.3495 | 780 | 200 | 3632.3495 | 90.81% | 95% | 0% | -130.4348 | 1596.1934 | -3550 | -400 | -2353.8066 | 58.85% | 89.59% | 95% | 0% | 2456 | -114
[5 empty] | 2019-02-02 | 16 | 776 | 2420 | -114 | 1 | 0 | 2534 | 1848.8046 | 1848.8046 | 1848.8046 | 2652.3495 | 780 | 200 | 3632.3495 | 90.81% | 95% | 0% | -130.4348 | 1718.3698 | -3550 | -400 | -2231.6302 | 55.79% | 89.59% | 95% | 0% | 2534 | -114
[5 empty] | 2019-02-02 | 17 | 776.5 | 2568 | -125 | 1 | 0 | 2693 | 2097.8566 | 2097.8566 | 2097.8566 | 2652.3495 | 780 | 200 | 3632.3495 | 90.81% | 95% | 0% | -143.0206 | 1954.836 | -3550 | -400 | -1995.164 | 49.88% | 89.58% | 95% | 0% | 2693 | -125
[5 empty] | 2019-02-02 | 18 | 777 | 2666 | -165 | 1 | 0 | 2831 | 2314.0148 | 2314.0148 | 2314.0148 | 2652.3495 | 780 | 200 | 3632.3495 | 90.81% | 95% | 0% | -188.7872 | 2125.2277 | -3550 | -400 | -1824.7723 | 45.62% | 89.56% | 95% | 0% | 2831 | -165
[5 empty] | 2019-02-02 | 19 | 777.5 | 2710 | -219 | 1 | 0 | 2929 | 2467.5185 | 2467.5185 | 2467.5185 | 2652.3495 | 780 | 200 | 3632.3495 | 90.81% | 95% | 0% | -250.5721 | 2216.9465 | -3550 | -400 | -1733.0535 | 43.33% | 89.56% | 95% | 0% | 2929 | -219
[5 empty] | 2019-02-02 | 20 | 778 | 2641 | -280 | 1 | 0 | 2921 | 2454.9876 | 2454.9876 | 2454.9876 | 2650.7832 | 780 | 200 | 3630.7832 | 90.77% | 95% | 0% | -320.3661 | 2134.6215 | -3550 | -400 | -1815.3785 | 45.38% | 89.56% | 95% | 0% | 2921 | -280
[5 empty] | 2019-02-02 | 21 | 778.5 | 2565 | -335 | 1 | 0 | 2900 | 2422.094 | 2422.094 | 2422.094 | 2650.7832 | 780 | 200 | 3630.7832 | 90.77% | 95% | 0% | -383.2952 | 2038.7988 | -3550 | -400 | -1911.2012 | 47.78% | 89.56% | 95% | 0% | 2900 | -335
[5 empty] | 2019-02-02 | 22 | 779 | 2501 | -379 | 1 | 0 | 2880 | 2390.7667 | 2390.7667 | 2390.7667 | 2650.7832 | 780 | 200 | 3630.7832 | 90.77% | 95% | 0% | -433.6384 | 1957.1283 | -3550 | -400 | -1992.8717 | 49.82% | 89.55% | 95% | 0% | 2880 | -379
[5 empty] | 2019-02-02 | 23 | 779.5 | 2425 | -424 | 1 | 0 | 2849 | 2342.2094 | 2342.2094 | 2342.2094 | 2650.7832 | 780 | 200 | 3630.7832 | 90.77% | 95% | 0% | -485.1259 | 1857.0835 | -3550 | -400 | -2092.9165 | 52.32% | 89.53% | 95% | 0% | 2849 | -424
[5 empty] | 2019-02-02 | 24 | 780 | 2366 | -454 | 1 | 0 | 2820 | 2296.7848 | 2296.7848 | 2296.7848 | 2649.2168 | 780 | 200 | 3629.2168 | 90.73% | 95% | 0% | -519.4508 | 1777.334 | -3550 | -400 | -2172.666 | 54.32% | 89.52% | 95% | 0% | 2820 | -454
[5 empty] | 2019-02-02 | 25 | 780.5 | 2314 | -467 | 1 | 0 | 2781 | 2235.6966 | 2235.6966 | 2235.6966 | 2649.2168 | 780 | 200 | 3629.2168 | 90.73% | 95% | 0% | -534.3249 | 1701.3717 | -3550 | -400 | -2248.6283 | 56.22% | 89.51% | 95% | 0% | 2781 | -467
[5 empty] | 2019-02-02 | 26 | 781 | 2261 | -467 | 1 | 0 | 2728 | 2152.6793 | 2152.6793 | 2152.6793 | 2649.2168 | 780 | 200 | 3629.2168 | 90.73% | 95% | 0% | -534.3249 | 1618.3544 | -3550 | -400 | -2331.6456 | 58.29% | 89.51% | 95% | 0% | 2728 | -467
[5 empty] | 2019-02-02 | 27 | 781.5 | 2264 | -441 | 1 | 0 | 2705 | 2116.6529 | 2116.6529 | 2116.6529 | 2649.2168 | 780 | 200 | 3629.2168 | 90.73% | 95% | 0% | -504.5767 | 1612.0763 | -3550 | -400 | -2337.9237 | 58.45% | 89.51% | 95% | 0% | 2705 | -441
[5 empty] | 2019-02-02 | 28 | 782 | 2263 | -421 | 1 | 0 | 2684 | 2083.7593 | 2083.7593 | 2083.7593 | 2647.6505 | 780 | 200 | 3627.6505 | 90.69% | 95% | 0% | -481.6934 | 1602.0659 | -3550 | -400 | -2347.9341 | 58.7% | 89.5% | 95% | 0% | 2684 | -421
[5 empty] | 2019-02-02 | 29 | 782.5 | 2312 | -385 | 1 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 2647.6505 | 780 | 200 | 3627.6505 | 90.69% | 95% | 0% | -440.5034 | 1663.6186 | -3550 | -400 | -2286.3814 | 57.16% | 89.49% | 95% | 0% | 2697 | -385
[5 empty] | 2019-02-02 | 30 | 783 | 2400 | -333 | 1 | 0 | 2733 | 2160.5111 | 2160.5111 | 2160.5111 | 2647.6505 | 780 | 200 | 3627.6505 | 90.69% | 95% | 0% | -381.0069 | 1779.5043 | -3550 | -400 | -2170.4957 | 54.26% | 89.47% | 95% | 0% | 2733 | -333
[5 empty] | 2019-02-02 | 31 | 783.5 | 2522 | -273 | 1 | 0 | 2795 | 2257.6257 | 2257.6257 | 2257.6257 | 2647.6505 | 780 | 200 | 3627.6505 | 90.69% | 95% | 0% | -312.357 | 1945.2687 | -3550 | -400 | -2004.7313 | 50.12% | 89.47% | 95% | 0% | 2795 | -273
[5 empty] | 2019-02-02 | 32 | 784 | 2670 | -209 | 1 | 0 | 2879 | 2389.2003 | 2389.2003 | 2389.2003 | 2647.6505 | 780 | 200 | 3627.6505 | 90.69% | 95% | 0% | -239.1304 | 2150.0699 | -3550 | -400 | -1799.9301 | 45% | 89.46% | 95% | 0% | 2879 | -209
[5 empty] | 2019-02-02 | 33 | 784.5 | 2844 | -149 | 1 | 0 | 2993 | 2567.7659 | 2567.7659 | 2567.7659 | 2647.6505 | 780 | 200 | 3627.6505 | 90.69% | 95% | 0% | -170.4805 | 2397.2853 | -3550 | -400 | -1552.7147 | 38.82% | 89.46% | 95% | 0% | 2993 | -149
[5 empty] | 2019-02-02 | 34 | 785 | 3016 | -108 | 1 | 0 | 3124 | 2772.9596 | 2772.9596 | 2772.9596 | 2647.6505 | 780 | 200 | 3627.6505 | 90.69% | 95% | 0% | -123.5698 | 2649.3898 | -3550 | -400 | -1300.6102 | 32.52% | 89.46% | 95% | 0% | 3124 | -108
[5 empty] | 2019-02-02 | 35 | 785.5 | 3173 | -100 | 1 | 0 | 3273 | 3006.3479 | 3006.3479 | 3006.3479 | 2647.6505 | 780 | 200 | 3627.6505 | 90.69% | 95% | 0% | -114.4165 | 2891.9314 | -3550 | -400 | -1058.0686 | 26.45% | 89.45% | 95% | 0% | 3273 | -100
[5 empty] | 2019-02-02 | 36 | 786 | 3249 | -98 | 1 | 0 | 3347 | 3122.2589 | 3122.2589 | 3122.2589 | 2647.6505 | 780 | 200 | 3627.6505 | 90.69% | 95% | 0% | -112.1281 | 3010.1307 | -3550 | -400 | -939.8693 | 23.5% | 89.45% | 95% | 0% | 3347 | -98
[5 empty] | 2019-02-02 | 37 | 786.5 | 3221 | -96 | 0 | 0 | 3317 | 3075.2679 | 3075.2679 | 3075.2679 | 2646.0841 | 780 | 200 | 3626.0841 | 90.65% | 95% | 0% | -109.8398 | 2965.4281 | -2750 | -200 | 15.4281 | -0.3857% | 89.44% | 95% | 0% | 3317 | -96
[5 empty] | 2019-02-02 | 38 | 787 | 3184 | -95 | 0 | 0 | 3279 | 3015.7461 | 3015.7461 | 3015.7461 | 2646.0841 | 780 | 200 | 3626.0841 | 90.65% | 95% | 0% | -108.6957 | 2907.0504 | -2750 | -200 | -42.9496 | 1.074% | 89.43% | 95% | 0% | 3279 | -95
[5 empty] | 2019-02-02 | 39 | 787.5 | 3143 | -92 | 0 | 0 | 3235 | 2946.8261 | 2946.8261 | 2946.8261 | 2646.0841 | 780 | 200 | 3626.0841 | 90.65% | 95% | 0% | -105.2632 | 2841.5629 | -2750 | -200 | -108.4371 | 2.711% | 89.42% | 95% | 0% | 3235 | -92
[5 empty] | 2019-02-02 | 40 | 788 | 3073 | -89 | 0 | 0 | 3162 | 2832.4815 | 2832.4815 | 2832.4815 | 2646.0841 | 780 | 200 | 3626.0841 | 90.65% | 95% | 0% | -101.8307 | 2730.6508 | -2750 | -200 | -219.3492 | 5.484% | 89.42% | 95% | 0% | 3162 | -89
[5 empty] | 2019-02-02 | 41 | 788.5 | 3000 | -85 | 0 | 0 | 3085 | 2711.8714 | 2711.8714 | 2711.8714 | 2646.0841 | 780 | 200 | 3626.0841 | 90.65% | 95% | 0% | -97.254 | 2614.6174 | -2750 | -200 | -335.3826 | 8.385% | 89.41% | 95% | 0% | 3085 | -85
[5 empty] | 2019-02-02 | 42 | 789 | 2898 | -82 | 0 | 0 | 2980 | 2547.4031 | 2547.4031 | 2547.4031 | 2646.0841 | 780 | 200 | 3626.0841 | 90.65% | 95% | 0% | -93.8215 | 2453.5816 | -2750 | -200 | -496.4184 | 12.41% | 89.41% | 95% | 0% | 2980 | -82
[5 empty] | 2019-02-02 | 43 | 789.5 | 2800 | -79 | 0 | 0 | 2879 | 2389.2003 | 2389.2003 | 2389.2003 | 2646.0841 | 780 | 200 | 3626.0841 | 90.65% | 95% | 0% | -90.389 | 2298.8113 | -2750 | -200 | -651.1887 | 16.28% | 89.41% | 95% | 0% | 2879 | -79
[5 empty] | 2019-02-02 | 44 | 790 | 2696 | -75 | 0 | 0 | 2771 | 2220.033 | 2220.033 | 2220.033 | 2644.5177 | 780 | 200 | 3624.5177 | 90.61% | 95% | 0% | -85.8124 | 2134.2206 | -2750 | -200 | -815.7794 | 20.39% | 89.41% | 95% | 0% | 2771 | -75
[5 empty] | 2019-02-02 | 45 | 790.5 | 2574 | -73 | 0 | 0 | 2647 | 2025.8038 | 2025.8038 | 2025.8038 | 2644.5177 | 780 | 200 | 3624.5177 | 90.61% | 95% | 0% | -83.524 | 1942.2798 | -2750 | -200 | -1007.7202 | 25.19% | 89.41% | 95% | 0% | 2647 | -73
[5 empty] | 2019-02-02 | 46 | 791 | 2488 | -71 | 0 | 0 | 2559 | 1887.9637 | 1887.9637 | 1887.9637 | 2644.5177 | 780 | 200 | 3624.5177 | 90.61% | 95% | 0% | -81.2357 | 1806.728 | -2750 | -200 | -1143.272 | 28.58% | 89.4% | 95% | 0% | 2559 | -71
[5 empty] | 2019-02-02 | 47 | 791.5 | 2369 | -69 | 0 | 0 | 2438 | 1698.4336 | 1698.4336 | 1698.4336 | 2644.5177 | 780 | 200 | 3624.5177 | 90.61% | 95% | 0% | -78.9474 | 1619.4863 | -2750 | -200 | -1330.5137 | 33.26% | 89.37% | 95% | 0% | 2438 | -69
[5 empty] | 2019-02-02 | 48 | 792 | 2298 | -68 | 0 | 0 | 2366 | 1585.6554 | 1585.6554 | 1585.6554 | 2644.5177 | 780 | 200 | 3624.5177 | 90.61% | 95% | 0% | -77.8032 | 1507.8522 | -2750 | -200 | -1442.1478 | 36.05% | 89.37% | 95% | 0% | 2366 | -68
[5 empty] | 2019-02-03 | 1 | 792.5 | 2265 | -69 | 0 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 2644.5177 | 780 | 200 | 3624.5177 | 90.61% | 95% | 0% | -78.9474 | 1456.5844 | -2750 | -200 | -1493.4156 | 37.34% | 89.35% | 95% | 0% | 2334 | -69
[5 empty] | 2019-02-03 | 2 | 793 | 2290 | -70 | 0 | 0 | 2360 | 1576.2572 | 1576.2572 | 1576.2572 | 2642.9514 | 780 | 200 | 3622.9514 | 90.57% | 95% | 0% | -80.0915 | 1496.1657 | -2750 | -200 | -1453.8343 | 36.35% | 89.35% | 95% | 0% | 2360 | -70
[5 empty] | 2019-02-03 | 3 | 793.5 | 2272 | -71 | 0 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 2642.9514 | 780 | 200 | 3622.9514 | 90.57% | 95% | 0% | -81.2357 | 1468.3933 | -2750 | -200 | -1481.6067 | 37.04% | 89.35% | 95% | 0% | 2343 | -71
[5 empty] | 2019-02-03 | 4 | 794 | 2198 | -73 | 0 | 0 | 2271 | 1436.8508 | 1436.8508 | 1436.8508 | 2642.9514 | 780 | 200 | 3622.9514 | 90.57% | 95% | 0% | -83.524 | 1353.3268 | -2750 | -200 | -1596.6732 | 39.92% | 89.33% | 95% | 0% | 2271 | -73
[5 empty] | 2019-02-03 | 5 | 794.5 | 2151 | -74 | 0 | 0 | 2225 | 1364.798 | 1364.798 | 1364.798 | 2642.9514 | 780 | 200 | 3622.9514 | 90.57% | 95% | 0% | -84.6682 | 1280.1298 | -2750 | -200 | -1669.8702 | 41.75% | 89.33% | 95% | 0% | 2225 | -74
[5 empty] | 2019-02-03 | 6 | 795 | 2136 | -75 | 0 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 2642.9514 | 780 | 200 | 3622.9514 | 90.57% | 95% | 0% | -85.8124 | 1257.0566 | -2750 | -200 | -1692.9434 | 42.32% | 89.33% | 95% | 0% | 2211 | -75
[5 empty] | 2019-02-03 | 7 | 795.5 | 2103 | -79 | 0 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 2641.385 | 780 | 200 | 3621.385 | 90.53% | 95% | 0% | -90.389 | 1207.0553 | -2750 | -200 | -1742.9447 | 43.57% | 89.32% | 95% | 0% | 2182 | -79
[5 empty] | 2019-02-03 | 8 | 796 | 2070 | -82 | 0 | 0 | 2152 | 1250.4534 | 1250.4534 | 1250.4534 | 2641.385 | 780 | 200 | 3621.385 | 90.53% | 95% | 0% | -93.8215 | 1156.6319 | -2750 | -200 | -1793.3681 | 44.83% | 89.32% | 95% | 0% | 2152 | -82
[5 empty] | 2019-02-03 | 9 | 796.5 | 2038 | -84 | 0 | 0 | 2122 | 1203.4625 | 1203.4625 | 1203.4625 | 2641.385 | 780 | 200 | 3621.385 | 90.53% | 95% | 0% | -96.1098 | 1107.3526 | -2750 | -200 | -1842.6474 | 46.07% | 89.31% | 95% | 0% | 2122 | -84
[5 empty] | 2019-02-03 | 10 | 797 | 2014 | -87 | 0 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 2641.385 | 780 | 200 | 3621.385 | 90.53% | 95% | 0% | -99.5423 | 1071.0265 | -2750 | -200 | -1878.9735 | 46.97% | 89.31% | 95% | 0% | 2101 | -87
[5 empty] | 2019-02-03 | 11 | 797.5 | 2018 | -89 | 0 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 2641.385 | 780 | 200 | 3621.385 | 90.53% | 95% | 0% | -101.8307 | 1078.1364 | -2750 | -200 | -1871.8636 | 46.8% | 89.31% | 95% | 0% | 2107 | -89
[5 empty] | 2019-02-03 | 12 | 798 | 2035 | -92 | 0 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 2641.385 | 780 | 200 | 3621.385 | 90.53% | 95% | 0% | -105.2632 | 1106.0312 | -2750 | -200 | -1843.9688 | 46.1% | 89.29% | 95% | 0% | 2127 | -92
[5 empty] | 2019-02-03 | 13 | 798.5 | 2101 | -92 | 0 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 2639.8186 | 780 | 200 | 3619.8186 | 90.5% | 95% | 0% | -105.2632 | 1209.4112 | -2750 | -200 | -1740.5888 | 43.51% | 89.29% | 95% | 0% | 2193 | -92
[5 empty] | 2019-02-03 | 14 | 799 | 2156 | -93 | 0 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 2639.8186 | 780 | 200 | 3619.8186 | 90.5% | 95% | 0% | -106.4073 | 1295.9834 | -2750 | -200 | -1654.0166 | 41.35% | 89.28% | 95% | 0% | 2249 | -93
[5 empty] | 2019-02-03 | 15 | 799.5 | 2227 | -97 | 1 | 0 | 2324 | 1519.8681 | 1519.8681 | 1519.8681 | 2639.8186 | 780 | 200 | 3619.8186 | 90.5% | 95% | 0% | -110.984 | 1408.8841 | -3550 | -400 | -2541.1159 | 63.53% | 89.28% | 95% | 0% | 2324 | -97
[5 empty] | 2019-02-03 | 16 | 800 | 2238 | -103 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 2639.8186 | 780 | 200 | 3619.8186 | 90.5% | 95% | 0% | -117.849 | 1428.6473 | -3550 | -400 | -2521.3527 | 63.03% | 89.27% | 95% | 0% | 2341 | -103
[5 empty] | 2019-02-03 | 17 | 800.5 | 2311 | -141 | 1 | 0 | 2452 | 1720.3627 | 1720.3627 | 1720.3627 | 2638.2523 | 780 | 200 | 3618.2523 | 90.46% | 95% | 0% | -161.3272 | 1559.0355 | -3550 | -400 | -2390.9645 | 59.77% | 89.27% | 95% | 0% | 2452 | -141
[5 empty] | 2019-02-03 | 18 | 801 | 2349 | -201 | 1 | 0 | 2550 | 1873.8664 | 1873.8664 | 1873.8664 | 2638.2523 | 780 | 200 | 3618.2523 | 90.46% | 95% | 0% | -229.9771 | 1643.8893 | -3550 | -400 | -2306.1107 | 57.65% | 89.27% | 95% | 0% | 2550 | -201
[5 empty] | 2019-02-03 | 19 | 801.5 | 2372 | -263 | 1 | 0 | 2635 | 2007.0074 | 2007.0074 | 2007.0074 | 2638.2523 | 780 | 200 | 3618.2523 | 90.46% | 95% | 0% | -300.9153 | 1706.0921 | -3550 | -400 | -2243.9079 | 56.1% | 89.26% | 95% | 0% | 2635 | -263
[5 empty] | 2019-02-03 | 20 | 802 | 2364 | -319 | 1 | 0 | 2683 | 2082.1929 | 2082.1929 | 2082.1929 | 2638.2523 | 780 | 200 | 3618.2523 | 90.46% | 95% | 0% | -364.9886 | 1717.2044 | -3550 | -400 | -2232.7956 | 55.82% | 89.24% | 95% | 0% | 2683 | -319
[5 empty] | 2019-02-03 | 21 | 802.5 | 2354 | -361 | 1 | 0 | 2715 | 2132.3166 | 2132.3166 | 2132.3166 | 2638.2523 | 780 | 200 | 3618.2523 | 90.46% | 95% | 0% | -413.0435 | 1719.2731 | -3550 | -400 | -2230.7269 | 55.77% | 89.23% | 95% | 0% | 2715 | -361
[5 empty] | 2019-02-03 | 22 | 803 | 2307 | -417 | 1 | 0 | 2724 | 2146.4138 | 2146.4138 | 2146.4138 | 2638.2523 | 780 | 200 | 3618.2523 | 90.46% | 95% | 0% | -477.1167 | 1669.2971 | -3550 | -400 | -2280.7029 | 57.02% | 89.23% | 95% | 0% | 2724 | -417
[5 empty] | 2019-02-03 | 23 | 803.5 | 2245 | -461 | 1 | 0 | 2706 | 2118.2193 | 2118.2193 | 2118.2193 | 2638.2523 | 780 | 200 | 3618.2523 | 90.46% | 95% | 0% | -527.46 | 1590.7593 | -3550 | -400 | -2359.2407 | 58.98% | 89.21% | 95% | 0% | 2706 | -461
[5 empty] | 2019-02-03 | 24 | 804 | 2198 | -490 | 1 | 0 | 2688 | 2090.0247 | 2090.0247 | 2090.0247 | 2638.2523 | 780 | 200 | 3618.2523 | 90.46% | 95% | 0% | -560.6407 | 1529.384 | -3550 | -400 | -2420.616 | 60.52% | 89.18% | 95% | 0% | 2688 | -490
[5 empty] | 2019-02-03 | 25 | 804.5 | 2209 | -491 | 1 | 0 | 2700 | 2108.8211 | 2108.8211 | 2108.8211 | 2636.6859 | 780 | 200 | 3616.6859 | 90.42% | 95% | 0% | -561.7849 | 1547.0362 | -3550 | -400 | -2402.9638 | 60.07% | 89.17% | 95% | 0% | 2700 | -491
[5 empty] | 2019-02-03 | 26 | 805 | 2244 | -465 | 1 | 0 | 2709 | 2122.9184 | 2122.9184 | 2122.9184 | 2636.6859 | 780 | 200 | 3616.6859 | 90.42% | 95% | 0% | -532.0366 | 1590.8818 | -3550 | -400 | -2359.1182 | 58.98% | 89.14% | 95% | 0% | 2709 | -465
[5 empty] | 2019-02-03 | 27 | 805.5 | 2293 | -421 | 1 | 0 | 2714 | 2130.7502 | 2130.7502 | 2130.7502 | 2636.6859 | 780 | 200 | 3616.6859 | 90.42% | 95% | 0% | -481.6934 | 1649.0568 | -3550 | -400 | -2300.9432 | 57.52% | 89.14% | 95% | 0% | 2714 | -421
[5 empty] | 2019-02-03 | 28 | 806 | 2329 | -385 | 1 | 0 | 2714 | 2130.7502 | 2130.7502 | 2130.7502 | 2636.6859 | 780 | 200 | 3616.6859 | 90.42% | 95% | 0% | -440.5034 | 1690.2468 | -3550 | -400 | -2259.7532 | 56.49% | 89.13% | 95% | 0% | 2714 | -385
[5 empty] | 2019-02-03 | 29 | 806.5 | 2423 | -332 | 1 | 0 | 2755 | 2194.9711 | 2194.9711 | 2194.9711 | 2636.6859 | 780 | 200 | 3616.6859 | 90.42% | 95% | 0% | -379.8627 | 1815.1084 | -3550 | -400 | -2134.8916 | 53.37% | 89.12% | 95% | 0% | 2755 | -332
[5 empty] | 2019-02-03 | 30 | 807 | 2523 | -276 | 1 | 0 | 2799 | 2263.8912 | 2263.8912 | 2263.8912 | 2636.6859 | 780 | 200 | 3616.6859 | 90.42% | 95% | 0% | -315.7895 | 1948.1017 | -3550 | -400 | -2001.8983 | 50.05% | 89.09% | 95% | 0% | 2799 | -276
[5 empty] | 2019-02-03 | 31 | 807.5 | 2674 | -218 | 1 | 0 | 2892 | 2409.5631 | 2409.5631 | 2409.5631 | 2636.6859 | 780 | 200 | 3616.6859 | 90.42% | 95% | 0% | -249.4279 | 2160.1351 | -3550 | -400 | -1789.8649 | 44.75% | 89.09% | 95% | 0% | 2892 | -218
[5 empty] | 2019-02-03 | 32 | 808 | 2813 | -167 | 1 | 0 | 2980 | 2547.4031 | 2547.4031 | 2547.4031 | 2635.1195 | 780 | 200 | 3615.1195 | 90.38% | 95% | 0% | -191.0755 | 2356.3276 | -3550 | -400 | -1593.6724 | 39.84% | 89.09% | 95% | 0% | 2980 | -167
[5 empty] | 2019-02-03 | 33 | 808.5 | 2939 | -131 | 1 | 0 | 3070 | 2688.3759 | 2688.3759 | 2688.3759 | 2635.1195 | 780 | 200 | 3615.1195 | 90.38% | 95% | 0% | -149.8856 | 2538.4903 | -3550 | -400 | -1411.5097 | 35.29% | 89.08% | 95% | 0% | 3070 | -131
[5 empty] | 2019-02-03 | 34 | 809 | 3082 | -116 | 1 | 0 | 3198 | 2888.8706 | 2888.8706 | 2888.8706 | 2635.1195 | 780 | 200 | 3615.1195 | 90.38% | 95% | 0% | -132.7231 | 2756.1475 | -3550 | -400 | -1193.8525 | 29.85% | 89.08% | 95% | 0% | 3198 | -116
[5 empty] | 2019-02-03 | 35 | 809.5 | 3216 | -117 | 1 | 0 | 3333 | 3100.3298 | 3100.3298 | 3100.3298 | 2635.1195 | 780 | 200 | 3615.1195 | 90.38% | 95% | 0% | -133.8673 | 2966.4625 | -3550 | -400 | -983.5375 | 24.59% | 89.07% | 95% | 0% | 3333 | -117
[5 empty] | 2019-02-03 | 36 | 810 | 3256 | -118 | 1 | 0 | 3374 | 3164.5507 | 3164.5507 | 3164.5507 | 2633.5532 | 780 | 200 | 3613.5532 | 90.34% | 95% | 0% | -135.0114 | 3029.5393 | -3550 | -400 | -920.4607 | 23.01% | 89.06% | 95% | 0% | 3374 | -118
[5 empty] | 2019-02-03 | 37 | 810.5 | 3217 | -122 | 1 | 0 | 3339 | 3109.7279 | 3109.7279 | 3109.7279 | 2633.5532 | 780 | 200 | 3613.5532 | 90.34% | 95% | 0% | -139.5881 | 2970.1398 | -3550 | -400 | -979.8602 | 24.5% | 89.05% | 95% | 0% | 3339 | -122
[5 empty] | 2019-02-03 | 38 | 811 | 3145 | -126 | 1 | 0 | 3271 | 3003.2152 | 3003.2152 | 3003.2152 | 2631.9868 | 780 | 200 | 3611.9868 | 90.3% | 95% | 0% | -144.1648 | 2859.0504 | -3550 | -400 | -1090.9496 | 27.27% | 89.04% | 95% | 0% | 3271 | -126
[5 empty] | 2019-02-03 | 39 | 811.5 | 3073 | -130 | 1 | 0 | 3203 | 2896.7024 | 2896.7024 | 2896.7024 | 2631.9868 | 780 | 200 | 3611.9868 | 90.3% | 95% | 0% | -148.7414 | 2747.961 | -3550 | -400 | -1202.039 | 30.05% | 89.03% | 95% | 0% | 3203 | -130
[5 empty] | 2019-02-03 | 40 | 812 | 2951 | -134 | 1 | 0 | 3085 | 2711.8714 | 2711.8714 | 2711.8714 | 2631.9868 | 780 | 200 | 3611.9868 | 90.3% | 95% | 0% | -153.3181 | 2558.5533 | -3550 | -400 | -1391.4467 | 34.79% | 89.03% | 95% | 0% | 3085 | -134
[5 empty] | 2019-02-03 | 41 | 812.5 | 2855 | -137 | 1 | 0 | 2992 | 2566.1995 | 2566.1995 | 2566.1995 | 2630.4204 | 780 | 200 | 3610.4204 | 90.26% | 95% | 0% | -156.7506 | 2409.4489 | -3550 | -400 | -1540.5511 | 38.51% | 89.03% | 95% | 0% | 2992 | -137
[5 empty] | 2019-02-03 | 42 | 813 | 2711 | -140 | 1 | 0 | 2851 | 2345.3421 | 2345.3421 | 2345.3421 | 2630.4204 | 780 | 200 | 3610.4204 | 90.26% | 95% | 0% | -160.1831 | 2185.1591 | -3550 | -400 | -1764.8409 | 44.12% | 89.03% | 95% | 0% | 2851 | -140
[5 empty] | 2019-02-03 | 43 | 813.5 | 2575 | -144 | 1 | 0 | 2719 | 2138.582 | 2138.582 | 2138.582 | 2630.4204 | 780 | 200 | 3610.4204 | 90.26% | 95% | 0% | -164.7597 | 1973.8223 | -3550 | -400 | -1976.1777 | 49.4% | 89.03% | 95% | 0% | 2719 | -144
[5 empty] | 2019-02-03 | 44 | 814 | 2403 | -149 | 1 | 0 | 2552 | 1876.9992 | 1876.9992 | 1876.9992 | 2630.4204 | 780 | 200 | 3610.4204 | 90.26% | 95% | 0% | -170.4805 | 1706.5186 | -3550 | -400 | -2243.4814 | 56.09% | 89.02% | 95% | 0% | 2552 | -149
[5 empty] | 2019-02-03 | 45 | 814.5 | 2238 | -154 | 1 | 0 | 2392 | 1626.3809 | 1626.3809 | 1626.3809 | 2630.4204 | 780 | 200 | 3610.4204 | 90.26% | 95% | 0% | -176.2014 | 1450.1795 | -3550 | -400 | -2499.8205 | 62.5% | 89.02% | 95% | 0% | 2392 | -154
[5 empty] | 2019-02-03 | 46 | 815 | 2103 | -158 | 1 | 0 | 2261 | 1421.1871 | 1421.1871 | 1421.1871 | 2630.4204 | 780 | 200 | 3610.4204 | 90.26% | 95% | 0% | -180.778 | 1240.4091 | -3550 | -400 | -2709.5909 | 67.74% | 89.02% | 95% | 0% | 2261 | -158
[5 empty] | 2019-02-03 | 47 | 815.5 | 1938 | -163 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 2630.4204 | 780 | 200 | 3610.4204 | 90.26% | 95% | 0% | -186.4989 | 984.07 | -3550 | -400 | -2965.93 | 74.15% | 89.02% | 95% | 0% | 2101 | -163
[5 empty] | 2019-02-03 | 48 | 816 | 1846 | -167 | 1 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 2630.4204 | 780 | 200 | 3610.4204 | 90.26% | 95% | 0% | -191.0755 | 841.6533 | -3550 | -400 | -3108.3467 | 77.71% | 89.02% | 95% | 0% | 2013 | -167
[5 empty] | 2019-02-04 | 1 | 816.5 | 1823 | -171 | 1 | 0 | 1994 | 1002.9678 | 1002.9678 | 1002.9678 | 2630.4204 | 780 | 200 | 3610.4204 | 90.26% | 95% | 0% | -195.6522 | 807.3157 | -3550 | -400 | -3142.6843 | 78.57% | 89.01% | 95% | 0% | 1994 | -171
[5 empty] | 2019-02-04 | 2 | 817 | 1839 | -174 | 1 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 2628.8541 | 780 | 200 | 3608.8541 | 90.22% | 95% | 0% | -199.0847 | 833.6441 | -3550 | -400 | -3116.3559 | 77.91% | 89.01% | 95% | 0% | 2013 | -174
[5 empty] | 2019-02-04 | 3 | 817.5 | 1810 | -181 | 1 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 2628.8541 | 780 | 200 | 3608.8541 | 90.22% | 95% | 0% | -207.0938 | 791.1749 | -3550 | -400 | -3158.8251 | 78.97% | 89% | 95% | 0% | 1991 | -181
[5 empty] | 2019-02-04 | 4 | 818 | 1760 | -187 | 1 | 0 | 1947 | 929.3487 | 929.3487 | 929.3487 | 2628.8541 | 780 | 200 | 3608.8541 | 90.22% | 95% | 0% | -213.9588 | 715.3899 | -3550 | -400 | -3234.6101 | 80.87% | 88.99% | 95% | 0% | 1947 | -187
[5 empty] | 2019-02-04 | 5 | 818.5 | 1750 | -190 | 1 | 0 | 1940 | 918.3842 | 918.3842 | 918.3842 | 2628.8541 | 780 | 200 | 3608.8541 | 90.22% | 95% | 0% | -217.3913 | 700.9929 | -3550 | -400 | -3249.0071 | 81.23% | 88.99% | 95% | 0% | 1940 | -190
[5 empty] | 2019-02-04 | 6 | 819 | 1728 | -193 | 1 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 2627.2877 | 780 | 200 | 3607.2877 | 90.18% | 95% | 0% | -220.8238 | 667.7994 | -3550 | -400 | -3282.2006 | 82.06% | 88.98% | 95% | 0% | 1921 | -193
[5 empty] | 2019-02-04 | 7 | 819.5 | 1709 | -195 | 1 | 0 | 1904 | 861.9951 | 861.9951 | 861.9951 | 2627.2877 | 780 | 200 | 3607.2877 | 90.18% | 95% | 0% | -223.1121 | 638.8829 | -3550 | -400 | -3311.1171 | 82.78% | 88.97% | 95% | 0% | 1904 | -195
[5 empty] | 2019-02-04 | 8 | 820 | 1673 | -196 | 1 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 2627.2877 | 780 | 200 | 3607.2877 | 90.18% | 95% | 0% | -224.2563 | 582.916 | -3550 | -400 | -3367.084 | 84.18% | 88.96% | 95% | 0% | 1869 | -196
[5 empty] | 2019-02-04 | 9 | 820.5 | 1671 | -195 | 1 | 0 | 1866 | 802.4732 | 802.4732 | 802.4732 | 2627.2877 | 780 | 200 | 3607.2877 | 90.18% | 95% | 0% | -223.1121 | 579.3611 | -3550 | -400 | -3370.6389 | 84.27% | 88.95% | 95% | 0% | 1866 | -195
[5 empty] | 2019-02-04 | 10 | 821 | 1688 | -194 | 1 | 0 | 1882 | 827.535 | 827.535 | 827.535 | 2627.2877 | 780 | 200 | 3607.2877 | 90.18% | 95% | 0% | -221.968 | 605.5671 | -3550 | -400 | -3344.4329 | 83.61% | 88.94% | 95% | 0% | 1882 | -194
[5 empty] | 2019-02-04 | 11 | 821.5 | 1772 | -190 | 1 | 0 | 1962 | 952.8442 | 952.8442 | 952.8442 | 2627.2877 | 780 | 200 | 3607.2877 | 90.18% | 95% | 0% | -217.3913 | 735.4529 | -3550 | -400 | -3214.5471 | 80.36% | 88.94% | 95% | 0% | 1962 | -190
[5 empty] | 2019-02-04 | 12 | 822 | 1890 | -187 | 1 | 0 | 2077 | 1132.9761 | 1132.9761 | 1132.9761 | 2627.2877 | 780 | 200 | 3607.2877 | 90.18% | 95% | 0% | -213.9588 | 919.0173 | -3550 | -400 | -3030.9827 | 75.77% | 88.94% | 95% | 0% | 2077 | -187
[5 empty] | 2019-02-04 | 13 | 822.5 | 2158 | -185 | 1 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 2627.2877 | 780 | 200 | 3607.2877 | 90.18% | 95% | 0% | -211.6705 | 1337.9585 | -3550 | -400 | -2612.0415 | 65.3% | 88.93% | 95% | 0% | 2343 | -185
[5 empty] | 2019-02-04 | 14 | 823 | 2432 | -183 | 1 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 2625.7214 | 780 | 200 | 3605.7214 | 90.14% | 95% | 0% | -209.3822 | 1766.298 | -3550 | -400 | -2183.702 | 54.59% | 88.93% | 95% | 0% | 2615 | -183
[5 empty] | 2019-02-04 | 15 | 823.5 | 2739 | -183 | 1 | 0 | 2922 | 2456.554 | 2456.554 | 2456.554 | 2625.7214 | 780 | 200 | 3605.7214 | 90.14% | 95% | 0% | -209.3822 | 2247.1718 | -3550 | -400 | -1702.8282 | 42.57% | 88.93% | 95% | 0% | 2922 | -183
[5 empty] | 2019-02-04 | 16 | 824 | 2894 | -184 | 1 | 0 | 3078 | 2700.9068 | 2700.9068 | 2700.9068 | 2625.7214 | 780 | 200 | 3605.7214 | 90.14% | 95% | 0% | -210.5263 | 2490.3805 | -3550 | -400 | -1459.6195 | 36.49% | 88.92% | 95% | 0% | 3078 | -184
[5 empty] | 2019-02-04 | 17 | 824.5 | 2990 | -183 | 1 | 0 | 3173 | 2849.7115 | 2849.7115 | 2849.7115 | 2625.7214 | 780 | 200 | 3605.7214 | 90.14% | 95% | 0% | -209.3822 | 2640.3293 | -3550 | -400 | -1309.6707 | 32.74% | 88.91% | 95% | 0% | 3173 | -183
[5 empty] | 2019-02-04 | 18 | 825 | 3003 | -190 | 1 | 0 | 3193 | 2881.0387 | 2881.0387 | 2881.0387 | 2625.7214 | 780 | 200 | 3605.7214 | 90.14% | 95% | 0% | -217.3913 | 2663.6474 | -3550 | -400 | -1286.3526 | 32.16% | 88.9% | 95% | 0% | 3193 | -190
[5 empty] | 2019-02-04 | 19 | 825.5 | 3044 | -206 | 1 | 0 | 3250 | 2970.3215 | 2970.3215 | 2970.3215 | 2625.7214 | 780 | 200 | 3605.7214 | 90.14% | 95% | 0% | -235.6979 | 2734.6236 | -3550 | -400 | -1215.3764 | 30.38% | 88.9% | 95% | 0% | 3250 | -206
[5 empty] | 2019-02-04 | 20 | 826 | 3055 | -221 | 1 | 0 | 3276 | 3011.047 | 3011.047 | 3011.047 | 2625.7214 | 780 | 200 | 3605.7214 | 90.14% | 95% | 0% | -252.8604 | 2758.1866 | -3550 | -400 | -1191.8134 | 29.8% | 88.87% | 95% | 0% | 3276 | -221
[5 empty] | 2019-02-04 | 21 | 826.5 | 3006 | -236 | 1 | 0 | 3242 | 2957.7906 | 2957.7906 | 2957.7906 | 2625.7214 | 780 | 200 | 3605.7214 | 90.14% | 95% | 0% | -270.0229 | 2687.7677 | -3550 | -400 | -1262.2323 | 31.56% | 88.87% | 95% | 0% | 3242 | -236
[5 empty] | 2019-02-04 | 22 | 827 | 2917 | -263 | 1 | 0 | 3180 | 2860.676 | 2860.676 | 2860.676 | 2624.155 | 780 | 200 | 3604.155 | 90.1% | 95% | 0% | -300.9153 | 2559.7607 | -3550 | -400 | -1390.2393 | 34.76% | 88.87% | 95% | 0% | 3180 | -263
[5 empty] | 2019-02-04 | 23 | 827.5 | 2908 | -305 | 1 | 0 | 3213 | 2912.366 | 2912.366 | 2912.366 | 2624.155 | 780 | 200 | 3604.155 | 90.1% | 95% | 0% | -348.9703 | 2563.3958 | -3550 | -400 | -1386.6042 | 34.67% | 88.86% | 95% | 0% | 3213 | -305
[5 empty] | 2019-02-04 | 24 | 828 | 2882 | -328 | 1 | 0 | 3210 | 2907.6669 | 2907.6669 | 2907.6669 | 2624.155 | 780 | 200 | 3604.155 | 90.1% | 95% | 0% | -375.286 | 2532.3809 | -3550 | -400 | -1417.6191 | 35.44% | 88.85% | 95% | 0% | 3210 | -328
[5 empty] | 2019-02-04 | 25 | 828.5 | 2855 | -353 | 1 | 0 | 3208 | 2904.5342 | 2904.5342 | 2904.5342 | 2624.155 | 780 | 200 | 3604.155 | 90.1% | 95% | 0% | -403.8902 | 2500.6441 | -3550 | -400 | -1449.3559 | 36.23% | 88.85% | 95% | 0% | 3208 | -353
[5 empty] | 2019-02-04 | 26 | 829 | 2786 | -382 | 1 | 0 | 3168 | 2841.8796 | 2841.8796 | 2841.8796 | 2624.155 | 780 | 200 | 3604.155 | 90.1% | 95% | 0% | -437.0709 | 2404.8087 | -3550 | -400 | -1545.1913 | 38.63% | 88.84% | 95% | 0% | 3168 | -382
[5 empty] | 2019-02-04 | 27 | 829.5 | 2741 | -385 | 1 | 0 | 3126 | 2776.0923 | 2776.0923 | 2776.0923 | 2624.155 | 780 | 200 | 3604.155 | 90.1% | 95% | 0% | -440.5034 | 2335.5889 | -3550 | -400 | -1614.4111 | 40.36% | 88.83% | 95% | 0% | 3126 | -385
[5 empty] | 2019-02-04 | 28 | 830 | 2718 | -363 | 1 | 0 | 3081 | 2705.6059 | 2705.6059 | 2705.6059 | 2622.5886 | 780 | 200 | 3602.5886 | 90.06% | 95% | 0% | -415.3318 | 2290.2741 | -3550 | -400 | -1659.7259 | 41.49% | 88.82% | 95% | 0% | 3081 | -363
[5 empty] | 2019-02-04 | 29 | 830.5 | 2764 | -329 | 1 | 0 | 3093 | 2724.4023 | 2724.4023 | 2724.4023 | 2622.5886 | 780 | 200 | 3602.5886 | 90.06% | 95% | 0% | -376.4302 | 2347.9721 | -3550 | -400 | -1602.0279 | 40.05% | 88.8% | 95% | 0% | 3093 | -329
[5 empty] | 2019-02-04 | 30 | 831 | 2783 | -296 | 1 | 0 | 3079 | 2702.4732 | 2702.4732 | 2702.4732 | 2622.5886 | 780 | 200 | 3602.5886 | 90.06% | 95% | 0% | -338.6728 | 2363.8004 | -3550 | -400 | -1586.1996 | 39.65% | 88.8% | 95% | 0% | 3079 | -296
[5 empty] | 2019-02-04 | 31 | 831.5 | 2865 | -247 | 1 | 0 | 3112 | 2754.1632 | 2754.1632 | 2754.1632 | 2622.5886 | 780 | 200 | 3602.5886 | 90.06% | 95% | 0% | -282.6087 | 2471.5545 | -3550 | -400 | -1478.4455 | 36.96% | 88.8% | 95% | 0% | 3112 | -247
[5 empty] | 2019-02-04 | 32 | 832 | 2993 | -201 | 1 | 0 | 3194 | 2882.6051 | 2882.6051 | 2882.6051 | 2622.5886 | 780 | 200 | 3602.5886 | 90.06% | 95% | 0% | -229.9771 | 2652.628 | -3550 | -400 | -1297.372 | 32.43% | 88.8% | 95% | 0% | 3194 | -201
[5 empty] | 2019-02-04 | 33 | 832.5 | 3156 | -150 | 1 | 0 | 3306 | 3058.0379 | 3058.0379 | 3058.0379 | 2622.5886 | 780 | 200 | 3602.5886 | 90.06% | 95% | 0% | -171.6247 | 2886.4132 | -3550 | -400 | -1063.5868 | 26.59% | 88.79% | 95% | 0% | 3306 | -150
[5 empty] | 2019-02-04 | 34 | 833 | 3276 | -106 | 1 | 0 | 3382 | 3177.0816 | 3177.0816 | 3177.0816 | 2622.5886 | 780 | 200 | 3602.5886 | 90.06% | 95% | 0% | -121.2815 | 3055.8002 | -3550 | -400 | -894.1998 | 22.35% | 88.79% | 95% | 0% | 3382 | -106
[5 empty] | 2019-02-04 | 35 | 833.5 | 3340 | -94 | 1 | 0 | 3434 | 3258.5326 | 3258.5326 | 3258.5326 | 2621.0223 | 780 | 200 | 3601.0223 | 90.03% | 95% | 0% | -107.5515 | 3150.9811 | -3550 | -400 | -799.0189 | 19.98% | 88.79% | 95% | 0% | 3434 | -94
[5 empty] | 2019-02-04 | 36 | 834 | 3397 | -91 | 1 | 0 | 3488 | 3343.1162 | 3343.1162 | 3343.1162 | 2621.0223 | 780 | 200 | 3601.0223 | 90.03% | 95% | 0% | -104.119 | 3238.9972 | -3550 | -400 | -711.0028 | 17.78% | 88.79% | 95% | 0% | 3488 | -91
[5 empty] | 2019-02-04 | 37 | 834.5 | 3398 | -87 | 1 | 0 | 3485 | 3338.4171 | 3338.4171 | 3338.4171 | 2621.0223 | 780 | 200 | 3601.0223 | 90.03% | 95% | 0% | -99.5423 | 3238.8748 | -3550 | -400 | -711.1252 | 17.78% | 88.79% | 95% | 0% | 3485 | -87
[5 empty] | 2019-02-04 | 38 | 835 | 3375 | -83 | 1 | 0 | 3458 | 3296.1253 | 3296.1253 | 3296.1253 | 2621.0223 | 780 | 200 | 3601.0223 | 90.03% | 95% | 0% | -94.9657 | 3201.1596 | -3550 | -400 | -748.8404 | 18.72% | 88.78% | 95% | 0% | 3458 | -83
[5 empty] | 2019-02-04 | 39 | 835.5 | 3351 | -80 | 1 | 0 | 3431 | 3253.8335 | 3253.8335 | 3253.8335 | 2621.0223 | 780 | 200 | 3601.0223 | 90.03% | 95% | 0% | -91.5332 | 3162.3003 | -3550 | -400 | -787.6997 | 19.69% | 88.77% | 95% | 0% | 3431 | -80
[5 empty] | 2019-02-04 | 40 | 836 | 3332 | -77 | 1 | 0 | 3409 | 3219.3735 | 3219.3735 | 3219.3735 | 2621.0223 | 780 | 200 | 3601.0223 | 90.03% | 95% | 0% | -88.1007 | 3131.2728 | -3550 | -400 | -818.7272 | 20.47% | 88.77% | 95% | 0% | 3409 | -77
[5 empty] | 2019-02-04 | 41 | 836.5 | 3248 | -75 | 1 | 0 | 3323 | 3084.6661 | 3084.6661 | 3084.6661 | 2621.0223 | 780 | 200 | 3601.0223 | 90.03% | 95% | 0% | -85.8124 | 2998.8538 | -3550 | -400 | -951.1462 | 23.78% | 88.76% | 95% | 0% | 3323 | -75
[5 empty] | 2019-02-04 | 42 | 837 | 3126 | -72 | 1 | 0 | 3198 | 2888.8706 | 2888.8706 | 2888.8706 | 2621.0223 | 780 | 200 | 3601.0223 | 90.03% | 95% | 0% | -82.3799 | 2806.4907 | -3550 | -400 | -1143.5093 | 28.59% | 88.76% | 95% | 0% | 3198 | -72
[5 empty] | 2019-02-04 | 43 | 837.5 | 2982 | -69 | 1 | 0 | 3051 | 2658.615 | 2658.615 | 2658.615 | 2619.4559 | 780 | 200 | 3599.4559 | 89.99% | 95% | 0% | -78.9474 | 2579.6676 | -3550 | -400 | -1370.3324 | 34.26% | 88.75% | 95% | 0% | 3051 | -69
[5 empty] | 2019-02-04 | 44 | 838 | 2821 | -67 | 1 | 0 | 2888 | 2403.2976 | 2403.2976 | 2403.2976 | 2617.8895 | 780 | 200 | 3597.8895 | 89.95% | 95% | 0% | -76.659 | 2326.6386 | -3550 | -400 | -1623.3614 | 40.58% | 88.74% | 95% | 0% | 2888 | -67
[5 empty] | 2019-02-04 | 45 | 838.5 | 2660 | -63 | 1 | 0 | 2723 | 2144.8475 | 2144.8475 | 2144.8475 | 2617.8895 | 780 | 200 | 3597.8895 | 89.95% | 95% | 0% | -72.0824 | 2072.7651 | -3550 | -400 | -1877.2349 | 46.93% | 88.74% | 95% | 0% | 2723 | -63
[5 empty] | 2019-02-04 | 46 | 839 | 2507 | -60 | 1 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 2617.8895 | 780 | 200 | 3597.8895 | 89.95% | 95% | 0% | -68.6499 | 1831.8448 | -3550 | -400 | -2118.1552 | 52.95% | 88.72% | 95% | 0% | 2567 | -60
[5 empty] | 2019-02-04 | 47 | 839.5 | 2346 | -54 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 2617.8895 | 780 | 200 | 3597.8895 | 89.95% | 95% | 0% | -61.7849 | 1577.1269 | -3550 | -400 | -2372.8731 | 59.32% | 88.71% | 95% | 0% | 2400 | -54
[5 empty] | 2019-02-04 | 48 | 840 | 2264 | -48 | 1 | 0 | 2312 | 1501.0717 | 1501.0717 | 1501.0717 | 2617.8895 | 780 | 200 | 3597.8895 | 89.95% | 95% | 0% | -54.9199 | 1446.1518 | -3550 | -400 | -2503.8482 | 62.6% | 88.71% | 95% | 0% | 2312 | -48
[5 empty] | 2019-02-05 | 1 | 840.5 | 2250 | -46 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 2617.8895 | 780 | 200 | 3597.8895 | 89.95% | 95% | 0% | -52.6316 | 1423.3783 | -3550 | -400 | -2526.6217 | 63.17% | 88.7% | 95% | 0% | 2296 | -46
[5 empty] | 2019-02-05 | 2 | 841 | 2282 | -44 | 1 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 2616.3232 | 780 | 200 | 3596.3232 | 89.91% | 95% | 0% | -50.3432 | 1472.6576 | -3550 | -400 | -2477.3424 | 61.93% | 88.7% | 95% | 0% | 2326 | -44
[5 empty] | 2019-02-05 | 3 | 841.5 | 2270 | -44 | 1 | 0 | 2314 | 1504.2045 | 1504.2045 | 1504.2045 | 2616.3232 | 780 | 200 | 3596.3232 | 89.91% | 95% | 0% | -50.3432 | 1453.8612 | -3550 | -400 | -2496.1388 | 62.4% | 88.69% | 95% | 0% | 2314 | -44
[5 empty] | 2019-02-05 | 4 | 842 | 2232 | -43 | 1 | 0 | 2275 | 1443.1162 | 1443.1162 | 1443.1162 | 2616.3232 | 780 | 200 | 3596.3232 | 89.91% | 95% | 0% | -49.1991 | 1393.9172 | -3550 | -400 | -2556.0828 | 63.9% | 88.69% | 95% | 0% | 2275 | -43
[5 empty] | 2019-02-05 | 5 | 842.5 | 2205 | -43 | 1 | 0 | 2248 | 1400.8244 | 1400.8244 | 1400.8244 | 2616.3232 | 780 | 200 | 3596.3232 | 89.91% | 95% | 0% | -49.1991 | 1351.6253 | -3550 | -400 | -2598.3747 | 64.96% | 88.68% | 95% | 0% | 2248 | -43
[5 empty] | 2019-02-05 | 6 | 843 | 2195 | -43 | 1 | 0 | 2238 | 1385.1608 | 1385.1608 | 1385.1608 | 2616.3232 | 780 | 200 | 3596.3232 | 89.91% | 95% | 0% | -49.1991 | 1335.9617 | -3550 | -400 | -2614.0383 | 65.35% | 88.68% | 95% | 0% | 2238 | -43
[5 empty] | 2019-02-05 | 7 | 843.5 | 2163 | -45 | 1 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 2616.3232 | 780 | 200 | 3596.3232 | 89.91% | 95% | 0% | -51.4874 | 1286.6824 | -3550 | -400 | -2663.3176 | 66.58% | 88.67% | 95% | 0% | 2208 | -45
[5 empty] | 2019-02-05 | 8 | 844 | 2132 | -46 | 1 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 2616.3232 | 780 | 200 | 3596.3232 | 89.91% | 95% | 0% | -52.6316 | 1238.5473 | -3550 | -400 | -2711.4527 | 67.79% | 88.67% | 95% | 0% | 2178 | -46
[5 empty] | 2019-02-05 | 9 | 844.5 | 2123 | -48 | 1 | 0 | 2171 | 1280.2143 | 1280.2143 | 1280.2143 | 2616.3232 | 780 | 200 | 3596.3232 | 89.91% | 95% | 0% | -54.9199 | 1225.2944 | -3550 | -400 | -2724.7056 | 68.12% | 88.66% | 95% | 0% | 2171 | -48
[5 empty] | 2019-02-05 | 10 | 845 | 2138 | -49 | 1 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 2614.7568 | 780 | 200 | 3594.7568 | 89.87% | 95% | 0% | -56.0641 | 1249.2121 | -3550 | -400 | -2700.7879 | 67.52% | 88.66% | 95% | 0% | 2187 | -49
[5 empty] | 2019-02-05 | 11 | 845.5 | 2192 | -51 | 1 | 0 | 2243 | 1392.9926 | 1392.9926 | 1392.9926 | 2614.7568 | 780 | 200 | 3594.7568 | 89.87% | 95% | 0% | -58.3524 | 1334.6402 | -3550 | -400 | -2615.3598 | 65.38% | 88.65% | 95% | 0% | 2243 | -51
[5 empty] | 2019-02-05 | 12 | 846 | 2291 | -53 | 1 | 0 | 2344 | 1551.1954 | 1551.1954 | 1551.1954 | 2614.7568 | 780 | 200 | 3594.7568 | 89.87% | 95% | 0% | -60.6407 | 1490.5547 | -3550 | -400 | -2459.4453 | 61.49% | 88.63% | 95% | 0% | 2344 | -53
[5 empty] | 2019-02-05 | 13 | 846.5 | 2550 | -54 | 1 | 0 | 2604 | 1958.4501 | 1958.4501 | 1958.4501 | 2614.7568 | 780 | 200 | 3594.7568 | 89.87% | 95% | 0% | -61.7849 | 1896.6652 | -3550 | -400 | -2053.3348 | 51.33% | 88.62% | 95% | 0% | 2604 | -54
[5 empty] | 2019-02-05 | 14 | 847 | 2784 | -56 | 1 | 0 | 2840 | 2328.1121 | 2328.1121 | 2328.1121 | 2614.7568 | 780 | 200 | 3594.7568 | 89.87% | 95% | 0% | -64.0732 | 2264.0389 | -3550 | -400 | -1685.9611 | 42.15% | 88.61% | 95% | 0% | 2840 | -56
[5 empty] | 2019-02-05 | 15 | 847.5 | 3091 | -60 | 1 | 0 | 3151 | 2815.2514 | 2815.2514 | 2815.2514 | 2614.7568 | 780 | 200 | 3594.7568 | 89.87% | 95% | 0% | -68.6499 | 2746.6016 | -3550 | -400 | -1203.3984 | 30.08% | 88.61% | 95% | 0% | 3151 | -60
[5 empty] | 2019-02-05 | 16 | 848 | 3186 | -64 | 1 | 0 | 3250 | 2970.3215 | 2970.3215 | 2970.3215 | 2614.7568 | 780 | 200 | 3594.7568 | 89.87% | 95% | 0% | -73.2265 | 2897.095 | -3550 | -400 | -1052.905 | 26.32% | 88.61% | 95% | 0% | 3250 | -64
[5 empty] | 2019-02-05 | 17 | 848.5 | 3237 | -77 | 1 | 0 | 3314 | 3070.5688 | 3070.5688 | 3070.5688 | 2614.7568 | 780 | 200 | 3594.7568 | 89.87% | 95% | 0% | -88.1007 | 2982.4682 | -3550 | -400 | -967.5318 | 24.19% | 88.61% | 95% | 0% | 3314 | -77
[5 empty] | 2019-02-05 | 18 | 849 | 3225 | -99 | 1 | 0 | 3324 | 3086.2325 | 3086.2325 | 3086.2325 | 2614.7568 | 780 | 200 | 3594.7568 | 89.87% | 95% | 0% | -113.2723 | 2972.9602 | -3550 | -400 | -977.0398 | 24.43% | 88.6% | 95% | 0% | 3324 | -99
[5 empty] | 2019-02-05 | 19 | 849.5 | 3228 | -123 | 1 | 0 | 3351 | 3128.5243 | 3128.5243 | 3128.5243 | 2614.7568 | 780 | 200 | 3594.7568 | 89.87% | 95% | 0% | -140.7323 | 2987.7921 | -3550 | -400 | -962.2079 | 24.06% | 88.58% | 95% | 0% | 3351 | -123
[5 empty] | 2019-02-05 | 20 | 850 | 3195 | -143 | 1 | 0 | 3338 | 3108.1616 | 3108.1616 | 3108.1616 | 2613.1904 | 780 | 200 | 3593.1904 | 89.83% | 95% | 0% | -163.6156 | 2944.546 | -3550 | -400 | -1005.454 | 25.14% | 88.58% | 95% | 0% | 3338 | -143
[5 empty] | 2019-02-05 | 21 | 850.5 | 3148 | -161 | 1 | 0 | 3309 | 3062.737 | 3062.737 | 3062.737 | 2613.1904 | 780 | 200 | 3593.1904 | 89.83% | 95% | 0% | -184.2105 | 2878.5265 | -3550 | -400 | -1071.4735 | 26.79% | 88.58% | 95% | 0% | 3309 | -161
[5 empty] | 2019-02-05 | 22 | 851 | 3118 | -179 | 1 | 0 | 3297 | 3043.9406 | 3043.9406 | 3043.9406 | 2613.1904 | 780 | 200 | 3593.1904 | 89.83% | 95% | 0% | -204.8055 | 2839.1352 | -3550 | -400 | -1110.8648 | 27.77% | 88.58% | 95% | 0% | 3297 | -179
[5 empty] | 2019-02-05 | 23 | 851.5 | 3091 | -192 | 1 | 0 | 3283 | 3022.0115 | 3022.0115 | 3022.0115 | 2613.1904 | 780 | 200 | 3593.1904 | 89.83% | 95% | 0% | -219.6796 | 2802.3319 | -3550 | -400 | -1147.6681 | 28.69% | 88.57% | 95% | 0% | 3283 | -192
[5 empty] | 2019-02-05 | 24 | 852 | 3088 | -197 | 1 | 0 | 3285 | 3025.1443 | 3025.1443 | 3025.1443 | 2613.1904 | 780 | 200 | 3593.1904 | 89.83% | 95% | 0% | -225.4005 | 2799.7438 | -3550 | -400 | -1150.2562 | 28.76% | 88.56% | 95% | 0% | 3285 | -197
[5 empty] | 2019-02-05 | 25 | 852.5 | 3107 | -201 | 1 | 0 | 3308 | 3061.1707 | 3061.1707 | 3061.1707 | 2613.1904 | 780 | 200 | 3593.1904 | 89.83% | 95% | 0% | -229.9771 | 2831.1935 | -3550 | -400 | -1118.8065 | 27.97% | 88.56% | 95% | 0% | 3308 | -201
[5 empty] | 2019-02-05 | 26 | 853 | 3124 | -198 | 1 | 0 | 3322 | 3083.0998 | 3083.0998 | 3083.0998 | 2613.1904 | 780 | 200 | 3593.1904 | 89.83% | 95% | 0% | -226.5446 | 2856.5551 | -3550 | -400 | -1093.4449 | 27.34% | 88.55% | 95% | 0% | 3322 | -198
[5 empty] | 2019-02-05 | 27 | 853.5 | 3123 | -191 | 1 | 0 | 3314 | 3070.5688 | 3070.5688 | 3070.5688 | 2611.6241 | 780 | 200 | 3591.6241 | 89.79% | 95% | 0% | -218.5355 | 2852.0334 | -3550 | -400 | -1097.9666 | 27.45% | 88.54% | 95% | 0% | 3314 | -191
[5 empty] | 2019-02-05 | 28 | 854 | 3127 | -184 | 1 | 0 | 3311 | 3065.8697 | 3065.8697 | 3065.8697 | 2611.6241 | 780 | 200 | 3591.6241 | 89.79% | 95% | 0% | -210.5263 | 2855.3434 | -3550 | -400 | -1094.6566 | 27.37% | 88.53% | 95% | 0% | 3311 | -184
[5 empty] | 2019-02-05 | 29 | 854.5 | 3135 | -179 | 1 | 0 | 3314 | 3070.5688 | 3070.5688 | 3070.5688 | 2611.6241 | 780 | 200 | 3591.6241 | 89.79% | 95% | 0% | -204.8055 | 2865.7633 | -3550 | -400 | -1084.2367 | 27.11% | 88.51% | 95% | 0% | 3314 | -179
[5 empty] | 2019-02-05 | 30 | 855 | 3121 | -175 | 1 | 0 | 3296 | 3042.3743 | 3042.3743 | 3042.3743 | 2611.6241 | 780 | 200 | 3591.6241 | 89.79% | 95% | 0% | -200.2288 | 2842.1454 | -3550 | -400 | -1107.8546 | 27.7% | 88.5% | 95% | 0% | 3296 | -175
[5 empty] | 2019-02-05 | 31 | 855.5 | 3124 | -170 | 1 | 0 | 3294 | 3039.2415 | 3039.2415 | 3039.2415 | 2611.6241 | 780 | 200 | 3591.6241 | 89.79% | 95% | 0% | -194.508 | 2844.7335 | -3550 | -400 | -1105.2665 | 27.63% | 88.49% | 95% | 0% | 3294 | -170
[5 empty] | 2019-02-05 | 32 | 856 | 3182 | -167 | 1 | 0 | 3349 | 3125.3916 | 3125.3916 | 3125.3916 | 2611.6241 | 780 | 200 | 3591.6241 | 89.79% | 95% | 0% | -191.0755 | 2934.3161 | -3550 | -400 | -1015.6839 | 25.39% | 88.49% | 95% | 0% | 3349 | -167
[5 empty] | 2019-02-05 | 33 | 856.5 | 3245 | -164 | 1 | 0 | 3409 | 3219.3735 | 3219.3735 | 3219.3735 | 2611.6241 | 780 | 200 | 3591.6241 | 89.79% | 95% | 0% | -187.643 | 3031.7304 | -3550 | -400 | -918.2696 | 22.96% | 88.49% | 95% | 0% | 3409 | -164
[5 empty] | 2019-02-05 | 34 | 857 | 3320 | -164 | 1 | 0 | 3484 | 3336.8508 | 3336.8508 | 3336.8508 | 2611.6241 | 780 | 200 | 3591.6241 | 89.79% | 95% | 0% | -187.643 | 3149.2078 | -3550 | -400 | -800.7922 | 20.02% | 88.48% | 95% | 0% | 3484 | -164
[5 empty] | 2019-02-05 | 35 | 857.5 | 3350 | -165 | 1 | 0 | 3515 | 3385.4081 | 3385.4081 | 3385.4081 | 2611.6241 | 780 | 200 | 3591.6241 | 89.79% | 95% | 0% | -188.7872 | 3196.6209 | -3550 | -400 | -753.3791 | 18.83% | 88.47% | 95% | 0% | 3515 | -165
[5 empty] | 2019-02-05 | 36 | 858 | 3302 | -166 | 1 | 0 | 3468 | 3311.789 | 3311.789 | 3311.789 | 2611.6241 | 780 | 200 | 3591.6241 | 89.79% | 95% | 0% | -189.9314 | 3121.8576 | -3550 | -400 | -828.1424 | 20.7% | 88.47% | 95% | 0% | 3468 | -166
[5 empty] | 2019-02-05 | 37 | 858.5 | 3272 | -167 | 1 | 0 | 3439 | 3266.3644 | 3266.3644 | 3266.3644 | 2610.0577 | 780 | 200 | 3590.0577 | 89.75% | 95% | 0% | -191.0755 | 3075.2889 | -3550 | -400 | -874.7111 | 21.87% | 88.46% | 95% | 0% | 3439 | -167
[5 empty] | 2019-02-05 | 38 | 859 | 3260 | -167 | 1 | 0 | 3427 | 3247.568 | 3247.568 | 3247.568 | 2610.0577 | 780 | 200 | 3590.0577 | 89.75% | 95% | 0% | -191.0755 | 3056.4925 | -3550 | -400 | -893.5075 | 22.34% | 88.45% | 95% | 0% | 3427 | -167
[5 empty] | 2019-02-05 | 39 | 859.5 | 3212 | -169 | 1 | 0 | 3381 | 3175.5153 | 3175.5153 | 3175.5153 | 2610.0577 | 780 | 200 | 3590.0577 | 89.75% | 95% | 0% | -193.3638 | 2982.1514 | -3550 | -400 | -967.8486 | 24.2% | 88.45% | 95% | 0% | 3381 | -169
[5 empty] | 2019-02-05 | 40 | 860 | 3121 | -171 | 1 | 0 | 3292 | 3036.1088 | 3036.1088 | 3036.1088 | 2610.0577 | 780 | 200 | 3590.0577 | 89.75% | 95% | 0% | -195.6522 | 2840.4566 | -3550 | -400 | -1109.5434 | 27.74% | 88.44% | 95% | 0% | 3292 | -171
[5 empty] | 2019-02-05 | 41 | 860.5 | 2999 | -170 | 1 | 0 | 3169 | 2843.446 | 2843.446 | 2843.446 | 2610.0577 | 780 | 200 | 3590.0577 | 89.75% | 95% | 0% | -194.508 | 2648.938 | -3550 | -400 | -1301.062 | 32.53% | 88.43% | 95% | 0% | 3169 | -170
[5 empty] | 2019-02-05 | 42 | 861 | 2852 | -169 | 1 | 0 | 3021 | 2611.6241 | 2611.6241 | 2611.6241 | 2610.0577 | 780 | 200 | 3590.0577 | 89.75% | 95% | 0% | -193.3638 | 2418.2602 | -3550 | -400 | -1531.7398 | 38.29% | 88.43% | 95% | 0% | 3021 | -169
[5 empty] | 2019-02-05 | 43 | 861.5 | 2695 | -167 | 1 | 0 | 2862 | 2362.5721 | 2362.5721 | 2362.5721 | 2610.0577 | 780 | 200 | 3590.0577 | 89.75% | 95% | 0% | -191.0755 | 2171.4966 | -3550 | -400 | -1778.5034 | 44.46% | 88.42% | 95% | 0% | 2862 | -167
[5 empty] | 2019-02-05 | 44 | 862 | 2535 | -164 | 1 | 0 | 2699 | 2107.2547 | 2107.2547 | 2107.2547 | 2610.0577 | 780 | 200 | 3590.0577 | 89.75% | 95% | 0% | -187.643 | 1919.6117 | -3550 | -400 | -2030.3883 | 50.76% | 88.41% | 95% | 0% | 2699 | -164
[5 empty] | 2019-02-05 | 45 | 862.5 | 2372 | -159 | 1 | 0 | 2531 | 1844.1055 | 1844.1055 | 1844.1055 | 2610.0577 | 780 | 200 | 3590.0577 | 89.75% | 95% | 0% | -181.9222 | 1662.1833 | -3550 | -400 | -2287.8167 | 57.2% | 88.4% | 95% | 0% | 2531 | -159
[5 empty] | 2019-02-05 | 46 | 863 | 2226 | -155 | 1 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 2610.0577 | 780 | 200 | 3590.0577 | 89.75% | 95% | 0% | -177.3455 | 1431.8053 | -3550 | -400 | -2518.1947 | 62.95% | 88.39% | 95% | 0% | 2381 | -155
[5 empty] | 2019-02-05 | 47 | 863.5 | 2072 | -153 | 1 | 0 | 2225 | 1364.798 | 1364.798 | 1364.798 | 2610.0577 | 780 | 200 | 3590.0577 | 89.75% | 95% | 0% | -175.0572 | 1189.7408 | -3550 | -400 | -2760.2592 | 69.01% | 88.38% | 95% | 0% | 2225 | -153
[5 empty] | 2019-02-05 | 48 | 864 | 1964 | -151 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 2608.4913 | 780 | 200 | 3588.4913 | 89.71% | 95% | 0% | -172.7689 | 1019.7291 | -3550 | -400 | -2930.2709 | 73.26% | 88.38% | 95% | 0% | 2115 | -151
[5 empty] | 2019-02-06 | 1 | 864.5 | 1952 | -147 | 1 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 2608.4913 | 780 | 200 | 3588.4913 | 89.71% | 95% | 0% | -168.1922 | 999.2439 | -3550 | -400 | -2950.7561 | 73.77% | 88.37% | 95% | 0% | 2099 | -147
[5 empty] | 2019-02-06 | 2 | 865 | 1985 | -144 | 1 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 2608.4913 | 780 | 200 | 3588.4913 | 89.71% | 95% | 0% | -164.7597 | 1049.6673 | -3550 | -400 | -2900.3327 | 72.51% | 88.37% | 95% | 0% | 2129 | -144
[5 empty] | 2019-02-06 | 3 | 865.5 | 1982 | -140 | 1 | 0 | 2122 | 1203.4625 | 1203.4625 | 1203.4625 | 2608.4913 | 780 | 200 | 3588.4913 | 89.71% | 95% | 0% | -160.1831 | 1043.2794 | -3550 | -400 | -2906.7206 | 72.67% | 88.37% | 95% | 0% | 2122 | -140
[5 empty] | 2019-02-06 | 4 | 866 | 1948 | -136 | 1 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 2608.4913 | 780 | 200 | 3588.4913 | 89.71% | 95% | 0% | -155.6064 | 988.3342 | -3550 | -400 | -2961.6658 | 74.04% | 88.37% | 95% | 0% | 2084 | -136
[5 empty] | 2019-02-06 | 5 | 866.5 | 1925 | -134 | 1 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 2608.4913 | 780 | 200 | 3588.4913 | 89.71% | 95% | 0% | -153.3181 | 951.4635 | -3550 | -400 | -2998.5365 | 74.96% | 88.36% | 95% | 0% | 2059 | -134
[5 empty] | 2019-02-06 | 6 | 867 | 1920 | -132 | 1 | 0 | 2052 | 1093.817 | 1093.817 | 1093.817 | 2608.4913 | 780 | 200 | 3588.4913 | 89.71% | 95% | 0% | -151.0297 | 942.7872 | -3550 | -400 | -3007.2128 | 75.18% | 88.36% | 95% | 0% | 2052 | -132
[5 empty] | 2019-02-06 | 7 | 867.5 | 1910 | -127 | 1 | 0 | 2037 | 1070.3215 | 1070.3215 | 1070.3215 | 2606.925 | 780 | 200 | 3586.925 | 89.67% | 95% | 0% | -145.3089 | 925.0126 | -3550 | -400 | -3024.9874 | 75.62% | 88.35% | 95% | 0% | 2037 | -127
[5 empty] | 2019-02-06 | 8 | 868 | 1896 | -123 | 1 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 2606.925 | 780 | 200 | 3586.925 | 89.67% | 95% | 0% | -140.7323 | 901.3947 | -3550 | -400 | -3048.6053 | 76.22% | 88.35% | 95% | 0% | 2019 | -123
[5 empty] | 2019-02-06 | 9 | 868.5 | 1899 | -120 | 1 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 2606.925 | 780 | 200 | 3586.925 | 89.67% | 95% | 0% | -137.2998 | 904.8272 | -3550 | -400 | -3045.1728 | 76.13% | 88.34% | 95% | 0% | 2019 | -120
[5 empty] | 2019-02-06 | 10 | 869 | 1909 | -118 | 1 | 0 | 2027 | 1054.6579 | 1054.6579 | 1054.6579 | 2606.925 | 780 | 200 | 3586.925 | 89.67% | 95% | 0% | -135.0114 | 919.6464 | -3550 | -400 | -3030.3536 | 75.76% | 88.33% | 95% | 0% | 2027 | -118
[5 empty] | 2019-02-06 | 11 | 869.5 | 1990 | -116 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 2606.925 | 780 | 200 | 3586.925 | 89.67% | 95% | 0% | -132.7231 | 1045.6775 | -3550 | -400 | -2904.3225 | 72.61% | 88.32% | 95% | 0% | 2106 | -116
[5 empty] | 2019-02-06 | 12 | 870 | 2084 | -114 | 1 | 0 | 2198 | 1322.5062 | 1322.5062 | 1322.5062 | 2606.925 | 780 | 200 | 3586.925 | 89.67% | 95% | 0% | -130.4348 | 1192.0714 | -3550 | -400 | -2757.9286 | 68.95% | 88.32% | 95% | 0% | 2198 | -114
[5 empty] | 2019-02-06 | 13 | 870.5 | 2358 | -112 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 2606.925 | 780 | 200 | 3586.925 | 89.67% | 95% | 0% | -128.1465 | 1620.4108 | -3550 | -400 | -2329.5892 | 58.24% | 88.31% | 95% | 0% | 2470 | -112
[5 empty] | 2019-02-06 | 14 | 871 | 2626 | -110 | 1 | 0 | 2736 | 2165.2102 | 2165.2102 | 2165.2102 | 2606.925 | 780 | 200 | 3586.925 | 89.67% | 95% | 0% | -125.8581 | 2039.3521 | -3550 | -400 | -1910.6479 | 47.77% | 88.31% | 95% | 0% | 2736 | -110
[5 empty] | 2019-02-06 | 15 | 871.5 | 2921 | -109 | 1 | 0 | 3030 | 2625.7214 | 2625.7214 | 2625.7214 | 2606.925 | 780 | 200 | 3586.925 | 89.67% | 95% | 0% | -124.714 | 2501.0074 | -3550 | -400 | -1448.9926 | 36.22% | 88.3% | 95% | 0% | 3030 | -109
[5 empty] | 2019-02-06 | 16 | 872 | 3011 | -108 | 1 | 0 | 3119 | 2765.1278 | 2765.1278 | 2765.1278 | 2605.3586 | 780 | 200 | 3585.3586 | 89.63% | 95% | 0% | -123.5698 | 2641.558 | -3550 | -400 | -1308.442 | 32.71% | 88.3% | 95% | 0% | 3119 | -108
[5 empty] | 2019-02-06 | 17 | 872.5 | 3050 | -123 | 1 | 0 | 3173 | 2849.7115 | 2849.7115 | 2849.7115 | 2605.3586 | 780 | 200 | 3585.3586 | 89.63% | 95% | 0% | -140.7323 | 2708.9792 | -3550 | -400 | -1241.0208 | 31.03% | 88.3% | 95% | 0% | 3173 | -123
[5 empty] | 2019-02-06 | 18 | 873 | 3000 | -152 | 1 | 0 | 3152 | 2816.8178 | 2816.8178 | 2816.8178 | 2605.3586 | 780 | 200 | 3585.3586 | 89.63% | 95% | 0% | -173.913 | 2642.9048 | -3550 | -400 | -1307.0952 | 32.68% | 88.3% | 95% | 0% | 3152 | -152
[5 empty] | 2019-02-06 | 19 | 873.5 | 2999 | -188 | 1 | 0 | 3187 | 2871.6406 | 2871.6406 | 2871.6406 | 2605.3586 | 780 | 200 | 3585.3586 | 89.63% | 95% | 0% | -215.103 | 2656.5376 | -3550 | -400 | -1293.4624 | 32.34% | 88.29% | 95% | 0% | 3187 | -188
[5 empty] | 2019-02-06 | 20 | 874 | 2938 | -224 | 1 | 0 | 3162 | 2832.4815 | 2832.4815 | 2832.4815 | 2605.3586 | 780 | 200 | 3585.3586 | 89.63% | 95% | 0% | -256.2929 | 2576.1885 | -3550 | -400 | -1373.8115 | 34.35% | 88.28% | 95% | 0% | 3162 | -224
[5 empty] | 2019-02-06 | 21 | 874.5 | 2836 | -263 | 1 | 0 | 3099 | 2733.8005 | 2733.8005 | 2733.8005 | 2605.3586 | 780 | 200 | 3585.3586 | 89.63% | 95% | 0% | -300.9153 | 2432.8852 | -3550 | -400 | -1517.1148 | 37.93% | 88.28% | 95% | 0% | 3099 | -263
[5 empty] | 2019-02-06 | 22 | 875 | 2729 | -309 | 1 | 0 | 3038 | 2638.2523 | 2638.2523 | 2638.2523 | 2605.3586 | 780 | 200 | 3585.3586 | 89.63% | 95% | 0% | -353.5469 | 2284.7054 | -3550 | -400 | -1665.2946 | 41.63% | 88.28% | 95% | 0% | 3038 | -309
[5 empty] | 2019-02-06 | 23 | 875.5 | 2647 | -364 | 1 | 0 | 3011 | 2595.9604 | 2595.9604 | 2595.9604 | 2603.7923 | 780 | 200 | 3583.7923 | 89.59% | 95% | 0% | -416.476 | 2179.4845 | -3550 | -400 | -1770.5155 | 44.26% | 88.28% | 95% | 0% | 3011 | -364
[5 empty] | 2019-02-06 | 24 | 876 | 2603 | -391 | 1 | 0 | 2994 | 2569.3322 | 2569.3322 | 2569.3322 | 2603.7923 | 780 | 200 | 3583.7923 | 89.59% | 95% | 0% | -447.3684 | 2121.9638 | -3550 | -400 | -1828.0362 | 45.7% | 88.28% | 95% | 0% | 2994 | -391
[5 empty] | 2019-02-06 | 25 | 876.5 | 2647 | -376 | 1 | 0 | 3023 | 2614.7568 | 2614.7568 | 2614.7568 | 2603.7923 | 780 | 200 | 3583.7923 | 89.59% | 95% | 0% | -430.2059 | 2184.5509 | -3550 | -400 | -1765.4491 | 44.14% | 88.26% | 95% | 0% | 3023 | -376
[5 empty] | 2019-02-06 | 26 | 877 | 2676 | -347 | 1 | 0 | 3023 | 2614.7568 | 2614.7568 | 2614.7568 | 2603.7923 | 780 | 200 | 3583.7923 | 89.59% | 95% | 0% | -397.0252 | 2217.7316 | -3550 | -400 | -1732.2684 | 43.31% | 88.24% | 95% | 0% | 3023 | -347
[5 empty] | 2019-02-06 | 27 | 877.5 | 2674 | -344 | 1 | 0 | 3018 | 2606.925 | 2606.925 | 2606.925 | 2603.7923 | 780 | 200 | 3583.7923 | 89.59% | 95% | 0% | -393.5927 | 2213.3323 | -3550 | -400 | -1736.6677 | 43.42% | 88.24% | 95% | 0% | 3018 | -344
[5 empty] | 2019-02-06 | 28 | 878 | 2693 | -319 | 1 | 0 | 3012 | 2597.5268 | 2597.5268 | 2597.5268 | 2603.7923 | 780 | 200 | 3583.7923 | 89.59% | 95% | 0% | -364.9886 | 2232.5382 | -3550 | -400 | -1717.4618 | 42.94% | 88.24% | 95% | 0% | 3012 | -319
[5 empty] | 2019-02-06 | 29 | 878.5 | 2763 | -265 | 1 | 0 | 3028 | 2622.5886 | 2622.5886 | 2622.5886 | 2603.7923 | 780 | 200 | 3583.7923 | 89.59% | 95% | 0% | -303.2037 | 2319.385 | -3550 | -400 | -1630.615 | 40.77% | 88.22% | 95% | 0% | 3028 | -265
[5 empty] | 2019-02-06 | 30 | 879 | 2799 | -230 | 1 | 0 | 3029 | 2624.155 | 2624.155 | 2624.155 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -263.1579 | 2360.9971 | -3550 | -400 | -1589.0029 | 39.73% | 88.22% | 95% | 0% | 3029 | -230
[5 empty] | 2019-02-06 | 31 | 879.5 | 2847 | -196 | 1 | 0 | 3043 | 2646.0841 | 2646.0841 | 2646.0841 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -224.2563 | 2421.8278 | -3550 | -400 | -1528.1722 | 38.2% | 88.21% | 95% | 0% | 3043 | -196
[5 empty] | 2019-02-06 | 32 | 880 | 2961 | -162 | 1 | 0 | 3123 | 2771.3932 | 2771.3932 | 2771.3932 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -185.3547 | 2586.0385 | -3550 | -400 | -1363.9615 | 34.1% | 88.19% | 95% | 0% | 3123 | -162
[5 empty] | 2019-02-06 | 33 | 880.5 | 3085 | -133 | 1 | 0 | 3218 | 2920.1979 | 2920.1979 | 2920.1979 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -152.1739 | 2768.0239 | -3550 | -400 | -1181.9761 | 29.55% | 88.19% | 95% | 0% | 3218 | -133
[5 empty] | 2019-02-06 | 34 | 881 | 3192 | -114 | 1 | 0 | 3306 | 3058.0379 | 3058.0379 | 3058.0379 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -130.4348 | 2927.6031 | -3550 | -400 | -1022.3969 | 25.56% | 88.19% | 95% | 0% | 3306 | -114
[5 empty] | 2019-02-06 | 35 | 881.5 | 3298 | -110 | 1 | 0 | 3408 | 3217.8071 | 3217.8071 | 3217.8071 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -125.8581 | 3091.949 | -3550 | -400 | -858.051 | 21.45% | 88.19% | 95% | 0% | 3408 | -110
[5 empty] | 2019-02-06 | 36 | 882 | 3335 | -109 | 1 | 0 | 3444 | 3274.1962 | 3274.1962 | 3274.1962 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -124.714 | 3149.4822 | -3550 | -400 | -800.5178 | 20.01% | 88.19% | 95% | 0% | 3444 | -109
[5 empty] | 2019-02-06 | 37 | 882.5 | 3317 | -109 | 0 | 0 | 3426 | 3246.0016 | 3246.0016 | 3246.0016 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -124.714 | 3121.2877 | -2750 | -200 | 171.2877 | -4.282% | 88.18% | 95% | 0% | 3426 | -109
[5 empty] | 2019-02-06 | 38 | 883 | 3272 | -110 | 0 | 0 | 3382 | 3177.0816 | 3177.0816 | 3177.0816 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -125.8581 | 3051.2235 | -2750 | -200 | 101.2235 | -2.531% | 88.18% | 95% | 0% | 3382 | -110
[5 empty] | 2019-02-06 | 39 | 883.5 | 3233 | -108 | 0 | 0 | 3341 | 3112.8607 | 3112.8607 | 3112.8607 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -123.5698 | 2989.2909 | -2750 | -200 | 39.2909 | -0.9823% | 88.18% | 95% | 0% | 3341 | -108
[5 empty] | 2019-02-06 | 40 | 884 | 3208 | -106 | 0 | 0 | 3314 | 3070.5688 | 3070.5688 | 3070.5688 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -121.2815 | 2949.2874 | -2750 | -200 | -0.71263 | 0.01782% | 88.18% | 95% | 0% | 3314 | -106
[5 empty] | 2019-02-06 | 41 | 884.5 | 3140 | -105 | 0 | 0 | 3245 | 2962.4897 | 2962.4897 | 2962.4897 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -120.1373 | 2842.3524 | -2750 | -200 | -107.6476 | 2.691% | 88.18% | 95% | 0% | 3245 | -105
[5 empty] | 2019-02-06 | 42 | 885 | 2997 | -103 | 0 | 0 | 3100 | 2735.3669 | 2735.3669 | 2735.3669 | 2602.2259 | 780 | 200 | 3582.2259 | 89.56% | 95% | 0% | -117.849 | 2617.5179 | -2750 | -200 | -332.4821 | 8.312% | 88.17% | 95% | 0% | 3100 | -103
[5 empty] | 2019-02-06 | 43 | 885.5 | 2862 | -103 | 0 | 0 | 2965 | 2523.9077 | 2523.9077 | 2523.9077 | 2600.6595 | 780 | 200 | 3580.6595 | 89.52% | 95% | 0% | -117.849 | 2406.0587 | -2750 | -200 | -543.9413 | 13.6% | 88.17% | 95% | 0% | 2965 | -103
[5 empty] | 2019-02-06 | 44 | 886 | 2680 | -103 | 0 | 0 | 2783 | 2238.8293 | 2238.8293 | 2238.8293 | 2600.6595 | 780 | 200 | 3580.6595 | 89.52% | 95% | 0% | -117.849 | 2120.9804 | -2750 | -200 | -829.0196 | 20.73% | 88.17% | 95% | 0% | 2783 | -103
[5 empty] | 2019-02-06 | 45 | 886.5 | 2488 | -105 | 0 | 0 | 2593 | 1941.2201 | 1941.2201 | 1941.2201 | 2600.6595 | 780 | 200 | 3580.6595 | 89.52% | 95% | 0% | -120.1373 | 1821.0828 | -2750 | -200 | -1128.9172 | 28.22% | 88.15% | 95% | 0% | 2593 | -105
[5 empty] | 2019-02-06 | 46 | 887 | 2347 | -107 | 0 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 2600.6595 | 780 | 200 | 3580.6595 | 89.52% | 95% | 0% | -122.4256 | 1601.0698 | -2750 | -200 | -1348.9302 | 33.72% | 88.15% | 95% | 0% | 2454 | -107
[5 empty] | 2019-02-06 | 47 | 887.5 | 2178 | -112 | 0 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 2600.6595 | 780 | 200 | 3580.6595 | 89.52% | 95% | 0% | -128.1465 | 1338.4653 | -2750 | -200 | -1611.5347 | 40.29% | 88.15% | 95% | 0% | 2290 | -112
[5 empty] | 2019-02-06 | 48 | 888 | 2068 | -118 | 0 | 0 | 2186 | 1303.7098 | 1303.7098 | 1303.7098 | 2600.6595 | 780 | 200 | 3580.6595 | 89.52% | 95% | 0% | -135.0114 | 1168.6984 | -2750 | -200 | -1781.3016 | 44.53% | 88.14% | 95% | 0% | 2186 | -118
[5 empty] | 2019-02-07 | 1 | 888.5 | 2026 | -123 | 0 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 2600.6595 | 780 | 200 | 3580.6595 | 89.52% | 95% | 0% | -140.7323 | 1105.0221 | -2750 | -200 | -1844.9779 | 46.12% | 88.14% | 95% | 0% | 2149 | -123
[5 empty] | 2019-02-07 | 2 | 889 | 2051 | -128 | 0 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 2600.6595 | 780 | 200 | 3580.6595 | 89.52% | 95% | 0% | -146.4531 | 1146.2922 | -2750 | -200 | -1803.7078 | 45.09% | 88.14% | 95% | 0% | 2179 | -128
[5 empty] | 2019-02-07 | 3 | 889.5 | 2028 | -128 | 0 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 2599.0932 | 780 | 200 | 3579.0932 | 89.48% | 95% | 0% | -146.4531 | 1110.2658 | -2750 | -200 | -1839.7342 | 45.99% | 88.13% | 95% | 0% | 2156 | -128
[5 empty] | 2019-02-07 | 4 | 890 | 1987 | -128 | 0 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 2599.0932 | 780 | 200 | 3579.0932 | 89.48% | 95% | 0% | -146.4531 | 1046.0448 | -2750 | -200 | -1903.9552 | 47.6% | 88.13% | 95% | 0% | 2115 | -128
[5 empty] | 2019-02-07 | 5 | 890.5 | 1934 | -128 | 0 | 0 | 2062 | 1109.4806 | 1109.4806 | 1109.4806 | 2599.0932 | 780 | 200 | 3579.0932 | 89.48% | 95% | 0% | -146.4531 | 963.0275 | -2750 | -200 | -1986.9725 | 49.67% | 88.13% | 95% | 0% | 2062 | -128
[5 empty] | 2019-02-07 | 6 | 891 | 1924 | -127 | 0 | 0 | 2051 | 1092.2506 | 1092.2506 | 1092.2506 | 2599.0932 | 780 | 200 | 3579.0932 | 89.48% | 95% | 0% | -145.3089 | 946.9417 | -2750 | -200 | -2003.0583 | 50.08% | 88.12% | 95% | 0% | 2051 | -127
[5 empty] | 2019-02-07 | 7 | 891.5 | 1905 | -121 | 0 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 2599.0932 | 780 | 200 | 3579.0932 | 89.48% | 95% | 0% | -138.4439 | 914.6476 | -2750 | -200 | -2035.3524 | 50.88% | 88.11% | 95% | 0% | 2026 | -121
[5 empty] | 2019-02-07 | 8 | 892 | 1873 | -115 | 0 | 0 | 1988 | 993.5697 | 993.5697 | 993.5697 | 2597.5268 | 780 | 200 | 3577.5268 | 89.44% | 95% | 0% | -131.5789 | 861.9907 | -2750 | -200 | -2088.0093 | 52.2% | 88.1% | 95% | 0% | 1988 | -115
[5 empty] | 2019-02-07 | 9 | 892.5 | 1847 | -116 | 0 | 0 | 1963 | 954.4106 | 954.4106 | 954.4106 | 2597.5268 | 780 | 200 | 3577.5268 | 89.44% | 95% | 0% | -132.7231 | 821.6874 | -2750 | -200 | -2128.3126 | 53.21% | 88.09% | 95% | 0% | 1963 | -116
[5 empty] | 2019-02-07 | 10 | 893 | 1869 | -116 | 0 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 2597.5268 | 780 | 200 | 3577.5268 | 89.44% | 95% | 0% | -132.7231 | 856.1475 | -2750 | -200 | -2093.8525 | 52.35% | 88.09% | 95% | 0% | 1985 | -116
[5 empty] | 2019-02-07 | 11 | 893.5 | 1945 | -115 | 0 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 2597.5268 | 780 | 200 | 3577.5268 | 89.44% | 95% | 0% | -131.5789 | 974.769 | -2750 | -200 | -1975.231 | 49.38% | 88.08% | 95% | 0% | 2060 | -115
[5 empty] | 2019-02-07 | 12 | 894 | 2044 | -115 | 0 | 0 | 2159 | 1261.418 | 1261.418 | 1261.418 | 2597.5268 | 780 | 200 | 3577.5268 | 89.44% | 95% | 0% | -131.5789 | 1129.839 | -2750 | -200 | -1820.161 | 45.5% | 88.07% | 95% | 0% | 2159 | -115
[5 empty] | 2019-02-07 | 13 | 894.5 | 2296 | -115 | 0 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 2597.5268 | 780 | 200 | 3577.5268 | 89.44% | 95% | 0% | -131.5789 | 1524.5628 | -2750 | -200 | -1425.4372 | 35.64% | 88.05% | 95% | 0% | 2411 | -115
[5 empty] | 2019-02-07 | 14 | 895 | 2534 | -116 | 0 | 0 | 2650 | 2030.5029 | 2030.5029 | 2030.5029 | 2597.5268 | 780 | 200 | 3577.5268 | 89.44% | 95% | 0% | -132.7231 | 1897.7798 | -2750 | -200 | -1052.2202 | 26.31% | 88.04% | 95% | 0% | 2650 | -116
[5 empty] | 2019-02-07 | 15 | 895.5 | 2789 | -124 | 0 | 0 | 2913 | 2442.4567 | 2442.4567 | 2442.4567 | 2595.9604 | 780 | 200 | 3575.9604 | 89.4% | 95% | 0% | -141.8764 | 2300.5803 | -2750 | -200 | -649.4197 | 16.24% | 88.03% | 95% | 0% | 2913 | -124
[5 empty] | 2019-02-07 | 16 | 896 | 2889 | -135 | 0 | 0 | 3024 | 2616.3232 | 2616.3232 | 2616.3232 | 2595.9604 | 780 | 200 | 3575.9604 | 89.4% | 95% | 0% | -154.4622 | 2461.8609 | -2750 | -200 | -488.1391 | 12.2% | 88.03% | 95% | 0% | 3024 | -135
[5 empty] | 2019-02-07 | 17 | 896.5 | 2914 | -160 | 0 | 0 | 3074 | 2694.6414 | 2694.6414 | 2694.6414 | 2595.9604 | 780 | 200 | 3575.9604 | 89.4% | 95% | 0% | -183.0664 | 2511.575 | -2750 | -200 | -438.425 | 10.96% | 88.02% | 95% | 0% | 3074 | -160
[5 empty] | 2019-02-07 | 18 | 897 | 2852 | -206 | 0 | 0 | 3058 | 2669.5796 | 2669.5796 | 2669.5796 | 2595.9604 | 780 | 200 | 3575.9604 | 89.4% | 95% | 0% | -235.6979 | 2433.8816 | -2750 | -200 | -516.1184 | 12.9% | 88.02% | 95% | 0% | 3058 | -206
[5 empty] | 2019-02-07 | 19 | 897.5 | 2855 | -235 | 0 | 0 | 3090 | 2719.7032 | 2719.7032 | 2719.7032 | 2595.9604 | 780 | 200 | 3575.9604 | 89.4% | 95% | 0% | -268.8787 | 2450.8245 | -2750 | -200 | -499.1755 | 12.48% | 88.02% | 95% | 0% | 3090 | -235
[5 empty] | 2019-02-07 | 20 | 898 | 2767 | -301 | 1 | 0 | 3068 | 2685.2432 | 2685.2432 | 2685.2432 | 2595.9604 | 780 | 200 | 3575.9604 | 89.4% | 95% | 0% | -344.3936 | 2340.8496 | -3550 | -400 | -1609.1504 | 40.23% | 88.02% | 95% | 0% | 3068 | -301
[5 empty] | 2019-02-07 | 21 | 898.5 | 2649 | -352 | 1 | 0 | 3001 | 2580.2968 | 2580.2968 | 2580.2968 | 2595.9604 | 780 | 200 | 3575.9604 | 89.4% | 95% | 0% | -402.746 | 2177.5508 | -3550 | -400 | -1772.4492 | 44.31% | 88% | 95% | 0% | 3001 | -352
[5 empty] | 2019-02-07 | 22 | 899 | 2590 | -389 | 1 | 0 | 2979 | 2545.8368 | 2545.8368 | 2545.8368 | 2595.9604 | 780 | 200 | 3575.9604 | 89.4% | 95% | 0% | -445.0801 | 2100.7567 | -3550 | -400 | -1849.2433 | 46.23% | 88% | 95% | 0% | 2979 | -389
[5 empty] | 2019-02-07 | 23 | 899.5 | 2523 | -430 | 1 | 0 | 2953 | 2505.1113 | 2505.1113 | 2505.1113 | 2595.9604 | 780 | 200 | 3575.9604 | 89.4% | 95% | 0% | -491.9908 | 2013.1204 | -3550 | -400 | -1936.8796 | 48.42% | 87.99% | 95% | 0% | 2953 | -430
[5 empty] | 2019-02-07 | 24 | 900 | 2446 | -464 | 1 | 0 | 2910 | 2437.7576 | 2437.7576 | 2437.7576 | 2594.3941 | 780 | 200 | 3574.3941 | 89.36% | 95% | 0% | -530.8924 | 1906.8652 | -3550 | -400 | -2043.1348 | 51.08% | 87.98% | 95% | 0% | 2910 | -464
[5 empty] | 2019-02-07 | 25 | 900.5 | 2421 | -474 | 1 | 0 | 2895 | 2414.2622 | 2414.2622 | 2414.2622 | 2594.3941 | 780 | 200 | 3574.3941 | 89.36% | 95% | 0% | -542.3341 | 1871.9281 | -3550 | -400 | -2078.0719 | 51.95% | 87.98% | 95% | 0% | 2895 | -474
[5 empty] | 2019-02-07 | 26 | 901 | 2372 | -489 | 1 | 0 | 2861 | 2361.0058 | 2361.0058 | 2361.0058 | 2594.3941 | 780 | 200 | 3574.3941 | 89.36% | 95% | 0% | -559.4966 | 1801.5092 | -3550 | -400 | -2148.4908 | 53.71% | 87.98% | 95% | 0% | 2861 | -489
[5 empty] | 2019-02-07 | 27 | 901.5 | 2346 | -479 | 1 | 0 | 2825 | 2304.6167 | 2304.6167 | 2304.6167 | 2594.3941 | 780 | 200 | 3574.3941 | 89.36% | 95% | 0% | -548.0549 | 1756.5617 | -3550 | -400 | -2193.4383 | 54.84% | 87.98% | 95% | 0% | 2825 | -479
[5 empty] | 2019-02-07 | 28 | 902 | 2355 | -450 | 1 | 0 | 2805 | 2273.2894 | 2273.2894 | 2273.2894 | 2594.3941 | 780 | 200 | 3574.3941 | 89.36% | 95% | 0% | -514.8741 | 1758.4152 | -3550 | -400 | -2191.5848 | 54.79% | 87.97% | 95% | 0% | 2805 | -450
[5 empty] | 2019-02-07 | 29 | 902.5 | 2412 | -408 | 1 | 0 | 2820 | 2296.7848 | 2296.7848 | 2296.7848 | 2592.8277 | 780 | 200 | 3572.8277 | 89.32% | 95% | 0% | -466.8192 | 1829.9656 | -3550 | -400 | -2120.0344 | 53% | 87.97% | 95% | 0% | 2820 | -408
[5 empty] | 2019-02-07 | 30 | 903 | 2434 | -389 | 1 | 0 | 2823 | 2301.4839 | 2301.4839 | 2301.4839 | 2592.8277 | 780 | 200 | 3572.8277 | 89.32% | 95% | 0% | -445.0801 | 1856.4038 | -3550 | -400 | -2093.5962 | 52.34% | 87.96% | 95% | 0% | 2823 | -389
[5 empty] | 2019-02-07 | 31 | 903.5 | 2501 | -353 | 1 | 0 | 2854 | 2350.0412 | 2350.0412 | 2350.0412 | 2592.8277 | 780 | 200 | 3572.8277 | 89.32% | 95% | 0% | -403.8902 | 1946.1511 | -3550 | -400 | -2003.8489 | 50.1% | 87.96% | 95% | 0% | 2854 | -353
[5 empty] | 2019-02-07 | 32 | 904 | 2671 | -289 | 1 | 0 | 2960 | 2516.0758 | 2516.0758 | 2516.0758 | 2592.8277 | 780 | 200 | 3572.8277 | 89.32% | 95% | 0% | -330.6636 | 2185.4122 | -3550 | -400 | -1764.5878 | 44.11% | 87.95% | 95% | 0% | 2960 | -289
[5 empty] | 2019-02-07 | 33 | 904.5 | 2881 | -200 | 1 | 0 | 3081 | 2705.6059 | 2705.6059 | 2705.6059 | 2592.8277 | 780 | 200 | 3572.8277 | 89.32% | 95% | 0% | -228.833 | 2476.773 | -3550 | -400 | -1473.227 | 36.83% | 87.94% | 95% | 0% | 3081 | -200
[5 empty] | 2019-02-07 | 34 | 905 | 3074 | -152 | 1 | 0 | 3226 | 2932.7288 | 2932.7288 | 2932.7288 | 2592.8277 | 780 | 200 | 3572.8277 | 89.32% | 95% | 0% | -173.913 | 2758.8157 | -3550 | -400 | -1191.1843 | 29.78% | 87.93% | 95% | 0% | 3226 | -152
[5 empty] | 2019-02-07 | 35 | 905.5 | 3210 | -146 | 1 | 0 | 3356 | 3136.3561 | 3136.3561 | 3136.3561 | 2592.8277 | 780 | 200 | 3572.8277 | 89.32% | 95% | 0% | -167.0481 | 2969.3081 | -3550 | -400 | -980.6919 | 24.52% | 87.93% | 95% | 0% | 3356 | -146
[5 empty] | 2019-02-07 | 36 | 906 | 3282 | -143 | 1 | 0 | 3425 | 3244.4353 | 3244.4353 | 3244.4353 | 2592.8277 | 780 | 200 | 3572.8277 | 89.32% | 95% | 0% | -163.6156 | 3080.8197 | -3550 | -400 | -869.1803 | 21.73% | 87.91% | 95% | 0% | 3425 | -143
[5 empty] | 2019-02-07 | 37 | 906.5 | 3283 | -141 | 0 | 0 | 3424 | 3242.8689 | 3242.8689 | 3242.8689 | 2591.2613 | 780 | 200 | 3571.2613 | 89.28% | 95% | 0% | -161.3272 | 3081.5417 | -2750 | -200 | 131.5417 | -3.289% | 87.91% | 95% | 0% | 3424 | -141
[5 empty] | 2019-02-07 | 38 | 907 | 3264 | -139 | 0 | 0 | 3403 | 3209.9753 | 3209.9753 | 3209.9753 | 2591.2613 | 780 | 200 | 3571.2613 | 89.28% | 95% | 0% | -159.0389 | 3050.9364 | -2750 | -200 | 100.9364 | -2.523% | 87.91% | 95% | 0% | 3403 | -139
[5 empty] | 2019-02-07 | 39 | 907.5 | 3176 | -139 | 0 | 0 | 3315 | 3072.1352 | 3072.1352 | 3072.1352 | 2591.2613 | 780 | 200 | 3571.2613 | 89.28% | 95% | 0% | -159.0389 | 2913.0963 | -2750 | -200 | -36.9037 | 0.9226% | 87.9% | 95% | 0% | 3315 | -139
[5 empty] | 2019-02-07 | 40 | 908 | 3118 | -139 | 0 | 0 | 3257 | 2981.2861 | 2981.2861 | 2981.2861 | 2591.2613 | 780 | 200 | 3571.2613 | 89.28% | 95% | 0% | -159.0389 | 2822.2472 | -2750 | -200 | -127.7528 | 3.194% | 87.89% | 95% | 0% | 3257 | -139
[5 empty] | 2019-02-07 | 41 | 908.5 | 3004 | -140 | 0 | 0 | 3144 | 2804.2869 | 2804.2869 | 2804.2869 | 2591.2613 | 780 | 200 | 3571.2613 | 89.28% | 95% | 0% | -160.1831 | 2644.1038 | -2750 | -200 | -305.8962 | 7.647% | 87.89% | 95% | 0% | 3144 | -140
[5 empty] | 2019-02-07 | 42 | 909 | 2875 | -141 | 0 | 0 | 3016 | 2603.7923 | 2603.7923 | 2603.7923 | 2591.2613 | 780 | 200 | 3571.2613 | 89.28% | 95% | 0% | -161.3272 | 2442.465 | -2750 | -200 | -507.535 | 12.69% | 87.88% | 95% | 0% | 3016 | -141
[5 empty] | 2019-02-07 | 43 | 909.5 | 2705 | -142 | 0 | 0 | 2847 | 2339.0767 | 2339.0767 | 2339.0767 | 2591.2613 | 780 | 200 | 3571.2613 | 89.28% | 95% | 0% | -162.4714 | 2176.6053 | -2750 | -200 | -773.3947 | 19.33% | 87.87% | 95% | 0% | 2847 | -142
[5 empty] | 2019-02-07 | 44 | 910 | 2532 | -144 | 0 | 0 | 2676 | 2071.2284 | 2071.2284 | 2071.2284 | 2589.695 | 780 | 200 | 3569.695 | 89.24% | 95% | 0% | -164.7597 | 1906.4686 | -2750 | -200 | -1043.5314 | 26.09% | 87.87% | 95% | 0% | 2676 | -144
[5 empty] | 2019-02-07 | 45 | 910.5 | 2338 | -144 | 0 | 0 | 2482 | 1767.3537 | 1767.3537 | 1767.3537 | 2589.695 | 780 | 200 | 3569.695 | 89.24% | 95% | 0% | -164.7597 | 1602.5939 | -2750 | -200 | -1347.4061 | 33.69% | 87.87% | 95% | 0% | 2482 | -144
[5 empty] | 2019-02-07 | 46 | 911 | 2202 | -145 | 0 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 2589.695 | 780 | 200 | 3569.695 | 89.24% | 95% | 0% | -165.9039 | 1389.9906 | -2750 | -200 | -1560.0094 | 39% | 87.86% | 95% | 0% | 2347 | -145
[5 empty] | 2019-02-07 | 47 | 911.5 | 2038 | -146 | 0 | 0 | 2184 | 1300.5771 | 1300.5771 | 1300.5771 | 2589.695 | 780 | 200 | 3569.695 | 89.24% | 95% | 0% | -167.0481 | 1133.529 | -2750 | -200 | -1816.471 | 45.41% | 87.86% | 95% | 0% | 2184 | -146
[5 empty] | 2019-02-07 | 48 | 912 | 1940 | -148 | 0 | 0 | 2088 | 1150.2061 | 1150.2061 | 1150.2061 | 2588.1286 | 780 | 200 | 3568.1286 | 89.2% | 95% | 0% | -169.3364 | 980.8697 | -2750 | -200 | -1969.1303 | 49.23% | 87.86% | 95% | 0% | 2088 | -148
[5 empty] | 2019-02-08 | 1 | 912.5 | 1910 | -151 | 0 | 0 | 2061 | 1107.9143 | 1107.9143 | 1107.9143 | 2588.1286 | 780 | 200 | 3568.1286 | 89.2% | 95% | 0% | -172.7689 | 935.1454 | -2750 | -200 | -2014.8546 | 50.37% | 87.84% | 95% | 0% | 2061 | -151
[5 empty] | 2019-02-08 | 2 | 913 | 1928 | -155 | 0 | 0 | 2083 | 1142.3743 | 1142.3743 | 1142.3743 | 2588.1286 | 780 | 200 | 3568.1286 | 89.2% | 95% | 0% | -177.3455 | 965.0287 | -2750 | -200 | -1984.9713 | 49.62% | 87.83% | 95% | 0% | 2083 | -155
[5 empty] | 2019-02-08 | 3 | 913.5 | 1907 | -160 | 0 | 0 | 2067 | 1117.3124 | 1117.3124 | 1117.3124 | 2586.5622 | 780 | 200 | 3566.5622 | 89.16% | 95% | 0% | -183.0664 | 934.2461 | -2750 | -200 | -2015.7539 | 50.39% | 87.82% | 95% | 0% | 2067 | -160
[5 empty] | 2019-02-08 | 4 | 914 | 1840 | -166 | 0 | 0 | 2006 | 1021.7642 | 1021.7642 | 1021.7642 | 2586.5622 | 780 | 200 | 3566.5622 | 89.16% | 95% | 0% | -189.9314 | 831.8329 | -2750 | -200 | -2118.1671 | 52.95% | 87.82% | 95% | 0% | 2006 | -166
[5 empty] | 2019-02-08 | 5 | 914.5 | 1788 | -169 | 0 | 0 | 1957 | 945.0124 | 945.0124 | 945.0124 | 2586.5622 | 780 | 200 | 3566.5622 | 89.16% | 95% | 0% | -193.3638 | 751.6485 | -2750 | -200 | -2198.3515 | 54.96% | 87.8% | 95% | 0% | 1957 | -169
[5 empty] | 2019-02-08 | 6 | 915 | 1763 | -173 | 0 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 2586.5622 | 780 | 200 | 3566.5622 | 89.16% | 95% | 0% | -197.9405 | 714.1782 | -2750 | -200 | -2235.8218 | 55.9% | 87.8% | 95% | 0% | 1936 | -173
[5 empty] | 2019-02-08 | 7 | 915.5 | 1696 | -179 | 0 | 0 | 1875 | 816.5705 | 816.5705 | 816.5705 | 2586.5622 | 780 | 200 | 3566.5622 | 89.16% | 95% | 0% | -204.8055 | 611.765 | -2750 | -200 | -2338.235 | 58.46% | 87.77% | 95% | 0% | 1875 | -179
[5 empty] | 2019-02-08 | 8 | 916 | 1651 | -185 | 0 | 0 | 1836 | 755.4823 | 755.4823 | 755.4823 | 2586.5622 | 780 | 200 | 3566.5622 | 89.16% | 95% | 0% | -211.6705 | 543.8118 | -2750 | -200 | -2406.1882 | 60.15% | 87.75% | 95% | 0% | 1836 | -185
[5 empty] | 2019-02-08 | 9 | 916.5 | 1608 | -190 | 0 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 2584.9959 | 780 | 200 | 3564.9959 | 89.12% | 95% | 0% | -217.3913 | 478.5691 | -2750 | -200 | -2471.4309 | 61.79% | 87.75% | 95% | 0% | 1798 | -190
[5 empty] | 2019-02-08 | 10 | 917 | 1604 | -195 | 0 | 0 | 1799 | 697.5268 | 697.5268 | 697.5268 | 2584.9959 | 780 | 200 | 3564.9959 | 89.12% | 95% | 0% | -223.1121 | 474.4147 | -2750 | -200 | -2475.5853 | 61.89% | 87.75% | 95% | 0% | 1799 | -195
[5 empty] | 2019-02-08 | 11 | 917.5 | 1648 | -198 | 0 | 0 | 1846 | 771.1459 | 771.1459 | 771.1459 | 2584.9959 | 780 | 200 | 3564.9959 | 89.12% | 95% | 0% | -226.5446 | 544.6013 | -2750 | -200 | -2405.3987 | 60.13% | 87.73% | 95% | 0% | 1846 | -198
[5 empty] | 2019-02-08 | 12 | 918 | 1723 | -202 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 2584.9959 | 780 | 200 | 3564.9959 | 89.12% | 95% | 0% | -231.1213 | 663.7674 | -2750 | -200 | -2286.2326 | 57.16% | 87.73% | 95% | 0% | 1925 | -202
[5 empty] | 2019-02-08 | 13 | 918.5 | 1951 | -207 | 0 | 0 | 2158 | 1259.8516 | 1259.8516 | 1259.8516 | 2584.9959 | 780 | 200 | 3564.9959 | 89.12% | 95% | 0% | -236.8421 | 1023.0095 | -2750 | -200 | -1926.9905 | 48.17% | 87.73% | 95% | 0% | 2158 | -207
[5 empty] | 2019-02-08 | 14 | 919 | 2194 | -211 | 0 | 0 | 2405 | 1646.7436 | 1646.7436 | 1646.7436 | 2583.4295 | 780 | 200 | 3563.4295 | 89.09% | 95% | 0% | -241.4188 | 1405.3248 | -2750 | -200 | -1544.6752 | 38.62% | 87.73% | 95% | 0% | 2405 | -211
[5 empty] | 2019-02-08 | 15 | 919.5 | 2475 | -218 | 0 | 0 | 2693 | 2097.8566 | 2097.8566 | 2097.8566 | 2583.4295 | 780 | 200 | 3563.4295 | 89.09% | 95% | 0% | -249.4279 | 1848.4286 | -2750 | -200 | -1101.5714 | 27.54% | 87.71% | 95% | 0% | 2693 | -218
[5 empty] | 2019-02-08 | 16 | 920 | 2608 | -224 | 0 | 0 | 2832 | 2315.5812 | 2315.5812 | 2315.5812 | 2583.4295 | 780 | 200 | 3563.4295 | 89.09% | 95% | 0% | -256.2929 | 2059.2883 | -2750 | -200 | -890.7117 | 22.27% | 87.71% | 95% | 0% | 2832 | -224
[5 empty] | 2019-02-08 | 17 | 920.5 | 2684 | -228 | 0 | 0 | 2912 | 2440.8904 | 2440.8904 | 2440.8904 | 2583.4295 | 780 | 200 | 3563.4295 | 89.09% | 95% | 0% | -260.8696 | 2180.0208 | -2750 | -200 | -769.9792 | 19.25% | 87.71% | 95% | 0% | 2912 | -228
[5 empty] | 2019-02-08 | 18 | 921 | 2692 | -234 | 0 | 0 | 2926 | 2462.8195 | 2462.8195 | 2462.8195 | 2583.4295 | 780 | 200 | 3563.4295 | 89.09% | 95% | 0% | -267.7346 | 2195.0849 | -2750 | -200 | -754.9151 | 18.87% | 87.69% | 95% | 0% | 2926 | -234
[5 empty] | 2019-02-08 | 19 | 921.5 | 2763 | -242 | 0 | 0 | 3005 | 2586.5622 | 2586.5622 | 2586.5622 | 2583.4295 | 780 | 200 | 3563.4295 | 89.09% | 95% | 0% | -276.8879 | 2309.6744 | -2750 | -200 | -640.3256 | 16.01% | 87.67% | 95% | 0% | 3005 | -242
[5 empty] | 2019-02-08 | 20 | 922 | 2761 | -260 | 1 | 0 | 3021 | 2611.6241 | 2611.6241 | 2611.6241 | 2583.4295 | 780 | 200 | 3563.4295 | 89.09% | 95% | 0% | -297.4828 | 2314.1412 | -3550 | -400 | -1635.8588 | 40.9% | 87.66% | 95% | 0% | 3021 | -260
[5 empty] | 2019-02-08 | 21 | 922.5 | 2741 | -279 | 1 | 0 | 3020 | 2610.0577 | 2610.0577 | 2610.0577 | 2583.4295 | 780 | 200 | 3563.4295 | 89.09% | 95% | 0% | -319.222 | 2290.8357 | -3550 | -400 | -1659.1643 | 41.48% | 87.65% | 95% | 0% | 3020 | -279
[5 empty] | 2019-02-08 | 22 | 923 | 2725 | -296 | 1 | 0 | 3021 | 2611.6241 | 2611.6241 | 2611.6241 | 2583.4295 | 780 | 200 | 3563.4295 | 89.09% | 95% | 0% | -338.6728 | 2272.9513 | -3550 | -400 | -1677.0487 | 41.93% | 87.65% | 95% | 0% | 3021 | -296
[5 empty] | 2019-02-08 | 23 | 923.5 | 2696 | -316 | 1 | 0 | 3012 | 2597.5268 | 2597.5268 | 2597.5268 | 2583.4295 | 780 | 200 | 3563.4295 | 89.09% | 95% | 0% | -361.5561 | 2235.9707 | -3550 | -400 | -1714.0293 | 42.85% | 87.64% | 95% | 0% | 3012 | -316
[5 empty] | 2019-02-08 | 24 | 924 | 2666 | -340 | 1 | 0 | 3006 | 2588.1286 | 2588.1286 | 2588.1286 | 2583.4295 | 780 | 200 | 3563.4295 | 89.09% | 95% | 0% | -389.016 | 2199.1126 | -3550 | -400 | -1750.8874 | 43.77% | 87.64% | 95% | 0% | 3006 | -340
[5 empty] | 2019-02-08 | 25 | 924.5 | 2662 | -353 | 1 | 0 | 3015 | 2602.2259 | 2602.2259 | 2602.2259 | 2583.4295 | 780 | 200 | 3563.4295 | 89.09% | 95% | 0% | -403.8902 | 2198.3357 | -3550 | -400 | -1751.6643 | 43.79% | 87.64% | 95% | 0% | 3015 | -353
[5 empty] | 2019-02-08 | 26 | 925 | 2620 | -367 | 1 | 0 | 2987 | 2558.3677 | 2558.3677 | 2558.3677 | 2581.8631 | 780 | 200 | 3561.8631 | 89.05% | 95% | 0% | -419.9085 | 2138.4592 | -3550 | -400 | -1811.5408 | 45.29% | 87.63% | 95% | 0% | 2987 | -367
[5 empty] | 2019-02-08 | 27 | 925.5 | 2559 | -386 | 1 | 0 | 2945 | 2492.5804 | 2492.5804 | 2492.5804 | 2581.8631 | 780 | 200 | 3561.8631 | 89.05% | 95% | 0% | -441.6476 | 2050.9328 | -3550 | -400 | -1899.0672 | 47.48% | 87.63% | 95% | 0% | 2945 | -386
[5 empty] | 2019-02-08 | 28 | 926 | 2517 | -375 | 1 | 0 | 2892 | 2409.5631 | 2409.5631 | 2409.5631 | 2581.8631 | 780 | 200 | 3561.8631 | 89.05% | 95% | 0% | -429.0618 | 1980.5013 | -3550 | -400 | -1969.4987 | 49.24% | 87.62% | 95% | 0% | 2892 | -375
[5 empty] | 2019-02-08 | 29 | 926.5 | 2498 | -367 | 1 | 0 | 2865 | 2367.2712 | 2367.2712 | 2367.2712 | 2581.8631 | 780 | 200 | 3561.8631 | 89.05% | 95% | 0% | -419.9085 | 1947.3628 | -3550 | -400 | -2002.6372 | 50.07% | 87.61% | 95% | 0% | 2865 | -367
[5 empty] | 2019-02-08 | 30 | 927 | 2474 | -351 | 1 | 0 | 2825 | 2304.6167 | 2304.6167 | 2304.6167 | 2581.8631 | 780 | 200 | 3561.8631 | 89.05% | 95% | 0% | -401.6018 | 1903.0148 | -3550 | -400 | -2046.9852 | 51.17% | 87.6% | 95% | 0% | 2825 | -351
[5 empty] | 2019-02-08 | 31 | 927.5 | 2481 | -339 | 1 | 0 | 2820 | 2296.7848 | 2296.7848 | 2296.7848 | 2581.8631 | 780 | 200 | 3561.8631 | 89.05% | 95% | 0% | -387.8719 | 1908.913 | -3550 | -400 | -2041.087 | 51.03% | 87.59% | 95% | 0% | 2820 | -339
[5 empty] | 2019-02-08 | 32 | 928 | 2548 | -310 | 1 | 0 | 2858 | 2356.3067 | 2356.3067 | 2356.3067 | 2581.8631 | 780 | 200 | 3561.8631 | 89.05% | 95% | 0% | -354.6911 | 2001.6156 | -3550 | -400 | -1948.3844 | 48.71% | 87.58% | 95% | 0% | 2858 | -310
[5 empty] | 2019-02-08 | 33 | 928.5 | 2646 | -276 | 1 | 0 | 2922 | 2456.554 | 2456.554 | 2456.554 | 2581.8631 | 780 | 200 | 3561.8631 | 89.05% | 95% | 0% | -315.7895 | 2140.7645 | -3550 | -400 | -1809.2355 | 45.23% | 87.57% | 95% | 0% | 2922 | -276
[5 empty] | 2019-02-08 | 34 | 929 | 2750 | -257 | 1 | 0 | 3007 | 2589.695 | 2589.695 | 2589.695 | 2580.2968 | 780 | 200 | 3560.2968 | 89.01% | 95% | 0% | -294.0503 | 2295.6446 | -3550 | -400 | -1654.3554 | 41.36% | 87.57% | 95% | 0% | 3007 | -257
[5 empty] | 2019-02-08 | 35 | 929.5 | 2881 | -250 | 1 | 0 | 3131 | 2783.9242 | 2783.9242 | 2783.9242 | 2580.2968 | 780 | 200 | 3560.2968 | 89.01% | 95% | 0% | -286.0412 | 2497.883 | -3550 | -400 | -1452.117 | 36.3% | 87.57% | 95% | 0% | 3131 | -250
[5 empty] | 2019-02-08 | 36 | 930 | 2943 | -248 | 1 | 0 | 3191 | 2877.906 | 2877.906 | 2877.906 | 2580.2968 | 780 | 200 | 3560.2968 | 89.01% | 95% | 0% | -283.7529 | 2594.1532 | -3550 | -400 | -1355.8468 | 33.9% | 87.56% | 95% | 0% | 3191 | -248
[5 empty] | 2019-02-08 | 37 | 930.5 | 2932 | -248 | 0 | 0 | 3180 | 2860.676 | 2860.676 | 2860.676 | 2580.2968 | 780 | 200 | 3560.2968 | 89.01% | 95% | 0% | -283.7529 | 2576.9231 | -2750 | -200 | -373.0769 | 9.327% | 87.56% | 95% | 0% | 3180 | -248
[5 empty] | 2019-02-08 | 38 | 931 | 2873 | -248 | 0 | 0 | 3121 | 2768.2605 | 2768.2605 | 2768.2605 | 2580.2968 | 780 | 200 | 3560.2968 | 89.01% | 95% | 0% | -283.7529 | 2484.5077 | -2750 | -200 | -465.4923 | 11.64% | 87.56% | 95% | 0% | 3121 | -248
[5 empty] | 2019-02-08 | 39 | 931.5 | 2796 | -247 | 0 | 0 | 3043 | 2646.0841 | 2646.0841 | 2646.0841 | 2580.2968 | 780 | 200 | 3560.2968 | 89.01% | 95% | 0% | -282.6087 | 2363.4754 | -2750 | -200 | -586.5246 | 14.66% | 87.55% | 95% | 0% | 3043 | -247
[5 empty] | 2019-02-08 | 40 | 932 | 2703 | -245 | 0 | 0 | 2948 | 2497.2795 | 2497.2795 | 2497.2795 | 2578.7304 | 780 | 200 | 3558.7304 | 88.97% | 95% | 0% | -280.3204 | 2216.9591 | -2750 | -200 | -733.0409 | 18.33% | 87.55% | 95% | 0% | 2948 | -245
[5 empty] | 2019-02-08 | 41 | 932.5 | 2581 | -242 | 0 | 0 | 2823 | 2301.4839 | 2301.4839 | 2301.4839 | 2578.7304 | 780 | 200 | 3558.7304 | 88.97% | 95% | 0% | -276.8879 | 2024.5961 | -2750 | -200 | -925.4039 | 23.14% | 87.54% | 95% | 0% | 2823 | -242
[5 empty] | 2019-02-08 | 42 | 933 | 2454 | -239 | 0 | 0 | 2693 | 2097.8566 | 2097.8566 | 2097.8566 | 2578.7304 | 780 | 200 | 3558.7304 | 88.97% | 95% | 0% | -273.4554 | 1824.4012 | -2750 | -200 | -1125.5988 | 28.14% | 87.54% | 95% | 0% | 2693 | -239
[5 empty] | 2019-02-08 | 43 | 933.5 | 2337 | -240 | 0 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 2578.7304 | 780 | 200 | 3558.7304 | 88.97% | 95% | 0% | -274.5995 | 1641.5587 | -2750 | -200 | -1308.4413 | 32.71% | 87.54% | 95% | 0% | 2577 | -240
[5 empty] | 2019-02-08 | 44 | 934 | 2193 | -241 | 0 | 0 | 2434 | 1692.1682 | 1692.1682 | 1692.1682 | 2578.7304 | 780 | 200 | 3558.7304 | 88.97% | 95% | 0% | -275.7437 | 1416.4245 | -2750 | -200 | -1533.5755 | 38.34% | 87.53% | 95% | 0% | 2434 | -241
[5 empty] | 2019-02-08 | 45 | 934.5 | 2051 | -237 | 0 | 0 | 2288 | 1463.479 | 1463.479 | 1463.479 | 2577.1641 | 780 | 200 | 3557.1641 | 88.93% | 95% | 0% | -271.167 | 1192.3119 | -2750 | -200 | -1757.6881 | 43.94% | 87.52% | 95% | 0% | 2288 | -237
[5 empty] | 2019-02-08 | 46 | 935 | 1949 | -233 | 0 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 2577.1641 | 780 | 200 | 3557.1641 | 88.93% | 95% | 0% | -266.5904 | 1030.854 | -2750 | -200 | -1919.146 | 47.98% | 87.52% | 95% | 0% | 2182 | -233
[5 empty] | 2019-02-08 | 47 | 935.5 | 1822 | -237 | 0 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 2577.1641 | 780 | 200 | 3557.1641 | 88.93% | 95% | 0% | -271.167 | 833.6145 | -2750 | -200 | -2116.3855 | 52.91% | 87.52% | 95% | 0% | 2059 | -237
[5 empty] | 2019-02-08 | 48 | 936 | 1733 | -241 | 0 | 0 | 1974 | 971.6406 | 971.6406 | 971.6406 | 2577.1641 | 780 | 200 | 3557.1641 | 88.93% | 95% | 0% | -275.7437 | 695.8969 | -2750 | -200 | -2254.1031 | 56.35% | 87.52% | 95% | 0% | 1974 | -241
[5 empty] | 2019-02-09 | 1 | 936.5 | 1717 | -237 | 0 | 0 | 1954 | 940.3133 | 940.3133 | 940.3133 | 2577.1641 | 780 | 200 | 3557.1641 | 88.93% | 95% | 0% | -271.167 | 669.1462 | -2750 | -200 | -2280.8538 | 57.02% | 87.51% | 95% | 0% | 1954 | -237
[5 empty] | 2019-02-09 | 2 | 937 | 1713 | -234 | 0 | 0 | 1947 | 929.3487 | 929.3487 | 929.3487 | 2577.1641 | 780 | 200 | 3557.1641 | 88.93% | 95% | 0% | -267.7346 | 661.6142 | -2750 | -200 | -2288.3858 | 57.21% | 87.51% | 95% | 0% | 1947 | -234
[5 empty] | 2019-02-09 | 3 | 937.5 | 1680 | -237 | 0 | 0 | 1917 | 882.3578 | 882.3578 | 882.3578 | 2577.1641 | 780 | 200 | 3557.1641 | 88.93% | 95% | 0% | -271.167 | 611.1907 | -2750 | -200 | -2338.8093 | 58.47% | 87.51% | 95% | 0% | 1917 | -237
[5 empty] | 2019-02-09 | 4 | 938 | 1622 | -240 | 0 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 2575.5977 | 780 | 200 | 3555.5977 | 88.89% | 95% | 0% | -274.5995 | 521.6082 | -2750 | -200 | -2428.3918 | 60.71% | 87.51% | 95% | 0% | 1862 | -240
[5 empty] | 2019-02-09 | 5 | 938.5 | 1577 | -242 | 0 | 0 | 1819 | 728.8541 | 728.8541 | 728.8541 | 2575.5977 | 780 | 200 | 3555.5977 | 88.89% | 95% | 0% | -276.8879 | 451.9662 | -2750 | -200 | -2498.0338 | 62.45% | 87.49% | 95% | 0% | 1819 | -242
[5 empty] | 2019-02-09 | 6 | 939 | 1560 | -245 | 0 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 2575.5977 | 780 | 200 | 3555.5977 | 88.89% | 95% | 0% | -280.3204 | 426.6046 | -2750 | -200 | -2523.3954 | 63.08% | 87.47% | 95% | 0% | 1805 | -245
[5 empty] | 2019-02-09 | 7 | 939.5 | 1519 | -248 | 0 | 0 | 1767 | 647.4031 | 647.4031 | 647.4031 | 2575.5977 | 780 | 200 | 3555.5977 | 88.89% | 95% | 0% | -283.7529 | 363.6503 | -2750 | -200 | -2586.3497 | 64.66% | 87.47% | 95% | 0% | 1767 | -248
[5 empty] | 2019-02-09 | 8 | 940 | 1486 | -250 | 0 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 2575.5977 | 780 | 200 | 3555.5977 | 88.89% | 95% | 0% | -286.0412 | 312.8046 | -2750 | -200 | -2637.1954 | 65.93% | 87.47% | 95% | 0% | 1736 | -250
[5 empty] | 2019-02-09 | 9 | 940.5 | 1465 | -251 | 0 | 0 | 1716 | 567.5185 | 567.5185 | 567.5185 | 2575.5977 | 780 | 200 | 3555.5977 | 88.89% | 95% | 0% | -287.1854 | 280.3332 | -2750 | -200 | -2669.6668 | 66.74% | 87.45% | 95% | 0% | 1716 | -251
[5 empty] | 2019-02-09 | 10 | 941 | 1457 | -252 | 0 | 0 | 1709 | 556.554 | 556.554 | 556.554 | 2574.0313 | 780 | 200 | 3554.0313 | 88.85% | 95% | 0% | -288.3295 | 268.2245 | -2750 | -200 | -2681.7755 | 67.04% | 87.45% | 95% | 0% | 1709 | -252
[5 empty] | 2019-02-09 | 11 | 941.5 | 1471 | -252 | 0 | 0 | 1723 | 578.4831 | 578.4831 | 578.4831 | 2574.0313 | 780 | 200 | 3554.0313 | 88.85% | 95% | 0% | -288.3295 | 290.1536 | -2750 | -200 | -2659.8464 | 66.5% | 87.45% | 95% | 0% | 1723 | -252
[5 empty] | 2019-02-09 | 12 | 942 | 1513 | -251 | 0 | 0 | 1764 | 642.704 | 642.704 | 642.704 | 2574.0313 | 780 | 200 | 3554.0313 | 88.85% | 95% | 0% | -287.1854 | 355.5187 | -2750 | -200 | -2594.4813 | 64.86% | 87.45% | 95% | 0% | 1764 | -251
[5 empty] | 2019-02-09 | 13 | 942.5 | 1614 | -255 | 0 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 2574.0313 | 780 | 200 | 3554.0313 | 88.85% | 95% | 0% | -291.762 | 515.4103 | -2750 | -200 | -2434.5897 | 60.86% | 87.45% | 95% | 0% | 1869 | -255
[5 empty] | 2019-02-09 | 14 | 943 | 1704 | -258 | 0 | 0 | 1962 | 952.8442 | 952.8442 | 952.8442 | 2574.0313 | 780 | 200 | 3554.0313 | 88.85% | 95% | 0% | -295.1945 | 657.6497 | -2750 | -200 | -2292.3503 | 57.31% | 87.45% | 95% | 0% | 1962 | -258
[5 empty] | 2019-02-09 | 15 | 943.5 | 1829 | -260 | 0 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 2574.0313 | 780 | 200 | 3554.0313 | 88.85% | 95% | 0% | -297.4828 | 854.2896 | -2750 | -200 | -2095.7104 | 52.39% | 87.44% | 95% | 0% | 2089 | -260
[5 empty] | 2019-02-09 | 16 | 944 | 1902 | -265 | 1 | 0 | 2167 | 1273.9489 | 1273.9489 | 1273.9489 | 2572.465 | 780 | 200 | 3552.465 | 88.81% | 95% | 0% | -303.2037 | 970.7452 | -3550 | -400 | -2979.2548 | 74.48% | 87.44% | 95% | 0% | 2167 | -265
[5 empty] | 2019-02-09 | 17 | 944.5 | 2012 | -288 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 2572.465 | 780 | 200 | 3552.465 | 88.81% | 95% | 0% | -329.5195 | 1152.7559 | -3550 | -400 | -2797.2441 | 69.93% | 87.44% | 95% | 0% | 2300 | -288
[5 empty] | 2019-02-09 | 18 | 945 | 2060 | -332 | 1 | 0 | 2392 | 1626.3809 | 1626.3809 | 1626.3809 | 2572.465 | 780 | 200 | 3552.465 | 88.81% | 95% | 0% | -379.8627 | 1246.5182 | -3550 | -400 | -2703.4818 | 67.59% | 87.42% | 95% | 0% | 2392 | -332
[5 empty] | 2019-02-09 | 19 | 945.5 | 2077 | -384 | 1 | 0 | 2461 | 1734.46 | 1734.46 | 1734.46 | 2572.465 | 780 | 200 | 3552.465 | 88.81% | 95% | 0% | -439.3593 | 1295.1007 | -3550 | -400 | -2654.8993 | 66.37% | 87.4% | 95% | 0% | 2461 | -384
[5 empty] | 2019-02-09 | 20 | 946 | 2021 | -442 | 1 | 0 | 2463 | 1737.5927 | 1737.5927 | 1737.5927 | 2572.465 | 780 | 200 | 3552.465 | 88.81% | 95% | 0% | -505.7208 | 1231.8719 | -3550 | -400 | -2718.1281 | 67.95% | 87.4% | 95% | 0% | 2463 | -442
[5 empty] | 2019-02-09 | 21 | 946.5 | 1986 | -480 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 2570.8986 | 780 | 200 | 3550.8986 | 88.77% | 95% | 0% | -549.1991 | 1193.0928 | -3550 | -400 | -2756.9072 | 68.92% | 87.38% | 95% | 0% | 2466 | -480
[5 empty] | 2019-02-09 | 22 | 947 | 1875 | -577 | 1 | 0 | 2452 | 1720.3627 | 1720.3627 | 1720.3627 | 2570.8986 | 780 | 200 | 3550.8986 | 88.77% | 95% | 0% | -660.1831 | 1060.1797 | -3550 | -400 | -2889.8203 | 72.25% | 87.37% | 95% | 0% | 2452 | -577
[5 empty] | 2019-02-09 | 23 | 947.5 | 1846 | -574 | 1 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 2570.8986 | 780 | 200 | 3550.8986 | 88.77% | 95% | 0% | -656.7506 | 1013.4885 | -3550 | -400 | -2936.5115 | 73.41% | 87.36% | 95% | 0% | 2420 | -574
[5 empty] | 2019-02-09 | 24 | 948 | 1788 | -603 | 1 | 0 | 2391 | 1624.8145 | 1624.8145 | 1624.8145 | 2570.8986 | 780 | 200 | 3550.8986 | 88.77% | 95% | 0% | -689.9314 | 934.8832 | -3550 | -400 | -3015.1168 | 75.38% | 87.36% | 95% | 0% | 2391 | -603
[5 empty] | 2019-02-09 | 25 | 948.5 | 1772 | -593 | 1 | 0 | 2365 | 1584.089 | 1584.089 | 1584.089 | 2570.8986 | 780 | 200 | 3550.8986 | 88.77% | 95% | 0% | -678.4897 | 905.5993 | -3550 | -400 | -3044.4007 | 76.11% | 87.35% | 95% | 0% | 2365 | -593
[5 empty] | 2019-02-09 | 26 | 949 | 1762 | -586 | 1 | 0 | 2348 | 1557.4608 | 1557.4608 | 1557.4608 | 2570.8986 | 780 | 200 | 3550.8986 | 88.77% | 95% | 0% | -670.4805 | 886.9803 | -3550 | -400 | -3063.0197 | 76.58% | 87.35% | 95% | 0% | 2348 | -586
[5 empty] | 2019-02-09 | 27 | 949.5 | 1781 | -571 | 1 | 0 | 2352 | 1563.7263 | 1563.7263 | 1563.7263 | 2570.8986 | 780 | 200 | 3550.8986 | 88.77% | 95% | 0% | -653.3181 | 910.4082 | -3550 | -400 | -3039.5918 | 75.99% | 87.34% | 95% | 0% | 2352 | -571
[5 empty] | 2019-02-09 | 28 | 950 | 1841 | -506 | 1 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 2570.8986 | 780 | 200 | 3550.8986 | 88.77% | 95% | 0% | -578.9474 | 976.9471 | -3550 | -400 | -2973.0529 | 74.33% | 87.32% | 95% | 0% | 2347 | -506
[5 empty] | 2019-02-09 | 29 | 950.5 | 1885 | -471 | 1 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 2570.8986 | 780 | 200 | 3550.8986 | 88.77% | 95% | 0% | -538.9016 | 1031.0902 | -3550 | -400 | -2918.9098 | 72.97% | 87.32% | 95% | 0% | 2356 | -471
[5 empty] | 2019-02-09 | 30 | 951 | 1972 | -412 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 2569.3322 | 780 | 200 | 3549.3322 | 88.73% | 95% | 0% | -471.3959 | 1142.4541 | -3550 | -400 | -2807.5459 | 70.19% | 87.31% | 95% | 0% | 2384 | -412
[5 empty] | 2019-02-09 | 31 | 951.5 | 2083 | -350 | 1 | 0 | 2433 | 1690.6018 | 1690.6018 | 1690.6018 | 2569.3322 | 780 | 200 | 3549.3322 | 88.73% | 95% | 0% | -400.4577 | 1290.1441 | -3550 | -400 | -2659.8559 | 66.5% | 87.31% | 95% | 0% | 2433 | -350
[5 empty] | 2019-02-09 | 32 | 952 | 2205 | -289 | 1 | 0 | 2494 | 1786.15 | 1786.15 | 1786.15 | 2569.3322 | 780 | 200 | 3549.3322 | 88.73% | 95% | 0% | -330.6636 | 1455.4864 | -3550 | -400 | -2494.5136 | 62.36% | 87.29% | 95% | 0% | 2494 | -289
[5 empty] | 2019-02-09 | 33 | 952.5 | 2362 | -231 | 1 | 0 | 2593 | 1941.2201 | 1941.2201 | 1941.2201 | 2569.3322 | 780 | 200 | 3549.3322 | 88.73% | 95% | 0% | -264.3021 | 1676.9181 | -3550 | -400 | -2273.0819 | 56.83% | 87.28% | 95% | 0% | 2593 | -231
[5 empty] | 2019-02-09 | 34 | 953 | 2531 | -197 | 1 | 0 | 2728 | 2152.6793 | 2152.6793 | 2152.6793 | 2569.3322 | 780 | 200 | 3549.3322 | 88.73% | 95% | 0% | -225.4005 | 1927.2788 | -3550 | -400 | -2022.7212 | 50.57% | 87.28% | 95% | 0% | 2728 | -197
[5 empty] | 2019-02-09 | 35 | 953.5 | 2694 | -186 | 1 | 0 | 2880 | 2390.7667 | 2390.7667 | 2390.7667 | 2569.3322 | 780 | 200 | 3549.3322 | 88.73% | 95% | 0% | -212.8146 | 2177.952 | -3550 | -400 | -1772.048 | 44.3% | 87.27% | 95% | 0% | 2880 | -186
[5 empty] | 2019-02-09 | 36 | 954 | 2777 | -177 | 1 | 0 | 2954 | 2506.6777 | 2506.6777 | 2506.6777 | 2569.3322 | 780 | 200 | 3549.3322 | 88.73% | 95% | 0% | -202.5172 | 2304.1605 | -3550 | -400 | -1645.8395 | 41.15% | 87.27% | 95% | 0% | 2954 | -177
[5 empty] | 2019-02-09 | 37 | 954.5 | 2756 | -172 | 0 | 0 | 2928 | 2465.9522 | 2465.9522 | 2465.9522 | 2569.3322 | 780 | 200 | 3549.3322 | 88.73% | 95% | 0% | -196.7963 | 2269.1558 | -2750 | -200 | -680.8442 | 17.02% | 87.27% | 95% | 0% | 2928 | -172
[5 empty] | 2019-02-09 | 38 | 955 | 2728 | -168 | 0 | 0 | 2896 | 2415.8285 | 2415.8285 | 2415.8285 | 2569.3322 | 780 | 200 | 3549.3322 | 88.73% | 95% | 0% | -192.2197 | 2223.6088 | -2750 | -200 | -726.3912 | 18.16% | 87.26% | 95% | 0% | 2896 | -168
[5 empty] | 2019-02-09 | 39 | 955.5 | 2660 | -163 | 0 | 0 | 2823 | 2301.4839 | 2301.4839 | 2301.4839 | 2567.7659 | 780 | 200 | 3547.7659 | 88.69% | 95% | 0% | -186.4989 | 2114.9851 | -2750 | -200 | -835.0149 | 20.88% | 87.25% | 95% | 0% | 2823 | -163
[5 empty] | 2019-02-09 | 40 | 956 | 2591 | -158 | 0 | 0 | 2749 | 2185.573 | 2185.573 | 2185.573 | 2567.7659 | 780 | 200 | 3547.7659 | 88.69% | 95% | 0% | -180.778 | 2004.7949 | -2750 | -200 | -945.2051 | 23.63% | 87.25% | 95% | 0% | 2749 | -158
[5 empty] | 2019-02-09 | 41 | 956.5 | 2541 | -153 | 0 | 0 | 2694 | 2099.4229 | 2099.4229 | 2099.4229 | 2567.7659 | 780 | 200 | 3547.7659 | 88.69% | 95% | 0% | -175.0572 | 1924.3657 | -2750 | -200 | -1025.6343 | 25.64% | 87.25% | 95% | 0% | 2694 | -153
[5 empty] | 2019-02-09 | 42 | 957 | 2470 | -149 | 0 | 0 | 2619 | 1981.9456 | 1981.9456 | 1981.9456 | 2567.7659 | 780 | 200 | 3547.7659 | 88.69% | 95% | 0% | -170.4805 | 1811.465 | -2750 | -200 | -1138.535 | 28.46% | 87.24% | 95% | 0% | 2619 | -149
[5 empty] | 2019-02-09 | 43 | 957.5 | 2396 | -144 | 0 | 0 | 2540 | 1858.2028 | 1858.2028 | 1858.2028 | 2566.1995 | 780 | 200 | 3546.1995 | 88.65% | 95% | 0% | -164.7597 | 1693.4431 | -2750 | -200 | -1256.5569 | 31.41% | 87.24% | 95% | 0% | 2540 | -144
[5 empty] | 2019-02-09 | 44 | 958 | 2323 | -140 | 0 | 0 | 2463 | 1737.5927 | 1737.5927 | 1737.5927 | 2566.1995 | 780 | 200 | 3546.1995 | 88.65% | 95% | 0% | -160.1831 | 1577.4097 | -2750 | -200 | -1372.5903 | 34.31% | 87.23% | 95% | 0% | 2463 | -140
[5 empty] | 2019-02-09 | 45 | 958.5 | 2222 | -134 | 0 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 2566.1995 | 780 | 200 | 3546.1995 | 88.65% | 95% | 0% | -153.3181 | 1416.6737 | -2750 | -200 | -1533.3263 | 38.33% | 87.23% | 95% | 0% | 2356 | -134
[5 empty] | 2019-02-09 | 46 | 959 | 2147 | -128 | 0 | 0 | 2275 | 1443.1162 | 1443.1162 | 1443.1162 | 2566.1995 | 780 | 200 | 3546.1995 | 88.65% | 95% | 0% | -146.4531 | 1296.6632 | -2750 | -200 | -1653.3368 | 41.33% | 87.22% | 95% | 0% | 2275 | -128
[5 empty] | 2019-02-09 | 47 | 959.5 | 2057 | -116 | 0 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 2564.6331 | 780 | 200 | 3544.6331 | 88.62% | 95% | 0% | -132.7231 | 1150.624 | -2750 | -200 | -1799.376 | 44.98% | 87.22% | 95% | 0% | 2173 | -116
[5 empty] | 2019-02-09 | 48 | 960 | 1998 | -104 | 0 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 2564.6331 | 780 | 200 | 3544.6331 | 88.62% | 95% | 0% | -118.9931 | 1053.1421 | -2750 | -200 | -1896.8579 | 47.42% | 87.22% | 95% | 0% | 2102 | -104
[5 empty] | 2019-02-10 | 1 | 960.5 | 2000 | -98 | 0 | 0 | 2098 | 1165.8697 | 1165.8697 | 1165.8697 | 2563.0668 | 780 | 200 | 3543.0668 | 88.58% | 95% | 0% | -112.1281 | 1053.7416 | -2750 | -200 | -1896.2584 | 47.41% | 87.21% | 95% | 0% | 2098 | -98
[5 empty] | 2019-02-10 | 2 | 961 | 2049 | -92 | 0 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 2563.0668 | 780 | 200 | 3543.0668 | 88.58% | 95% | 0% | -105.2632 | 1127.9603 | -2750 | -200 | -1822.0397 | 45.55% | 87.18% | 95% | 0% | 2141 | -92
[5 empty] | 2019-02-10 | 3 | 961.5 | 2018 | -87 | 0 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 2561.5004 | 780 | 200 | 3541.5004 | 88.54% | 95% | 0% | -99.5423 | 1077.292 | -2750 | -200 | -1872.708 | 46.82% | 87.18% | 95% | 0% | 2105 | -87
[5 empty] | 2019-02-10 | 4 | 962 | 1990 | -82 | 0 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 2561.5004 | 780 | 200 | 3541.5004 | 88.54% | 95% | 0% | -93.8215 | 1031.3228 | -2750 | -200 | -1918.6772 | 47.97% | 87.18% | 95% | 0% | 2072 | -82
[5 empty] | 2019-02-10 | 5 | 962.5 | 1966 | -78 | 0 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 2561.5004 | 780 | 200 | 3541.5004 | 88.54% | 95% | 0% | -89.2449 | 992.0412 | -2750 | -200 | -1957.9588 | 48.95% | 87.17% | 95% | 0% | 2044 | -78
[5 empty] | 2019-02-10 | 6 | 963 | 1949 | -74 | 0 | 0 | 2023 | 1048.3924 | 1048.3924 | 1048.3924 | 2561.5004 | 780 | 200 | 3541.5004 | 88.54% | 95% | 0% | -84.6682 | 963.7242 | -2750 | -200 | -1986.2758 | 49.66% | 87.17% | 95% | 0% | 2023 | -74
[5 empty] | 2019-02-10 | 7 | 963.5 | 1912 | -69 | 0 | 0 | 1981 | 982.6051 | 982.6051 | 982.6051 | 2561.5004 | 780 | 200 | 3541.5004 | 88.54% | 95% | 0% | -78.9474 | 903.6577 | -2750 | -200 | -2046.3423 | 51.16% | 87.16% | 95% | 0% | 1981 | -69
[5 empty] | 2019-02-10 | 8 | 964 | 1871 | -63 | 0 | 0 | 1934 | 908.986 | 908.986 | 908.986 | 2559.934 | 780 | 200 | 3539.934 | 88.5% | 95% | 0% | -72.0824 | 836.9036 | -2750 | -200 | -2113.0964 | 52.83% | 87.13% | 95% | 0% | 1934 | -63
[5 empty] | 2019-02-10 | 9 | 964.5 | 1841 | -64 | 0 | 0 | 1905 | 863.5614 | 863.5614 | 863.5614 | 2559.934 | 780 | 200 | 3539.934 | 88.5% | 95% | 0% | -73.2265 | 790.3349 | -2750 | -200 | -2159.6651 | 53.99% | 87.12% | 95% | 0% | 1905 | -64
[5 empty] | 2019-02-10 | 10 | 965 | 1838 | -64 | 0 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 2559.934 | 780 | 200 | 3539.934 | 88.5% | 95% | 0% | -73.2265 | 785.6358 | -2750 | -200 | -2164.3642 | 54.11% | 87.12% | 95% | 0% | 1902 | -64
[5 empty] | 2019-02-10 | 11 | 965.5 | 1845 | -67 | 0 | 0 | 1912 | 874.526 | 874.526 | 874.526 | 2559.934 | 780 | 200 | 3539.934 | 88.5% | 95% | 0% | -76.659 | 797.8669 | -2750 | -200 | -2152.1331 | 53.8% | 87.11% | 95% | 0% | 1912 | -67
[5 empty] | 2019-02-10 | 12 | 966 | 1854 | -69 | 0 | 0 | 1923 | 891.756 | 891.756 | 891.756 | 2559.934 | 780 | 200 | 3539.934 | 88.5% | 95% | 0% | -78.9474 | 812.8086 | -2750 | -200 | -2137.1914 | 53.43% | 87.11% | 95% | 0% | 1923 | -69
[5 empty] | 2019-02-10 | 13 | 966.5 | 1925 | -70 | 0 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 2558.3677 | 780 | 200 | 3538.3677 | 88.46% | 95% | 0% | -80.0915 | 924.4427 | -2750 | -200 | -2025.5573 | 50.64% | 87.11% | 95% | 0% | 1995 | -70
[5 empty] | 2019-02-10 | 14 | 967 | 1977 | -71 | 0 | 0 | 2048 | 1087.5515 | 1087.5515 | 1087.5515 | 2558.3677 | 780 | 200 | 3538.3677 | 88.46% | 95% | 0% | -81.2357 | 1006.3158 | -2750 | -200 | -1943.6842 | 48.59% | 87.11% | 95% | 0% | 2048 | -71
[5 empty] | 2019-02-10 | 15 | 967.5 | 2055 | -74 | 0 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 2558.3677 | 780 | 200 | 3538.3677 | 88.46% | 95% | 0% | -84.6682 | 1129.7588 | -2750 | -200 | -1820.2412 | 45.51% | 87.11% | 95% | 0% | 2129 | -74
[5 empty] | 2019-02-10 | 16 | 968 | 2100 | -78 | 0 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 2558.3677 | 780 | 200 | 3538.3677 | 88.46% | 95% | 0% | -89.2449 | 1201.934 | -2750 | -200 | -1748.066 | 43.7% | 87.1% | 95% | 0% | 2178 | -78
[5 empty] | 2019-02-10 | 17 | 968.5 | 2210 | -88 | 0 | 0 | 2298 | 1479.1426 | 1479.1426 | 1479.1426 | 2558.3677 | 780 | 200 | 3538.3677 | 88.46% | 95% | 0% | -100.6865 | 1378.4561 | -2750 | -200 | -1571.5439 | 39.29% | 87.09% | 95% | 0% | 2298 | -88
[5 empty] | 2019-02-10 | 18 | 969 | 2310 | -103 | 0 | 0 | 2413 | 1659.2745 | 1659.2745 | 1659.2745 | 2558.3677 | 780 | 200 | 3538.3677 | 88.46% | 95% | 0% | -117.849 | 1541.4256 | -2750 | -200 | -1408.5744 | 35.21% | 87.07% | 95% | 0% | 2413 | -103
[5 empty] | 2019-02-10 | 19 | 969.5 | 2392 | -128 | 0 | 0 | 2520 | 1826.8755 | 1826.8755 | 1826.8755 | 2558.3677 | 780 | 200 | 3538.3677 | 88.46% | 95% | 0% | -146.4531 | 1680.4224 | -2750 | -200 | -1269.5776 | 31.74% | 87.06% | 95% | 0% | 2520 | -128
[5 empty] | 2019-02-10 | 20 | 970 | 2412 | -162 | 1 | 0 | 2574 | 1911.4592 | 1911.4592 | 1911.4592 | 2556.8013 | 780 | 200 | 3536.8013 | 88.42% | 95% | 0% | -185.3547 | 1726.1045 | -3550 | -400 | -2223.8955 | 55.6% | 87.04% | 95% | 0% | 2574 | -162
[5 empty] | 2019-02-10 | 21 | 970.5 | 2410 | -209 | 1 | 0 | 2619 | 1981.9456 | 1981.9456 | 1981.9456 | 2556.8013 | 780 | 200 | 3536.8013 | 88.42% | 95% | 0% | -239.1304 | 1742.8152 | -3550 | -400 | -2207.1848 | 55.18% | 87.04% | 95% | 0% | 2619 | -209
[5 empty] | 2019-02-10 | 22 | 971 | 2368 | -269 | 1 | 0 | 2637 | 2010.1401 | 2010.1401 | 2010.1401 | 2555.235 | 780 | 200 | 3535.235 | 88.38% | 95% | 0% | -307.7803 | 1702.3598 | -3550 | -400 | -2247.6402 | 56.19% | 87.04% | 95% | 0% | 2637 | -269
[5 empty] | 2019-02-10 | 23 | 971.5 | 2366 | -311 | 1 | 0 | 2677 | 2072.7947 | 2072.7947 | 2072.7947 | 2555.235 | 780 | 200 | 3535.235 | 88.38% | 95% | 0% | -355.8352 | 1716.9595 | -3550 | -400 | -2233.0405 | 55.83% | 87.03% | 95% | 0% | 2677 | -311
[5 empty] | 2019-02-10 | 24 | 972 | 2336 | -344 | 1 | 0 | 2680 | 2077.4938 | 2077.4938 | 2077.4938 | 2555.235 | 780 | 200 | 3535.235 | 88.38% | 95% | 0% | -393.5927 | 1683.9011 | -3550 | -400 | -2266.0989 | 56.65% | 87.03% | 95% | 0% | 2680 | -344
[5 empty] | 2019-02-10 | 25 | 972.5 | 2291 | -383 | 1 | 0 | 2674 | 2068.0956 | 2068.0956 | 2068.0956 | 2555.235 | 780 | 200 | 3535.235 | 88.38% | 95% | 0% | -438.2151 | 1629.8805 | -3550 | -400 | -2320.1195 | 58% | 87.02% | 95% | 0% | 2674 | -383
[5 empty] | 2019-02-10 | 26 | 973 | 2236 | -404 | 1 | 0 | 2640 | 2014.8392 | 2014.8392 | 2014.8392 | 2555.235 | 780 | 200 | 3535.235 | 88.38% | 95% | 0% | -462.2426 | 1552.5967 | -3550 | -400 | -2397.4033 | 59.94% | 87.02% | 95% | 0% | 2640 | -404
[5 empty] | 2019-02-10 | 27 | 973.5 | 2179 | -419 | 1 | 0 | 2598 | 1949.0519 | 1949.0519 | 1949.0519 | 2553.6686 | 780 | 200 | 3533.6686 | 88.34% | 95% | 0% | -479.405 | 1469.6469 | -3550 | -400 | -2480.3531 | 62.01% | 87.01% | 95% | 0% | 2598 | -419
[5 empty] | 2019-02-10 | 28 | 974 | 2142 | -398 | 1 | 0 | 2540 | 1858.2028 | 1858.2028 | 1858.2028 | 2553.6686 | 780 | 200 | 3533.6686 | 88.34% | 95% | 0% | -455.3776 | 1402.8252 | -3550 | -400 | -2547.1748 | 63.68% | 87% | 95% | 0% | 2540 | -398
[5 empty] | 2019-02-10 | 29 | 974.5 | 2142 | -391 | 1 | 0 | 2533 | 1847.2383 | 1847.2383 | 1847.2383 | 2553.6686 | 780 | 200 | 3533.6686 | 88.34% | 95% | 0% | -447.3684 | 1399.8698 | -3550 | -400 | -2550.1302 | 63.75% | 87% | 95% | 0% | 2533 | -391
[5 empty] | 2019-02-10 | 30 | 975 | 2157 | -374 | 1 | 0 | 2531 | 1844.1055 | 1844.1055 | 1844.1055 | 2553.6686 | 780 | 200 | 3533.6686 | 88.34% | 95% | 0% | -427.9176 | 1416.1879 | -3550 | -400 | -2533.8121 | 63.35% | 87% | 95% | 0% | 2531 | -374
[5 empty] | 2019-02-10 | 31 | 975.5 | 2244 | -328 | 1 | 0 | 2572 | 1908.3265 | 1908.3265 | 1908.3265 | 2552.1022 | 780 | 200 | 3532.1022 | 88.3% | 95% | 0% | -375.286 | 1533.0404 | -3550 | -400 | -2416.9596 | 60.42% | 87% | 95% | 0% | 2572 | -328
[5 empty] | 2019-02-10 | 32 | 976 | 2389 | -271 | 1 | 0 | 2660 | 2046.1665 | 2046.1665 | 2046.1665 | 2552.1022 | 780 | 200 | 3532.1022 | 88.3% | 95% | 0% | -310.0686 | 1736.0979 | -3550 | -400 | -2213.9021 | 55.35% | 86.99% | 95% | 0% | 2660 | -271
[5 empty] | 2019-02-10 | 33 | 976.5 | 2557 | -201 | 1 | 0 | 2758 | 2199.6702 | 2199.6702 | 2199.6702 | 2552.1022 | 780 | 200 | 3532.1022 | 88.3% | 95% | 0% | -229.9771 | 1969.6931 | -3550 | -400 | -1980.3069 | 49.51% | 86.99% | 95% | 0% | 2758 | -201
[5 empty] | 2019-02-10 | 34 | 977 | 2763 | -140 | 1 | 0 | 2903 | 2426.7931 | 2426.7931 | 2426.7931 | 2552.1022 | 780 | 200 | 3532.1022 | 88.3% | 95% | 0% | -160.1831 | 2266.61 | -3550 | -400 | -1683.39 | 42.08% | 86.97% | 95% | 0% | 2903 | -140
[5 empty] | 2019-02-10 | 35 | 977.5 | 2966 | -124 | 1 | 0 | 3090 | 2719.7032 | 2719.7032 | 2719.7032 | 2552.1022 | 780 | 200 | 3532.1022 | 88.3% | 95% | 0% | -141.8764 | 2577.8268 | -3550 | -400 | -1372.1732 | 34.3% | 86.97% | 95% | 0% | 3090 | -124
[5 empty] | 2019-02-10 | 36 | 978 | 3047 | -121 | 1 | 0 | 3168 | 2841.8796 | 2841.8796 | 2841.8796 | 2550.5359 | 780 | 200 | 3530.5359 | 88.26% | 95% | 0% | -138.4439 | 2703.4357 | -3550 | -400 | -1246.5643 | 31.16% | 86.97% | 95% | 0% | 3168 | -121
[5 empty] | 2019-02-10 | 37 | 978.5 | 3025 | -121 | 0 | 0 | 3146 | 2807.4196 | 2807.4196 | 2807.4196 | 2550.5359 | 780 | 200 | 3530.5359 | 88.26% | 95% | 0% | -138.4439 | 2668.9757 | -2750 | -200 | -281.0243 | 7.026% | 86.96% | 95% | 0% | 3146 | -121
[5 empty] | 2019-02-10 | 38 | 979 | 2985 | -120 | 0 | 0 | 3105 | 2743.1987 | 2743.1987 | 2743.1987 | 2550.5359 | 780 | 200 | 3530.5359 | 88.26% | 95% | 0% | -137.2998 | 2605.8989 | -2750 | -200 | -344.1011 | 8.603% | 86.95% | 95% | 0% | 3105 | -120
[5 empty] | 2019-02-10 | 39 | 979.5 | 2968 | -121 | 0 | 0 | 3089 | 2718.1369 | 2718.1369 | 2718.1369 | 2550.5359 | 780 | 200 | 3530.5359 | 88.26% | 95% | 0% | -138.4439 | 2579.6929 | -2750 | -200 | -370.3071 | 9.258% | 86.95% | 95% | 0% | 3089 | -121
[5 empty] | 2019-02-10 | 40 | 980 | 2883 | -121 | 0 | 0 | 3004 | 2584.9959 | 2584.9959 | 2584.9959 | 2548.9695 | 780 | 200 | 3528.9695 | 88.22% | 95% | 0% | -138.4439 | 2446.5519 | -2750 | -200 | -503.4481 | 12.59% | 86.94% | 95% | 0% | 3004 | -121
[5 empty] | 2019-02-10 | 41 | 980.5 | 2787 | -122 | 0 | 0 | 2909 | 2436.1913 | 2436.1913 | 2436.1913 | 2548.9695 | 780 | 200 | 3528.9695 | 88.22% | 95% | 0% | -139.5881 | 2296.6032 | -2750 | -200 | -653.3968 | 16.33% | 86.93% | 95% | 0% | 2909 | -122
[5 empty] | 2019-02-10 | 42 | 981 | 2671 | -122 | 0 | 0 | 2793 | 2254.493 | 2254.493 | 2254.493 | 2548.9695 | 780 | 200 | 3528.9695 | 88.22% | 95% | 0% | -139.5881 | 2114.9049 | -2750 | -200 | -835.0951 | 20.88% | 86.92% | 95% | 0% | 2793 | -122
[5 empty] | 2019-02-10 | 43 | 981.5 | 2560 | -124 | 0 | 0 | 2684 | 2083.7593 | 2083.7593 | 2083.7593 | 2548.9695 | 780 | 200 | 3528.9695 | 88.22% | 95% | 0% | -141.8764 | 1941.8828 | -2750 | -200 | -1008.1172 | 25.2% | 86.91% | 95% | 0% | 2684 | -124
[5 empty] | 2019-02-10 | 44 | 982 | 2407 | -126 | 0 | 0 | 2533 | 1847.2383 | 1847.2383 | 1847.2383 | 2548.9695 | 780 | 200 | 3528.9695 | 88.22% | 95% | 0% | -144.1648 | 1703.0735 | -2750 | -200 | -1246.9265 | 31.17% | 86.91% | 95% | 0% | 2533 | -126
[5 empty] | 2019-02-10 | 45 | 982.5 | 2267 | -127 | 0 | 0 | 2394 | 1629.5136 | 1629.5136 | 1629.5136 | 2547.4031 | 780 | 200 | 3527.4031 | 88.19% | 95% | 0% | -145.3089 | 1484.2047 | -2750 | -200 | -1465.7953 | 36.64% | 86.9% | 95% | 0% | 2394 | -127
[5 empty] | 2019-02-10 | 46 | 983 | 2143 | -128 | 0 | 0 | 2271 | 1436.8508 | 1436.8508 | 1436.8508 | 2547.4031 | 780 | 200 | 3527.4031 | 88.19% | 95% | 0% | -146.4531 | 1290.3977 | -2750 | -200 | -1659.6023 | 41.49% | 86.89% | 95% | 0% | 2271 | -128
[5 empty] | 2019-02-10 | 47 | 983.5 | 2010 | -125 | 0 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 2547.4031 | 780 | 200 | 3527.4031 | 88.19% | 95% | 0% | -143.0206 | 1080.8046 | -2750 | -200 | -1869.1954 | 46.73% | 86.89% | 95% | 0% | 2135 | -125
[5 empty] | 2019-02-10 | 48 | 984 | 1924 | -121 | 0 | 0 | 2045 | 1082.8524 | 1082.8524 | 1082.8524 | 2547.4031 | 780 | 200 | 3527.4031 | 88.19% | 95% | 0% | -138.4439 | 944.4085 | -2750 | -200 | -2005.5915 | 50.14% | 86.89% | 95% | 0% | 2045 | -121
[5 empty] | 2019-02-11 | 1 | 984.5 | 1940 | -118 | 0 | 0 | 2058 | 1103.2152 | 1103.2152 | 1103.2152 | 2547.4031 | 780 | 200 | 3527.4031 | 88.19% | 95% | 0% | -135.0114 | 968.2037 | -2750 | -200 | -1981.7963 | 49.54% | 86.87% | 95% | 0% | 2058 | -118
[5 empty] | 2019-02-11 | 2 | 985 | 1993 | -116 | 0 | 0 | 2109 | 1183.0998 | 1183.0998 | 1183.0998 | 2545.8368 | 780 | 200 | 3525.8368 | 88.15% | 95% | 0% | -132.7231 | 1050.3766 | -2750 | -200 | -1899.6234 | 47.49% | 86.86% | 95% | 0% | 2109 | -116
[5 empty] | 2019-02-11 | 3 | 985.5 | 2007 | -113 | 0 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 2545.8368 | 780 | 200 | 3525.8368 | 88.15% | 95% | 0% | -129.2906 | 1071.0391 | -2750 | -200 | -1878.9609 | 46.97% | 86.86% | 95% | 0% | 2120 | -113
[5 empty] | 2019-02-11 | 4 | 986 | 1955 | -110 | 0 | 0 | 2065 | 1114.1797 | 1114.1797 | 1114.1797 | 2545.8368 | 780 | 200 | 3525.8368 | 88.15% | 95% | 0% | -125.8581 | 988.3216 | -2750 | -200 | -1961.6784 | 49.04% | 86.85% | 95% | 0% | 2065 | -110
[5 empty] | 2019-02-11 | 5 | 986.5 | 1917 | -106 | 0 | 0 | 2023 | 1048.3924 | 1048.3924 | 1048.3924 | 2545.8368 | 780 | 200 | 3525.8368 | 88.15% | 95% | 0% | -121.2815 | 927.111 | -2750 | -200 | -2022.889 | 50.57% | 86.85% | 95% | 0% | 2023 | -106
[5 empty] | 2019-02-11 | 6 | 987 | 1930 | -102 | 0 | 0 | 2032 | 1062.4897 | 1062.4897 | 1062.4897 | 2545.8368 | 780 | 200 | 3525.8368 | 88.15% | 95% | 0% | -116.7048 | 945.7849 | -2750 | -200 | -2004.2151 | 50.11% | 86.85% | 95% | 0% | 2032 | -102
[5 empty] | 2019-02-11 | 7 | 987.5 | 1915 | -98 | 0 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 2544.2704 | 780 | 200 | 3524.2704 | 88.11% | 95% | 0% | -112.1281 | 920.6006 | -2750 | -200 | -2029.3994 | 50.73% | 86.85% | 95% | 0% | 2013 | -98
[5 empty] | 2019-02-11 | 8 | 988 | 1890 | -93 | 0 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 2544.2704 | 780 | 200 | 3524.2704 | 88.11% | 95% | 0% | -106.4073 | 879.3305 | -2750 | -200 | -2070.6695 | 51.77% | 86.85% | 95% | 0% | 1983 | -93
[5 empty] | 2019-02-11 | 9 | 988.5 | 1890 | -89 | 0 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 2544.2704 | 780 | 200 | 3524.2704 | 88.11% | 95% | 0% | -101.8307 | 877.6417 | -2750 | -200 | -2072.3583 | 51.81% | 86.85% | 95% | 0% | 1979 | -89
[5 empty] | 2019-02-11 | 10 | 989 | 1905 | -84 | 0 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 2542.704 | 780 | 200 | 3522.704 | 88.07% | 95% | 0% | -96.1098 | 899.0262 | -2750 | -200 | -2050.9738 | 51.27% | 86.84% | 95% | 0% | 1989 | -84
[5 empty] | 2019-02-11 | 11 | 989.5 | 1977 | -80 | 0 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 2542.704 | 780 | 200 | 3522.704 | 88.07% | 95% | 0% | -91.5332 | 1010.1156 | -2750 | -200 | -1939.8844 | 48.5% | 86.84% | 95% | 0% | 2057 | -80
[5 empty] | 2019-02-11 | 12 | 990 | 2097 | -77 | 0 | 0 | 2174 | 1284.9134 | 1284.9134 | 1284.9134 | 2542.704 | 780 | 200 | 3522.704 | 88.07% | 95% | 0% | -88.1007 | 1196.8128 | -2750 | -200 | -1753.1872 | 43.83% | 86.82% | 95% | 0% | 2174 | -77
[5 empty] | 2019-02-11 | 13 | 990.5 | 2360 | -73 | 0 | 0 | 2433 | 1690.6018 | 1690.6018 | 1690.6018 | 2541.1377 | 780 | 200 | 3521.1377 | 88.03% | 95% | 0% | -83.524 | 1607.0778 | -2750 | -200 | -1342.9222 | 33.57% | 86.82% | 95% | 0% | 2433 | -73
[5 empty] | 2019-02-11 | 14 | 991 | 2634 | -69 | 0 | 0 | 2703 | 2113.5202 | 2113.5202 | 2113.5202 | 2541.1377 | 780 | 200 | 3521.1377 | 88.03% | 95% | 0% | -78.9474 | 2034.5728 | -2750 | -200 | -915.4272 | 22.89% | 86.81% | 95% | 0% | 2703 | -69
[5 empty] | 2019-02-11 | 15 | 991.5 | 2880 | -67 | 0 | 0 | 2947 | 2495.7131 | 2495.7131 | 2495.7131 | 2541.1377 | 780 | 200 | 3521.1377 | 88.03% | 95% | 0% | -76.659 | 2419.0541 | -2750 | -200 | -530.9459 | 13.27% | 86.81% | 95% | 0% | 2947 | -67
[5 empty] | 2019-02-11 | 16 | 992 | 2957 | -71 | 0 | 0 | 3028 | 2622.5886 | 2622.5886 | 2622.5886 | 2541.1377 | 780 | 200 | 3521.1377 | 88.03% | 95% | 0% | -81.2357 | 2541.3529 | -2750 | -200 | -408.6471 | 10.22% | 86.81% | 95% | 0% | 3028 | -71
[5 empty] | 2019-02-11 | 17 | 992.5 | 2991 | -105 | 0 | 0 | 3096 | 2729.1014 | 2729.1014 | 2729.1014 | 2541.1377 | 780 | 200 | 3521.1377 | 88.03% | 95% | 0% | -120.1373 | 2608.9641 | -2750 | -200 | -341.0359 | 8.526% | 86.79% | 95% | 0% | 3096 | -105
[5 empty] | 2019-02-11 | 18 | 993 | 2964 | -157 | 0 | 0 | 3121 | 2768.2605 | 2768.2605 | 2768.2605 | 2541.1377 | 780 | 200 | 3521.1377 | 88.03% | 95% | 0% | -179.6339 | 2588.6266 | -2750 | -200 | -361.3734 | 9.034% | 86.79% | 95% | 0% | 3121 | -157
[5 empty] | 2019-02-11 | 19 | 993.5 | 2940 | -202 | 0 | 0 | 3142 | 2801.1542 | 2801.1542 | 2801.1542 | 2539.5713 | 780 | 200 | 3519.5713 | 87.99% | 95% | 0% | -231.1213 | 2570.0329 | -2750 | -200 | -379.9671 | 9.499% | 86.77% | 95% | 0% | 3142 | -202
[5 empty] | 2019-02-11 | 20 | 994 | 2847 | -260 | 1 | 0 | 3107 | 2746.3314 | 2746.3314 | 2746.3314 | 2539.5713 | 780 | 200 | 3519.5713 | 87.99% | 95% | 0% | -297.4828 | 2448.8486 | -3550 | -400 | -1501.1514 | 37.53% | 86.76% | 95% | 0% | 3107 | -260
[5 empty] | 2019-02-11 | 21 | 994.5 | 2764 | -311 | 1 | 0 | 3075 | 2696.2077 | 2696.2077 | 2696.2077 | 2539.5713 | 780 | 200 | 3519.5713 | 87.99% | 95% | 0% | -355.8352 | 2340.3725 | -3550 | -400 | -1609.6275 | 40.24% | 86.76% | 95% | 0% | 3075 | -311
[5 empty] | 2019-02-11 | 22 | 995 | 2635 | -412 | 1 | 0 | 3047 | 2652.3495 | 2652.3495 | 2652.3495 | 2539.5713 | 780 | 200 | 3519.5713 | 87.99% | 95% | 0% | -471.3959 | 2180.9537 | -3550 | -400 | -1769.0463 | 44.23% | 86.75% | 95% | 0% | 3047 | -412
[5 empty] | 2019-02-11 | 23 | 995.5 | 2580 | -438 | 1 | 0 | 3018 | 2606.925 | 2606.925 | 2606.925 | 2539.5713 | 780 | 200 | 3519.5713 | 87.99% | 95% | 0% | -501.1442 | 2105.7808 | -3550 | -400 | -1844.2192 | 46.11% | 86.75% | 95% | 0% | 3018 | -438
[5 empty] | 2019-02-11 | 24 | 996 | 2586 | -426 | 1 | 0 | 3012 | 2597.5268 | 2597.5268 | 2597.5268 | 2539.5713 | 780 | 200 | 3519.5713 | 87.99% | 95% | 0% | -487.4142 | 2110.1126 | -3550 | -400 | -1839.8874 | 46% | 86.74% | 95% | 0% | 3012 | -426
[5 empty] | 2019-02-11 | 25 | 996.5 | 2611 | -412 | 1 | 0 | 3023 | 2614.7568 | 2614.7568 | 2614.7568 | 2539.5713 | 780 | 200 | 3519.5713 | 87.99% | 95% | 0% | -471.3959 | 2143.3609 | -3550 | -400 | -1806.6391 | 45.17% | 86.73% | 95% | 0% | 3023 | -412
[5 empty] | 2019-02-11 | 26 | 997 | 2590 | -412 | 1 | 0 | 3002 | 2581.8631 | 2581.8631 | 2581.8631 | 2538.0049 | 780 | 200 | 3518.0049 | 87.95% | 95% | 0% | -471.3959 | 2110.4673 | -3550 | -400 | -1839.5327 | 45.99% | 86.73% | 95% | 0% | 3002 | -412
[5 empty] | 2019-02-11 | 27 | 997.5 | 2624 | -375 | 1 | 0 | 2999 | 2577.1641 | 2577.1641 | 2577.1641 | 2538.0049 | 780 | 200 | 3518.0049 | 87.95% | 95% | 0% | -429.0618 | 2148.1023 | -3550 | -400 | -1801.8977 | 45.05% | 86.72% | 95% | 0% | 2999 | -375
[5 empty] | 2019-02-11 | 28 | 998 | 2646 | -339 | 1 | 0 | 2985 | 2555.235 | 2555.235 | 2555.235 | 2538.0049 | 780 | 200 | 3518.0049 | 87.95% | 95% | 0% | -387.8719 | 2167.3631 | -3550 | -400 | -1782.6369 | 44.57% | 86.72% | 95% | 0% | 2985 | -339
[5 empty] | 2019-02-11 | 29 | 998.5 | 2731 | -291 | 1 | 0 | 3022 | 2613.1904 | 2613.1904 | 2613.1904 | 2536.4386 | 780 | 200 | 3516.4386 | 87.91% | 95% | 0% | -332.9519 | 2280.2385 | -3550 | -400 | -1669.7615 | 41.74% | 86.71% | 95% | 0% | 3022 | -291
[5 empty] | 2019-02-11 | 30 | 999 | 2802 | -231 | 1 | 0 | 3033 | 2630.4204 | 2630.4204 | 2630.4204 | 2536.4386 | 780 | 200 | 3516.4386 | 87.91% | 95% | 0% | -264.3021 | 2366.1184 | -3550 | -400 | -1583.8816 | 39.6% | 86.71% | 95% | 0% | 3033 | -231
[5 empty] | 2019-02-11 | 31 | 999.5 | 2871 | -184 | 1 | 0 | 3055 | 2664.8805 | 2664.8805 | 2664.8805 | 2536.4386 | 780 | 200 | 3516.4386 | 87.91% | 95% | 0% | -210.5263 | 2454.3541 | -3550 | -400 | -1495.6459 | 37.39% | 86.7% | 95% | 0% | 3055 | -184
[5 empty] | 2019-02-11 | 32 | 1000 | 2995 | -133 | 1 | 0 | 3128 | 2779.2251 | 2779.2251 | 2779.2251 | 2536.4386 | 780 | 200 | 3516.4386 | 87.91% | 95% | 0% | -152.1739 | 2627.0511 | -3550 | -400 | -1322.9489 | 33.07% | 86.69% | 95% | 0% | 3128 | -133
[5 empty] | 2019-02-11 | 33 | 1000.5 | 3128 | -87 | 1 | 0 | 3215 | 2915.4988 | 2915.4988 | 2915.4988 | 2536.4386 | 780 | 200 | 3516.4386 | 87.91% | 95% | 0% | -99.5423 | 2815.9564 | -3550 | -400 | -1134.0436 | 28.35% | 86.69% | 95% | 0% | 3215 | -87
[5 empty] | 2019-02-11 | 34 | 1001 | 3194 | -54 | 1 | 0 | 3248 | 2967.1888 | 2967.1888 | 2967.1888 | 2534.8722 | 780 | 200 | 3514.8722 | 87.87% | 95% | 0% | -61.7849 | 2905.4039 | -3550 | -400 | -1044.5961 | 26.11% | 86.67% | 95% | 0% | 3248 | -54
[5 empty] | 2019-02-11 | 35 | 1001.5 | 3302 | -47 | 1 | 0 | 3349 | 3125.3916 | 3125.3916 | 3125.3916 | 2534.8722 | 780 | 200 | 3514.8722 | 87.87% | 95% | 0% | -53.7757 | 3071.6158 | -3550 | -400 | -878.3842 | 21.96% | 86.65% | 95% | 0% | 3349 | -47
[5 empty] | 2019-02-11 | 36 | 1002 | 3401 | -50 | 0 | 0 | 3451 | 3285.1608 | 3285.1608 | 3285.1608 | 2534.8722 | 780 | 200 | 3514.8722 | 87.87% | 95% | 0% | -57.2082 | 3227.9525 | -2750 | -200 | 277.9525 | -6.949% | 86.62% | 95% | 0% | 3451 | -50
[5 empty] | 2019-02-11 | 37 | 1002.5 | 3404 | -53 | 0 | 0 | 3457 | 3294.5589 | 3294.5589 | 3294.5589 | 2534.8722 | 780 | 200 | 3514.8722 | 87.87% | 95% | 0% | -60.6407 | 3233.9182 | -2750 | -200 | 283.9182 | -7.098% | 86.62% | 95% | 0% | 3457 | -53
[5 empty] | 2019-02-11 | 38 | 1003 | 3406 | -55 | 0 | 0 | 3461 | 3300.8244 | 3300.8244 | 3300.8244 | 2534.8722 | 780 | 200 | 3514.8722 | 87.87% | 95% | 0% | -62.9291 | 3237.8953 | -2750 | -200 | 287.8953 | -7.197% | 86.61% | 95% | 0% | 3461 | -55
[5 empty] | 2019-02-11 | 39 | 1003.5 | 3356 | -59 | 0 | 0 | 3415 | 3228.7716 | 3228.7716 | 3228.7716 | 2534.8722 | 780 | 200 | 3514.8722 | 87.87% | 95% | 0% | -67.5057 | 3161.2659 | -2750 | -200 | 211.2659 | -5.282% | 86.6% | 95% | 0% | 3415 | -59
[5 empty] | 2019-02-11 | 40 | 1004 | 3299 | -63 | 0 | 0 | 3362 | 3145.7543 | 3145.7543 | 3145.7543 | 2534.8722 | 780 | 200 | 3514.8722 | 87.87% | 95% | 0% | -72.0824 | 3073.6719 | -2750 | -200 | 123.6719 | -3.092% | 86.59% | 95% | 0% | 3362 | -63
[5 empty] | 2019-02-11 | 41 | 1004.5 | 3221 | -68 | 0 | 0 | 3289 | 3031.4097 | 3031.4097 | 3031.4097 | 2534.8722 | 780 | 200 | 3514.8722 | 87.87% | 95% | 0% | -77.8032 | 2953.6065 | -2750 | -200 | 3.6065 | -0.09016% | 86.59% | 95% | 0% | 3289 | -68
[5 empty] | 2019-02-11 | 42 | 1005 | 3089 | -73 | 0 | 0 | 3162 | 2832.4815 | 2832.4815 | 2832.4815 | 2533.3059 | 780 | 200 | 3513.3059 | 87.83% | 95% | 0% | -83.524 | 2748.9574 | -2750 | -200 | -201.0426 | 5.026% | 86.59% | 95% | 0% | 3162 | -73
[5 empty] | 2019-02-11 | 43 | 1005.5 | 2928 | -78 | 0 | 0 | 3006 | 2588.1286 | 2588.1286 | 2588.1286 | 2533.3059 | 780 | 200 | 3513.3059 | 87.83% | 95% | 0% | -89.2449 | 2498.8838 | -2750 | -200 | -451.1162 | 11.28% | 86.59% | 95% | 0% | 3006 | -78
[5 empty] | 2019-02-11 | 44 | 1006 | 2726 | -84 | 0 | 0 | 2810 | 2281.1212 | 2281.1212 | 2281.1212 | 2533.3059 | 780 | 200 | 3513.3059 | 87.83% | 95% | 0% | -96.1098 | 2185.0113 | -2750 | -200 | -764.9887 | 19.12% | 86.58% | 95% | 0% | 2810 | -84
[5 empty] | 2019-02-11 | 45 | 1006.5 | 2537 | -89 | 0 | 0 | 2626 | 1992.9101 | 1992.9101 | 1992.9101 | 2533.3059 | 780 | 200 | 3513.3059 | 87.83% | 95% | 0% | -101.8307 | 1891.0795 | -2750 | -200 | -1058.9205 | 26.47% | 86.58% | 95% | 0% | 2626 | -89
[5 empty] | 2019-02-11 | 46 | 1007 | 2380 | -94 | 0 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 2533.3059 | 780 | 200 | 3513.3059 | 87.83% | 95% | 0% | -107.5515 | 1647.2713 | -2750 | -200 | -1302.7287 | 32.57% | 86.57% | 95% | 0% | 2474 | -94
[5 empty] | 2019-02-11 | 47 | 1007.5 | 2207 | -97 | 0 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 2531.7395 | 780 | 200 | 3511.7395 | 87.79% | 95% | 0% | -110.984 | 1377.5568 | -2750 | -200 | -1572.4432 | 39.31% | 86.56% | 95% | 0% | 2304 | -97
[5 empty] | 2019-02-11 | 48 | 1008 | 2122 | -101 | 0 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 2531.7395 | 780 | 200 | 3511.7395 | 87.79% | 95% | 0% | -115.5606 | 1246.1047 | -2750 | -200 | -1703.8953 | 42.6% | 86.55% | 95% | 0% | 2223 | -101
[5 empty] | 2019-02-12 | 1 | 1008.5 | 2090 | -104 | 0 | 0 | 2194 | 1316.2407 | 1316.2407 | 1316.2407 | 2531.7395 | 780 | 200 | 3511.7395 | 87.79% | 95% | 0% | -118.9931 | 1197.2476 | -2750 | -200 | -1752.7524 | 43.82% | 86.55% | 95% | 0% | 2194 | -104
[5 empty] | 2019-02-12 | 2 | 1009 | 2109 | -107 | 0 | 0 | 2216 | 1350.7007 | 1350.7007 | 1350.7007 | 2530.1731 | 780 | 200 | 3510.1731 | 87.75% | 95% | 0% | -122.4256 | 1228.2751 | -2750 | -200 | -1721.7249 | 43.04% | 86.54% | 95% | 0% | 2216 | -107
[5 empty] | 2019-02-12 | 3 | 1009.5 | 2083 | -109 | 0 | 0 | 2192 | 1313.108 | 1313.108 | 1313.108 | 2530.1731 | 780 | 200 | 3510.1731 | 87.75% | 95% | 0% | -124.714 | 1188.394 | -2750 | -200 | -1761.606 | 44.04% | 86.54% | 95% | 0% | 2192 | -109
[5 empty] | 2019-02-12 | 4 | 1010 | 2031 | -112 | 0 | 0 | 2143 | 1236.3561 | 1236.3561 | 1236.3561 | 2530.1731 | 780 | 200 | 3510.1731 | 87.75% | 95% | 0% | -128.1465 | 1108.2097 | -2750 | -200 | -1841.7903 | 46.04% | 86.54% | 95% | 0% | 2143 | -112
[5 empty] | 2019-02-12 | 5 | 1010.5 | 1982 | -114 | 0 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 2530.1731 | 780 | 200 | 3510.1731 | 87.75% | 95% | 0% | -130.4348 | 1032.3022 | -2750 | -200 | -1917.6978 | 47.94% | 86.52% | 95% | 0% | 2096 | -114
[5 empty] | 2019-02-12 | 6 | 1011 | 1962 | -117 | 0 | 0 | 2079 | 1136.1088 | 1136.1088 | 1136.1088 | 2530.1731 | 780 | 200 | 3510.1731 | 87.75% | 95% | 0% | -133.8673 | 1002.2415 | -2750 | -200 | -1947.7585 | 48.69% | 86.51% | 95% | 0% | 2079 | -117
[5 empty] | 2019-02-12 | 7 | 1011.5 | 1920 | -120 | 0 | 0 | 2040 | 1075.0206 | 1075.0206 | 1075.0206 | 2530.1731 | 780 | 200 | 3510.1731 | 87.75% | 95% | 0% | -137.2998 | 937.7208 | -2750 | -200 | -2012.2792 | 50.31% | 86.51% | 95% | 0% | 2040 | -120
[5 empty] | 2019-02-12 | 8 | 1012 | 1893 | -123 | 0 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 2530.1731 | 780 | 200 | 3510.1731 | 87.75% | 95% | 0% | -140.7323 | 896.6956 | -2750 | -200 | -2053.3044 | 51.33% | 86.48% | 95% | 0% | 2016 | -123
[5 empty] | 2019-02-12 | 9 | 1012.5 | 1866 | -126 | 0 | 0 | 1992 | 999.8351 | 999.8351 | 999.8351 | 2530.1731 | 780 | 200 | 3510.1731 | 87.75% | 95% | 0% | -144.1648 | 855.6704 | -2750 | -200 | -2094.3296 | 52.36% | 86.48% | 95% | 0% | 1992 | -126
[5 empty] | 2019-02-12 | 10 | 1013 | 1874 | -129 | 0 | 0 | 2003 | 1017.0651 | 1017.0651 | 1017.0651 | 2528.6068 | 780 | 200 | 3508.6068 | 87.72% | 95% | 0% | -147.5973 | 869.4679 | -2750 | -200 | -2080.5321 | 52.01% | 86.48% | 95% | 0% | 2003 | -129
[5 empty] | 2019-02-12 | 11 | 1013.5 | 1924 | -132 | 0 | 0 | 2056 | 1100.0824 | 1100.0824 | 1100.0824 | 2528.6068 | 780 | 200 | 3508.6068 | 87.72% | 95% | 0% | -151.0297 | 949.0527 | -2750 | -200 | -2000.9473 | 50.02% | 86.47% | 95% | 0% | 2056 | -132
[5 empty] | 2019-02-12 | 12 | 1014 | 2030 | -134 | 0 | 0 | 2164 | 1269.2498 | 1269.2498 | 1269.2498 | 2528.6068 | 780 | 200 | 3508.6068 | 87.72% | 95% | 0% | -153.3181 | 1115.9317 | -2750 | -200 | -1834.0683 | 45.85% | 86.47% | 95% | 0% | 2164 | -134
[5 empty] | 2019-02-12 | 13 | 1014.5 | 2305 | -135 | 0 | 0 | 2440 | 1701.5664 | 1701.5664 | 1701.5664 | 2527.0404 | 780 | 200 | 3507.0404 | 87.68% | 95% | 0% | -154.4622 | 1547.1041 | -2750 | -200 | -1402.8959 | 35.07% | 86.46% | 95% | 0% | 2440 | -135
[5 empty] | 2019-02-12 | 14 | 1015 | 2539 | -136 | 0 | 0 | 2675 | 2069.662 | 2069.662 | 2069.662 | 2527.0404 | 780 | 200 | 3507.0404 | 87.68% | 95% | 0% | -155.6064 | 1914.0556 | -2750 | -200 | -1035.9444 | 25.9% | 86.44% | 95% | 0% | 2675 | -136
[5 empty] | 2019-02-12 | 15 | 1015.5 | 2826 | -137 | 0 | 0 | 2963 | 2520.7749 | 2520.7749 | 2520.7749 | 2527.0404 | 780 | 200 | 3507.0404 | 87.68% | 95% | 0% | -156.7506 | 2364.0244 | -2750 | -200 | -585.9756 | 14.65% | 86.43% | 95% | 0% | 2963 | -137
[5 empty] | 2019-02-12 | 16 | 1016 | 2906 | -146 | 0 | 0 | 3052 | 2660.1814 | 2660.1814 | 2660.1814 | 2527.0404 | 780 | 200 | 3507.0404 | 87.68% | 95% | 0% | -167.0481 | 2493.1333 | -2750 | -200 | -456.8667 | 11.42% | 86.42% | 95% | 0% | 3052 | -146
[5 empty] | 2019-02-12 | 17 | 1016.5 | 2911 | -174 | 0 | 0 | 3085 | 2711.8714 | 2711.8714 | 2711.8714 | 2527.0404 | 780 | 200 | 3507.0404 | 87.68% | 95% | 0% | -199.0847 | 2512.7867 | -2750 | -200 | -437.2133 | 10.93% | 86.4% | 95% | 0% | 3085 | -174
[5 empty] | 2019-02-12 | 18 | 1017 | 2874 | -210 | 0 | 0 | 3084 | 2710.305 | 2710.305 | 2710.305 | 2527.0404 | 780 | 200 | 3507.0404 | 87.68% | 95% | 0% | -240.2746 | 2470.0304 | -2750 | -200 | -479.9696 | 12% | 86.4% | 95% | 0% | 3084 | -210
[5 empty] | 2019-02-12 | 19 | 1017.5 | 2866 | -234 | 0 | 0 | 3100 | 2735.3669 | 2735.3669 | 2735.3669 | 2525.474 | 780 | 200 | 3505.474 | 87.64% | 95% | 0% | -267.7346 | 2467.6323 | -2750 | -200 | -482.3677 | 12.06% | 86.4% | 95% | 0% | 3100 | -234
[5 empty] | 2019-02-12 | 20 | 1018 | 2800 | -283 | 0 | 0 | 3083 | 2708.7387 | 2708.7387 | 2708.7387 | 2525.474 | 780 | 200 | 3505.474 | 87.64% | 95% | 0% | -323.7986 | 2384.94 | -2750 | -200 | -565.06 | 14.13% | 86.4% | 95% | 0% | 3083 | -283
[5 empty] | 2019-02-12 | 21 | 1018.5 | 2755 | -306 | 0 | 0 | 3061 | 2674.2786 | 2674.2786 | 2674.2786 | 2523.9077 | 780 | 200 | 3503.9077 | 87.6% | 95% | 0% | -350.1144 | 2324.1642 | -2750 | -200 | -625.8358 | 15.65% | 86.39% | 95% | 0% | 3061 | -306
[5 empty] | 2019-02-12 | 22 | 1019 | 2704 | -339 | 1 | 0 | 3043 | 2646.0841 | 2646.0841 | 2646.0841 | 2523.9077 | 780 | 200 | 3503.9077 | 87.6% | 95% | 0% | -387.8719 | 2258.2122 | -3550 | -400 | -1691.7878 | 42.29% | 86.38% | 95% | 0% | 3043 | -339
[5 empty] | 2019-02-12 | 23 | 1019.5 | 2632 | -367 | 1 | 0 | 2999 | 2577.1641 | 2577.1641 | 2577.1641 | 2523.9077 | 780 | 200 | 3503.9077 | 87.6% | 95% | 0% | -419.9085 | 2157.2556 | -3550 | -400 | -1792.7444 | 44.82% | 86.38% | 95% | 0% | 2999 | -367
[5 empty] | 2019-02-12 | 24 | 1020 | 2603 | -368 | 1 | 0 | 2971 | 2533.3059 | 2533.3059 | 2533.3059 | 2523.9077 | 780 | 200 | 3503.9077 | 87.6% | 95% | 0% | -421.0526 | 2112.2532 | -3550 | -400 | -1837.7468 | 45.94% | 86.37% | 95% | 0% | 2971 | -368
[5 empty] | 2019-02-12 | 25 | 1020.5 | 2619 | -361 | 1 | 0 | 2980 | 2547.4031 | 2547.4031 | 2547.4031 | 2523.9077 | 780 | 200 | 3503.9077 | 87.6% | 95% | 0% | -413.0435 | 2134.3597 | -3550 | -400 | -1815.6403 | 45.39% | 86.37% | 95% | 0% | 2980 | -361
[5 empty] | 2019-02-12 | 26 | 1021 | 2596 | -366 | 1 | 0 | 2962 | 2519.2086 | 2519.2086 | 2519.2086 | 2523.9077 | 780 | 200 | 3503.9077 | 87.6% | 95% | 0% | -418.7643 | 2100.4443 | -3550 | -400 | -1849.5557 | 46.24% | 86.37% | 95% | 0% | 2962 | -366
[5 empty] | 2019-02-12 | 27 | 1021.5 | 2563 | -384 | 1 | 0 | 2947 | 2495.7131 | 2495.7131 | 2495.7131 | 2523.9077 | 780 | 200 | 3503.9077 | 87.6% | 95% | 0% | -439.3593 | 2056.3538 | -3550 | -400 | -1893.6462 | 47.34% | 86.37% | 95% | 0% | 2947 | -384
[5 empty] | 2019-02-12 | 28 | 1022 | 2593 | -350 | 1 | 0 | 2943 | 2489.4477 | 2489.4477 | 2489.4477 | 2523.9077 | 780 | 200 | 3503.9077 | 87.6% | 95% | 0% | -400.4577 | 2088.99 | -3550 | -400 | -1861.01 | 46.53% | 86.36% | 95% | 0% | 2943 | -350
[5 empty] | 2019-02-12 | 29 | 1022.5 | 2637 | -314 | 1 | 0 | 2951 | 2501.9786 | 2501.9786 | 2501.9786 | 2522.3413 | 780 | 200 | 3502.3413 | 87.56% | 95% | 0% | -359.2677 | 2142.7108 | -3550 | -400 | -1807.2892 | 45.18% | 86.35% | 95% | 0% | 2951 | -314
[5 empty] | 2019-02-12 | 30 | 1023 | 2674 | -278 | 1 | 0 | 2952 | 2503.5449 | 2503.5449 | 2503.5449 | 2522.3413 | 780 | 200 | 3502.3413 | 87.56% | 95% | 0% | -318.0778 | 2185.4671 | -3550 | -400 | -1764.5329 | 44.11% | 86.34% | 95% | 0% | 2952 | -278
[5 empty] | 2019-02-12 | 31 | 1023.5 | 2722 | -242 | 1 | 0 | 2964 | 2522.3413 | 2522.3413 | 2522.3413 | 2522.3413 | 780 | 200 | 3502.3413 | 87.56% | 95% | 0% | -276.8879 | 2245.4534 | -3550 | -400 | -1704.5466 | 42.61% | 86.34% | 95% | 0% | 2964 | -242
[5 empty] | 2019-02-12 | 32 | 1024 | 2825 | -208 | 1 | 0 | 3033 | 2630.4204 | 2630.4204 | 2630.4204 | 2522.3413 | 780 | 200 | 3502.3413 | 87.56% | 95% | 0% | -237.9863 | 2392.4342 | -3550 | -400 | -1557.5658 | 38.94% | 86.34% | 95% | 0% | 3033 | -208
[5 empty] | 2019-02-12 | 33 | 1024.5 | 2953 | -179 | 1 | 0 | 3132 | 2785.4905 | 2785.4905 | 2785.4905 | 2522.3413 | 780 | 200 | 3502.3413 | 87.56% | 95% | 0% | -204.8055 | 2580.685 | -3550 | -400 | -1369.315 | 34.23% | 86.34% | 95% | 0% | 3132 | -179
[5 empty] | 2019-02-12 | 34 | 1025 | 3060 | -155 | 1 | 0 | 3215 | 2915.4988 | 2915.4988 | 2915.4988 | 2520.7749 | 780 | 200 | 3500.7749 | 87.52% | 95% | 0% | -177.3455 | 2738.1532 | -3550 | -400 | -1211.8468 | 30.3% | 86.33% | 95% | 0% | 3215 | -155
[5 empty] | 2019-02-12 | 35 | 1025.5 | 3189 | -144 | 1 | 0 | 3333 | 3100.3298 | 3100.3298 | 3100.3298 | 2520.7749 | 780 | 200 | 3500.7749 | 87.52% | 95% | 0% | -164.7597 | 2935.57 | -3550 | -400 | -1014.43 | 25.36% | 86.33% | 95% | 0% | 3333 | -144
[5 empty] | 2019-02-12 | 36 | 1026 | 3302 | -140 | 1 | 0 | 3442 | 3271.0635 | 3271.0635 | 3271.0635 | 2520.7749 | 780 | 200 | 3500.7749 | 87.52% | 95% | 0% | -160.1831 | 3110.8804 | -3550 | -400 | -839.1196 | 20.98% | 86.32% | 95% | 0% | 3442 | -140
[5 empty] | 2019-02-12 | 37 | 1026.5 | 3307 | -137 | 0 | 0 | 3444 | 3274.1962 | 3274.1962 | 3274.1962 | 2520.7749 | 780 | 200 | 3500.7749 | 87.52% | 95% | 0% | -156.7506 | 3117.4456 | -2750 | -200 | 167.4456 | -4.186% | 86.32% | 95% | 0% | 3444 | -137
[5 empty] | 2019-02-12 | 38 | 1027 | 3283 | -134 | 0 | 0 | 3417 | 3231.9044 | 3231.9044 | 3231.9044 | 2520.7749 | 780 | 200 | 3500.7749 | 87.52% | 95% | 0% | -153.3181 | 3078.5863 | -2750 | -200 | 128.5863 | -3.215% | 86.31% | 95% | 0% | 3417 | -134
[5 empty] | 2019-02-12 | 39 | 1027.5 | 3234 | -131 | 0 | 0 | 3365 | 3150.4534 | 3150.4534 | 3150.4534 | 2519.2086 | 780 | 200 | 3499.2086 | 87.48% | 95% | 0% | -149.8856 | 3000.5678 | -2750 | -200 | 50.5678 | -1.264% | 86.3% | 95% | 0% | 3365 | -131
[5 empty] | 2019-02-12 | 40 | 1028 | 3143 | -128 | 0 | 0 | 3271 | 3003.2152 | 3003.2152 | 3003.2152 | 2519.2086 | 780 | 200 | 3499.2086 | 87.48% | 95% | 0% | -146.4531 | 2856.7621 | -2750 | -200 | -93.2379 | 2.331% | 86.3% | 95% | 0% | 3271 | -128
[5 empty] | 2019-02-12 | 41 | 1028.5 | 3043 | -124 | 0 | 0 | 3167 | 2840.3133 | 2840.3133 | 2840.3133 | 2519.2086 | 780 | 200 | 3499.2086 | 87.48% | 95% | 0% | -141.8764 | 2698.4368 | -2750 | -200 | -251.5632 | 6.289% | 86.3% | 95% | 0% | 3167 | -124
[5 empty] | 2019-02-12 | 42 | 1029 | 2901 | -121 | 0 | 0 | 3022 | 2613.1904 | 2613.1904 | 2613.1904 | 2519.2086 | 780 | 200 | 3499.2086 | 87.48% | 95% | 0% | -138.4439 | 2474.7465 | -2750 | -200 | -475.2535 | 11.88% | 86.29% | 95% | 0% | 3022 | -121
[5 empty] | 2019-02-12 | 43 | 1029.5 | 2773 | -120 | 0 | 0 | 2893 | 2411.1294 | 2411.1294 | 2411.1294 | 2519.2086 | 780 | 200 | 3499.2086 | 87.48% | 95% | 0% | -137.2998 | 2273.8297 | -2750 | -200 | -676.1703 | 16.9% | 86.29% | 95% | 0% | 2893 | -120
[5 empty] | 2019-02-12 | 44 | 1030 | 2601 | -118 | 0 | 0 | 2719 | 2138.582 | 2138.582 | 2138.582 | 2519.2086 | 780 | 200 | 3499.2086 | 87.48% | 95% | 0% | -135.0114 | 2003.5706 | -2750 | -200 | -946.4294 | 23.66% | 86.29% | 95% | 0% | 2719 | -118
[5 empty] | 2019-02-12 | 45 | 1030.5 | 2450 | -118 | 0 | 0 | 2568 | 1902.061 | 1902.061 | 1902.061 | 2517.6422 | 780 | 200 | 3497.6422 | 87.44% | 95% | 0% | -135.0114 | 1767.0496 | -2750 | -200 | -1182.9504 | 29.57% | 86.28% | 95% | 0% | 2568 | -118
[5 empty] | 2019-02-12 | 46 | 1031 | 2296 | -119 | 0 | 0 | 2415 | 1662.4073 | 1662.4073 | 1662.4073 | 2517.6422 | 780 | 200 | 3497.6422 | 87.44% | 95% | 0% | -136.1556 | 1526.2516 | -2750 | -200 | -1423.7484 | 35.59% | 86.28% | 95% | 0% | 2415 | -119
[5 empty] | 2019-02-12 | 47 | 1031.5 | 2133 | -117 | 0 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 2517.6422 | 780 | 200 | 3497.6422 | 87.44% | 95% | 0% | -133.8673 | 1270.0899 | -2750 | -200 | -1679.9101 | 42% | 86.27% | 95% | 0% | 2250 | -117
[5 empty] | 2019-02-12 | 48 | 1032 | 2027 | -115 | 0 | 0 | 2142 | 1234.7898 | 1234.7898 | 1234.7898 | 2517.6422 | 780 | 200 | 3497.6422 | 87.44% | 95% | 0% | -131.5789 | 1103.2108 | -2750 | -200 | -1846.7892 | 46.17% | 86.26% | 95% | 0% | 2142 | -115
[5 empty] | 2019-02-13 | 1 | 1032.5 | 1989 | -118 | 0 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 2517.6422 | 780 | 200 | 3497.6422 | 87.44% | 95% | 0% | -135.0114 | 1044.9556 | -2750 | -200 | -1905.0444 | 47.63% | 86.26% | 95% | 0% | 2107 | -118
[5 empty] | 2019-02-13 | 2 | 1033 | 2015 | -120 | 0 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 2517.6422 | 780 | 200 | 3497.6422 | 87.44% | 95% | 0% | -137.2998 | 1086.5255 | -2750 | -200 | -1863.4745 | 46.59% | 86.26% | 95% | 0% | 2135 | -120
[5 empty] | 2019-02-13 | 3 | 1033.5 | 1995 | -123 | 0 | 0 | 2118 | 1197.197 | 1197.197 | 1197.197 | 2517.6422 | 780 | 200 | 3497.6422 | 87.44% | 95% | 0% | -140.7323 | 1056.4648 | -2750 | -200 | -1893.5352 | 47.34% | 86.26% | 95% | 0% | 2118 | -123
[5 empty] | 2019-02-13 | 4 | 1034 | 1934 | -126 | 0 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 2517.6422 | 780 | 200 | 3497.6422 | 87.44% | 95% | 0% | -144.1648 | 962.1831 | -2750 | -200 | -1987.8169 | 49.7% | 86.25% | 95% | 0% | 2060 | -126
[5 empty] | 2019-02-13 | 5 | 1034.5 | 1892 | -130 | 0 | 0 | 2022 | 1046.8261 | 1046.8261 | 1046.8261 | 2516.0758 | 780 | 200 | 3496.0758 | 87.4% | 95% | 0% | -148.7414 | 898.0846 | -2750 | -200 | -2051.9154 | 51.3% | 86.24% | 95% | 0% | 2022 | -130
[5 empty] | 2019-02-13 | 6 | 1035 | 1860 | -133 | 0 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 2516.0758 | 780 | 200 | 3496.0758 | 87.4% | 95% | 0% | -152.1739 | 849.2276 | -2750 | -200 | -2100.7724 | 52.52% | 86.24% | 95% | 0% | 1993 | -133
[5 empty] | 2019-02-13 | 7 | 1035.5 | 1823 | -137 | 0 | 0 | 1960 | 949.7115 | 949.7115 | 949.7115 | 2516.0758 | 780 | 200 | 3496.0758 | 87.4% | 95% | 0% | -156.7506 | 792.9609 | -2750 | -200 | -2157.0391 | 53.93% | 86.23% | 95% | 0% | 1960 | -137
[5 empty] | 2019-02-13 | 8 | 1036 | 1782 | -140 | 0 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 2516.0758 | 780 | 200 | 3496.0758 | 87.4% | 95% | 0% | -160.1831 | 730.0065 | -2750 | -200 | -2219.9935 | 55.5% | 86.23% | 95% | 0% | 1922 | -140
[5 empty] | 2019-02-13 | 9 | 1036.5 | 1771 | -143 | 0 | 0 | 1914 | 877.6587 | 877.6587 | 877.6587 | 2516.0758 | 780 | 200 | 3496.0758 | 87.4% | 95% | 0% | -163.6156 | 714.0431 | -2750 | -200 | -2235.9569 | 55.9% | 86.23% | 95% | 0% | 1914 | -143
[5 empty] | 2019-02-13 | 10 | 1037 | 1779 | -146 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 2514.5095 | 780 | 200 | 3494.5095 | 87.36% | 95% | 0% | -167.0481 | 727.8407 | -2750 | -200 | -2222.1593 | 55.55% | 86.23% | 95% | 0% | 1925 | -146
[5 empty] | 2019-02-13 | 11 | 1037.5 | 1820 | -148 | 0 | 0 | 1968 | 962.2424 | 962.2424 | 962.2424 | 2514.5095 | 780 | 200 | 3494.5095 | 87.36% | 95% | 0% | -169.3364 | 792.906 | -2750 | -200 | -2157.094 | 53.93% | 86.23% | 95% | 0% | 1968 | -148
[5 empty] | 2019-02-13 | 12 | 1038 | 1922 | -149 | 0 | 0 | 2071 | 1123.5779 | 1123.5779 | 1123.5779 | 2512.9431 | 780 | 200 | 3492.9431 | 87.32% | 95% | 0% | -170.4805 | 953.0974 | -2750 | -200 | -1996.9026 | 49.92% | 86.22% | 95% | 0% | 2071 | -149
[5 empty] | 2019-02-13 | 13 | 1038.5 | 2176 | -150 | 0 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 2512.9431 | 780 | 200 | 3492.9431 | 87.32% | 95% | 0% | -171.6247 | 1351.3761 | -2750 | -200 | -1598.6239 | 39.97% | 86.22% | 95% | 0% | 2326 | -150
[5 empty] | 2019-02-13 | 14 | 1039 | 2429 | -151 | 0 | 0 | 2580 | 1920.8574 | 1920.8574 | 1920.8574 | 2512.9431 | 780 | 200 | 3492.9431 | 87.32% | 95% | 0% | -172.7689 | 1748.0885 | -2750 | -200 | -1201.9115 | 30.05% | 86.21% | 95% | 0% | 2580 | -151
[5 empty] | 2019-02-13 | 15 | 1039.5 | 2709 | -152 | 0 | 0 | 2861 | 2361.0058 | 2361.0058 | 2361.0058 | 2512.9431 | 780 | 200 | 3492.9431 | 87.32% | 95% | 0% | -173.913 | 2187.0927 | -2750 | -200 | -762.9073 | 19.07% | 86.21% | 95% | 0% | 2861 | -152
[5 empty] | 2019-02-13 | 16 | 1040 | 2796 | -158 | 0 | 0 | 2954 | 2506.6777 | 2506.6777 | 2506.6777 | 2512.9431 | 780 | 200 | 3492.9431 | 87.32% | 95% | 0% | -180.778 | 2325.8996 | -2750 | -200 | -624.1004 | 15.6% | 86.2% | 95% | 0% | 2954 | -158
[5 empty] | 2019-02-13 | 17 | 1040.5 | 2826 | -177 | 0 | 0 | 3003 | 2583.4295 | 2583.4295 | 2583.4295 | 2512.9431 | 780 | 200 | 3492.9431 | 87.32% | 95% | 0% | -202.5172 | 2380.9124 | -2750 | -200 | -569.0876 | 14.23% | 86.2% | 95% | 0% | 3003 | -177
[5 empty] | 2019-02-13 | 18 | 1041 | 2790 | -204 | 1 | 0 | 2994 | 2569.3322 | 2569.3322 | 2569.3322 | 2512.9431 | 780 | 200 | 3492.9431 | 87.32% | 95% | 0% | -233.4096 | 2335.9226 | -3550 | -400 | -1614.0774 | 40.35% | 86.2% | 95% | 0% | 2994 | -204
[5 empty] | 2019-02-13 | 19 | 1041.5 | 2762 | -237 | 1 | 0 | 2999 | 2577.1641 | 2577.1641 | 2577.1641 | 2511.3768 | 780 | 200 | 3491.3768 | 87.28% | 95% | 0% | -271.167 | 2305.997 | -3550 | -400 | -1644.003 | 41.1% | 86.19% | 95% | 0% | 2999 | -237
[5 empty] | 2019-02-13 | 20 | 1042 | 2688 | -285 | 1 | 0 | 2973 | 2536.4386 | 2536.4386 | 2536.4386 | 2511.3768 | 780 | 200 | 3491.3768 | 87.28% | 95% | 0% | -326.087 | 2210.3516 | -3550 | -400 | -1739.6484 | 43.49% | 86.19% | 95% | 0% | 2973 | -285
[5 empty] | 2019-02-13 | 21 | 1042.5 | 2580 | -331 | 1 | 0 | 2911 | 2439.324 | 2439.324 | 2439.324 | 2511.3768 | 780 | 200 | 3491.3768 | 87.28% | 95% | 0% | -378.7185 | 2060.6055 | -3550 | -400 | -1889.3945 | 47.23% | 86.17% | 95% | 0% | 2911 | -331
[5 empty] | 2019-02-13 | 22 | 1043 | 2417 | -431 | 1 | 0 | 2848 | 2340.643 | 2340.643 | 2340.643 | 2509.8104 | 780 | 200 | 3489.8104 | 87.25% | 95% | 0% | -493.135 | 1847.508 | -3550 | -400 | -2102.492 | 52.56% | 86.17% | 95% | 0% | 2848 | -431
[5 empty] | 2019-02-13 | 23 | 1043.5 | 2351 | -445 | 1 | 0 | 2796 | 2259.1921 | 2259.1921 | 2259.1921 | 2509.8104 | 780 | 200 | 3489.8104 | 87.25% | 95% | 0% | -509.1533 | 1750.0388 | -3550 | -400 | -2199.9612 | 55% | 86.17% | 95% | 0% | 2796 | -445
[5 empty] | 2019-02-13 | 24 | 1044 | 2260 | -490 | 1 | 0 | 2750 | 2187.1393 | 2187.1393 | 2187.1393 | 2509.8104 | 780 | 200 | 3489.8104 | 87.25% | 95% | 0% | -560.6407 | 1626.4986 | -3550 | -400 | -2323.5014 | 58.09% | 86.15% | 95% | 0% | 2750 | -490
[5 empty] | 2019-02-13 | 25 | 1044.5 | 2243 | -498 | 1 | 0 | 2741 | 2173.042 | 2173.042 | 2173.042 | 2509.8104 | 780 | 200 | 3489.8104 | 87.25% | 95% | 0% | -569.7941 | 1603.248 | -3550 | -400 | -2346.752 | 58.67% | 86.15% | 95% | 0% | 2741 | -498
[5 empty] | 2019-02-13 | 26 | 1045 | 2195 | -503 | 1 | 0 | 2698 | 2105.6884 | 2105.6884 | 2105.6884 | 2509.8104 | 780 | 200 | 3489.8104 | 87.25% | 95% | 0% | -575.5149 | 1530.1735 | -3550 | -400 | -2419.8265 | 60.5% | 86.13% | 95% | 0% | 2698 | -503
[5 empty] | 2019-02-13 | 27 | 1045.5 | 2209 | -488 | 1 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 2508.244 | 780 | 200 | 3488.244 | 87.21% | 95% | 0% | -558.3524 | 1545.7696 | -3550 | -400 | -2404.2304 | 60.11% | 86.13% | 95% | 0% | 2697 | -488
[5 empty] | 2019-02-13 | 28 | 1046 | 2220 | -475 | 1 | 0 | 2695 | 2100.9893 | 2100.9893 | 2100.9893 | 2508.244 | 780 | 200 | 3488.244 | 87.21% | 95% | 0% | -543.4783 | 1557.511 | -3550 | -400 | -2392.489 | 59.81% | 86.12% | 95% | 0% | 2695 | -475
[5 empty] | 2019-02-13 | 29 | 1046.5 | 2282 | -436 | 1 | 0 | 2718 | 2137.0157 | 2137.0157 | 2137.0157 | 2508.244 | 780 | 200 | 3488.244 | 87.21% | 95% | 0% | -498.8558 | 1638.1598 | -3550 | -400 | -2311.8402 | 57.8% | 86.12% | 95% | 0% | 2718 | -436
[5 empty] | 2019-02-13 | 30 | 1047 | 2349 | -388 | 1 | 0 | 2737 | 2166.7766 | 2166.7766 | 2166.7766 | 2506.6777 | 780 | 200 | 3486.6777 | 87.17% | 95% | 0% | -443.9359 | 1722.8407 | -3550 | -400 | -2227.1593 | 55.68% | 86.12% | 95% | 0% | 2737 | -388
[5 empty] | 2019-02-13 | 31 | 1047.5 | 2461 | -322 | 1 | 0 | 2783 | 2238.8293 | 2238.8293 | 2238.8293 | 2506.6777 | 780 | 200 | 3486.6777 | 87.17% | 95% | 0% | -368.4211 | 1870.4083 | -3550 | -400 | -2079.5917 | 51.99% | 86.11% | 95% | 0% | 2783 | -322
[5 empty] | 2019-02-13 | 32 | 1048 | 2623 | -257 | 1 | 0 | 2880 | 2390.7667 | 2390.7667 | 2390.7667 | 2506.6777 | 780 | 200 | 3486.6777 | 87.17% | 95% | 0% | -294.0503 | 2096.7164 | -3550 | -400 | -1853.2836 | 46.33% | 86.11% | 95% | 0% | 2880 | -257
[5 empty] | 2019-02-13 | 33 | 1048.5 | 2765 | -206 | 1 | 0 | 2971 | 2533.3059 | 2533.3059 | 2533.3059 | 2505.1113 | 780 | 200 | 3485.1113 | 87.13% | 95% | 0% | -235.6979 | 2297.6079 | -3550 | -400 | -1652.3921 | 41.31% | 86.11% | 95% | 0% | 2971 | -206
[5 empty] | 2019-02-13 | 34 | 1049 | 2925 | -164 | 1 | 0 | 3089 | 2718.1369 | 2718.1369 | 2718.1369 | 2503.5449 | 780 | 200 | 3483.5449 | 87.09% | 95% | 0% | -187.643 | 2530.4938 | -3550 | -400 | -1419.5062 | 35.49% | 86.1% | 95% | 0% | 3089 | -164
[5 empty] | 2019-02-13 | 35 | 1049.5 | 3077 | -148 | 1 | 0 | 3225 | 2931.1624 | 2931.1624 | 2931.1624 | 2503.5449 | 780 | 200 | 3483.5449 | 87.09% | 95% | 0% | -169.3364 | 2761.826 | -3550 | -400 | -1188.174 | 29.7% | 86.1% | 95% | 0% | 3225 | -148
[5 empty] | 2019-02-13 | 36 | 1050 | 3193 | -148 | 1 | 0 | 3341 | 3112.8607 | 3112.8607 | 3112.8607 | 2503.5449 | 780 | 200 | 3483.5449 | 87.09% | 95% | 0% | -169.3364 | 2943.5243 | -3550 | -400 | -1006.4757 | 25.16% | 86.09% | 95% | 0% | 3341 | -148
[5 empty] | 2019-02-13 | 37 | 1050.5 | 3172 | -148 | 1 | 0 | 3320 | 3079.967 | 3079.967 | 3079.967 | 2503.5449 | 780 | 200 | 3483.5449 | 87.09% | 95% | 0% | -169.3364 | 2910.6306 | -3550 | -400 | -1039.3694 | 25.98% | 86.09% | 95% | 0% | 3320 | -148
[5 empty] | 2019-02-13 | 38 | 1051 | 3135 | -149 | 0 | 0 | 3284 | 3023.5779 | 3023.5779 | 3023.5779 | 2503.5449 | 780 | 200 | 3483.5449 | 87.09% | 95% | 0% | -170.4805 | 2853.0974 | -2750 | -200 | -96.9026 | 2.423% | 86.09% | 95% | 0% | 3284 | -149
[5 empty] | 2019-02-13 | 39 | 1051.5 | 3107 | -149 | 0 | 0 | 3256 | 2979.7197 | 2979.7197 | 2979.7197 | 2503.5449 | 780 | 200 | 3483.5449 | 87.09% | 95% | 0% | -170.4805 | 2809.2392 | -2750 | -200 | -140.7608 | 3.519% | 86.09% | 95% | 0% | 3256 | -149
[5 empty] | 2019-02-13 | 40 | 1052 | 3030 | -149 | 0 | 0 | 3179 | 2859.1096 | 2859.1096 | 2859.1096 | 2503.5449 | 780 | 200 | 3483.5449 | 87.09% | 95% | 0% | -170.4805 | 2688.6291 | -2750 | -200 | -261.3709 | 6.534% | 86.09% | 95% | 0% | 3179 | -149
[5 empty] | 2019-02-13 | 41 | 1052.5 | 2945 | -149 | 0 | 0 | 3094 | 2725.9687 | 2725.9687 | 2725.9687 | 2503.5449 | 780 | 200 | 3483.5449 | 87.09% | 95% | 0% | -170.4805 | 2555.4881 | -2750 | -200 | -394.5119 | 9.863% | 86.08% | 95% | 0% | 3094 | -149
[5 empty] | 2019-02-13 | 42 | 1053 | 2801 | -150 | 0 | 0 | 2951 | 2501.9786 | 2501.9786 | 2501.9786 | 2503.5449 | 780 | 200 | 3483.5449 | 87.09% | 95% | 0% | -171.6247 | 2330.3539 | -2750 | -200 | -619.6461 | 15.49% | 86.05% | 95% | 0% | 2951 | -150
[5 empty] | 2019-02-13 | 43 | 1053.5 | 2662 | -150 | 0 | 0 | 2812 | 2284.2539 | 2284.2539 | 2284.2539 | 2501.9786 | 780 | 200 | 3481.9786 | 87.05% | 95% | 0% | -171.6247 | 2112.6292 | -2750 | -200 | -837.3708 | 20.93% | 86.05% | 95% | 0% | 2812 | -150
[5 empty] | 2019-02-13 | 44 | 1054 | 2492 | -151 | 0 | 0 | 2643 | 2019.5383 | 2019.5383 | 2019.5383 | 2501.9786 | 780 | 200 | 3481.9786 | 87.05% | 95% | 0% | -172.7689 | 1846.7695 | -2750 | -200 | -1103.2305 | 27.58% | 86.03% | 95% | 0% | 2643 | -151
[5 empty] | 2019-02-13 | 45 | 1054.5 | 2340 | -151 | 0 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 2501.9786 | 780 | 200 | 3481.9786 | 87.05% | 95% | 0% | -172.7689 | 1608.6821 | -2750 | -200 | -1341.3179 | 33.53% | 86.03% | 95% | 0% | 2491 | -151
[5 empty] | 2019-02-13 | 46 | 1055 | 2182 | -150 | 0 | 0 | 2332 | 1532.399 | 1532.399 | 1532.399 | 2501.9786 | 780 | 200 | 3481.9786 | 87.05% | 95% | 0% | -171.6247 | 1360.7743 | -2750 | -200 | -1589.2257 | 39.73% | 86.02% | 95% | 0% | 2332 | -150
[5 empty] | 2019-02-13 | 47 | 1055.5 | 2039 | -148 | 0 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 2501.9786 | 780 | 200 | 3481.9786 | 87.05% | 95% | 0% | -169.3364 | 1135.9398 | -2750 | -200 | -1814.0602 | 45.35% | 86.01% | 95% | 0% | 2187 | -148
[5 empty] | 2019-02-13 | 48 | 1056 | 1946 | -145 | 0 | 0 | 2091 | 1154.9052 | 1154.9052 | 1154.9052 | 2501.9786 | 780 | 200 | 3481.9786 | 87.05% | 95% | 0% | -165.9039 | 989.0013 | -2750 | -200 | -1960.9987 | 49.02% | 86% | 95% | 0% | 2091 | -145
[5 empty] | 2019-02-14 | 1 | 1056.5 | 1922 | -145 | 0 | 0 | 2067 | 1117.3124 | 1117.3124 | 1117.3124 | 2501.9786 | 780 | 200 | 3481.9786 | 87.05% | 95% | 0% | -165.9039 | 951.4086 | -2750 | -200 | -1998.5914 | 49.96% | 85.99% | 95% | 0% | 2067 | -145
[5 empty] | 2019-02-14 | 2 | 1057 | 1963 | -145 | 0 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 2501.9786 | 780 | 200 | 3481.9786 | 87.05% | 95% | 0% | -165.9039 | 1015.6295 | -2750 | -200 | -1934.3705 | 48.36% | 85.99% | 95% | 0% | 2108 | -145
[5 empty] | 2019-02-14 | 3 | 1057.5 | 1950 | -144 | 0 | 0 | 2094 | 1159.6043 | 1159.6043 | 1159.6043 | 2501.9786 | 780 | 200 | 3481.9786 | 87.05% | 95% | 0% | -164.7597 | 994.8446 | -2750 | -200 | -1955.1554 | 48.88% | 85.99% | 95% | 0% | 2094 | -144
[5 empty] | 2019-02-14 | 4 | 1058 | 1893 | -143 | 0 | 0 | 2036 | 1068.7552 | 1068.7552 | 1068.7552 | 2500.4122 | 780 | 200 | 3480.4122 | 87.01% | 95% | 0% | -163.6156 | 905.1396 | -2750 | -200 | -2044.8604 | 51.12% | 85.98% | 95% | 0% | 2036 | -143
[5 empty] | 2019-02-14 | 5 | 1058.5 | 1866 | -142 | 0 | 0 | 2008 | 1024.8969 | 1024.8969 | 1024.8969 | 2500.4122 | 780 | 200 | 3480.4122 | 87.01% | 95% | 0% | -162.4714 | 862.4256 | -2750 | -200 | -2087.5744 | 52.19% | 85.98% | 95% | 0% | 2008 | -142
[5 empty] | 2019-02-14 | 6 | 1059 | 1851 | -141 | 0 | 0 | 1992 | 999.8351 | 999.8351 | 999.8351 | 2500.4122 | 780 | 200 | 3480.4122 | 87.01% | 95% | 0% | -161.3272 | 838.5079 | -2750 | -200 | -2111.4921 | 52.79% | 85.98% | 95% | 0% | 1992 | -141
[5 empty] | 2019-02-14 | 7 | 1059.5 | 1835 | -139 | 0 | 0 | 1974 | 971.6406 | 971.6406 | 971.6406 | 2500.4122 | 780 | 200 | 3480.4122 | 87.01% | 95% | 0% | -159.0389 | 812.6017 | -2750 | -200 | -2137.3983 | 53.43% | 85.96% | 95% | 0% | 1974 | -139
[5 empty] | 2019-02-14 | 8 | 1060 | 1814 | -137 | 0 | 0 | 1951 | 935.6142 | 935.6142 | 935.6142 | 2498.8458 | 780 | 200 | 3478.8458 | 86.97% | 95% | 0% | -156.7506 | 778.8636 | -2750 | -200 | -2171.1364 | 54.28% | 85.94% | 95% | 0% | 1951 | -137
[5 empty] | 2019-02-14 | 9 | 1060.5 | 1810 | -135 | 0 | 0 | 1945 | 926.216 | 926.216 | 926.216 | 2498.8458 | 780 | 200 | 3478.8458 | 86.97% | 95% | 0% | -154.4622 | 771.7538 | -2750 | -200 | -2178.2462 | 54.46% | 85.92% | 95% | 0% | 1945 | -135
[5 empty] | 2019-02-14 | 10 | 1061 | 1839 | -134 | 0 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 2498.8458 | 780 | 200 | 3478.8458 | 86.97% | 95% | 0% | -153.3181 | 816.7561 | -2750 | -200 | -2133.2439 | 53.33% | 85.92% | 95% | 0% | 1973 | -134
[5 empty] | 2019-02-14 | 11 | 1061.5 | 1914 | -130 | 0 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 2498.8458 | 780 | 200 | 3478.8458 | 86.97% | 95% | 0% | -148.7414 | 932.5446 | -2750 | -200 | -2017.4554 | 50.44% | 85.91% | 95% | 0% | 2044 | -130
[5 empty] | 2019-02-14 | 12 | 1062 | 2033 | -125 | 0 | 0 | 2158 | 1259.8516 | 1259.8516 | 1259.8516 | 2498.8458 | 780 | 200 | 3478.8458 | 86.97% | 95% | 0% | -143.0206 | 1116.831 | -2750 | -200 | -1833.169 | 45.83% | 85.9% | 95% | 0% | 2158 | -125
[5 empty] | 2019-02-14 | 13 | 1062.5 | 2303 | -122 | 0 | 0 | 2425 | 1678.0709 | 1678.0709 | 1678.0709 | 2497.2795 | 780 | 200 | 3477.2795 | 86.93% | 95% | 0% | -139.5881 | 1538.4828 | -2750 | -200 | -1411.5172 | 35.29% | 85.9% | 95% | 0% | 2425 | -122
[5 empty] | 2019-02-14 | 14 | 1063 | 2555 | -118 | 0 | 0 | 2673 | 2066.5293 | 2066.5293 | 2066.5293 | 2497.2795 | 780 | 200 | 3477.2795 | 86.93% | 95% | 0% | -135.0114 | 1931.5178 | -2750 | -200 | -1018.4822 | 25.46% | 85.89% | 95% | 0% | 2673 | -118
[5 empty] | 2019-02-14 | 15 | 1063.5 | 2799 | -116 | 0 | 0 | 2915 | 2445.5894 | 2445.5894 | 2445.5894 | 2497.2795 | 780 | 200 | 3477.2795 | 86.93% | 95% | 0% | -132.7231 | 2312.8663 | -2750 | -200 | -637.1337 | 15.93% | 85.88% | 95% | 0% | 2915 | -116
[5 empty] | 2019-02-14 | 16 | 1064 | 2873 | -122 | 0 | 0 | 2995 | 2570.8986 | 2570.8986 | 2570.8986 | 2497.2795 | 780 | 200 | 3477.2795 | 86.93% | 95% | 0% | -139.5881 | 2431.3105 | -2750 | -200 | -518.6895 | 12.97% | 85.88% | 95% | 0% | 2995 | -122
[5 empty] | 2019-02-14 | 17 | 1064.5 | 2850 | -159 | 0 | 0 | 3009 | 2592.8277 | 2592.8277 | 2592.8277 | 2495.7131 | 780 | 200 | 3475.7131 | 86.89% | 95% | 0% | -181.9222 | 2410.9055 | -2750 | -200 | -539.0945 | 13.48% | 85.87% | 95% | 0% | 3009 | -159
[5 empty] | 2019-02-14 | 18 | 1065 | 2768 | -218 | 1 | 0 | 2986 | 2556.8013 | 2556.8013 | 2556.8013 | 2495.7131 | 780 | 200 | 3475.7131 | 86.89% | 95% | 0% | -249.4279 | 2307.3734 | -3550 | -400 | -1642.6266 | 41.07% | 85.86% | 95% | 0% | 2986 | -218
[5 empty] | 2019-02-14 | 19 | 1065.5 | 2678 | -283 | 1 | 0 | 2961 | 2517.6422 | 2517.6422 | 2517.6422 | 2495.7131 | 780 | 200 | 3475.7131 | 86.89% | 95% | 0% | -323.7986 | 2193.8436 | -3550 | -400 | -1756.1564 | 43.9% | 85.85% | 95% | 0% | 2961 | -283
[5 empty] | 2019-02-14 | 20 | 1066 | 2586 | -336 | 1 | 0 | 2922 | 2456.554 | 2456.554 | 2456.554 | 2495.7131 | 780 | 200 | 3475.7131 | 86.89% | 95% | 0% | -384.4394 | 2072.1146 | -3550 | -400 | -1877.8854 | 46.95% | 85.85% | 95% | 0% | 2922 | -336
[5 empty] | 2019-02-14 | 21 | 1066.5 | 2454 | -400 | 1 | 0 | 2854 | 2350.0412 | 2350.0412 | 2350.0412 | 2495.7131 | 780 | 200 | 3475.7131 | 86.89% | 95% | 0% | -457.6659 | 1892.3753 | -3550 | -400 | -2057.6247 | 51.44% | 85.85% | 95% | 0% | 2854 | -400
[5 empty] | 2019-02-14 | 22 | 1067 | 2303 | -498 | 1 | 0 | 2801 | 2267.0239 | 2267.0239 | 2267.0239 | 2495.7131 | 780 | 200 | 3475.7131 | 86.89% | 95% | 0% | -569.7941 | 1697.2299 | -3550 | -400 | -2252.7701 | 56.32% | 85.84% | 95% | 0% | 2801 | -498
[5 empty] | 2019-02-14 | 23 | 1067.5 | 2206 | -538 | 1 | 0 | 2744 | 2177.7411 | 2177.7411 | 2177.7411 | 2495.7131 | 780 | 200 | 3475.7131 | 86.89% | 95% | 0% | -615.5606 | 1562.1805 | -3550 | -400 | -2387.8195 | 59.7% | 85.83% | 95% | 0% | 2744 | -538
[5 empty] | 2019-02-14 | 24 | 1068 | 2129 | -562 | 1 | 0 | 2691 | 2094.7238 | 2094.7238 | 2094.7238 | 2495.7131 | 780 | 200 | 3475.7131 | 86.89% | 95% | 0% | -643.0206 | 1451.7032 | -3550 | -400 | -2498.2968 | 62.46% | 85.82% | 95% | 0% | 2691 | -562
[5 empty] | 2019-02-14 | 25 | 1068.5 | 2096 | -576 | 1 | 0 | 2672 | 2064.9629 | 2064.9629 | 2064.9629 | 2494.1467 | 780 | 200 | 3474.1467 | 86.85% | 95% | 0% | -659.0389 | 1405.924 | -3550 | -400 | -2544.076 | 63.6% | 85.82% | 95% | 0% | 2672 | -576
[5 empty] | 2019-02-14 | 26 | 1069 | 2052 | -586 | 1 | 0 | 2638 | 2011.7065 | 2011.7065 | 2011.7065 | 2494.1467 | 780 | 200 | 3474.1467 | 86.85% | 95% | 0% | -670.4805 | 1341.226 | -3550 | -400 | -2608.774 | 65.22% | 85.82% | 95% | 0% | 2638 | -586
[5 empty] | 2019-02-14 | 27 | 1069.5 | 2038 | -572 | 1 | 0 | 2610 | 1967.8483 | 1967.8483 | 1967.8483 | 2494.1467 | 780 | 200 | 3474.1467 | 86.85% | 95% | 0% | -654.4622 | 1313.3861 | -3550 | -400 | -2636.6139 | 65.92% | 85.81% | 95% | 0% | 2610 | -572
[5 empty] | 2019-02-14 | 28 | 1070 | 2067 | -554 | 1 | 0 | 2621 | 1985.0783 | 1985.0783 | 1985.0783 | 2494.1467 | 780 | 200 | 3474.1467 | 86.85% | 95% | 0% | -633.8673 | 1351.211 | -3550 | -400 | -2598.789 | 64.97% | 85.81% | 95% | 0% | 2621 | -554
[5 empty] | 2019-02-14 | 29 | 1070.5 | 2121 | -506 | 1 | 0 | 2627 | 1994.4765 | 1994.4765 | 1994.4765 | 2494.1467 | 780 | 200 | 3474.1467 | 86.85% | 95% | 0% | -578.9474 | 1415.5291 | -3550 | -400 | -2534.4709 | 63.36% | 85.81% | 95% | 0% | 2627 | -506
[5 empty] | 2019-02-14 | 30 | 1071 | 2199 | -444 | 1 | 0 | 2643 | 2019.5383 | 2019.5383 | 2019.5383 | 2492.5804 | 780 | 200 | 3472.5804 | 86.81% | 95% | 0% | -508.0092 | 1511.5292 | -3550 | -400 | -2438.4708 | 60.96% | 85.81% | 95% | 0% | 2643 | -444
[5 empty] | 2019-02-14 | 31 | 1071.5 | 2319 | -370 | 1 | 0 | 2689 | 2091.5911 | 2091.5911 | 2091.5911 | 2492.5804 | 780 | 200 | 3472.5804 | 86.81% | 95% | 0% | -423.341 | 1668.2501 | -3550 | -400 | -2281.7499 | 57.04% | 85.81% | 95% | 0% | 2689 | -370
[5 empty] | 2019-02-14 | 32 | 1072 | 2505 | -296 | 1 | 0 | 2801 | 2267.0239 | 2267.0239 | 2267.0239 | 2492.5804 | 780 | 200 | 3472.5804 | 86.81% | 95% | 0% | -338.6728 | 1928.3511 | -3550 | -400 | -2021.6489 | 50.54% | 85.8% | 95% | 0% | 2801 | -296
[5 empty] | 2019-02-14 | 33 | 1072.5 | 2696 | -211 | 1 | 0 | 2907 | 2433.0585 | 2433.0585 | 2433.0585 | 2492.5804 | 780 | 200 | 3472.5804 | 86.81% | 95% | 0% | -241.4188 | 2191.6398 | -3550 | -400 | -1758.3602 | 43.96% | 85.78% | 95% | 0% | 2907 | -211
[5 empty] | 2019-02-14 | 34 | 1073 | 2882 | -133 | 1 | 0 | 3015 | 2602.2259 | 2602.2259 | 2602.2259 | 2492.5804 | 780 | 200 | 3472.5804 | 86.81% | 95% | 0% | -152.1739 | 2450.052 | -3550 | -400 | -1499.948 | 37.5% | 85.77% | 95% | 0% | 3015 | -133
[5 empty] | 2019-02-14 | 35 | 1073.5 | 3044 | -103 | 1 | 0 | 3147 | 2808.986 | 2808.986 | 2808.986 | 2492.5804 | 780 | 200 | 3472.5804 | 86.81% | 95% | 0% | -117.849 | 2691.137 | -3550 | -400 | -1258.863 | 31.47% | 85.77% | 95% | 0% | 3147 | -103
[5 empty] | 2019-02-14 | 36 | 1074 | 3197 | -102 | 1 | 0 | 3299 | 3047.0734 | 3047.0734 | 3047.0734 | 2492.5804 | 780 | 200 | 3472.5804 | 86.81% | 95% | 0% | -116.7048 | 2930.3686 | -3550 | -400 | -1019.6314 | 25.49% | 85.77% | 95% | 0% | 3299 | -102
[5 empty] | 2019-02-14 | 37 | 1074.5 | 3229 | -103 | 0 | 0 | 3332 | 3098.7634 | 3098.7634 | 3098.7634 | 2492.5804 | 780 | 200 | 3472.5804 | 86.81% | 95% | 0% | -117.849 | 2980.9144 | -2750 | -200 | 30.9144 | -0.7729% | 85.77% | 95% | 0% | 3332 | -103
[5 empty] | 2019-02-14 | 38 | 1075 | 3208 | -104 | 0 | 0 | 3312 | 3067.4361 | 3067.4361 | 3067.4361 | 2492.5804 | 780 | 200 | 3472.5804 | 86.81% | 95% | 0% | -118.9931 | 2948.443 | -2750 | -200 | -1.557 | 0.03893% | 85.77% | 95% | 0% | 3312 | -104
[5 empty] | 2019-02-14 | 39 | 1075.5 | 3150 | -105 | 0 | 0 | 3255 | 2978.1533 | 2978.1533 | 2978.1533 | 2492.5804 | 780 | 200 | 3472.5804 | 86.81% | 95% | 0% | -120.1373 | 2858.016 | -2750 | -200 | -91.984 | 2.3% | 85.75% | 95% | 0% | 3255 | -105
[5 empty] | 2019-02-14 | 40 | 1076 | 3067 | -106 | 0 | 0 | 3173 | 2849.7115 | 2849.7115 | 2849.7115 | 2492.5804 | 780 | 200 | 3472.5804 | 86.81% | 95% | 0% | -121.2815 | 2728.43 | -2750 | -200 | -221.57 | 5.539% | 85.74% | 95% | 0% | 3173 | -106
[5 empty] | 2019-02-14 | 41 | 1076.5 | 2992 | -107 | 0 | 0 | 3099 | 2733.8005 | 2733.8005 | 2733.8005 | 2491.014 | 780 | 200 | 3471.014 | 86.78% | 95% | 0% | -122.4256 | 2611.3749 | -2750 | -200 | -338.6251 | 8.466% | 85.73% | 95% | 0% | 3099 | -107
[5 empty] | 2019-02-14 | 42 | 1077 | 2877 | -108 | 0 | 0 | 2985 | 2555.235 | 2555.235 | 2555.235 | 2491.014 | 780 | 200 | 3471.014 | 86.78% | 95% | 0% | -123.5698 | 2431.6652 | -2750 | -200 | -518.3348 | 12.96% | 85.73% | 95% | 0% | 2985 | -108
[5 empty] | 2019-02-14 | 43 | 1077.5 | 2729 | -110 | 0 | 0 | 2839 | 2326.5458 | 2326.5458 | 2326.5458 | 2491.014 | 780 | 200 | 3471.014 | 86.78% | 95% | 0% | -125.8581 | 2200.6876 | -2750 | -200 | -749.3124 | 18.73% | 85.72% | 95% | 0% | 2839 | -110
[5 empty] | 2019-02-14 | 44 | 1078 | 2561 | -111 | 0 | 0 | 2672 | 2064.9629 | 2064.9629 | 2064.9629 | 2491.014 | 780 | 200 | 3471.014 | 86.78% | 95% | 0% | -127.0023 | 1937.9606 | -2750 | -200 | -1012.0394 | 25.3% | 85.71% | 95% | 0% | 2672 | -111
[5 empty] | 2019-02-14 | 45 | 1078.5 | 2397 | -111 | 0 | 0 | 2508 | 1808.0791 | 1808.0791 | 1808.0791 | 2491.014 | 780 | 200 | 3471.014 | 86.78% | 95% | 0% | -127.0023 | 1681.0769 | -2750 | -200 | -1268.9231 | 31.72% | 85.71% | 95% | 0% | 2508 | -111
[5 empty] | 2019-02-14 | 46 | 1079 | 2269 | -111 | 0 | 0 | 2380 | 1607.5845 | 1607.5845 | 1607.5845 | 2491.014 | 780 | 200 | 3471.014 | 86.78% | 95% | 0% | -127.0023 | 1480.5822 | -2750 | -200 | -1469.4178 | 36.74% | 85.69% | 95% | 0% | 2380 | -111
[5 empty] | 2019-02-14 | 47 | 1079.5 | 2122 | -110 | 0 | 0 | 2232 | 1375.7626 | 1375.7626 | 1375.7626 | 2489.4477 | 780 | 200 | 3469.4477 | 86.74% | 95% | 0% | -125.8581 | 1249.9044 | -2750 | -200 | -1700.0956 | 42.5% | 85.69% | 95% | 0% | 2232 | -110
[5 empty] | 2019-02-14 | 48 | 1080 | 2034 | -109 | 0 | 0 | 2143 | 1236.3561 | 1236.3561 | 1236.3561 | 2489.4477 | 780 | 200 | 3469.4477 | 86.74% | 95% | 0% | -124.714 | 1111.6422 | -2750 | -200 | -1838.3578 | 45.96% | 85.68% | 95% | 0% | 2143 | -109
[5 empty] | 2019-02-15 | 1 | 1080.5 | 2016 | -109 | 0 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 2489.4477 | 780 | 200 | 3469.4477 | 86.74% | 95% | 0% | -124.714 | 1083.4476 | -2750 | -200 | -1866.5524 | 46.66% | 85.66% | 95% | 0% | 2125 | -109
[5 empty] | 2019-02-15 | 2 | 1081 | 2048 | -110 | 0 | 0 | 2158 | 1259.8516 | 1259.8516 | 1259.8516 | 2489.4477 | 780 | 200 | 3469.4477 | 86.74% | 95% | 0% | -125.8581 | 1133.9935 | -2750 | -200 | -1816.0065 | 45.4% | 85.66% | 95% | 0% | 2158 | -110
[5 empty] | 2019-02-15 | 3 | 1081.5 | 2030 | -110 | 0 | 0 | 2140 | 1231.657 | 1231.657 | 1231.657 | 2487.8813 | 780 | 200 | 3467.8813 | 86.7% | 95% | 0% | -125.8581 | 1105.7989 | -2750 | -200 | -1844.2011 | 46.11% | 85.65% | 95% | 0% | 2140 | -110
[5 empty] | 2019-02-15 | 4 | 1082 | 1985 | -110 | 0 | 0 | 2095 | 1161.1707 | 1161.1707 | 1161.1707 | 2487.8813 | 780 | 200 | 3467.8813 | 86.7% | 95% | 0% | -125.8581 | 1035.3125 | -2750 | -200 | -1914.6875 | 47.87% | 85.65% | 95% | 0% | 2095 | -110
[5 empty] | 2019-02-15 | 5 | 1082.5 | 1940 | -110 | 0 | 0 | 2050 | 1090.6843 | 1090.6843 | 1090.6843 | 2487.8813 | 780 | 200 | 3467.8813 | 86.7% | 95% | 0% | -125.8581 | 964.8261 | -2750 | -200 | -1985.1739 | 49.63% | 85.65% | 95% | 0% | 2050 | -110
[5 empty] | 2019-02-15 | 6 | 1083 | 1923 | -110 | 0 | 0 | 2033 | 1064.0561 | 1064.0561 | 1064.0561 | 2487.8813 | 780 | 200 | 3467.8813 | 86.7% | 95% | 0% | -125.8581 | 938.1979 | -2750 | -200 | -2011.8021 | 50.3% | 85.64% | 95% | 0% | 2033 | -110
[5 empty] | 2019-02-15 | 7 | 1083.5 | 1893 | -111 | 0 | 0 | 2004 | 1018.6315 | 1018.6315 | 1018.6315 | 2487.8813 | 780 | 200 | 3467.8813 | 86.7% | 95% | 0% | -127.0023 | 891.6292 | -2750 | -200 | -2058.3708 | 51.46% | 85.64% | 95% | 0% | 2004 | -111
[5 empty] | 2019-02-15 | 8 | 1084 | 1872 | -113 | 0 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 2486.3149 | 780 | 200 | 3466.3149 | 86.66% | 95% | 0% | -129.2906 | 859.58 | -2750 | -200 | -2090.42 | 52.26% | 85.64% | 95% | 0% | 1985 | -113
[5 empty] | 2019-02-15 | 9 | 1084.5 | 1872 | -114 | 0 | 0 | 1986 | 990.4369 | 990.4369 | 990.4369 | 2486.3149 | 780 | 200 | 3466.3149 | 86.66% | 95% | 0% | -130.4348 | 860.0022 | -2750 | -200 | -2089.9978 | 52.25% | 85.63% | 95% | 0% | 1986 | -114
[5 empty] | 2019-02-15 | 10 | 1085 | 1877 | -116 | 0 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 2486.3149 | 780 | 200 | 3466.3149 | 86.66% | 95% | 0% | -132.7231 | 868.6784 | -2750 | -200 | -2081.3216 | 52.03% | 85.63% | 95% | 0% | 1993 | -116
[5 empty] | 2019-02-15 | 11 | 1085.5 | 1937 | -117 | 0 | 0 | 2054 | 1096.9497 | 1096.9497 | 1096.9497 | 2486.3149 | 780 | 200 | 3466.3149 | 86.66% | 95% | 0% | -133.8673 | 963.0824 | -2750 | -200 | -1986.9176 | 49.67% | 85.62% | 95% | 0% | 2054 | -117
[5 empty] | 2019-02-15 | 12 | 1086 | 2030 | -118 | 0 | 0 | 2148 | 1244.188 | 1244.188 | 1244.188 | 2484.7486 | 780 | 200 | 3464.7486 | 86.62% | 95% | 0% | -135.0114 | 1109.1765 | -2750 | -200 | -1840.8235 | 46.02% | 85.61% | 95% | 0% | 2148 | -118
[5 empty] | 2019-02-15 | 13 | 1086.5 | 2287 | -118 | 0 | 0 | 2405 | 1646.7436 | 1646.7436 | 1646.7436 | 2484.7486 | 780 | 200 | 3464.7486 | 86.62% | 95% | 0% | -135.0114 | 1511.7322 | -2750 | -200 | -1438.2678 | 35.96% | 85.6% | 95% | 0% | 2405 | -118
[5 empty] | 2019-02-15 | 14 | 1087 | 2522 | -119 | 0 | 0 | 2641 | 2016.4056 | 2016.4056 | 2016.4056 | 2484.7486 | 780 | 200 | 3464.7486 | 86.62% | 95% | 0% | -136.1556 | 1880.25 | -2750 | -200 | -1069.75 | 26.74% | 85.6% | 95% | 0% | 2641 | -119
[5 empty] | 2019-02-15 | 15 | 1087.5 | 2768 | -121 | 0 | 0 | 2889 | 2404.864 | 2404.864 | 2404.864 | 2484.7486 | 780 | 200 | 3464.7486 | 86.62% | 95% | 0% | -138.4439 | 2266.42 | -2750 | -200 | -683.58 | 17.09% | 85.6% | 95% | 0% | 2889 | -121
[5 empty] | 2019-02-15 | 16 | 1088 | 2837 | -137 | 0 | 0 | 2974 | 2538.0049 | 2538.0049 | 2538.0049 | 2483.1822 | 780 | 200 | 3463.1822 | 86.58% | 95% | 0% | -156.7506 | 2381.2544 | -2750 | -200 | -568.7456 | 14.22% | 85.6% | 95% | 0% | 2974 | -137
[5 empty] | 2019-02-15 | 17 | 1088.5 | 2809 | -194 | 0 | 0 | 3003 | 2583.4295 | 2583.4295 | 2583.4295 | 2483.1822 | 780 | 200 | 3463.1822 | 86.58% | 95% | 0% | -221.968 | 2361.4616 | -2750 | -200 | -588.5384 | 14.71% | 85.6% | 95% | 0% | 3003 | -194
[5 empty] | 2019-02-15 | 18 | 1089 | 2719 | -264 | 1 | 0 | 2983 | 2552.1022 | 2552.1022 | 2552.1022 | 2481.6158 | 780 | 200 | 3461.6158 | 86.54% | 95% | 0% | -302.0595 | 2250.0427 | -3550 | -400 | -1699.9573 | 42.5% | 85.59% | 95% | 0% | 2983 | -264
[5 empty] | 2019-02-15 | 19 | 1089.5 | 2636 | -329 | 1 | 0 | 2965 | 2523.9077 | 2523.9077 | 2523.9077 | 2481.6158 | 780 | 200 | 3461.6158 | 86.54% | 95% | 0% | -376.4302 | 2147.4775 | -3550 | -400 | -1802.5225 | 45.06% | 85.59% | 95% | 0% | 2965 | -329
[5 empty] | 2019-02-15 | 20 | 1090 | 2485 | -412 | 1 | 0 | 2897 | 2417.3949 | 2417.3949 | 2417.3949 | 2481.6158 | 780 | 200 | 3461.6158 | 86.54% | 95% | 0% | -471.3959 | 1945.999 | -3550 | -400 | -2004.001 | 50.1% | 85.58% | 95% | 0% | 2897 | -412
[5 empty] | 2019-02-15 | 21 | 1090.5 | 2337 | -474 | 1 | 0 | 2811 | 2282.6876 | 2282.6876 | 2282.6876 | 2481.6158 | 780 | 200 | 3461.6158 | 86.54% | 95% | 0% | -542.3341 | 1740.3535 | -3550 | -400 | -2209.6465 | 55.24% | 85.58% | 95% | 0% | 2811 | -474
[5 empty] | 2019-02-15 | 22 | 1091 | 2144 | -589 | 1 | 0 | 2733 | 2160.5111 | 2160.5111 | 2160.5111 | 2481.6158 | 780 | 200 | 3461.6158 | 86.54% | 95% | 0% | -673.913 | 1486.5981 | -3550 | -400 | -2463.4019 | 61.59% | 85.58% | 95% | 0% | 2733 | -589
[5 empty] | 2019-02-15 | 23 | 1091.5 | 2029 | -634 | 1 | 0 | 2663 | 2050.8656 | 2050.8656 | 2050.8656 | 2480.0495 | 780 | 200 | 3460.0495 | 86.5% | 95% | 0% | -725.4005 | 1325.4652 | -3550 | -400 | -2624.5348 | 65.61% | 85.57% | 95% | 0% | 2663 | -634
[5 empty] | 2019-02-15 | 24 | 1092 | 1944 | -662 | 1 | 0 | 2606 | 1961.5829 | 1961.5829 | 1961.5829 | 2480.0495 | 780 | 200 | 3460.0495 | 86.5% | 95% | 0% | -757.4371 | 1204.1458 | -3550 | -400 | -2745.8542 | 68.65% | 85.55% | 95% | 0% | 2606 | -662
[5 empty] | 2019-02-15 | 25 | 1092.5 | 1899 | -677 | 1 | 0 | 2576 | 1914.5919 | 1914.5919 | 1914.5919 | 2480.0495 | 780 | 200 | 3460.0495 | 86.5% | 95% | 0% | -774.5995 | 1139.9924 | -3550 | -400 | -2810.0076 | 70.25% | 85.54% | 95% | 0% | 2576 | -677
[5 empty] | 2019-02-15 | 26 | 1093 | 1853 | -673 | 1 | 0 | 2526 | 1836.2737 | 1836.2737 | 1836.2737 | 2480.0495 | 780 | 200 | 3460.0495 | 86.5% | 95% | 0% | -770.0229 | 1066.2508 | -3550 | -400 | -2883.7492 | 72.09% | 85.54% | 95% | 0% | 2526 | -673
[5 empty] | 2019-02-15 | 27 | 1093.5 | 1850 | -649 | 1 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 2480.0495 | 780 | 200 | 3460.0495 | 86.5% | 95% | 0% | -742.5629 | 1051.4189 | -3550 | -400 | -2898.5811 | 72.46% | 85.54% | 95% | 0% | 2499 | -649
[5 empty] | 2019-02-15 | 28 | 1094 | 1866 | -612 | 1 | 0 | 2478 | 1761.0882 | 1761.0882 | 1761.0882 | 2480.0495 | 780 | 200 | 3460.0495 | 86.5% | 95% | 0% | -700.2288 | 1060.8594 | -3550 | -400 | -2889.1406 | 72.23% | 85.53% | 95% | 0% | 2478 | -612
[5 empty] | 2019-02-15 | 29 | 1094.5 | 1914 | -563 | 1 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 2478.4831 | 780 | 200 | 3458.4831 | 86.46% | 95% | 0% | -644.1648 | 1115.3571 | -3550 | -400 | -2834.6429 | 70.87% | 85.49% | 95% | 0% | 2477 | -563
[5 empty] | 2019-02-15 | 30 | 1095 | 2012 | -497 | 1 | 0 | 2509 | 1809.6455 | 1809.6455 | 1809.6455 | 2476.9167 | 780 | 200 | 3456.9167 | 86.42% | 95% | 0% | -568.6499 | 1240.9956 | -3550 | -400 | -2709.0044 | 67.73% | 85.49% | 95% | 0% | 2509 | -497
[5 empty] | 2019-02-15 | 31 | 1095.5 | 2116 | -425 | 1 | 0 | 2541 | 1859.7692 | 1859.7692 | 1859.7692 | 2476.9167 | 780 | 200 | 3456.9167 | 86.42% | 95% | 0% | -486.27 | 1373.4991 | -3550 | -400 | -2576.5009 | 64.41% | 85.49% | 95% | 0% | 2541 | -425
[5 empty] | 2019-02-15 | 32 | 1096 | 2292 | -345 | 1 | 0 | 2637 | 2010.1401 | 2010.1401 | 2010.1401 | 2476.9167 | 780 | 200 | 3456.9167 | 86.42% | 95% | 0% | -394.7368 | 1615.4033 | -3550 | -400 | -2334.5967 | 58.36% | 85.48% | 95% | 0% | 2637 | -345
[5 empty] | 2019-02-15 | 33 | 1096.5 | 2515 | -255 | 1 | 0 | 2770 | 2218.4666 | 2218.4666 | 2218.4666 | 2476.9167 | 780 | 200 | 3456.9167 | 86.42% | 95% | 0% | -291.762 | 1926.7046 | -3550 | -400 | -2023.2954 | 50.58% | 85.48% | 95% | 0% | 2770 | -255
[5 empty] | 2019-02-15 | 34 | 1097 | 2719 | -174 | 1 | 0 | 2893 | 2411.1294 | 2411.1294 | 2411.1294 | 2473.784 | 780 | 200 | 3453.784 | 86.34% | 95% | 0% | -199.0847 | 2212.0448 | -3550 | -400 | -1737.9552 | 43.45% | 85.47% | 95% | 0% | 2893 | -174
[5 empty] | 2019-02-15 | 35 | 1097.5 | 2871 | -147 | 1 | 0 | 3018 | 2606.925 | 2606.925 | 2606.925 | 2473.784 | 780 | 200 | 3453.784 | 86.34% | 95% | 0% | -168.1922 | 2438.7328 | -3550 | -400 | -1511.2672 | 37.78% | 85.47% | 95% | 0% | 3018 | -147
[5 empty] | 2019-02-15 | 36 | 1098 | 2986 | -148 | 1 | 0 | 3134 | 2788.6232 | 2788.6232 | 2788.6232 | 2473.784 | 780 | 200 | 3453.784 | 86.34% | 95% | 0% | -169.3364 | 2619.2869 | -3550 | -400 | -1330.7131 | 33.27% | 85.46% | 95% | 0% | 3134 | -148
[5 empty] | 2019-02-15 | 37 | 1098.5 | 3020 | -152 | 0 | 0 | 3172 | 2848.1451 | 2848.1451 | 2848.1451 | 2473.784 | 780 | 200 | 3453.784 | 86.34% | 95% | 0% | -173.913 | 2674.2321 | -2750 | -200 | -275.7679 | 6.894% | 85.46% | 95% | 0% | 3172 | -152
[5 empty] | 2019-02-15 | 38 | 1099 | 2988 | -156 | 0 | 0 | 3144 | 2804.2869 | 2804.2869 | 2804.2869 | 2473.784 | 780 | 200 | 3453.784 | 86.34% | 95% | 0% | -178.4897 | 2625.7972 | -2750 | -200 | -324.2028 | 8.105% | 85.44% | 95% | 0% | 3144 | -156
[5 empty] | 2019-02-15 | 39 | 1099.5 | 2952 | -157 | 0 | 0 | 3109 | 2749.4641 | 2749.4641 | 2749.4641 | 2473.784 | 780 | 200 | 3453.784 | 86.34% | 95% | 0% | -179.6339 | 2569.8303 | -2750 | -200 | -380.1697 | 9.504% | 85.44% | 95% | 0% | 3109 | -157
[5 empty] | 2019-02-15 | 40 | 1100 | 2852 | -157 | 0 | 0 | 3009 | 2592.8277 | 2592.8277 | 2592.8277 | 2472.2176 | 780 | 200 | 3452.2176 | 86.31% | 95% | 0% | -179.6339 | 2413.1938 | -2750 | -200 | -536.8062 | 13.42% | 85.43% | 95% | 0% | 3009 | -157
[5 empty] | 2019-02-15 | 41 | 1100.5 | 2729 | -160 | 0 | 0 | 2889 | 2404.864 | 2404.864 | 2404.864 | 2472.2176 | 780 | 200 | 3452.2176 | 86.31% | 95% | 0% | -183.0664 | 2221.7976 | -2750 | -200 | -728.2024 | 18.21% | 85.43% | 95% | 0% | 2889 | -160
[5 empty] | 2019-02-15 | 42 | 1101 | 2596 | -163 | 0 | 0 | 2759 | 2201.2366 | 2201.2366 | 2201.2366 | 2472.2176 | 780 | 200 | 3452.2176 | 86.31% | 95% | 0% | -186.4989 | 2014.7377 | -2750 | -200 | -935.2623 | 23.38% | 85.42% | 95% | 0% | 2759 | -163
[5 empty] | 2019-02-15 | 43 | 1101.5 | 2482 | -165 | 0 | 0 | 2647 | 2025.8038 | 2025.8038 | 2025.8038 | 2472.2176 | 780 | 200 | 3452.2176 | 86.31% | 95% | 0% | -188.7872 | 1837.0166 | -2750 | -200 | -1112.9834 | 27.82% | 85.42% | 95% | 0% | 2647 | -165
[5 empty] | 2019-02-15 | 44 | 1102 | 2338 | -167 | 0 | 0 | 2505 | 1803.38 | 1803.38 | 1803.38 | 2470.6513 | 780 | 200 | 3450.6513 | 86.27% | 95% | 0% | -191.0755 | 1612.3045 | -2750 | -200 | -1337.6955 | 33.44% | 85.41% | 95% | 0% | 2505 | -167
[5 empty] | 2019-02-15 | 45 | 1102.5 | 2179 | -168 | 0 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 2470.6513 | 780 | 200 | 3450.6513 | 86.27% | 95% | 0% | -192.2197 | 1363.6748 | -2750 | -200 | -1586.3252 | 39.66% | 85.4% | 95% | 0% | 2347 | -168
[5 empty] | 2019-02-15 | 46 | 1103 | 2040 | -168 | 0 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 2469.0849 | 780 | 200 | 3449.0849 | 86.23% | 95% | 0% | -192.2197 | 1145.9501 | -2750 | -200 | -1804.0499 | 45.1% | 85.4% | 95% | 0% | 2208 | -168
[5 empty] | 2019-02-15 | 47 | 1103.5 | 1905 | -167 | 0 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 2469.0849 | 780 | 200 | 3449.0849 | 86.23% | 95% | 0% | -191.0755 | 934.0688 | -2750 | -200 | -2015.9312 | 50.4% | 85.39% | 95% | 0% | 2072 | -167
[5 empty] | 2019-02-15 | 48 | 1104 | 1812 | -166 | 0 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 2469.0849 | 780 | 200 | 3449.0849 | 86.23% | 95% | 0% | -189.9314 | 787.9747 | -2750 | -200 | -2162.0253 | 54.05% | 85.39% | 95% | 0% | 1978 | -166
[5 empty] | 2019-02-16 | 1 | 1104.5 | 1796 | -167 | 0 | 0 | 1963 | 954.4106 | 954.4106 | 954.4106 | 2469.0849 | 780 | 200 | 3449.0849 | 86.23% | 95% | 0% | -191.0755 | 763.335 | -2750 | -200 | -2186.665 | 54.67% | 85.39% | 95% | 0% | 1963 | -167
[5 empty] | 2019-02-16 | 2 | 1105 | 1821 | -167 | 0 | 0 | 1988 | 993.5697 | 993.5697 | 993.5697 | 2469.0849 | 780 | 200 | 3449.0849 | 86.23% | 95% | 0% | -191.0755 | 802.4941 | -2750 | -200 | -2147.5059 | 53.69% | 85.37% | 95% | 0% | 1988 | -167
[5 empty] | 2019-02-16 | 3 | 1105.5 | 1782 | -166 | 0 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 2469.0849 | 780 | 200 | 3449.0849 | 86.23% | 95% | 0% | -189.9314 | 740.9837 | -2750 | -200 | -2209.0163 | 55.23% | 85.36% | 95% | 0% | 1948 | -166
[5 empty] | 2019-02-16 | 4 | 1106 | 1715 | -166 | 0 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 2469.0849 | 780 | 200 | 3449.0849 | 86.23% | 95% | 0% | -189.9314 | 636.0373 | -2750 | -200 | -2313.9627 | 57.85% | 85.34% | 95% | 0% | 1881 | -166
[5 empty] | 2019-02-16 | 5 | 1106.5 | 1686 | -162 | 0 | 0 | 1848 | 774.2786 | 774.2786 | 774.2786 | 2467.5185 | 780 | 200 | 3447.5185 | 86.19% | 95% | 0% | -185.3547 | 588.924 | -2750 | -200 | -2361.076 | 59.03% | 85.34% | 95% | 0% | 1848 | -162
[5 empty] | 2019-02-16 | 6 | 1107 | 1656 | -159 | 0 | 0 | 1815 | 722.5886 | 722.5886 | 722.5886 | 2467.5185 | 780 | 200 | 3447.5185 | 86.19% | 95% | 0% | -181.9222 | 540.6664 | -2750 | -200 | -2409.3336 | 60.23% | 85.34% | 95% | 0% | 1815 | -159
[5 empty] | 2019-02-16 | 7 | 1107.5 | 1630 | -152 | 0 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 2467.5185 | 780 | 200 | 3447.5185 | 86.19% | 95% | 0% | -173.913 | 496.9856 | -2750 | -200 | -2453.0144 | 61.33% | 85.33% | 95% | 0% | 1782 | -152
[5 empty] | 2019-02-16 | 8 | 1108 | 1614 | -144 | 0 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 2467.5185 | 780 | 200 | 3447.5185 | 86.19% | 95% | 0% | -164.7597 | 468.5461 | -2750 | -200 | -2481.4539 | 62.04% | 85.33% | 95% | 0% | 1758 | -144
[5 empty] | 2019-02-16 | 9 | 1108.5 | 1609 | -142 | 0 | 0 | 1751 | 622.3413 | 622.3413 | 622.3413 | 2467.5185 | 780 | 200 | 3447.5185 | 86.19% | 95% | 0% | -162.4714 | 459.8699 | -2750 | -200 | -2490.1301 | 62.25% | 85.33% | 95% | 0% | 1751 | -142
[5 empty] | 2019-02-16 | 10 | 1109 | 1616 | -139 | 0 | 0 | 1755 | 628.6068 | 628.6068 | 628.6068 | 2465.9522 | 780 | 200 | 3445.9522 | 86.15% | 95% | 0% | -159.0389 | 469.5679 | -2750 | -200 | -2480.4321 | 62.01% | 85.33% | 95% | 0% | 1755 | -139
[5 empty] | 2019-02-16 | 11 | 1109.5 | 1663 | -136 | 0 | 0 | 1799 | 697.5268 | 697.5268 | 697.5268 | 2465.9522 | 780 | 200 | 3445.9522 | 86.15% | 95% | 0% | -155.6064 | 541.9204 | -2750 | -200 | -2408.0796 | 60.2% | 85.29% | 95% | 0% | 1799 | -136
[5 empty] | 2019-02-16 | 12 | 1110 | 1684 | -133 | 0 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 2465.9522 | 780 | 200 | 3445.9522 | 86.15% | 95% | 0% | -152.1739 | 573.5474 | -2750 | -200 | -2376.4526 | 59.41% | 85.29% | 95% | 0% | 1817 | -133
[5 empty] | 2019-02-16 | 13 | 1110.5 | 1820 | -128 | 0 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 2465.9522 | 780 | 200 | 3445.9522 | 86.15% | 95% | 0% | -146.4531 | 784.462 | -2750 | -200 | -2165.538 | 54.14% | 85.29% | 95% | 0% | 1948 | -128
[5 empty] | 2019-02-16 | 14 | 1111 | 1930 | -123 | 0 | 0 | 2053 | 1095.3833 | 1095.3833 | 1095.3833 | 2465.9522 | 780 | 200 | 3445.9522 | 86.15% | 95% | 0% | -140.7323 | 954.6511 | -2750 | -200 | -1995.3489 | 49.88% | 85.27% | 95% | 0% | 2053 | -123
[5 empty] | 2019-02-16 | 15 | 1111.5 | 2049 | -121 | 0 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 2465.9522 | 780 | 200 | 3445.9522 | 86.15% | 95% | 0% | -138.4439 | 1140.204 | -2750 | -200 | -1809.796 | 45.24% | 85.26% | 95% | 0% | 2170 | -121
[5 empty] | 2019-02-16 | 16 | 1112 | 2135 | -123 | 0 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 2465.9522 | 780 | 200 | 3445.9522 | 86.15% | 95% | 0% | -140.7323 | 1275.7558 | -2750 | -200 | -1674.2442 | 41.86% | 85.26% | 95% | 0% | 2258 | -123
[5 empty] | 2019-02-16 | 17 | 1112.5 | 2259 | -141 | 0 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 2465.9522 | 780 | 200 | 3445.9522 | 86.15% | 95% | 0% | -161.3272 | 1477.5846 | -2750 | -200 | -1472.4154 | 36.81% | 85.25% | 95% | 0% | 2400 | -141
[5 empty] | 2019-02-16 | 18 | 1113 | 2333 | -167 | 1 | 0 | 2500 | 1795.5482 | 1795.5482 | 1795.5482 | 2465.9522 | 780 | 200 | 3445.9522 | 86.15% | 95% | 0% | -191.0755 | 1604.4727 | -3550 | -400 | -2345.5273 | 58.64% | 85.24% | 95% | 0% | 2500 | -167
[5 empty] | 2019-02-16 | 19 | 1113.5 | 2370 | -201 | 1 | 0 | 2571 | 1906.7601 | 1906.7601 | 1906.7601 | 2464.3858 | 780 | 200 | 3444.3858 | 86.11% | 95% | 0% | -229.9771 | 1676.783 | -3550 | -400 | -2273.217 | 56.83% | 85.24% | 95% | 0% | 2571 | -201
[5 empty] | 2019-02-16 | 20 | 1114 | 2341 | -236 | 1 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 2464.3858 | 780 | 200 | 3444.3858 | 86.11% | 95% | 0% | -270.0229 | 1646.1354 | -3550 | -400 | -2303.8646 | 57.6% | 85.23% | 95% | 0% | 2577 | -236
[5 empty] | 2019-02-16 | 21 | 1114.5 | 2288 | -273 | 1 | 0 | 2561 | 1891.0965 | 1891.0965 | 1891.0965 | 2464.3858 | 780 | 200 | 3444.3858 | 86.11% | 95% | 0% | -312.357 | 1578.7395 | -3550 | -400 | -2371.2605 | 59.28% | 85.23% | 95% | 0% | 2561 | -273
[5 empty] | 2019-02-16 | 22 | 1115 | 2233 | -301 | 1 | 0 | 2534 | 1848.8046 | 1848.8046 | 1848.8046 | 2462.8195 | 780 | 200 | 3442.8195 | 86.07% | 95% | 0% | -344.3936 | 1504.411 | -3550 | -400 | -2445.589 | 61.14% | 85.2% | 95% | 0% | 2534 | -301
[5 empty] | 2019-02-16 | 23 | 1115.5 | 2203 | -309 | 1 | 0 | 2512 | 1814.3446 | 1814.3446 | 1814.3446 | 2462.8195 | 780 | 200 | 3442.8195 | 86.07% | 95% | 0% | -353.5469 | 1460.7977 | -3550 | -400 | -2489.2023 | 62.23% | 85.2% | 95% | 0% | 2512 | -309
[5 empty] | 2019-02-16 | 24 | 1116 | 2212 | -300 | 1 | 0 | 2512 | 1814.3446 | 1814.3446 | 1814.3446 | 2462.8195 | 780 | 200 | 3442.8195 | 86.07% | 95% | 0% | -343.2494 | 1471.0952 | -3550 | -400 | -2478.9048 | 61.97% | 85.2% | 95% | 0% | 2512 | -300
[5 empty] | 2019-02-16 | 25 | 1116.5 | 2199 | -306 | 1 | 0 | 2505 | 1803.38 | 1803.38 | 1803.38 | 2462.8195 | 780 | 200 | 3442.8195 | 86.07% | 95% | 0% | -350.1144 | 1453.2656 | -3550 | -400 | -2496.7344 | 62.42% | 85.2% | 95% | 0% | 2505 | -306
[5 empty] | 2019-02-16 | 26 | 1117 | 2163 | -309 | 1 | 0 | 2472 | 1751.69 | 1751.69 | 1751.69 | 2462.8195 | 780 | 200 | 3442.8195 | 86.07% | 95% | 0% | -353.5469 | 1398.1431 | -3550 | -400 | -2551.8569 | 63.8% | 85.2% | 95% | 0% | 2472 | -309
[5 empty] | 2019-02-16 | 27 | 1117.5 | 2145 | -306 | 1 | 0 | 2451 | 1718.7964 | 1718.7964 | 1718.7964 | 2461.2531 | 780 | 200 | 3441.2531 | 86.03% | 95% | 0% | -350.1144 | 1368.682 | -3550 | -400 | -2581.318 | 64.53% | 85.2% | 95% | 0% | 2451 | -306
[5 empty] | 2019-02-16 | 28 | 1118 | 2113 | -305 | 1 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 2461.2531 | 780 | 200 | 3441.2531 | 86.03% | 95% | 0% | -348.9703 | 1318.1361 | -3550 | -400 | -2631.8639 | 65.8% | 85.19% | 95% | 0% | 2418 | -305
[5 empty] | 2019-02-16 | 29 | 1118.5 | 2129 | -290 | 1 | 0 | 2419 | 1668.6727 | 1668.6727 | 1668.6727 | 2461.2531 | 780 | 200 | 3441.2531 | 86.03% | 95% | 0% | -331.8078 | 1336.8649 | -3550 | -400 | -2613.1351 | 65.33% | 85.19% | 95% | 0% | 2419 | -290
[5 empty] | 2019-02-16 | 30 | 1119 | 2161 | -257 | 1 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 2461.2531 | 780 | 200 | 3441.2531 | 86.03% | 95% | 0% | -294.0503 | 1373.056 | -3550 | -400 | -2576.944 | 64.42% | 85.18% | 95% | 0% | 2418 | -257
[5 empty] | 2019-02-16 | 31 | 1119.5 | 2245 | -212 | 1 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 2459.6867 | 780 | 200 | 3439.6867 | 85.99% | 95% | 0% | -242.5629 | 1485.6316 | -3550 | -400 | -2464.3684 | 61.61% | 85.18% | 95% | 0% | 2457 | -212
[5 empty] | 2019-02-16 | 32 | 1120 | 2329 | -176 | 1 | 0 | 2505 | 1803.38 | 1803.38 | 1803.38 | 2459.6867 | 780 | 200 | 3439.6867 | 85.99% | 95% | 0% | -201.373 | 1602.0071 | -3550 | -400 | -2347.9929 | 58.7% | 85.16% | 95% | 0% | 2505 | -176
[5 empty] | 2019-02-16 | 33 | 1120.5 | 2445 | -148 | 1 | 0 | 2593 | 1941.2201 | 1941.2201 | 1941.2201 | 2459.6867 | 780 | 200 | 3439.6867 | 85.99% | 95% | 0% | -169.3364 | 1771.8837 | -3550 | -400 | -2178.1163 | 54.45% | 85.16% | 95% | 0% | 2593 | -148
[5 empty] | 2019-02-16 | 34 | 1121 | 2561 | -132 | 1 | 0 | 2693 | 2097.8566 | 2097.8566 | 2097.8566 | 2459.6867 | 780 | 200 | 3439.6867 | 85.99% | 95% | 0% | -151.0297 | 1946.8268 | -3550 | -400 | -2003.1732 | 50.08% | 85.15% | 95% | 0% | 2693 | -132
[5 empty] | 2019-02-16 | 35 | 1121.5 | 2714 | -129 | 1 | 0 | 2843 | 2332.8112 | 2332.8112 | 2332.8112 | 2459.6867 | 780 | 200 | 3439.6867 | 85.99% | 95% | 0% | -147.5973 | 2185.214 | -3550 | -400 | -1764.786 | 44.12% | 85.15% | 95% | 0% | 2843 | -129
[5 empty] | 2019-02-16 | 36 | 1122 | 2817 | -129 | 1 | 0 | 2946 | 2494.1467 | 2494.1467 | 2494.1467 | 2459.6867 | 780 | 200 | 3439.6867 | 85.99% | 95% | 0% | -147.5973 | 2346.5495 | -3550 | -400 | -1603.4505 | 40.09% | 85.14% | 95% | 0% | 2946 | -129
[5 empty] | 2019-02-16 | 37 | 1122.5 | 2784 | -133 | 0 | 0 | 2917 | 2448.7222 | 2448.7222 | 2448.7222 | 2459.6867 | 780 | 200 | 3439.6867 | 85.99% | 95% | 0% | -152.1739 | 2296.5483 | -2750 | -200 | -653.4517 | 16.34% | 85.14% | 95% | 0% | 2917 | -133
[5 empty] | 2019-02-16 | 38 | 1123 | 2756 | -137 | 0 | 0 | 2893 | 2411.1294 | 2411.1294 | 2411.1294 | 2458.1204 | 780 | 200 | 3438.1204 | 85.95% | 95% | 0% | -156.7506 | 2254.3789 | -2750 | -200 | -695.6211 | 17.39% | 85.12% | 95% | 0% | 2893 | -137
[5 empty] | 2019-02-16 | 39 | 1123.5 | 2696 | -141 | 0 | 0 | 2837 | 2323.413 | 2323.413 | 2323.413 | 2458.1204 | 780 | 200 | 3438.1204 | 85.95% | 95% | 0% | -161.3272 | 2162.0858 | -2750 | -200 | -787.9142 | 19.7% | 85.11% | 95% | 0% | 2837 | -141
[5 empty] | 2019-02-16 | 40 | 1124 | 2580 | -145 | 0 | 0 | 2725 | 2147.9802 | 2147.9802 | 2147.9802 | 2458.1204 | 780 | 200 | 3438.1204 | 85.95% | 95% | 0% | -165.9039 | 1982.0763 | -2750 | -200 | -967.9237 | 24.2% | 85.11% | 95% | 0% | 2725 | -145
[5 empty] | 2019-02-16 | 41 | 1124.5 | 2467 | -148 | 0 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 2458.1204 | 780 | 200 | 3438.1204 | 85.95% | 95% | 0% | -169.3364 | 1806.3437 | -2750 | -200 | -1143.6563 | 28.59% | 85.11% | 95% | 0% | 2615 | -148
[5 empty] | 2019-02-16 | 42 | 1125 | 2350 | -151 | 0 | 0 | 2501 | 1797.1146 | 1797.1146 | 1797.1146 | 2458.1204 | 780 | 200 | 3438.1204 | 85.95% | 95% | 0% | -172.7689 | 1624.3457 | -2750 | -200 | -1325.6543 | 33.14% | 85.11% | 95% | 0% | 2501 | -151
[5 empty] | 2019-02-16 | 43 | 1125.5 | 2241 | -154 | 0 | 0 | 2395 | 1631.08 | 1631.08 | 1631.08 | 2456.554 | 780 | 200 | 3436.554 | 85.91% | 95% | 0% | -176.2014 | 1454.8786 | -2750 | -200 | -1495.1214 | 37.38% | 85.09% | 95% | 0% | 2395 | -154
[5 empty] | 2019-02-16 | 44 | 1126 | 2132 | -157 | 0 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 2456.554 | 780 | 200 | 3436.554 | 85.91% | 95% | 0% | -179.6339 | 1285.4115 | -2750 | -200 | -1664.5885 | 41.61% | 85.08% | 95% | 0% | 2289 | -157
[5 empty] | 2019-02-16 | 45 | 1126.5 | 2013 | -161 | 0 | 0 | 2174 | 1284.9134 | 1284.9134 | 1284.9134 | 2456.554 | 780 | 200 | 3436.554 | 85.91% | 95% | 0% | -184.2105 | 1100.7029 | -2750 | -200 | -1849.2971 | 46.23% | 85.08% | 95% | 0% | 2174 | -161
[5 empty] | 2019-02-16 | 46 | 1127 | 1925 | -165 | 0 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 2456.554 | 780 | 200 | 3436.554 | 85.91% | 95% | 0% | -188.7872 | 964.5516 | -2750 | -200 | -1985.4484 | 49.64% | 85.06% | 95% | 0% | 2090 | -165
[5 empty] | 2019-02-16 | 47 | 1127.5 | 1802 | -166 | 0 | 0 | 1968 | 962.2424 | 962.2424 | 962.2424 | 2456.554 | 780 | 200 | 3436.554 | 85.91% | 95% | 0% | -189.9314 | 772.311 | -2750 | -200 | -2177.689 | 54.44% | 85.06% | 95% | 0% | 1968 | -166
[5 empty] | 2019-02-16 | 48 | 1128 | 1735 | -166 | 0 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 2456.554 | 780 | 200 | 3436.554 | 85.91% | 95% | 0% | -189.9314 | 667.3646 | -2750 | -200 | -2282.6354 | 57.07% | 85.05% | 95% | 0% | 1901 | -166
[5 empty] | 2019-02-17 | 1 | 1128.5 | 1710 | -169 | 0 | 0 | 1879 | 822.8359 | 822.8359 | 822.8359 | 2456.554 | 780 | 200 | 3436.554 | 85.91% | 95% | 0% | -193.3638 | 629.4721 | -2750 | -200 | -2320.5279 | 58.01% | 85.05% | 95% | 0% | 1879 | -169
[5 empty] | 2019-02-17 | 2 | 1129 | 1728 | -172 | 0 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 2454.9876 | 780 | 200 | 3434.9876 | 85.87% | 95% | 0% | -196.7963 | 658.9333 | -2750 | -200 | -2291.0667 | 57.28% | 85.05% | 95% | 0% | 1900 | -172
[5 empty] | 2019-02-17 | 3 | 1129.5 | 1698 | -171 | 0 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 2454.9876 | 780 | 200 | 3434.9876 | 85.87% | 95% | 0% | -195.6522 | 611.5201 | -2750 | -200 | -2338.4799 | 58.46% | 85.05% | 95% | 0% | 1869 | -171
[5 empty] | 2019-02-17 | 4 | 1130 | 1629 | -170 | 0 | 0 | 1799 | 697.5268 | 697.5268 | 697.5268 | 2454.9876 | 780 | 200 | 3434.9876 | 85.87% | 95% | 0% | -194.508 | 503.0188 | -2750 | -200 | -2446.9812 | 61.17% | 85.04% | 95% | 0% | 1799 | -170
[5 empty] | 2019-02-17 | 5 | 1130.5 | 1562 | -169 | 0 | 0 | 1731 | 591.014 | 591.014 | 591.014 | 2454.9876 | 780 | 200 | 3434.9876 | 85.87% | 95% | 0% | -193.3638 | 397.6502 | -2750 | -200 | -2552.3498 | 63.81% | 85.03% | 95% | 0% | 1731 | -169
[5 empty] | 2019-02-17 | 6 | 1131 | 1538 | -168 | 0 | 0 | 1706 | 551.8549 | 551.8549 | 551.8549 | 2454.9876 | 780 | 200 | 3434.9876 | 85.87% | 95% | 0% | -192.2197 | 359.6352 | -2750 | -200 | -2590.3648 | 64.76% | 85.03% | 95% | 0% | 1706 | -168
[5 empty] | 2019-02-17 | 7 | 1131.5 | 1483 | -171 | 0 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 2454.9876 | 780 | 200 | 3434.9876 | 85.87% | 95% | 0% | -195.6522 | 274.7518 | -2750 | -200 | -2675.2482 | 66.88% | 85.02% | 95% | 0% | 1654 | -171
[5 empty] | 2019-02-17 | 8 | 1132 | 1459 | -173 | 0 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 2454.9876 | 780 | 200 | 3434.9876 | 85.87% | 95% | 0% | -197.9405 | 238.0034 | -2750 | -200 | -2711.9966 | 67.8% | 85.02% | 95% | 0% | 1632 | -173
[5 empty] | 2019-02-17 | 9 | 1132.5 | 1432 | -173 | 0 | 0 | 1605 | 393.6521 | 393.6521 | 393.6521 | 2454.9876 | 780 | 200 | 3434.9876 | 85.87% | 95% | 0% | -197.9405 | 195.7116 | -2750 | -200 | -2754.2884 | 68.86% | 85.01% | 95% | 0% | 1605 | -173
[5 empty] | 2019-02-17 | 10 | 1133 | 1427 | -172 | 0 | 0 | 1599 | 384.2539 | 384.2539 | 384.2539 | 2454.9876 | 780 | 200 | 3434.9876 | 85.87% | 95% | 0% | -196.7963 | 187.4576 | -2750 | -200 | -2762.5424 | 69.06% | 85.01% | 95% | 0% | 1599 | -172
[5 empty] | 2019-02-17 | 11 | 1133.5 | 1447 | -172 | 0 | 0 | 1619 | 415.5812 | 415.5812 | 415.5812 | 2453.4213 | 780 | 200 | 3433.4213 | 85.84% | 95% | 0% | -196.7963 | 218.7849 | -2750 | -200 | -2731.2151 | 68.28% | 85% | 95% | 0% | 1619 | -172
[5 empty] | 2019-02-17 | 12 | 1134 | 1471 | -173 | 0 | 0 | 1644 | 454.7403 | 454.7403 | 454.7403 | 2453.4213 | 780 | 200 | 3433.4213 | 85.84% | 95% | 0% | -197.9405 | 256.7998 | -2750 | -200 | -2693.2002 | 67.33% | 84.99% | 95% | 0% | 1644 | -173
[5 empty] | 2019-02-17 | 13 | 1134.5 | 1554 | -173 | 0 | 0 | 1727 | 584.7486 | 584.7486 | 584.7486 | 2453.4213 | 780 | 200 | 3433.4213 | 85.84% | 95% | 0% | -197.9405 | 386.8081 | -2750 | -200 | -2563.1919 | 64.08% | 84.99% | 95% | 0% | 1727 | -173
[5 empty] | 2019-02-17 | 14 | 1135 | 1618 | -174 | 0 | 0 | 1792 | 686.5622 | 686.5622 | 686.5622 | 2453.4213 | 780 | 200 | 3433.4213 | 85.84% | 95% | 0% | -199.0847 | 487.4776 | -2750 | -200 | -2462.5224 | 61.56% | 84.98% | 95% | 0% | 1792 | -174
[5 empty] | 2019-02-17 | 15 | 1135.5 | 1677 | -177 | 0 | 0 | 1854 | 783.6768 | 783.6768 | 783.6768 | 2451.8549 | 780 | 200 | 3431.8549 | 85.8% | 95% | 0% | -202.5172 | 581.1597 | -2750 | -200 | -2368.8403 | 59.22% | 84.97% | 95% | 0% | 1854 | -177
[5 empty] | 2019-02-17 | 16 | 1136 | 1711 | -196 | 1 | 0 | 1907 | 866.6941 | 866.6941 | 866.6941 | 2451.8549 | 780 | 200 | 3431.8549 | 85.8% | 95% | 0% | -224.2563 | 642.4379 | -3550 | -400 | -3307.5621 | 82.69% | 84.97% | 95% | 0% | 1907 | -196
[5 empty] | 2019-02-17 | 17 | 1136.5 | 1761 | -248 | 1 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 2451.8549 | 780 | 200 | 3431.8549 | 85.8% | 95% | 0% | -283.7529 | 742.7105 | -3550 | -400 | -3207.2895 | 80.18% | 84.95% | 95% | 0% | 2009 | -248
[5 empty] | 2019-02-17 | 18 | 1137 | 1771 | -299 | 1 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 2451.8549 | 780 | 200 | 3431.8549 | 85.8% | 95% | 0% | -342.1053 | 779.9063 | -3550 | -400 | -3170.0937 | 79.25% | 84.95% | 95% | 0% | 2070 | -299
[5 empty] | 2019-02-17 | 19 | 1137.5 | 1783 | -344 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 2450.2885 | 780 | 200 | 3430.2885 | 85.76% | 95% | 0% | -393.5927 | 817.7016 | -3550 | -400 | -3132.2984 | 78.31% | 84.95% | 95% | 0% | 2127 | -344
[5 empty] | 2019-02-17 | 20 | 1138 | 1810 | -369 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 2450.2885 | 780 | 200 | 3430.2885 | 85.76% | 95% | 0% | -422.1968 | 870.5485 | -3550 | -400 | -3079.4515 | 76.99% | 84.93% | 95% | 0% | 2179 | -369
[5 empty] | 2019-02-17 | 21 | 1138.5 | 1800 | -403 | 1 | 0 | 2203 | 1330.338 | 1330.338 | 1330.338 | 2448.7222 | 780 | 200 | 3428.7222 | 85.72% | 95% | 0% | -461.0984 | 869.2396 | -3550 | -400 | -3080.7604 | 77.02% | 84.93% | 95% | 0% | 2203 | -403
[5 empty] | 2019-02-17 | 22 | 1139 | 1723 | -482 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 2448.7222 | 780 | 200 | 3428.7222 | 85.72% | 95% | 0% | -551.4874 | 781.9833 | -3550 | -400 | -3168.0167 | 79.2% | 84.93% | 95% | 0% | 2205 | -482
[5 empty] | 2019-02-17 | 23 | 1139.5 | 1724 | -497 | 1 | 0 | 2221 | 1358.5326 | 1358.5326 | 1358.5326 | 2448.7222 | 780 | 200 | 3428.7222 | 85.72% | 95% | 0% | -568.6499 | 789.8827 | -3550 | -400 | -3160.1173 | 79% | 84.92% | 95% | 0% | 2221 | -497
[5 empty] | 2019-02-17 | 24 | 1140 | 1703 | -529 | 1 | 0 | 2232 | 1375.7626 | 1375.7626 | 1375.7626 | 2448.7222 | 780 | 200 | 3428.7222 | 85.72% | 95% | 0% | -605.2632 | 770.4994 | -3550 | -400 | -3179.5006 | 79.49% | 84.91% | 95% | 0% | 2232 | -529
[5 empty] | 2019-02-17 | 25 | 1140.5 | 1718 | -507 | 1 | 0 | 2225 | 1364.798 | 1364.798 | 1364.798 | 2448.7222 | 780 | 200 | 3428.7222 | 85.72% | 95% | 0% | -580.0915 | 784.7065 | -3550 | -400 | -3165.2935 | 79.13% | 84.9% | 95% | 0% | 2225 | -507
[5 empty] | 2019-02-17 | 26 | 1141 | 1737 | -497 | 1 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 2448.7222 | 780 | 200 | 3428.7222 | 85.72% | 95% | 0% | -568.6499 | 810.2454 | -3550 | -400 | -3139.7546 | 78.49% | 84.9% | 95% | 0% | 2234 | -497
[5 empty] | 2019-02-17 | 27 | 1141.5 | 1741 | -464 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 2447.1558 | 780 | 200 | 3427.1558 | 85.68% | 95% | 0% | -530.8924 | 802.5783 | -3550 | -400 | -3147.4217 | 78.69% | 84.89% | 95% | 0% | 2205 | -464
[5 empty] | 2019-02-17 | 28 | 1142 | 1747 | -444 | 1 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 2447.1558 | 780 | 200 | 3427.1558 | 85.68% | 95% | 0% | -508.0092 | 803.5325 | -3550 | -400 | -3146.4675 | 78.66% | 84.89% | 95% | 0% | 2191 | -444
[5 empty] | 2019-02-17 | 29 | 1142.5 | 1776 | -414 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 2447.1558 | 780 | 200 | 3427.1558 | 85.68% | 95% | 0% | -473.6842 | 836.2911 | -3550 | -400 | -3113.7089 | 77.84% | 84.88% | 95% | 0% | 2190 | -414
[5 empty] | 2019-02-17 | 30 | 1143 | 1830 | -375 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 2447.1558 | 780 | 200 | 3427.1558 | 85.68% | 95% | 0% | -429.0618 | 904.4089 | -3550 | -400 | -3045.5911 | 76.14% | 84.87% | 95% | 0% | 2205 | -375
[5 empty] | 2019-02-17 | 31 | 1143.5 | 1921 | -337 | 1 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 2447.1558 | 780 | 200 | 3427.1558 | 85.68% | 95% | 0% | -385.5835 | 1030.9045 | -3550 | -400 | -2919.0955 | 72.98% | 84.86% | 95% | 0% | 2258 | -337
[5 empty] | 2019-02-17 | 32 | 1144 | 2034 | -297 | 1 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 2445.5894 | 780 | 200 | 3425.5894 | 85.64% | 95% | 0% | -339.8169 | 1191.0157 | -3550 | -400 | -2758.9843 | 68.97% | 84.86% | 95% | 0% | 2331 | -297
[5 empty] | 2019-02-17 | 33 | 1144.5 | 2203 | -237 | 1 | 0 | 2440 | 1701.5664 | 1701.5664 | 1701.5664 | 2445.5894 | 780 | 200 | 3425.5894 | 85.64% | 95% | 0% | -271.167 | 1430.3993 | -3550 | -400 | -2519.6007 | 62.99% | 84.84% | 95% | 0% | 2440 | -237
[5 empty] | 2019-02-17 | 34 | 1145 | 2385 | -188 | 1 | 0 | 2573 | 1909.8928 | 1909.8928 | 1909.8928 | 2445.5894 | 780 | 200 | 3425.5894 | 85.64% | 95% | 0% | -215.103 | 1694.7899 | -3550 | -400 | -2255.2101 | 56.38% | 84.84% | 95% | 0% | 2573 | -188
[5 empty] | 2019-02-17 | 35 | 1145.5 | 2524 | -166 | 1 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 2445.5894 | 780 | 200 | 3425.5894 | 85.64% | 95% | 0% | -189.9314 | 1903.2261 | -3550 | -400 | -2046.7739 | 51.17% | 84.84% | 95% | 0% | 2690 | -166
[5 empty] | 2019-02-17 | 36 | 1146 | 2640 | -162 | 1 | 0 | 2802 | 2268.5903 | 2268.5903 | 2268.5903 | 2444.0231 | 780 | 200 | 3424.0231 | 85.6% | 95% | 0% | -185.3547 | 2083.2356 | -3550 | -400 | -1866.7644 | 46.67% | 84.83% | 95% | 0% | 2802 | -162
[5 empty] | 2019-02-17 | 37 | 1146.5 | 2678 | -163 | 1 | 0 | 2841 | 2329.6785 | 2329.6785 | 2329.6785 | 2444.0231 | 780 | 200 | 3424.0231 | 85.6% | 95% | 0% | -186.4989 | 2143.1796 | -3550 | -400 | -1806.8204 | 45.17% | 84.83% | 95% | 0% | 2841 | -163
[5 empty] | 2019-02-17 | 38 | 1147 | 2619 | -164 | 0 | 0 | 2783 | 2238.8293 | 2238.8293 | 2238.8293 | 2444.0231 | 780 | 200 | 3424.0231 | 85.6% | 95% | 0% | -187.643 | 2051.1863 | -2750 | -200 | -898.8137 | 22.47% | 84.81% | 95% | 0% | 2783 | -164
[5 empty] | 2019-02-17 | 39 | 1147.5 | 2571 | -165 | 0 | 0 | 2736 | 2165.2102 | 2165.2102 | 2165.2102 | 2442.4567 | 780 | 200 | 3422.4567 | 85.56% | 95% | 0% | -188.7872 | 1976.423 | -2750 | -200 | -973.577 | 24.34% | 84.81% | 95% | 0% | 2736 | -165
[5 empty] | 2019-02-17 | 40 | 1148 | 2501 | -165 | 0 | 0 | 2666 | 2055.5647 | 2055.5647 | 2055.5647 | 2442.4567 | 780 | 200 | 3422.4567 | 85.56% | 95% | 0% | -188.7872 | 1866.7775 | -2750 | -200 | -1083.2225 | 27.08% | 84.81% | 95% | 0% | 2666 | -165
[5 empty] | 2019-02-17 | 41 | 1148.5 | 2419 | -166 | 0 | 0 | 2585 | 1928.6892 | 1928.6892 | 1928.6892 | 2442.4567 | 780 | 200 | 3422.4567 | 85.56% | 95% | 0% | -189.9314 | 1738.7579 | -2750 | -200 | -1211.2421 | 30.28% | 84.8% | 95% | 0% | 2585 | -166
[5 empty] | 2019-02-17 | 42 | 1149 | 2324 | -167 | 0 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 2442.4567 | 780 | 200 | 3422.4567 | 85.56% | 95% | 0% | -191.0755 | 1590.3754 | -2750 | -200 | -1359.6246 | 33.99% | 84.8% | 95% | 0% | 2491 | -167
[5 empty] | 2019-02-17 | 43 | 1149.5 | 2213 | -168 | 0 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 2442.4567 | 780 | 200 | 3422.4567 | 85.56% | 95% | 0% | -192.2197 | 1416.9312 | -2750 | -200 | -1533.0688 | 38.33% | 84.79% | 95% | 0% | 2381 | -168
[5 empty] | 2019-02-17 | 44 | 1150 | 2079 | -168 | 0 | 0 | 2247 | 1399.258 | 1399.258 | 1399.258 | 2442.4567 | 780 | 200 | 3422.4567 | 85.56% | 95% | 0% | -192.2197 | 1207.0384 | -2750 | -200 | -1742.9616 | 43.57% | 84.79% | 95% | 0% | 2247 | -168
[5 empty] | 2019-02-17 | 45 | 1150.5 | 1962 | -169 | 0 | 0 | 2131 | 1217.5598 | 1217.5598 | 1217.5598 | 2440.8904 | 780 | 200 | 3420.8904 | 85.52% | 95% | 0% | -193.3638 | 1024.1959 | -2750 | -200 | -1925.8041 | 48.15% | 84.79% | 95% | 0% | 2131 | -169
[5 empty] | 2019-02-17 | 46 | 1151 | 1865 | -169 | 0 | 0 | 2034 | 1065.6224 | 1065.6224 | 1065.6224 | 2440.8904 | 780 | 200 | 3420.8904 | 85.52% | 95% | 0% | -193.3638 | 872.2586 | -2750 | -200 | -2077.7414 | 51.94% | 84.78% | 95% | 0% | 2034 | -169
[5 empty] | 2019-02-17 | 47 | 1151.5 | 1718 | -171 | 0 | 0 | 1889 | 838.4996 | 838.4996 | 838.4996 | 2440.8904 | 780 | 200 | 3420.8904 | 85.52% | 95% | 0% | -195.6522 | 642.8474 | -2750 | -200 | -2307.1526 | 57.68% | 84.77% | 95% | 0% | 1889 | -171
[5 empty] | 2019-02-17 | 48 | 1152 | 1640 | -174 | 0 | 0 | 1814 | 721.0223 | 721.0223 | 721.0223 | 2440.8904 | 780 | 200 | 3420.8904 | 85.52% | 95% | 0% | -199.0847 | 521.9376 | -2750 | -200 | -2428.0624 | 60.7% | 84.77% | 95% | 0% | 1814 | -174
[5 empty] | 2019-02-18 | 1 | 1152.5 | 1630 | -174 | 0 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 2440.8904 | 780 | 200 | 3420.8904 | 85.52% | 95% | 0% | -199.0847 | 506.2739 | -2750 | -200 | -2443.7261 | 61.09% | 84.76% | 95% | 0% | 1804 | -174
[5 empty] | 2019-02-18 | 2 | 1153 | 1659 | -175 | 0 | 0 | 1834 | 752.3495 | 752.3495 | 752.3495 | 2440.8904 | 780 | 200 | 3420.8904 | 85.52% | 95% | 0% | -200.2288 | 552.1207 | -2750 | -200 | -2397.8793 | 59.95% | 84.76% | 95% | 0% | 1834 | -175
[5 empty] | 2019-02-18 | 3 | 1153.5 | 1650 | -175 | 0 | 0 | 1825 | 738.2523 | 738.2523 | 738.2523 | 2440.8904 | 780 | 200 | 3420.8904 | 85.52% | 95% | 0% | -200.2288 | 538.0234 | -2750 | -200 | -2411.9766 | 60.3% | 84.76% | 95% | 0% | 1825 | -175
[5 empty] | 2019-02-18 | 4 | 1154 | 1605 | -175 | 0 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 2440.8904 | 780 | 200 | 3420.8904 | 85.52% | 95% | 0% | -200.2288 | 467.537 | -2750 | -200 | -2482.463 | 62.06% | 84.76% | 95% | 0% | 1780 | -175
[5 empty] | 2019-02-18 | 5 | 1154.5 | 1569 | -174 | 0 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 2440.8904 | 780 | 200 | 3420.8904 | 85.52% | 95% | 0% | -199.0847 | 410.7257 | -2750 | -200 | -2539.2743 | 63.48% | 84.76% | 95% | 0% | 1743 | -174
[5 empty] | 2019-02-18 | 6 | 1155 | 1562 | -174 | 0 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 2439.324 | 780 | 200 | 3419.324 | 85.48% | 95% | 0% | -199.0847 | 399.7612 | -2750 | -200 | -2550.2388 | 63.76% | 84.74% | 95% | 0% | 1736 | -174
[5 empty] | 2019-02-18 | 7 | 1155.5 | 1528 | -171 | 0 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 2439.324 | 780 | 200 | 3419.324 | 85.48% | 95% | 0% | -195.6522 | 345.2382 | -2750 | -200 | -2604.7618 | 65.12% | 84.72% | 95% | 0% | 1699 | -171
[5 empty] | 2019-02-18 | 8 | 1156 | 1511 | -168 | 0 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 2439.324 | 780 | 200 | 3419.324 | 85.48% | 95% | 0% | -192.2197 | 317.3434 | -2750 | -200 | -2632.6566 | 65.82% | 84.71% | 95% | 0% | 1679 | -168
[5 empty] | 2019-02-18 | 9 | 1156.5 | 1505 | -168 | 0 | 0 | 1673 | 500.1649 | 500.1649 | 500.1649 | 2439.324 | 780 | 200 | 3419.324 | 85.48% | 95% | 0% | -192.2197 | 307.9452 | -2750 | -200 | -2642.0548 | 66.05% | 84.7% | 95% | 0% | 1673 | -168
[5 empty] | 2019-02-18 | 10 | 1157 | 1517 | -169 | 0 | 0 | 1686 | 520.5276 | 520.5276 | 520.5276 | 2437.7576 | 780 | 200 | 3417.7576 | 85.44% | 95% | 0% | -193.3638 | 327.1638 | -2750 | -200 | -2622.8362 | 65.57% | 84.69% | 95% | 0% | 1686 | -169
[5 empty] | 2019-02-18 | 11 | 1157.5 | 1589 | -166 | 0 | 0 | 1755 | 628.6068 | 628.6068 | 628.6068 | 2437.7576 | 780 | 200 | 3417.7576 | 85.44% | 95% | 0% | -189.9314 | 438.6754 | -2750 | -200 | -2511.3246 | 62.78% | 84.69% | 95% | 0% | 1755 | -166
[5 empty] | 2019-02-18 | 12 | 1158 | 1699 | -163 | 0 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 2437.7576 | 780 | 200 | 3417.7576 | 85.44% | 95% | 0% | -186.4989 | 609.7089 | -2750 | -200 | -2340.2911 | 58.51% | 84.69% | 95% | 0% | 1862 | -163
[5 empty] | 2019-02-18 | 13 | 1158.5 | 1950 | -163 | 0 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 2437.7576 | 780 | 200 | 3417.7576 | 85.44% | 95% | 0% | -186.4989 | 1002.8664 | -2750 | -200 | -1947.1336 | 48.68% | 84.68% | 95% | 0% | 2113 | -163
[5 empty] | 2019-02-18 | 14 | 1159 | 2163 | -163 | 0 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 2437.7576 | 780 | 200 | 3417.7576 | 85.44% | 95% | 0% | -186.4989 | 1336.502 | -2750 | -200 | -1613.498 | 40.34% | 84.68% | 95% | 0% | 2326 | -163
[5 empty] | 2019-02-18 | 15 | 1159.5 | 2367 | -164 | 0 | 0 | 2531 | 1844.1055 | 1844.1055 | 1844.1055 | 2437.7576 | 780 | 200 | 3417.7576 | 85.44% | 95% | 0% | -187.643 | 1656.4625 | -2750 | -200 | -1293.5375 | 32.34% | 84.68% | 95% | 0% | 2531 | -164
[5 empty] | 2019-02-18 | 16 | 1160 | 2469 | -170 | 0 | 0 | 2639 | 2013.2729 | 2013.2729 | 2013.2729 | 2436.1913 | 780 | 200 | 3416.1913 | 85.4% | 95% | 0% | -194.508 | 1818.7649 | -2750 | -200 | -1131.2351 | 28.28% | 84.67% | 95% | 0% | 2639 | -170
[5 empty] | 2019-02-18 | 17 | 1160.5 | 2565 | -194 | 0 | 0 | 2759 | 2201.2366 | 2201.2366 | 2201.2366 | 2436.1913 | 780 | 200 | 3416.1913 | 85.4% | 95% | 0% | -221.968 | 1979.2686 | -2750 | -200 | -970.7314 | 24.27% | 84.66% | 95% | 0% | 2759 | -194
[5 empty] | 2019-02-18 | 18 | 1161 | 2610 | -225 | 0 | 0 | 2835 | 2320.2803 | 2320.2803 | 2320.2803 | 2436.1913 | 780 | 200 | 3416.1913 | 85.4% | 95% | 0% | -257.4371 | 2062.8432 | -2750 | -200 | -887.1568 | 22.18% | 84.66% | 95% | 0% | 2835 | -225
[5 empty] | 2019-02-18 | 19 | 1161.5 | 2623 | -253 | 1 | 0 | 2876 | 2384.5012 | 2384.5012 | 2384.5012 | 2436.1913 | 780 | 200 | 3416.1913 | 85.4% | 95% | 0% | -289.4737 | 2095.0276 | -3550 | -400 | -1854.9724 | 46.37% | 84.65% | 95% | 0% | 2876 | -253
[5 empty] | 2019-02-18 | 20 | 1162 | 2591 | -285 | 1 | 0 | 2876 | 2384.5012 | 2384.5012 | 2384.5012 | 2436.1913 | 780 | 200 | 3416.1913 | 85.4% | 95% | 0% | -326.087 | 2058.4143 | -3550 | -400 | -1891.5857 | 47.29% | 84.65% | 95% | 0% | 2876 | -285
[5 empty] | 2019-02-18 | 21 | 1162.5 | 2533 | -315 | 1 | 0 | 2848 | 2340.643 | 2340.643 | 2340.643 | 2436.1913 | 780 | 200 | 3416.1913 | 85.4% | 95% | 0% | -360.4119 | 1980.2311 | -3550 | -400 | -1969.7689 | 49.24% | 84.64% | 95% | 0% | 2848 | -315
[5 empty] | 2019-02-18 | 22 | 1163 | 2446 | -375 | 1 | 0 | 2821 | 2298.3512 | 2298.3512 | 2298.3512 | 2436.1913 | 780 | 200 | 3416.1913 | 85.4% | 95% | 0% | -429.0618 | 1869.2894 | -3550 | -400 | -2080.7106 | 52.02% | 84.64% | 95% | 0% | 2821 | -375
[5 empty] | 2019-02-18 | 23 | 1163.5 | 2446 | -373 | 1 | 0 | 2819 | 2295.2185 | 2295.2185 | 2295.2185 | 2436.1913 | 780 | 200 | 3416.1913 | 85.4% | 95% | 0% | -426.7735 | 1868.445 | -3550 | -400 | -2081.555 | 52.04% | 84.63% | 95% | 0% | 2819 | -373
[5 empty] | 2019-02-18 | 24 | 1164 | 2475 | -360 | 1 | 0 | 2835 | 2320.2803 | 2320.2803 | 2320.2803 | 2434.6249 | 780 | 200 | 3414.6249 | 85.37% | 95% | 0% | -411.8993 | 1908.381 | -3550 | -400 | -2041.619 | 51.04% | 84.62% | 95% | 0% | 2835 | -360
[5 empty] | 2019-02-18 | 25 | 1164.5 | 2499 | -367 | 1 | 0 | 2866 | 2368.8376 | 2368.8376 | 2368.8376 | 2434.6249 | 780 | 200 | 3414.6249 | 85.37% | 95% | 0% | -419.9085 | 1948.9291 | -3550 | -400 | -2001.0709 | 50.03% | 84.62% | 95% | 0% | 2866 | -367
[5 empty] | 2019-02-18 | 26 | 1165 | 2464 | -390 | 1 | 0 | 2854 | 2350.0412 | 2350.0412 | 2350.0412 | 2434.6249 | 780 | 200 | 3414.6249 | 85.37% | 95% | 0% | -446.2243 | 1903.817 | -3550 | -400 | -2046.183 | 51.15% | 84.61% | 95% | 0% | 2854 | -390
[5 empty] | 2019-02-18 | 27 | 1165.5 | 2447 | -394 | 1 | 0 | 2841 | 2329.6785 | 2329.6785 | 2329.6785 | 2433.0585 | 780 | 200 | 3413.0585 | 85.33% | 95% | 0% | -450.8009 | 1878.8776 | -3550 | -400 | -2071.1224 | 51.78% | 84.61% | 95% | 0% | 2841 | -394
[5 empty] | 2019-02-18 | 28 | 1166 | 2414 | -384 | 1 | 0 | 2798 | 2262.3248 | 2262.3248 | 2262.3248 | 2433.0585 | 780 | 200 | 3413.0585 | 85.33% | 95% | 0% | -439.3593 | 1822.9655 | -3550 | -400 | -2127.0345 | 53.18% | 84.61% | 95% | 0% | 2798 | -384
[5 empty] | 2019-02-18 | 29 | 1166.5 | 2411 | -382 | 1 | 0 | 2793 | 2254.493 | 2254.493 | 2254.493 | 2433.0585 | 780 | 200 | 3413.0585 | 85.33% | 95% | 0% | -437.0709 | 1817.4221 | -3550 | -400 | -2132.5779 | 53.31% | 84.6% | 95% | 0% | 2793 | -382
[5 empty] | 2019-02-18 | 30 | 1167 | 2441 | -353 | 1 | 0 | 2794 | 2256.0594 | 2256.0594 | 2256.0594 | 2433.0585 | 780 | 200 | 3413.0585 | 85.33% | 95% | 0% | -403.8902 | 1852.1692 | -3550 | -400 | -2097.8308 | 52.45% | 84.6% | 95% | 0% | 2794 | -353
[5 empty] | 2019-02-18 | 31 | 1167.5 | 2503 | -312 | 1 | 0 | 2815 | 2288.953 | 2288.953 | 2288.953 | 2433.0585 | 780 | 200 | 3413.0585 | 85.33% | 95% | 0% | -356.9794 | 1931.9736 | -3550 | -400 | -2018.0264 | 50.45% | 84.6% | 95% | 0% | 2815 | -312
[5 empty] | 2019-02-18 | 32 | 1168 | 2570 | -284 | 1 | 0 | 2854 | 2350.0412 | 2350.0412 | 2350.0412 | 2433.0585 | 780 | 200 | 3413.0585 | 85.33% | 95% | 0% | -324.9428 | 2025.0984 | -3550 | -400 | -1924.9016 | 48.12% | 84.59% | 95% | 0% | 2854 | -284
[5 empty] | 2019-02-18 | 33 | 1168.5 | 2672 | -239 | 1 | 0 | 2911 | 2439.324 | 2439.324 | 2439.324 | 2433.0585 | 780 | 200 | 3413.0585 | 85.33% | 95% | 0% | -273.4554 | 2165.8686 | -3550 | -400 | -1784.1314 | 44.6% | 84.59% | 95% | 0% | 2911 | -239
[5 empty] | 2019-02-18 | 34 | 1169 | 2790 | -199 | 1 | 0 | 2989 | 2561.5004 | 2561.5004 | 2561.5004 | 2433.0585 | 780 | 200 | 3413.0585 | 85.33% | 95% | 0% | -227.6888 | 2333.8116 | -3550 | -400 | -1616.1884 | 40.4% | 84.59% | 95% | 0% | 2989 | -199
[5 empty] | 2019-02-18 | 35 | 1169.5 | 2950 | -171 | 1 | 0 | 3121 | 2768.2605 | 2768.2605 | 2768.2605 | 2433.0585 | 780 | 200 | 3413.0585 | 85.33% | 95% | 0% | -195.6522 | 2572.6083 | -3550 | -400 | -1377.3917 | 34.43% | 84.58% | 95% | 0% | 3121 | -171
[5 empty] | 2019-02-18 | 36 | 1170 | 3073 | -163 | 1 | 0 | 3236 | 2948.3924 | 2948.3924 | 2948.3924 | 2431.4922 | 780 | 200 | 3411.4922 | 85.29% | 95% | 0% | -186.4989 | 2761.8936 | -3550 | -400 | -1188.1064 | 29.7% | 84.58% | 95% | 0% | 3236 | -163
[5 empty] | 2019-02-18 | 37 | 1170.5 | 3127 | -162 | 1 | 0 | 3289 | 3031.4097 | 3031.4097 | 3031.4097 | 2431.4922 | 780 | 200 | 3411.4922 | 85.29% | 95% | 0% | -185.3547 | 2846.055 | -3550 | -400 | -1103.945 | 27.6% | 84.57% | 95% | 0% | 3289 | -162
[5 empty] | 2019-02-18 | 38 | 1171 | 3094 | -161 | 0 | 0 | 3255 | 2978.1533 | 2978.1533 | 2978.1533 | 2431.4922 | 780 | 200 | 3411.4922 | 85.29% | 95% | 0% | -184.2105 | 2793.9428 | -2750 | -200 | -156.0572 | 3.901% | 84.57% | 95% | 0% | 3255 | -161
[5 empty] | 2019-02-18 | 39 | 1171.5 | 3012 | -160 | 0 | 0 | 3172 | 2848.1451 | 2848.1451 | 2848.1451 | 2431.4922 | 780 | 200 | 3411.4922 | 85.29% | 95% | 0% | -183.0664 | 2665.0787 | -2750 | -200 | -284.9213 | 7.123% | 84.56% | 95% | 0% | 3172 | -160
[5 empty] | 2019-02-18 | 40 | 1172 | 2912 | -159 | 0 | 0 | 3071 | 2689.9423 | 2689.9423 | 2689.9423 | 2429.9258 | 780 | 200 | 3409.9258 | 85.25% | 95% | 0% | -181.9222 | 2508.0201 | -2750 | -200 | -441.9799 | 11.05% | 84.55% | 95% | 0% | 3071 | -159
[5 empty] | 2019-02-18 | 41 | 1172.5 | 2823 | -157 | 0 | 0 | 2980 | 2547.4031 | 2547.4031 | 2547.4031 | 2429.9258 | 780 | 200 | 3409.9258 | 85.25% | 95% | 0% | -179.6339 | 2367.7693 | -2750 | -200 | -582.2307 | 14.56% | 84.55% | 95% | 0% | 2980 | -157
[5 empty] | 2019-02-18 | 42 | 1173 | 2716 | -155 | 0 | 0 | 2871 | 2376.6694 | 2376.6694 | 2376.6694 | 2429.9258 | 780 | 200 | 3409.9258 | 85.25% | 95% | 0% | -177.3455 | 2199.3239 | -2750 | -200 | -750.6761 | 18.77% | 84.54% | 95% | 0% | 2871 | -155
[5 empty] | 2019-02-18 | 43 | 1173.5 | 2586 | -154 | 0 | 0 | 2740 | 2171.4757 | 2171.4757 | 2171.4757 | 2428.3594 | 780 | 200 | 3408.3594 | 85.21% | 95% | 0% | -176.2014 | 1995.2743 | -2750 | -200 | -954.7257 | 23.87% | 84.54% | 95% | 0% | 2740 | -154
[5 empty] | 2019-02-18 | 44 | 1174 | 2441 | -153 | 0 | 0 | 2594 | 1942.7865 | 1942.7865 | 1942.7865 | 2428.3594 | 780 | 200 | 3408.3594 | 85.21% | 95% | 0% | -175.0572 | 1767.7293 | -2750 | -200 | -1182.2707 | 29.56% | 84.54% | 95% | 0% | 2594 | -153
[5 empty] | 2019-02-18 | 45 | 1174.5 | 2274 | -152 | 0 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 2428.3594 | 780 | 200 | 3408.3594 | 85.21% | 95% | 0% | -173.913 | 1505.7242 | -2750 | -200 | -1444.2758 | 36.11% | 84.54% | 95% | 0% | 2426 | -152
[5 empty] | 2019-02-18 | 46 | 1175 | 2129 | -150 | 0 | 0 | 2279 | 1449.3817 | 1449.3817 | 1449.3817 | 2428.3594 | 780 | 200 | 3408.3594 | 85.21% | 95% | 0% | -171.6247 | 1277.757 | -2750 | -200 | -1672.243 | 41.81% | 84.51% | 95% | 0% | 2279 | -150
[5 empty] | 2019-02-18 | 47 | 1175.5 | 1966 | -149 | 0 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 2426.7931 | 780 | 200 | 3406.7931 | 85.17% | 95% | 0% | -170.4805 | 1022.0174 | -2750 | -200 | -1927.9826 | 48.2% | 84.49% | 95% | 0% | 2115 | -149
[5 empty] | 2019-02-18 | 48 | 1176 | 1873 | -147 | 0 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 2426.7931 | 780 | 200 | 3406.7931 | 85.17% | 95% | 0% | -168.1922 | 875.5011 | -2750 | -200 | -2074.4989 | 51.86% | 84.48% | 95% | 0% | 2020 | -147
[5 empty] | 2019-02-19 | 1 | 1176.5 | 1866 | -146 | 0 | 0 | 2012 | 1031.1624 | 1031.1624 | 1031.1624 | 2426.7931 | 780 | 200 | 3406.7931 | 85.17% | 95% | 0% | -167.0481 | 864.1144 | -2750 | -200 | -2085.8856 | 52.15% | 84.48% | 95% | 0% | 2012 | -146
[5 empty] | 2019-02-19 | 2 | 1177 | 1896 | -145 | 0 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 2426.7931 | 780 | 200 | 3406.7931 | 85.17% | 95% | 0% | -165.9039 | 910.6831 | -2750 | -200 | -2039.3169 | 50.98% | 84.48% | 95% | 0% | 2041 | -145
[5 empty] | 2019-02-19 | 3 | 1177.5 | 1878 | -142 | 1 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 2426.7931 | 780 | 200 | 3406.7931 | 85.17% | 95% | 0% | -162.4714 | 881.2219 | -3550 | -400 | -3068.7781 | 76.72% | 84.47% | 95% | 0% | 2020 | -142
[5 empty] | 2019-02-19 | 4 | 1178 | 1844 | -140 | 1 | 0 | 1984 | 987.3042 | 987.3042 | 987.3042 | 2426.7931 | 780 | 200 | 3406.7931 | 85.17% | 95% | 0% | -160.1831 | 827.1211 | -3550 | -400 | -3122.8789 | 78.07% | 84.47% | 95% | 0% | 1984 | -140
[5 empty] | 2019-02-19 | 5 | 1178.5 | 1813 | -139 | 1 | 0 | 1952 | 937.1805 | 937.1805 | 937.1805 | 2426.7931 | 780 | 200 | 3406.7931 | 85.17% | 95% | 0% | -159.0389 | 778.1416 | -3550 | -400 | -3171.8584 | 79.3% | 84.47% | 95% | 0% | 1952 | -139
[5 empty] | 2019-02-19 | 6 | 1179 | 1786 | -137 | 1 | 0 | 1923 | 891.756 | 891.756 | 891.756 | 2426.7931 | 780 | 200 | 3406.7931 | 85.17% | 95% | 0% | -156.7506 | 735.0054 | -3550 | -400 | -3214.9946 | 80.37% | 84.47% | 95% | 0% | 1923 | -137
[5 empty] | 2019-02-19 | 7 | 1179.5 | 1769 | -134 | 1 | 0 | 1903 | 860.4287 | 860.4287 | 860.4287 | 2426.7931 | 780 | 200 | 3406.7931 | 85.17% | 95% | 0% | -153.3181 | 707.1106 | -3550 | -400 | -3242.8894 | 81.07% | 84.46% | 95% | 0% | 1903 | -134
[5 empty] | 2019-02-19 | 8 | 1180 | 1736 | -131 | 1 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 2425.2267 | 780 | 200 | 3405.2267 | 85.13% | 95% | 0% | -149.8856 | 654.154 | -3550 | -400 | -3295.846 | 82.4% | 84.45% | 95% | 0% | 1867 | -131
[5 empty] | 2019-02-19 | 9 | 1180.5 | 1738 | -128 | 1 | 0 | 1866 | 802.4732 | 802.4732 | 802.4732 | 2425.2267 | 780 | 200 | 3405.2267 | 85.13% | 95% | 0% | -146.4531 | 656.0201 | -3550 | -400 | -3293.9799 | 82.35% | 84.45% | 95% | 0% | 1866 | -128
[5 empty] | 2019-02-19 | 10 | 1181 | 1760 | -126 | 1 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 2425.2267 | 780 | 200 | 3405.2267 | 85.13% | 95% | 0% | -144.1648 | 689.6357 | -3550 | -400 | -3260.3643 | 81.51% | 84.44% | 95% | 0% | 1886 | -126
[5 empty] | 2019-02-19 | 11 | 1181.5 | 1827 | -122 | 1 | 0 | 1949 | 932.4815 | 932.4815 | 932.4815 | 2425.2267 | 780 | 200 | 3405.2267 | 85.13% | 95% | 0% | -139.5881 | 792.8934 | -3550 | -400 | -3157.1066 | 78.93% | 84.43% | 95% | 0% | 1949 | -122
[5 empty] | 2019-02-19 | 12 | 1182 | 1935 | -117 | 1 | 0 | 2052 | 1093.817 | 1093.817 | 1093.817 | 2425.2267 | 780 | 200 | 3405.2267 | 85.13% | 95% | 0% | -133.8673 | 959.9497 | -3550 | -400 | -2990.0503 | 74.75% | 84.42% | 95% | 0% | 2052 | -117
[5 empty] | 2019-02-19 | 13 | 1182.5 | 2172 | -114 | 1 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 2423.6603 | 780 | 200 | 3403.6603 | 85.09% | 95% | 0% | -130.4348 | 1329.9115 | -3550 | -400 | -2620.0885 | 65.5% | 84.42% | 95% | 0% | 2286 | -114
[5 empty] | 2019-02-19 | 14 | 1183 | 2397 | -110 | 1 | 0 | 2507 | 1806.5128 | 1806.5128 | 1806.5128 | 2423.6603 | 780 | 200 | 3403.6603 | 85.09% | 95% | 0% | -125.8581 | 1680.6547 | -3550 | -400 | -2269.3453 | 56.73% | 84.4% | 95% | 0% | 2507 | -110
[5 empty] | 2019-02-19 | 15 | 1183.5 | 2607 | -108 | 1 | 0 | 2715 | 2132.3166 | 2132.3166 | 2132.3166 | 2423.6603 | 780 | 200 | 3403.6603 | 85.09% | 95% | 0% | -123.5698 | 2008.7468 | -3550 | -400 | -1941.2532 | 48.53% | 84.4% | 95% | 0% | 2715 | -108
[5 empty] | 2019-02-19 | 16 | 1184 | 2687 | -131 | 1 | 0 | 2818 | 2293.6521 | 2293.6521 | 2293.6521 | 2423.6603 | 780 | 200 | 3403.6603 | 85.09% | 95% | 0% | -149.8856 | 2143.7665 | -3550 | -400 | -1806.2335 | 45.16% | 84.39% | 95% | 0% | 2818 | -131
[5 empty] | 2019-02-19 | 17 | 1184.5 | 2695 | -187 | 1 | 0 | 2882 | 2393.8994 | 2393.8994 | 2393.8994 | 2423.6603 | 780 | 200 | 3403.6603 | 85.09% | 95% | 0% | -213.9588 | 2179.9406 | -3550 | -400 | -1770.0594 | 44.25% | 84.38% | 95% | 0% | 2882 | -187
[5 empty] | 2019-02-19 | 18 | 1185 | 2640 | -254 | 1 | 0 | 2894 | 2412.6958 | 2412.6958 | 2412.6958 | 2423.6603 | 780 | 200 | 3403.6603 | 85.09% | 95% | 0% | -290.6178 | 2122.0779 | -3550 | -400 | -1827.9221 | 45.7% | 84.37% | 95% | 0% | 2894 | -254
[5 empty] | 2019-02-19 | 19 | 1185.5 | 2583 | -300 | 1 | 0 | 2883 | 2395.4658 | 2395.4658 | 2395.4658 | 2422.094 | 780 | 200 | 3402.094 | 85.05% | 95% | 0% | -343.2494 | 2052.2164 | -3550 | -400 | -1897.7836 | 47.44% | 84.36% | 95% | 0% | 2883 | -300
[5 empty] | 2019-02-19 | 20 | 1186 | 2460 | -364 | 1 | 0 | 2824 | 2303.0503 | 2303.0503 | 2303.0503 | 2422.094 | 780 | 200 | 3402.094 | 85.05% | 95% | 0% | -416.476 | 1886.5743 | -3550 | -400 | -2063.4257 | 51.59% | 84.36% | 95% | 0% | 2824 | -364
[5 empty] | 2019-02-19 | 21 | 1186.5 | 2362 | -401 | 1 | 0 | 2763 | 2207.5021 | 2207.5021 | 2207.5021 | 2422.094 | 780 | 200 | 3402.094 | 85.05% | 95% | 0% | -458.8101 | 1748.692 | -3550 | -400 | -2201.308 | 55.03% | 84.36% | 95% | 0% | 2763 | -401
[5 empty] | 2019-02-19 | 22 | 1187 | 2229 | -484 | 1 | 0 | 2713 | 2129.1838 | 2129.1838 | 2129.1838 | 2422.094 | 780 | 200 | 3402.094 | 85.05% | 95% | 0% | -553.7757 | 1575.4081 | -3550 | -400 | -2374.5919 | 59.36% | 84.36% | 95% | 0% | 2713 | -484
[5 empty] | 2019-02-19 | 23 | 1187.5 | 2191 | -496 | 1 | 0 | 2687 | 2088.4584 | 2088.4584 | 2088.4584 | 2420.5276 | 780 | 200 | 3400.5276 | 85.01% | 95% | 0% | -567.5057 | 1520.9526 | -3550 | -400 | -2429.0474 | 60.73% | 84.35% | 95% | 0% | 2687 | -496
[5 empty] | 2019-02-19 | 24 | 1188 | 2215 | -482 | 1 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 2418.9613 | 780 | 200 | 3398.9613 | 84.97% | 95% | 0% | -551.4874 | 1552.6346 | -3550 | -400 | -2397.3654 | 59.93% | 84.35% | 95% | 0% | 2697 | -482
[5 empty] | 2019-02-19 | 25 | 1188.5 | 2279 | -451 | 1 | 0 | 2730 | 2155.812 | 2155.812 | 2155.812 | 2418.9613 | 780 | 200 | 3398.9613 | 84.97% | 95% | 0% | -516.0183 | 1639.7937 | -3550 | -400 | -2310.2063 | 57.76% | 84.34% | 95% | 0% | 2730 | -451
[5 empty] | 2019-02-19 | 26 | 1189 | 2336 | -399 | 1 | 0 | 2735 | 2163.6439 | 2163.6439 | 2163.6439 | 2418.9613 | 780 | 200 | 3398.9613 | 84.97% | 95% | 0% | -456.5217 | 1707.1221 | -3550 | -400 | -2242.8779 | 56.07% | 84.34% | 95% | 0% | 2735 | -399
[5 empty] | 2019-02-19 | 27 | 1189.5 | 2350 | -390 | 1 | 0 | 2740 | 2171.4757 | 2171.4757 | 2171.4757 | 2418.9613 | 780 | 200 | 3398.9613 | 84.97% | 95% | 0% | -446.2243 | 1725.2514 | -3550 | -400 | -2224.7486 | 55.62% | 84.33% | 95% | 0% | 2740 | -390
[5 empty] | 2019-02-19 | 28 | 1190 | 2399 | -361 | 1 | 0 | 2760 | 2202.803 | 2202.803 | 2202.803 | 2417.3949 | 780 | 200 | 3397.3949 | 84.93% | 95% | 0% | -413.0435 | 1789.7595 | -3550 | -400 | -2160.2405 | 54.01% | 84.33% | 95% | 0% | 2760 | -361
[5 empty] | 2019-02-19 | 29 | 1190.5 | 2446 | -344 | 1 | 0 | 2790 | 2249.7939 | 2249.7939 | 2249.7939 | 2417.3949 | 780 | 200 | 3397.3949 | 84.93% | 95% | 0% | -393.5927 | 1856.2012 | -3550 | -400 | -2093.7988 | 52.34% | 84.33% | 95% | 0% | 2790 | -344
[5 empty] | 2019-02-19 | 30 | 1191 | 2536 | -285 | 1 | 0 | 2821 | 2298.3512 | 2298.3512 | 2298.3512 | 2417.3949 | 780 | 200 | 3397.3949 | 84.93% | 95% | 0% | -326.087 | 1972.2642 | -3550 | -400 | -1977.7358 | 49.44% | 84.32% | 95% | 0% | 2821 | -285
[5 empty] | 2019-02-19 | 31 | 1191.5 | 2652 | -227 | 1 | 0 | 2879 | 2389.2003 | 2389.2003 | 2389.2003 | 2417.3949 | 780 | 200 | 3397.3949 | 84.93% | 95% | 0% | -259.7254 | 2129.4749 | -3550 | -400 | -1820.5251 | 45.51% | 84.32% | 95% | 0% | 2879 | -227
[5 empty] | 2019-02-19 | 32 | 1192 | 2763 | -176 | 1 | 0 | 2939 | 2483.1822 | 2483.1822 | 2483.1822 | 2417.3949 | 780 | 200 | 3397.3949 | 84.93% | 95% | 0% | -201.373 | 2281.8092 | -3550 | -400 | -1668.1908 | 41.7% | 84.31% | 95% | 0% | 2939 | -176
[5 empty] | 2019-02-19 | 33 | 1192.5 | 2877 | -142 | 1 | 0 | 3019 | 2608.4913 | 2608.4913 | 2608.4913 | 2417.3949 | 780 | 200 | 3397.3949 | 84.93% | 95% | 0% | -162.4714 | 2446.0199 | -3550 | -400 | -1503.9801 | 37.6% | 84.31% | 95% | 0% | 3019 | -142
[5 empty] | 2019-02-19 | 34 | 1193 | 2973 | -118 | 1 | 0 | 3091 | 2721.2696 | 2721.2696 | 2721.2696 | 2417.3949 | 780 | 200 | 3397.3949 | 84.93% | 95% | 0% | -135.0114 | 2586.2581 | -3550 | -400 | -1363.7419 | 34.09% | 84.29% | 95% | 0% | 3091 | -118
[5 empty] | 2019-02-19 | 35 | 1193.5 | 3094 | -111 | 1 | 0 | 3205 | 2899.8351 | 2899.8351 | 2899.8351 | 2417.3949 | 780 | 200 | 3397.3949 | 84.93% | 95% | 0% | -127.0023 | 2772.8328 | -3550 | -400 | -1177.1672 | 29.43% | 84.29% | 95% | 0% | 3205 | -111
[5 empty] | 2019-02-19 | 36 | 1194 | 3185 | -113 | 1 | 0 | 3298 | 3045.507 | 3045.507 | 3045.507 | 2415.8285 | 780 | 200 | 3395.8285 | 84.9% | 95% | 0% | -129.2906 | 2916.2164 | -3550 | -400 | -1033.7836 | 25.84% | 84.29% | 95% | 0% | 3298 | -113
[5 empty] | 2019-02-19 | 37 | 1194.5 | 3204 | -118 | 0 | 0 | 3322 | 3083.0998 | 3083.0998 | 3083.0998 | 2415.8285 | 780 | 200 | 3395.8285 | 84.9% | 95% | 0% | -135.0114 | 2948.0883 | -2750 | -200 | -1.9117 | 0.04779% | 84.28% | 95% | 0% | 3322 | -118
[5 empty] | 2019-02-19 | 38 | 1195 | 3189 | -124 | 0 | 0 | 3313 | 3069.0025 | 3069.0025 | 3069.0025 | 2415.8285 | 780 | 200 | 3395.8285 | 84.9% | 95% | 0% | -141.8764 | 2927.126 | -2750 | -200 | -22.874 | 0.5718% | 84.27% | 95% | 0% | 3313 | -124
[5 empty] | 2019-02-19 | 39 | 1195.5 | 3155 | -129 | 0 | 0 | 3284 | 3023.5779 | 3023.5779 | 3023.5779 | 2415.8285 | 780 | 200 | 3395.8285 | 84.9% | 95% | 0% | -147.5973 | 2875.9807 | -2750 | -200 | -74.0193 | 1.85% | 84.27% | 95% | 0% | 3284 | -129
[5 empty] | 2019-02-19 | 40 | 1196 | 3039 | -135 | 0 | 0 | 3174 | 2851.2778 | 2851.2778 | 2851.2778 | 2415.8285 | 780 | 200 | 3395.8285 | 84.9% | 95% | 0% | -154.4622 | 2696.8156 | -2750 | -200 | -253.1844 | 6.33% | 84.26% | 95% | 0% | 3174 | -135
[5 empty] | 2019-02-19 | 41 | 1196.5 | 2919 | -139 | 0 | 0 | 3058 | 2669.5796 | 2669.5796 | 2669.5796 | 2414.2622 | 780 | 200 | 3394.2622 | 84.86% | 95% | 0% | -159.0389 | 2510.5407 | -2750 | -200 | -439.4593 | 10.99% | 84.26% | 95% | 0% | 3058 | -139
[5 empty] | 2019-02-19 | 42 | 1197 | 2769 | -144 | 0 | 0 | 2913 | 2442.4567 | 2442.4567 | 2442.4567 | 2414.2622 | 780 | 200 | 3394.2622 | 84.86% | 95% | 0% | -164.7597 | 2277.697 | -2750 | -200 | -672.303 | 16.81% | 84.24% | 95% | 0% | 2913 | -144
[5 empty] | 2019-02-19 | 43 | 1197.5 | 2613 | -147 | 0 | 0 | 2760 | 2202.803 | 2202.803 | 2202.803 | 2414.2622 | 780 | 200 | 3394.2622 | 84.86% | 95% | 0% | -168.1922 | 2034.6107 | -2750 | -200 | -915.3893 | 22.88% | 84.24% | 95% | 0% | 2760 | -147
[5 empty] | 2019-02-19 | 44 | 1198 | 2432 | -151 | 0 | 0 | 2583 | 1925.5565 | 1925.5565 | 1925.5565 | 2414.2622 | 780 | 200 | 3394.2622 | 84.86% | 95% | 0% | -172.7689 | 1752.7876 | -2750 | -200 | -1197.2124 | 29.93% | 84.24% | 95% | 0% | 2583 | -151
[5 empty] | 2019-02-19 | 45 | 1198.5 | 2258 | -156 | 0 | 0 | 2414 | 1660.8409 | 1660.8409 | 1660.8409 | 2414.2622 | 780 | 200 | 3394.2622 | 84.86% | 95% | 0% | -178.4897 | 1482.3512 | -2750 | -200 | -1467.6488 | 36.69% | 84.23% | 95% | 0% | 2414 | -156
[5 empty] | 2019-02-19 | 46 | 1199 | 2106 | -160 | 0 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 2414.2622 | 780 | 200 | 3394.2622 | 84.86% | 95% | 0% | -183.0664 | 1245.9526 | -2750 | -200 | -1704.0474 | 42.6% | 84.22% | 95% | 0% | 2266 | -160
[5 empty] | 2019-02-19 | 47 | 1199.5 | 1951 | -161 | 0 | 0 | 2112 | 1187.7988 | 1187.7988 | 1187.7988 | 2412.6958 | 780 | 200 | 3392.6958 | 84.82% | 95% | 0% | -184.2105 | 1003.5883 | -2750 | -200 | -1946.4117 | 48.66% | 84.21% | 95% | 0% | 2112 | -161
[5 empty] | 2019-02-19 | 48 | 1200 | 1859 | -162 | 0 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 2412.6958 | 780 | 200 | 3392.6958 | 84.82% | 95% | 0% | -185.3547 | 859.905 | -2750 | -200 | -2090.095 | 52.25% | 84.21% | 95% | 0% | 2021 | -162
[5 empty] | 2019-02-20 | 1 | 1200.5 | 1824 | -164 | 0 | 0 | 1988 | 993.5697 | 993.5697 | 993.5697 | 2412.6958 | 780 | 200 | 3392.6958 | 84.82% | 95% | 0% | -187.643 | 805.9266 | -2750 | -200 | -2144.0734 | 53.6% | 84.2% | 95% | 0% | 1988 | -164
[5 empty] | 2019-02-20 | 2 | 1201 | 1837 | -165 | 1 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 2412.6958 | 780 | 200 | 3392.6958 | 84.82% | 95% | 0% | -188.7872 | 826.7116 | -3550 | -400 | -3123.2884 | 78.08% | 84.2% | 95% | 0% | 2002 | -165
[5 empty] | 2019-02-20 | 3 | 1201.5 | 1800 | -166 | 1 | 0 | 1966 | 959.1096 | 959.1096 | 959.1096 | 2412.6958 | 780 | 200 | 3392.6958 | 84.82% | 95% | 0% | -189.9314 | 769.1783 | -3550 | -400 | -3180.8217 | 79.52% | 84.18% | 95% | 0% | 1966 | -166
[5 empty] | 2019-02-20 | 4 | 1202 | 1749 | -167 | 1 | 0 | 1916 | 880.7914 | 880.7914 | 880.7914 | 2412.6958 | 780 | 200 | 3392.6958 | 84.82% | 95% | 0% | -191.0755 | 689.7159 | -3550 | -400 | -3260.2841 | 81.51% | 84.18% | 95% | 0% | 1916 | -167
[5 empty] | 2019-02-20 | 5 | 1202.5 | 1696 | -168 | 1 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 2411.1294 | 780 | 200 | 3391.1294 | 84.78% | 95% | 0% | -192.2197 | 607.1208 | -3550 | -400 | -3342.8792 | 83.57% | 84.15% | 95% | 0% | 1864 | -168
[5 empty] | 2019-02-20 | 6 | 1203 | 1673 | -168 | 1 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 2411.1294 | 780 | 200 | 3391.1294 | 84.78% | 95% | 0% | -192.2197 | 571.0944 | -3550 | -400 | -3378.9056 | 84.47% | 84.14% | 95% | 0% | 1841 | -168
[5 empty] | 2019-02-20 | 7 | 1203.5 | 1637 | -168 | 1 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 2411.1294 | 780 | 200 | 3391.1294 | 84.78% | 95% | 0% | -192.2197 | 514.7053 | -3550 | -400 | -3435.2947 | 85.88% | 84.14% | 95% | 0% | 1805 | -168
[5 empty] | 2019-02-20 | 8 | 1204 | 1601 | -169 | 1 | 0 | 1770 | 652.1022 | 652.1022 | 652.1022 | 2411.1294 | 780 | 200 | 3391.1294 | 84.78% | 95% | 0% | -193.3638 | 458.7384 | -3550 | -400 | -3491.2616 | 87.28% | 84.13% | 95% | 0% | 1770 | -169
[5 empty] | 2019-02-20 | 9 | 1204.5 | 1585 | -170 | 1 | 0 | 1755 | 628.6068 | 628.6068 | 628.6068 | 2411.1294 | 780 | 200 | 3391.1294 | 84.78% | 95% | 0% | -194.508 | 434.0988 | -3550 | -400 | -3515.9012 | 87.9% | 84.13% | 95% | 0% | 1755 | -170
[5 empty] | 2019-02-20 | 10 | 1205 | 1593 | -171 | 1 | 0 | 1764 | 642.704 | 642.704 | 642.704 | 2411.1294 | 780 | 200 | 3391.1294 | 84.78% | 95% | 0% | -195.6522 | 447.0519 | -3550 | -400 | -3502.9481 | 87.57% | 84.12% | 95% | 0% | 1764 | -171
[5 empty] | 2019-02-20 | 11 | 1205.5 | 1656 | -171 | 1 | 0 | 1827 | 741.385 | 741.385 | 741.385 | 2411.1294 | 780 | 200 | 3391.1294 | 84.78% | 95% | 0% | -195.6522 | 545.7328 | -3550 | -400 | -3404.2672 | 85.11% | 84.12% | 95% | 0% | 1827 | -171
[5 empty] | 2019-02-20 | 12 | 1206 | 1757 | -172 | 1 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 2409.5631 | 780 | 200 | 3389.5631 | 84.74% | 95% | 0% | -196.7963 | 704.3578 | -3550 | -400 | -3245.6422 | 81.14% | 84.11% | 95% | 0% | 1929 | -172
[5 empty] | 2019-02-20 | 13 | 1206.5 | 1990 | -171 | 1 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 2409.5631 | 780 | 200 | 3389.5631 | 84.74% | 95% | 0% | -195.6522 | 1068.8985 | -3550 | -400 | -2881.1015 | 72.03% | 84.11% | 95% | 0% | 2161 | -171
[5 empty] | 2019-02-20 | 14 | 1207 | 2175 | -170 | 1 | 0 | 2345 | 1552.7617 | 1552.7617 | 1552.7617 | 2409.5631 | 780 | 200 | 3389.5631 | 84.74% | 95% | 0% | -194.508 | 1358.2537 | -3550 | -400 | -2591.7463 | 64.79% | 84.1% | 95% | 0% | 2345 | -170
[5 empty] | 2019-02-20 | 15 | 1207.5 | 2384 | -171 | 1 | 0 | 2555 | 1881.6983 | 1881.6983 | 1881.6983 | 2409.5631 | 780 | 200 | 3389.5631 | 84.74% | 95% | 0% | -195.6522 | 1686.0461 | -3550 | -400 | -2263.9539 | 56.6% | 84.1% | 95% | 0% | 2555 | -171
[5 empty] | 2019-02-20 | 16 | 1208 | 2475 | -182 | 1 | 0 | 2657 | 2041.4674 | 2041.4674 | 2041.4674 | 2409.5631 | 780 | 200 | 3389.5631 | 84.74% | 95% | 0% | -208.238 | 1833.2294 | -3550 | -400 | -2116.7706 | 52.92% | 84.1% | 95% | 0% | 2657 | -182
[5 empty] | 2019-02-20 | 17 | 1208.5 | 2552 | -212 | 1 | 0 | 2764 | 2209.0684 | 2209.0684 | 2209.0684 | 2409.5631 | 780 | 200 | 3389.5631 | 84.74% | 95% | 0% | -242.5629 | 1966.5055 | -3550 | -400 | -1983.4945 | 49.59% | 84.1% | 95% | 0% | 2764 | -212
[5 empty] | 2019-02-20 | 18 | 1209 | 2541 | -258 | 1 | 0 | 2799 | 2263.8912 | 2263.8912 | 2263.8912 | 2409.5631 | 780 | 200 | 3389.5631 | 84.74% | 95% | 0% | -295.1945 | 1968.6967 | -3550 | -400 | -1981.3033 | 49.53% | 84.09% | 95% | 0% | 2799 | -258
[5 empty] | 2019-02-20 | 19 | 1209.5 | 2542 | -276 | 1 | 0 | 2818 | 2293.6521 | 2293.6521 | 2293.6521 | 2409.5631 | 780 | 200 | 3389.5631 | 84.74% | 95% | 0% | -315.7895 | 1977.8626 | -3550 | -400 | -1972.1374 | 49.3% | 84.09% | 95% | 0% | 2818 | -276
[5 empty] | 2019-02-20 | 20 | 1210 | 2476 | -322 | 1 | 0 | 2798 | 2262.3248 | 2262.3248 | 2262.3248 | 2407.9967 | 780 | 200 | 3387.9967 | 84.7% | 95% | 0% | -368.4211 | 1893.9038 | -3550 | -400 | -2056.0962 | 51.4% | 84.08% | 95% | 0% | 2798 | -322
[5 empty] | 2019-02-20 | 21 | 1210.5 | 2403 | -361 | 1 | 0 | 2764 | 2209.0684 | 2209.0684 | 2209.0684 | 2407.9967 | 780 | 200 | 3387.9967 | 84.7% | 95% | 0% | -413.0435 | 1796.0249 | -3550 | -400 | -2153.9751 | 53.85% | 84.07% | 95% | 0% | 2764 | -361
[5 empty] | 2019-02-20 | 22 | 1211 | 2369 | -381 | 1 | 0 | 2750 | 2187.1393 | 2187.1393 | 2187.1393 | 2407.9967 | 780 | 200 | 3387.9967 | 84.7% | 95% | 0% | -435.9268 | 1751.2126 | -3550 | -400 | -2198.7874 | 54.97% | 84.07% | 95% | 0% | 2750 | -381
[5 empty] | 2019-02-20 | 23 | 1211.5 | 2345 | -403 | 1 | 0 | 2748 | 2184.0066 | 2184.0066 | 2184.0066 | 2406.4303 | 780 | 200 | 3386.4303 | 84.66% | 95% | 0% | -461.0984 | 1722.9082 | -3550 | -400 | -2227.0918 | 55.68% | 84.06% | 95% | 0% | 2748 | -403
[5 empty] | 2019-02-20 | 24 | 1212 | 2340 | -398 | 1 | 0 | 2738 | 2168.343 | 2168.343 | 2168.343 | 2404.864 | 780 | 200 | 3384.864 | 84.62% | 95% | 0% | -455.3776 | 1712.9654 | -3550 | -400 | -2237.0346 | 55.93% | 84.05% | 95% | 0% | 2738 | -398
[5 empty] | 2019-02-20 | 25 | 1212.5 | 2349 | -398 | 1 | 0 | 2747 | 2182.4402 | 2182.4402 | 2182.4402 | 2404.864 | 780 | 200 | 3384.864 | 84.62% | 95% | 0% | -455.3776 | 1727.0627 | -3550 | -400 | -2222.9373 | 55.57% | 84.05% | 95% | 0% | 2747 | -398
[5 empty] | 2019-02-20 | 26 | 1213 | 2333 | -391 | 1 | 0 | 2724 | 2146.4138 | 2146.4138 | 2146.4138 | 2404.864 | 780 | 200 | 3384.864 | 84.62% | 95% | 0% | -447.3684 | 1699.0454 | -3550 | -400 | -2250.9546 | 56.27% | 84.04% | 95% | 0% | 2724 | -391
[5 empty] | 2019-02-20 | 27 | 1213.5 | 2308 | -396 | 1 | 0 | 2704 | 2115.0866 | 2115.0866 | 2115.0866 | 2404.864 | 780 | 200 | 3384.864 | 84.62% | 95% | 0% | -453.0892 | 1661.9973 | -3550 | -400 | -2288.0027 | 57.2% | 84.02% | 95% | 0% | 2704 | -396
[5 empty] | 2019-02-20 | 28 | 1214 | 2311 | -374 | 1 | 0 | 2685 | 2085.3256 | 2085.3256 | 2085.3256 | 2404.864 | 780 | 200 | 3384.864 | 84.62% | 95% | 0% | -427.9176 | 1657.408 | -3550 | -400 | -2292.592 | 57.31% | 84.01% | 95% | 0% | 2685 | -374
[5 empty] | 2019-02-20 | 29 | 1214.5 | 2353 | -346 | 1 | 0 | 2699 | 2107.2547 | 2107.2547 | 2107.2547 | 2404.864 | 780 | 200 | 3384.864 | 84.62% | 95% | 0% | -395.881 | 1711.3737 | -3550 | -400 | -2238.6263 | 55.97% | 84.01% | 95% | 0% | 2699 | -346
[5 empty] | 2019-02-20 | 30 | 1215 | 2401 | -317 | 1 | 0 | 2718 | 2137.0157 | 2137.0157 | 2137.0157 | 2404.864 | 780 | 200 | 3384.864 | 84.62% | 95% | 0% | -362.7002 | 1774.3154 | -3550 | -400 | -2175.6846 | 54.39% | 84% | 95% | 0% | 2718 | -317
[5 empty] | 2019-02-20 | 31 | 1215.5 | 2464 | -289 | 1 | 0 | 2753 | 2191.8384 | 2191.8384 | 2191.8384 | 2403.2976 | 780 | 200 | 3383.2976 | 84.58% | 95% | 0% | -330.6636 | 1861.1748 | -3550 | -400 | -2088.8252 | 52.22% | 84% | 95% | 0% | 2753 | -289
[5 empty] | 2019-02-20 | 32 | 1216 | 2560 | -251 | 1 | 0 | 2811 | 2282.6876 | 2282.6876 | 2282.6876 | 2403.2976 | 780 | 200 | 3383.2976 | 84.58% | 95% | 0% | -287.1854 | 1995.5022 | -3550 | -400 | -1954.4978 | 48.86% | 84% | 95% | 0% | 2811 | -251
[5 empty] | 2019-02-20 | 33 | 1216.5 | 2662 | -216 | 1 | 0 | 2878 | 2387.634 | 2387.634 | 2387.634 | 2403.2976 | 780 | 200 | 3383.2976 | 84.58% | 95% | 0% | -247.1396 | 2140.4944 | -3550 | -400 | -1809.5056 | 45.24% | 83.99% | 95% | 0% | 2878 | -216
[5 empty] | 2019-02-20 | 34 | 1217 | 2788 | -184 | 1 | 0 | 2972 | 2534.8722 | 2534.8722 | 2534.8722 | 2403.2976 | 780 | 200 | 3383.2976 | 84.58% | 95% | 0% | -210.5263 | 2324.3459 | -3550 | -400 | -1625.6541 | 40.64% | 83.99% | 95% | 0% | 2972 | -184
[5 empty] | 2019-02-20 | 35 | 1217.5 | 2904 | -160 | 1 | 0 | 3064 | 2678.9777 | 2678.9777 | 2678.9777 | 2403.2976 | 780 | 200 | 3383.2976 | 84.58% | 95% | 0% | -183.0664 | 2495.9114 | -3550 | -400 | -1454.0886 | 36.35% | 83.98% | 95% | 0% | 3064 | -160
[5 empty] | 2019-02-20 | 36 | 1218 | 3027 | -154 | 1 | 0 | 3181 | 2862.2424 | 2862.2424 | 2862.2424 | 2403.2976 | 780 | 200 | 3383.2976 | 84.58% | 95% | 0% | -176.2014 | 2686.041 | -3550 | -400 | -1263.959 | 31.6% | 83.97% | 95% | 0% | 3181 | -154
[5 empty] | 2019-02-20 | 37 | 1218.5 | 3055 | -153 | 0 | 0 | 3208 | 2904.5342 | 2904.5342 | 2904.5342 | 2403.2976 | 780 | 200 | 3383.2976 | 84.58% | 95% | 0% | -175.0572 | 2729.477 | -2750 | -200 | -220.523 | 5.513% | 83.97% | 95% | 0% | 3208 | -153
[5 empty] | 2019-02-20 | 38 | 1219 | 3010 | -152 | 0 | 0 | 3162 | 2832.4815 | 2832.4815 | 2832.4815 | 2401.7312 | 780 | 200 | 3381.7312 | 84.54% | 95% | 0% | -173.913 | 2658.5684 | -2750 | -200 | -291.4316 | 7.286% | 83.95% | 95% | 0% | 3162 | -152
[5 empty] | 2019-02-20 | 39 | 1219.5 | 2952 | -150 | 0 | 0 | 3102 | 2738.4996 | 2738.4996 | 2738.4996 | 2401.7312 | 780 | 200 | 3381.7312 | 84.54% | 95% | 0% | -171.6247 | 2566.8749 | -2750 | -200 | -383.1251 | 9.578% | 83.95% | 95% | 0% | 3102 | -150
[5 empty] | 2019-02-20 | 40 | 1220 | 2910 | -147 | 0 | 0 | 3057 | 2668.0132 | 2668.0132 | 2668.0132 | 2401.7312 | 780 | 200 | 3381.7312 | 84.54% | 95% | 0% | -168.1922 | 2499.821 | -2750 | -200 | -450.179 | 11.25% | 83.94% | 95% | 0% | 3057 | -147
[5 empty] | 2019-02-20 | 41 | 1220.5 | 2830 | -145 | 0 | 0 | 2975 | 2539.5713 | 2539.5713 | 2539.5713 | 2401.7312 | 780 | 200 | 3381.7312 | 84.54% | 95% | 0% | -165.9039 | 2373.6674 | -2750 | -200 | -576.3326 | 14.41% | 83.93% | 95% | 0% | 2975 | -145
[5 empty] | 2019-02-20 | 42 | 1221 | 2700 | -143 | 0 | 0 | 2843 | 2332.8112 | 2332.8112 | 2332.8112 | 2401.7312 | 780 | 200 | 3381.7312 | 84.54% | 95% | 0% | -163.6156 | 2169.1957 | -2750 | -200 | -780.8043 | 19.52% | 83.93% | 95% | 0% | 2843 | -143
[5 empty] | 2019-02-20 | 43 | 1221.5 | 2567 | -142 | 0 | 0 | 2709 | 2122.9184 | 2122.9184 | 2122.9184 | 2400.1649 | 780 | 200 | 3380.1649 | 84.5% | 95% | 0% | -162.4714 | 1960.447 | -2750 | -200 | -989.553 | 24.74% | 83.93% | 95% | 0% | 2709 | -142
[5 empty] | 2019-02-20 | 44 | 1222 | 2409 | -140 | 1 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 2400.1649 | 780 | 200 | 3380.1649 | 84.5% | 95% | 0% | -160.1831 | 1712.117 | -3550 | -400 | -2237.883 | 55.95% | 83.93% | 95% | 0% | 2549 | -140
[5 empty] | 2019-02-20 | 45 | 1222.5 | 2258 | -140 | 1 | 0 | 2398 | 1635.7791 | 1635.7791 | 1635.7791 | 2400.1649 | 780 | 200 | 3380.1649 | 84.5% | 95% | 0% | -160.1831 | 1475.596 | -3550 | -400 | -2474.404 | 61.86% | 83.92% | 95% | 0% | 2398 | -140
[5 empty] | 2019-02-20 | 46 | 1223 | 2120 | -140 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 2398.5985 | 780 | 200 | 3378.5985 | 84.46% | 95% | 0% | -160.1831 | 1259.4377 | -3550 | -400 | -2690.5623 | 67.26% | 83.92% | 95% | 0% | 2260 | -140
[5 empty] | 2019-02-20 | 47 | 1223.5 | 1978 | -137 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 2398.5985 | 780 | 200 | 3378.5985 | 84.46% | 95% | 0% | -156.7506 | 1035.7474 | -3550 | -400 | -2914.2526 | 72.86% | 83.91% | 95% | 0% | 2115 | -137
[5 empty] | 2019-02-20 | 48 | 1224 | 1891 | -135 | 1 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 2398.5985 | 780 | 200 | 3378.5985 | 84.46% | 95% | 0% | -154.4622 | 898.6293 | -3550 | -400 | -3051.3707 | 76.28% | 83.91% | 95% | 0% | 2026 | -135
[5 empty] | 2019-02-21 | 1 | 1224.5 | 1877 | -135 | 1 | 0 | 2012 | 1031.1624 | 1031.1624 | 1031.1624 | 2398.5985 | 780 | 200 | 3378.5985 | 84.46% | 95% | 0% | -154.4622 | 876.7002 | -3550 | -400 | -3073.2998 | 76.83% | 83.9% | 95% | 0% | 2012 | -135
[5 empty] | 2019-02-21 | 2 | 1225 | 1904 | -134 | 1 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 2398.5985 | 780 | 200 | 3378.5985 | 84.46% | 95% | 0% | -153.3181 | 918.5698 | -3550 | -400 | -3031.4302 | 75.79% | 83.9% | 95% | 0% | 2038 | -134
[5 empty] | 2019-02-21 | 3 | 1225.5 | 1880 | -133 | 1 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 2398.5985 | 780 | 200 | 3378.5985 | 84.46% | 95% | 0% | -152.1739 | 880.5549 | -3550 | -400 | -3069.4451 | 76.74% | 83.9% | 95% | 0% | 2013 | -133
[5 empty] | 2019-02-21 | 4 | 1226 | 1823 | -133 | 1 | 0 | 1956 | 943.446 | 943.446 | 943.446 | 2397.0322 | 780 | 200 | 3377.0322 | 84.43% | 95% | 0% | -152.1739 | 791.2721 | -3550 | -400 | -3158.7279 | 78.97% | 83.89% | 95% | 0% | 1956 | -133
[5 empty] | 2019-02-21 | 5 | 1226.5 | 1785 | -131 | 1 | 0 | 1916 | 880.7914 | 880.7914 | 880.7914 | 2397.0322 | 780 | 200 | 3377.0322 | 84.43% | 95% | 0% | -149.8856 | 730.9058 | -3550 | -400 | -3219.0942 | 80.48% | 83.89% | 95% | 0% | 1916 | -131
[5 empty] | 2019-02-21 | 6 | 1227 | 1761 | -130 | 1 | 0 | 1891 | 841.6323 | 841.6323 | 841.6323 | 2397.0322 | 780 | 200 | 3377.0322 | 84.43% | 95% | 0% | -148.7414 | 692.8909 | -3550 | -400 | -3257.1091 | 81.43% | 83.89% | 95% | 0% | 1891 | -130
[5 empty] | 2019-02-21 | 7 | 1227.5 | 1723 | -129 | 1 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 2397.0322 | 780 | 200 | 3377.0322 | 84.43% | 95% | 0% | -147.5973 | 632.9469 | -3550 | -400 | -3317.0531 | 82.93% | 83.87% | 95% | 0% | 1852 | -129
[5 empty] | 2019-02-21 | 8 | 1228 | 1686 | -128 | 1 | 0 | 1814 | 721.0223 | 721.0223 | 721.0223 | 2397.0322 | 780 | 200 | 3377.0322 | 84.43% | 95% | 0% | -146.4531 | 574.5692 | -3550 | -400 | -3375.4308 | 84.39% | 83.87% | 95% | 0% | 1814 | -128
[5 empty] | 2019-02-21 | 9 | 1228.5 | 1683 | -130 | 1 | 0 | 1813 | 719.4559 | 719.4559 | 719.4559 | 2395.4658 | 780 | 200 | 3375.4658 | 84.39% | 95% | 0% | -148.7414 | 570.7145 | -3550 | -400 | -3379.2855 | 84.48% | 83.87% | 95% | 0% | 1813 | -130
[5 empty] | 2019-02-21 | 10 | 1229 | 1703 | -132 | 1 | 0 | 1835 | 753.9159 | 753.9159 | 753.9159 | 2395.4658 | 780 | 200 | 3375.4658 | 84.39% | 95% | 0% | -151.0297 | 602.8862 | -3550 | -400 | -3347.1138 | 83.68% | 83.87% | 95% | 0% | 1835 | -132
[5 empty] | 2019-02-21 | 11 | 1229.5 | 1767 | -131 | 1 | 0 | 1898 | 852.5969 | 852.5969 | 852.5969 | 2395.4658 | 780 | 200 | 3375.4658 | 84.39% | 95% | 0% | -149.8856 | 702.7113 | -3550 | -400 | -3247.2887 | 81.18% | 83.86% | 95% | 0% | 1898 | -131
[5 empty] | 2019-02-21 | 12 | 1230 | 1872 | -130 | 1 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 2395.4658 | 780 | 200 | 3375.4658 | 84.39% | 95% | 0% | -148.7414 | 866.7573 | -3550 | -400 | -3083.2427 | 77.08% | 83.84% | 95% | 0% | 2002 | -130
[5 empty] | 2019-02-21 | 13 | 1230.5 | 2091 | -127 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 2395.4658 | 780 | 200 | 3375.4658 | 84.39% | 95% | 0% | -145.3089 | 1208.5245 | -3550 | -400 | -2741.4755 | 68.54% | 83.84% | 95% | 0% | 2218 | -127
[5 empty] | 2019-02-21 | 14 | 1231 | 2275 | -124 | 1 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 2393.8994 | 780 | 200 | 3373.8994 | 84.35% | 95% | 0% | -141.8764 | 1495.469 | -3550 | -400 | -2454.531 | 61.36% | 83.83% | 95% | 0% | 2399 | -124
[5 empty] | 2019-02-21 | 15 | 1231.5 | 2467 | -125 | 1 | 0 | 2592 | 1939.6538 | 1939.6538 | 1939.6538 | 2393.8994 | 780 | 200 | 3373.8994 | 84.35% | 95% | 0% | -143.0206 | 1796.6332 | -3550 | -400 | -2153.3668 | 53.83% | 83.83% | 95% | 0% | 2592 | -125
[5 empty] | 2019-02-21 | 16 | 1232 | 2583 | -133 | 1 | 0 | 2716 | 2133.8829 | 2133.8829 | 2133.8829 | 2393.8994 | 780 | 200 | 3373.8994 | 84.35% | 95% | 0% | -152.1739 | 1981.709 | -3550 | -400 | -1968.291 | 49.21% | 83.82% | 95% | 0% | 2716 | -133
[5 empty] | 2019-02-21 | 17 | 1232.5 | 2653 | -157 | 1 | 0 | 2810 | 2281.1212 | 2281.1212 | 2281.1212 | 2393.8994 | 780 | 200 | 3373.8994 | 84.35% | 95% | 0% | -179.6339 | 2101.4873 | -3550 | -400 | -1848.5127 | 46.21% | 83.81% | 95% | 0% | 2810 | -157
[5 empty] | 2019-02-21 | 18 | 1233 | 2684 | -183 | 1 | 0 | 2867 | 2370.404 | 2370.404 | 2370.404 | 2393.8994 | 780 | 200 | 3373.8994 | 84.35% | 95% | 0% | -209.3822 | 2161.0218 | -3550 | -400 | -1788.9782 | 44.72% | 83.79% | 95% | 0% | 2867 | -183
[5 empty] | 2019-02-21 | 19 | 1233.5 | 2668 | -220 | 1 | 0 | 2888 | 2403.2976 | 2403.2976 | 2403.2976 | 2393.8994 | 780 | 200 | 3373.8994 | 84.35% | 95% | 0% | -251.7162 | 2151.5814 | -3550 | -400 | -1798.4186 | 44.96% | 83.78% | 95% | 0% | 2888 | -220
[5 empty] | 2019-02-21 | 20 | 1234 | 2586 | -253 | 1 | 0 | 2839 | 2326.5458 | 2326.5458 | 2326.5458 | 2393.8994 | 780 | 200 | 3373.8994 | 84.35% | 95% | 0% | -289.4737 | 2037.0721 | -3550 | -400 | -1912.9279 | 47.82% | 83.76% | 95% | 0% | 2839 | -253
[5 empty] | 2019-02-21 | 21 | 1234.5 | 2518 | -289 | 1 | 0 | 2807 | 2276.4221 | 2276.4221 | 2276.4221 | 2393.8994 | 780 | 200 | 3373.8994 | 84.35% | 95% | 0% | -330.6636 | 1945.7585 | -3550 | -400 | -2004.2415 | 50.11% | 83.76% | 95% | 0% | 2807 | -289
[5 empty] | 2019-02-21 | 22 | 1235 | 2407 | -362 | 1 | 0 | 2769 | 2216.9002 | 2216.9002 | 2216.9002 | 2393.8994 | 780 | 200 | 3373.8994 | 84.35% | 95% | 0% | -414.1876 | 1802.7126 | -3550 | -400 | -2147.2874 | 53.68% | 83.75% | 95% | 0% | 2769 | -362
[5 empty] | 2019-02-21 | 23 | 1235.5 | 2334 | -394 | 1 | 0 | 2728 | 2152.6793 | 2152.6793 | 2152.6793 | 2393.8994 | 780 | 200 | 3373.8994 | 84.35% | 95% | 0% | -450.8009 | 1701.8784 | -3550 | -400 | -2248.1216 | 56.2% | 83.75% | 95% | 0% | 2728 | -394
[5 empty] | 2019-02-21 | 24 | 1236 | 2189 | -472 | 1 | 0 | 2661 | 2047.7329 | 2047.7329 | 2047.7329 | 2392.3331 | 780 | 200 | 3372.3331 | 84.31% | 95% | 0% | -540.0458 | 1507.6871 | -3550 | -400 | -2442.3129 | 61.06% | 83.75% | 95% | 0% | 2661 | -472
[5 empty] | 2019-02-21 | 25 | 1236.5 | 2074 | -538 | 1 | 0 | 2612 | 1970.981 | 1970.981 | 1970.981 | 2392.3331 | 780 | 200 | 3372.3331 | 84.31% | 95% | 0% | -615.5606 | 1355.4204 | -3550 | -400 | -2594.5796 | 64.86% | 83.75% | 95% | 0% | 2612 | -538
[5 empty] | 2019-02-21 | 26 | 1237 | 1983 | -576 | 1 | 0 | 2559 | 1887.9637 | 1887.9637 | 1887.9637 | 2392.3331 | 780 | 200 | 3372.3331 | 84.31% | 95% | 0% | -659.0389 | 1228.9248 | -3550 | -400 | -2721.0752 | 68.03% | 83.75% | 95% | 0% | 2559 | -576
[5 empty] | 2019-02-21 | 27 | 1237.5 | 1952 | -573 | 1 | 0 | 2525 | 1834.7073 | 1834.7073 | 1834.7073 | 2392.3331 | 780 | 200 | 3372.3331 | 84.31% | 95% | 0% | -655.6064 | 1179.1009 | -3550 | -400 | -2770.8991 | 69.27% | 83.74% | 95% | 0% | 2525 | -573
[5 empty] | 2019-02-21 | 28 | 1238 | 1945 | -552 | 1 | 0 | 2497 | 1790.8491 | 1790.8491 | 1790.8491 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -631.5789 | 1159.2702 | -3550 | -400 | -2790.7298 | 69.77% | 83.74% | 95% | 0% | 2497 | -552
[5 empty] | 2019-02-21 | 29 | 1238.5 | 2003 | -505 | 1 | 0 | 2508 | 1808.0791 | 1808.0791 | 1808.0791 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -577.8032 | 1230.2759 | -3550 | -400 | -2719.7241 | 67.99% | 83.74% | 95% | 0% | 2508 | -505
[5 empty] | 2019-02-21 | 30 | 1239 | 2069 | -449 | 1 | 0 | 2518 | 1823.7428 | 1823.7428 | 1823.7428 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -513.73 | 1310.0128 | -3550 | -400 | -2639.9872 | 66% | 83.73% | 95% | 0% | 2518 | -449
[5 empty] | 2019-02-21 | 31 | 1239.5 | 2171 | -388 | 1 | 0 | 2559 | 1887.9637 | 1887.9637 | 1887.9637 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -443.9359 | 1444.0278 | -3550 | -400 | -2505.9722 | 62.65% | 83.72% | 95% | 0% | 2559 | -388
[5 empty] | 2019-02-21 | 32 | 1240 | 2328 | -315 | 1 | 0 | 2643 | 2019.5383 | 2019.5383 | 2019.5383 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -360.4119 | 1659.1264 | -3550 | -400 | -2290.8736 | 57.27% | 83.71% | 95% | 0% | 2643 | -315
[5 empty] | 2019-02-21 | 33 | 1240.5 | 2502 | -239 | 1 | 0 | 2741 | 2173.042 | 2173.042 | 2173.042 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -273.4554 | 1899.5867 | -3550 | -400 | -2050.4133 | 51.26% | 83.71% | 95% | 0% | 2741 | -239
[5 empty] | 2019-02-21 | 34 | 1241 | 2685 | -164 | 1 | 0 | 2849 | 2342.2094 | 2342.2094 | 2342.2094 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -187.643 | 2154.5664 | -3550 | -400 | -1795.4336 | 44.89% | 83.71% | 95% | 0% | 2849 | -164
[5 empty] | 2019-02-21 | 35 | 1241.5 | 2835 | -121 | 1 | 0 | 2956 | 2509.8104 | 2509.8104 | 2509.8104 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -138.4439 | 2371.3665 | -3550 | -400 | -1578.6335 | 39.47% | 83.71% | 95% | 0% | 2956 | -121
[5 empty] | 2019-02-21 | 36 | 1242 | 2969 | -114 | 1 | 0 | 3083 | 2708.7387 | 2708.7387 | 2708.7387 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -130.4348 | 2578.3039 | -3550 | -400 | -1371.6961 | 34.29% | 83.7% | 95% | 0% | 3083 | -114
[5 empty] | 2019-02-21 | 37 | 1242.5 | 3063 | -114 | 1 | 0 | 3177 | 2855.9769 | 2855.9769 | 2855.9769 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -130.4348 | 2725.5421 | -3550 | -400 | -1224.4579 | 30.61% | 83.69% | 95% | 0% | 3177 | -114
[5 empty] | 2019-02-21 | 38 | 1243 | 3045 | -115 | 0 | 0 | 3160 | 2829.3487 | 2829.3487 | 2829.3487 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -131.5789 | 2697.7698 | -2750 | -200 | -252.2302 | 6.306% | 83.68% | 95% | 0% | 3160 | -115
[5 empty] | 2019-02-21 | 39 | 1243.5 | 2994 | -115 | 0 | 0 | 3109 | 2749.4641 | 2749.4641 | 2749.4641 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -131.5789 | 2617.8852 | -2750 | -200 | -332.1148 | 8.303% | 83.68% | 95% | 0% | 3109 | -115
[5 empty] | 2019-02-21 | 40 | 1244 | 2921 | -116 | 0 | 0 | 3037 | 2636.6859 | 2636.6859 | 2636.6859 | 2390.7667 | 780 | 200 | 3370.7667 | 84.27% | 95% | 0% | -132.7231 | 2503.9628 | -2750 | -200 | -446.0372 | 11.15% | 83.67% | 95% | 0% | 3037 | -116
[5 empty] | 2019-02-21 | 41 | 1244.5 | 2847 | -116 | 0 | 0 | 2963 | 2520.7749 | 2520.7749 | 2520.7749 | 2389.2003 | 780 | 200 | 3369.2003 | 84.23% | 95% | 0% | -132.7231 | 2388.0518 | -2750 | -200 | -561.9482 | 14.05% | 83.67% | 95% | 0% | 2963 | -116
[5 empty] | 2019-02-21 | 42 | 1245 | 2749 | -117 | 0 | 0 | 2866 | 2368.8376 | 2368.8376 | 2368.8376 | 2389.2003 | 780 | 200 | 3369.2003 | 84.23% | 95% | 0% | -133.8673 | 2234.9703 | -2750 | -200 | -715.0297 | 17.88% | 83.66% | 95% | 0% | 2866 | -117
[5 empty] | 2019-02-21 | 43 | 1245.5 | 2607 | -119 | 0 | 0 | 2726 | 2149.5466 | 2149.5466 | 2149.5466 | 2389.2003 | 780 | 200 | 3369.2003 | 84.23% | 95% | 0% | -136.1556 | 2013.391 | -2750 | -200 | -936.609 | 23.42% | 83.66% | 95% | 0% | 2726 | -119
[5 empty] | 2019-02-21 | 44 | 1246 | 2437 | -120 | 0 | 0 | 2557 | 1884.831 | 1884.831 | 1884.831 | 2389.2003 | 780 | 200 | 3369.2003 | 84.23% | 95% | 0% | -137.2998 | 1747.5312 | -2750 | -200 | -1202.4688 | 30.06% | 83.65% | 95% | 0% | 2557 | -120
[5 empty] | 2019-02-21 | 45 | 1246.5 | 2294 | -122 | 0 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 2389.2003 | 780 | 200 | 3369.2003 | 84.23% | 95% | 0% | -139.5881 | 1524.3855 | -2750 | -200 | -1425.6145 | 35.64% | 83.64% | 95% | 0% | 2416 | -122
[5 empty] | 2019-02-21 | 46 | 1247 | 2159 | -124 | 0 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 2389.2003 | 780 | 200 | 3369.2003 | 84.23% | 95% | 0% | -141.8764 | 1313.7707 | -2750 | -200 | -1636.2293 | 40.91% | 83.64% | 95% | 0% | 2283 | -124
[5 empty] | 2019-02-21 | 47 | 1247.5 | 2031 | -123 | 0 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 2387.634 | 780 | 200 | 3367.634 | 84.19% | 95% | 0% | -140.7323 | 1112.8539 | -2750 | -200 | -1837.1461 | 45.93% | 83.63% | 95% | 0% | 2154 | -123
[5 empty] | 2019-02-21 | 48 | 1248 | 1945 | -121 | 0 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 2387.634 | 780 | 200 | 3367.634 | 84.19% | 95% | 0% | -138.4439 | 977.3021 | -2750 | -200 | -1972.6979 | 49.32% | 83.62% | 95% | 0% | 2066 | -121
[5 empty] | 2019-02-22 | 1 | 1248.5 | 1923 | -121 | 0 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 2387.634 | 780 | 200 | 3367.634 | 84.19% | 95% | 0% | -138.4439 | 942.8421 | -2750 | -200 | -2007.1579 | 50.18% | 83.61% | 95% | 0% | 2044 | -121
[5 empty] | 2019-02-22 | 2 | 1249 | 1943 | -121 | 0 | 0 | 2064 | 1112.6134 | 1112.6134 | 1112.6134 | 2387.634 | 780 | 200 | 3367.634 | 84.19% | 95% | 0% | -138.4439 | 974.1694 | -2750 | -200 | -1975.8306 | 49.4% | 83.6% | 95% | 0% | 2064 | -121
[5 empty] | 2019-02-22 | 3 | 1249.5 | 1904 | -121 | 0 | 0 | 2025 | 1051.5251 | 1051.5251 | 1051.5251 | 2387.634 | 780 | 200 | 3367.634 | 84.19% | 95% | 0% | -138.4439 | 913.0812 | -2750 | -200 | -2036.9188 | 50.92% | 83.59% | 95% | 0% | 2025 | -121
[5 empty] | 2019-02-22 | 4 | 1250 | 1851 | -121 | 0 | 0 | 1972 | 968.5078 | 968.5078 | 968.5078 | 2387.634 | 780 | 200 | 3367.634 | 84.19% | 95% | 0% | -138.4439 | 830.0639 | -2750 | -200 | -2119.9361 | 53% | 83.57% | 95% | 0% | 1972 | -121
[5 empty] | 2019-02-22 | 5 | 1250.5 | 1806 | -121 | 0 | 0 | 1927 | 898.0214 | 898.0214 | 898.0214 | 2387.634 | 780 | 200 | 3367.634 | 84.19% | 95% | 0% | -138.4439 | 759.5775 | -2750 | -200 | -2190.4225 | 54.76% | 83.57% | 95% | 0% | 1927 | -121
[5 empty] | 2019-02-22 | 6 | 1251 | 1787 | -121 | 0 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 2386.0676 | 780 | 200 | 3366.0676 | 84.15% | 95% | 0% | -138.4439 | 729.8166 | -2750 | -200 | -2220.1834 | 55.5% | 83.57% | 95% | 0% | 1908 | -121
[5 empty] | 2019-02-22 | 7 | 1251.5 | 1748 | -120 | 0 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 2386.0676 | 780 | 200 | 3366.0676 | 84.15% | 95% | 0% | -137.2998 | 668.3062 | -2750 | -200 | -2281.6938 | 57.04% | 83.56% | 95% | 0% | 1868 | -120
[5 empty] | 2019-02-22 | 8 | 1252 | 1731 | -119 | 0 | 0 | 1850 | 777.4114 | 777.4114 | 777.4114 | 2386.0676 | 780 | 200 | 3366.0676 | 84.15% | 95% | 0% | -136.1556 | 641.2558 | -2750 | -200 | -2308.7442 | 57.72% | 83.55% | 95% | 0% | 1850 | -119
[5 empty] | 2019-02-22 | 9 | 1252.5 | 1722 | -118 | 1 | 0 | 1840 | 761.7477 | 761.7477 | 761.7477 | 2386.0676 | 780 | 200 | 3366.0676 | 84.15% | 95% | 0% | -135.0114 | 626.7363 | -3550 | -400 | -3323.2637 | 83.08% | 83.55% | 95% | 0% | 1840 | -118
[5 empty] | 2019-02-22 | 10 | 1253 | 1727 | -117 | 1 | 0 | 1844 | 768.0132 | 768.0132 | 768.0132 | 2386.0676 | 780 | 200 | 3366.0676 | 84.15% | 95% | 0% | -133.8673 | 634.1459 | -3550 | -400 | -3315.8541 | 82.9% | 83.54% | 95% | 0% | 1844 | -117
[5 empty] | 2019-02-22 | 11 | 1253.5 | 1789 | -116 | 1 | 0 | 1905 | 863.5614 | 863.5614 | 863.5614 | 2386.0676 | 780 | 200 | 3366.0676 | 84.15% | 95% | 0% | -132.7231 | 730.8383 | -3550 | -400 | -3219.1617 | 80.48% | 83.54% | 95% | 0% | 1905 | -116
[5 empty] | 2019-02-22 | 12 | 1254 | 1881 | -114 | 1 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 2386.0676 | 780 | 200 | 3366.0676 | 84.15% | 95% | 0% | -130.4348 | 874.0994 | -3550 | -400 | -3075.9006 | 76.9% | 83.54% | 95% | 0% | 1995 | -114
[5 empty] | 2019-02-22 | 13 | 1254.5 | 2103 | -117 | 1 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 2386.0676 | 780 | 200 | 3366.0676 | 84.15% | 95% | 0% | -133.8673 | 1223.0989 | -3550 | -400 | -2726.9011 | 68.17% | 83.51% | 95% | 0% | 2220 | -117
[5 empty] | 2019-02-22 | 14 | 1255 | 2289 | -119 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 2384.5012 | 780 | 200 | 3364.5012 | 84.11% | 95% | 0% | -136.1556 | 1515.2871 | -3550 | -400 | -2434.7129 | 60.87% | 83.51% | 95% | 0% | 2408 | -119
[5 empty] | 2019-02-22 | 15 | 1255.5 | 2473 | -122 | 1 | 0 | 2595 | 1944.3528 | 1944.3528 | 1944.3528 | 2384.5012 | 780 | 200 | 3364.5012 | 84.11% | 95% | 0% | -139.5881 | 1804.7647 | -3550 | -400 | -2145.2353 | 53.63% | 83.5% | 95% | 0% | 2595 | -122
[5 empty] | 2019-02-22 | 16 | 1256 | 2543 | -143 | 1 | 0 | 2686 | 2086.892 | 2086.892 | 2086.892 | 2384.5012 | 780 | 200 | 3364.5012 | 84.11% | 95% | 0% | -163.6156 | 1923.2764 | -3550 | -400 | -2026.7236 | 50.67% | 83.5% | 95% | 0% | 2686 | -143
[5 empty] | 2019-02-22 | 17 | 1256.5 | 2622 | -176 | 1 | 0 | 2798 | 2262.3248 | 2262.3248 | 2262.3248 | 2384.5012 | 780 | 200 | 3364.5012 | 84.11% | 95% | 0% | -201.373 | 2060.9518 | -3550 | -400 | -1889.0482 | 47.23% | 83.49% | 95% | 0% | 2798 | -176
[5 empty] | 2019-02-22 | 18 | 1257 | 2616 | -210 | 1 | 0 | 2826 | 2306.183 | 2306.183 | 2306.183 | 2384.5012 | 780 | 200 | 3364.5012 | 84.11% | 95% | 0% | -240.2746 | 2065.9084 | -3550 | -400 | -1884.0916 | 47.1% | 83.48% | 95% | 0% | 2826 | -210
[5 empty] | 2019-02-22 | 19 | 1257.5 | 2577 | -242 | 1 | 0 | 2819 | 2295.2185 | 2295.2185 | 2295.2185 | 2384.5012 | 780 | 200 | 3364.5012 | 84.11% | 95% | 0% | -276.8879 | 2018.3306 | -3550 | -400 | -1931.6694 | 48.29% | 83.48% | 95% | 0% | 2819 | -242
[5 empty] | 2019-02-22 | 20 | 1258 | 2504 | -292 | 1 | 0 | 2796 | 2259.1921 | 2259.1921 | 2259.1921 | 2382.9349 | 780 | 200 | 3362.9349 | 84.07% | 95% | 0% | -334.0961 | 1925.096 | -3550 | -400 | -2024.904 | 50.62% | 83.48% | 95% | 0% | 2796 | -292
[5 empty] | 2019-02-22 | 21 | 1258.5 | 2421 | -334 | 1 | 0 | 2755 | 2194.9711 | 2194.9711 | 2194.9711 | 2382.9349 | 780 | 200 | 3362.9349 | 84.07% | 95% | 0% | -382.151 | 1812.8201 | -3550 | -400 | -2137.1799 | 53.43% | 83.47% | 95% | 0% | 2755 | -334
[5 empty] | 2019-02-22 | 22 | 1259 | 2295 | -419 | 1 | 0 | 2714 | 2130.7502 | 2130.7502 | 2130.7502 | 2382.9349 | 780 | 200 | 3362.9349 | 84.07% | 95% | 0% | -479.405 | 1651.3452 | -3550 | -400 | -2298.6548 | 57.47% | 83.46% | 95% | 0% | 2714 | -419
[5 empty] | 2019-02-22 | 23 | 1259.5 | 2182 | -482 | 1 | 0 | 2664 | 2052.432 | 2052.432 | 2052.432 | 2382.9349 | 780 | 200 | 3362.9349 | 84.07% | 95% | 0% | -551.4874 | 1500.9446 | -3550 | -400 | -2449.0554 | 61.23% | 83.45% | 95% | 0% | 2664 | -482
[5 empty] | 2019-02-22 | 24 | 1260 | 2103 | -516 | 1 | 0 | 2619 | 1981.9456 | 1981.9456 | 1981.9456 | 2382.9349 | 780 | 200 | 3362.9349 | 84.07% | 95% | 0% | -590.389 | 1391.5566 | -3550 | -400 | -2558.4434 | 63.96% | 83.45% | 95% | 0% | 2619 | -516
[5 empty] | 2019-02-22 | 25 | 1260.5 | 2037 | -552 | 1 | 0 | 2589 | 1934.9547 | 1934.9547 | 1934.9547 | 2382.9349 | 780 | 200 | 3362.9349 | 84.07% | 95% | 0% | -631.5789 | 1303.3757 | -3550 | -400 | -2646.6243 | 66.17% | 83.43% | 95% | 0% | 2589 | -552
[5 empty] | 2019-02-22 | 26 | 1261 | 1944 | -579 | 1 | 0 | 2523 | 1831.5746 | 1831.5746 | 1831.5746 | 2381.3685 | 780 | 200 | 3361.3685 | 84.03% | 95% | 0% | -662.4714 | 1169.1032 | -3550 | -400 | -2780.8968 | 69.52% | 83.41% | 95% | 0% | 2523 | -579
[5 empty] | 2019-02-22 | 27 | 1261.5 | 1899 | -570 | 1 | 0 | 2469 | 1746.9909 | 1746.9909 | 1746.9909 | 2381.3685 | 780 | 200 | 3361.3685 | 84.03% | 95% | 0% | -652.1739 | 1094.817 | -3550 | -400 | -2855.183 | 71.38% | 83.41% | 95% | 0% | 2469 | -570
[5 empty] | 2019-02-22 | 28 | 1262 | 1905 | -547 | 1 | 0 | 2452 | 1720.3627 | 1720.3627 | 1720.3627 | 2381.3685 | 780 | 200 | 3361.3685 | 84.03% | 95% | 0% | -625.8581 | 1094.5046 | -3550 | -400 | -2855.4954 | 71.39% | 83.39% | 95% | 0% | 2452 | -547
[5 empty] | 2019-02-22 | 29 | 1262.5 | 1926 | -514 | 1 | 0 | 2440 | 1701.5664 | 1701.5664 | 1701.5664 | 2381.3685 | 780 | 200 | 3361.3685 | 84.03% | 95% | 0% | -588.1007 | 1113.4657 | -3550 | -400 | -2836.5343 | 70.91% | 83.39% | 95% | 0% | 2440 | -514
[5 empty] | 2019-02-22 | 30 | 1263 | 1999 | -452 | 1 | 0 | 2451 | 1718.7964 | 1718.7964 | 1718.7964 | 2379.8021 | 780 | 200 | 3359.8021 | 84% | 95% | 0% | -517.1625 | 1201.6339 | -3550 | -400 | -2748.3661 | 68.71% | 83.38% | 95% | 0% | 2451 | -452
[5 empty] | 2019-02-22 | 31 | 1263.5 | 2125 | -370 | 1 | 0 | 2495 | 1787.7164 | 1787.7164 | 1787.7164 | 2379.8021 | 780 | 200 | 3359.8021 | 84% | 95% | 0% | -423.341 | 1364.3754 | -3550 | -400 | -2585.6246 | 64.64% | 83.38% | 95% | 0% | 2495 | -370
[5 empty] | 2019-02-22 | 32 | 1264 | 2303 | -287 | 1 | 0 | 2590 | 1936.521 | 1936.521 | 1936.521 | 2379.8021 | 780 | 200 | 3359.8021 | 84% | 95% | 0% | -328.3753 | 1608.1457 | -3550 | -400 | -2341.8543 | 58.55% | 83.38% | 95% | 0% | 2590 | -287
[5 empty] | 2019-02-22 | 33 | 1264.5 | 2452 | -221 | 1 | 0 | 2673 | 2066.5293 | 2066.5293 | 2066.5293 | 2378.2358 | 780 | 200 | 3358.2358 | 83.96% | 95% | 0% | -252.8604 | 1813.6689 | -3550 | -400 | -2136.3311 | 53.41% | 83.36% | 95% | 0% | 2673 | -221
[5 empty] | 2019-02-22 | 34 | 1265 | 2612 | -159 | 1 | 0 | 2771 | 2220.033 | 2220.033 | 2220.033 | 2378.2358 | 780 | 200 | 3358.2358 | 83.96% | 95% | 0% | -181.9222 | 2038.1108 | -3550 | -400 | -1911.8892 | 47.8% | 83.34% | 95% | 0% | 2771 | -159
[5 empty] | 2019-02-22 | 35 | 1265.5 | 2760 | -132 | 1 | 0 | 2892 | 2409.5631 | 2409.5631 | 2409.5631 | 2378.2358 | 780 | 200 | 3358.2358 | 83.96% | 95% | 0% | -151.0297 | 2258.5333 | -3550 | -400 | -1691.4667 | 42.29% | 83.34% | 95% | 0% | 2892 | -132
[5 empty] | 2019-02-22 | 36 | 1266 | 2870 | -130 | 1 | 0 | 3000 | 2578.7304 | 2578.7304 | 2578.7304 | 2378.2358 | 780 | 200 | 3358.2358 | 83.96% | 95% | 0% | -148.7414 | 2429.989 | -3550 | -400 | -1520.011 | 38% | 83.3% | 95% | 0% | 3000 | -130
[5 empty] | 2019-02-22 | 37 | 1266.5 | 2917 | -133 | 0 | 0 | 3050 | 2657.0486 | 2657.0486 | 2657.0486 | 2378.2358 | 780 | 200 | 3358.2358 | 83.96% | 95% | 0% | -152.1739 | 2504.8747 | -2750 | -200 | -445.1253 | 11.13% | 83.3% | 95% | 0% | 3050 | -133
[5 empty] | 2019-02-22 | 38 | 1267 | 2881 | -137 | 0 | 0 | 3018 | 2606.925 | 2606.925 | 2606.925 | 2378.2358 | 780 | 200 | 3358.2358 | 83.96% | 95% | 0% | -156.7506 | 2450.1744 | -2750 | -200 | -499.8256 | 12.5% | 83.3% | 95% | 0% | 3018 | -137
[5 empty] | 2019-02-22 | 39 | 1267.5 | 2868 | -140 | 0 | 0 | 3008 | 2591.2613 | 2591.2613 | 2591.2613 | 2376.6694 | 780 | 200 | 3356.6694 | 83.92% | 95% | 0% | -160.1831 | 2431.0783 | -2750 | -200 | -518.9217 | 12.97% | 83.3% | 95% | 0% | 3008 | -140
[5 empty] | 2019-02-22 | 40 | 1268 | 2784 | -142 | 0 | 0 | 2926 | 2462.8195 | 2462.8195 | 2462.8195 | 2376.6694 | 780 | 200 | 3356.6694 | 83.92% | 95% | 0% | -162.4714 | 2300.3481 | -2750 | -200 | -649.6519 | 16.24% | 83.29% | 95% | 0% | 2926 | -142
[5 empty] | 2019-02-22 | 41 | 1268.5 | 2680 | -145 | 0 | 0 | 2825 | 2304.6167 | 2304.6167 | 2304.6167 | 2376.6694 | 780 | 200 | 3356.6694 | 83.92% | 95% | 0% | -165.9039 | 2138.7128 | -2750 | -200 | -811.2872 | 20.28% | 83.28% | 95% | 0% | 2825 | -145
[5 empty] | 2019-02-22 | 42 | 1269 | 2565 | -147 | 0 | 0 | 2712 | 2127.6175 | 2127.6175 | 2127.6175 | 2376.6694 | 780 | 200 | 3356.6694 | 83.92% | 95% | 0% | -168.1922 | 1959.4253 | -2750 | -200 | -990.5747 | 24.76% | 83.25% | 95% | 0% | 2712 | -147
[5 empty] | 2019-02-22 | 43 | 1269.5 | 2448 | -148 | 0 | 0 | 2596 | 1945.9192 | 1945.9192 | 1945.9192 | 2376.6694 | 780 | 200 | 3356.6694 | 83.92% | 95% | 0% | -169.3364 | 1776.5828 | -2750 | -200 | -1173.4172 | 29.34% | 83.25% | 95% | 0% | 2596 | -148
[5 empty] | 2019-02-22 | 44 | 1270 | 2318 | -149 | 0 | 0 | 2467 | 1743.8582 | 1743.8582 | 1743.8582 | 2376.6694 | 780 | 200 | 3356.6694 | 83.92% | 95% | 0% | -170.4805 | 1573.3777 | -2750 | -200 | -1376.6223 | 34.42% | 83.24% | 95% | 0% | 2467 | -149
[5 empty] | 2019-02-22 | 45 | 1270.5 | 2180 | -150 | 0 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 2376.6694 | 780 | 200 | 3356.6694 | 83.92% | 95% | 0% | -171.6247 | 1357.6416 | -2750 | -200 | -1592.3584 | 39.81% | 83.24% | 95% | 0% | 2330 | -150
[5 empty] | 2019-02-22 | 46 | 1271 | 2067 | -151 | 0 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 2375.1031 | 780 | 200 | 3355.1031 | 83.88% | 95% | 0% | -172.7689 | 1181.0646 | -2750 | -200 | -1768.9354 | 44.22% | 83.23% | 95% | 0% | 2218 | -151
[5 empty] | 2019-02-22 | 47 | 1271.5 | 1945 | -146 | 0 | 0 | 2091 | 1154.9052 | 1154.9052 | 1154.9052 | 2375.1031 | 780 | 200 | 3355.1031 | 83.88% | 95% | 0% | -167.0481 | 987.8571 | -2750 | -200 | -1962.1429 | 49.05% | 83.23% | 95% | 0% | 2091 | -146
[5 empty] | 2019-02-22 | 48 | 1272 | 1873 | -141 | 0 | 0 | 2014 | 1034.2951 | 1034.2951 | 1034.2951 | 2375.1031 | 780 | 200 | 3355.1031 | 83.88% | 95% | 0% | -161.3272 | 872.9679 | -2750 | -200 | -2077.0321 | 51.93% | 83.22% | 95% | 0% | 2014 | -141
[5 empty] | 2019-02-23 | 1 | 1272.5 | 1839 | -141 | 0 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 2375.1031 | 780 | 200 | 3355.1031 | 83.88% | 95% | 0% | -161.3272 | 819.7115 | -2750 | -200 | -2130.2885 | 53.26% | 83.21% | 95% | 0% | 1980 | -141
[5 empty] | 2019-02-23 | 2 | 1273 | 1855 | -141 | 0 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 2375.1031 | 780 | 200 | 3355.1031 | 83.88% | 95% | 0% | -161.3272 | 844.7733 | -2750 | -200 | -2105.2267 | 52.63% | 83.21% | 95% | 0% | 1996 | -141
[5 empty] | 2019-02-23 | 3 | 1273.5 | 1826 | -142 | 0 | 0 | 1968 | 962.2424 | 962.2424 | 962.2424 | 2373.5367 | 780 | 200 | 3353.5367 | 83.84% | 95% | 0% | -162.4714 | 799.771 | -2750 | -200 | -2150.229 | 53.76% | 83.21% | 95% | 0% | 1968 | -142
[5 empty] | 2019-02-23 | 4 | 1274 | 1747 | -143 | 1 | 0 | 1890 | 840.066 | 840.066 | 840.066 | 2373.5367 | 780 | 200 | 3353.5367 | 83.84% | 95% | 0% | -163.6156 | 676.4504 | -3550 | -400 | -3273.5496 | 81.84% | 83.2% | 95% | 0% | 1890 | -143
[5 empty] | 2019-02-23 | 5 | 1274.5 | 1699 | -143 | 1 | 0 | 1842 | 764.8805 | 764.8805 | 764.8805 | 2373.5367 | 780 | 200 | 3353.5367 | 83.84% | 95% | 0% | -163.6156 | 601.2649 | -3550 | -400 | -3348.7351 | 83.72% | 83.2% | 95% | 0% | 1842 | -143
[5 empty] | 2019-02-23 | 6 | 1275 | 1662 | -144 | 1 | 0 | 1806 | 708.4913 | 708.4913 | 708.4913 | 2373.5367 | 780 | 200 | 3353.5367 | 83.84% | 95% | 0% | -164.7597 | 543.7316 | -3550 | -400 | -3406.2684 | 85.16% | 83.2% | 95% | 0% | 1806 | -144
[5 empty] | 2019-02-23 | 7 | 1275.5 | 1641 | -143 | 1 | 0 | 1784 | 674.0313 | 674.0313 | 674.0313 | 2373.5367 | 780 | 200 | 3353.5367 | 83.84% | 95% | 0% | -163.6156 | 510.4158 | -3550 | -400 | -3439.5842 | 85.99% | 83.19% | 95% | 0% | 1784 | -143
[5 empty] | 2019-02-23 | 8 | 1276 | 1606 | -143 | 1 | 0 | 1749 | 619.2086 | 619.2086 | 619.2086 | 2373.5367 | 780 | 200 | 3353.5367 | 83.84% | 95% | 0% | -163.6156 | 455.593 | -3550 | -400 | -3494.407 | 87.36% | 83.18% | 95% | 0% | 1749 | -143
[5 empty] | 2019-02-23 | 9 | 1276.5 | 1594 | -144 | 1 | 0 | 1738 | 601.9786 | 601.9786 | 601.9786 | 2373.5367 | 780 | 200 | 3353.5367 | 83.84% | 95% | 0% | -164.7597 | 437.2188 | -3550 | -400 | -3512.7812 | 87.82% | 83.18% | 95% | 0% | 1738 | -144
[5 empty] | 2019-02-23 | 10 | 1277 | 1594 | -144 | 1 | 0 | 1738 | 601.9786 | 601.9786 | 601.9786 | 2373.5367 | 780 | 200 | 3353.5367 | 83.84% | 95% | 0% | -164.7597 | 437.2188 | -3550 | -400 | -3512.7812 | 87.82% | 83.18% | 95% | 0% | 1738 | -144
[5 empty] | 2019-02-23 | 11 | 1277.5 | 1600 | -145 | 1 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 2373.5367 | 780 | 200 | 3353.5367 | 83.84% | 95% | 0% | -165.9039 | 447.0392 | -3550 | -400 | -3502.9608 | 87.57% | 83.17% | 95% | 0% | 1745 | -145
[5 empty] | 2019-02-23 | 12 | 1278 | 1645 | -145 | 1 | 0 | 1790 | 683.4295 | 683.4295 | 683.4295 | 2373.5367 | 780 | 200 | 3353.5367 | 83.84% | 95% | 0% | -165.9039 | 517.5256 | -3550 | -400 | -3432.4744 | 85.81% | 83.15% | 95% | 0% | 1790 | -145
[5 empty] | 2019-02-23 | 13 | 1278.5 | 1769 | -145 | 1 | 0 | 1914 | 877.6587 | 877.6587 | 877.6587 | 2373.5367 | 780 | 200 | 3353.5367 | 83.84% | 95% | 0% | -165.9039 | 711.7548 | -3550 | -400 | -3238.2452 | 80.96% | 83.14% | 95% | 0% | 1914 | -145
[5 empty] | 2019-02-23 | 14 | 1279 | 1856 | -144 | 1 | 0 | 2000 | 1012.366 | 1012.366 | 1012.366 | 2371.9703 | 780 | 200 | 3351.9703 | 83.8% | 95% | 0% | -164.7597 | 847.6063 | -3550 | -400 | -3102.3937 | 77.56% | 83.14% | 95% | 0% | 2000 | -144
[5 empty] | 2019-02-23 | 15 | 1279.5 | 1962 | -147 | 1 | 0 | 2109 | 1183.0998 | 1183.0998 | 1183.0998 | 2371.9703 | 780 | 200 | 3351.9703 | 83.8% | 95% | 0% | -168.1922 | 1014.9075 | -3550 | -400 | -2935.0925 | 73.38% | 83.12% | 95% | 0% | 2109 | -147
[5 empty] | 2019-02-23 | 16 | 1280 | 2022 | -172 | 1 | 0 | 2194 | 1316.2407 | 1316.2407 | 1316.2407 | 2371.9703 | 780 | 200 | 3351.9703 | 83.8% | 95% | 0% | -196.7963 | 1119.4444 | -3550 | -400 | -2830.5556 | 70.76% | 83.12% | 95% | 0% | 2194 | -172
[5 empty] | 2019-02-23 | 17 | 1280.5 | 2060 | -219 | 1 | 0 | 2279 | 1449.3817 | 1449.3817 | 1449.3817 | 2371.9703 | 780 | 200 | 3351.9703 | 83.8% | 95% | 0% | -250.5721 | 1198.8096 | -3550 | -400 | -2751.1904 | 68.78% | 83.12% | 95% | 0% | 2279 | -219
[5 empty] | 2019-02-23 | 18 | 1281 | 2085 | -272 | 1 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 2370.404 | 780 | 200 | 3350.404 | 83.76% | 95% | 0% | -311.2128 | 1260.3453 | -3550 | -400 | -2689.6547 | 67.24% | 83.12% | 95% | 0% | 2357 | -272
[5 empty] | 2019-02-23 | 19 | 1281.5 | 2072 | -331 | 1 | 0 | 2403 | 1643.6109 | 1643.6109 | 1643.6109 | 2370.404 | 780 | 200 | 3350.404 | 83.76% | 95% | 0% | -378.7185 | 1264.8923 | -3550 | -400 | -2685.1077 | 67.13% | 83.11% | 95% | 0% | 2403 | -331
[5 empty] | 2019-02-23 | 20 | 1282 | 1995 | -387 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 2370.404 | 780 | 200 | 3350.404 | 83.76% | 95% | 0% | -442.7918 | 1167.9255 | -3550 | -400 | -2782.0745 | 69.55% | 83.11% | 95% | 0% | 2382 | -387
[5 empty] | 2019-02-23 | 21 | 1282.5 | 1899 | -453 | 1 | 0 | 2352 | 1563.7263 | 1563.7263 | 1563.7263 | 2370.404 | 780 | 200 | 3350.404 | 83.76% | 95% | 0% | -518.3066 | 1045.4197 | -3550 | -400 | -2904.5803 | 72.61% | 83.09% | 95% | 0% | 2352 | -453
[5 empty] | 2019-02-23 | 22 | 1283 | 1737 | -523 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 2370.404 | 780 | 200 | 3350.404 | 83.76% | 95% | 0% | -598.3982 | 821.2226 | -3550 | -400 | -3128.7774 | 78.22% | 83.08% | 95% | 0% | 2260 | -523
[5 empty] | 2019-02-23 | 23 | 1283.5 | 1593 | -583 | 1 | 0 | 2176 | 1288.0462 | 1288.0462 | 1288.0462 | 2370.404 | 780 | 200 | 3350.404 | 83.76% | 95% | 0% | -667.0481 | 620.9981 | -3550 | -400 | -3329.0019 | 83.23% | 83.08% | 95% | 0% | 2176 | -583
[5 empty] | 2019-02-23 | 24 | 1284 | 1480 | -634 | 1 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 2370.404 | 780 | 200 | 3350.404 | 83.76% | 95% | 0% | -725.4005 | 465.5311 | -3550 | -400 | -3484.4689 | 87.11% | 83.08% | 95% | 0% | 2114 | -634
[5 empty] | 2019-02-23 | 25 | 1284.5 | 1424 | -660 | 1 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 2370.404 | 780 | 200 | 3350.404 | 83.76% | 95% | 0% | -755.1487 | 388.7919 | -3550 | -400 | -3561.2081 | 89.03% | 83.07% | 95% | 0% | 2084 | -660
[5 empty] | 2019-02-23 | 26 | 1285 | 1404 | -652 | 1 | 0 | 2056 | 1100.0824 | 1100.0824 | 1100.0824 | 2370.404 | 780 | 200 | 3350.404 | 83.76% | 95% | 0% | -745.9954 | 354.087 | -3550 | -400 | -3595.913 | 89.9% | 83.07% | 95% | 0% | 2056 | -652
[5 empty] | 2019-02-23 | 27 | 1285.5 | 1421 | -618 | 1 | 0 | 2039 | 1073.4542 | 1073.4542 | 1073.4542 | 2370.404 | 780 | 200 | 3350.404 | 83.76% | 95% | 0% | -707.0938 | 366.3604 | -3550 | -400 | -3583.6396 | 89.59% | 83.07% | 95% | 0% | 2039 | -618
[5 empty] | 2019-02-23 | 28 | 1286 | 1461 | -568 | 1 | 0 | 2029 | 1057.7906 | 1057.7906 | 1057.7906 | 2368.8376 | 780 | 200 | 3348.8376 | 83.72% | 95% | 0% | -649.8856 | 407.905 | -3550 | -400 | -3542.095 | 88.55% | 83.07% | 95% | 0% | 2029 | -568
[5 empty] | 2019-02-23 | 29 | 1286.5 | 1553 | -502 | 1 | 0 | 2055 | 1098.5161 | 1098.5161 | 1098.5161 | 2368.8376 | 780 | 200 | 3348.8376 | 83.72% | 95% | 0% | -574.3707 | 524.1454 | -3550 | -400 | -3425.8546 | 85.65% | 83.07% | 95% | 0% | 2055 | -502
[5 empty] | 2019-02-23 | 30 | 1287 | 1652 | -429 | 1 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 2368.8376 | 780 | 200 | 3348.8376 | 83.72% | 95% | 0% | -490.8467 | 648.3949 | -3550 | -400 | -3301.6051 | 82.54% | 83.04% | 95% | 0% | 2081 | -429
[5 empty] | 2019-02-23 | 31 | 1287.5 | 1810 | -352 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 2368.8376 | 780 | 200 | 3348.8376 | 83.72% | 95% | 0% | -402.746 | 863.3711 | -3550 | -400 | -3086.6289 | 77.17% | 83.04% | 95% | 0% | 2162 | -352
[5 empty] | 2019-02-23 | 32 | 1288 | 1984 | -279 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 2368.8376 | 780 | 200 | 3348.8376 | 83.72% | 95% | 0% | -319.222 | 1105.0979 | -3550 | -400 | -2844.9021 | 71.12% | 83.03% | 95% | 0% | 2263 | -279
[5 empty] | 2019-02-23 | 33 | 1288.5 | 2159 | -207 | 1 | 0 | 2366 | 1585.6554 | 1585.6554 | 1585.6554 | 2368.8376 | 780 | 200 | 3348.8376 | 83.72% | 95% | 0% | -236.8421 | 1348.8133 | -3550 | -400 | -2601.1867 | 65.03% | 83.02% | 95% | 0% | 2366 | -207
[5 empty] | 2019-02-23 | 34 | 1289 | 2372 | -141 | 1 | 0 | 2513 | 1815.911 | 1815.911 | 1815.911 | 2368.8376 | 780 | 200 | 3348.8376 | 83.72% | 95% | 0% | -161.3272 | 1654.5837 | -3550 | -400 | -2295.4163 | 57.39% | 83.02% | 95% | 0% | 2513 | -141
[5 empty] | 2019-02-23 | 35 | 1289.5 | 2542 | -111 | 1 | 0 | 2653 | 2035.202 | 2035.202 | 2035.202 | 2367.2712 | 780 | 200 | 3347.2712 | 83.68% | 95% | 0% | -127.0023 | 1908.1997 | -3550 | -400 | -2041.8003 | 51.05% | 83.02% | 95% | 0% | 2653 | -111
[5 empty] | 2019-02-23 | 36 | 1290 | 2703 | -103 | 1 | 0 | 2806 | 2274.8557 | 2274.8557 | 2274.8557 | 2367.2712 | 780 | 200 | 3347.2712 | 83.68% | 95% | 0% | -117.849 | 2157.0068 | -3550 | -400 | -1792.9932 | 44.82% | 83.01% | 95% | 0% | 2806 | -103
[5 empty] | 2019-02-23 | 37 | 1290.5 | 2745 | -99 | 1 | 0 | 2844 | 2334.3776 | 2334.3776 | 2334.3776 | 2367.2712 | 780 | 200 | 3347.2712 | 83.68% | 95% | 0% | -113.2723 | 2221.1053 | -3550 | -400 | -1728.8947 | 43.22% | 83.01% | 95% | 0% | 2844 | -99
[5 empty] | 2019-02-23 | 38 | 1291 | 2733 | -95 | 0 | 0 | 2828 | 2309.3157 | 2309.3157 | 2309.3157 | 2367.2712 | 780 | 200 | 3347.2712 | 83.68% | 95% | 0% | -108.6957 | 2200.6201 | -2750 | -200 | -749.3799 | 18.73% | 83.01% | 95% | 0% | 2828 | -95
[5 empty] | 2019-02-23 | 39 | 1291.5 | 2687 | -90 | 0 | 0 | 2777 | 2229.4312 | 2229.4312 | 2229.4312 | 2367.2712 | 780 | 200 | 3347.2712 | 83.68% | 95% | 0% | -102.9748 | 2126.4563 | -2750 | -200 | -823.5437 | 20.59% | 83% | 95% | 0% | 2777 | -90
[5 empty] | 2019-02-23 | 40 | 1292 | 2608 | -85 | 0 | 0 | 2693 | 2097.8566 | 2097.8566 | 2097.8566 | 2367.2712 | 780 | 200 | 3347.2712 | 83.68% | 95% | 0% | -97.254 | 2000.6025 | -2750 | -200 | -949.3975 | 23.73% | 83% | 95% | 0% | 2693 | -85
[5 empty] | 2019-02-23 | 41 | 1292.5 | 2548 | -81 | 0 | 0 | 2629 | 1997.6092 | 1997.6092 | 1997.6092 | 2365.7049 | 780 | 200 | 3345.7049 | 83.64% | 95% | 0% | -92.6773 | 1904.9319 | -2750 | -200 | -1045.0681 | 26.13% | 83% | 95% | 0% | 2629 | -81
[5 empty] | 2019-02-23 | 42 | 1293 | 2456 | -77 | 0 | 0 | 2533 | 1847.2383 | 1847.2383 | 1847.2383 | 2365.7049 | 780 | 200 | 3345.7049 | 83.64% | 95% | 0% | -88.1007 | 1759.1376 | -2750 | -200 | -1190.8624 | 29.77% | 82.99% | 95% | 0% | 2533 | -77
[5 empty] | 2019-02-23 | 43 | 1293.5 | 2374 | -74 | 0 | 0 | 2448 | 1714.0973 | 1714.0973 | 1714.0973 | 2365.7049 | 780 | 200 | 3345.7049 | 83.64% | 95% | 0% | -84.6682 | 1629.4291 | -2750 | -200 | -1320.5709 | 33.01% | 82.98% | 95% | 0% | 2448 | -74
[5 empty] | 2019-02-23 | 44 | 1294 | 2284 | -72 | 0 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 2365.7049 | 780 | 200 | 3345.7049 | 83.64% | 95% | 0% | -82.3799 | 1487.6119 | -2750 | -200 | -1462.3881 | 36.56% | 82.98% | 95% | 0% | 2356 | -72
[5 empty] | 2019-02-23 | 45 | 1294.5 | 2187 | -68 | 0 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 2365.7049 | 780 | 200 | 3345.7049 | 83.64% | 95% | 0% | -77.8032 | 1333.9857 | -2750 | -200 | -1616.0143 | 40.4% | 82.98% | 95% | 0% | 2255 | -68
[5 empty] | 2019-02-23 | 46 | 1295 | 2115 | -63 | 0 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 2365.7049 | 780 | 200 | 3345.7049 | 83.64% | 95% | 0% | -72.0824 | 1219.0965 | -2750 | -200 | -1730.9035 | 43.27% | 82.97% | 95% | 0% | 2178 | -63
[5 empty] | 2019-02-23 | 47 | 1295.5 | 2022 | -57 | 0 | 0 | 2079 | 1136.1088 | 1136.1088 | 1136.1088 | 2365.7049 | 780 | 200 | 3345.7049 | 83.64% | 95% | 0% | -65.2174 | 1070.8914 | -2750 | -200 | -1879.1086 | 46.98% | 82.97% | 95% | 0% | 2079 | -57
[5 empty] | 2019-02-23 | 48 | 1296 | 1977 | -50 | 0 | 0 | 2027 | 1054.6579 | 1054.6579 | 1054.6579 | 2365.7049 | 780 | 200 | 3345.7049 | 83.64% | 95% | 0% | -57.2082 | 997.4496 | -2750 | -200 | -1952.5504 | 48.81% | 82.96% | 95% | 0% | 2027 | -50
[5 empty] | 2019-02-24 | 1 | 1296.5 | 1977 | -46 | 0 | 0 | 2023 | 1048.3924 | 1048.3924 | 1048.3924 | 2365.7049 | 780 | 200 | 3345.7049 | 83.64% | 95% | 0% | -52.6316 | 995.7608 | -2750 | -200 | -1954.2392 | 48.86% | 82.95% | 95% | 0% | 2023 | -46
[5 empty] | 2019-02-24 | 2 | 1297 | 1992 | -42 | 0 | 0 | 2034 | 1065.6224 | 1065.6224 | 1065.6224 | 2364.1385 | 780 | 200 | 3344.1385 | 83.6% | 95% | 0% | -48.0549 | 1017.5675 | -2750 | -200 | -1932.4325 | 48.31% | 82.95% | 95% | 0% | 2034 | -42
[5 empty] | 2019-02-24 | 3 | 1297.5 | 1959 | -40 | 0 | 0 | 1999 | 1010.7997 | 1010.7997 | 1010.7997 | 2364.1385 | 780 | 200 | 3344.1385 | 83.6% | 95% | 0% | -45.7666 | 965.0331 | -2750 | -200 | -1984.9669 | 49.62% | 82.94% | 95% | 0% | 1999 | -40
[5 empty] | 2019-02-24 | 4 | 1298 | 1899 | -37 | 0 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 2364.1385 | 780 | 200 | 3344.1385 | 83.6% | 95% | 0% | -42.3341 | 869.7846 | -2750 | -200 | -2080.2154 | 52.01% | 82.94% | 95% | 0% | 1936 | -37
[5 empty] | 2019-02-24 | 5 | 1298.5 | 1857 | -36 | 0 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 2364.1385 | 780 | 200 | 3344.1385 | 83.6% | 95% | 0% | -41.1899 | 803.5751 | -2750 | -200 | -2146.4249 | 53.66% | 82.93% | 95% | 0% | 1893 | -36
[5 empty] | 2019-02-24 | 6 | 1299 | 1834 | -35 | 0 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 2364.1385 | 780 | 200 | 3344.1385 | 83.6% | 95% | 0% | -40.0458 | 767.1265 | -2750 | -200 | -2182.8735 | 54.57% | 82.93% | 95% | 0% | 1869 | -35
[5 empty] | 2019-02-24 | 7 | 1299.5 | 1797 | -36 | 0 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 2364.1385 | 780 | 200 | 3344.1385 | 83.6% | 95% | 0% | -41.1899 | 709.5933 | -2750 | -200 | -2240.4067 | 56.01% | 82.92% | 95% | 0% | 1833 | -36
[5 empty] | 2019-02-24 | 8 | 1300 | 1763 | -37 | 0 | 0 | 1800 | 699.0932 | 699.0932 | 699.0932 | 2364.1385 | 780 | 200 | 3344.1385 | 83.6% | 95% | 0% | -42.3341 | 656.7591 | -2750 | -200 | -2293.2409 | 57.33% | 82.9% | 95% | 0% | 1800 | -37
[5 empty] | 2019-02-24 | 9 | 1300.5 | 1736 | -38 | 0 | 0 | 1774 | 658.3677 | 658.3677 | 658.3677 | 2364.1385 | 780 | 200 | 3344.1385 | 83.6% | 95% | 0% | -43.4783 | 614.8894 | -2750 | -200 | -2335.1106 | 58.38% | 82.89% | 95% | 0% | 1774 | -38
[5 empty] | 2019-02-24 | 10 | 1301 | 1741 | -40 | 0 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 2362.5721 | 780 | 200 | 3342.5721 | 83.56% | 95% | 0% | -45.7666 | 623.5656 | -2750 | -200 | -2326.4344 | 58.16% | 82.89% | 95% | 0% | 1781 | -40
[5 empty] | 2019-02-24 | 11 | 1301.5 | 1757 | -41 | 0 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 2362.5721 | 780 | 200 | 3342.5721 | 83.56% | 95% | 0% | -46.9108 | 649.0497 | -2750 | -200 | -2300.9503 | 57.52% | 82.89% | 95% | 0% | 1798 | -41
[5 empty] | 2019-02-24 | 12 | 1302 | 1779 | -43 | 0 | 0 | 1822 | 733.5532 | 733.5532 | 733.5532 | 2362.5721 | 780 | 200 | 3342.5721 | 83.56% | 95% | 0% | -49.1991 | 684.3541 | -2750 | -200 | -2265.6459 | 56.64% | 82.88% | 95% | 0% | 1822 | -43
[5 empty] | 2019-02-24 | 13 | 1302.5 | 1863 | -42 | 0 | 0 | 1905 | 863.5614 | 863.5614 | 863.5614 | 2362.5721 | 780 | 200 | 3342.5721 | 83.56% | 95% | 0% | -48.0549 | 815.5065 | -2750 | -200 | -2134.4935 | 53.36% | 82.87% | 95% | 0% | 1905 | -42
[5 empty] | 2019-02-24 | 14 | 1303 | 1917 | -42 | 0 | 0 | 1959 | 948.1451 | 948.1451 | 948.1451 | 2362.5721 | 780 | 200 | 3342.5721 | 83.56% | 95% | 0% | -48.0549 | 900.0902 | -2750 | -200 | -2049.9098 | 51.25% | 82.86% | 95% | 0% | 1959 | -42
[5 empty] | 2019-02-24 | 15 | 1303.5 | 1971 | -48 | 0 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 2362.5721 | 780 | 200 | 3342.5721 | 83.56% | 95% | 0% | -54.9199 | 987.207 | -2750 | -200 | -1962.793 | 49.07% | 82.85% | 95% | 0% | 2019 | -48
[5 empty] | 2019-02-24 | 16 | 1304 | 1980 | -92 | 0 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 2362.5721 | 780 | 200 | 3342.5721 | 83.56% | 95% | 0% | -105.2632 | 1019.8811 | -2750 | -200 | -1930.1189 | 48.25% | 82.85% | 95% | 0% | 2072 | -92
[5 empty] | 2019-02-24 | 17 | 1304.5 | 1986 | -170 | 0 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 2362.5721 | 780 | 200 | 3342.5721 | 83.56% | 95% | 0% | -194.508 | 1062.2109 | -2750 | -200 | -1887.7891 | 47.19% | 82.84% | 95% | 0% | 2156 | -170
[5 empty] | 2019-02-24 | 18 | 1305 | 1938 | -250 | 1 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 2361.0058 | 780 | 200 | 3341.0058 | 83.53% | 95% | 0% | -286.0412 | 1020.8013 | -3550 | -400 | -2929.1987 | 73.23% | 82.83% | 95% | 0% | 2188 | -250
[5 empty] | 2019-02-24 | 19 | 1305.5 | 1910 | -329 | 1 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 2361.0058 | 780 | 200 | 3341.0058 | 83.53% | 95% | 0% | -376.4302 | 1010.2969 | -3550 | -400 | -2939.7031 | 73.49% | 82.83% | 95% | 0% | 2239 | -329
[5 empty] | 2019-02-24 | 20 | 1306 | 1842 | -396 | 1 | 0 | 2238 | 1385.1608 | 1385.1608 | 1385.1608 | 2361.0058 | 780 | 200 | 3341.0058 | 83.53% | 95% | 0% | -453.0892 | 932.0715 | -3550 | -400 | -3017.9285 | 75.45% | 82.82% | 95% | 0% | 2238 | -396
[5 empty] | 2019-02-24 | 21 | 1306.5 | 1766 | -458 | 1 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 2361.0058 | 780 | 200 | 3341.0058 | 83.53% | 95% | 0% | -524.0275 | 839.2042 | -3550 | -400 | -3110.7958 | 77.77% | 82.82% | 95% | 0% | 2224 | -458
[5 empty] | 2019-02-24 | 22 | 1307 | 1677 | -511 | 1 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 2361.0058 | 780 | 200 | 3341.0058 | 83.53% | 95% | 0% | -584.6682 | 722.1743 | -3550 | -400 | -3227.8257 | 80.7% | 82.82% | 95% | 0% | 2188 | -511
[5 empty] | 2019-02-24 | 23 | 1307.5 | 1613 | -556 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 2361.0058 | 780 | 200 | 3341.0058 | 83.53% | 95% | 0% | -636.1556 | 640.926 | -3550 | -400 | -3309.074 | 82.73% | 82.81% | 95% | 0% | 2169 | -556
[5 empty] | 2019-02-24 | 24 | 1308 | 1546 | -594 | 1 | 0 | 2140 | 1231.657 | 1231.657 | 1231.657 | 2361.0058 | 780 | 200 | 3341.0058 | 83.53% | 95% | 0% | -679.6339 | 552.0232 | -3550 | -400 | -3397.9768 | 84.95% | 82.79% | 95% | 0% | 2140 | -594
[5 empty] | 2019-02-24 | 25 | 1308.5 | 1520 | -613 | 1 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 2361.0058 | 780 | 200 | 3341.0058 | 83.53% | 95% | 0% | -701.373 | 519.3195 | -3550 | -400 | -3430.6805 | 85.77% | 82.79% | 95% | 0% | 2133 | -613
[5 empty] | 2019-02-24 | 26 | 1309 | 1500 | -606 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 2361.0058 | 780 | 200 | 3341.0058 | 83.53% | 95% | 0% | -693.3638 | 485.0368 | -3550 | -400 | -3464.9632 | 86.62% | 82.79% | 95% | 0% | 2106 | -606
[5 empty] | 2019-02-24 | 27 | 1309.5 | 1503 | -581 | 1 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 2359.4394 | 780 | 200 | 3339.4394 | 83.49% | 95% | 0% | -664.7597 | 479.1809 | -3550 | -400 | -3470.8191 | 86.77% | 82.78% | 95% | 0% | 2084 | -581
[5 empty] | 2019-02-24 | 28 | 1310 | 1534 | -543 | 1 | 0 | 2077 | 1132.9761 | 1132.9761 | 1132.9761 | 2359.4394 | 780 | 200 | 3339.4394 | 83.49% | 95% | 0% | -621.2815 | 511.6946 | -3550 | -400 | -3438.3054 | 85.96% | 82.78% | 95% | 0% | 2077 | -543
[5 empty] | 2019-02-24 | 29 | 1310.5 | 1603 | -485 | 1 | 0 | 2088 | 1150.2061 | 1150.2061 | 1150.2061 | 2359.4394 | 780 | 200 | 3339.4394 | 83.49% | 95% | 0% | -554.9199 | 595.2862 | -3550 | -400 | -3354.7138 | 83.87% | 82.78% | 95% | 0% | 2088 | -485
[5 empty] | 2019-02-24 | 30 | 1311 | 1677 | -438 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 2359.4394 | 780 | 200 | 3339.4394 | 83.49% | 95% | 0% | -501.1442 | 691.3538 | -3550 | -400 | -3258.6462 | 81.47% | 82.78% | 95% | 0% | 2115 | -438
[5 empty] | 2019-02-24 | 31 | 1311.5 | 1838 | -362 | 1 | 0 | 2200 | 1325.6389 | 1325.6389 | 1325.6389 | 2357.873 | 780 | 200 | 3337.873 | 83.45% | 95% | 0% | -414.1876 | 911.4513 | -3550 | -400 | -3038.5487 | 75.96% | 82.78% | 95% | 0% | 2200 | -362
[5 empty] | 2019-02-24 | 32 | 1312 | 2012 | -282 | 1 | 0 | 2294 | 1472.8772 | 1472.8772 | 1472.8772 | 2357.873 | 780 | 200 | 3337.873 | 83.45% | 95% | 0% | -322.6545 | 1150.2227 | -3550 | -400 | -2799.7773 | 69.99% | 82.78% | 95% | 0% | 2294 | -282
[5 empty] | 2019-02-24 | 33 | 1312.5 | 2254 | -201 | 1 | 0 | 2455 | 1725.0618 | 1725.0618 | 1725.0618 | 2357.873 | 780 | 200 | 3337.873 | 83.45% | 95% | 0% | -229.9771 | 1495.0847 | -3550 | -400 | -2454.9153 | 61.37% | 82.77% | 95% | 0% | 2455 | -201
[5 empty] | 2019-02-24 | 34 | 1313 | 2494 | -130 | 1 | 0 | 2624 | 1989.7774 | 1989.7774 | 1989.7774 | 2357.873 | 780 | 200 | 3337.873 | 83.45% | 95% | 0% | -148.7414 | 1841.036 | -3550 | -400 | -2108.964 | 52.72% | 82.76% | 95% | 0% | 2624 | -130
[5 empty] | 2019-02-24 | 35 | 1313.5 | 2700 | -84 | 1 | 0 | 2784 | 2240.3957 | 2240.3957 | 2240.3957 | 2357.873 | 780 | 200 | 3337.873 | 83.45% | 95% | 0% | -96.1098 | 2144.2859 | -3550 | -400 | -1805.7141 | 45.14% | 82.75% | 95% | 0% | 2784 | -84
[5 empty] | 2019-02-24 | 36 | 1314 | 2836 | -80 | 1 | 0 | 2916 | 2447.1558 | 2447.1558 | 2447.1558 | 2356.3067 | 780 | 200 | 3336.3067 | 83.41% | 95% | 0% | -91.5332 | 2355.6226 | -3550 | -400 | -1594.3774 | 39.86% | 82.75% | 95% | 0% | 2916 | -80
[5 empty] | 2019-02-24 | 37 | 1314.5 | 2855 | -82 | 1 | 0 | 2937 | 2480.0495 | 2480.0495 | 2480.0495 | 2356.3067 | 780 | 200 | 3336.3067 | 83.41% | 95% | 0% | -93.8215 | 2386.228 | -3550 | -400 | -1563.772 | 39.09% | 82.75% | 95% | 0% | 2937 | -82
[5 empty] | 2019-02-24 | 38 | 1315 | 2840 | -84 | 0 | 0 | 2924 | 2459.6867 | 2459.6867 | 2459.6867 | 2356.3067 | 780 | 200 | 3336.3067 | 83.41% | 95% | 0% | -96.1098 | 2363.5769 | -2750 | -200 | -586.4231 | 14.66% | 82.75% | 95% | 0% | 2924 | -84
[5 empty] | 2019-02-24 | 39 | 1315.5 | 2793 | -85 | 0 | 0 | 2878 | 2387.634 | 2387.634 | 2387.634 | 2356.3067 | 780 | 200 | 3336.3067 | 83.41% | 95% | 0% | -97.254 | 2290.38 | -2750 | -200 | -659.62 | 16.49% | 82.75% | 95% | 0% | 2878 | -85
[5 empty] | 2019-02-24 | 40 | 1316 | 2728 | -86 | 0 | 0 | 2814 | 2287.3866 | 2287.3866 | 2287.3866 | 2354.7403 | 780 | 200 | 3334.7403 | 83.37% | 95% | 0% | -98.3982 | 2188.9885 | -2750 | -200 | -761.0115 | 19.03% | 82.75% | 95% | 0% | 2814 | -86
[5 empty] | 2019-02-24 | 41 | 1316.5 | 2643 | -87 | 0 | 0 | 2730 | 2155.812 | 2155.812 | 2155.812 | 2354.7403 | 780 | 200 | 3334.7403 | 83.37% | 95% | 0% | -99.5423 | 2056.2697 | -2750 | -200 | -893.7303 | 22.34% | 82.74% | 95% | 0% | 2730 | -87
[5 empty] | 2019-02-24 | 42 | 1317 | 2523 | -89 | 0 | 0 | 2612 | 1970.981 | 1970.981 | 1970.981 | 2354.7403 | 780 | 200 | 3334.7403 | 83.37% | 95% | 0% | -101.8307 | 1869.1504 | -2750 | -200 | -1080.8496 | 27.02% | 82.74% | 95% | 0% | 2612 | -89
[5 empty] | 2019-02-24 | 43 | 1317.5 | 2425 | -88 | 0 | 0 | 2513 | 1815.911 | 1815.911 | 1815.911 | 2354.7403 | 780 | 200 | 3334.7403 | 83.37% | 95% | 0% | -100.6865 | 1715.2245 | -2750 | -200 | -1234.7755 | 30.87% | 82.74% | 95% | 0% | 2513 | -88
[5 empty] | 2019-02-24 | 44 | 1318 | 2300 | -87 | 0 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 2354.7403 | 780 | 200 | 3334.7403 | 83.37% | 95% | 0% | -99.5423 | 1519.0067 | -2750 | -200 | -1430.9933 | 35.77% | 82.73% | 95% | 0% | 2387 | -87
[5 empty] | 2019-02-24 | 45 | 1318.5 | 2166 | -86 | 0 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 2354.7403 | 780 | 200 | 3334.7403 | 83.37% | 95% | 0% | -98.3982 | 1308.6917 | -2750 | -200 | -1641.3083 | 41.03% | 82.73% | 95% | 0% | 2252 | -86
[5 empty] | 2019-02-24 | 46 | 1319 | 2047 | -85 | 0 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 2354.7403 | 780 | 200 | 3334.7403 | 83.37% | 95% | 0% | -97.254 | 1121.8721 | -2750 | -200 | -1828.1279 | 45.7% | 82.73% | 95% | 0% | 2132 | -85
[5 empty] | 2019-02-24 | 47 | 1319.5 | 1919 | -83 | 0 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 2354.7403 | 780 | 200 | 3334.7403 | 83.37% | 95% | 0% | -94.9657 | 920.5331 | -2750 | -200 | -2029.4669 | 50.74% | 82.72% | 95% | 0% | 2002 | -83
[5 empty] | 2019-02-24 | 48 | 1320 | 1861 | -81 | 0 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 2354.7403 | 780 | 200 | 3334.7403 | 83.37% | 95% | 0% | -92.6773 | 828.8396 | -2750 | -200 | -2121.1604 | 53.03% | 82.72% | 95% | 0% | 1942 | -81
[5 empty] | 2019-02-25 | 1 | 1320.5 | 1850 | -79 | 0 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 2353.1739 | 780 | 200 | 3333.1739 | 83.33% | 95% | 0% | -90.389 | 810.7651 | -2750 | -200 | -2139.2349 | 53.48% | 82.71% | 95% | 0% | 1929 | -79
[5 empty] | 2019-02-25 | 2 | 1321 | 1888 | -76 | 0 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 2353.1739 | 780 | 200 | 3333.1739 | 83.33% | 95% | 0% | -86.9565 | 869.0204 | -2750 | -200 | -2080.9796 | 52.02% | 82.7% | 95% | 0% | 1964 | -76
[5 empty] | 2019-02-25 | 3 | 1321.5 | 1875 | -73 | 0 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 2353.1739 | 780 | 200 | 3333.1739 | 83.33% | 95% | 0% | -83.524 | 847.3911 | -2750 | -200 | -2102.6089 | 52.57% | 82.69% | 95% | 0% | 1948 | -73
[5 empty] | 2019-02-25 | 4 | 1322 | 1844 | -70 | 0 | 0 | 1914 | 877.6587 | 877.6587 | 877.6587 | 2353.1739 | 780 | 200 | 3333.1739 | 83.33% | 95% | 0% | -80.0915 | 797.5672 | -2750 | -200 | -2152.4328 | 53.81% | 82.68% | 95% | 0% | 1914 | -70
[5 empty] | 2019-02-25 | 5 | 1322.5 | 1824 | -66 | 0 | 0 | 1890 | 840.066 | 840.066 | 840.066 | 2353.1739 | 780 | 200 | 3333.1739 | 83.33% | 95% | 0% | -75.5149 | 764.5511 | -2750 | -200 | -2185.4489 | 54.64% | 82.68% | 95% | 0% | 1890 | -66
[5 empty] | 2019-02-25 | 6 | 1323 | 1812 | -63 | 0 | 0 | 1875 | 816.5705 | 816.5705 | 816.5705 | 2353.1739 | 780 | 200 | 3333.1739 | 83.33% | 95% | 0% | -72.0824 | 744.4881 | -2750 | -200 | -2205.5119 | 55.14% | 82.67% | 95% | 0% | 1875 | -63
[5 empty] | 2019-02-25 | 7 | 1323.5 | 1799 | -62 | 0 | 0 | 1861 | 794.6414 | 794.6414 | 794.6414 | 2353.1739 | 780 | 200 | 3333.1739 | 83.33% | 95% | 0% | -70.9382 | 723.7032 | -2750 | -200 | -2226.2968 | 55.66% | 82.67% | 95% | 0% | 1861 | -62
[5 empty] | 2019-02-25 | 8 | 1324 | 1773 | -62 | 0 | 0 | 1835 | 753.9159 | 753.9159 | 753.9159 | 2353.1739 | 780 | 200 | 3333.1739 | 83.33% | 95% | 0% | -70.9382 | 682.9777 | -2750 | -200 | -2267.0223 | 56.68% | 82.67% | 95% | 0% | 1835 | -62
[5 empty] | 2019-02-25 | 9 | 1324.5 | 1780 | -60 | 0 | 0 | 1840 | 761.7477 | 761.7477 | 761.7477 | 2353.1739 | 780 | 200 | 3333.1739 | 83.33% | 95% | 0% | -68.6499 | 693.0978 | -2750 | -200 | -2256.9022 | 56.42% | 82.66% | 95% | 0% | 1840 | -60
[5 empty] | 2019-02-25 | 10 | 1325 | 1798 | -58 | 0 | 0 | 1856 | 786.8096 | 786.8096 | 786.8096 | 2353.1739 | 780 | 200 | 3333.1739 | 83.33% | 95% | 0% | -66.3616 | 720.448 | -2750 | -200 | -2229.552 | 55.74% | 82.66% | 95% | 0% | 1856 | -58
[5 empty] | 2019-02-25 | 11 | 1325.5 | 1864 | -58 | 0 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 2353.1739 | 780 | 200 | 3333.1739 | 83.33% | 95% | 0% | -66.3616 | 823.8281 | -2750 | -200 | -2126.1719 | 53.15% | 82.66% | 95% | 0% | 1922 | -58
[5 empty] | 2019-02-25 | 12 | 1326 | 1996 | -57 | 0 | 0 | 2053 | 1095.3833 | 1095.3833 | 1095.3833 | 2351.6076 | 780 | 200 | 3331.6076 | 83.29% | 95% | 0% | -65.2174 | 1030.166 | -2750 | -200 | -1919.834 | 48% | 82.63% | 95% | 0% | 2053 | -57
[5 empty] | 2019-02-25 | 13 | 1326.5 | 2269 | -56 | 0 | 0 | 2325 | 1521.4345 | 1521.4345 | 1521.4345 | 2351.6076 | 780 | 200 | 3331.6076 | 83.29% | 95% | 0% | -64.0732 | 1457.3612 | -2750 | -200 | -1492.6388 | 37.32% | 82.63% | 95% | 0% | 2325 | -56
[5 empty] | 2019-02-25 | 14 | 1327 | 2522 | -54 | 0 | 0 | 2576 | 1914.5919 | 1914.5919 | 1914.5919 | 2351.6076 | 780 | 200 | 3331.6076 | 83.29% | 95% | 0% | -61.7849 | 1852.807 | -2750 | -200 | -1097.193 | 27.43% | 82.62% | 95% | 0% | 2576 | -54
[5 empty] | 2019-02-25 | 15 | 1327.5 | 2758 | -69 | 0 | 0 | 2827 | 2307.7494 | 2307.7494 | 2307.7494 | 2350.0412 | 780 | 200 | 3330.0412 | 83.25% | 95% | 0% | -78.9474 | 2228.802 | -2750 | -200 | -721.198 | 18.03% | 82.61% | 95% | 0% | 2827 | -69
[5 empty] | 2019-02-25 | 16 | 1328 | 2737 | -135 | 0 | 0 | 2872 | 2378.2358 | 2378.2358 | 2378.2358 | 2350.0412 | 780 | 200 | 3330.0412 | 83.25% | 95% | 0% | -154.4622 | 2223.7735 | -2750 | -200 | -726.2265 | 18.16% | 82.6% | 95% | 0% | 2872 | -135
[5 empty] | 2019-02-25 | 17 | 1328.5 | 2676 | -218 | 0 | 0 | 2894 | 2412.6958 | 2412.6958 | 2412.6958 | 2350.0412 | 780 | 200 | 3330.0412 | 83.25% | 95% | 0% | -249.4279 | 2163.2679 | -2750 | -200 | -786.7321 | 19.67% | 82.6% | 95% | 0% | 2894 | -218
[5 empty] | 2019-02-25 | 18 | 1329 | 2578 | -298 | 1 | 0 | 2876 | 2384.5012 | 2384.5012 | 2384.5012 | 2350.0412 | 780 | 200 | 3330.0412 | 83.25% | 95% | 0% | -340.9611 | 2043.5401 | -3550 | -400 | -1906.4599 | 47.66% | 82.6% | 95% | 0% | 2876 | -298
[5 empty] | 2019-02-25 | 19 | 1329.5 | 2462 | -378 | 1 | 0 | 2840 | 2328.1121 | 2328.1121 | 2328.1121 | 2350.0412 | 780 | 200 | 3330.0412 | 83.25% | 95% | 0% | -432.4943 | 1895.6178 | -3550 | -400 | -2054.3822 | 51.36% | 82.6% | 95% | 0% | 2840 | -378
[5 empty] | 2019-02-25 | 20 | 1330 | 2330 | -446 | 1 | 0 | 2776 | 2227.8648 | 2227.8648 | 2227.8648 | 2350.0412 | 780 | 200 | 3330.0412 | 83.25% | 95% | 0% | -510.2975 | 1717.5673 | -3550 | -400 | -2232.4327 | 55.81% | 82.59% | 95% | 0% | 2776 | -446
[5 empty] | 2019-02-25 | 21 | 1330.5 | 2185 | -507 | 1 | 0 | 2692 | 2096.2902 | 2096.2902 | 2096.2902 | 2350.0412 | 780 | 200 | 3330.0412 | 83.25% | 95% | 0% | -580.0915 | 1516.1987 | -3550 | -400 | -2433.8013 | 60.85% | 82.57% | 95% | 0% | 2692 | -507
[5 empty] | 2019-02-25 | 22 | 1331 | 2065 | -552 | 1 | 0 | 2617 | 1978.8129 | 1978.8129 | 1978.8129 | 2350.0412 | 780 | 200 | 3330.0412 | 83.25% | 95% | 0% | -631.5789 | 1347.2339 | -3550 | -400 | -2602.7661 | 65.07% | 82.57% | 95% | 0% | 2617 | -552
[5 empty] | 2019-02-25 | 23 | 1331.5 | 1975 | -589 | 1 | 0 | 2564 | 1895.7955 | 1895.7955 | 1895.7955 | 2350.0412 | 780 | 200 | 3330.0412 | 83.25% | 95% | 0% | -673.913 | 1221.8825 | -3550 | -400 | -2728.1175 | 68.2% | 82.56% | 95% | 0% | 2564 | -589
[5 empty] | 2019-02-25 | 24 | 1332 | 1918 | -612 | 1 | 0 | 2530 | 1842.5392 | 1842.5392 | 1842.5392 | 2350.0412 | 780 | 200 | 3330.0412 | 83.25% | 95% | 0% | -700.2288 | 1142.3103 | -3550 | -400 | -2807.6897 | 70.19% | 82.55% | 95% | 0% | 2530 | -612
[5 empty] | 2019-02-25 | 25 | 1332.5 | 1895 | -617 | 1 | 0 | 2512 | 1814.3446 | 1814.3446 | 1814.3446 | 2350.0412 | 780 | 200 | 3330.0412 | 83.25% | 95% | 0% | -705.9497 | 1108.3949 | -3550 | -400 | -2841.6051 | 71.04% | 82.54% | 95% | 0% | 2512 | -617
[5 empty] | 2019-02-25 | 26 | 1333 | 1863 | -612 | 1 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 2350.0412 | 780 | 200 | 3330.0412 | 83.25% | 95% | 0% | -700.2288 | 1056.1603 | -3550 | -400 | -2893.8397 | 72.35% | 82.53% | 95% | 0% | 2475 | -612
[5 empty] | 2019-02-25 | 27 | 1333.5 | 1868 | -589 | 1 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 2348.4749 | 780 | 200 | 3328.4749 | 83.21% | 95% | 0% | -673.913 | 1054.2815 | -3550 | -400 | -2895.7185 | 72.39% | 82.52% | 95% | 0% | 2457 | -589
[5 empty] | 2019-02-25 | 28 | 1334 | 1897 | -552 | 1 | 0 | 2449 | 1715.6636 | 1715.6636 | 1715.6636 | 2348.4749 | 780 | 200 | 3328.4749 | 83.21% | 95% | 0% | -631.5789 | 1084.0847 | -3550 | -400 | -2865.9153 | 71.65% | 82.52% | 95% | 0% | 2449 | -552
[5 empty] | 2019-02-25 | 29 | 1334.5 | 1958 | -504 | 1 | 0 | 2462 | 1736.0264 | 1736.0264 | 1736.0264 | 2348.4749 | 780 | 200 | 3328.4749 | 83.21% | 95% | 0% | -576.659 | 1159.3673 | -3550 | -400 | -2790.6327 | 69.77% | 82.5% | 95% | 0% | 2462 | -504
[5 empty] | 2019-02-25 | 30 | 1335 | 2040 | -443 | 1 | 0 | 2483 | 1768.92 | 1768.92 | 1768.92 | 2346.9085 | 780 | 200 | 3326.9085 | 83.17% | 95% | 0% | -506.865 | 1262.055 | -3550 | -400 | -2687.945 | 67.2% | 82.5% | 95% | 0% | 2483 | -443
[5 empty] | 2019-02-25 | 31 | 1335.5 | 2157 | -375 | 1 | 0 | 2532 | 1845.6719 | 1845.6719 | 1845.6719 | 2346.9085 | 780 | 200 | 3326.9085 | 83.17% | 95% | 0% | -429.0618 | 1416.6101 | -3550 | -400 | -2533.3899 | 63.33% | 82.5% | 95% | 0% | 2532 | -375
[5 empty] | 2019-02-25 | 32 | 1336 | 2333 | -300 | 1 | 0 | 2633 | 2003.8747 | 2003.8747 | 2003.8747 | 2346.9085 | 780 | 200 | 3326.9085 | 83.17% | 95% | 0% | -343.2494 | 1660.6253 | -3550 | -400 | -2289.3747 | 57.23% | 82.49% | 95% | 0% | 2633 | -300
[5 empty] | 2019-02-25 | 33 | 1336.5 | 2526 | -225 | 1 | 0 | 2751 | 2188.7057 | 2188.7057 | 2188.7057 | 2346.9085 | 780 | 200 | 3326.9085 | 83.17% | 95% | 0% | -257.4371 | 1931.2686 | -3550 | -400 | -2018.7314 | 50.47% | 82.49% | 95% | 0% | 2751 | -225
[5 empty] | 2019-02-25 | 34 | 1337 | 2729 | -148 | 1 | 0 | 2877 | 2386.0676 | 2386.0676 | 2386.0676 | 2345.3421 | 780 | 200 | 3325.3421 | 83.13% | 95% | 0% | -169.3364 | 2216.7312 | -3550 | -400 | -1733.2688 | 43.33% | 82.48% | 95% | 0% | 2877 | -148
[5 empty] | 2019-02-25 | 35 | 1337.5 | 2925 | -86 | 1 | 0 | 3011 | 2595.9604 | 2595.9604 | 2595.9604 | 2345.3421 | 780 | 200 | 3325.3421 | 83.13% | 95% | 0% | -98.3982 | 2497.5623 | -3550 | -400 | -1452.4377 | 36.31% | 82.48% | 95% | 0% | 3011 | -86
[5 empty] | 2019-02-25 | 36 | 1338 | 3068 | -77 | 1 | 0 | 3145 | 2805.8533 | 2805.8533 | 2805.8533 | 2345.3421 | 780 | 200 | 3325.3421 | 83.13% | 95% | 0% | -88.1007 | 2717.7526 | -3550 | -400 | -1232.2474 | 30.81% | 82.46% | 95% | 0% | 3145 | -77
[5 empty] | 2019-02-25 | 37 | 1338.5 | 3142 | -79 | 1 | 0 | 3221 | 2924.8969 | 2924.8969 | 2924.8969 | 2343.7758 | 780 | 200 | 3323.7758 | 83.09% | 95% | 0% | -90.389 | 2834.5079 | -3550 | -400 | -1115.4921 | 27.89% | 82.46% | 95% | 0% | 3221 | -79
[5 empty] | 2019-02-25 | 38 | 1339 | 3131 | -82 | 0 | 0 | 3213 | 2912.366 | 2912.366 | 2912.366 | 2343.7758 | 780 | 200 | 3323.7758 | 83.09% | 95% | 0% | -93.8215 | 2818.5445 | -2750 | -200 | -131.4555 | 3.286% | 82.46% | 95% | 0% | 3213 | -82
[5 empty] | 2019-02-25 | 39 | 1339.5 | 3083 | -83 | 0 | 0 | 3166 | 2838.7469 | 2838.7469 | 2838.7469 | 2343.7758 | 780 | 200 | 3323.7758 | 83.09% | 95% | 0% | -94.9657 | 2743.7812 | -2750 | -200 | -206.2188 | 5.155% | 82.46% | 95% | 0% | 3166 | -83
[5 empty] | 2019-02-25 | 40 | 1340 | 3014 | -85 | 0 | 0 | 3099 | 2733.8005 | 2733.8005 | 2733.8005 | 2343.7758 | 780 | 200 | 3323.7758 | 83.09% | 95% | 0% | -97.254 | 2636.5465 | -2750 | -200 | -313.4535 | 7.836% | 82.46% | 95% | 0% | 3099 | -85
[5 empty] | 2019-02-25 | 41 | 1340.5 | 2901 | -86 | 0 | 0 | 2987 | 2558.3677 | 2558.3677 | 2558.3677 | 2343.7758 | 780 | 200 | 3323.7758 | 83.09% | 95% | 0% | -98.3982 | 2459.9695 | -2750 | -200 | -490.0305 | 12.25% | 82.46% | 95% | 0% | 2987 | -86
[5 empty] | 2019-02-25 | 42 | 1341 | 2790 | -87 | 0 | 0 | 2877 | 2386.0676 | 2386.0676 | 2386.0676 | 2343.7758 | 780 | 200 | 3323.7758 | 83.09% | 95% | 0% | -99.5423 | 2286.5253 | -2750 | -200 | -663.4747 | 16.59% | 82.43% | 95% | 0% | 2877 | -87
[5 empty] | 2019-02-25 | 43 | 1341.5 | 2648 | -88 | 0 | 0 | 2736 | 2165.2102 | 2165.2102 | 2165.2102 | 2343.7758 | 780 | 200 | 3323.7758 | 83.09% | 95% | 0% | -100.6865 | 2064.5237 | -2750 | -200 | -885.4763 | 22.14% | 82.42% | 95% | 0% | 2736 | -88
[5 empty] | 2019-02-25 | 44 | 1342 | 2496 | -88 | 0 | 0 | 2584 | 1927.1228 | 1927.1228 | 1927.1228 | 2342.2094 | 780 | 200 | 3322.2094 | 83.06% | 95% | 0% | -100.6865 | 1826.4363 | -2750 | -200 | -1123.5637 | 28.09% | 82.42% | 95% | 0% | 2584 | -88
[5 empty] | 2019-02-25 | 45 | 1342.5 | 2319 | -88 | 0 | 0 | 2407 | 1649.8763 | 1649.8763 | 1649.8763 | 2342.2094 | 780 | 200 | 3322.2094 | 83.06% | 95% | 0% | -100.6865 | 1549.1898 | -2750 | -200 | -1400.8102 | 35.02% | 82.41% | 95% | 0% | 2407 | -88
[5 empty] | 2019-02-25 | 46 | 1343 | 2186 | -88 | 0 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 2342.2094 | 780 | 200 | 3322.2094 | 83.06% | 95% | 0% | -100.6865 | 1340.8634 | -2750 | -200 | -1609.1366 | 40.23% | 82.4% | 95% | 0% | 2274 | -88
[5 empty] | 2019-02-25 | 47 | 1343.5 | 2040 | -89 | 0 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 2342.2094 | 780 | 200 | 3322.2094 | 83.06% | 95% | 0% | -101.8307 | 1112.5964 | -2750 | -200 | -1837.4036 | 45.94% | 82.4% | 95% | 0% | 2129 | -89
[5 empty] | 2019-02-25 | 48 | 1344 | 1937 | -89 | 0 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 2342.2094 | 780 | 200 | 3322.2094 | 83.06% | 95% | 0% | -101.8307 | 951.2608 | -2750 | -200 | -1998.7392 | 49.97% | 82.4% | 95% | 0% | 2026 | -89
[5 empty] | 2019-02-26 | 1 | 1344.5 | 1918 | -87 | 0 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 2340.643 | 780 | 200 | 3320.643 | 83.02% | 95% | 0% | -99.5423 | 920.6555 | -2750 | -200 | -2029.3445 | 50.73% | 82.39% | 95% | 0% | 2005 | -87
[5 empty] | 2019-02-26 | 2 | 1345 | 1942 | -84 | 0 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 2340.643 | 780 | 200 | 3320.643 | 83.02% | 95% | 0% | -96.1098 | 956.9817 | -2750 | -200 | -1993.0183 | 49.83% | 82.38% | 95% | 0% | 2026 | -84
[5 empty] | 2019-02-26 | 3 | 1345.5 | 1925 | -81 | 0 | 0 | 2006 | 1021.7642 | 1021.7642 | 1021.7642 | 2340.643 | 780 | 200 | 3320.643 | 83.02% | 95% | 0% | -92.6773 | 929.0869 | -2750 | -200 | -2020.9131 | 50.52% | 82.38% | 95% | 0% | 2006 | -81
[5 empty] | 2019-02-26 | 4 | 1346 | 1888 | -78 | 0 | 0 | 1966 | 959.1096 | 959.1096 | 959.1096 | 2340.643 | 780 | 200 | 3320.643 | 83.02% | 95% | 0% | -89.2449 | 869.8648 | -2750 | -200 | -2080.1352 | 52% | 82.38% | 95% | 0% | 1966 | -78
[5 empty] | 2019-02-26 | 5 | 1346.5 | 1863 | -75 | 0 | 0 | 1938 | 915.2514 | 915.2514 | 915.2514 | 2340.643 | 780 | 200 | 3320.643 | 83.02% | 95% | 0% | -85.8124 | 829.4391 | -2750 | -200 | -2120.5609 | 53.01% | 82.37% | 95% | 0% | 1938 | -75
[5 empty] | 2019-02-26 | 6 | 1347 | 1858 | -72 | 0 | 0 | 1930 | 902.7205 | 902.7205 | 902.7205 | 2340.643 | 780 | 200 | 3320.643 | 83.02% | 95% | 0% | -82.3799 | 820.3407 | -2750 | -200 | -2129.6593 | 53.24% | 82.37% | 95% | 0% | 1930 | -72
[5 empty] | 2019-02-26 | 7 | 1347.5 | 1849 | -71 | 0 | 0 | 1920 | 887.0569 | 887.0569 | 887.0569 | 2340.643 | 780 | 200 | 3320.643 | 83.02% | 95% | 0% | -81.2357 | 805.8212 | -2750 | -200 | -2144.1788 | 53.6% | 82.36% | 95% | 0% | 1920 | -71
[5 empty] | 2019-02-26 | 8 | 1348 | 1819 | -70 | 0 | 0 | 1889 | 838.4996 | 838.4996 | 838.4996 | 2340.643 | 780 | 200 | 3320.643 | 83.02% | 95% | 0% | -80.0915 | 758.4081 | -2750 | -200 | -2191.5919 | 54.79% | 82.36% | 95% | 0% | 1889 | -70
[5 empty] | 2019-02-26 | 9 | 1348.5 | 1819 | -69 | 0 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 2340.643 | 780 | 200 | 3320.643 | 83.02% | 95% | 0% | -78.9474 | 757.9859 | -2750 | -200 | -2192.0141 | 54.8% | 82.35% | 95% | 0% | 1888 | -69
[5 empty] | 2019-02-26 | 10 | 1349 | 1842 | -67 | 0 | 0 | 1909 | 869.8269 | 869.8269 | 869.8269 | 2340.643 | 780 | 200 | 3320.643 | 83.02% | 95% | 0% | -76.659 | 793.1678 | -2750 | -200 | -2156.8322 | 53.92% | 82.35% | 95% | 0% | 1909 | -67
[5 empty] | 2019-02-26 | 11 | 1349.5 | 1915 | -67 | 0 | 0 | 1982 | 984.1715 | 984.1715 | 984.1715 | 2340.643 | 780 | 200 | 3320.643 | 83.02% | 95% | 0% | -76.659 | 907.5124 | -2750 | -200 | -2042.4876 | 51.06% | 82.35% | 95% | 0% | 1982 | -67
[5 empty] | 2019-02-26 | 12 | 1350 | 2037 | -66 | 0 | 0 | 2103 | 1173.7016 | 1173.7016 | 1173.7016 | 2339.0767 | 780 | 200 | 3319.0767 | 82.98% | 95% | 0% | -75.5149 | 1098.1867 | -2750 | -200 | -1851.8133 | 46.3% | 82.35% | 95% | 0% | 2103 | -66
[5 empty] | 2019-02-26 | 13 | 1350.5 | 2312 | -63 | 0 | 0 | 2375 | 1599.7527 | 1599.7527 | 1599.7527 | 2339.0767 | 780 | 200 | 3319.0767 | 82.98% | 95% | 0% | -72.0824 | 1527.6703 | -2750 | -200 | -1422.3297 | 35.56% | 82.34% | 95% | 0% | 2375 | -63
[5 empty] | 2019-02-26 | 14 | 1351 | 2556 | -59 | 0 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 2339.0767 | 780 | 200 | 3319.0767 | 82.98% | 95% | 0% | -67.5057 | 1908.1744 | -2750 | -200 | -1041.8256 | 26.05% | 82.34% | 95% | 0% | 2615 | -59
[5 empty] | 2019-02-26 | 15 | 1351.5 | 2776 | -70 | 0 | 0 | 2846 | 2337.5103 | 2337.5103 | 2337.5103 | 2339.0767 | 780 | 200 | 3319.0767 | 82.98% | 95% | 0% | -80.0915 | 2257.4188 | -2750 | -200 | -692.5812 | 17.31% | 82.33% | 95% | 0% | 2846 | -70
[5 empty] | 2019-02-26 | 16 | 1352 | 2768 | -135 | 0 | 0 | 2903 | 2426.7931 | 2426.7931 | 2426.7931 | 2339.0767 | 780 | 200 | 3319.0767 | 82.98% | 95% | 0% | -154.4622 | 2272.3308 | -2750 | -200 | -677.6692 | 16.94% | 82.33% | 95% | 0% | 2903 | -135
[5 empty] | 2019-02-26 | 17 | 1352.5 | 2679 | -218 | 1 | 0 | 2897 | 2417.3949 | 2417.3949 | 2417.3949 | 2339.0767 | 780 | 200 | 3319.0767 | 82.98% | 95% | 0% | -249.4279 | 2167.967 | -3550 | -400 | -1782.033 | 44.55% | 82.33% | 95% | 0% | 2897 | -218
[5 empty] | 2019-02-26 | 18 | 1353 | 2530 | -299 | 1 | 0 | 2829 | 2310.8821 | 2310.8821 | 2310.8821 | 2339.0767 | 780 | 200 | 3319.0767 | 82.98% | 95% | 0% | -342.1053 | 1968.7768 | -3550 | -400 | -1981.2232 | 49.53% | 82.32% | 95% | 0% | 2829 | -299
[5 empty] | 2019-02-26 | 19 | 1353.5 | 2399 | -377 | 1 | 0 | 2776 | 2227.8648 | 2227.8648 | 2227.8648 | 2339.0767 | 780 | 200 | 3319.0767 | 82.98% | 95% | 0% | -431.3501 | 1796.5147 | -3550 | -400 | -2153.4853 | 53.84% | 82.32% | 95% | 0% | 2776 | -377
[5 empty] | 2019-02-26 | 20 | 1354 | 2258 | -446 | 1 | 0 | 2704 | 2115.0866 | 2115.0866 | 2115.0866 | 2339.0767 | 780 | 200 | 3319.0767 | 82.98% | 95% | 0% | -510.2975 | 1604.7891 | -3550 | -400 | -2345.2109 | 58.63% | 82.32% | 95% | 0% | 2704 | -446
[5 empty] | 2019-02-26 | 21 | 1354.5 | 2109 | -502 | 1 | 0 | 2611 | 1969.4147 | 1969.4147 | 1969.4147 | 2339.0767 | 780 | 200 | 3319.0767 | 82.98% | 95% | 0% | -574.3707 | 1395.044 | -3550 | -400 | -2554.956 | 63.87% | 82.31% | 95% | 0% | 2611 | -502
[5 empty] | 2019-02-26 | 22 | 1355 | 2015 | -549 | 1 | 0 | 2564 | 1895.7955 | 1895.7955 | 1895.7955 | 2337.5103 | 780 | 200 | 3317.5103 | 82.94% | 95% | 0% | -628.1465 | 1267.6491 | -3550 | -400 | -2682.3509 | 67.06% | 82.31% | 95% | 0% | 2564 | -549
[5 empty] | 2019-02-26 | 23 | 1355.5 | 1934 | -583 | 1 | 0 | 2517 | 1822.1764 | 1822.1764 | 1822.1764 | 2337.5103 | 780 | 200 | 3317.5103 | 82.94% | 95% | 0% | -667.0481 | 1155.1284 | -3550 | -400 | -2794.8716 | 69.87% | 82.31% | 95% | 0% | 2517 | -583
[5 empty] | 2019-02-26 | 24 | 1356 | 1878 | -603 | 1 | 0 | 2481 | 1765.7873 | 1765.7873 | 1765.7873 | 2337.5103 | 780 | 200 | 3317.5103 | 82.94% | 95% | 0% | -689.9314 | 1075.856 | -3550 | -400 | -2874.144 | 71.85% | 82.3% | 95% | 0% | 2481 | -603
[5 empty] | 2019-02-26 | 25 | 1356.5 | 1845 | -609 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 2337.5103 | 780 | 200 | 3317.5103 | 82.94% | 95% | 0% | -696.7963 | 1026.6991 | -3550 | -400 | -2923.3009 | 73.08% | 82.3% | 95% | 0% | 2454 | -609
[5 empty] | 2019-02-26 | 26 | 1357 | 1822 | -601 | 1 | 0 | 2423 | 1674.9382 | 1674.9382 | 1674.9382 | 2337.5103 | 780 | 200 | 3317.5103 | 82.94% | 95% | 0% | -687.643 | 987.2951 | -3550 | -400 | -2962.7049 | 74.07% | 82.3% | 95% | 0% | 2423 | -601
[5 empty] | 2019-02-26 | 27 | 1357.5 | 1839 | -579 | 1 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 2337.5103 | 780 | 200 | 3317.5103 | 82.94% | 95% | 0% | -662.4714 | 1004.635 | -3550 | -400 | -2945.365 | 73.63% | 82.28% | 95% | 0% | 2418 | -579
[5 empty] | 2019-02-26 | 28 | 1358 | 1868 | -542 | 1 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 2337.5103 | 780 | 200 | 3317.5103 | 82.94% | 95% | 0% | -620.1373 | 1034.4381 | -3550 | -400 | -2915.5619 | 72.89% | 82.28% | 95% | 0% | 2410 | -542
[5 empty] | 2019-02-26 | 29 | 1358.5 | 1926 | -496 | 1 | 0 | 2422 | 1673.3718 | 1673.3718 | 1673.3718 | 2337.5103 | 780 | 200 | 3317.5103 | 82.94% | 95% | 0% | -567.5057 | 1105.8661 | -3550 | -400 | -2844.1339 | 71.1% | 82.27% | 95% | 0% | 2422 | -496
[5 empty] | 2019-02-26 | 30 | 1359 | 2004 | -438 | 1 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 2337.5103 | 780 | 200 | 3317.5103 | 82.94% | 95% | 0% | -501.1442 | 1203.5549 | -3550 | -400 | -2746.4451 | 68.66% | 82.26% | 95% | 0% | 2442 | -438
[5 empty] | 2019-02-26 | 31 | 1359.5 | 2130 | -369 | 1 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 2335.9439 | 780 | 200 | 3315.9439 | 82.9% | 95% | 0% | -422.1968 | 1371.7851 | -3550 | -400 | -2578.2149 | 64.46% | 82.26% | 95% | 0% | 2499 | -369
[5 empty] | 2019-02-26 | 32 | 1360 | 2302 | -292 | 1 | 0 | 2594 | 1942.7865 | 1942.7865 | 1942.7865 | 2335.9439 | 780 | 200 | 3315.9439 | 82.9% | 95% | 0% | -334.0961 | 1608.6904 | -3550 | -400 | -2341.3096 | 58.53% | 82.25% | 95% | 0% | 2594 | -292
[5 empty] | 2019-02-26 | 33 | 1360.5 | 2508 | -211 | 1 | 0 | 2719 | 2138.582 | 2138.582 | 2138.582 | 2335.9439 | 780 | 200 | 3315.9439 | 82.9% | 95% | 0% | -241.4188 | 1897.1633 | -3550 | -400 | -2052.8367 | 51.32% | 82.25% | 95% | 0% | 2719 | -211
[5 empty] | 2019-02-26 | 34 | 1361 | 2727 | -129 | 1 | 0 | 2856 | 2353.1739 | 2353.1739 | 2353.1739 | 2335.9439 | 780 | 200 | 3315.9439 | 82.9% | 95% | 0% | -147.5973 | 2205.5767 | -3550 | -400 | -1744.4233 | 43.61% | 82.25% | 95% | 0% | 2856 | -129
[5 empty] | 2019-02-26 | 35 | 1361.5 | 2897 | -64 | 1 | 0 | 2961 | 2517.6422 | 2517.6422 | 2517.6422 | 2335.9439 | 780 | 200 | 3315.9439 | 82.9% | 95% | 0% | -73.2265 | 2444.4157 | -3550 | -400 | -1505.5843 | 37.64% | 82.25% | 95% | 0% | 2961 | -64
[5 empty] | 2019-02-26 | 36 | 1362 | 3011 | -50 | 1 | 0 | 3061 | 2674.2786 | 2674.2786 | 2674.2786 | 2335.9439 | 780 | 200 | 3315.9439 | 82.9% | 95% | 0% | -57.2082 | 2617.0704 | -3550 | -400 | -1332.9296 | 33.32% | 82.24% | 95% | 0% | 3061 | -50
[5 empty] | 2019-02-26 | 37 | 1362.5 | 3132 | -52 | 1 | 0 | 3184 | 2866.9415 | 2866.9415 | 2866.9415 | 2334.3776 | 780 | 200 | 3314.3776 | 82.86% | 95% | 0% | -59.4966 | 2807.4449 | -3550 | -400 | -1142.5551 | 28.56% | 82.24% | 95% | 0% | 3184 | -52
[5 empty] | 2019-02-26 | 38 | 1363 | 3129 | -54 | 0 | 0 | 3183 | 2865.3751 | 2865.3751 | 2865.3751 | 2334.3776 | 780 | 200 | 3314.3776 | 82.86% | 95% | 0% | -61.7849 | 2803.5902 | -2750 | -200 | -146.4098 | 3.66% | 82.24% | 95% | 0% | 3183 | -54
[5 empty] | 2019-02-26 | 39 | 1363.5 | 3089 | -55 | 0 | 0 | 3144 | 2804.2869 | 2804.2869 | 2804.2869 | 2334.3776 | 780 | 200 | 3314.3776 | 82.86% | 95% | 0% | -62.9291 | 2741.3578 | -2750 | -200 | -208.6422 | 5.216% | 82.24% | 95% | 0% | 3144 | -55
[5 empty] | 2019-02-26 | 40 | 1364 | 3063 | -57 | 0 | 0 | 3120 | 2766.6941 | 2766.6941 | 2766.6941 | 2334.3776 | 780 | 200 | 3314.3776 | 82.86% | 95% | 0% | -65.2174 | 2701.4768 | -2750 | -200 | -248.5232 | 6.213% | 82.24% | 95% | 0% | 3120 | -57
[5 empty] | 2019-02-26 | 41 | 1364.5 | 2983 | -60 | 0 | 0 | 3043 | 2646.0841 | 2646.0841 | 2646.0841 | 2332.8112 | 780 | 200 | 3312.8112 | 82.82% | 95% | 0% | -68.6499 | 2577.4342 | -2750 | -200 | -372.5658 | 9.314% | 82.22% | 95% | 0% | 3043 | -60
[5 empty] | 2019-02-26 | 42 | 1365 | 2848 | -62 | 0 | 0 | 2910 | 2437.7576 | 2437.7576 | 2437.7576 | 2332.8112 | 780 | 200 | 3312.8112 | 82.82% | 95% | 0% | -70.9382 | 2366.8194 | -2750 | -200 | -583.1806 | 14.58% | 82.21% | 95% | 0% | 2910 | -62
[5 empty] | 2019-02-26 | 43 | 1365.5 | 2702 | -63 | 0 | 0 | 2765 | 2210.6348 | 2210.6348 | 2210.6348 | 2332.8112 | 780 | 200 | 3312.8112 | 82.82% | 95% | 0% | -72.0824 | 2138.5524 | -2750 | -200 | -811.4476 | 20.29% | 82.21% | 95% | 0% | 2765 | -63
[5 empty] | 2019-02-26 | 44 | 1366 | 2536 | -64 | 0 | 0 | 2600 | 1952.1847 | 1952.1847 | 1952.1847 | 2332.8112 | 780 | 200 | 3312.8112 | 82.82% | 95% | 0% | -73.2265 | 1878.9581 | -2750 | -200 | -1071.0419 | 26.78% | 82.21% | 95% | 0% | 2600 | -64
[5 empty] | 2019-02-26 | 45 | 1366.5 | 2386 | -64 | 0 | 0 | 2450 | 1717.23 | 1717.23 | 1717.23 | 2332.8112 | 780 | 200 | 3312.8112 | 82.82% | 95% | 0% | -73.2265 | 1644.0035 | -2750 | -200 | -1305.9965 | 32.65% | 82.21% | 95% | 0% | 2450 | -64
[5 empty] | 2019-02-26 | 46 | 1367 | 2235 | -64 | 0 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 2332.8112 | 780 | 200 | 3312.8112 | 82.82% | 95% | 0% | -73.2265 | 1407.4824 | -2750 | -200 | -1542.5176 | 38.56% | 82.21% | 95% | 0% | 2299 | -64
[5 empty] | 2019-02-26 | 47 | 1367.5 | 2086 | -66 | 0 | 0 | 2152 | 1250.4534 | 1250.4534 | 1250.4534 | 2332.8112 | 780 | 200 | 3312.8112 | 82.82% | 95% | 0% | -75.5149 | 1174.9385 | -2750 | -200 | -1775.0615 | 44.38% | 82.2% | 95% | 0% | 2152 | -66
[5 empty] | 2019-02-26 | 48 | 1368 | 1992 | -68 | 0 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 2331.2448 | 780 | 200 | 3311.2448 | 82.78% | 95% | 0% | -77.8032 | 1028.5447 | -2750 | -200 | -1921.4553 | 48.04% | 82.2% | 95% | 0% | 2060 | -68
[5 empty] | 2019-02-27 | 1 | 1368.5 | 1976 | -66 | 0 | 0 | 2042 | 1078.1533 | 1078.1533 | 1078.1533 | 2331.2448 | 780 | 200 | 3311.2448 | 82.78% | 95% | 0% | -75.5149 | 1002.6385 | -2750 | -200 | -1947.3615 | 48.68% | 82.18% | 95% | 0% | 2042 | -66
[5 empty] | 2019-02-27 | 2 | 1369 | 1990 | -65 | 0 | 0 | 2055 | 1098.5161 | 1098.5161 | 1098.5161 | 2331.2448 | 780 | 200 | 3311.2448 | 82.78% | 95% | 0% | -74.3707 | 1024.1454 | -2750 | -200 | -1925.8546 | 48.15% | 82.18% | 95% | 0% | 2055 | -65
[5 empty] | 2019-02-27 | 3 | 1369.5 | 1964 | -64 | 0 | 0 | 2028 | 1056.2242 | 1056.2242 | 1056.2242 | 2331.2448 | 780 | 200 | 3311.2448 | 82.78% | 95% | 0% | -73.2265 | 982.9977 | -2750 | -200 | -1967.0023 | 49.18% | 82.18% | 95% | 0% | 2028 | -64
[5 empty] | 2019-02-27 | 4 | 1370 | 1921 | -64 | 0 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 2331.2448 | 780 | 200 | 3311.2448 | 82.78% | 95% | 0% | -73.2265 | 915.644 | -2750 | -200 | -2034.356 | 50.86% | 82.17% | 95% | 0% | 1985 | -64
[5 empty] | 2019-02-27 | 5 | 1370.5 | 1896 | -62 | 0 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 2329.6785 | 780 | 200 | 3309.6785 | 82.74% | 95% | 0% | -70.9382 | 875.6405 | -2750 | -200 | -2074.3595 | 51.86% | 82.17% | 95% | 0% | 1958 | -62
[5 empty] | 2019-02-27 | 6 | 1371 | 1883 | -60 | 0 | 0 | 1943 | 923.0833 | 923.0833 | 923.0833 | 2329.6785 | 780 | 200 | 3309.6785 | 82.74% | 95% | 0% | -68.6499 | 854.4334 | -2750 | -200 | -2095.5666 | 52.39% | 82.17% | 95% | 0% | 1943 | -60
[5 empty] | 2019-02-27 | 7 | 1371.5 | 1857 | -59 | 0 | 0 | 1916 | 880.7914 | 880.7914 | 880.7914 | 2329.6785 | 780 | 200 | 3309.6785 | 82.74% | 95% | 0% | -67.5057 | 813.2857 | -2750 | -200 | -2136.7143 | 53.42% | 82.16% | 95% | 0% | 1916 | -59
[5 empty] | 2019-02-27 | 8 | 1372 | 1835 | -57 | 0 | 0 | 1892 | 843.1987 | 843.1987 | 843.1987 | 2329.6785 | 780 | 200 | 3309.6785 | 82.74% | 95% | 0% | -65.2174 | 777.9813 | -2750 | -200 | -2172.0187 | 54.3% | 82.16% | 95% | 0% | 1892 | -57
[5 empty] | 2019-02-27 | 9 | 1372.5 | 1837 | -57 | 0 | 0 | 1894 | 846.3314 | 846.3314 | 846.3314 | 2329.6785 | 780 | 200 | 3309.6785 | 82.74% | 95% | 0% | -65.2174 | 781.114 | -2750 | -200 | -2168.886 | 54.22% | 82.15% | 95% | 0% | 1894 | -57
[5 empty] | 2019-02-27 | 10 | 1373 | 1857 | -56 | 0 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 2329.6785 | 780 | 200 | 3309.6785 | 82.74% | 95% | 0% | -64.0732 | 812.0191 | -2750 | -200 | -2137.9809 | 53.45% | 82.15% | 95% | 0% | 1913 | -56
[5 empty] | 2019-02-27 | 11 | 1373.5 | 1937 | -56 | 0 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 2328.1121 | 780 | 200 | 3308.1121 | 82.7% | 95% | 0% | -64.0732 | 937.3283 | -2750 | -200 | -2012.6717 | 50.32% | 82.14% | 95% | 0% | 1993 | -56
[5 empty] | 2019-02-27 | 12 | 1374 | 2051 | -56 | 0 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 2328.1121 | 780 | 200 | 3308.1121 | 82.7% | 95% | 0% | -64.0732 | 1115.8938 | -2750 | -200 | -1834.1062 | 45.85% | 82.14% | 95% | 0% | 2107 | -56
[5 empty] | 2019-02-27 | 13 | 1374.5 | 2325 | -54 | 0 | 0 | 2379 | 1606.0181 | 1606.0181 | 1606.0181 | 2328.1121 | 780 | 200 | 3308.1121 | 82.7% | 95% | 0% | -61.7849 | 1544.2332 | -2750 | -200 | -1405.7668 | 35.14% | 82.13% | 95% | 0% | 2379 | -54
[5 empty] | 2019-02-27 | 14 | 1375 | 2518 | -52 | 0 | 0 | 2570 | 1905.1937 | 1905.1937 | 1905.1937 | 2328.1121 | 780 | 200 | 3308.1121 | 82.7% | 95% | 0% | -59.4966 | 1845.6972 | -2750 | -200 | -1104.3028 | 27.61% | 82.12% | 95% | 0% | 2570 | -52
[5 empty] | 2019-02-27 | 15 | 1375.5 | 2708 | -65 | 0 | 0 | 2773 | 2223.1657 | 2223.1657 | 2223.1657 | 2328.1121 | 780 | 200 | 3308.1121 | 82.7% | 95% | 0% | -74.3707 | 2148.795 | -2750 | -200 | -801.205 | 20.03% | 82.12% | 95% | 0% | 2773 | -65
[5 empty] | 2019-02-27 | 16 | 1376 | 2691 | -127 | 0 | 0 | 2818 | 2293.6521 | 2293.6521 | 2293.6521 | 2328.1121 | 780 | 200 | 3308.1121 | 82.7% | 95% | 0% | -145.3089 | 2148.3432 | -2750 | -200 | -801.6568 | 20.04% | 82.11% | 95% | 0% | 2818 | -127
[5 empty] | 2019-02-27 | 17 | 1376.5 | 2598 | -209 | 0 | 0 | 2807 | 2276.4221 | 2276.4221 | 2276.4221 | 2328.1121 | 780 | 200 | 3308.1121 | 82.7% | 95% | 0% | -239.1304 | 2037.2917 | -2750 | -200 | -912.7083 | 22.82% | 82.11% | 95% | 0% | 2807 | -209
[5 empty] | 2019-02-27 | 18 | 1377 | 2492 | -290 | 1 | 0 | 2782 | 2237.263 | 2237.263 | 2237.263 | 2328.1121 | 780 | 200 | 3308.1121 | 82.7% | 95% | 0% | -331.8078 | 1905.4552 | -3550 | -400 | -2044.5448 | 51.11% | 82.11% | 95% | 0% | 2782 | -290
[5 empty] | 2019-02-27 | 19 | 1377.5 | 2388 | -366 | 1 | 0 | 2754 | 2193.4048 | 2193.4048 | 2193.4048 | 2328.1121 | 780 | 200 | 3308.1121 | 82.7% | 95% | 0% | -418.7643 | 1774.6405 | -3550 | -400 | -2175.3595 | 54.38% | 82.11% | 95% | 0% | 2754 | -366
[5 empty] | 2019-02-27 | 20 | 1378 | 2267 | -434 | 1 | 0 | 2701 | 2110.3875 | 2110.3875 | 2110.3875 | 2328.1121 | 780 | 200 | 3308.1121 | 82.7% | 95% | 0% | -496.5675 | 1613.82 | -3550 | -400 | -2336.18 | 58.4% | 82.11% | 95% | 0% | 2701 | -434
[5 empty] | 2019-02-27 | 21 | 1378.5 | 2128 | -492 | 1 | 0 | 2620 | 1983.512 | 1983.512 | 1983.512 | 2326.5458 | 780 | 200 | 3306.5458 | 82.66% | 95% | 0% | -562.9291 | 1420.5829 | -3550 | -400 | -2529.4171 | 63.24% | 82.11% | 95% | 0% | 2620 | -492
[5 empty] | 2019-02-27 | 22 | 1379 | 2027 | -539 | 1 | 0 | 2566 | 1898.9283 | 1898.9283 | 1898.9283 | 2326.5458 | 780 | 200 | 3306.5458 | 82.66% | 95% | 0% | -616.7048 | 1282.2235 | -3550 | -400 | -2667.7765 | 66.69% | 82.11% | 95% | 0% | 2566 | -539
[5 empty] | 2019-02-27 | 23 | 1379.5 | 1944 | -573 | 1 | 0 | 2517 | 1822.1764 | 1822.1764 | 1822.1764 | 2326.5458 | 780 | 200 | 3306.5458 | 82.66% | 95% | 0% | -655.6064 | 1166.57 | -3550 | -400 | -2783.43 | 69.59% | 82.11% | 95% | 0% | 2517 | -573
[5 empty] | 2019-02-27 | 24 | 1380 | 1874 | -593 | 1 | 0 | 2467 | 1743.8582 | 1743.8582 | 1743.8582 | 2326.5458 | 780 | 200 | 3306.5458 | 82.66% | 95% | 0% | -678.4897 | 1065.3685 | -3550 | -400 | -2884.6315 | 72.12% | 82.1% | 95% | 0% | 2467 | -593
[5 empty] | 2019-02-27 | 25 | 1380.5 | 1848 | -600 | 1 | 0 | 2448 | 1714.0973 | 1714.0973 | 1714.0973 | 2326.5458 | 780 | 200 | 3306.5458 | 82.66% | 95% | 0% | -686.4989 | 1027.5984 | -3550 | -400 | -2922.4016 | 73.06% | 82.1% | 95% | 0% | 2448 | -600
[5 empty] | 2019-02-27 | 26 | 1381 | 1826 | -593 | 1 | 0 | 2419 | 1668.6727 | 1668.6727 | 1668.6727 | 2326.5458 | 780 | 200 | 3306.5458 | 82.66% | 95% | 0% | -678.4897 | 990.183 | -3550 | -400 | -2959.817 | 74% | 82.08% | 95% | 0% | 2419 | -593
[5 empty] | 2019-02-27 | 27 | 1381.5 | 1829 | -571 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 2326.5458 | 780 | 200 | 3306.5458 | 82.66% | 95% | 0% | -653.3181 | 985.5937 | -3550 | -400 | -2964.4063 | 74.11% | 82.07% | 95% | 0% | 2400 | -571
[5 empty] | 2019-02-27 | 28 | 1382 | 1855 | -537 | 1 | 0 | 2392 | 1626.3809 | 1626.3809 | 1626.3809 | 2326.5458 | 780 | 200 | 3306.5458 | 82.66% | 95% | 0% | -614.4165 | 1011.9644 | -3550 | -400 | -2938.0356 | 73.45% | 82.07% | 95% | 0% | 2392 | -537
[5 empty] | 2019-02-27 | 29 | 1382.5 | 1922 | -489 | 1 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 2324.9794 | 780 | 200 | 3304.9794 | 82.62% | 95% | 0% | -559.4966 | 1096.6452 | -3550 | -400 | -2853.3548 | 71.33% | 82.07% | 95% | 0% | 2411 | -489
[5 empty] | 2019-02-27 | 30 | 1383 | 2005 | -431 | 1 | 0 | 2436 | 1695.3009 | 1695.3009 | 1695.3009 | 2324.9794 | 780 | 200 | 3304.9794 | 82.62% | 95% | 0% | -493.135 | 1202.1659 | -3550 | -400 | -2747.8341 | 68.7% | 82.06% | 95% | 0% | 2436 | -431
[5 empty] | 2019-02-27 | 31 | 1383.5 | 2135 | -357 | 1 | 0 | 2492 | 1783.0173 | 1783.0173 | 1783.0173 | 2324.9794 | 780 | 200 | 3304.9794 | 82.62% | 95% | 0% | -408.4668 | 1374.5505 | -3550 | -400 | -2575.4495 | 64.39% | 82.06% | 95% | 0% | 2492 | -357
[5 empty] | 2019-02-27 | 32 | 1384 | 2320 | -277 | 1 | 0 | 2597 | 1947.4856 | 1947.4856 | 1947.4856 | 2324.9794 | 780 | 200 | 3304.9794 | 82.62% | 95% | 0% | -316.9336 | 1630.5519 | -3550 | -400 | -2319.4481 | 57.99% | 82.06% | 95% | 0% | 2597 | -277
[5 empty] | 2019-02-27 | 33 | 1384.5 | 2523 | -194 | 1 | 0 | 2717 | 2135.4493 | 2135.4493 | 2135.4493 | 2324.9794 | 780 | 200 | 3304.9794 | 82.62% | 95% | 0% | -221.968 | 1913.4813 | -3550 | -400 | -2036.5187 | 50.91% | 82.05% | 95% | 0% | 2717 | -194
[5 empty] | 2019-02-27 | 34 | 1385 | 2739 | -115 | 1 | 0 | 2854 | 2350.0412 | 2350.0412 | 2350.0412 | 2324.9794 | 780 | 200 | 3304.9794 | 82.62% | 95% | 0% | -131.5789 | 2218.4623 | -3550 | -400 | -1731.5377 | 43.29% | 82.05% | 95% | 0% | 2854 | -115
[5 empty] | 2019-02-27 | 35 | 1385.5 | 2929 | -54 | 1 | 0 | 2983 | 2552.1022 | 2552.1022 | 2552.1022 | 2323.413 | 780 | 200 | 3303.413 | 82.59% | 95% | 0% | -61.7849 | 2490.3173 | -3550 | -400 | -1459.6827 | 36.49% | 82.04% | 95% | 0% | 2983 | -54
[5 empty] | 2019-02-27 | 36 | 1386 | 3049 | -37 | 1 | 0 | 3086 | 2713.4378 | 2713.4378 | 2713.4378 | 2323.413 | 780 | 200 | 3303.413 | 82.59% | 95% | 0% | -42.3341 | 2671.1037 | -3550 | -400 | -1278.8963 | 31.97% | 82.04% | 95% | 0% | 3086 | -37
[5 empty] | 2019-02-27 | 37 | 1386.5 | 3145 | -37 | 1 | 0 | 3182 | 2863.8087 | 2863.8087 | 2863.8087 | 2323.413 | 780 | 200 | 3303.413 | 82.59% | 95% | 0% | -42.3341 | 2821.4746 | -3550 | -400 | -1128.5254 | 28.21% | 82.03% | 95% | 0% | 3182 | -37
[5 empty] | 2019-02-27 | 38 | 1387 | 3152 | -36 | 0 | 0 | 3188 | 2873.2069 | 2873.2069 | 2873.2069 | 2323.413 | 780 | 200 | 3303.413 | 82.59% | 95% | 0% | -41.1899 | 2832.017 | -2750 | -200 | -117.983 | 2.95% | 82.03% | 95% | 0% | 3188 | -36
[5 empty] | 2019-02-27 | 39 | 1387.5 | 3095 | -37 | 0 | 0 | 3132 | 2785.4905 | 2785.4905 | 2785.4905 | 2321.8467 | 780 | 200 | 3301.8467 | 82.55% | 95% | 0% | -42.3341 | 2743.1564 | -2750 | -200 | -206.8436 | 5.171% | 82.03% | 95% | 0% | 3132 | -37
[5 empty] | 2019-02-27 | 40 | 1388 | 3038 | -37 | 0 | 0 | 3075 | 2696.2077 | 2696.2077 | 2696.2077 | 2321.8467 | 780 | 200 | 3301.8467 | 82.55% | 95% | 0% | -42.3341 | 2653.8737 | -2750 | -200 | -296.1263 | 7.403% | 82.02% | 95% | 0% | 3075 | -37
[5 empty] | 2019-02-27 | 41 | 1388.5 | 2979 | -36 | 0 | 0 | 3015 | 2602.2259 | 2602.2259 | 2602.2259 | 2321.8467 | 780 | 200 | 3301.8467 | 82.55% | 95% | 0% | -41.1899 | 2561.036 | -2750 | -200 | -388.964 | 9.724% | 82.02% | 95% | 0% | 3015 | -36
[5 empty] | 2019-02-27 | 42 | 1389 | 2883 | -36 | 0 | 0 | 2919 | 2451.8549 | 2451.8549 | 2451.8549 | 2321.8467 | 780 | 200 | 3301.8467 | 82.55% | 95% | 0% | -41.1899 | 2410.665 | -2750 | -200 | -539.335 | 13.48% | 82.01% | 95% | 0% | 2919 | -36
[5 empty] | 2019-02-27 | 43 | 1389.5 | 2760 | -36 | 0 | 0 | 2796 | 2259.1921 | 2259.1921 | 2259.1921 | 2321.8467 | 780 | 200 | 3301.8467 | 82.55% | 95% | 0% | -41.1899 | 2218.0022 | -2750 | -200 | -731.9978 | 18.3% | 82.01% | 95% | 0% | 2796 | -36
[5 empty] | 2019-02-27 | 44 | 1390 | 2602 | -36 | 0 | 0 | 2638 | 2011.7065 | 2011.7065 | 2011.7065 | 2320.2803 | 780 | 200 | 3300.2803 | 82.51% | 95% | 0% | -41.1899 | 1970.5166 | -2750 | -200 | -979.4834 | 24.49% | 82.01% | 95% | 0% | 2638 | -36
[5 empty] | 2019-02-27 | 45 | 1390.5 | 2444 | -37 | 0 | 0 | 2481 | 1765.7873 | 1765.7873 | 1765.7873 | 2320.2803 | 780 | 200 | 3300.2803 | 82.51% | 95% | 0% | -42.3341 | 1723.4532 | -2750 | -200 | -1226.5468 | 30.66% | 82.01% | 95% | 0% | 2481 | -37
[5 empty] | 2019-02-27 | 46 | 1391 | 2304 | -38 | 0 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 2320.2803 | 780 | 200 | 3300.2803 | 82.51% | 95% | 0% | -43.4783 | 1504.5844 | -2750 | -200 | -1445.4156 | 36.14% | 82% | 95% | 0% | 2342 | -38
[5 empty] | 2019-02-27 | 47 | 1391.5 | 2154 | -36 | 0 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 2320.2803 | 780 | 200 | 3300.2803 | 82.51% | 95% | 0% | -41.1899 | 1268.7853 | -2750 | -200 | -1681.2147 | 42.03% | 81.99% | 95% | 0% | 2190 | -36
[5 empty] | 2019-02-27 | 48 | 1392 | 2069 | -34 | 0 | 0 | 2103 | 1173.7016 | 1173.7016 | 1173.7016 | 2320.2803 | 780 | 200 | 3300.2803 | 82.51% | 95% | 0% | -38.9016 | 1134.8 | -2750 | -200 | -1815.2 | 45.38% | 81.99% | 95% | 0% | 2103 | -34
[5 empty] | 2019-02-28 | 1 | 1392.5 | 2043 | -36 | 0 | 0 | 2079 | 1136.1088 | 1136.1088 | 1136.1088 | 2320.2803 | 780 | 200 | 3300.2803 | 82.51% | 95% | 0% | -41.1899 | 1094.9189 | -2750 | -200 | -1855.0811 | 46.38% | 81.99% | 95% | 0% | 2079 | -36
[5 empty] | 2019-02-28 | 2 | 1393 | 2048 | -37 | 0 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 2320.2803 | 780 | 200 | 3300.2803 | 82.51% | 95% | 0% | -42.3341 | 1103.1729 | -2750 | -200 | -1846.8271 | 46.17% | 81.97% | 95% | 0% | 2085 | -37
[5 empty] | 2019-02-28 | 3 | 1393.5 | 2017 | -39 | 0 | 0 | 2056 | 1100.0824 | 1100.0824 | 1100.0824 | 2320.2803 | 780 | 200 | 3300.2803 | 82.51% | 95% | 0% | -44.6224 | 1055.46 | -2750 | -200 | -1894.54 | 47.36% | 81.97% | 95% | 0% | 2056 | -39
[5 empty] | 2019-02-28 | 4 | 1394 | 1966 | -41 | 0 | 0 | 2007 | 1023.3306 | 1023.3306 | 1023.3306 | 2320.2803 | 780 | 200 | 3300.2803 | 82.51% | 95% | 0% | -46.9108 | 976.4198 | -2750 | -200 | -1973.5802 | 49.34% | 81.95% | 95% | 0% | 2007 | -41
[5 empty] | 2019-02-28 | 5 | 1394.5 | 1921 | -42 | 0 | 0 | 1963 | 954.4106 | 954.4106 | 954.4106 | 2320.2803 | 780 | 200 | 3300.2803 | 82.51% | 95% | 0% | -48.0549 | 906.3556 | -2750 | -200 | -2043.6444 | 51.09% | 81.93% | 95% | 0% | 1963 | -42
[5 empty] | 2019-02-28 | 6 | 1395 | 1893 | -44 | 0 | 0 | 1937 | 913.6851 | 913.6851 | 913.6851 | 2318.7139 | 780 | 200 | 3298.7139 | 82.47% | 95% | 0% | -50.3432 | 863.3418 | -2750 | -200 | -2086.6582 | 52.17% | 81.92% | 95% | 0% | 1937 | -44
[5 empty] | 2019-02-28 | 7 | 1395.5 | 1864 | -46 | 0 | 0 | 1910 | 871.3932 | 871.3932 | 871.3932 | 2318.7139 | 780 | 200 | 3298.7139 | 82.47% | 95% | 0% | -52.6316 | 818.7617 | -2750 | -200 | -2131.2383 | 53.28% | 81.92% | 95% | 0% | 1910 | -46
[5 empty] | 2019-02-28 | 8 | 1396 | 1837 | -49 | 0 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 2318.7139 | 780 | 200 | 3298.7139 | 82.47% | 95% | 0% | -56.0641 | 777.7364 | -2750 | -200 | -2172.2636 | 54.31% | 81.91% | 95% | 0% | 1886 | -49
[5 empty] | 2019-02-28 | 9 | 1396.5 | 1822 | -50 | 0 | 0 | 1872 | 811.8714 | 811.8714 | 811.8714 | 2318.7139 | 780 | 200 | 3298.7139 | 82.47% | 95% | 0% | -57.2082 | 754.6632 | -2750 | -200 | -2195.3368 | 54.88% | 81.91% | 95% | 0% | 1872 | -50
[5 empty] | 2019-02-28 | 10 | 1397 | 1835 | -51 | 0 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 2317.1476 | 780 | 200 | 3297.1476 | 82.43% | 95% | 0% | -58.3524 | 775.4481 | -2750 | -200 | -2174.5519 | 54.36% | 81.9% | 95% | 0% | 1886 | -51
[5 empty] | 2019-02-28 | 11 | 1397.5 | 1902 | -52 | 0 | 0 | 1954 | 940.3133 | 940.3133 | 940.3133 | 2317.1476 | 780 | 200 | 3297.1476 | 82.43% | 95% | 0% | -59.4966 | 880.8167 | -2750 | -200 | -2069.1833 | 51.73% | 81.89% | 95% | 0% | 1954 | -52
[5 empty] | 2019-02-28 | 12 | 1398 | 1996 | -53 | 0 | 0 | 2049 | 1089.1179 | 1089.1179 | 1089.1179 | 2317.1476 | 780 | 200 | 3297.1476 | 82.43% | 95% | 0% | -60.6407 | 1028.4772 | -2750 | -200 | -1921.5228 | 48.04% | 81.89% | 95% | 0% | 2049 | -53
[5 empty] | 2019-02-28 | 13 | 1398.5 | 2249 | -52 | 0 | 0 | 2301 | 1483.8417 | 1483.8417 | 1483.8417 | 2317.1476 | 780 | 200 | 3297.1476 | 82.43% | 95% | 0% | -59.4966 | 1424.3451 | -2750 | -200 | -1525.6549 | 38.14% | 81.87% | 95% | 0% | 2301 | -52
[5 empty] | 2019-02-28 | 14 | 1399 | 2473 | -51 | 0 | 0 | 2524 | 1833.141 | 1833.141 | 1833.141 | 2317.1476 | 780 | 200 | 3297.1476 | 82.43% | 95% | 0% | -58.3524 | 1774.7886 | -2750 | -200 | -1175.2114 | 29.38% | 81.87% | 95% | 0% | 2524 | -51
[5 empty] | 2019-02-28 | 15 | 1399.5 | 2715 | -59 | 1 | 0 | 2774 | 2224.7321 | 2224.7321 | 2224.7321 | 2317.1476 | 780 | 200 | 3297.1476 | 82.43% | 95% | 0% | -67.5057 | 2157.2263 | -3550 | -400 | -1792.7737 | 44.82% | 81.87% | 95% | 0% | 2774 | -59
[5 empty] | 2019-02-28 | 16 | 1400 | 2797 | -81 | 1 | 0 | 2878 | 2387.634 | 2387.634 | 2387.634 | 2315.5812 | 780 | 200 | 3295.5812 | 82.39% | 95% | 0% | -92.6773 | 2294.9566 | -3550 | -400 | -1655.0434 | 41.38% | 81.86% | 95% | 0% | 2878 | -81
[5 empty] | 2019-02-28 | 17 | 1400.5 | 2840 | -105 | 1 | 0 | 2945 | 2492.5804 | 2492.5804 | 2492.5804 | 2315.5812 | 780 | 200 | 3295.5812 | 82.39% | 95% | 0% | -120.1373 | 2372.4431 | -3550 | -400 | -1577.5569 | 39.44% | 81.86% | 95% | 0% | 2945 | -105
[5 empty] | 2019-02-28 | 18 | 1401 | 2800 | -140 | 1 | 0 | 2940 | 2484.7486 | 2484.7486 | 2484.7486 | 2315.5812 | 780 | 200 | 3295.5812 | 82.39% | 95% | 0% | -160.1831 | 2324.5655 | -3550 | -400 | -1625.4345 | 40.64% | 81.85% | 95% | 0% | 2940 | -140
[5 empty] | 2019-02-28 | 19 | 1401.5 | 2788 | -179 | 1 | 0 | 2967 | 2527.0404 | 2527.0404 | 2527.0404 | 2315.5812 | 780 | 200 | 3295.5812 | 82.39% | 95% | 0% | -204.8055 | 2322.2349 | -3550 | -400 | -1627.7651 | 40.69% | 81.85% | 95% | 0% | 2967 | -179
[5 empty] | 2019-02-28 | 20 | 1402 | 2790 | -176 | 1 | 0 | 2966 | 2525.474 | 2525.474 | 2525.474 | 2315.5812 | 780 | 200 | 3295.5812 | 82.39% | 95% | 0% | -201.373 | 2324.101 | -3550 | -400 | -1625.899 | 40.65% | 81.84% | 95% | 0% | 2966 | -176
[5 empty] | 2019-02-28 | 21 | 1402.5 | 2759 | -191 | 1 | 0 | 2950 | 2500.4122 | 2500.4122 | 2500.4122 | 2315.5812 | 780 | 200 | 3295.5812 | 82.39% | 95% | 0% | -218.5355 | 2281.8767 | -3550 | -400 | -1668.1233 | 41.7% | 81.84% | 95% | 0% | 2950 | -191
[5 empty] | 2019-02-28 | 22 | 1403 | 2734 | -203 | 1 | 0 | 2937 | 2480.0495 | 2480.0495 | 2480.0495 | 2315.5812 | 780 | 200 | 3295.5812 | 82.39% | 95% | 0% | -232.2654 | 2247.784 | -3550 | -400 | -1702.216 | 42.56% | 81.82% | 95% | 0% | 2937 | -203
[5 empty] | 2019-02-28 | 23 | 1403.5 | 2723 | -222 | 1 | 0 | 2945 | 2492.5804 | 2492.5804 | 2492.5804 | 2315.5812 | 780 | 200 | 3295.5812 | 82.39% | 95% | 0% | -254.0046 | 2238.5758 | -3550 | -400 | -1711.4242 | 42.79% | 81.82% | 95% | 0% | 2945 | -222
[5 empty] | 2019-02-28 | 24 | 1404 | 2706 | -237 | 1 | 0 | 2943 | 2489.4477 | 2489.4477 | 2489.4477 | 2315.5812 | 780 | 200 | 3295.5812 | 82.39% | 95% | 0% | -271.167 | 2218.2806 | -3550 | -400 | -1731.7194 | 43.29% | 81.81% | 95% | 0% | 2943 | -237
[5 empty] | 2019-02-28 | 25 | 1404.5 | 2719 | -233 | 1 | 0 | 2952 | 2503.5449 | 2503.5449 | 2503.5449 | 2315.5812 | 780 | 200 | 3295.5812 | 82.39% | 95% | 0% | -266.5904 | 2236.9545 | -3550 | -400 | -1713.0455 | 42.83% | 81.81% | 95% | 0% | 2952 | -233
[5 empty] | 2019-02-28 | 26 | 1405 | 2698 | -235 | 1 | 0 | 2933 | 2473.784 | 2473.784 | 2473.784 | 2314.0148 | 780 | 200 | 3294.0148 | 82.35% | 95% | 0% | -268.8787 | 2204.9053 | -3550 | -400 | -1745.0947 | 43.63% | 81.8% | 95% | 0% | 2933 | -235
[5 empty] | 2019-02-28 | 27 | 1405.5 | 2700 | -240 | 1 | 0 | 2940 | 2484.7486 | 2484.7486 | 2484.7486 | 2314.0148 | 780 | 200 | 3294.0148 | 82.35% | 95% | 0% | -274.5995 | 2210.149 | -3550 | -400 | -1739.851 | 43.5% | 81.8% | 95% | 0% | 2940 | -240
[5 empty] | 2019-02-28 | 28 | 1406 | 2684 | -227 | 1 | 0 | 2911 | 2439.324 | 2439.324 | 2439.324 | 2314.0148 | 780 | 200 | 3294.0148 | 82.35% | 95% | 0% | -259.7254 | 2179.5986 | -3550 | -400 | -1770.4014 | 44.26% | 81.8% | 95% | 0% | 2911 | -227
[5 empty] | 2019-02-28 | 29 | 1406.5 | 2708 | -199 | 1 | 0 | 2907 | 2433.0585 | 2433.0585 | 2433.0585 | 2314.0148 | 780 | 200 | 3294.0148 | 82.35% | 95% | 0% | -227.6888 | 2205.3697 | -3550 | -400 | -1744.6303 | 43.62% | 81.8% | 95% | 0% | 2907 | -199
[5 empty] | 2019-02-28 | 30 | 1407 | 2725 | -176 | 1 | 0 | 2901 | 2423.6603 | 2423.6603 | 2423.6603 | 2314.0148 | 780 | 200 | 3294.0148 | 82.35% | 95% | 0% | -201.373 | 2222.2873 | -3550 | -400 | -1727.7127 | 43.19% | 81.78% | 95% | 0% | 2901 | -176
[5 empty] | 2019-02-28 | 31 | 1407.5 | 2743 | -167 | 1 | 0 | 2910 | 2437.7576 | 2437.7576 | 2437.7576 | 2314.0148 | 780 | 200 | 3294.0148 | 82.35% | 95% | 0% | -191.0755 | 2246.6821 | -3550 | -400 | -1703.3179 | 42.58% | 81.78% | 95% | 0% | 2910 | -167
[5 empty] | 2019-02-28 | 32 | 1408 | 2846 | -130 | 1 | 0 | 2976 | 2541.1377 | 2541.1377 | 2541.1377 | 2314.0148 | 780 | 200 | 3294.0148 | 82.35% | 95% | 0% | -148.7414 | 2392.3963 | -3550 | -400 | -1557.6037 | 38.94% | 81.77% | 95% | 0% | 2976 | -130
[5 empty] | 2019-02-28 | 33 | 1408.5 | 2941 | -103 | 1 | 0 | 3044 | 2647.6505 | 2647.6505 | 2647.6505 | 2312.4485 | 780 | 200 | 3292.4485 | 82.31% | 95% | 0% | -117.849 | 2529.8015 | -3550 | -400 | -1420.1985 | 35.5% | 81.77% | 95% | 0% | 3044 | -103
[5 empty] | 2019-02-28 | 34 | 1409 | 3019 | -77 | 1 | 0 | 3096 | 2729.1014 | 2729.1014 | 2729.1014 | 2312.4485 | 780 | 200 | 3292.4485 | 82.31% | 95% | 0% | -88.1007 | 2641.0007 | -3550 | -400 | -1308.9993 | 32.72% | 81.76% | 95% | 0% | 3096 | -77
[5 empty] | 2019-02-28 | 35 | 1409.5 | 3087 | -62 | 1 | 0 | 3149 | 2812.1187 | 2812.1187 | 2812.1187 | 2312.4485 | 780 | 200 | 3292.4485 | 82.31% | 95% | 0% | -70.9382 | 2741.1805 | -3550 | -400 | -1208.8195 | 30.22% | 81.73% | 95% | 0% | 3149 | -62
[5 empty] | 2019-02-28 | 36 | 1410 | 3174 | -58 | 1 | 0 | 3232 | 2942.127 | 2942.127 | 2942.127 | 2312.4485 | 780 | 200 | 3292.4485 | 82.31% | 95% | 0% | -66.3616 | 2875.7654 | -3550 | -400 | -1074.2346 | 26.86% | 81.73% | 95% | 0% | 3232 | -58
[5 empty] | 2019-02-28 | 37 | 1410.5 | 3225 | -58 | 0 | 0 | 3283 | 3022.0115 | 3022.0115 | 3022.0115 | 2310.8821 | 780 | 200 | 3290.8821 | 82.27% | 95% | 0% | -66.3616 | 2955.65 | -2750 | -200 | 5.65 | -0.1412% | 81.71% | 95% | 0% | 3283 | -58
[5 empty] | 2019-02-28 | 38 | 1411 | 3198 | -58 | 0 | 0 | 3256 | 2979.7197 | 2979.7197 | 2979.7197 | 2310.8821 | 780 | 200 | 3290.8821 | 82.27% | 95% | 0% | -66.3616 | 2913.3581 | -2750 | -200 | -36.6419 | 0.916% | 81.71% | 95% | 0% | 3256 | -58
[5 empty] | 2019-02-28 | 39 | 1411.5 | 3166 | -58 | 0 | 0 | 3224 | 2929.596 | 2929.596 | 2929.596 | 2310.8821 | 780 | 200 | 3290.8821 | 82.27% | 95% | 0% | -66.3616 | 2863.2345 | -2750 | -200 | -86.7655 | 2.169% | 81.71% | 95% | 0% | 3224 | -58
[5 empty] | 2019-02-28 | 40 | 1412 | 3115 | -58 | 0 | 0 | 3173 | 2849.7115 | 2849.7115 | 2849.7115 | 2310.8821 | 780 | 200 | 3290.8821 | 82.27% | 95% | 0% | -66.3616 | 2783.3499 | -2750 | -200 | -166.6501 | 4.166% | 81.71% | 95% | 0% | 3173 | -58
[5 empty] | 2019-02-28 | 41 | 1412.5 | 3026 | -58 | 0 | 0 | 3084 | 2710.305 | 2710.305 | 2710.305 | 2310.8821 | 780 | 200 | 3290.8821 | 82.27% | 95% | 0% | -66.3616 | 2643.9435 | -2750 | -200 | -306.0565 | 7.651% | 81.7% | 95% | 0% | 3084 | -58
[5 empty] | 2019-02-28 | 42 | 1413 | 2910 | -57 | 0 | 0 | 2967 | 2527.0404 | 2527.0404 | 2527.0404 | 2310.8821 | 780 | 200 | 3290.8821 | 82.27% | 95% | 0% | -65.2174 | 2461.823 | -2750 | -200 | -488.177 | 12.2% | 81.7% | 95% | 0% | 2967 | -57
[5 empty] | 2019-02-28 | 43 | 1413.5 | 2764 | -56 | 0 | 0 | 2820 | 2296.7848 | 2296.7848 | 2296.7848 | 2310.8821 | 780 | 200 | 3290.8821 | 82.27% | 95% | 0% | -64.0732 | 2232.7116 | -2750 | -200 | -717.2884 | 17.93% | 81.68% | 95% | 0% | 2820 | -56
[5 empty] | 2019-02-28 | 44 | 1414 | 2600 | -55 | 0 | 0 | 2655 | 2038.3347 | 2038.3347 | 2038.3347 | 2309.3157 | 780 | 200 | 3289.3157 | 82.23% | 95% | 0% | -62.9291 | 1975.4056 | -2750 | -200 | -974.5944 | 24.36% | 81.68% | 95% | 0% | 2655 | -55
[5 empty] | 2019-02-28 | 45 | 1414.5 | 2448 | -55 | 0 | 0 | 2503 | 1800.2473 | 1800.2473 | 1800.2473 | 2309.3157 | 780 | 200 | 3289.3157 | 82.23% | 95% | 0% | -62.9291 | 1737.3183 | -2750 | -200 | -1212.6817 | 30.32% | 81.67% | 95% | 0% | 2503 | -55
[5 empty] | 2019-02-28 | 46 | 1415 | 2303 | -54 | 0 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 2309.3157 | 780 | 200 | 3289.3157 | 82.23% | 95% | 0% | -61.7849 | 1509.7732 | -2750 | -200 | -1440.2268 | 36.01% | 81.67% | 95% | 0% | 2357 | -54
[5 empty] | 2019-02-28 | 47 | 1415.5 | 2162 | -51 | 0 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 2309.3157 | 780 | 200 | 3289.3157 | 82.23% | 95% | 0% | -58.3524 | 1287.6492 | -2750 | -200 | -1662.3508 | 41.56% | 81.66% | 95% | 0% | 2213 | -51
[5 empty] | 2019-02-28 | 48 | 1416 | 2072 | -49 | 0 | 0 | 2121 | 1201.8961 | 1201.8961 | 1201.8961 | 2309.3157 | 780 | 200 | 3289.3157 | 82.23% | 95% | 0% | -56.0641 | 1145.8321 | -2750 | -200 | -1804.1679 | 45.1% | 81.65% | 95% | 0% | 2121 | -49
[5 empty] | 2019-03-01 | 1 | 1416.5 | 2038 | -49 | 0 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 2309.3157 | 780 | 200 | 3289.3157 | 82.23% | 95% | 0% | -56.0641 | 1092.5757 | -2750 | -200 | -1857.4243 | 46.44% | 81.64% | 95% | 0% | 2087 | -49
[5 empty] | 2019-03-01 | 2 | 1417 | 2059 | -49 | 0 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 2309.3157 | 780 | 200 | 3289.3157 | 82.23% | 95% | 0% | -56.0641 | 1125.4693 | -2750 | -200 | -1824.5307 | 45.61% | 81.63% | 95% | 0% | 2108 | -49
[5 empty] | 2019-03-01 | 3 | 1417.5 | 2024 | -48 | 0 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 2309.3157 | 780 | 200 | 3289.3157 | 82.23% | 95% | 0% | -54.9199 | 1070.2244 | -2750 | -200 | -1879.7756 | 46.99% | 81.63% | 95% | 0% | 2072 | -48
[5 empty] | 2019-03-01 | 4 | 1418 | 1982 | -47 | 0 | 0 | 2029 | 1057.7906 | 1057.7906 | 1057.7906 | 2309.3157 | 780 | 200 | 3289.3157 | 82.23% | 95% | 0% | -53.7757 | 1004.0149 | -2750 | -200 | -1945.9851 | 48.65% | 81.61% | 95% | 0% | 2029 | -47
[5 empty] | 2019-03-01 | 5 | 1418.5 | 1934 | -46 | 0 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 2307.7494 | 780 | 200 | 3287.7494 | 82.19% | 95% | 0% | -52.6316 | 928.4072 | -2750 | -200 | -2021.5928 | 50.54% | 81.61% | 95% | 0% | 1980 | -46
[5 empty] | 2019-03-01 | 6 | 1419 | 1912 | -46 | 0 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 2307.7494 | 780 | 200 | 3287.7494 | 82.19% | 95% | 0% | -52.6316 | 893.9472 | -2750 | -200 | -2056.0528 | 51.4% | 81.6% | 95% | 0% | 1958 | -46
[5 empty] | 2019-03-01 | 7 | 1419.5 | 1880 | -44 | 0 | 0 | 1924 | 893.3223 | 893.3223 | 893.3223 | 2307.7494 | 780 | 200 | 3287.7494 | 82.19% | 95% | 0% | -50.3432 | 842.9791 | -2750 | -200 | -2107.0209 | 52.68% | 81.59% | 95% | 0% | 1924 | -44
[5 empty] | 2019-03-01 | 8 | 1420 | 1867 | -41 | 0 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 2307.7494 | 780 | 200 | 3287.7494 | 82.19% | 95% | 0% | -46.9108 | 821.3498 | -2750 | -200 | -2128.6502 | 53.22% | 81.59% | 95% | 0% | 1908 | -41
[5 empty] | 2019-03-01 | 9 | 1420.5 | 1855 | -40 | 0 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 2307.7494 | 780 | 200 | 3287.7494 | 82.19% | 95% | 0% | -45.7666 | 802.1312 | -2750 | -200 | -2147.8688 | 53.7% | 81.59% | 95% | 0% | 1895 | -40
[5 empty] | 2019-03-01 | 10 | 1421 | 1877 | -39 | 0 | 0 | 1916 | 880.7914 | 880.7914 | 880.7914 | 2307.7494 | 780 | 200 | 3287.7494 | 82.19% | 95% | 0% | -44.6224 | 836.169 | -2750 | -200 | -2113.831 | 52.85% | 81.59% | 95% | 0% | 1916 | -39
[5 empty] | 2019-03-01 | 11 | 1421.5 | 1952 | -37 | 0 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 2307.7494 | 780 | 200 | 3287.7494 | 82.19% | 95% | 0% | -42.3341 | 952.8019 | -2750 | -200 | -1997.1981 | 49.93% | 81.59% | 95% | 0% | 1989 | -37
[5 empty] | 2019-03-01 | 12 | 1422 | 2056 | -35 | 0 | 0 | 2091 | 1154.9052 | 1154.9052 | 1154.9052 | 2307.7494 | 780 | 200 | 3287.7494 | 82.19% | 95% | 0% | -40.0458 | 1114.8594 | -2750 | -200 | -1835.1406 | 45.88% | 81.58% | 95% | 0% | 2091 | -35
[5 empty] | 2019-03-01 | 13 | 1422.5 | 2308 | -33 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 2307.7494 | 780 | 200 | 3287.7494 | 82.19% | 95% | 0% | -37.7574 | 1508.7389 | -3550 | -400 | -2441.2611 | 61.03% | 81.57% | 95% | 0% | 2341 | -33
[5 empty] | 2019-03-01 | 14 | 1423 | 2527 | -31 | 1 | 0 | 2558 | 1886.3974 | 1886.3974 | 1886.3974 | 2307.7494 | 780 | 200 | 3287.7494 | 82.19% | 95% | 0% | -35.4691 | 1850.9283 | -3550 | -400 | -2099.0717 | 52.48% | 81.57% | 95% | 0% | 2558 | -31
[5 empty] | 2019-03-01 | 15 | 1423.5 | 2774 | -31 | 1 | 0 | 2805 | 2273.2894 | 2273.2894 | 2273.2894 | 2307.7494 | 780 | 200 | 3287.7494 | 82.19% | 95% | 0% | -35.4691 | 2237.8203 | -3550 | -400 | -1712.1797 | 42.8% | 81.56% | 95% | 0% | 2805 | -31
[5 empty] | 2019-03-01 | 16 | 1424 | 2880 | -41 | 1 | 0 | 2921 | 2454.9876 | 2454.9876 | 2454.9876 | 2306.183 | 780 | 200 | 3286.183 | 82.15% | 95% | 0% | -46.9108 | 2408.0769 | -3550 | -400 | -1541.9231 | 38.55% | 81.56% | 95% | 0% | 2921 | -41
[5 empty] | 2019-03-01 | 17 | 1424.5 | 2922 | -56 | 1 | 0 | 2978 | 2544.2704 | 2544.2704 | 2544.2704 | 2306.183 | 780 | 200 | 3286.183 | 82.15% | 95% | 0% | -64.0732 | 2480.1972 | -3550 | -400 | -1469.8028 | 36.75% | 81.55% | 95% | 0% | 2978 | -56
[5 empty] | 2019-03-01 | 18 | 1425 | 2881 | -77 | 1 | 0 | 2958 | 2512.9431 | 2512.9431 | 2512.9431 | 2306.183 | 780 | 200 | 3286.183 | 82.15% | 95% | 0% | -88.1007 | 2424.8424 | -3550 | -400 | -1525.1576 | 38.13% | 81.55% | 95% | 0% | 2958 | -77
[5 empty] | 2019-03-01 | 19 | 1425.5 | 2901 | -104 | 1 | 0 | 3005 | 2586.5622 | 2586.5622 | 2586.5622 | 2306.183 | 780 | 200 | 3286.183 | 82.15% | 95% | 0% | -118.9931 | 2467.5691 | -3550 | -400 | -1482.4309 | 37.06% | 81.55% | 95% | 0% | 3005 | -104
[5 empty] | 2019-03-01 | 20 | 1426 | 2884 | -127 | 1 | 0 | 3011 | 2595.9604 | 2595.9604 | 2595.9604 | 2306.183 | 780 | 200 | 3286.183 | 82.15% | 95% | 0% | -145.3089 | 2450.6515 | -3550 | -400 | -1499.3485 | 37.48% | 81.55% | 95% | 0% | 3011 | -127
[5 empty] | 2019-03-01 | 21 | 1426.5 | 2850 | -144 | 1 | 0 | 2994 | 2569.3322 | 2569.3322 | 2569.3322 | 2306.183 | 780 | 200 | 3286.183 | 82.15% | 95% | 0% | -164.7597 | 2404.5725 | -3550 | -400 | -1545.4275 | 38.64% | 81.54% | 95% | 0% | 2994 | -144
[5 empty] | 2019-03-01 | 22 | 1427 | 2809 | -167 | 1 | 0 | 2976 | 2541.1377 | 2541.1377 | 2541.1377 | 2306.183 | 780 | 200 | 3286.183 | 82.15% | 95% | 0% | -191.0755 | 2350.0622 | -3550 | -400 | -1599.9378 | 40% | 81.53% | 95% | 0% | 2976 | -167
[5 empty] | 2019-03-01 | 23 | 1427.5 | 2784 | -179 | 1 | 0 | 2963 | 2520.7749 | 2520.7749 | 2520.7749 | 2304.6167 | 780 | 200 | 3284.6167 | 82.12% | 95% | 0% | -204.8055 | 2315.9694 | -3550 | -400 | -1634.0306 | 40.85% | 81.52% | 95% | 0% | 2963 | -179
[5 empty] | 2019-03-01 | 24 | 1428 | 2762 | -190 | 1 | 0 | 2952 | 2503.5449 | 2503.5449 | 2503.5449 | 2304.6167 | 780 | 200 | 3284.6167 | 82.12% | 95% | 0% | -217.3913 | 2286.1536 | -3550 | -400 | -1663.8464 | 41.6% | 81.51% | 95% | 0% | 2952 | -190
[5 empty] | 2019-03-01 | 25 | 1428.5 | 2771 | -184 | 1 | 0 | 2955 | 2508.244 | 2508.244 | 2508.244 | 2304.6167 | 780 | 200 | 3284.6167 | 82.12% | 95% | 0% | -210.5263 | 2297.7177 | -3550 | -400 | -1652.2823 | 41.31% | 81.51% | 95% | 0% | 2955 | -184
[5 empty] | 2019-03-01 | 26 | 1429 | 2735 | -193 | 1 | 0 | 2928 | 2465.9522 | 2465.9522 | 2465.9522 | 2304.6167 | 780 | 200 | 3284.6167 | 82.12% | 95% | 0% | -220.8238 | 2245.1284 | -3550 | -400 | -1704.8716 | 42.62% | 81.51% | 95% | 0% | 2928 | -193
[5 empty] | 2019-03-01 | 27 | 1429.5 | 2717 | -190 | 1 | 0 | 2907 | 2433.0585 | 2433.0585 | 2433.0585 | 2304.6167 | 780 | 200 | 3284.6167 | 82.12% | 95% | 0% | -217.3913 | 2215.6672 | -3550 | -400 | -1734.3328 | 43.36% | 81.51% | 95% | 0% | 2907 | -190
[5 empty] | 2019-03-01 | 28 | 1430 | 2701 | -188 | 1 | 0 | 2889 | 2404.864 | 2404.864 | 2404.864 | 2304.6167 | 780 | 200 | 3284.6167 | 82.12% | 95% | 0% | -215.103 | 2189.761 | -3550 | -400 | -1760.239 | 44.01% | 81.5% | 95% | 0% | 2889 | -188
[5 empty] | 2019-03-01 | 29 | 1430.5 | 2687 | -181 | 1 | 0 | 2868 | 2371.9703 | 2371.9703 | 2371.9703 | 2304.6167 | 780 | 200 | 3284.6167 | 82.12% | 95% | 0% | -207.0938 | 2164.8765 | -3550 | -400 | -1785.1235 | 44.63% | 81.48% | 95% | 0% | 2868 | -181
[5 empty] | 2019-03-01 | 30 | 1431 | 2667 | -181 | 1 | 0 | 2848 | 2340.643 | 2340.643 | 2340.643 | 2304.6167 | 780 | 200 | 3284.6167 | 82.12% | 95% | 0% | -207.0938 | 2133.5492 | -3550 | -400 | -1816.4508 | 45.41% | 81.47% | 95% | 0% | 2848 | -181
[5 empty] | 2019-03-01 | 31 | 1431.5 | 2678 | -154 | 1 | 0 | 2832 | 2315.5812 | 2315.5812 | 2315.5812 | 2304.6167 | 780 | 200 | 3284.6167 | 82.12% | 95% | 0% | -176.2014 | 2139.3798 | -3550 | -400 | -1810.6202 | 45.27% | 81.46% | 95% | 0% | 2832 | -154
[5 empty] | 2019-03-01 | 32 | 1432 | 2734 | -129 | 1 | 0 | 2863 | 2364.1385 | 2364.1385 | 2364.1385 | 2304.6167 | 780 | 200 | 3284.6167 | 82.12% | 95% | 0% | -147.5973 | 2216.5412 | -3550 | -400 | -1733.4588 | 43.34% | 81.46% | 95% | 0% | 2863 | -129
[5 empty] | 2019-03-01 | 33 | 1432.5 | 2823 | -106 | 1 | 0 | 2929 | 2467.5185 | 2467.5185 | 2467.5185 | 2303.0503 | 780 | 200 | 3283.0503 | 82.08% | 95% | 0% | -121.2815 | 2346.2371 | -3550 | -400 | -1603.7629 | 40.09% | 81.46% | 95% | 0% | 2929 | -106
[5 empty] | 2019-03-01 | 34 | 1433 | 2921 | -87 | 1 | 0 | 3008 | 2591.2613 | 2591.2613 | 2591.2613 | 2303.0503 | 780 | 200 | 3283.0503 | 82.08% | 95% | 0% | -99.5423 | 2491.719 | -3550 | -400 | -1458.281 | 36.46% | 81.46% | 95% | 0% | 3008 | -87
[5 empty] | 2019-03-01 | 35 | 1433.5 | 3002 | -72 | 1 | 0 | 3074 | 2694.6414 | 2694.6414 | 2694.6414 | 2303.0503 | 780 | 200 | 3283.0503 | 82.08% | 95% | 0% | -82.3799 | 2612.2615 | -3550 | -400 | -1337.7385 | 33.44% | 81.45% | 95% | 0% | 3074 | -72
[5 empty] | 2019-03-01 | 36 | 1434 | 3071 | -68 | 1 | 0 | 3139 | 2796.4551 | 2796.4551 | 2796.4551 | 2303.0503 | 780 | 200 | 3283.0503 | 82.08% | 95% | 0% | -77.8032 | 2718.6519 | -3550 | -400 | -1231.3481 | 30.78% | 81.45% | 95% | 0% | 3139 | -68
[5 empty] | 2019-03-01 | 37 | 1434.5 | 3102 | -71 | 1 | 0 | 3173 | 2849.7115 | 2849.7115 | 2849.7115 | 2303.0503 | 780 | 200 | 3283.0503 | 82.08% | 95% | 0% | -81.2357 | 2768.4758 | -3550 | -400 | -1181.5242 | 29.54% | 81.45% | 95% | 0% | 3173 | -71
[5 empty] | 2019-03-01 | 38 | 1435 | 3082 | -74 | 0 | 0 | 3156 | 2823.0833 | 2823.0833 | 2823.0833 | 2303.0503 | 780 | 200 | 3283.0503 | 82.08% | 95% | 0% | -84.6682 | 2738.4151 | -2750 | -200 | -211.5849 | 5.29% | 81.43% | 95% | 0% | 3156 | -74
[5 empty] | 2019-03-01 | 39 | 1435.5 | 2985 | -76 | 0 | 0 | 3061 | 2674.2786 | 2674.2786 | 2674.2786 | 2303.0503 | 780 | 200 | 3283.0503 | 82.08% | 95% | 0% | -86.9565 | 2587.3221 | -2750 | -200 | -362.6779 | 9.067% | 81.42% | 95% | 0% | 3061 | -76
[5 empty] | 2019-03-01 | 40 | 1436 | 2903 | -78 | 0 | 0 | 2981 | 2548.9695 | 2548.9695 | 2548.9695 | 2303.0503 | 780 | 200 | 3283.0503 | 82.08% | 95% | 0% | -89.2449 | 2459.7246 | -2750 | -200 | -490.2754 | 12.26% | 81.42% | 95% | 0% | 2981 | -78
[5 empty] | 2019-03-01 | 41 | 1436.5 | 2815 | -80 | 0 | 0 | 2895 | 2414.2622 | 2414.2622 | 2414.2622 | 2303.0503 | 780 | 200 | 3283.0503 | 82.08% | 95% | 0% | -91.5332 | 2322.729 | -2750 | -200 | -627.271 | 15.68% | 81.42% | 95% | 0% | 2895 | -80
[5 empty] | 2019-03-01 | 42 | 1437 | 2715 | -83 | 0 | 0 | 2798 | 2262.3248 | 2262.3248 | 2262.3248 | 2301.4839 | 780 | 200 | 3281.4839 | 82.04% | 95% | 0% | -94.9657 | 2167.3591 | -2750 | -200 | -782.6409 | 19.57% | 81.41% | 95% | 0% | 2798 | -83
[5 empty] | 2019-03-01 | 43 | 1437.5 | 2574 | -84 | 0 | 0 | 2658 | 2043.0338 | 2043.0338 | 2043.0338 | 2301.4839 | 780 | 200 | 3281.4839 | 82.04% | 95% | 0% | -96.1098 | 1946.924 | -2750 | -200 | -1003.076 | 25.08% | 81.4% | 95% | 0% | 2658 | -84
[5 empty] | 2019-03-01 | 44 | 1438 | 2412 | -85 | 0 | 0 | 2497 | 1790.8491 | 1790.8491 | 1790.8491 | 2301.4839 | 780 | 200 | 3281.4839 | 82.04% | 95% | 0% | -97.254 | 1693.5951 | -2750 | -200 | -1256.4049 | 31.41% | 81.39% | 95% | 0% | 2497 | -85
[5 empty] | 2019-03-01 | 45 | 1438.5 | 2276 | -86 | 0 | 0 | 2362 | 1579.3899 | 1579.3899 | 1579.3899 | 2301.4839 | 780 | 200 | 3281.4839 | 82.04% | 95% | 0% | -98.3982 | 1480.9918 | -2750 | -200 | -1469.0082 | 36.73% | 81.39% | 95% | 0% | 2362 | -86
[5 empty] | 2019-03-01 | 46 | 1439 | 2163 | -87 | 0 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 2301.4839 | 780 | 200 | 3281.4839 | 82.04% | 95% | 0% | -99.5423 | 1304.4148 | -2750 | -200 | -1645.5852 | 41.14% | 81.38% | 95% | 0% | 2250 | -87
[5 empty] | 2019-03-01 | 47 | 1439.5 | 2034 | -91 | 0 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 2301.4839 | 780 | 200 | 3281.4839 | 82.04% | 95% | 0% | -104.119 | 1104.0426 | -2750 | -200 | -1845.9574 | 46.15% | 81.38% | 95% | 0% | 2125 | -91
[5 empty] | 2019-03-01 | 48 | 1440 | 1946 | -95 | 0 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 2301.4839 | 780 | 200 | 3281.4839 | 82.04% | 95% | 0% | -108.6957 | 967.8913 | -2750 | -200 | -1982.1087 | 49.55% | 81.37% | 95% | 0% | 2041 | -95
[5 empty] | 2019-03-02 | 1 | 1440.5 | 1935 | -94 | 0 | 0 | 2029 | 1057.7906 | 1057.7906 | 1057.7906 | 2301.4839 | 780 | 200 | 3281.4839 | 82.04% | 95% | 0% | -107.5515 | 950.2391 | -2750 | -200 | -1999.7609 | 49.99% | 81.36% | 95% | 0% | 2029 | -94
[5 empty] | 2019-03-02 | 2 | 1441 | 1941 | -92 | 0 | 0 | 2033 | 1064.0561 | 1064.0561 | 1064.0561 | 2299.9176 | 780 | 200 | 3279.9176 | 82% | 95% | 0% | -105.2632 | 958.7929 | -2750 | -200 | -1991.2071 | 49.78% | 81.36% | 95% | 0% | 2033 | -92
[5 empty] | 2019-03-02 | 3 | 1441.5 | 1901 | -90 | 0 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 2299.9176 | 780 | 200 | 3279.9176 | 82% | 95% | 0% | -102.9748 | 895.2939 | -2750 | -200 | -2054.7061 | 51.37% | 81.34% | 95% | 0% | 1991 | -90
[5 empty] | 2019-03-02 | 4 | 1442 | 1837 | -88 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 2299.9176 | 780 | 200 | 3279.9176 | 82% | 95% | 0% | -100.6865 | 794.2022 | -2750 | -200 | -2155.7978 | 53.89% | 81.34% | 95% | 0% | 1925 | -88
[5 empty] | 2019-03-02 | 5 | 1442.5 | 1794 | -86 | 0 | 0 | 1880 | 824.4023 | 824.4023 | 824.4023 | 2299.9176 | 780 | 200 | 3279.9176 | 82% | 95% | 0% | -98.3982 | 726.0041 | -2750 | -200 | -2223.9959 | 55.6% | 81.33% | 95% | 0% | 1880 | -86
[5 empty] | 2019-03-02 | 6 | 1443 | 1768 | -84 | 0 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 2298.3512 | 780 | 200 | 3278.3512 | 81.96% | 95% | 0% | -96.1098 | 684.4343 | -2750 | -200 | -2265.5657 | 56.64% | 81.33% | 95% | 0% | 1852 | -84
[5 empty] | 2019-03-02 | 7 | 1443.5 | 1727 | -85 | 0 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 2298.3512 | 780 | 200 | 3278.3512 | 81.96% | 95% | 0% | -97.254 | 620.6355 | -2750 | -200 | -2329.3645 | 58.23% | 81.33% | 95% | 0% | 1812 | -85
[5 empty] | 2019-03-02 | 8 | 1444 | 1690 | -86 | 0 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 2298.3512 | 780 | 200 | 3278.3512 | 81.96% | 95% | 0% | -98.3982 | 563.1022 | -2750 | -200 | -2386.8978 | 59.67% | 81.32% | 95% | 0% | 1776 | -86
[5 empty] | 2019-03-02 | 9 | 1444.5 | 1664 | -85 | 0 | 0 | 1749 | 619.2086 | 619.2086 | 619.2086 | 2298.3512 | 780 | 200 | 3278.3512 | 81.96% | 95% | 0% | -97.254 | 521.9546 | -2750 | -200 | -2428.0454 | 60.7% | 81.31% | 95% | 0% | 1749 | -85
[5 empty] | 2019-03-02 | 10 | 1445 | 1671 | -84 | 0 | 0 | 1755 | 628.6068 | 628.6068 | 628.6068 | 2298.3512 | 780 | 200 | 3278.3512 | 81.96% | 95% | 0% | -96.1098 | 532.4969 | -2750 | -200 | -2417.5031 | 60.44% | 81.31% | 95% | 0% | 1755 | -84
[5 empty] | 2019-03-02 | 11 | 1445.5 | 1698 | -83 | 0 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 2298.3512 | 780 | 200 | 3278.3512 | 81.96% | 95% | 0% | -94.9657 | 574.3666 | -2750 | -200 | -2375.6334 | 59.39% | 81.31% | 95% | 0% | 1781 | -83
[5 empty] | 2019-03-02 | 12 | 1446 | 1724 | -83 | 0 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 2298.3512 | 780 | 200 | 3278.3512 | 81.96% | 95% | 0% | -94.9657 | 615.092 | -2750 | -200 | -2334.908 | 58.37% | 81.3% | 95% | 0% | 1807 | -83
[5 empty] | 2019-03-02 | 13 | 1446.5 | 1846 | -82 | 0 | 0 | 1928 | 899.5878 | 899.5878 | 899.5878 | 2296.7848 | 780 | 200 | 3276.7848 | 81.92% | 95% | 0% | -93.8215 | 805.7663 | -2750 | -200 | -2144.2337 | 53.61% | 81.3% | 95% | 0% | 1928 | -82
[5 empty] | 2019-03-02 | 14 | 1447 | 1934 | -80 | 0 | 0 | 2014 | 1034.2951 | 1034.2951 | 1034.2951 | 2296.7848 | 780 | 200 | 3276.7848 | 81.92% | 95% | 0% | -91.5332 | 942.762 | -2750 | -200 | -2007.238 | 50.18% | 81.29% | 95% | 0% | 2014 | -80
[5 empty] | 2019-03-02 | 15 | 1447.5 | 1997 | -84 | 0 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 2296.7848 | 780 | 200 | 3276.7848 | 81.92% | 95% | 0% | -96.1098 | 1043.1317 | -2750 | -200 | -1906.8683 | 47.67% | 81.28% | 95% | 0% | 2081 | -84
[5 empty] | 2019-03-02 | 16 | 1448 | 2032 | -105 | 0 | 0 | 2137 | 1226.958 | 1226.958 | 1226.958 | 2296.7848 | 780 | 200 | 3276.7848 | 81.92% | 95% | 0% | -120.1373 | 1106.8207 | -2750 | -200 | -1843.1793 | 46.08% | 81.27% | 95% | 0% | 2137 | -105
[5 empty] | 2019-03-02 | 17 | 1448.5 | 2091 | -144 | 0 | 0 | 2235 | 1380.4617 | 1380.4617 | 1380.4617 | 2296.7848 | 780 | 200 | 3276.7848 | 81.92% | 95% | 0% | -164.7597 | 1215.7019 | -2750 | -200 | -1734.2981 | 43.36% | 81.27% | 95% | 0% | 2235 | -144
[5 empty] | 2019-03-02 | 18 | 1449 | 2135 | -180 | 1 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 2296.7848 | 780 | 200 | 3276.7848 | 81.92% | 95% | 0% | -205.9497 | 1299.8212 | -3550 | -400 | -2650.1788 | 66.25% | 81.26% | 95% | 0% | 2315 | -180
[5 empty] | 2019-03-02 | 19 | 1449.5 | 2125 | -234 | 1 | 0 | 2359 | 1574.6908 | 1574.6908 | 1574.6908 | 2296.7848 | 780 | 200 | 3276.7848 | 81.92% | 95% | 0% | -267.7346 | 1306.9563 | -3550 | -400 | -2643.0437 | 66.08% | 81.26% | 95% | 0% | 2359 | -234
[5 empty] | 2019-03-02 | 20 | 1450 | 2078 | -261 | 1 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 2296.7848 | 780 | 200 | 3276.7848 | 81.92% | 95% | 0% | -298.627 | 1244.7366 | -3550 | -400 | -2705.2634 | 67.63% | 81.25% | 95% | 0% | 2339 | -261
[5 empty] | 2019-03-02 | 21 | 1450.5 | 2014 | -332 | 1 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 2296.7848 | 780 | 200 | 3276.7848 | 81.92% | 95% | 0% | -379.8627 | 1174.4654 | -3550 | -400 | -2775.5346 | 69.39% | 81.24% | 95% | 0% | 2346 | -332
[5 empty] | 2019-03-02 | 22 | 1451 | 1937 | -392 | 1 | 0 | 2329 | 1527.6999 | 1527.6999 | 1527.6999 | 2296.7848 | 780 | 200 | 3276.7848 | 81.92% | 95% | 0% | -448.5126 | 1079.1873 | -3550 | -400 | -2870.8127 | 71.77% | 81.23% | 95% | 0% | 2329 | -392
[5 empty] | 2019-03-02 | 23 | 1451.5 | 1871 | -436 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 2295.2185 | 780 | 200 | 3275.2185 | 81.88% | 95% | 0% | -498.8558 | 994.3841 | -3550 | -400 | -2955.6159 | 73.89% | 81.23% | 95% | 0% | 2307 | -436
[5 empty] | 2019-03-02 | 24 | 1452 | 1770 | -496 | 1 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 2295.2185 | 780 | 200 | 3275.2185 | 81.88% | 95% | 0% | -567.5057 | 861.5132 | -3550 | -400 | -3088.4868 | 77.21% | 81.21% | 95% | 0% | 2266 | -496
[5 empty] | 2019-03-02 | 25 | 1452.5 | 1702 | -527 | 1 | 0 | 2229 | 1371.0635 | 1371.0635 | 1371.0635 | 2295.2185 | 780 | 200 | 3275.2185 | 81.88% | 95% | 0% | -602.9748 | 768.0887 | -3550 | -400 | -3181.9113 | 79.55% | 81.2% | 95% | 0% | 2229 | -527
[5 empty] | 2019-03-02 | 26 | 1453 | 1668 | -513 | 1 | 0 | 2181 | 1295.878 | 1295.878 | 1295.878 | 2295.2185 | 780 | 200 | 3275.2185 | 81.88% | 95% | 0% | -586.9565 | 708.9215 | -3550 | -400 | -3241.0785 | 81.03% | 81.19% | 95% | 0% | 2181 | -513
[5 empty] | 2019-03-02 | 27 | 1453.5 | 1668 | -491 | 1 | 0 | 2159 | 1261.418 | 1261.418 | 1261.418 | 2295.2185 | 780 | 200 | 3275.2185 | 81.88% | 95% | 0% | -561.7849 | 699.6331 | -3550 | -400 | -3250.3669 | 81.26% | 81.19% | 95% | 0% | 2159 | -491
[5 empty] | 2019-03-02 | 28 | 1454 | 1746 | -417 | 1 | 0 | 2163 | 1267.6834 | 1267.6834 | 1267.6834 | 2295.2185 | 780 | 200 | 3275.2185 | 81.88% | 95% | 0% | -477.1167 | 790.5667 | -3550 | -400 | -3159.4333 | 78.99% | 81.18% | 95% | 0% | 2163 | -417
[5 empty] | 2019-03-02 | 29 | 1454.5 | 1799 | -366 | 1 | 0 | 2165 | 1270.8162 | 1270.8162 | 1270.8162 | 2295.2185 | 780 | 200 | 3275.2185 | 81.88% | 95% | 0% | -418.7643 | 852.0519 | -3550 | -400 | -3097.9481 | 77.45% | 81.18% | 95% | 0% | 2165 | -366
[5 empty] | 2019-03-02 | 30 | 1455 | 1852 | -324 | 1 | 0 | 2176 | 1288.0462 | 1288.0462 | 1288.0462 | 2295.2185 | 780 | 200 | 3275.2185 | 81.88% | 95% | 0% | -370.7094 | 917.3368 | -3550 | -400 | -3032.6632 | 75.82% | 81.18% | 95% | 0% | 2176 | -324
[5 empty] | 2019-03-02 | 31 | 1455.5 | 1922 | -286 | 1 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 2295.2185 | 780 | 200 | 3275.2185 | 81.88% | 95% | 0% | -327.2311 | 1010.9387 | -3550 | -400 | -2939.0613 | 73.48% | 81.18% | 95% | 0% | 2208 | -286
[5 empty] | 2019-03-02 | 32 | 1456 | 1967 | -271 | 1 | 0 | 2238 | 1385.1608 | 1385.1608 | 1385.1608 | 2293.6521 | 780 | 200 | 3273.6521 | 81.84% | 95% | 0% | -310.0686 | 1075.0921 | -3550 | -400 | -2874.9079 | 71.87% | 81.18% | 95% | 0% | 2238 | -271
[5 empty] | 2019-03-02 | 33 | 1456.5 | 2065 | -249 | 1 | 0 | 2314 | 1504.2045 | 1504.2045 | 1504.2045 | 2293.6521 | 780 | 200 | 3273.6521 | 81.84% | 95% | 0% | -284.897 | 1219.3074 | -3550 | -400 | -2730.6926 | 68.27% | 81.17% | 95% | 0% | 2314 | -249
[5 empty] | 2019-03-02 | 34 | 1457 | 2154 | -242 | 1 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 2293.6521 | 780 | 200 | 3273.6521 | 81.84% | 95% | 0% | -276.8879 | 1355.7585 | -3550 | -400 | -2594.2415 | 64.86% | 81.17% | 95% | 0% | 2396 | -242
[5 empty] | 2019-03-02 | 35 | 1457.5 | 2284 | -232 | 1 | 0 | 2516 | 1820.6101 | 1820.6101 | 1820.6101 | 2293.6521 | 780 | 200 | 3273.6521 | 81.84% | 95% | 0% | -265.4462 | 1555.1638 | -3550 | -400 | -2394.8362 | 59.87% | 81.16% | 95% | 0% | 2516 | -232
[5 empty] | 2019-03-02 | 36 | 1458 | 2361 | -231 | 1 | 0 | 2592 | 1939.6538 | 1939.6538 | 1939.6538 | 2293.6521 | 780 | 200 | 3273.6521 | 81.84% | 95% | 0% | -264.3021 | 1675.3517 | -3550 | -400 | -2274.6483 | 56.87% | 81.16% | 95% | 0% | 2592 | -231
[5 empty] | 2019-03-02 | 37 | 1458.5 | 2390 | -231 | 1 | 0 | 2621 | 1985.0783 | 1985.0783 | 1985.0783 | 2293.6521 | 780 | 200 | 3273.6521 | 81.84% | 95% | 0% | -264.3021 | 1720.7763 | -3550 | -400 | -2229.2237 | 55.73% | 81.16% | 95% | 0% | 2621 | -231
[5 empty] | 2019-03-02 | 38 | 1459 | 2355 | -232 | 1 | 0 | 2587 | 1931.8219 | 1931.8219 | 1931.8219 | 2293.6521 | 780 | 200 | 3273.6521 | 81.84% | 95% | 0% | -265.4462 | 1666.3757 | -3550 | -400 | -2283.6243 | 57.09% | 81.16% | 95% | 0% | 2587 | -232
[5 empty] | 2019-03-02 | 39 | 1459.5 | 2315 | -233 | 0 | 0 | 2548 | 1870.7337 | 1870.7337 | 1870.7337 | 2293.6521 | 780 | 200 | 3273.6521 | 81.84% | 95% | 0% | -266.5904 | 1604.1433 | -2750 | -200 | -1345.8567 | 33.65% | 81.16% | 95% | 0% | 2548 | -233
[5 empty] | 2019-03-02 | 40 | 1460 | 2255 | -233 | 0 | 0 | 2488 | 1776.7519 | 1776.7519 | 1776.7519 | 2293.6521 | 780 | 200 | 3273.6521 | 81.84% | 95% | 0% | -266.5904 | 1510.1615 | -2750 | -200 | -1439.8385 | 36% | 81.16% | 95% | 0% | 2488 | -233
[5 empty] | 2019-03-02 | 41 | 1460.5 | 2173 | -227 | 0 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 2292.0857 | 780 | 200 | 3272.0857 | 81.8% | 95% | 0% | -259.7254 | 1379.1864 | -2750 | -200 | -1570.8136 | 39.27% | 81.15% | 95% | 0% | 2400 | -227
[5 empty] | 2019-03-02 | 42 | 1461 | 2075 | -221 | 0 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 2292.0857 | 780 | 200 | 3272.0857 | 81.8% | 95% | 0% | -252.8604 | 1223.1495 | -2750 | -200 | -1726.8505 | 43.17% | 81.14% | 95% | 0% | 2296 | -221
[5 empty] | 2019-03-02 | 43 | 1461.5 | 1978 | -219 | 0 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 2292.0857 | 780 | 200 | 3272.0857 | 81.8% | 95% | 0% | -250.5721 | 1070.3677 | -2750 | -200 | -1879.6323 | 46.99% | 81.14% | 95% | 0% | 2197 | -219
[5 empty] | 2019-03-02 | 44 | 1462 | 1881 | -216 | 0 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 2292.0857 | 780 | 200 | 3272.0857 | 81.8% | 95% | 0% | -247.1396 | 917.1638 | -2750 | -200 | -2032.8362 | 50.82% | 81.14% | 95% | 0% | 2097 | -216
[5 empty] | 2019-03-02 | 45 | 1462.5 | 1771 | -214 | 0 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 2292.0857 | 780 | 200 | 3272.0857 | 81.8% | 95% | 0% | -244.8513 | 744.0193 | -2750 | -200 | -2205.9807 | 55.15% | 81.12% | 95% | 0% | 1985 | -214
[5 empty] | 2019-03-02 | 46 | 1463 | 1685 | -212 | 0 | 0 | 1897 | 851.0305 | 851.0305 | 851.0305 | 2292.0857 | 780 | 200 | 3272.0857 | 81.8% | 95% | 0% | -242.5629 | 608.4676 | -2750 | -200 | -2341.5324 | 58.54% | 81.12% | 95% | 0% | 1897 | -212
[5 empty] | 2019-03-02 | 47 | 1463.5 | 1574 | -218 | 0 | 0 | 1792 | 686.5622 | 686.5622 | 686.5622 | 2292.0857 | 780 | 200 | 3272.0857 | 81.8% | 95% | 0% | -249.4279 | 437.1343 | -2750 | -200 | -2512.8657 | 62.82% | 81.12% | 95% | 0% | 1792 | -218
[5 empty] | 2019-03-02 | 48 | 1464 | 1504 | -223 | 0 | 0 | 1727 | 584.7486 | 584.7486 | 584.7486 | 2292.0857 | 780 | 200 | 3272.0857 | 81.8% | 95% | 0% | -255.1487 | 329.5998 | -2750 | -200 | -2620.4002 | 65.51% | 81.11% | 95% | 0% | 1727 | -223
[5 empty] | 2019-03-03 | 1 | 1464.5 | 1481 | -223 | 0 | 0 | 1704 | 548.7222 | 548.7222 | 548.7222 | 2290.5194 | 780 | 200 | 3270.5194 | 81.76% | 95% | 0% | -255.1487 | 293.5734 | -2750 | -200 | -2656.4266 | 66.41% | 81.11% | 95% | 0% | 1704 | -223
[5 empty] | 2019-03-03 | 2 | 1465 | 1502 | -222 | 0 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 2290.5194 | 780 | 200 | 3270.5194 | 81.76% | 95% | 0% | -254.0046 | 326.0449 | -2750 | -200 | -2623.9551 | 65.6% | 81.11% | 95% | 0% | 1724 | -222
[5 empty] | 2019-03-03 | 3 | 1465.5 | 1481 | -219 | 0 | 0 | 1700 | 542.4567 | 542.4567 | 542.4567 | 2290.5194 | 780 | 200 | 3270.5194 | 81.76% | 95% | 0% | -250.5721 | 291.8846 | -2750 | -200 | -2658.1154 | 66.45% | 81.11% | 95% | 0% | 1700 | -219
[5 empty] | 2019-03-03 | 4 | 1466 | 1428 | -217 | 0 | 0 | 1645 | 456.3067 | 456.3067 | 456.3067 | 2288.953 | 780 | 200 | 3268.953 | 81.72% | 95% | 0% | -248.2838 | 208.0229 | -2750 | -200 | -2741.9771 | 68.55% | 81.11% | 95% | 0% | 1645 | -217
[5 empty] | 2019-03-03 | 5 | 1466.5 | 1384 | -215 | 0 | 0 | 1599 | 384.2539 | 384.2539 | 384.2539 | 2288.953 | 780 | 200 | 3268.953 | 81.72% | 95% | 0% | -245.9954 | 138.2585 | -2750 | -200 | -2811.7415 | 70.29% | 81.11% | 95% | 0% | 1599 | -215
[5 empty] | 2019-03-03 | 6 | 1467 | 1357 | -213 | 0 | 0 | 1570 | 338.8293 | 338.8293 | 338.8293 | 2288.953 | 780 | 200 | 3268.953 | 81.72% | 95% | 0% | -243.7071 | 95.1223 | -2750 | -200 | -2854.8777 | 71.37% | 81.11% | 95% | 0% | 1570 | -213
[5 empty] | 2019-03-03 | 7 | 1467.5 | 1315 | -209 | 0 | 0 | 1524 | 266.7766 | 266.7766 | 266.7766 | 2288.953 | 780 | 200 | 3268.953 | 81.72% | 95% | 0% | -239.1304 | 27.6462 | -2750 | -200 | -2922.3538 | 73.06% | 81.1% | 95% | 0% | 1524 | -209
[5 empty] | 2019-03-03 | 8 | 1468 | 1283 | -205 | 0 | 0 | 1488 | 210.3875 | 210.3875 | 210.3875 | 2287.3866 | 780 | 200 | 3267.3866 | 81.68% | 95% | 0% | -234.5538 | -24.1663 | -2750 | -200 | -2974.1663 | 74.35% | 81.1% | 95% | 0% | 1488 | -205
[5 empty] | 2019-03-03 | 9 | 1468.5 | 1268 | -204 | 0 | 0 | 1472 | 185.3256 | 185.3256 | 185.3256 | 2287.3866 | 780 | 200 | 3267.3866 | 81.68% | 95% | 0% | -233.4096 | -48.084 | -2750 | -200 | -2998.084 | 74.95% | 81.1% | 95% | 0% | 1472 | -204
[5 empty] | 2019-03-03 | 10 | 1469 | 1267 | -203 | 0 | 0 | 1470 | 182.1929 | 182.1929 | 182.1929 | 2287.3866 | 780 | 200 | 3267.3866 | 81.68% | 95% | 0% | -232.2654 | -50.0725 | -2750 | -200 | -3000.0725 | 75% | 81.1% | 95% | 0% | 1470 | -203
[5 empty] | 2019-03-03 | 11 | 1469.5 | 1282 | -198 | 0 | 0 | 1480 | 197.8566 | 197.8566 | 197.8566 | 2287.3866 | 780 | 200 | 3267.3866 | 81.68% | 95% | 0% | -226.5446 | -28.6881 | -2750 | -200 | -2978.6881 | 74.47% | 81.09% | 95% | 0% | 1480 | -198
[5 empty] | 2019-03-03 | 12 | 1470 | 1326 | -193 | 0 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 2287.3866 | 780 | 200 | 3267.3866 | 81.68% | 95% | 0% | -220.8238 | 38.121 | -2750 | -200 | -2911.879 | 72.8% | 81.09% | 95% | 0% | 1519 | -193
[5 empty] | 2019-03-03 | 13 | 1470.5 | 1412 | -191 | 0 | 0 | 1603 | 390.5194 | 390.5194 | 390.5194 | 2287.3866 | 780 | 200 | 3267.3866 | 81.68% | 95% | 0% | -218.5355 | 171.9839 | -2750 | -200 | -2778.0161 | 69.45% | 81.08% | 95% | 0% | 1603 | -191
[5 empty] | 2019-03-03 | 14 | 1471 | 1466 | -189 | 0 | 0 | 1655 | 471.9703 | 471.9703 | 471.9703 | 2287.3866 | 780 | 200 | 3267.3866 | 81.68% | 95% | 0% | -216.2471 | 255.7232 | -2750 | -200 | -2694.2768 | 67.36% | 81.08% | 95% | 0% | 1655 | -189
[5 empty] | 2019-03-03 | 15 | 1471.5 | 1550 | -187 | 0 | 0 | 1737 | 600.4122 | 600.4122 | 600.4122 | 2287.3866 | 780 | 200 | 3267.3866 | 81.68% | 95% | 0% | -213.9588 | 386.4534 | -2750 | -200 | -2563.5466 | 64.09% | 81.07% | 95% | 0% | 1737 | -187
[5 empty] | 2019-03-03 | 16 | 1472 | 1628 | -194 | 0 | 0 | 1822 | 733.5532 | 733.5532 | 733.5532 | 2285.8203 | 780 | 200 | 3265.8203 | 81.65% | 95% | 0% | -221.968 | 511.5852 | -2750 | -200 | -2438.4148 | 60.96% | 81.07% | 95% | 0% | 1822 | -194
[5 empty] | 2019-03-03 | 17 | 1472.5 | 1752 | -207 | 0 | 0 | 1959 | 948.1451 | 948.1451 | 948.1451 | 2285.8203 | 780 | 200 | 3265.8203 | 81.65% | 95% | 0% | -236.8421 | 711.303 | -2750 | -200 | -2238.697 | 55.97% | 81.07% | 95% | 0% | 1959 | -207
[5 empty] | 2019-03-03 | 18 | 1473 | 1854 | -224 | 1 | 0 | 2078 | 1134.5425 | 1134.5425 | 1134.5425 | 2284.2539 | 780 | 200 | 3264.2539 | 81.61% | 95% | 0% | -256.2929 | 878.2496 | -3550 | -400 | -3071.7504 | 76.79% | 81.07% | 95% | 0% | 2078 | -224
[5 empty] | 2019-03-03 | 19 | 1473.5 | 1964 | -250 | 1 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 2284.2539 | 780 | 200 | 3264.2539 | 81.61% | 95% | 0% | -286.0412 | 1061.5268 | -3550 | -400 | -2888.4732 | 72.21% | 81.06% | 95% | 0% | 2214 | -250
[5 empty] | 2019-03-03 | 20 | 1474 | 2048 | -261 | 1 | 0 | 2309 | 1496.3726 | 1496.3726 | 1496.3726 | 2284.2539 | 780 | 200 | 3264.2539 | 81.61% | 95% | 0% | -298.627 | 1197.7456 | -3550 | -400 | -2752.2544 | 68.81% | 81.06% | 95% | 0% | 2309 | -261
[5 empty] | 2019-03-03 | 21 | 1474.5 | 2082 | -280 | 1 | 0 | 2362 | 1579.3899 | 1579.3899 | 1579.3899 | 2284.2539 | 780 | 200 | 3264.2539 | 81.61% | 95% | 0% | -320.3661 | 1259.0238 | -3550 | -400 | -2690.9762 | 67.27% | 81.05% | 95% | 0% | 2362 | -280
[5 empty] | 2019-03-03 | 22 | 1475 | 2106 | -302 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 2284.2539 | 780 | 200 | 3264.2539 | 81.61% | 95% | 0% | -345.5378 | 1305.9049 | -3550 | -400 | -2644.0951 | 66.1% | 81.03% | 95% | 0% | 2408 | -302
[5 empty] | 2019-03-03 | 23 | 1475.5 | 2162 | -290 | 1 | 0 | 2452 | 1720.3627 | 1720.3627 | 1720.3627 | 2284.2539 | 780 | 200 | 3264.2539 | 81.61% | 95% | 0% | -331.8078 | 1388.555 | -3550 | -400 | -2561.445 | 64.04% | 81.03% | 95% | 0% | 2452 | -290
[5 empty] | 2019-03-03 | 24 | 1476 | 2167 | -296 | 1 | 0 | 2463 | 1737.5927 | 1737.5927 | 1737.5927 | 2282.6876 | 780 | 200 | 3262.6876 | 81.57% | 95% | 0% | -338.6728 | 1398.92 | -3550 | -400 | -2551.08 | 63.78% | 81.03% | 95% | 0% | 2463 | -296
[5 empty] | 2019-03-03 | 25 | 1476.5 | 2174 | -309 | 1 | 0 | 2483 | 1768.92 | 1768.92 | 1768.92 | 2282.6876 | 780 | 200 | 3262.6876 | 81.57% | 95% | 0% | -353.5469 | 1415.3731 | -3550 | -400 | -2534.6269 | 63.37% | 81.02% | 95% | 0% | 2483 | -309
[5 empty] | 2019-03-03 | 26 | 1477 | 2183 | -285 | 1 | 0 | 2468 | 1745.4246 | 1745.4246 | 1745.4246 | 2282.6876 | 780 | 200 | 3262.6876 | 81.57% | 95% | 0% | -326.087 | 1419.3376 | -3550 | -400 | -2530.6624 | 63.27% | 80.99% | 95% | 0% | 2468 | -285
[5 empty] | 2019-03-03 | 27 | 1477.5 | 2192 | -272 | 1 | 0 | 2464 | 1739.1591 | 1739.1591 | 1739.1591 | 2282.6876 | 780 | 200 | 3262.6876 | 81.57% | 95% | 0% | -311.2128 | 1427.9463 | -3550 | -400 | -2522.0537 | 63.05% | 80.98% | 95% | 0% | 2464 | -272
[5 empty] | 2019-03-03 | 28 | 1478 | 2186 | -256 | 1 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 2282.6876 | 780 | 200 | 3262.6876 | 81.57% | 95% | 0% | -292.9062 | 1411.7929 | -3550 | -400 | -2538.2071 | 63.46% | 80.97% | 95% | 0% | 2442 | -256
[5 empty] | 2019-03-03 | 29 | 1478.5 | 2225 | -232 | 1 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 2282.6876 | 780 | 200 | 3262.6876 | 81.57% | 95% | 0% | -265.4462 | 1462.7483 | -3550 | -400 | -2487.2517 | 62.18% | 80.96% | 95% | 0% | 2457 | -232
[5 empty] | 2019-03-03 | 30 | 1479 | 2271 | -206 | 1 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 2282.6876 | 780 | 200 | 3262.6876 | 81.57% | 95% | 0% | -235.6979 | 1523.8239 | -3550 | -400 | -2426.1761 | 60.65% | 80.95% | 95% | 0% | 2477 | -206
[5 empty] | 2019-03-03 | 31 | 1479.5 | 2331 | -197 | 1 | 0 | 2528 | 1839.4064 | 1839.4064 | 1839.4064 | 2282.6876 | 780 | 200 | 3262.6876 | 81.57% | 95% | 0% | -225.4005 | 1614.006 | -3550 | -400 | -2335.994 | 58.4% | 80.95% | 95% | 0% | 2528 | -197
[5 empty] | 2019-03-03 | 32 | 1480 | 2384 | -185 | 1 | 0 | 2569 | 1903.6274 | 1903.6274 | 1903.6274 | 2282.6876 | 780 | 200 | 3262.6876 | 81.57% | 95% | 0% | -211.6705 | 1691.9569 | -3550 | -400 | -2258.0431 | 56.45% | 80.95% | 95% | 0% | 2569 | -185
[5 empty] | 2019-03-03 | 33 | 1480.5 | 2432 | -178 | 1 | 0 | 2610 | 1967.8483 | 1967.8483 | 1967.8483 | 2282.6876 | 780 | 200 | 3262.6876 | 81.57% | 95% | 0% | -203.6613 | 1764.187 | -3550 | -400 | -2185.813 | 54.65% | 80.95% | 95% | 0% | 2610 | -178
[5 empty] | 2019-03-03 | 34 | 1481 | 2504 | -164 | 1 | 0 | 2668 | 2058.6974 | 2058.6974 | 2058.6974 | 2282.6876 | 780 | 200 | 3262.6876 | 81.57% | 95% | 0% | -187.643 | 1871.0544 | -3550 | -400 | -2078.9456 | 51.97% | 80.93% | 95% | 0% | 2668 | -164
[5 empty] | 2019-03-03 | 35 | 1481.5 | 2567 | -155 | 1 | 0 | 2722 | 2143.2811 | 2143.2811 | 2143.2811 | 2282.6876 | 780 | 200 | 3262.6876 | 81.57% | 95% | 0% | -177.3455 | 1965.9356 | -3550 | -400 | -1984.0644 | 49.6% | 80.93% | 95% | 0% | 2722 | -155
[5 empty] | 2019-03-03 | 36 | 1482 | 2619 | -151 | 1 | 0 | 2770 | 2218.4666 | 2218.4666 | 2218.4666 | 2281.1212 | 780 | 200 | 3261.1212 | 81.53% | 95% | 0% | -172.7689 | 2045.6977 | -3550 | -400 | -1904.3023 | 47.61% | 80.93% | 95% | 0% | 2770 | -151
[5 empty] | 2019-03-03 | 37 | 1482.5 | 2684 | -156 | 1 | 0 | 2840 | 2328.1121 | 2328.1121 | 2328.1121 | 2281.1212 | 780 | 200 | 3261.1212 | 81.53% | 95% | 0% | -178.4897 | 2149.6224 | -3550 | -400 | -1800.3776 | 45.01% | 80.92% | 95% | 0% | 2840 | -156
[5 empty] | 2019-03-03 | 38 | 1483 | 2663 | -161 | 0 | 0 | 2824 | 2303.0503 | 2303.0503 | 2303.0503 | 2281.1212 | 780 | 200 | 3261.1212 | 81.53% | 95% | 0% | -184.2105 | 2118.8398 | -2750 | -200 | -831.1602 | 20.78% | 80.92% | 95% | 0% | 2824 | -161
[5 empty] | 2019-03-03 | 39 | 1483.5 | 2599 | -167 | 0 | 0 | 2766 | 2212.2012 | 2212.2012 | 2212.2012 | 2281.1212 | 780 | 200 | 3261.1212 | 81.53% | 95% | 0% | -191.0755 | 2021.1256 | -2750 | -200 | -928.8744 | 23.22% | 80.91% | 95% | 0% | 2766 | -167
[5 empty] | 2019-03-03 | 40 | 1484 | 2508 | -173 | 0 | 0 | 2681 | 2079.0602 | 2079.0602 | 2079.0602 | 2281.1212 | 780 | 200 | 3261.1212 | 81.53% | 95% | 0% | -197.9405 | 1881.1197 | -2750 | -200 | -1068.8803 | 26.72% | 80.91% | 95% | 0% | 2681 | -173
[5 empty] | 2019-03-03 | 41 | 1484.5 | 2453 | -173 | 0 | 0 | 2626 | 1992.9101 | 1992.9101 | 1992.9101 | 2281.1212 | 780 | 200 | 3261.1212 | 81.53% | 95% | 0% | -197.9405 | 1794.9696 | -2750 | -200 | -1155.0304 | 28.88% | 80.91% | 95% | 0% | 2626 | -173
[5 empty] | 2019-03-03 | 42 | 1485 | 2344 | -172 | 0 | 0 | 2516 | 1820.6101 | 1820.6101 | 1820.6101 | 2281.1212 | 780 | 200 | 3261.1212 | 81.53% | 95% | 0% | -196.7963 | 1623.8137 | -2750 | -200 | -1326.1863 | 33.15% | 80.9% | 95% | 0% | 2516 | -172
[5 empty] | 2019-03-03 | 43 | 1485.5 | 2241 | -179 | 0 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 2279.5548 | 780 | 200 | 3259.5548 | 81.49% | 95% | 0% | -204.8055 | 1465.4336 | -2750 | -200 | -1484.5664 | 37.11% | 80.89% | 95% | 0% | 2420 | -179
[5 empty] | 2019-03-03 | 44 | 1486 | 2104 | -185 | 0 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 2279.5548 | 780 | 200 | 3259.5548 | 81.49% | 95% | 0% | -211.6705 | 1253.3749 | -2750 | -200 | -1696.6251 | 42.42% | 80.88% | 95% | 0% | 2289 | -185
[5 empty] | 2019-03-03 | 45 | 1486.5 | 1967 | -186 | 0 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 2279.5548 | 780 | 200 | 3259.5548 | 81.49% | 95% | 0% | -212.8146 | 1039.2051 | -2750 | -200 | -1910.7949 | 47.77% | 80.88% | 95% | 0% | 2153 | -186
[5 empty] | 2019-03-03 | 46 | 1487 | 1853 | -187 | 0 | 0 | 2040 | 1075.0206 | 1075.0206 | 1075.0206 | 2279.5548 | 780 | 200 | 3259.5548 | 81.49% | 95% | 0% | -213.9588 | 861.0618 | -2750 | -200 | -2088.9382 | 52.22% | 80.87% | 95% | 0% | 2040 | -187
[5 empty] | 2019-03-03 | 47 | 1487.5 | 1706 | -185 | 0 | 0 | 1891 | 841.6323 | 841.6323 | 841.6323 | 2279.5548 | 780 | 200 | 3259.5548 | 81.49% | 95% | 0% | -211.6705 | 629.9618 | -2750 | -200 | -2320.0382 | 58% | 80.87% | 95% | 0% | 1891 | -185
[5 empty] | 2019-03-03 | 48 | 1488 | 1632 | -184 | 0 | 0 | 1816 | 724.155 | 724.155 | 724.155 | 2277.9885 | 780 | 200 | 3257.9885 | 81.45% | 95% | 0% | -210.5263 | 513.6287 | -2750 | -200 | -2436.3713 | 60.91% | 80.86% | 95% | 0% | 1816 | -184
[5 empty] | 2019-03-04 | 1 | 1488.5 | 1613 | -180 | 0 | 0 | 1793 | 688.1286 | 688.1286 | 688.1286 | 2277.9885 | 780 | 200 | 3257.9885 | 81.45% | 95% | 0% | -205.9497 | 482.179 | -2750 | -200 | -2467.821 | 61.7% | 80.86% | 95% | 0% | 1793 | -180
[5 empty] | 2019-03-04 | 2 | 1489 | 1643 | -175 | 0 | 0 | 1818 | 727.2877 | 727.2877 | 727.2877 | 2277.9885 | 780 | 200 | 3257.9885 | 81.45% | 95% | 0% | -200.2288 | 527.0589 | -2750 | -200 | -2422.9411 | 60.57% | 80.85% | 95% | 0% | 1818 | -175
[5 empty] | 2019-03-04 | 3 | 1489.5 | 1642 | -172 | 0 | 0 | 1814 | 721.0223 | 721.0223 | 721.0223 | 2277.9885 | 780 | 200 | 3257.9885 | 81.45% | 95% | 0% | -196.7963 | 524.2259 | -2750 | -200 | -2425.7741 | 60.64% | 80.85% | 95% | 0% | 1814 | -172
[5 empty] | 2019-03-04 | 4 | 1490 | 1603 | -170 | 0 | 0 | 1773 | 656.8013 | 656.8013 | 656.8013 | 2276.4221 | 780 | 200 | 3256.4221 | 81.41% | 95% | 0% | -194.508 | 462.2933 | -2750 | -200 | -2487.7067 | 62.19% | 80.85% | 95% | 0% | 1773 | -170
[5 empty] | 2019-03-04 | 5 | 1490.5 | 1575 | -168 | 0 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 2276.4221 | 780 | 200 | 3256.4221 | 81.41% | 95% | 0% | -192.2197 | 417.5907 | -2750 | -200 | -2532.4093 | 63.31% | 80.84% | 95% | 0% | 1743 | -168
[5 empty] | 2019-03-04 | 6 | 1491 | 1555 | -167 | 0 | 0 | 1722 | 576.9167 | 576.9167 | 576.9167 | 2276.4221 | 780 | 200 | 3256.4221 | 81.41% | 95% | 0% | -191.0755 | 385.8412 | -2750 | -200 | -2564.1588 | 64.1% | 80.84% | 95% | 0% | 1722 | -167
[5 empty] | 2019-03-04 | 7 | 1491.5 | 1524 | -168 | 0 | 0 | 1692 | 529.9258 | 529.9258 | 529.9258 | 2276.4221 | 780 | 200 | 3256.4221 | 81.41% | 95% | 0% | -192.2197 | 337.7061 | -2750 | -200 | -2612.2939 | 65.31% | 80.83% | 95% | 0% | 1692 | -168
[5 empty] | 2019-03-04 | 8 | 1492 | 1502 | -168 | 0 | 0 | 1670 | 495.4658 | 495.4658 | 495.4658 | 2276.4221 | 780 | 200 | 3256.4221 | 81.41% | 95% | 0% | -192.2197 | 303.2461 | -2750 | -200 | -2646.7539 | 66.17% | 80.83% | 95% | 0% | 1670 | -168
[5 empty] | 2019-03-04 | 9 | 1492.5 | 1481 | -171 | 0 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 2276.4221 | 780 | 200 | 3256.4221 | 81.41% | 95% | 0% | -195.6522 | 271.6191 | -2750 | -200 | -2678.3809 | 66.96% | 80.82% | 95% | 0% | 1652 | -171
[5 empty] | 2019-03-04 | 10 | 1493 | 1489 | -175 | 0 | 0 | 1664 | 486.0676 | 486.0676 | 486.0676 | 2276.4221 | 780 | 200 | 3256.4221 | 81.41% | 95% | 0% | -200.2288 | 285.8388 | -2750 | -200 | -2664.1612 | 66.6% | 80.82% | 95% | 0% | 1664 | -175
[5 empty] | 2019-03-04 | 11 | 1493.5 | 1574 | -177 | 0 | 0 | 1751 | 622.3413 | 622.3413 | 622.3413 | 2276.4221 | 780 | 200 | 3256.4221 | 81.41% | 95% | 0% | -202.5172 | 419.8241 | -2750 | -200 | -2530.1759 | 63.25% | 80.82% | 95% | 0% | 1751 | -177
[5 empty] | 2019-03-04 | 12 | 1494 | 1681 | -180 | 0 | 0 | 1861 | 794.6414 | 794.6414 | 794.6414 | 2276.4221 | 780 | 200 | 3256.4221 | 81.41% | 95% | 0% | -205.9497 | 588.6917 | -2750 | -200 | -2361.3083 | 59.03% | 80.81% | 95% | 0% | 1861 | -180
[5 empty] | 2019-03-04 | 13 | 1494.5 | 1949 | -182 | 0 | 0 | 2131 | 1217.5598 | 1217.5598 | 1217.5598 | 2276.4221 | 780 | 200 | 3256.4221 | 81.41% | 95% | 0% | -208.238 | 1009.3218 | -2750 | -200 | -1940.6782 | 48.52% | 80.8% | 95% | 0% | 2131 | -182
[5 empty] | 2019-03-04 | 14 | 1495 | 2152 | -184 | 0 | 0 | 2336 | 1538.6645 | 1538.6645 | 1538.6645 | 2276.4221 | 780 | 200 | 3256.4221 | 81.41% | 95% | 0% | -210.5263 | 1328.1382 | -2750 | -200 | -1621.8618 | 40.55% | 80.8% | 95% | 0% | 2336 | -184
[5 empty] | 2019-03-04 | 15 | 1495.5 | 2370 | -201 | 0 | 0 | 2571 | 1906.7601 | 1906.7601 | 1906.7601 | 2274.8557 | 780 | 200 | 3254.8557 | 81.37% | 95% | 0% | -229.9771 | 1676.783 | -2750 | -200 | -1273.217 | 31.83% | 80.79% | 95% | 0% | 2571 | -201
[5 empty] | 2019-03-04 | 16 | 1496 | 2416 | -249 | 0 | 0 | 2665 | 2053.9984 | 2053.9984 | 2053.9984 | 2274.8557 | 780 | 200 | 3254.8557 | 81.37% | 95% | 0% | -284.897 | 1769.1013 | -2750 | -200 | -1180.8987 | 29.52% | 80.78% | 95% | 0% | 2665 | -249
[5 empty] | 2019-03-04 | 17 | 1496.5 | 2380 | -309 | 0 | 0 | 2689 | 2091.5911 | 2091.5911 | 2091.5911 | 2274.8557 | 780 | 200 | 3254.8557 | 81.37% | 95% | 0% | -353.5469 | 1738.0442 | -2750 | -200 | -1211.9558 | 30.3% | 80.78% | 95% | 0% | 2689 | -309
[5 empty] | 2019-03-04 | 18 | 1497 | 2316 | -369 | 1 | 0 | 2685 | 2085.3256 | 2085.3256 | 2085.3256 | 2273.2894 | 780 | 200 | 3253.2894 | 81.33% | 95% | 0% | -422.1968 | 1663.1288 | -3550 | -400 | -2286.8712 | 57.17% | 80.78% | 95% | 0% | 2685 | -369
[5 empty] | 2019-03-04 | 19 | 1497.5 | 2219 | -446 | 1 | 0 | 2665 | 2053.9984 | 2053.9984 | 2053.9984 | 2273.2894 | 780 | 200 | 3253.2894 | 81.33% | 95% | 0% | -510.2975 | 1543.7009 | -3550 | -400 | -2406.2991 | 60.16% | 80.77% | 95% | 0% | 2665 | -446
[5 empty] | 2019-03-04 | 20 | 1498 | 2106 | -516 | 1 | 0 | 2622 | 1986.6447 | 1986.6447 | 1986.6447 | 2273.2894 | 780 | 200 | 3253.2894 | 81.33% | 95% | 0% | -590.389 | 1396.2557 | -3550 | -400 | -2553.7443 | 63.84% | 80.77% | 95% | 0% | 2622 | -516
[5 empty] | 2019-03-04 | 21 | 1498.5 | 1999 | -568 | 1 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 2273.2894 | 780 | 200 | 3253.2894 | 81.33% | 95% | 0% | -649.8856 | 1250.6091 | -3550 | -400 | -2699.3909 | 67.48% | 80.77% | 95% | 0% | 2567 | -568
[5 empty] | 2019-03-04 | 22 | 1499 | 1918 | -611 | 1 | 0 | 2529 | 1840.9728 | 1840.9728 | 1840.9728 | 2273.2894 | 780 | 200 | 3253.2894 | 81.33% | 95% | 0% | -699.0847 | 1141.8881 | -3550 | -400 | -2808.1119 | 70.2% | 80.77% | 95% | 0% | 2529 | -611
[5 empty] | 2019-03-04 | 23 | 1499.5 | 1890 | -622 | 1 | 0 | 2512 | 1814.3446 | 1814.3446 | 1814.3446 | 2273.2894 | 780 | 200 | 3253.2894 | 81.33% | 95% | 0% | -711.6705 | 1102.6741 | -3550 | -400 | -2847.3259 | 71.18% | 80.76% | 95% | 0% | 2512 | -622
[5 empty] | 2019-03-04 | 24 | 1500 | 1902 | -627 | 1 | 0 | 2529 | 1840.9728 | 1840.9728 | 1840.9728 | 2273.2894 | 780 | 200 | 3253.2894 | 81.33% | 95% | 0% | -717.3913 | 1123.5815 | -3550 | -400 | -2826.4185 | 70.66% | 80.75% | 95% | 0% | 2529 | -627
[5 empty] | 2019-03-04 | 25 | 1500.5 | 1960 | -597 | 1 | 0 | 2557 | 1884.831 | 1884.831 | 1884.831 | 2273.2894 | 780 | 200 | 3253.2894 | 81.33% | 95% | 0% | -683.0664 | 1201.7646 | -3550 | -400 | -2748.2354 | 68.71% | 80.74% | 95% | 0% | 2557 | -597
[5 empty] | 2019-03-04 | 26 | 1501 | 1944 | -593 | 1 | 0 | 2537 | 1853.5037 | 1853.5037 | 1853.5037 | 2273.2894 | 780 | 200 | 3253.2894 | 81.33% | 95% | 0% | -678.4897 | 1175.014 | -3550 | -400 | -2774.986 | 69.37% | 80.74% | 95% | 0% | 2537 | -593
[5 empty] | 2019-03-04 | 27 | 1501.5 | 1990 | -549 | 1 | 0 | 2539 | 1856.6364 | 1856.6364 | 1856.6364 | 2273.2894 | 780 | 200 | 3253.2894 | 81.33% | 95% | 0% | -628.1465 | 1228.49 | -3550 | -400 | -2721.51 | 68.04% | 80.74% | 95% | 0% | 2539 | -549
[5 empty] | 2019-03-04 | 28 | 1502 | 2041 | -510 | 1 | 0 | 2551 | 1875.4328 | 1875.4328 | 1875.4328 | 2271.723 | 780 | 200 | 3251.723 | 81.29% | 95% | 0% | -583.524 | 1291.9088 | -3550 | -400 | -2658.0912 | 66.45% | 80.73% | 95% | 0% | 2551 | -510
[5 empty] | 2019-03-04 | 29 | 1502.5 | 2123 | -477 | 1 | 0 | 2600 | 1952.1847 | 1952.1847 | 1952.1847 | 2270.1566 | 780 | 200 | 3250.1566 | 81.25% | 95% | 0% | -545.7666 | 1406.4181 | -3550 | -400 | -2543.5819 | 63.59% | 80.72% | 95% | 0% | 2600 | -477
[5 empty] | 2019-03-04 | 30 | 1503 | 2154 | -456 | 1 | 0 | 2610 | 1967.8483 | 1967.8483 | 1967.8483 | 2270.1566 | 780 | 200 | 3250.1566 | 81.25% | 95% | 0% | -521.7391 | 1446.1092 | -3550 | -400 | -2503.8908 | 62.6% | 80.71% | 95% | 0% | 2610 | -456
[5 empty] | 2019-03-04 | 31 | 1503.5 | 2242 | -387 | 1 | 0 | 2629 | 1997.6092 | 1997.6092 | 1997.6092 | 2270.1566 | 780 | 200 | 3250.1566 | 81.25% | 95% | 0% | -442.7918 | 1554.8175 | -3550 | -400 | -2395.1825 | 59.88% | 80.7% | 95% | 0% | 2629 | -387
[5 empty] | 2019-03-04 | 32 | 1504 | 2391 | -335 | 1 | 0 | 2726 | 2149.5466 | 2149.5466 | 2149.5466 | 2270.1566 | 780 | 200 | 3250.1566 | 81.25% | 95% | 0% | -383.2952 | 1766.2514 | -3550 | -400 | -2183.7486 | 54.59% | 80.7% | 95% | 0% | 2726 | -335
[5 empty] | 2019-03-04 | 33 | 1504.5 | 2553 | -283 | 1 | 0 | 2836 | 2321.8467 | 2321.8467 | 2321.8467 | 2268.5903 | 780 | 200 | 3248.5903 | 81.21% | 95% | 0% | -323.7986 | 1998.048 | -3550 | -400 | -1951.952 | 48.8% | 80.7% | 95% | 0% | 2836 | -283
[5 empty] | 2019-03-04 | 34 | 1505 | 2734 | -228 | 1 | 0 | 2962 | 2519.2086 | 2519.2086 | 2519.2086 | 2268.5903 | 780 | 200 | 3248.5903 | 81.21% | 95% | 0% | -260.8696 | 2258.339 | -3550 | -400 | -1691.661 | 42.29% | 80.7% | 95% | 0% | 2962 | -228
[5 empty] | 2019-03-04 | 35 | 1505.5 | 2886 | -181 | 1 | 0 | 3067 | 2683.6768 | 2683.6768 | 2683.6768 | 2268.5903 | 780 | 200 | 3248.5903 | 81.21% | 95% | 0% | -207.0938 | 2476.583 | -3550 | -400 | -1473.417 | 36.84% | 80.7% | 95% | 0% | 3067 | -181
[5 empty] | 2019-03-04 | 36 | 1506 | 3000 | -161 | 1 | 0 | 3161 | 2830.9151 | 2830.9151 | 2830.9151 | 2268.5903 | 780 | 200 | 3248.5903 | 81.21% | 95% | 0% | -184.2105 | 2646.7046 | -3550 | -400 | -1303.2954 | 32.58% | 80.7% | 95% | 0% | 3161 | -161
[5 empty] | 2019-03-04 | 37 | 1506.5 | 3108 | -160 | 1 | 0 | 3268 | 2998.5161 | 2998.5161 | 2998.5161 | 2268.5903 | 780 | 200 | 3248.5903 | 81.21% | 95% | 0% | -183.0664 | 2815.4497 | -3550 | -400 | -1134.5503 | 28.36% | 80.69% | 95% | 0% | 3268 | -160
[5 empty] | 2019-03-04 | 38 | 1507 | 3094 | -160 | 1 | 0 | 3254 | 2976.587 | 2976.587 | 2976.587 | 2268.5903 | 780 | 200 | 3248.5903 | 81.21% | 95% | 0% | -183.0664 | 2793.5206 | -3550 | -400 | -1156.4794 | 28.91% | 80.69% | 95% | 0% | 3254 | -160
[5 empty] | 2019-03-04 | 39 | 1507.5 | 3024 | -157 | 0 | 0 | 3181 | 2862.2424 | 2862.2424 | 2862.2424 | 2268.5903 | 780 | 200 | 3248.5903 | 81.21% | 95% | 0% | -179.6339 | 2682.6085 | -2750 | -200 | -267.3915 | 6.685% | 80.69% | 95% | 0% | 3181 | -157
[5 empty] | 2019-03-04 | 40 | 1508 | 2943 | -155 | 0 | 0 | 3098 | 2732.2341 | 2732.2341 | 2732.2341 | 2268.5903 | 780 | 200 | 3248.5903 | 81.21% | 95% | 0% | -177.3455 | 2554.8886 | -2750 | -200 | -395.1114 | 9.878% | 80.69% | 95% | 0% | 3098 | -155
[5 empty] | 2019-03-04 | 41 | 1508.5 | 2884 | -152 | 0 | 0 | 3036 | 2635.1195 | 2635.1195 | 2635.1195 | 2267.0239 | 780 | 200 | 3247.0239 | 81.18% | 95% | 0% | -173.913 | 2461.2065 | -2750 | -200 | -488.7935 | 12.22% | 80.69% | 95% | 0% | 3036 | -152
[5 empty] | 2019-03-04 | 42 | 1509 | 2749 | -148 | 0 | 0 | 2897 | 2417.3949 | 2417.3949 | 2417.3949 | 2267.0239 | 780 | 200 | 3247.0239 | 81.18% | 95% | 0% | -169.3364 | 2248.0585 | -2750 | -200 | -701.9415 | 17.55% | 80.69% | 95% | 0% | 2897 | -148
[5 empty] | 2019-03-04 | 43 | 1509.5 | 2605 | -147 | 0 | 0 | 2752 | 2190.2721 | 2190.2721 | 2190.2721 | 2267.0239 | 780 | 200 | 3247.0239 | 81.18% | 95% | 0% | -168.1922 | 2022.0798 | -2750 | -200 | -927.9202 | 23.2% | 80.68% | 95% | 0% | 2752 | -147
[5 empty] | 2019-03-04 | 44 | 1510 | 2438 | -145 | 0 | 0 | 2583 | 1925.5565 | 1925.5565 | 1925.5565 | 2267.0239 | 780 | 200 | 3247.0239 | 81.18% | 95% | 0% | -165.9039 | 1759.6526 | -2750 | -200 | -1190.3474 | 29.76% | 80.68% | 95% | 0% | 2583 | -145
[5 empty] | 2019-03-04 | 45 | 1510.5 | 2276 | -142 | 0 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 2267.0239 | 780 | 200 | 3247.0239 | 81.18% | 95% | 0% | -162.4714 | 1504.635 | -2750 | -200 | -1445.365 | 36.13% | 80.68% | 95% | 0% | 2418 | -142
[5 empty] | 2019-03-04 | 46 | 1511 | 2133 | -139 | 0 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 2267.0239 | 780 | 200 | 3247.0239 | 81.18% | 95% | 0% | -159.0389 | 1279.3782 | -2750 | -200 | -1670.6218 | 41.77% | 80.67% | 95% | 0% | 2272 | -139
[5 empty] | 2019-03-04 | 47 | 1511.5 | 1977 | -137 | 0 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 2267.0239 | 780 | 200 | 3247.0239 | 81.18% | 95% | 0% | -156.7506 | 1034.181 | -2750 | -200 | -1915.819 | 47.9% | 80.67% | 95% | 0% | 2114 | -137
[5 empty] | 2019-03-04 | 48 | 1512 | 1901 | -136 | 0 | 0 | 2037 | 1070.3215 | 1070.3215 | 1070.3215 | 2267.0239 | 780 | 200 | 3247.0239 | 81.18% | 95% | 0% | -155.6064 | 914.7151 | -2750 | -200 | -2035.2849 | 50.88% | 80.66% | 95% | 0% | 2037 | -136
[5 empty] | 2019-03-05 | 1 | 1512.5 | 1885 | -134 | 0 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 2267.0239 | 780 | 200 | 3247.0239 | 81.18% | 95% | 0% | -153.3181 | 888.8089 | -2750 | -200 | -2061.1911 | 51.53% | 80.65% | 95% | 0% | 2019 | -134
[5 empty] | 2019-03-05 | 2 | 1513 | 1925 | -132 | 0 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 2267.0239 | 780 | 200 | 3247.0239 | 81.18% | 95% | 0% | -151.0297 | 950.6191 | -2750 | -200 | -1999.3809 | 49.98% | 80.64% | 95% | 0% | 2057 | -132
[5 empty] | 2019-03-05 | 3 | 1513.5 | 1898 | -128 | 0 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 2267.0239 | 780 | 200 | 3247.0239 | 81.18% | 95% | 0% | -146.4531 | 906.6384 | -2750 | -200 | -2043.3616 | 51.08% | 80.63% | 95% | 0% | 2026 | -128
[5 empty] | 2019-03-05 | 4 | 1514 | 1864 | -124 | 0 | 0 | 1988 | 993.5697 | 993.5697 | 993.5697 | 2267.0239 | 780 | 200 | 3247.0239 | 81.18% | 95% | 0% | -141.8764 | 851.6932 | -2750 | -200 | -2098.3068 | 52.46% | 80.62% | 95% | 0% | 1988 | -124
[5 empty] | 2019-03-05 | 5 | 1514.5 | 1843 | -122 | 0 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 2265.4575 | 780 | 200 | 3245.4575 | 81.14% | 95% | 0% | -139.5881 | 817.9552 | -2750 | -200 | -2132.0448 | 53.3% | 80.6% | 95% | 0% | 1965 | -122
[5 empty] | 2019-03-05 | 6 | 1515 | 1828 | -119 | 0 | 0 | 1947 | 929.3487 | 929.3487 | 929.3487 | 2265.4575 | 780 | 200 | 3245.4575 | 81.14% | 95% | 0% | -136.1556 | 793.1931 | -2750 | -200 | -2156.8069 | 53.92% | 80.6% | 95% | 0% | 1947 | -119
[5 empty] | 2019-03-05 | 7 | 1515.5 | 1808 | -117 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 2265.4575 | 780 | 200 | 3245.4575 | 81.14% | 95% | 0% | -133.8673 | 761.0214 | -2750 | -200 | -2188.9786 | 54.72% | 80.6% | 95% | 0% | 1925 | -117
[5 empty] | 2019-03-05 | 8 | 1516 | 1785 | -115 | 0 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 2265.4575 | 780 | 200 | 3245.4575 | 81.14% | 95% | 0% | -131.5789 | 724.1506 | -2750 | -200 | -2225.8494 | 55.65% | 80.6% | 95% | 0% | 1900 | -115
[5 empty] | 2019-03-05 | 9 | 1516.5 | 1766 | -115 | 0 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 2263.8912 | 780 | 200 | 3243.8912 | 81.1% | 95% | 0% | -131.5789 | 694.3897 | -2750 | -200 | -2255.6103 | 56.39% | 80.59% | 95% | 0% | 1881 | -115
[5 empty] | 2019-03-05 | 10 | 1517 | 1785 | -116 | 0 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 2263.8912 | 780 | 200 | 3243.8912 | 81.1% | 95% | 0% | -132.7231 | 724.5728 | -2750 | -200 | -2225.4272 | 55.64% | 80.59% | 95% | 0% | 1901 | -116
[5 empty] | 2019-03-05 | 11 | 1517.5 | 1843 | -118 | 0 | 0 | 1961 | 951.2778 | 951.2778 | 951.2778 | 2263.8912 | 780 | 200 | 3243.8912 | 81.1% | 95% | 0% | -135.0114 | 816.2664 | -2750 | -200 | -2133.7336 | 53.34% | 80.59% | 95% | 0% | 1961 | -118
[5 empty] | 2019-03-05 | 12 | 1518 | 1951 | -120 | 0 | 0 | 2071 | 1123.5779 | 1123.5779 | 1123.5779 | 2263.8912 | 780 | 200 | 3243.8912 | 81.1% | 95% | 0% | -137.2998 | 986.2781 | -2750 | -200 | -1963.7219 | 49.09% | 80.59% | 95% | 0% | 2071 | -120
[5 empty] | 2019-03-05 | 13 | 1518.5 | 2204 | -117 | 0 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 2263.8912 | 780 | 200 | 3243.8912 | 81.1% | 95% | 0% | -133.8673 | 1381.3017 | -2750 | -200 | -1568.6983 | 39.22% | 80.58% | 95% | 0% | 2321 | -117
[5 empty] | 2019-03-05 | 14 | 1519 | 2396 | -115 | 0 | 0 | 2511 | 1812.7782 | 1812.7782 | 1812.7782 | 2263.8912 | 780 | 200 | 3243.8912 | 81.1% | 95% | 0% | -131.5789 | 1681.1993 | -2750 | -200 | -1268.8007 | 31.72% | 80.58% | 95% | 0% | 2511 | -115
[5 empty] | 2019-03-05 | 15 | 1519.5 | 2599 | -151 | 0 | 0 | 2750 | 2187.1393 | 2187.1393 | 2187.1393 | 2263.8912 | 780 | 200 | 3243.8912 | 81.1% | 95% | 0% | -172.7689 | 2014.3704 | -2750 | -200 | -935.6296 | 23.39% | 80.57% | 95% | 0% | 2750 | -151
[5 empty] | 2019-03-05 | 16 | 1520 | 2612 | -223 | 0 | 0 | 2835 | 2320.2803 | 2320.2803 | 2320.2803 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -255.1487 | 2065.1316 | -2750 | -200 | -884.8684 | 22.12% | 80.57% | 95% | 0% | 2835 | -223
[5 empty] | 2019-03-05 | 17 | 1520.5 | 2542 | -303 | 1 | 0 | 2845 | 2335.9439 | 2335.9439 | 2335.9439 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -346.6819 | 1989.262 | -3550 | -400 | -1960.738 | 49.02% | 80.56% | 95% | 0% | 2845 | -303
[5 empty] | 2019-03-05 | 18 | 1521 | 2412 | -372 | 1 | 0 | 2784 | 2240.3957 | 2240.3957 | 2240.3957 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -425.6293 | 1814.7664 | -3550 | -400 | -2135.2336 | 53.38% | 80.55% | 95% | 0% | 2784 | -372
[5 empty] | 2019-03-05 | 19 | 1521.5 | 2335 | -431 | 1 | 0 | 2766 | 2212.2012 | 2212.2012 | 2212.2012 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -493.135 | 1719.0661 | -3550 | -400 | -2230.9339 | 55.77% | 80.54% | 95% | 0% | 2766 | -431
[5 empty] | 2019-03-05 | 20 | 1522 | 2226 | -485 | 1 | 0 | 2711 | 2126.0511 | 2126.0511 | 2126.0511 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -554.9199 | 1571.1312 | -3550 | -400 | -2378.8688 | 59.47% | 80.54% | 95% | 0% | 2711 | -485
[5 empty] | 2019-03-05 | 21 | 1522.5 | 2114 | -541 | 1 | 0 | 2655 | 2038.3347 | 2038.3347 | 2038.3347 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -618.9931 | 1419.3416 | -3550 | -400 | -2530.6584 | 63.27% | 80.52% | 95% | 0% | 2655 | -541
[5 empty] | 2019-03-05 | 22 | 1523 | 2081 | -551 | 1 | 0 | 2632 | 2002.3083 | 2002.3083 | 2002.3083 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -630.4348 | 1371.8735 | -3550 | -400 | -2578.1265 | 64.45% | 80.51% | 95% | 0% | 2632 | -551
[5 empty] | 2019-03-05 | 23 | 1523.5 | 2059 | -566 | 1 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -647.5973 | 1343.7465 | -3550 | -400 | -2606.2535 | 65.16% | 80.51% | 95% | 0% | 2625 | -566
[5 empty] | 2019-03-05 | 24 | 1524 | 2070 | -557 | 1 | 0 | 2627 | 1994.4765 | 1994.4765 | 1994.4765 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -637.2998 | 1357.1767 | -3550 | -400 | -2592.8233 | 64.82% | 80.51% | 95% | 0% | 2627 | -557
[5 empty] | 2019-03-05 | 25 | 1524.5 | 2134 | -503 | 1 | 0 | 2637 | 2010.1401 | 2010.1401 | 2010.1401 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -575.5149 | 1434.6253 | -3550 | -400 | -2515.3747 | 62.88% | 80.5% | 95% | 0% | 2637 | -503
[5 empty] | 2019-03-05 | 26 | 1525 | 2137 | -496 | 1 | 0 | 2633 | 2003.8747 | 2003.8747 | 2003.8747 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -567.5057 | 1436.369 | -3550 | -400 | -2513.631 | 62.84% | 80.5% | 95% | 0% | 2633 | -496
[5 empty] | 2019-03-05 | 27 | 1525.5 | 2163 | -485 | 1 | 0 | 2648 | 2027.3702 | 2027.3702 | 2027.3702 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -554.9199 | 1472.4502 | -3550 | -400 | -2477.5498 | 61.94% | 80.5% | 95% | 0% | 2648 | -485
[5 empty] | 2019-03-05 | 28 | 1526 | 2222 | -444 | 1 | 0 | 2666 | 2055.5647 | 2055.5647 | 2055.5647 | 2262.3248 | 780 | 200 | 3242.3248 | 81.06% | 95% | 0% | -508.0092 | 1547.5556 | -3550 | -400 | -2402.4444 | 60.06% | 80.5% | 95% | 0% | 2666 | -444
[5 empty] | 2019-03-05 | 29 | 1526.5 | 2289 | -385 | 1 | 0 | 2674 | 2068.0956 | 2068.0956 | 2068.0956 | 2260.7585 | 780 | 200 | 3240.7585 | 81.02% | 95% | 0% | -440.5034 | 1627.5922 | -3550 | -400 | -2322.4078 | 58.06% | 80.49% | 95% | 0% | 2674 | -385
[5 empty] | 2019-03-05 | 30 | 1527 | 2348 | -344 | 1 | 0 | 2692 | 2096.2902 | 2096.2902 | 2096.2902 | 2260.7585 | 780 | 200 | 3240.7585 | 81.02% | 95% | 0% | -393.5927 | 1702.6975 | -3550 | -400 | -2247.3025 | 56.18% | 80.49% | 95% | 0% | 2692 | -344
[5 empty] | 2019-03-05 | 31 | 1527.5 | 2471 | -271 | 1 | 0 | 2742 | 2174.6084 | 2174.6084 | 2174.6084 | 2260.7585 | 780 | 200 | 3240.7585 | 81.02% | 95% | 0% | -310.0686 | 1864.5398 | -3550 | -400 | -2085.4602 | 52.14% | 80.48% | 95% | 0% | 2742 | -271
[5 empty] | 2019-03-05 | 32 | 1528 | 2605 | -223 | 1 | 0 | 2828 | 2309.3157 | 2309.3157 | 2309.3157 | 2260.7585 | 780 | 200 | 3240.7585 | 81.02% | 95% | 0% | -255.1487 | 2054.167 | -3550 | -400 | -1895.833 | 47.4% | 80.48% | 95% | 0% | 2828 | -223
[5 empty] | 2019-03-05 | 33 | 1528.5 | 2736 | -185 | 1 | 0 | 2921 | 2454.9876 | 2454.9876 | 2454.9876 | 2260.7585 | 780 | 200 | 3240.7585 | 81.02% | 95% | 0% | -211.6705 | 2243.3172 | -3550 | -400 | -1706.6828 | 42.67% | 80.48% | 95% | 0% | 2921 | -185
[5 empty] | 2019-03-05 | 34 | 1529 | 2902 | -121 | 1 | 0 | 3023 | 2614.7568 | 2614.7568 | 2614.7568 | 2260.7585 | 780 | 200 | 3240.7585 | 81.02% | 95% | 0% | -138.4439 | 2476.3129 | -3550 | -400 | -1473.6871 | 36.84% | 80.48% | 95% | 0% | 3023 | -121
[5 empty] | 2019-03-05 | 35 | 1529.5 | 3027 | -96 | 1 | 0 | 3123 | 2771.3932 | 2771.3932 | 2771.3932 | 2259.1921 | 780 | 200 | 3239.1921 | 80.98% | 95% | 0% | -109.8398 | 2661.5534 | -3550 | -400 | -1288.4466 | 32.21% | 80.47% | 95% | 0% | 3123 | -96
[5 empty] | 2019-03-05 | 36 | 1530 | 3123 | -86 | 1 | 0 | 3209 | 2906.1006 | 2906.1006 | 2906.1006 | 2259.1921 | 780 | 200 | 3239.1921 | 80.98% | 95% | 0% | -98.3982 | 2807.7024 | -3550 | -400 | -1142.2976 | 28.56% | 80.47% | 95% | 0% | 3209 | -86
[5 empty] | 2019-03-05 | 37 | 1530.5 | 3199 | -87 | 1 | 0 | 3286 | 3026.7106 | 3026.7106 | 3026.7106 | 2259.1921 | 780 | 200 | 3239.1921 | 80.98% | 95% | 0% | -99.5423 | 2927.1683 | -3550 | -400 | -1022.8317 | 25.57% | 80.46% | 95% | 0% | 3286 | -87
[5 empty] | 2019-03-05 | 38 | 1531 | 3178 | -89 | 1 | 0 | 3267 | 2996.9497 | 2996.9497 | 2996.9497 | 2259.1921 | 780 | 200 | 3239.1921 | 80.98% | 95% | 0% | -101.8307 | 2895.119 | -3550 | -400 | -1054.881 | 26.37% | 80.45% | 95% | 0% | 3267 | -89
[5 empty] | 2019-03-05 | 39 | 1531.5 | 3116 | -92 | 0 | 0 | 3208 | 2904.5342 | 2904.5342 | 2904.5342 | 2259.1921 | 780 | 200 | 3239.1921 | 80.98% | 95% | 0% | -105.2632 | 2799.2711 | -2750 | -200 | -150.7289 | 3.768% | 80.45% | 95% | 0% | 3208 | -92
[5 empty] | 2019-03-05 | 40 | 1532 | 3041 | -95 | 0 | 0 | 3136 | 2791.756 | 2791.756 | 2791.756 | 2259.1921 | 780 | 200 | 3239.1921 | 80.98% | 95% | 0% | -108.6957 | 2683.0603 | -2750 | -200 | -266.9397 | 6.673% | 80.44% | 95% | 0% | 3136 | -95
[5 empty] | 2019-03-05 | 41 | 1532.5 | 2963 | -98 | 0 | 0 | 3061 | 2674.2786 | 2674.2786 | 2674.2786 | 2259.1921 | 780 | 200 | 3239.1921 | 80.98% | 95% | 0% | -112.1281 | 2562.1505 | -2750 | -200 | -387.8495 | 9.696% | 80.44% | 95% | 0% | 3061 | -98
[5 empty] | 2019-03-05 | 42 | 1533 | 2819 | -101 | 0 | 0 | 2920 | 2453.4213 | 2453.4213 | 2453.4213 | 2257.6257 | 780 | 200 | 3237.6257 | 80.94% | 95% | 0% | -115.5606 | 2337.8606 | -2750 | -200 | -612.1394 | 15.3% | 80.43% | 95% | 0% | 2920 | -101
[5 empty] | 2019-03-05 | 43 | 1533.5 | 2671 | -106 | 0 | 0 | 2777 | 2229.4312 | 2229.4312 | 2229.4312 | 2257.6257 | 780 | 200 | 3237.6257 | 80.94% | 95% | 0% | -121.2815 | 2108.1497 | -2750 | -200 | -841.8503 | 21.05% | 80.43% | 95% | 0% | 2777 | -106
[5 empty] | 2019-03-05 | 44 | 1534 | 2506 | -111 | 0 | 0 | 2617 | 1978.8129 | 1978.8129 | 1978.8129 | 2257.6257 | 780 | 200 | 3237.6257 | 80.94% | 95% | 0% | -127.0023 | 1851.8106 | -2750 | -200 | -1098.1894 | 27.45% | 80.43% | 95% | 0% | 2617 | -111
[5 empty] | 2019-03-05 | 45 | 1534.5 | 2346 | -116 | 0 | 0 | 2462 | 1736.0264 | 1736.0264 | 1736.0264 | 2257.6257 | 780 | 200 | 3237.6257 | 80.94% | 95% | 0% | -132.7231 | 1603.3033 | -2750 | -200 | -1346.6967 | 33.67% | 80.43% | 95% | 0% | 2462 | -116
[5 empty] | 2019-03-05 | 46 | 1535 | 2193 | -120 | 0 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 2257.6257 | 780 | 200 | 3237.6257 | 80.94% | 95% | 0% | -137.2998 | 1365.3383 | -2750 | -200 | -1584.6617 | 39.62% | 80.43% | 95% | 0% | 2313 | -120
[5 empty] | 2019-03-05 | 47 | 1535.5 | 2022 | -123 | 0 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 2257.6257 | 780 | 200 | 3237.6257 | 80.94% | 95% | 0% | -140.7323 | 1098.7566 | -2750 | -200 | -1851.2434 | 46.28% | 80.43% | 95% | 0% | 2145 | -123
[5 empty] | 2019-03-05 | 48 | 1536 | 1919 | -127 | 0 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 2257.6257 | 780 | 200 | 3237.6257 | 80.94% | 95% | 0% | -145.3089 | 939.1099 | -2750 | -200 | -2010.8901 | 50.27% | 80.42% | 95% | 0% | 2046 | -127
[5 empty] | 2019-03-06 | 1 | 1536.5 | 1883 | -133 | 1 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 2257.6257 | 780 | 200 | 3237.6257 | 80.94% | 95% | 0% | -152.1739 | 885.254 | -3550 | -400 | -3064.746 | 76.62% | 80.42% | 95% | 0% | 2016 | -133
[5 empty] | 2019-03-06 | 2 | 1537 | 1888 | -140 | 1 | 0 | 2028 | 1056.2242 | 1056.2242 | 1056.2242 | 2257.6257 | 780 | 200 | 3237.6257 | 80.94% | 95% | 0% | -160.1831 | 896.0412 | -3550 | -400 | -3053.9588 | 76.35% | 80.38% | 95% | 0% | 2028 | -140
[5 empty] | 2019-03-06 | 3 | 1537.5 | 1840 | -146 | 1 | 0 | 1986 | 990.4369 | 990.4369 | 990.4369 | 2257.6257 | 780 | 200 | 3237.6257 | 80.94% | 95% | 0% | -167.0481 | 823.3889 | -3550 | -400 | -3126.6111 | 78.17% | 80.37% | 95% | 0% | 1986 | -146
[5 empty] | 2019-03-06 | 4 | 1538 | 1770 | -152 | 1 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 2257.6257 | 780 | 200 | 3237.6257 | 80.94% | 95% | 0% | -173.913 | 716.2766 | -3550 | -400 | -3233.7234 | 80.84% | 80.37% | 95% | 0% | 1922 | -152
[5 empty] | 2019-03-06 | 5 | 1538.5 | 1715 | -158 | 1 | 0 | 1873 | 813.4378 | 813.4378 | 813.4378 | 2257.6257 | 780 | 200 | 3237.6257 | 80.94% | 95% | 0% | -180.778 | 632.6597 | -3550 | -400 | -3317.3403 | 82.93% | 80.37% | 95% | 0% | 1873 | -158
[5 empty] | 2019-03-06 | 6 | 1539 | 1678 | -163 | 1 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 2256.0594 | 780 | 200 | 3236.0594 | 80.9% | 95% | 0% | -186.4989 | 576.8152 | -3550 | -400 | -3373.1848 | 84.33% | 80.36% | 95% | 0% | 1841 | -163
[5 empty] | 2019-03-06 | 7 | 1539.5 | 1628 | -168 | 1 | 0 | 1796 | 692.8277 | 692.8277 | 692.8277 | 2256.0594 | 780 | 200 | 3236.0594 | 80.9% | 95% | 0% | -192.2197 | 500.608 | -3550 | -400 | -3449.392 | 86.23% | 80.36% | 95% | 0% | 1796 | -168
[5 empty] | 2019-03-06 | 8 | 1540 | 1594 | -172 | 1 | 0 | 1766 | 645.8368 | 645.8368 | 645.8368 | 2256.0594 | 780 | 200 | 3236.0594 | 80.9% | 95% | 0% | -196.7963 | 449.0404 | -3550 | -400 | -3500.9596 | 87.52% | 80.35% | 95% | 0% | 1766 | -172
[5 empty] | 2019-03-06 | 9 | 1540.5 | 1569 | -177 | 1 | 0 | 1746 | 614.5095 | 614.5095 | 614.5095 | 2256.0594 | 780 | 200 | 3236.0594 | 80.9% | 95% | 0% | -202.5172 | 411.9923 | -3550 | -400 | -3538.0077 | 88.45% | 80.34% | 95% | 0% | 1746 | -177
[5 empty] | 2019-03-06 | 10 | 1541 | 1580 | -182 | 1 | 0 | 1762 | 639.5713 | 639.5713 | 639.5713 | 2256.0594 | 780 | 200 | 3236.0594 | 80.9% | 95% | 0% | -208.238 | 431.3333 | -3550 | -400 | -3518.6667 | 87.97% | 80.34% | 95% | 0% | 1762 | -182
[5 empty] | 2019-03-06 | 11 | 1541.5 | 1648 | -183 | 1 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 2256.0594 | 780 | 200 | 3236.0594 | 80.9% | 95% | 0% | -209.3822 | 538.2683 | -3550 | -400 | -3411.7317 | 85.29% | 80.34% | 95% | 0% | 1831 | -183
[5 empty] | 2019-03-06 | 12 | 1542 | 1745 | -184 | 1 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 2256.0594 | 780 | 200 | 3236.0594 | 80.9% | 95% | 0% | -210.5263 | 690.6278 | -3550 | -400 | -3259.3722 | 81.48% | 80.33% | 95% | 0% | 1929 | -184
[5 empty] | 2019-03-06 | 13 | 1542.5 | 2012 | -183 | 1 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 2256.0594 | 780 | 200 | 3236.0594 | 80.9% | 95% | 0% | -209.3822 | 1108.4249 | -3550 | -400 | -2841.5751 | 71.04% | 80.33% | 95% | 0% | 2195 | -183
[5 empty] | 2019-03-06 | 14 | 1543 | 2245 | -181 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 2256.0594 | 780 | 200 | 3236.0594 | 80.9% | 95% | 0% | -207.0938 | 1472.5434 | -3550 | -400 | -2477.4566 | 61.94% | 80.32% | 95% | 0% | 2426 | -181
[5 empty] | 2019-03-06 | 15 | 1543.5 | 2491 | -180 | 1 | 0 | 2671 | 2063.3965 | 2063.3965 | 2063.3965 | 2256.0594 | 780 | 200 | 3236.0594 | 80.9% | 95% | 0% | -205.9497 | 1857.4469 | -3550 | -400 | -2092.5531 | 52.31% | 80.32% | 95% | 0% | 2671 | -180
[5 empty] | 2019-03-06 | 16 | 1544 | 2610 | -185 | 1 | 0 | 2795 | 2257.6257 | 2257.6257 | 2257.6257 | 2254.493 | 780 | 200 | 3234.493 | 80.86% | 95% | 0% | -211.6705 | 2045.9552 | -3550 | -400 | -1904.0448 | 47.6% | 80.32% | 95% | 0% | 2795 | -185
[5 empty] | 2019-03-06 | 17 | 1544.5 | 2654 | -198 | 1 | 0 | 2852 | 2346.9085 | 2346.9085 | 2346.9085 | 2254.493 | 780 | 200 | 3234.493 | 80.86% | 95% | 0% | -226.5446 | 2120.3639 | -3550 | -400 | -1829.6361 | 45.74% | 80.32% | 95% | 0% | 2852 | -198
[5 empty] | 2019-03-06 | 18 | 1545 | 2642 | -217 | 1 | 0 | 2859 | 2357.873 | 2357.873 | 2357.873 | 2254.493 | 780 | 200 | 3234.493 | 80.86% | 95% | 0% | -248.2838 | 2109.5893 | -3550 | -400 | -1840.4107 | 46.01% | 80.32% | 95% | 0% | 2859 | -217
[5 empty] | 2019-03-06 | 19 | 1545.5 | 2649 | -244 | 1 | 0 | 2893 | 2411.1294 | 2411.1294 | 2411.1294 | 2254.493 | 780 | 200 | 3234.493 | 80.86% | 95% | 0% | -279.1762 | 2131.9532 | -3550 | -400 | -1818.0468 | 45.45% | 80.31% | 95% | 0% | 2893 | -244
[5 empty] | 2019-03-06 | 20 | 1546 | 2591 | -283 | 1 | 0 | 2874 | 2381.3685 | 2381.3685 | 2381.3685 | 2254.493 | 780 | 200 | 3234.493 | 80.86% | 95% | 0% | -323.7986 | 2057.5699 | -3550 | -400 | -1892.4301 | 47.31% | 80.31% | 95% | 0% | 2874 | -283
[5 empty] | 2019-03-06 | 21 | 1546.5 | 2558 | -290 | 1 | 0 | 2848 | 2340.643 | 2340.643 | 2340.643 | 2254.493 | 780 | 200 | 3234.493 | 80.86% | 95% | 0% | -331.8078 | 2008.8353 | -3550 | -400 | -1941.1647 | 48.53% | 80.3% | 95% | 0% | 2848 | -290
[5 empty] | 2019-03-06 | 22 | 1547 | 2563 | -284 | 1 | 0 | 2847 | 2339.0767 | 2339.0767 | 2339.0767 | 2254.493 | 780 | 200 | 3234.493 | 80.86% | 95% | 0% | -324.9428 | 2014.1339 | -3550 | -400 | -1935.8661 | 48.4% | 80.3% | 95% | 0% | 2847 | -284
[5 empty] | 2019-03-06 | 23 | 1547.5 | 2536 | -304 | 1 | 0 | 2840 | 2328.1121 | 2328.1121 | 2328.1121 | 2254.493 | 780 | 200 | 3234.493 | 80.86% | 95% | 0% | -347.8261 | 1980.286 | -3550 | -400 | -1969.714 | 49.24% | 80.28% | 95% | 0% | 2840 | -304
[5 empty] | 2019-03-06 | 24 | 1548 | 2519 | -308 | 1 | 0 | 2827 | 2307.7494 | 2307.7494 | 2307.7494 | 2252.9266 | 780 | 200 | 3232.9266 | 80.82% | 95% | 0% | -352.4027 | 1955.3466 | -3550 | -400 | -1994.6534 | 49.87% | 80.27% | 95% | 0% | 2827 | -308
[5 empty] | 2019-03-06 | 25 | 1548.5 | 2536 | -311 | 1 | 0 | 2847 | 2339.0767 | 2339.0767 | 2339.0767 | 2252.9266 | 780 | 200 | 3232.9266 | 80.82% | 95% | 0% | -355.8352 | 1983.2414 | -3550 | -400 | -1966.7586 | 49.17% | 80.27% | 95% | 0% | 2847 | -311
[5 empty] | 2019-03-06 | 26 | 1549 | 2546 | -297 | 1 | 0 | 2843 | 2332.8112 | 2332.8112 | 2332.8112 | 2252.9266 | 780 | 200 | 3232.9266 | 80.82% | 95% | 0% | -339.8169 | 1992.9943 | -3550 | -400 | -1957.0057 | 48.93% | 80.27% | 95% | 0% | 2843 | -297
[5 empty] | 2019-03-06 | 27 | 1549.5 | 2545 | -306 | 1 | 0 | 2851 | 2345.3421 | 2345.3421 | 2345.3421 | 2251.3603 | 780 | 200 | 3231.3603 | 80.78% | 95% | 0% | -350.1144 | 1995.2277 | -3550 | -400 | -1954.7723 | 48.87% | 80.25% | 95% | 0% | 2851 | -306
[5 empty] | 2019-03-06 | 28 | 1550 | 2517 | -302 | 1 | 0 | 2819 | 2295.2185 | 2295.2185 | 2295.2185 | 2251.3603 | 780 | 200 | 3231.3603 | 80.78% | 95% | 0% | -345.5378 | 1949.6807 | -3550 | -400 | -2000.3193 | 50.01% | 80.25% | 95% | 0% | 2819 | -302
[5 empty] | 2019-03-06 | 29 | 1550.5 | 2501 | -308 | 1 | 0 | 2809 | 2279.5548 | 2279.5548 | 2279.5548 | 2249.7939 | 780 | 200 | 3229.7939 | 80.74% | 95% | 0% | -352.4027 | 1927.1521 | -3550 | -400 | -2022.8479 | 50.57% | 80.24% | 95% | 0% | 2809 | -308
[5 empty] | 2019-03-06 | 30 | 1551 | 2530 | -262 | 1 | 0 | 2792 | 2252.9266 | 2252.9266 | 2252.9266 | 2249.7939 | 780 | 200 | 3229.7939 | 80.74% | 95% | 0% | -299.7712 | 1953.1555 | -3550 | -400 | -1996.8445 | 49.92% | 80.24% | 95% | 0% | 2792 | -262
[5 empty] | 2019-03-06 | 31 | 1551.5 | 2553 | -248 | 1 | 0 | 2801 | 2267.0239 | 2267.0239 | 2267.0239 | 2249.7939 | 780 | 200 | 3229.7939 | 80.74% | 95% | 0% | -283.7529 | 1983.271 | -3550 | -400 | -1966.729 | 49.17% | 80.24% | 95% | 0% | 2801 | -248
[5 empty] | 2019-03-06 | 32 | 1552 | 2601 | -247 | 1 | 0 | 2848 | 2340.643 | 2340.643 | 2340.643 | 2249.7939 | 780 | 200 | 3229.7939 | 80.74% | 95% | 0% | -282.6087 | 2058.0343 | -3550 | -400 | -1891.9657 | 47.3% | 80.24% | 95% | 0% | 2848 | -247
[5 empty] | 2019-03-06 | 33 | 1552.5 | 2698 | -227 | 1 | 0 | 2925 | 2461.2531 | 2461.2531 | 2461.2531 | 2249.7939 | 780 | 200 | 3229.7939 | 80.74% | 95% | 0% | -259.7254 | 2201.5277 | -3550 | -400 | -1748.4723 | 43.71% | 80.23% | 95% | 0% | 2925 | -227
[5 empty] | 2019-03-06 | 34 | 1553 | 2831 | -183 | 1 | 0 | 3014 | 2600.6595 | 2600.6595 | 2600.6595 | 2249.7939 | 780 | 200 | 3229.7939 | 80.74% | 95% | 0% | -209.3822 | 2391.2774 | -3550 | -400 | -1558.7226 | 38.97% | 80.22% | 95% | 0% | 3014 | -183
[5 empty] | 2019-03-06 | 35 | 1553.5 | 2950 | -151 | 1 | 0 | 3101 | 2736.9332 | 2736.9332 | 2736.9332 | 2249.7939 | 780 | 200 | 3229.7939 | 80.74% | 95% | 0% | -172.7689 | 2564.1643 | -3550 | -400 | -1385.8357 | 34.65% | 80.22% | 95% | 0% | 3101 | -151
[5 empty] | 2019-03-06 | 36 | 1554 | 3006 | -135 | 1 | 0 | 3141 | 2799.5878 | 2799.5878 | 2799.5878 | 2249.7939 | 780 | 200 | 3229.7939 | 80.74% | 95% | 0% | -154.4622 | 2645.1256 | -3550 | -400 | -1304.8744 | 32.62% | 80.22% | 95% | 0% | 3141 | -135
[5 empty] | 2019-03-06 | 37 | 1554.5 | 3077 | -134 | 1 | 0 | 3211 | 2909.2333 | 2909.2333 | 2909.2333 | 2249.7939 | 780 | 200 | 3229.7939 | 80.74% | 95% | 0% | -153.3181 | 2755.9152 | -3550 | -400 | -1194.0848 | 29.85% | 80.21% | 95% | 0% | 3211 | -134
[5 empty] | 2019-03-06 | 38 | 1555 | 3076 | -134 | 0 | 0 | 3210 | 2907.6669 | 2907.6669 | 2907.6669 | 2249.7939 | 780 | 200 | 3229.7939 | 80.74% | 95% | 0% | -153.3181 | 2754.3489 | -2750 | -200 | -195.6511 | 4.891% | 80.21% | 95% | 0% | 3210 | -134
[5 empty] | 2019-03-06 | 39 | 1555.5 | 3007 | -132 | 0 | 0 | 3139 | 2796.4551 | 2796.4551 | 2796.4551 | 2248.2275 | 780 | 200 | 3228.2275 | 80.71% | 95% | 0% | -151.0297 | 2645.4253 | -2750 | -200 | -304.5747 | 7.614% | 80.2% | 95% | 0% | 3139 | -132
[5 empty] | 2019-03-06 | 40 | 1556 | 2931 | -131 | 0 | 0 | 3062 | 2675.845 | 2675.845 | 2675.845 | 2248.2275 | 780 | 200 | 3228.2275 | 80.71% | 95% | 0% | -149.8856 | 2525.9594 | -2750 | -200 | -424.0406 | 10.6% | 80.2% | 95% | 0% | 3062 | -131
[5 empty] | 2019-03-06 | 41 | 1556.5 | 2894 | -128 | 0 | 0 | 3022 | 2613.1904 | 2613.1904 | 2613.1904 | 2248.2275 | 780 | 200 | 3228.2275 | 80.71% | 95% | 0% | -146.4531 | 2466.7373 | -2750 | -200 | -483.2627 | 12.08% | 80.2% | 95% | 0% | 3022 | -128
[5 empty] | 2019-03-06 | 42 | 1557 | 2768 | -126 | 0 | 0 | 2894 | 2412.6958 | 2412.6958 | 2412.6958 | 2248.2275 | 780 | 200 | 3228.2275 | 80.71% | 95% | 0% | -144.1648 | 2268.531 | -2750 | -200 | -681.469 | 17.04% | 80.19% | 95% | 0% | 2894 | -126
[5 empty] | 2019-03-06 | 43 | 1557.5 | 2634 | -125 | 0 | 0 | 2759 | 2201.2366 | 2201.2366 | 2201.2366 | 2248.2275 | 780 | 200 | 3228.2275 | 80.71% | 95% | 0% | -143.0206 | 2058.216 | -2750 | -200 | -891.784 | 22.29% | 80.18% | 95% | 0% | 2759 | -125
[5 empty] | 2019-03-06 | 44 | 1558 | 2474 | -125 | 0 | 0 | 2599 | 1950.6183 | 1950.6183 | 1950.6183 | 2246.6612 | 780 | 200 | 3226.6612 | 80.67% | 95% | 0% | -143.0206 | 1807.5977 | -2750 | -200 | -1142.4023 | 28.56% | 80.18% | 95% | 0% | 2599 | -125
[5 empty] | 2019-03-06 | 45 | 1558.5 | 2306 | -125 | 0 | 0 | 2431 | 1687.4691 | 1687.4691 | 1687.4691 | 2246.6612 | 780 | 200 | 3226.6612 | 80.67% | 95% | 0% | -143.0206 | 1544.4485 | -2750 | -200 | -1405.5515 | 35.14% | 80.17% | 95% | 0% | 2431 | -125
[5 empty] | 2019-03-06 | 46 | 1559 | 2156 | -124 | 0 | 0 | 2280 | 1450.9481 | 1450.9481 | 1450.9481 | 2246.6612 | 780 | 200 | 3226.6612 | 80.67% | 95% | 0% | -141.8764 | 1309.0716 | -2750 | -200 | -1640.9284 | 41.02% | 80.13% | 95% | 0% | 2280 | -124
[5 empty] | 2019-03-06 | 47 | 1559.5 | 1979 | -126 | 0 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 2246.6612 | 780 | 200 | 3226.6612 | 80.67% | 95% | 0% | -144.1648 | 1032.6695 | -2750 | -200 | -1917.3305 | 47.93% | 80.13% | 95% | 0% | 2105 | -126
[5 empty] | 2019-03-06 | 48 | 1560 | 1875 | -127 | 0 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 2246.6612 | 780 | 200 | 3226.6612 | 80.67% | 95% | 0% | -145.3089 | 870.1898 | -2750 | -200 | -2079.8102 | 52% | 80.13% | 95% | 0% | 2002 | -127
[5 empty] | 2019-03-07 | 1 | 1560.5 | 1861 | -126 | 0 | 0 | 1987 | 992.0033 | 992.0033 | 992.0033 | 2246.6612 | 780 | 200 | 3226.6612 | 80.67% | 95% | 0% | -144.1648 | 847.8385 | -2750 | -200 | -2102.1615 | 52.55% | 80.13% | 95% | 0% | 1987 | -126
[5 empty] | 2019-03-07 | 2 | 1561 | 1882 | -125 | 0 | 0 | 2007 | 1023.3306 | 1023.3306 | 1023.3306 | 2246.6612 | 780 | 200 | 3226.6612 | 80.67% | 95% | 0% | -143.0206 | 880.31 | -2750 | -200 | -2069.69 | 51.74% | 80.12% | 95% | 0% | 2007 | -125
[5 empty] | 2019-03-07 | 3 | 1561.5 | 1856 | -125 | 0 | 0 | 1981 | 982.6051 | 982.6051 | 982.6051 | 2246.6612 | 780 | 200 | 3226.6612 | 80.67% | 95% | 0% | -143.0206 | 839.5845 | -2750 | -200 | -2110.4155 | 52.76% | 80.12% | 95% | 0% | 1981 | -125
[5 empty] | 2019-03-07 | 4 | 1562 | 1821 | -124 | 0 | 0 | 1945 | 926.216 | 926.216 | 926.216 | 2245.0948 | 780 | 200 | 3225.0948 | 80.63% | 95% | 0% | -141.8764 | 784.3396 | -2750 | -200 | -2165.6604 | 54.14% | 80.11% | 95% | 0% | 1945 | -124
[5 empty] | 2019-03-07 | 5 | 1562.5 | 1777 | -125 | 0 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 2245.0948 | 780 | 200 | 3225.0948 | 80.63% | 95% | 0% | -143.0206 | 715.8417 | -2750 | -200 | -2234.1583 | 55.85% | 80.1% | 95% | 0% | 1902 | -125
[5 empty] | 2019-03-07 | 6 | 1563 | 1763 | -125 | 0 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 2245.0948 | 780 | 200 | 3225.0948 | 80.63% | 95% | 0% | -143.0206 | 693.9126 | -2750 | -200 | -2256.0874 | 56.4% | 80.1% | 95% | 0% | 1888 | -125
[5 empty] | 2019-03-07 | 7 | 1563.5 | 1720 | -128 | 0 | 0 | 1848 | 774.2786 | 774.2786 | 774.2786 | 2245.0948 | 780 | 200 | 3225.0948 | 80.63% | 95% | 0% | -146.4531 | 627.8256 | -2750 | -200 | -2322.1744 | 58.05% | 80.1% | 95% | 0% | 1848 | -128
[5 empty] | 2019-03-07 | 8 | 1564 | 1678 | -131 | 0 | 0 | 1809 | 713.1904 | 713.1904 | 713.1904 | 2245.0948 | 780 | 200 | 3225.0948 | 80.63% | 95% | 0% | -149.8856 | 563.3049 | -2750 | -200 | -2386.6951 | 59.67% | 80.09% | 95% | 0% | 1809 | -131
[5 empty] | 2019-03-07 | 9 | 1564.5 | 1654 | -135 | 0 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 2245.0948 | 780 | 200 | 3225.0948 | 80.63% | 95% | 0% | -154.4622 | 527.4009 | -2750 | -200 | -2422.5991 | 60.56% | 80.08% | 95% | 0% | 1789 | -135
[5 empty] | 2019-03-07 | 10 | 1565 | 1660 | -139 | 0 | 0 | 1799 | 697.5268 | 697.5268 | 697.5268 | 2245.0948 | 780 | 200 | 3225.0948 | 80.63% | 95% | 0% | -159.0389 | 538.4879 | -2750 | -200 | -2411.5121 | 60.29% | 80.08% | 95% | 0% | 1799 | -139
[5 empty] | 2019-03-07 | 11 | 1565.5 | 1725 | -145 | 0 | 0 | 1870 | 808.7387 | 808.7387 | 808.7387 | 2243.5284 | 780 | 200 | 3223.5284 | 80.59% | 95% | 0% | -165.9039 | 642.8348 | -2750 | -200 | -2307.1652 | 57.68% | 80.07% | 95% | 0% | 1870 | -145
[5 empty] | 2019-03-07 | 12 | 1566 | 1828 | -150 | 0 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 2243.5284 | 780 | 200 | 3223.5284 | 80.59% | 95% | 0% | -171.6247 | 806.2813 | -2750 | -200 | -2143.7187 | 53.59% | 80.07% | 95% | 0% | 1978 | -150
[5 empty] | 2019-03-07 | 13 | 1566.5 | 2060 | -155 | 0 | 0 | 2215 | 1349.1344 | 1349.1344 | 1349.1344 | 2243.5284 | 780 | 200 | 3223.5284 | 80.59% | 95% | 0% | -177.3455 | 1171.7888 | -2750 | -200 | -1778.2112 | 44.46% | 80.06% | 95% | 0% | 2215 | -155
[5 empty] | 2019-03-07 | 14 | 1567 | 2254 | -163 | 0 | 0 | 2417 | 1665.54 | 1665.54 | 1665.54 | 2243.5284 | 780 | 200 | 3223.5284 | 80.59% | 95% | 0% | -186.4989 | 1479.0411 | -2750 | -200 | -1470.9589 | 36.77% | 80.06% | 95% | 0% | 2417 | -163
[5 empty] | 2019-03-07 | 15 | 1567.5 | 2445 | -199 | 0 | 0 | 2644 | 2021.1047 | 2021.1047 | 2021.1047 | 2243.5284 | 780 | 200 | 3223.5284 | 80.59% | 95% | 0% | -227.6888 | 1793.4159 | -2750 | -200 | -1156.5841 | 28.91% | 80.06% | 95% | 0% | 2644 | -199
[5 empty] | 2019-03-07 | 16 | 1568 | 2446 | -253 | 0 | 0 | 2699 | 2107.2547 | 2107.2547 | 2107.2547 | 2243.5284 | 780 | 200 | 3223.5284 | 80.59% | 95% | 0% | -289.4737 | 1817.7811 | -2750 | -200 | -1132.2189 | 28.31% | 80.05% | 95% | 0% | 2699 | -253
[5 empty] | 2019-03-07 | 17 | 1568.5 | 2389 | -313 | 1 | 0 | 2702 | 2111.9538 | 2111.9538 | 2111.9538 | 2241.9621 | 780 | 200 | 3221.9621 | 80.55% | 95% | 0% | -358.1236 | 1753.8303 | -3550 | -400 | -2196.1697 | 54.9% | 80.05% | 95% | 0% | 2702 | -313
[5 empty] | 2019-03-07 | 18 | 1569 | 2279 | -372 | 1 | 0 | 2651 | 2032.0692 | 2032.0692 | 2032.0692 | 2241.9621 | 780 | 200 | 3221.9621 | 80.55% | 95% | 0% | -425.6293 | 1606.44 | -3550 | -400 | -2343.56 | 58.59% | 80.05% | 95% | 0% | 2651 | -372
[5 empty] | 2019-03-07 | 19 | 1569.5 | 2229 | -424 | 1 | 0 | 2653 | 2035.202 | 2035.202 | 2035.202 | 2241.9621 | 780 | 200 | 3221.9621 | 80.55% | 95% | 0% | -485.1259 | 1550.0761 | -3550 | -400 | -2399.9239 | 60% | 80.04% | 95% | 0% | 2653 | -424
[5 empty] | 2019-03-07 | 20 | 1570 | 2186 | -451 | 1 | 0 | 2637 | 2010.1401 | 2010.1401 | 2010.1401 | 2241.9621 | 780 | 200 | 3221.9621 | 80.55% | 95% | 0% | -516.0183 | 1494.1218 | -3550 | -400 | -2455.8782 | 61.4% | 80.04% | 95% | 0% | 2637 | -451
[5 empty] | 2019-03-07 | 21 | 1570.5 | 2136 | -488 | 1 | 0 | 2624 | 1989.7774 | 1989.7774 | 1989.7774 | 2241.9621 | 780 | 200 | 3221.9621 | 80.55% | 95% | 0% | -558.3524 | 1431.425 | -3550 | -400 | -2518.575 | 62.96% | 80.04% | 95% | 0% | 2624 | -488
[5 empty] | 2019-03-07 | 22 | 1571 | 2118 | -501 | 1 | 0 | 2619 | 1981.9456 | 1981.9456 | 1981.9456 | 2241.9621 | 780 | 200 | 3221.9621 | 80.55% | 95% | 0% | -573.2265 | 1408.719 | -3550 | -400 | -2541.281 | 63.53% | 80.03% | 95% | 0% | 2619 | -501
[5 empty] | 2019-03-07 | 23 | 1571.5 | 2096 | -526 | 1 | 0 | 2622 | 1986.6447 | 1986.6447 | 1986.6447 | 2241.9621 | 780 | 200 | 3221.9621 | 80.55% | 95% | 0% | -601.8307 | 1384.814 | -3550 | -400 | -2565.186 | 64.13% | 80.03% | 95% | 0% | 2622 | -526
[5 empty] | 2019-03-07 | 24 | 1572 | 2098 | -523 | 1 | 0 | 2621 | 1985.0783 | 1985.0783 | 1985.0783 | 2241.9621 | 780 | 200 | 3221.9621 | 80.55% | 95% | 0% | -598.3982 | 1386.6801 | -3550 | -400 | -2563.3199 | 64.08% | 80.03% | 95% | 0% | 2621 | -523
[5 empty] | 2019-03-07 | 25 | 1572.5 | 2153 | -500 | 1 | 0 | 2653 | 2035.202 | 2035.202 | 2035.202 | 2240.3957 | 780 | 200 | 3220.3957 | 80.51% | 95% | 0% | -572.0824 | 1463.1196 | -3550 | -400 | -2486.8804 | 62.17% | 80.02% | 95% | 0% | 2653 | -500
[5 empty] | 2019-03-07 | 26 | 1573 | 2163 | -489 | 1 | 0 | 2652 | 2033.6356 | 2033.6356 | 2033.6356 | 2240.3957 | 780 | 200 | 3220.3957 | 80.51% | 95% | 0% | -559.4966 | 1474.139 | -3550 | -400 | -2475.861 | 61.9% | 80.02% | 95% | 0% | 2652 | -489
[5 empty] | 2019-03-07 | 27 | 1573.5 | 2179 | -472 | 1 | 0 | 2651 | 2032.0692 | 2032.0692 | 2032.0692 | 2240.3957 | 780 | 200 | 3220.3957 | 80.51% | 95% | 0% | -540.0458 | 1492.0235 | -3550 | -400 | -2457.9765 | 61.45% | 80.01% | 95% | 0% | 2651 | -472
[5 empty] | 2019-03-07 | 28 | 1574 | 2212 | -435 | 1 | 0 | 2647 | 2025.8038 | 2025.8038 | 2025.8038 | 2240.3957 | 780 | 200 | 3220.3957 | 80.51% | 95% | 0% | -497.7117 | 1528.0921 | -3550 | -400 | -2421.9079 | 60.55% | 80.01% | 95% | 0% | 2647 | -435
[5 empty] | 2019-03-07 | 29 | 1574.5 | 2281 | -383 | 1 | 0 | 2664 | 2052.432 | 2052.432 | 2052.432 | 2240.3957 | 780 | 200 | 3220.3957 | 80.51% | 95% | 0% | -438.2151 | 1614.2169 | -3550 | -400 | -2335.7831 | 58.39% | 80.01% | 95% | 0% | 2664 | -383
[5 empty] | 2019-03-07 | 30 | 1575 | 2324 | -354 | 1 | 0 | 2678 | 2074.3611 | 2074.3611 | 2074.3611 | 2240.3957 | 780 | 200 | 3220.3957 | 80.51% | 95% | 0% | -405.0343 | 1669.3268 | -3550 | -400 | -2280.6732 | 57.02% | 80% | 95% | 0% | 2678 | -354
[5 empty] | 2019-03-07 | 31 | 1575.5 | 2367 | -334 | 1 | 0 | 2701 | 2110.3875 | 2110.3875 | 2110.3875 | 2240.3957 | 780 | 200 | 3220.3957 | 80.51% | 95% | 0% | -382.151 | 1728.2364 | -3550 | -400 | -2221.7636 | 55.54% | 80% | 95% | 0% | 2701 | -334
[5 empty] | 2019-03-07 | 32 | 1576 | 2470 | -313 | 1 | 0 | 2783 | 2238.8293 | 2238.8293 | 2238.8293 | 2240.3957 | 780 | 200 | 3220.3957 | 80.51% | 95% | 0% | -358.1236 | 1880.7058 | -3550 | -400 | -2069.2942 | 51.73% | 79.99% | 95% | 0% | 2783 | -313
[5 empty] | 2019-03-07 | 33 | 1576.5 | 2575 | -291 | 1 | 0 | 2866 | 2368.8376 | 2368.8376 | 2368.8376 | 2240.3957 | 780 | 200 | 3220.3957 | 80.51% | 95% | 0% | -332.9519 | 2035.8856 | -3550 | -400 | -1914.1144 | 47.85% | 79.98% | 95% | 0% | 2866 | -291
[5 empty] | 2019-03-07 | 34 | 1577 | 2663 | -265 | 1 | 0 | 2928 | 2465.9522 | 2465.9522 | 2465.9522 | 2240.3957 | 780 | 200 | 3220.3957 | 80.51% | 95% | 0% | -303.2037 | 2162.7485 | -3550 | -400 | -1787.2515 | 44.68% | 79.98% | 95% | 0% | 2928 | -265
[5 empty] | 2019-03-07 | 35 | 1577.5 | 2758 | -242 | 1 | 0 | 3000 | 2578.7304 | 2578.7304 | 2578.7304 | 2238.8293 | 780 | 200 | 3218.8293 | 80.47% | 95% | 0% | -276.8879 | 2301.8425 | -3550 | -400 | -1648.1575 | 41.2% | 79.98% | 95% | 0% | 3000 | -242
[5 empty] | 2019-03-07 | 36 | 1578 | 2831 | -224 | 1 | 0 | 3055 | 2664.8805 | 2664.8805 | 2664.8805 | 2238.8293 | 780 | 200 | 3218.8293 | 80.47% | 95% | 0% | -256.2929 | 2408.5876 | -3550 | -400 | -1541.4124 | 38.54% | 79.98% | 95% | 0% | 3055 | -224
[5 empty] | 2019-03-07 | 37 | 1578.5 | 2908 | -219 | 1 | 0 | 3127 | 2777.6587 | 2777.6587 | 2777.6587 | 2238.8293 | 780 | 200 | 3218.8293 | 80.47% | 95% | 0% | -250.5721 | 2527.0866 | -3550 | -400 | -1422.9134 | 35.57% | 79.98% | 95% | 0% | 3127 | -219
[5 empty] | 2019-03-07 | 38 | 1579 | 2926 | -216 | 1 | 0 | 3142 | 2801.1542 | 2801.1542 | 2801.1542 | 2238.8293 | 780 | 200 | 3218.8293 | 80.47% | 95% | 0% | -247.1396 | 2554.0146 | -3550 | -400 | -1395.9854 | 34.9% | 79.97% | 95% | 0% | 3142 | -216
[5 empty] | 2019-03-07 | 39 | 1579.5 | 2880 | -209 | 0 | 0 | 3089 | 2718.1369 | 2718.1369 | 2718.1369 | 2238.8293 | 780 | 200 | 3218.8293 | 80.47% | 95% | 0% | -239.1304 | 2479.0064 | -2750 | -200 | -470.9936 | 11.77% | 79.96% | 95% | 0% | 3089 | -209
[5 empty] | 2019-03-07 | 40 | 1580 | 2800 | -203 | 0 | 0 | 3003 | 2583.4295 | 2583.4295 | 2583.4295 | 2238.8293 | 780 | 200 | 3218.8293 | 80.47% | 95% | 0% | -232.2654 | 2351.1641 | -2750 | -200 | -598.8359 | 14.97% | 79.95% | 95% | 0% | 3003 | -203
[5 empty] | 2019-03-07 | 41 | 1580.5 | 2748 | -194 | 0 | 0 | 2942 | 2487.8813 | 2487.8813 | 2487.8813 | 2238.8293 | 780 | 200 | 3218.8293 | 80.47% | 95% | 0% | -221.968 | 2265.9133 | -2750 | -200 | -684.0867 | 17.1% | 79.95% | 95% | 0% | 2942 | -194
[5 empty] | 2019-03-07 | 42 | 1581 | 2654 | -186 | 0 | 0 | 2840 | 2328.1121 | 2328.1121 | 2328.1121 | 2237.263 | 780 | 200 | 3217.263 | 80.43% | 95% | 0% | -212.8146 | 2115.2975 | -2750 | -200 | -834.7025 | 20.87% | 79.94% | 95% | 0% | 2840 | -186
[5 empty] | 2019-03-07 | 43 | 1581.5 | 2535 | -176 | 0 | 0 | 2711 | 2126.0511 | 2126.0511 | 2126.0511 | 2237.263 | 780 | 200 | 3217.263 | 80.43% | 95% | 0% | -201.373 | 1924.6781 | -2750 | -200 | -1025.3219 | 25.63% | 79.93% | 95% | 0% | 2711 | -176
[5 empty] | 2019-03-07 | 44 | 1582 | 2402 | -167 | 0 | 0 | 2569 | 1903.6274 | 1903.6274 | 1903.6274 | 2237.263 | 780 | 200 | 3217.263 | 80.43% | 95% | 0% | -191.0755 | 1712.5519 | -2750 | -200 | -1237.4481 | 30.94% | 79.91% | 95% | 0% | 2569 | -167
[5 empty] | 2019-03-07 | 45 | 1582.5 | 2261 | -157 | 0 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 2237.263 | 780 | 200 | 3217.263 | 80.43% | 95% | 0% | -179.6339 | 1487.4725 | -2750 | -200 | -1462.5275 | 36.56% | 79.91% | 95% | 0% | 2418 | -157
[5 empty] | 2019-03-07 | 46 | 1583 | 2138 | -148 | 0 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 2237.263 | 780 | 200 | 3217.263 | 80.43% | 95% | 0% | -169.3364 | 1291.0099 | -2750 | -200 | -1658.9901 | 41.47% | 79.91% | 95% | 0% | 2286 | -148
[5 empty] | 2019-03-07 | 47 | 1583.5 | 2000 | -133 | 0 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 2235.6966 | 780 | 200 | 3215.6966 | 80.39% | 95% | 0% | -152.1739 | 1068.5186 | -2750 | -200 | -1881.4814 | 47.04% | 79.91% | 95% | 0% | 2133 | -133
[5 empty] | 2019-03-07 | 48 | 1584 | 1932 | -118 | 0 | 0 | 2050 | 1090.6843 | 1090.6843 | 1090.6843 | 2235.6966 | 780 | 200 | 3215.6966 | 80.39% | 95% | 0% | -135.0114 | 955.6728 | -2750 | -200 | -1994.3272 | 49.86% | 79.9% | 95% | 0% | 2050 | -118
[5 empty] | 2019-03-08 | 1 | 1584.5 | 1928 | -110 | 0 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 2235.6966 | 780 | 200 | 3215.6966 | 80.39% | 95% | 0% | -125.8581 | 946.0298 | -2750 | -200 | -2003.9702 | 50.1% | 79.9% | 95% | 0% | 2038 | -110
[5 empty] | 2019-03-08 | 2 | 1585 | 1963 | -103 | 0 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 2235.6966 | 780 | 200 | 3215.6966 | 80.39% | 95% | 0% | -117.849 | 997.8971 | -2750 | -200 | -1952.1029 | 48.8% | 79.9% | 95% | 0% | 2066 | -103
[5 empty] | 2019-03-08 | 3 | 1585.5 | 1982 | -96 | 0 | 0 | 2078 | 1134.5425 | 1134.5425 | 1134.5425 | 2235.6966 | 780 | 200 | 3215.6966 | 80.39% | 95% | 0% | -109.8398 | 1024.7026 | -2750 | -200 | -1925.2974 | 48.13% | 79.9% | 95% | 0% | 2078 | -96
[5 empty] | 2019-03-08 | 4 | 1586 | 1950 | -89 | 0 | 0 | 2039 | 1073.4542 | 1073.4542 | 1073.4542 | 2235.6966 | 780 | 200 | 3215.6966 | 80.39% | 95% | 0% | -101.8307 | 971.6236 | -2750 | -200 | -1978.3764 | 49.46% | 79.9% | 95% | 0% | 2039 | -89
[5 empty] | 2019-03-08 | 5 | 1586.5 | 1932 | -84 | 0 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 2235.6966 | 780 | 200 | 3215.6966 | 80.39% | 95% | 0% | -96.1098 | 941.318 | -2750 | -200 | -2008.682 | 50.22% | 79.89% | 95% | 0% | 2016 | -84
[5 empty] | 2019-03-08 | 6 | 1587 | 1930 | -80 | 0 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 2235.6966 | 780 | 200 | 3215.6966 | 80.39% | 95% | 0% | -91.5332 | 936.4965 | -2750 | -200 | -2013.5035 | 50.34% | 79.87% | 95% | 0% | 2010 | -80
[5 empty] | 2019-03-08 | 7 | 1587.5 | 1917 | -76 | 0 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 2235.6966 | 780 | 200 | 3215.6966 | 80.39% | 95% | 0% | -86.9565 | 914.445 | -2750 | -200 | -2035.555 | 50.89% | 79.87% | 95% | 0% | 1993 | -76
[5 empty] | 2019-03-08 | 8 | 1588 | 1899 | -71 | 0 | 0 | 1970 | 965.3751 | 965.3751 | 965.3751 | 2234.1303 | 780 | 200 | 3214.1303 | 80.35% | 95% | 0% | -81.2357 | 884.1394 | -2750 | -200 | -2065.8606 | 51.65% | 79.87% | 95% | 0% | 1970 | -71
[5 empty] | 2019-03-08 | 9 | 1588.5 | 1897 | -70 | 1 | 0 | 1967 | 960.676 | 960.676 | 960.676 | 2234.1303 | 780 | 200 | 3214.1303 | 80.35% | 95% | 0% | -80.0915 | 880.5845 | -3550 | -400 | -3069.4155 | 76.74% | 79.87% | 95% | 0% | 1967 | -70
[5 empty] | 2019-03-08 | 10 | 1589 | 1922 | -69 | 1 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 2234.1303 | 780 | 200 | 3214.1303 | 80.35% | 95% | 0% | -78.9474 | 919.3214 | -3550 | -400 | -3030.6786 | 75.77% | 79.86% | 95% | 0% | 1991 | -69
[5 empty] | 2019-03-08 | 11 | 1589.5 | 1989 | -68 | 1 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 2234.1303 | 780 | 200 | 3214.1303 | 80.35% | 95% | 0% | -77.8032 | 1023.8456 | -3550 | -400 | -2926.1544 | 73.15% | 79.86% | 95% | 0% | 2057 | -68
[5 empty] | 2019-03-08 | 12 | 1590 | 2089 | -68 | 1 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 2234.1303 | 780 | 200 | 3214.1303 | 80.35% | 95% | 0% | -77.8032 | 1180.482 | -3550 | -400 | -2769.518 | 69.24% | 79.85% | 95% | 0% | 2157 | -68
[5 empty] | 2019-03-08 | 13 | 1590.5 | 2292 | -68 | 1 | 0 | 2360 | 1576.2572 | 1576.2572 | 1576.2572 | 2234.1303 | 780 | 200 | 3214.1303 | 80.35% | 95% | 0% | -77.8032 | 1498.454 | -3550 | -400 | -2451.546 | 61.29% | 79.84% | 95% | 0% | 2360 | -68
[5 empty] | 2019-03-08 | 14 | 1591 | 2464 | -75 | 1 | 0 | 2539 | 1856.6364 | 1856.6364 | 1856.6364 | 2232.5639 | 780 | 200 | 3212.5639 | 80.31% | 95% | 0% | -85.8124 | 1770.8241 | -3550 | -400 | -2179.1759 | 54.48% | 79.84% | 95% | 0% | 2539 | -75
[5 empty] | 2019-03-08 | 15 | 1591.5 | 2609 | -121 | 1 | 0 | 2730 | 2155.812 | 2155.812 | 2155.812 | 2230.9975 | 780 | 200 | 3210.9975 | 80.27% | 95% | 0% | -138.4439 | 2017.3681 | -3550 | -400 | -1932.6319 | 48.32% | 79.83% | 95% | 0% | 2730 | -121
[5 empty] | 2019-03-08 | 16 | 1592 | 2590 | -185 | 1 | 0 | 2775 | 2226.2984 | 2226.2984 | 2226.2984 | 2230.9975 | 780 | 200 | 3210.9975 | 80.27% | 95% | 0% | -211.6705 | 2014.628 | -3550 | -400 | -1935.372 | 48.38% | 79.83% | 95% | 0% | 2775 | -185
[5 empty] | 2019-03-08 | 17 | 1592.5 | 2576 | -248 | 1 | 0 | 2824 | 2303.0503 | 2303.0503 | 2303.0503 | 2230.9975 | 780 | 200 | 3210.9975 | 80.27% | 95% | 0% | -283.7529 | 2019.2974 | -3550 | -400 | -1930.7026 | 48.27% | 79.82% | 95% | 0% | 2824 | -248
[5 empty] | 2019-03-08 | 18 | 1593 | 2544 | -285 | 1 | 0 | 2829 | 2310.8821 | 2310.8821 | 2310.8821 | 2230.9975 | 780 | 200 | 3210.9975 | 80.27% | 95% | 0% | -326.087 | 1984.7952 | -3550 | -400 | -1965.2048 | 49.13% | 79.82% | 95% | 0% | 2829 | -285
[5 empty] | 2019-03-08 | 19 | 1593.5 | 2534 | -325 | 1 | 0 | 2859 | 2357.873 | 2357.873 | 2357.873 | 2230.9975 | 780 | 200 | 3210.9975 | 80.27% | 95% | 0% | -371.8535 | 1986.0195 | -3550 | -400 | -1963.9805 | 49.1% | 79.82% | 95% | 0% | 2859 | -325
[5 empty] | 2019-03-08 | 20 | 1594 | 2494 | -354 | 1 | 0 | 2848 | 2340.643 | 2340.643 | 2340.643 | 2230.9975 | 780 | 200 | 3210.9975 | 80.27% | 95% | 0% | -405.0343 | 1935.6087 | -3550 | -400 | -2014.3913 | 50.36% | 79.81% | 95% | 0% | 2848 | -354
[5 empty] | 2019-03-08 | 21 | 1594.5 | 2511 | -356 | 1 | 0 | 2867 | 2370.404 | 2370.404 | 2370.404 | 2229.4312 | 780 | 200 | 3209.4312 | 80.24% | 95% | 0% | -407.3227 | 1963.0813 | -3550 | -400 | -1986.9187 | 49.67% | 79.8% | 95% | 0% | 2867 | -356
[5 empty] | 2019-03-08 | 22 | 1595 | 2545 | -338 | 1 | 0 | 2883 | 2395.4658 | 2395.4658 | 2395.4658 | 2229.4312 | 780 | 200 | 3209.4312 | 80.24% | 95% | 0% | -386.7277 | 2008.7381 | -3550 | -400 | -1941.2619 | 48.53% | 79.8% | 95% | 0% | 2883 | -338
[5 empty] | 2019-03-08 | 23 | 1595.5 | 2548 | -316 | 1 | 0 | 2864 | 2365.7049 | 2365.7049 | 2365.7049 | 2229.4312 | 780 | 200 | 3209.4312 | 80.24% | 95% | 0% | -361.5561 | 2004.1488 | -3550 | -400 | -1945.8512 | 48.65% | 79.8% | 95% | 0% | 2864 | -316
[5 empty] | 2019-03-08 | 24 | 1596 | 2575 | -300 | 1 | 0 | 2875 | 2382.9349 | 2382.9349 | 2382.9349 | 2229.4312 | 780 | 200 | 3209.4312 | 80.24% | 95% | 0% | -343.2494 | 2039.6854 | -3550 | -400 | -1910.3146 | 47.76% | 79.79% | 95% | 0% | 2875 | -300
[5 empty] | 2019-03-08 | 25 | 1596.5 | 2592 | -302 | 1 | 0 | 2894 | 2412.6958 | 2412.6958 | 2412.6958 | 2229.4312 | 780 | 200 | 3209.4312 | 80.24% | 95% | 0% | -345.5378 | 2067.158 | -3550 | -400 | -1882.842 | 47.07% | 79.79% | 95% | 0% | 2894 | -302
[5 empty] | 2019-03-08 | 26 | 1597 | 2574 | -304 | 1 | 0 | 2878 | 2387.634 | 2387.634 | 2387.634 | 2229.4312 | 780 | 200 | 3209.4312 | 80.24% | 95% | 0% | -347.8261 | 2039.8079 | -3550 | -400 | -1910.1921 | 47.75% | 79.79% | 95% | 0% | 2878 | -304
[5 empty] | 2019-03-08 | 27 | 1597.5 | 2529 | -321 | 1 | 0 | 2850 | 2343.7758 | 2343.7758 | 2343.7758 | 2229.4312 | 780 | 200 | 3209.4312 | 80.24% | 95% | 0% | -367.2769 | 1976.4989 | -3550 | -400 | -1973.5011 | 49.34% | 79.78% | 95% | 0% | 2850 | -321
[5 empty] | 2019-03-08 | 28 | 1598 | 2474 | -321 | 1 | 0 | 2795 | 2257.6257 | 2257.6257 | 2257.6257 | 2229.4312 | 780 | 200 | 3209.4312 | 80.24% | 95% | 0% | -367.2769 | 1890.3488 | -3550 | -400 | -2059.6512 | 51.49% | 79.78% | 95% | 0% | 2795 | -321
[5 empty] | 2019-03-08 | 29 | 1598.5 | 2459 | -315 | 1 | 0 | 2774 | 2224.7321 | 2224.7321 | 2224.7321 | 2227.8648 | 780 | 200 | 3207.8648 | 80.2% | 95% | 0% | -360.4119 | 1864.3202 | -3550 | -400 | -2085.6798 | 52.14% | 79.78% | 95% | 0% | 2774 | -315
[5 empty] | 2019-03-08 | 30 | 1599 | 2461 | -298 | 1 | 0 | 2759 | 2201.2366 | 2201.2366 | 2201.2366 | 2227.8648 | 780 | 200 | 3207.8648 | 80.2% | 95% | 0% | -340.9611 | 1860.2755 | -3550 | -400 | -2089.7245 | 52.24% | 79.78% | 95% | 0% | 2759 | -298
[5 empty] | 2019-03-08 | 31 | 1599.5 | 2487 | -266 | 1 | 0 | 2753 | 2191.8384 | 2191.8384 | 2191.8384 | 2227.8648 | 780 | 200 | 3207.8648 | 80.2% | 95% | 0% | -304.3478 | 1887.4906 | -3550 | -400 | -2062.5094 | 51.56% | 79.77% | 95% | 0% | 2753 | -266
[5 empty] | 2019-03-08 | 32 | 1600 | 2565 | -245 | 1 | 0 | 2810 | 2281.1212 | 2281.1212 | 2281.1212 | 2227.8648 | 780 | 200 | 3207.8648 | 80.2% | 95% | 0% | -280.3204 | 2000.8008 | -3550 | -400 | -1949.1992 | 48.73% | 79.77% | 95% | 0% | 2810 | -245
[5 empty] | 2019-03-08 | 33 | 1600.5 | 2658 | -229 | 1 | 0 | 2887 | 2401.7312 | 2401.7312 | 2401.7312 | 2226.2984 | 780 | 200 | 3206.2984 | 80.16% | 95% | 0% | -262.0137 | 2139.7175 | -3550 | -400 | -1810.2825 | 45.26% | 79.77% | 95% | 0% | 2887 | -229
[5 empty] | 2019-03-08 | 34 | 1601 | 2747 | -205 | 1 | 0 | 2952 | 2503.5449 | 2503.5449 | 2503.5449 | 2226.2984 | 780 | 200 | 3206.2984 | 80.16% | 95% | 0% | -234.5538 | 2268.9912 | -3550 | -400 | -1681.0088 | 42.03% | 79.75% | 95% | 0% | 2952 | -205
[5 empty] | 2019-03-08 | 35 | 1601.5 | 2830 | -194 | 1 | 0 | 3024 | 2616.3232 | 2616.3232 | 2616.3232 | 2226.2984 | 780 | 200 | 3206.2984 | 80.16% | 95% | 0% | -221.968 | 2394.3552 | -3550 | -400 | -1555.6448 | 38.89% | 79.75% | 95% | 0% | 3024 | -194
[5 empty] | 2019-03-08 | 36 | 1602 | 2869 | -190 | 1 | 0 | 3059 | 2671.1459 | 2671.1459 | 2671.1459 | 2226.2984 | 780 | 200 | 3206.2984 | 80.16% | 95% | 0% | -217.3913 | 2453.7546 | -3550 | -400 | -1496.2454 | 37.41% | 79.75% | 95% | 0% | 3059 | -190
[5 empty] | 2019-03-08 | 37 | 1602.5 | 2932 | -195 | 1 | 0 | 3127 | 2777.6587 | 2777.6587 | 2777.6587 | 2226.2984 | 780 | 200 | 3206.2984 | 80.16% | 95% | 0% | -223.1121 | 2554.5466 | -3550 | -400 | -1395.4534 | 34.89% | 79.75% | 95% | 0% | 3127 | -195
[5 empty] | 2019-03-08 | 38 | 1603 | 2919 | -201 | 1 | 0 | 3120 | 2766.6941 | 2766.6941 | 2766.6941 | 2226.2984 | 780 | 200 | 3206.2984 | 80.16% | 95% | 0% | -229.9771 | 2536.717 | -3550 | -400 | -1413.283 | 35.33% | 79.74% | 95% | 0% | 3120 | -201
[5 empty] | 2019-03-08 | 39 | 1603.5 | 2845 | -204 | 0 | 0 | 3049 | 2655.4823 | 2655.4823 | 2655.4823 | 2226.2984 | 780 | 200 | 3206.2984 | 80.16% | 95% | 0% | -233.4096 | 2422.0727 | -2750 | -200 | -527.9273 | 13.2% | 79.74% | 95% | 0% | 3049 | -204
[5 empty] | 2019-03-08 | 40 | 1604 | 2737 | -207 | 0 | 0 | 2944 | 2491.014 | 2491.014 | 2491.014 | 2226.2984 | 780 | 200 | 3206.2984 | 80.16% | 95% | 0% | -236.8421 | 2254.1719 | -2750 | -200 | -695.8281 | 17.4% | 79.73% | 95% | 0% | 2944 | -207
[5 empty] | 2019-03-08 | 41 | 1604.5 | 2594 | -209 | 0 | 0 | 2803 | 2270.1566 | 2270.1566 | 2270.1566 | 2224.7321 | 780 | 200 | 3204.7321 | 80.12% | 95% | 0% | -239.1304 | 2031.0262 | -2750 | -200 | -918.9738 | 22.97% | 79.72% | 95% | 0% | 2803 | -209
[5 empty] | 2019-03-08 | 42 | 1605 | 2454 | -210 | 0 | 0 | 2664 | 2052.432 | 2052.432 | 2052.432 | 2224.7321 | 780 | 200 | 3204.7321 | 80.12% | 95% | 0% | -240.2746 | 1812.1574 | -2750 | -200 | -1137.8426 | 28.45% | 79.71% | 95% | 0% | 2664 | -210
[5 empty] | 2019-03-08 | 43 | 1605.5 | 2317 | -210 | 0 | 0 | 2527 | 1837.8401 | 1837.8401 | 1837.8401 | 2224.7321 | 780 | 200 | 3204.7321 | 80.12% | 95% | 0% | -240.2746 | 1597.5655 | -2750 | -200 | -1352.4345 | 33.81% | 79.71% | 95% | 0% | 2527 | -210
[5 empty] | 2019-03-08 | 44 | 1606 | 2184 | -209 | 0 | 0 | 2393 | 1627.9472 | 1627.9472 | 1627.9472 | 2224.7321 | 780 | 200 | 3204.7321 | 80.12% | 95% | 0% | -239.1304 | 1388.8168 | -2750 | -200 | -1561.1832 | 39.03% | 79.71% | 95% | 0% | 2393 | -209
[5 empty] | 2019-03-08 | 45 | 1606.5 | 2029 | -206 | 0 | 0 | 2235 | 1380.4617 | 1380.4617 | 1380.4617 | 2224.7321 | 780 | 200 | 3204.7321 | 80.12% | 95% | 0% | -235.6979 | 1144.7637 | -2750 | -200 | -1805.2363 | 45.13% | 79.7% | 95% | 0% | 2235 | -206
[5 empty] | 2019-03-08 | 46 | 1607 | 1913 | -203 | 0 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 2224.7321 | 780 | 200 | 3204.7321 | 80.12% | 95% | 0% | -232.2654 | 961.7989 | -2750 | -200 | -1988.2011 | 49.71% | 79.7% | 95% | 0% | 2116 | -203
[5 empty] | 2019-03-08 | 47 | 1607.5 | 1775 | -207 | 0 | 0 | 1982 | 984.1715 | 984.1715 | 984.1715 | 2223.1657 | 780 | 200 | 3203.1657 | 80.08% | 95% | 0% | -236.8421 | 747.3294 | -2750 | -200 | -2202.6706 | 55.07% | 79.69% | 95% | 0% | 1982 | -207
[5 empty] | 2019-03-08 | 48 | 1608 | 1693 | -211 | 0 | 0 | 1904 | 861.9951 | 861.9951 | 861.9951 | 2223.1657 | 780 | 200 | 3203.1657 | 80.08% | 95% | 0% | -241.4188 | 620.5763 | -2750 | -200 | -2329.4237 | 58.24% | 79.68% | 95% | 0% | 1904 | -211
[5 empty] | 2019-03-09 | 1 | 1608.5 | 1671 | -209 | 0 | 0 | 1880 | 824.4023 | 824.4023 | 824.4023 | 2223.1657 | 780 | 200 | 3203.1657 | 80.08% | 95% | 0% | -239.1304 | 585.2719 | -2750 | -200 | -2364.7281 | 59.12% | 79.67% | 95% | 0% | 1880 | -209
[5 empty] | 2019-03-09 | 2 | 1609 | 1693 | -208 | 0 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 2223.1657 | 780 | 200 | 3203.1657 | 80.08% | 95% | 0% | -237.9863 | 619.3097 | -2750 | -200 | -2330.6903 | 58.27% | 79.67% | 95% | 0% | 1901 | -208
[5 empty] | 2019-03-09 | 3 | 1609.5 | 1656 | -208 | 0 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 2221.5993 | 780 | 200 | 3201.5993 | 80.04% | 95% | 0% | -237.9863 | 561.3542 | -2750 | -200 | -2388.6458 | 59.72% | 79.66% | 95% | 0% | 1864 | -208
[5 empty] | 2019-03-09 | 4 | 1610 | 1594 | -207 | 0 | 0 | 1801 | 700.6595 | 700.6595 | 700.6595 | 2221.5993 | 780 | 200 | 3201.5993 | 80.04% | 95% | 0% | -236.8421 | 463.8174 | -2750 | -200 | -2486.1826 | 62.15% | 79.65% | 95% | 0% | 1801 | -207
[5 empty] | 2019-03-09 | 5 | 1610.5 | 1541 | -205 | 0 | 0 | 1746 | 614.5095 | 614.5095 | 614.5095 | 2221.5993 | 780 | 200 | 3201.5993 | 80.04% | 95% | 0% | -234.5538 | 379.9557 | -2750 | -200 | -2570.0443 | 64.25% | 79.65% | 95% | 0% | 1746 | -205
[5 empty] | 2019-03-09 | 6 | 1611 | 1525 | -203 | 0 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 2221.5993 | 780 | 200 | 3201.5993 | 80.04% | 95% | 0% | -232.2654 | 354.0495 | -2750 | -200 | -2595.9505 | 64.9% | 79.64% | 95% | 0% | 1728 | -203
[5 empty] | 2019-03-09 | 7 | 1611.5 | 1494 | -197 | 0 | 0 | 1691 | 528.3594 | 528.3594 | 528.3594 | 2220.033 | 780 | 200 | 3200.033 | 80% | 95% | 0% | -225.4005 | 302.959 | -2750 | -200 | -2647.041 | 66.18% | 79.64% | 95% | 0% | 1691 | -197
[5 empty] | 2019-03-09 | 8 | 1612 | 1478 | -191 | 0 | 0 | 1669 | 493.8994 | 493.8994 | 493.8994 | 2220.033 | 780 | 200 | 3200.033 | 80% | 95% | 0% | -218.5355 | 275.364 | -2750 | -200 | -2674.636 | 66.87% | 79.63% | 95% | 0% | 1669 | -191
[5 empty] | 2019-03-09 | 9 | 1612.5 | 1460 | -190 | 0 | 0 | 1650 | 464.1385 | 464.1385 | 464.1385 | 2220.033 | 780 | 200 | 3200.033 | 80% | 95% | 0% | -217.3913 | 246.7472 | -2750 | -200 | -2703.2528 | 67.58% | 79.62% | 95% | 0% | 1650 | -190
[5 empty] | 2019-03-09 | 10 | 1613 | 1452 | -189 | 0 | 0 | 1641 | 450.0412 | 450.0412 | 450.0412 | 2220.033 | 780 | 200 | 3200.033 | 80% | 95% | 0% | -216.2471 | 233.7941 | -2750 | -200 | -2716.2059 | 67.91% | 79.62% | 95% | 0% | 1641 | -189
[5 empty] | 2019-03-09 | 11 | 1613.5 | 1477 | -190 | 0 | 0 | 1667 | 490.7667 | 490.7667 | 490.7667 | 2220.033 | 780 | 200 | 3200.033 | 80% | 95% | 0% | -217.3913 | 273.3754 | -2750 | -200 | -2676.6246 | 66.92% | 79.62% | 95% | 0% | 1667 | -190
[5 empty] | 2019-03-09 | 12 | 1614 | 1504 | -191 | 0 | 0 | 1695 | 534.6249 | 534.6249 | 534.6249 | 2220.033 | 780 | 200 | 3200.033 | 80% | 95% | 0% | -218.5355 | 316.0894 | -2750 | -200 | -2633.9106 | 65.85% | 79.61% | 95% | 0% | 1695 | -191
[5 empty] | 2019-03-09 | 13 | 1614.5 | 1619 | -185 | 0 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 2220.033 | 780 | 200 | 3200.033 | 80% | 95% | 0% | -211.6705 | 493.6881 | -2750 | -200 | -2456.3119 | 61.41% | 79.61% | 95% | 0% | 1804 | -185
[5 empty] | 2019-03-09 | 14 | 1615 | 1691 | -179 | 0 | 0 | 1870 | 808.7387 | 808.7387 | 808.7387 | 2218.4666 | 780 | 200 | 3198.4666 | 79.96% | 95% | 0% | -204.8055 | 603.9332 | -2750 | -200 | -2346.0668 | 58.65% | 79.61% | 95% | 0% | 1870 | -179
[5 empty] | 2019-03-09 | 15 | 1615.5 | 1803 | -201 | 0 | 0 | 2004 | 1018.6315 | 1018.6315 | 1018.6315 | 2218.4666 | 780 | 200 | 3198.4666 | 79.96% | 95% | 0% | -229.9771 | 788.6544 | -2750 | -200 | -2161.3456 | 54.03% | 79.61% | 95% | 0% | 2004 | -201
[5 empty] | 2019-03-09 | 16 | 1616 | 1841 | -243 | 1 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 2218.4666 | 780 | 200 | 3198.4666 | 79.96% | 95% | 0% | -278.032 | 865.9086 | -3550 | -400 | -3084.0914 | 77.1% | 79.61% | 95% | 0% | 2084 | -243
[5 empty] | 2019-03-09 | 17 | 1616.5 | 1870 | -309 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 2218.4666 | 780 | 200 | 3198.4666 | 79.96% | 95% | 0% | -353.5469 | 939.1983 | -3550 | -400 | -3010.8017 | 75.27% | 79.6% | 95% | 0% | 2179 | -309
[5 empty] | 2019-03-09 | 18 | 1617 | 1848 | -372 | 1 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 2218.4666 | 780 | 200 | 3198.4666 | 79.96% | 95% | 0% | -425.6293 | 931.3369 | -3550 | -400 | -3018.6631 | 75.47% | 79.6% | 95% | 0% | 2220 | -372
[5 empty] | 2019-03-09 | 19 | 1617.5 | 1798 | -452 | 1 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 2216.9002 | 780 | 200 | 3196.9002 | 79.92% | 95% | 0% | -517.1625 | 886.7947 | -3550 | -400 | -3063.2053 | 76.58% | 79.6% | 95% | 0% | 2250 | -452
[5 empty] | 2019-03-09 | 20 | 1618 | 1719 | -518 | 1 | 0 | 2237 | 1383.5944 | 1383.5944 | 1383.5944 | 2216.9002 | 780 | 200 | 3196.9002 | 79.92% | 95% | 0% | -592.6773 | 790.917 | -3550 | -400 | -3159.083 | 78.98% | 79.6% | 95% | 0% | 2237 | -518
[5 empty] | 2019-03-09 | 21 | 1618.5 | 1680 | -535 | 1 | 0 | 2215 | 1349.1344 | 1349.1344 | 1349.1344 | 2216.9002 | 780 | 200 | 3196.9002 | 79.92% | 95% | 0% | -612.1281 | 737.0062 | -3550 | -400 | -3212.9938 | 80.32% | 79.59% | 95% | 0% | 2215 | -535
[5 empty] | 2019-03-09 | 22 | 1619 | 1523 | -656 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 2216.9002 | 780 | 200 | 3196.9002 | 79.92% | 95% | 0% | -750.5721 | 542.1732 | -3550 | -400 | -3407.8268 | 85.2% | 79.59% | 95% | 0% | 2179 | -656
[5 empty] | 2019-03-09 | 23 | 1619.5 | 1406 | -700 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 2216.9002 | 780 | 200 | 3196.9002 | 79.92% | 95% | 0% | -800.9153 | 377.4853 | -3550 | -400 | -3572.5147 | 89.31% | 79.59% | 95% | 0% | 2106 | -700
[5 empty] | 2019-03-09 | 24 | 1620 | 1294 | -768 | 1 | 0 | 2062 | 1109.4806 | 1109.4806 | 1109.4806 | 2216.9002 | 780 | 200 | 3196.9002 | 79.92% | 95% | 0% | -878.7185 | 230.7621 | -3550 | -400 | -3719.2379 | 92.98% | 79.58% | 95% | 0% | 2062 | -768
[5 empty] | 2019-03-09 | 25 | 1620.5 | 1291 | -761 | 1 | 0 | 2052 | 1093.817 | 1093.817 | 1093.817 | 2216.9002 | 780 | 200 | 3196.9002 | 79.92% | 95% | 0% | -870.7094 | 223.1076 | -3550 | -400 | -3726.8924 | 93.17% | 79.57% | 95% | 0% | 2052 | -761
[5 empty] | 2019-03-09 | 26 | 1621 | 1289 | -760 | 1 | 0 | 2049 | 1089.1179 | 1089.1179 | 1089.1179 | 2216.9002 | 780 | 200 | 3196.9002 | 79.92% | 95% | 0% | -869.5652 | 219.5527 | -3550 | -400 | -3730.4473 | 93.26% | 79.57% | 95% | 0% | 2049 | -760
[5 empty] | 2019-03-09 | 27 | 1621.5 | 1309 | -729 | 1 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 2215.3339 | 780 | 200 | 3195.3339 | 79.88% | 95% | 0% | -834.0961 | 237.7918 | -3550 | -400 | -3712.2082 | 92.81% | 79.57% | 95% | 0% | 2038 | -729
[5 empty] | 2019-03-09 | 28 | 1622 | 1410 | -631 | 1 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 2215.3339 | 780 | 200 | 3195.3339 | 79.88% | 95% | 0% | -721.968 | 354.619 | -3550 | -400 | -3595.381 | 89.88% | 79.57% | 95% | 0% | 2041 | -631
[5 empty] | 2019-03-09 | 29 | 1622.5 | 1472 | -571 | 1 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 2215.3339 | 780 | 200 | 3195.3339 | 79.88% | 95% | 0% | -653.3181 | 426.4016 | -3550 | -400 | -3523.5984 | 88.09% | 79.57% | 95% | 0% | 2043 | -571
[5 empty] | 2019-03-09 | 30 | 1623 | 1520 | -540 | 1 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 2215.3339 | 780 | 200 | 3195.3339 | 79.88% | 95% | 0% | -617.849 | 488.4989 | -3550 | -400 | -3461.5011 | 86.54% | 79.56% | 95% | 0% | 2060 | -540
[5 empty] | 2019-03-09 | 31 | 1623.5 | 1685 | -442 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 2215.3339 | 780 | 200 | 3195.3339 | 79.88% | 95% | 0% | -505.7208 | 705.5735 | -3550 | -400 | -3244.4265 | 81.11% | 79.56% | 95% | 0% | 2127 | -442
[5 empty] | 2019-03-09 | 32 | 1624 | 1803 | -379 | 1 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 2215.3339 | 780 | 200 | 3195.3339 | 79.88% | 95% | 0% | -433.6384 | 863.8059 | -3550 | -400 | -3086.1941 | 77.15% | 79.55% | 95% | 0% | 2182 | -379
[5 empty] | 2019-03-09 | 33 | 1624.5 | 1981 | -304 | 1 | 0 | 2285 | 1458.7799 | 1458.7799 | 1458.7799 | 2215.3339 | 780 | 200 | 3195.3339 | 79.88% | 95% | 0% | -347.8261 | 1110.9538 | -3550 | -400 | -2839.0462 | 70.98% | 79.55% | 95% | 0% | 2285 | -304
[5 empty] | 2019-03-09 | 34 | 1625 | 2182 | -242 | 1 | 0 | 2424 | 1676.5045 | 1676.5045 | 1676.5045 | 2213.7675 | 780 | 200 | 3193.7675 | 79.84% | 95% | 0% | -276.8879 | 1399.6167 | -3550 | -400 | -2550.3833 | 63.76% | 79.54% | 95% | 0% | 2424 | -242
[5 empty] | 2019-03-09 | 35 | 1625.5 | 2371 | -202 | 1 | 0 | 2573 | 1909.8928 | 1909.8928 | 1909.8928 | 2213.7675 | 780 | 200 | 3193.7675 | 79.84% | 95% | 0% | -231.1213 | 1678.7715 | -3550 | -400 | -2271.2285 | 56.78% | 79.54% | 95% | 0% | 2573 | -202
[5 empty] | 2019-03-09 | 36 | 1626 | 2531 | -175 | 1 | 0 | 2706 | 2118.2193 | 2118.2193 | 2118.2193 | 2213.7675 | 780 | 200 | 3193.7675 | 79.84% | 95% | 0% | -200.2288 | 1917.9905 | -3550 | -400 | -2032.0095 | 50.8% | 79.54% | 95% | 0% | 2706 | -175
[5 empty] | 2019-03-09 | 37 | 1626.5 | 2645 | -165 | 1 | 0 | 2810 | 2281.1212 | 2281.1212 | 2281.1212 | 2213.7675 | 780 | 200 | 3193.7675 | 79.84% | 95% | 0% | -188.7872 | 2092.334 | -3550 | -400 | -1857.666 | 46.44% | 79.52% | 95% | 0% | 2810 | -165
[5 empty] | 2019-03-09 | 38 | 1627 | 2698 | -155 | 1 | 0 | 2853 | 2348.4749 | 2348.4749 | 2348.4749 | 2213.7675 | 780 | 200 | 3193.7675 | 79.84% | 95% | 0% | -177.3455 | 2171.1293 | -3550 | -400 | -1778.8707 | 44.47% | 79.52% | 95% | 0% | 2853 | -155
[5 empty] | 2019-03-09 | 39 | 1627.5 | 2644 | -145 | 0 | 0 | 2789 | 2248.2275 | 2248.2275 | 2248.2275 | 2213.7675 | 780 | 200 | 3193.7675 | 79.84% | 95% | 0% | -165.9039 | 2082.3236 | -2750 | -200 | -867.6764 | 21.69% | 79.52% | 95% | 0% | 2789 | -145
[5 empty] | 2019-03-09 | 40 | 1628 | 2556 | -135 | 0 | 0 | 2691 | 2094.7238 | 2094.7238 | 2094.7238 | 2212.2012 | 780 | 200 | 3192.2012 | 79.81% | 95% | 0% | -154.4622 | 1940.2616 | -2750 | -200 | -1009.7384 | 25.24% | 79.51% | 95% | 0% | 2691 | -135
[5 empty] | 2019-03-09 | 41 | 1628.5 | 2531 | -124 | 0 | 0 | 2655 | 2038.3347 | 2038.3347 | 2038.3347 | 2212.2012 | 780 | 200 | 3192.2012 | 79.81% | 95% | 0% | -141.8764 | 1896.4583 | -2750 | -200 | -1053.5417 | 26.34% | 79.51% | 95% | 0% | 2655 | -124
[5 empty] | 2019-03-09 | 42 | 1629 | 2469 | -114 | 0 | 0 | 2583 | 1925.5565 | 1925.5565 | 1925.5565 | 2212.2012 | 780 | 200 | 3192.2012 | 79.81% | 95% | 0% | -130.4348 | 1795.1217 | -2750 | -200 | -1154.8783 | 28.87% | 79.51% | 95% | 0% | 2583 | -114
[5 empty] | 2019-03-09 | 43 | 1629.5 | 2401 | -106 | 0 | 0 | 2507 | 1806.5128 | 1806.5128 | 1806.5128 | 2212.2012 | 780 | 200 | 3192.2012 | 79.81% | 95% | 0% | -121.2815 | 1685.2313 | -2750 | -200 | -1264.7687 | 31.62% | 79.51% | 95% | 0% | 2507 | -106
[5 empty] | 2019-03-09 | 44 | 1630 | 2344 | -98 | 0 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 2212.2012 | 780 | 200 | 3192.2012 | 79.81% | 95% | 0% | -112.1281 | 1592.5709 | -2750 | -200 | -1357.4291 | 33.94% | 79.5% | 95% | 0% | 2442 | -98
[5 empty] | 2019-03-09 | 45 | 1630.5 | 2242 | -93 | 0 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 2212.2012 | 780 | 200 | 3192.2012 | 79.81% | 95% | 0% | -106.4073 | 1430.6908 | -2750 | -200 | -1519.3092 | 37.98% | 79.5% | 95% | 0% | 2335 | -93
[5 empty] | 2019-03-09 | 46 | 1631 | 2167 | -89 | 0 | 0 | 2256 | 1413.3553 | 1413.3553 | 1413.3553 | 2212.2012 | 780 | 200 | 3192.2012 | 79.81% | 95% | 0% | -101.8307 | 1311.5247 | -2750 | -200 | -1638.4753 | 40.96% | 79.49% | 95% | 0% | 2256 | -89
[5 empty] | 2019-03-09 | 47 | 1631.5 | 2060 | -82 | 0 | 0 | 2142 | 1234.7898 | 1234.7898 | 1234.7898 | 2212.2012 | 780 | 200 | 3192.2012 | 79.81% | 95% | 0% | -93.8215 | 1140.9683 | -2750 | -200 | -1809.0317 | 45.23% | 79.49% | 95% | 0% | 2142 | -82
[5 empty] | 2019-03-09 | 48 | 1632 | 1989 | -76 | 0 | 0 | 2065 | 1114.1797 | 1114.1797 | 1114.1797 | 2212.2012 | 780 | 200 | 3192.2012 | 79.81% | 95% | 0% | -86.9565 | 1027.2232 | -2750 | -200 | -1922.7768 | 48.07% | 79.49% | 95% | 0% | 2065 | -76
[5 empty] | 2019-03-10 | 1 | 1632.5 | 1975 | -74 | 0 | 0 | 2049 | 1089.1179 | 1089.1179 | 1089.1179 | 2210.6348 | 780 | 200 | 3190.6348 | 79.77% | 95% | 0% | -84.6682 | 1004.4497 | -2750 | -200 | -1945.5503 | 48.64% | 79.48% | 95% | 0% | 2049 | -74
[5 empty] | 2019-03-10 | 2 | 1633 | 2003 | -73 | 0 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 2210.6348 | 780 | 200 | 3190.6348 | 79.77% | 95% | 0% | -83.524 | 1047.8857 | -2750 | -200 | -1902.1143 | 47.55% | 79.48% | 95% | 0% | 2076 | -73
[5 empty] | 2019-03-10 | 3 | 1633.5 | 1952 | -72 | 0 | 0 | 2024 | 1049.9588 | 1049.9588 | 1049.9588 | 2210.6348 | 780 | 200 | 3190.6348 | 79.77% | 95% | 0% | -82.3799 | 967.5789 | -2750 | -200 | -1982.4211 | 49.56% | 79.47% | 95% | 0% | 2024 | -72
[5 empty] | 2019-03-10 | 4 | 1634 | 1915 | -70 | 0 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 2210.6348 | 780 | 200 | 3190.6348 | 79.77% | 95% | 0% | -80.0915 | 908.779 | -2750 | -200 | -2041.221 | 51.03% | 79.46% | 95% | 0% | 1985 | -70
[5 empty] | 2019-03-10 | 5 | 1634.5 | 1870 | -74 | 0 | 0 | 1944 | 924.6496 | 924.6496 | 924.6496 | 2210.6348 | 780 | 200 | 3190.6348 | 79.77% | 95% | 0% | -84.6682 | 839.9814 | -2750 | -200 | -2110.0186 | 52.75% | 79.46% | 95% | 0% | 1944 | -74
[5 empty] | 2019-03-10 | 6 | 1635 | 1828 | -78 | 0 | 0 | 1906 | 865.1278 | 865.1278 | 865.1278 | 2210.6348 | 780 | 200 | 3190.6348 | 79.77% | 95% | 0% | -89.2449 | 775.8829 | -2750 | -200 | -2174.1171 | 54.35% | 79.46% | 95% | 0% | 1906 | -78
[5 empty] | 2019-03-10 | 7 | 1635.5 | 1788 | -80 | 0 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 2209.0684 | 780 | 200 | 3189.0684 | 79.73% | 95% | 0% | -91.5332 | 714.0728 | -2750 | -200 | -2235.9272 | 55.9% | 79.45% | 95% | 0% | 1868 | -80
[5 empty] | 2019-03-10 | 8 | 1636 | 1746 | -82 | 0 | 0 | 1828 | 742.9514 | 742.9514 | 742.9514 | 2209.0684 | 780 | 200 | 3189.0684 | 79.73% | 95% | 0% | -93.8215 | 649.1298 | -2750 | -200 | -2300.8702 | 57.52% | 79.45% | 95% | 0% | 1828 | -82
[5 empty] | 2019-03-10 | 9 | 1636.5 | 1716 | -86 | 0 | 0 | 1802 | 702.2259 | 702.2259 | 702.2259 | 2209.0684 | 780 | 200 | 3189.0684 | 79.73% | 95% | 0% | -98.3982 | 603.8277 | -2750 | -200 | -2346.1723 | 58.65% | 79.45% | 95% | 0% | 1802 | -86
[5 empty] | 2019-03-10 | 10 | 1637 | 1697 | -91 | 0 | 0 | 1788 | 680.2968 | 680.2968 | 680.2968 | 2209.0684 | 780 | 200 | 3189.0684 | 79.73% | 95% | 0% | -104.119 | 576.1778 | -2750 | -200 | -2373.8222 | 59.35% | 79.45% | 95% | 0% | 1788 | -91
[5 empty] | 2019-03-10 | 11 | 1637.5 | 1700 | -95 | 0 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 2209.0684 | 780 | 200 | 3189.0684 | 79.73% | 95% | 0% | -108.6957 | 582.5657 | -2750 | -200 | -2367.4343 | 59.19% | 79.44% | 95% | 0% | 1795 | -95
[5 empty] | 2019-03-10 | 12 | 1638 | 1713 | -100 | 1 | 0 | 1813 | 719.4559 | 719.4559 | 719.4559 | 2209.0684 | 780 | 200 | 3189.0684 | 79.73% | 95% | 0% | -114.4165 | 605.0394 | -3550 | -400 | -3344.9606 | 83.62% | 79.43% | 95% | 0% | 1813 | -100
[5 empty] | 2019-03-10 | 13 | 1638.5 | 1781 | -103 | 1 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 2207.5021 | 780 | 200 | 3187.5021 | 79.69% | 95% | 0% | -117.849 | 712.8188 | -3550 | -400 | -3237.1812 | 80.93% | 79.42% | 95% | 0% | 1884 | -103
[5 empty] | 2019-03-10 | 14 | 1639 | 1814 | -107 | 1 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 2207.5021 | 780 | 200 | 3187.5021 | 79.69% | 95% | 0% | -122.4256 | 766.1976 | -3550 | -400 | -3183.8024 | 79.6% | 79.42% | 95% | 0% | 1921 | -107
[5 empty] | 2019-03-10 | 15 | 1639.5 | 1855 | -125 | 1 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 2207.5021 | 780 | 200 | 3187.5021 | 79.69% | 95% | 0% | -143.0206 | 838.0182 | -3550 | -400 | -3111.9818 | 77.8% | 79.41% | 95% | 0% | 1980 | -125
[5 empty] | 2019-03-10 | 16 | 1640 | 1842 | -174 | 1 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 2207.5021 | 780 | 200 | 3187.5021 | 79.69% | 95% | 0% | -199.0847 | 838.3432 | -3550 | -400 | -3111.6568 | 77.79% | 79.41% | 95% | 0% | 2016 | -174
[5 empty] | 2019-03-10 | 17 | 1640.5 | 1877 | -220 | 1 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 2207.5021 | 780 | 200 | 3187.5021 | 79.69% | 95% | 0% | -251.7162 | 912.5871 | -3550 | -400 | -3037.4129 | 75.94% | 79.4% | 95% | 0% | 2097 | -220
[5 empty] | 2019-03-10 | 18 | 1641 | 1915 | -258 | 1 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 2207.5021 | 780 | 200 | 3187.5021 | 79.69% | 95% | 0% | -295.1945 | 988.1526 | -3550 | -400 | -2961.8474 | 74.05% | 79.4% | 95% | 0% | 2173 | -258
[5 empty] | 2019-03-10 | 19 | 1641.5 | 1926 | -318 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 2205.9357 | 780 | 200 | 3185.9357 | 79.65% | 95% | 0% | -363.8444 | 1030.7146 | -3550 | -400 | -2919.2854 | 72.98% | 79.4% | 95% | 0% | 2244 | -318
[5 empty] | 2019-03-10 | 20 | 1642 | 1943 | -370 | 1 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 2205.9357 | 780 | 200 | 3185.9357 | 79.65% | 95% | 0% | -423.341 | 1079.2971 | -3550 | -400 | -2870.7029 | 71.77% | 79.4% | 95% | 0% | 2313 | -370
[5 empty] | 2019-03-10 | 21 | 1642.5 | 1946 | -399 | 1 | 0 | 2345 | 1552.7617 | 1552.7617 | 1552.7617 | 2205.9357 | 780 | 200 | 3185.9357 | 79.65% | 95% | 0% | -456.5217 | 1096.24 | -3550 | -400 | -2853.76 | 71.34% | 79.39% | 95% | 0% | 2345 | -399
[5 empty] | 2019-03-10 | 22 | 1643 | 1902 | -440 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 2205.9357 | 780 | 200 | 3185.9357 | 79.65% | 95% | 0% | -503.4325 | 1044.6302 | -3550 | -400 | -2905.3698 | 72.63% | 79.39% | 95% | 0% | 2342 | -440
[5 empty] | 2019-03-10 | 23 | 1643.5 | 1819 | -491 | 1 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 2205.9357 | 780 | 200 | 3185.9357 | 79.65% | 95% | 0% | -561.7849 | 936.1541 | -3550 | -400 | -3013.8459 | 75.35% | 79.38% | 95% | 0% | 2310 | -491
[5 empty] | 2019-03-10 | 24 | 1644 | 1717 | -551 | 1 | 0 | 2268 | 1432.1517 | 1432.1517 | 1432.1517 | 2204.3693 | 780 | 200 | 3184.3693 | 79.61% | 95% | 0% | -630.4348 | 801.7169 | -3550 | -400 | -3148.2831 | 78.71% | 79.38% | 95% | 0% | 2268 | -551
[5 empty] | 2019-03-10 | 25 | 1644.5 | 1624 | -596 | 1 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 2204.3693 | 780 | 200 | 3184.3693 | 79.61% | 95% | 0% | -681.9222 | 675.044 | -3550 | -400 | -3274.956 | 81.87% | 79.38% | 95% | 0% | 2220 | -596
[5 empty] | 2019-03-10 | 26 | 1645 | 1545 | -654 | 1 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 2204.3693 | 780 | 200 | 3184.3693 | 79.61% | 95% | 0% | -748.2838 | 575.7888 | -3550 | -400 | -3374.2112 | 84.36% | 79.37% | 95% | 0% | 2199 | -654
[5 empty] | 2019-03-10 | 27 | 1645.5 | 1454 | -672 | 1 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 2204.3693 | 780 | 200 | 3184.3693 | 79.61% | 95% | 0% | -768.8787 | 440.8492 | -3550 | -400 | -3509.1508 | 87.73% | 79.36% | 95% | 0% | 2126 | -672
[5 empty] | 2019-03-10 | 28 | 1646 | 1404 | -695 | 1 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 2204.3693 | 780 | 200 | 3184.3693 | 79.61% | 95% | 0% | -795.1945 | 372.2416 | -3550 | -400 | -3577.7584 | 89.44% | 79.36% | 95% | 0% | 2099 | -695
[5 empty] | 2019-03-10 | 29 | 1646.5 | 1413 | -672 | 1 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 2204.3693 | 780 | 200 | 3184.3693 | 79.61% | 95% | 0% | -768.8787 | 376.6283 | -3550 | -400 | -3573.3717 | 89.33% | 79.36% | 95% | 0% | 2085 | -672
[5 empty] | 2019-03-10 | 30 | 1647 | 1512 | -585 | 1 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 2204.3693 | 780 | 200 | 3184.3693 | 79.61% | 95% | 0% | -669.3364 | 494.967 | -3550 | -400 | -3455.033 | 86.38% | 79.36% | 95% | 0% | 2097 | -585
[5 empty] | 2019-03-10 | 31 | 1647.5 | 1587 | -566 | 1 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 2202.803 | 780 | 200 | 3182.803 | 79.57% | 95% | 0% | -647.5973 | 604.4225 | -3550 | -400 | -3345.5775 | 83.64% | 79.35% | 95% | 0% | 2153 | -566
[5 empty] | 2019-03-10 | 32 | 1648 | 1780 | -462 | 1 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 2202.803 | 780 | 200 | 3182.803 | 79.57% | 95% | 0% | -528.6041 | 862.8221 | -3550 | -400 | -3087.1779 | 77.18% | 79.35% | 95% | 0% | 2242 | -462
[5 empty] | 2019-03-10 | 33 | 1648.5 | 1952 | -410 | 1 | 0 | 2362 | 1579.3899 | 1579.3899 | 1579.3899 | 2202.803 | 780 | 200 | 3182.803 | 79.57% | 95% | 0% | -469.1076 | 1110.2824 | -3550 | -400 | -2839.7176 | 70.99% | 79.34% | 95% | 0% | 2362 | -410
[5 empty] | 2019-03-10 | 34 | 1649 | 2149 | -323 | 1 | 0 | 2472 | 1751.69 | 1751.69 | 1751.69 | 2202.803 | 780 | 200 | 3182.803 | 79.57% | 95% | 0% | -369.5652 | 1382.1248 | -3550 | -400 | -2567.8752 | 64.2% | 79.34% | 95% | 0% | 2472 | -323
[5 empty] | 2019-03-10 | 35 | 1649.5 | 2334 | -258 | 1 | 0 | 2592 | 1939.6538 | 1939.6538 | 1939.6538 | 2202.803 | 780 | 200 | 3182.803 | 79.57% | 95% | 0% | -295.1945 | 1644.4592 | -3550 | -400 | -2305.5408 | 57.64% | 79.33% | 95% | 0% | 2592 | -258
[5 empty] | 2019-03-10 | 36 | 1650 | 2462 | -229 | 1 | 0 | 2691 | 2094.7238 | 2094.7238 | 2094.7238 | 2202.803 | 780 | 200 | 3182.803 | 79.57% | 95% | 0% | -262.0137 | 1832.7101 | -3550 | -400 | -2117.2899 | 52.93% | 79.33% | 95% | 0% | 2691 | -229
[5 empty] | 2019-03-10 | 37 | 1650.5 | 2569 | -222 | 1 | 0 | 2791 | 2251.3603 | 2251.3603 | 2251.3603 | 2202.803 | 780 | 200 | 3182.803 | 79.57% | 95% | 0% | -254.0046 | 1997.3557 | -3550 | -400 | -1952.6443 | 48.82% | 79.33% | 95% | 0% | 2791 | -222
[5 empty] | 2019-03-10 | 38 | 1651 | 2624 | -218 | 1 | 0 | 2842 | 2331.2448 | 2331.2448 | 2331.2448 | 2202.803 | 780 | 200 | 3182.803 | 79.57% | 95% | 0% | -249.4279 | 2081.8169 | -3550 | -400 | -1868.1831 | 46.7% | 79.33% | 95% | 0% | 2842 | -218
[5 empty] | 2019-03-10 | 39 | 1651.5 | 2574 | -221 | 0 | 0 | 2795 | 2257.6257 | 2257.6257 | 2257.6257 | 2201.2366 | 780 | 200 | 3181.2366 | 79.53% | 95% | 0% | -252.8604 | 2004.7653 | -2750 | -200 | -945.2347 | 23.63% | 79.33% | 95% | 0% | 2795 | -221
[5 empty] | 2019-03-10 | 40 | 1652 | 2501 | -224 | 0 | 0 | 2725 | 2147.9802 | 2147.9802 | 2147.9802 | 2201.2366 | 780 | 200 | 3181.2366 | 79.53% | 95% | 0% | -256.2929 | 1891.6873 | -2750 | -200 | -1058.3127 | 26.46% | 79.32% | 95% | 0% | 2725 | -224
[5 empty] | 2019-03-10 | 41 | 1652.5 | 2453 | -223 | 0 | 0 | 2676 | 2071.2284 | 2071.2284 | 2071.2284 | 2201.2366 | 780 | 200 | 3181.2366 | 79.53% | 95% | 0% | -255.1487 | 1816.0796 | -2750 | -200 | -1133.9204 | 28.35% | 79.32% | 95% | 0% | 2676 | -223
[5 empty] | 2019-03-10 | 42 | 1653 | 2353 | -222 | 0 | 0 | 2575 | 1913.0256 | 1913.0256 | 1913.0256 | 2201.2366 | 780 | 200 | 3181.2366 | 79.53% | 95% | 0% | -254.0046 | 1659.021 | -2750 | -200 | -1290.979 | 32.27% | 79.31% | 95% | 0% | 2575 | -222
[5 empty] | 2019-03-10 | 43 | 1653.5 | 2232 | -221 | 0 | 0 | 2453 | 1721.9291 | 1721.9291 | 1721.9291 | 2201.2366 | 780 | 200 | 3181.2366 | 79.53% | 95% | 0% | -252.8604 | 1469.0687 | -2750 | -200 | -1480.9313 | 37.02% | 79.3% | 95% | 0% | 2453 | -221
[5 empty] | 2019-03-10 | 44 | 1654 | 2098 | -220 | 0 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 2201.2366 | 780 | 200 | 3181.2366 | 79.53% | 95% | 0% | -251.7162 | 1258.7537 | -2750 | -200 | -1691.2463 | 42.28% | 79.3% | 95% | 0% | 2318 | -220
[5 empty] | 2019-03-10 | 45 | 1654.5 | 1955 | -223 | 0 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 2201.2366 | 780 | 200 | 3181.2366 | 79.53% | 95% | 0% | -255.1487 | 1036.0302 | -2750 | -200 | -1913.9698 | 47.85% | 79.3% | 95% | 0% | 2178 | -223
[5 empty] | 2019-03-10 | 46 | 1655 | 1831 | -225 | 0 | 0 | 2056 | 1100.0824 | 1100.0824 | 1100.0824 | 2201.2366 | 780 | 200 | 3181.2366 | 79.53% | 95% | 0% | -257.4371 | 842.6454 | -2750 | -200 | -2107.3546 | 52.68% | 79.3% | 95% | 0% | 2056 | -225
[5 empty] | 2019-03-10 | 47 | 1655.5 | 1679 | -232 | 0 | 0 | 1911 | 872.9596 | 872.9596 | 872.9596 | 2199.6702 | 780 | 200 | 3179.6702 | 79.49% | 95% | 0% | -265.4462 | 607.5134 | -2750 | -200 | -2342.4866 | 58.56% | 79.29% | 95% | 0% | 1911 | -232
[5 empty] | 2019-03-10 | 48 | 1656 | 1591 | -238 | 0 | 0 | 1829 | 744.5177 | 744.5177 | 744.5177 | 2199.6702 | 780 | 200 | 3179.6702 | 79.49% | 95% | 0% | -272.3112 | 472.2065 | -2750 | -200 | -2477.7935 | 61.94% | 79.29% | 95% | 0% | 1829 | -238
[5 empty] | 2019-03-11 | 1 | 1656.5 | 1574 | -237 | 0 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 2199.6702 | 780 | 200 | 3179.6702 | 79.49% | 95% | 0% | -271.167 | 445.1561 | -2750 | -200 | -2504.8439 | 62.62% | 79.28% | 95% | 0% | 1811 | -237
[5 empty] | 2019-03-11 | 2 | 1657 | 1621 | -235 | 0 | 0 | 1856 | 786.8096 | 786.8096 | 786.8096 | 2199.6702 | 780 | 200 | 3179.6702 | 79.49% | 95% | 0% | -268.8787 | 517.9308 | -2750 | -200 | -2432.0692 | 60.8% | 79.28% | 95% | 0% | 1856 | -235
[5 empty] | 2019-03-11 | 3 | 1657.5 | 1603 | -236 | 0 | 0 | 1839 | 760.1814 | 760.1814 | 760.1814 | 2199.6702 | 780 | 200 | 3179.6702 | 79.49% | 95% | 0% | -270.0229 | 490.1585 | -2750 | -200 | -2459.8415 | 61.5% | 79.27% | 95% | 0% | 1839 | -236
[5 empty] | 2019-03-11 | 4 | 1658 | 1563 | -237 | 0 | 0 | 1800 | 699.0932 | 699.0932 | 699.0932 | 2199.6702 | 780 | 200 | 3179.6702 | 79.49% | 95% | 0% | -271.167 | 427.9261 | -2750 | -200 | -2522.0739 | 63.05% | 79.26% | 95% | 0% | 1800 | -237
[5 empty] | 2019-03-11 | 5 | 1658.5 | 1533 | -234 | 0 | 0 | 1767 | 647.4031 | 647.4031 | 647.4031 | 2199.6702 | 780 | 200 | 3179.6702 | 79.49% | 95% | 0% | -267.7346 | 379.6686 | -2750 | -200 | -2570.3314 | 64.26% | 79.26% | 95% | 0% | 1767 | -234
[5 empty] | 2019-03-11 | 6 | 1659 | 1519 | -232 | 0 | 0 | 1751 | 622.3413 | 622.3413 | 622.3413 | 2199.6702 | 780 | 200 | 3179.6702 | 79.49% | 95% | 0% | -265.4462 | 356.8951 | -2750 | -200 | -2593.1049 | 64.83% | 79.25% | 95% | 0% | 1751 | -232
[5 empty] | 2019-03-11 | 7 | 1659.5 | 1511 | -228 | 0 | 0 | 1739 | 603.5449 | 603.5449 | 603.5449 | 2199.6702 | 780 | 200 | 3179.6702 | 79.49% | 95% | 0% | -260.8696 | 342.6754 | -2750 | -200 | -2607.3246 | 65.18% | 79.25% | 95% | 0% | 1739 | -228
[5 empty] | 2019-03-11 | 8 | 1660 | 1486 | -224 | 0 | 0 | 1710 | 558.1204 | 558.1204 | 558.1204 | 2199.6702 | 780 | 200 | 3179.6702 | 79.49% | 95% | 0% | -256.2929 | 301.8275 | -2750 | -200 | -2648.1725 | 66.2% | 79.24% | 95% | 0% | 1710 | -224
[5 empty] | 2019-03-11 | 9 | 1660.5 | 1483 | -225 | 0 | 0 | 1708 | 554.9876 | 554.9876 | 554.9876 | 2198.1039 | 780 | 200 | 3178.1039 | 79.45% | 95% | 0% | -257.4371 | 297.5506 | -2750 | -200 | -2652.4494 | 66.31% | 79.23% | 95% | 0% | 1708 | -225
[5 empty] | 2019-03-11 | 10 | 1661 | 1499 | -226 | 0 | 0 | 1725 | 581.6158 | 581.6158 | 581.6158 | 2198.1039 | 780 | 200 | 3178.1039 | 79.45% | 95% | 0% | -258.5812 | 323.0346 | -2750 | -200 | -2626.9654 | 65.67% | 79.23% | 95% | 0% | 1725 | -226
[5 empty] | 2019-03-11 | 11 | 1661.5 | 1585 | -223 | 1 | 0 | 1808 | 711.6241 | 711.6241 | 711.6241 | 2198.1039 | 780 | 200 | 3178.1039 | 79.45% | 95% | 0% | -255.1487 | 456.4753 | -3550 | -400 | -3493.5247 | 87.34% | 79.22% | 95% | 0% | 1808 | -223
[5 empty] | 2019-03-11 | 12 | 1662 | 1716 | -220 | 1 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 2198.1039 | 780 | 200 | 3178.1039 | 79.45% | 95% | 0% | -251.7162 | 660.4025 | -3550 | -400 | -3289.5975 | 82.24% | 79.22% | 95% | 0% | 1936 | -220
[5 empty] | 2019-03-11 | 13 | 1662.5 | 1984 | -216 | 1 | 0 | 2200 | 1325.6389 | 1325.6389 | 1325.6389 | 2198.1039 | 780 | 200 | 3178.1039 | 79.45% | 95% | 0% | -247.1396 | 1078.4993 | -3550 | -400 | -2871.5007 | 71.79% | 79.22% | 95% | 0% | 2200 | -216
[5 empty] | 2019-03-11 | 14 | 1663 | 2208 | -221 | 1 | 0 | 2429 | 1684.3364 | 1684.3364 | 1684.3364 | 2198.1039 | 780 | 200 | 3178.1039 | 79.45% | 95% | 0% | -252.8604 | 1431.4759 | -3550 | -400 | -2518.5241 | 62.96% | 79.21% | 95% | 0% | 2429 | -221
[5 empty] | 2019-03-11 | 15 | 1663.5 | 2401 | -273 | 1 | 0 | 2674 | 2068.0956 | 2068.0956 | 2068.0956 | 2198.1039 | 780 | 200 | 3178.1039 | 79.45% | 95% | 0% | -312.357 | 1755.7387 | -3550 | -400 | -2194.2613 | 54.86% | 79.2% | 95% | 0% | 2674 | -273
[5 empty] | 2019-03-11 | 16 | 1664 | 2378 | -351 | 1 | 0 | 2729 | 2154.2457 | 2154.2457 | 2154.2457 | 2198.1039 | 780 | 200 | 3178.1039 | 79.45% | 95% | 0% | -401.6018 | 1752.6438 | -3550 | -400 | -2197.3562 | 54.93% | 79.2% | 95% | 0% | 2729 | -351
[5 empty] | 2019-03-11 | 17 | 1664.5 | 2283 | -440 | 1 | 0 | 2723 | 2144.8475 | 2144.8475 | 2144.8475 | 2198.1039 | 780 | 200 | 3178.1039 | 79.45% | 95% | 0% | -503.4325 | 1641.415 | -3550 | -400 | -2308.585 | 57.71% | 79.2% | 95% | 0% | 2723 | -440
[5 empty] | 2019-03-11 | 18 | 1665 | 2158 | -525 | 1 | 0 | 2683 | 2082.1929 | 2082.1929 | 2082.1929 | 2196.5375 | 780 | 200 | 3176.5375 | 79.41% | 95% | 0% | -600.6865 | 1481.5064 | -3550 | -400 | -2468.4936 | 61.71% | 79.2% | 95% | 0% | 2683 | -525
[5 empty] | 2019-03-11 | 19 | 1665.5 | 2060 | -594 | 1 | 0 | 2654 | 2036.7683 | 2036.7683 | 2036.7683 | 2196.5375 | 780 | 200 | 3176.5375 | 79.41% | 95% | 0% | -679.6339 | 1357.1345 | -3550 | -400 | -2592.8655 | 64.82% | 79.2% | 95% | 0% | 2654 | -594
[5 empty] | 2019-03-11 | 20 | 1666 | 1947 | -657 | 1 | 0 | 2604 | 1958.4501 | 1958.4501 | 1958.4501 | 2196.5375 | 780 | 200 | 3176.5375 | 79.41% | 95% | 0% | -751.7162 | 1206.7339 | -3550 | -400 | -2743.2661 | 68.58% | 79.19% | 95% | 0% | 2604 | -657
[5 empty] | 2019-03-11 | 21 | 1666.5 | 1833 | -703 | 1 | 0 | 2536 | 1851.9373 | 1851.9373 | 1851.9373 | 2196.5375 | 780 | 200 | 3176.5375 | 79.41% | 95% | 0% | -804.3478 | 1047.5895 | -3550 | -400 | -2902.4105 | 72.56% | 79.18% | 95% | 0% | 2536 | -703
[5 empty] | 2019-03-11 | 22 | 1667 | 1761 | -740 | 1 | 0 | 2501 | 1797.1146 | 1797.1146 | 1797.1146 | 2196.5375 | 780 | 200 | 3176.5375 | 79.41% | 95% | 0% | -846.6819 | 950.4327 | -3550 | -400 | -2999.5673 | 74.99% | 79.18% | 95% | 0% | 2501 | -740
[5 empty] | 2019-03-11 | 23 | 1667.5 | 1731 | -756 | 1 | 0 | 2487 | 1775.1855 | 1775.1855 | 1775.1855 | 2196.5375 | 780 | 200 | 3176.5375 | 79.41% | 95% | 0% | -864.9886 | 910.1969 | -3550 | -400 | -3039.8031 | 76% | 79.17% | 95% | 0% | 2487 | -756
[5 empty] | 2019-03-11 | 24 | 1668 | 1701 | -774 | 1 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 2196.5375 | 780 | 200 | 3176.5375 | 79.41% | 95% | 0% | -885.5835 | 870.8056 | -3550 | -400 | -3079.1944 | 76.98% | 79.16% | 95% | 0% | 2475 | -774
[5 empty] | 2019-03-11 | 25 | 1668.5 | 1714 | -763 | 1 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 2194.9711 | 780 | 200 | 3174.9711 | 79.37% | 95% | 0% | -872.9977 | 886.5241 | -3550 | -400 | -3063.4759 | 76.59% | 79.15% | 95% | 0% | 2477 | -763
[5 empty] | 2019-03-11 | 26 | 1669 | 1728 | -735 | 1 | 0 | 2463 | 1737.5927 | 1737.5927 | 1737.5927 | 2194.9711 | 780 | 200 | 3174.9711 | 79.37% | 95% | 0% | -840.9611 | 896.6316 | -3550 | -400 | -3053.3684 | 76.33% | 79.15% | 95% | 0% | 2463 | -735
[5 empty] | 2019-03-11 | 27 | 1669.5 | 1744 | -721 | 1 | 0 | 2465 | 1740.7255 | 1740.7255 | 1740.7255 | 2194.9711 | 780 | 200 | 3174.9711 | 79.37% | 95% | 0% | -824.9428 | 915.7827 | -3550 | -400 | -3034.2173 | 75.86% | 79.14% | 95% | 0% | 2465 | -721
[5 empty] | 2019-03-11 | 28 | 1670 | 1801 | -669 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 2194.9711 | 780 | 200 | 3174.9711 | 79.37% | 95% | 0% | -765.4462 | 983.1111 | -3550 | -400 | -2966.8889 | 74.17% | 79.13% | 95% | 0% | 2470 | -669
[5 empty] | 2019-03-11 | 29 | 1670.5 | 1894 | -612 | 1 | 0 | 2506 | 1804.9464 | 1804.9464 | 1804.9464 | 2194.9711 | 780 | 200 | 3174.9711 | 79.37% | 95% | 0% | -700.2288 | 1104.7176 | -3550 | -400 | -2845.2824 | 71.13% | 79.13% | 95% | 0% | 2506 | -612
[5 empty] | 2019-03-11 | 30 | 1671 | 1991 | -545 | 1 | 0 | 2536 | 1851.9373 | 1851.9373 | 1851.9373 | 2194.9711 | 780 | 200 | 3174.9711 | 79.37% | 95% | 0% | -623.5698 | 1228.3676 | -3550 | -400 | -2721.6324 | 68.04% | 79.13% | 95% | 0% | 2536 | -545
[5 empty] | 2019-03-11 | 31 | 1671.5 | 2138 | -454 | 1 | 0 | 2592 | 1939.6538 | 1939.6538 | 1939.6538 | 2193.4048 | 780 | 200 | 3173.4048 | 79.34% | 95% | 0% | -519.4508 | 1420.203 | -3550 | -400 | -2529.797 | 63.24% | 79.13% | 95% | 0% | 2592 | -454
[5 empty] | 2019-03-11 | 32 | 1672 | 2362 | -358 | 1 | 0 | 2720 | 2140.1484 | 2140.1484 | 2140.1484 | 2193.4048 | 780 | 200 | 3173.4048 | 79.34% | 95% | 0% | -409.611 | 1730.5374 | -3550 | -400 | -2219.4626 | 55.49% | 79.12% | 95% | 0% | 2720 | -358
[5 empty] | 2019-03-11 | 33 | 1672.5 | 2613 | -267 | 1 | 0 | 2880 | 2390.7667 | 2390.7667 | 2390.7667 | 2193.4048 | 780 | 200 | 3173.4048 | 79.34% | 95% | 0% | -305.492 | 2085.2747 | -3550 | -400 | -1864.7253 | 46.62% | 79.11% | 95% | 0% | 2880 | -267
[5 empty] | 2019-03-11 | 34 | 1673 | 2809 | -193 | 1 | 0 | 3002 | 2581.8631 | 2581.8631 | 2581.8631 | 2193.4048 | 780 | 200 | 3173.4048 | 79.34% | 95% | 0% | -220.8238 | 2361.0394 | -3550 | -400 | -1588.9606 | 39.72% | 79.11% | 95% | 0% | 3002 | -193
[5 empty] | 2019-03-11 | 35 | 1673.5 | 2933 | -156 | 1 | 0 | 3089 | 2718.1369 | 2718.1369 | 2718.1369 | 2193.4048 | 780 | 200 | 3173.4048 | 79.34% | 95% | 0% | -178.4897 | 2539.6471 | -3550 | -400 | -1410.3529 | 35.26% | 79.11% | 95% | 0% | 3089 | -156
[5 empty] | 2019-03-11 | 36 | 1674 | 3035 | -138 | 1 | 0 | 3173 | 2849.7115 | 2849.7115 | 2849.7115 | 2193.4048 | 780 | 200 | 3173.4048 | 79.34% | 95% | 0% | -157.8947 | 2691.8167 | -3550 | -400 | -1258.1833 | 31.45% | 79.1% | 95% | 0% | 3173 | -138
[5 empty] | 2019-03-11 | 37 | 1674.5 | 3109 | -143 | 1 | 0 | 3252 | 2973.4542 | 2973.4542 | 2973.4542 | 2193.4048 | 780 | 200 | 3173.4048 | 79.34% | 95% | 0% | -163.6156 | 2809.8387 | -3550 | -400 | -1140.1613 | 28.5% | 79.09% | 95% | 0% | 3252 | -143
[5 empty] | 2019-03-11 | 38 | 1675 | 3098 | -151 | 1 | 0 | 3249 | 2968.7552 | 2968.7552 | 2968.7552 | 2193.4048 | 780 | 200 | 3173.4048 | 79.34% | 95% | 0% | -172.7689 | 2795.9863 | -3550 | -400 | -1154.0137 | 28.85% | 79.09% | 95% | 0% | 3249 | -151
[5 empty] | 2019-03-11 | 39 | 1675.5 | 3046 | -160 | 0 | 0 | 3206 | 2901.4015 | 2901.4015 | 2901.4015 | 2191.8384 | 780 | 200 | 3171.8384 | 79.3% | 95% | 0% | -183.0664 | 2718.3351 | -2750 | -200 | -231.6649 | 5.792% | 79.09% | 95% | 0% | 3206 | -160
[5 empty] | 2019-03-11 | 40 | 1676 | 2954 | -169 | 0 | 0 | 3123 | 2771.3932 | 2771.3932 | 2771.3932 | 2191.8384 | 780 | 200 | 3171.8384 | 79.3% | 95% | 0% | -193.3638 | 2578.0294 | -2750 | -200 | -371.9706 | 9.299% | 79.08% | 95% | 0% | 3123 | -169
[5 empty] | 2019-03-11 | 41 | 1676.5 | 2817 | -174 | 0 | 0 | 2991 | 2564.6331 | 2564.6331 | 2564.6331 | 2191.8384 | 780 | 200 | 3171.8384 | 79.3% | 95% | 0% | -199.0847 | 2365.5485 | -2750 | -200 | -584.4515 | 14.61% | 79.07% | 95% | 0% | 2991 | -174
[5 empty] | 2019-03-11 | 42 | 1677 | 2669 | -178 | 0 | 0 | 2847 | 2339.0767 | 2339.0767 | 2339.0767 | 2191.8384 | 780 | 200 | 3171.8384 | 79.3% | 95% | 0% | -203.6613 | 2135.4153 | -2750 | -200 | -814.5847 | 20.36% | 79.07% | 95% | 0% | 2847 | -178
[5 empty] | 2019-03-11 | 43 | 1677.5 | 2487 | -180 | 0 | 0 | 2667 | 2057.1311 | 2057.1311 | 2057.1311 | 2191.8384 | 780 | 200 | 3171.8384 | 79.3% | 95% | 0% | -205.9497 | 1851.1814 | -2750 | -200 | -1098.8186 | 27.47% | 79.07% | 95% | 0% | 2667 | -180
[5 empty] | 2019-03-11 | 44 | 1678 | 2292 | -183 | 0 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 2190.2721 | 780 | 200 | 3170.2721 | 79.26% | 95% | 0% | -209.3822 | 1547.007 | -2750 | -200 | -1402.993 | 35.07% | 79.06% | 95% | 0% | 2475 | -183
[5 empty] | 2019-03-11 | 45 | 1678.5 | 2104 | -191 | 0 | 0 | 2295 | 1474.4435 | 1474.4435 | 1474.4435 | 2190.2721 | 780 | 200 | 3170.2721 | 79.26% | 95% | 0% | -218.5355 | 1255.9081 | -2750 | -200 | -1694.0919 | 42.35% | 79.06% | 95% | 0% | 2295 | -191
[5 empty] | 2019-03-11 | 46 | 1679 | 1932 | -200 | 0 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 2190.2721 | 780 | 200 | 3170.2721 | 79.26% | 95% | 0% | -228.833 | 990.2932 | -2750 | -200 | -1959.7068 | 48.99% | 79.05% | 95% | 0% | 2132 | -200
[5 empty] | 2019-03-11 | 47 | 1679.5 | 1757 | -213 | 0 | 0 | 1970 | 965.3751 | 965.3751 | 965.3751 | 2190.2721 | 780 | 200 | 3170.2721 | 79.26% | 95% | 0% | -243.7071 | 721.668 | -2750 | -200 | -2228.332 | 55.71% | 79.05% | 95% | 0% | 1970 | -213
[5 empty] | 2019-03-11 | 48 | 1680 | 1646 | -226 | 0 | 0 | 1872 | 811.8714 | 811.8714 | 811.8714 | 2190.2721 | 780 | 200 | 3170.2721 | 79.26% | 95% | 0% | -258.5812 | 553.2902 | -2750 | -200 | -2396.7098 | 59.92% | 79.04% | 95% | 0% | 1872 | -226
[5 empty] | 2019-03-12 | 1 | 1680.5 | 1615 | -231 | 0 | 0 | 1846 | 771.1459 | 771.1459 | 771.1459 | 2190.2721 | 780 | 200 | 3170.2721 | 79.26% | 95% | 0% | -264.3021 | 506.8439 | -2750 | -200 | -2443.1561 | 61.08% | 79.04% | 95% | 0% | 1846 | -231
[5 empty] | 2019-03-12 | 2 | 1681 | 1631 | -236 | 0 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 2188.7057 | 780 | 200 | 3168.7057 | 79.22% | 95% | 0% | -270.0229 | 534.0167 | -2750 | -200 | -2415.9833 | 60.4% | 79.04% | 95% | 0% | 1867 | -236
[5 empty] | 2019-03-12 | 3 | 1681.5 | 1601 | -237 | 0 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 2188.7057 | 780 | 200 | 3168.7057 | 79.22% | 95% | 0% | -271.167 | 487.448 | -2750 | -200 | -2462.552 | 61.56% | 79.04% | 95% | 0% | 1838 | -237
[5 empty] | 2019-03-12 | 4 | 1682 | 1552 | -237 | 0 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 2188.7057 | 780 | 200 | 3168.7057 | 79.22% | 95% | 0% | -271.167 | 410.6961 | -2750 | -200 | -2539.3039 | 63.48% | 79.01% | 95% | 0% | 1789 | -237
[5 empty] | 2019-03-12 | 5 | 1682.5 | 1515 | -238 | 0 | 0 | 1753 | 625.474 | 625.474 | 625.474 | 2188.7057 | 780 | 200 | 3168.7057 | 79.22% | 95% | 0% | -272.3112 | 353.1628 | -2750 | -200 | -2596.8372 | 64.92% | 79.01% | 95% | 0% | 1753 | -238
[5 empty] | 2019-03-12 | 6 | 1683 | 1501 | -238 | 0 | 0 | 1739 | 603.5449 | 603.5449 | 603.5449 | 2188.7057 | 780 | 200 | 3168.7057 | 79.22% | 95% | 0% | -272.3112 | 331.2337 | -2750 | -200 | -2618.7663 | 65.47% | 79.01% | 95% | 0% | 1739 | -238
[5 empty] | 2019-03-12 | 7 | 1683.5 | 1468 | -235 | 0 | 0 | 1703 | 547.1558 | 547.1558 | 547.1558 | 2187.1393 | 780 | 200 | 3167.1393 | 79.18% | 95% | 0% | -268.8787 | 278.2771 | -2750 | -200 | -2671.7229 | 66.79% | 79% | 95% | 0% | 1703 | -235
[5 empty] | 2019-03-12 | 8 | 1684 | 1461 | -232 | 0 | 0 | 1693 | 531.4922 | 531.4922 | 531.4922 | 2187.1393 | 780 | 200 | 3167.1393 | 79.18% | 95% | 0% | -265.4462 | 266.0459 | -2750 | -200 | -2683.9541 | 67.1% | 79% | 95% | 0% | 1693 | -232
[5 empty] | 2019-03-12 | 9 | 1684.5 | 1454 | -232 | 0 | 0 | 1686 | 520.5276 | 520.5276 | 520.5276 | 2187.1393 | 780 | 200 | 3167.1393 | 79.18% | 95% | 0% | -265.4462 | 255.0814 | -2750 | -200 | -2694.9186 | 67.37% | 78.99% | 95% | 0% | 1686 | -232
[5 empty] | 2019-03-12 | 10 | 1685 | 1475 | -231 | 0 | 0 | 1706 | 551.8549 | 551.8549 | 551.8549 | 2187.1393 | 780 | 200 | 3167.1393 | 79.18% | 95% | 0% | -264.3021 | 287.5528 | -2750 | -200 | -2662.4472 | 66.56% | 78.98% | 95% | 0% | 1706 | -231
[5 empty] | 2019-03-12 | 11 | 1685.5 | 1547 | -235 | 0 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 2187.1393 | 780 | 200 | 3167.1393 | 79.18% | 95% | 0% | -268.8787 | 402.0199 | -2750 | -200 | -2547.9801 | 63.7% | 78.98% | 95% | 0% | 1782 | -235
[5 empty] | 2019-03-12 | 12 | 1686 | 1642 | -239 | 0 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 2187.1393 | 780 | 200 | 3167.1393 | 79.18% | 95% | 0% | -273.4554 | 552.5133 | -2750 | -200 | -2397.4867 | 59.94% | 78.98% | 95% | 0% | 1881 | -239
[5 empty] | 2019-03-12 | 13 | 1686.5 | 1914 | -233 | 0 | 0 | 2147 | 1242.6216 | 1242.6216 | 1242.6216 | 2187.1393 | 780 | 200 | 3167.1393 | 79.18% | 95% | 0% | -266.5904 | 976.0312 | -2750 | -200 | -1973.9688 | 49.35% | 78.98% | 95% | 0% | 2147 | -233
[5 empty] | 2019-03-12 | 14 | 1687 | 2155 | -226 | 1 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 2185.573 | 780 | 200 | 3165.573 | 79.14% | 95% | 0% | -258.5812 | 1350.5696 | -3550 | -400 | -2599.4304 | 64.99% | 78.98% | 95% | 0% | 2381 | -226
[5 empty] | 2019-03-12 | 15 | 1687.5 | 2420 | -225 | 1 | 0 | 2645 | 2022.6711 | 2022.6711 | 2022.6711 | 2185.573 | 780 | 200 | 3165.573 | 79.14% | 95% | 0% | -257.4371 | 1765.234 | -3550 | -400 | -2184.766 | 54.62% | 78.97% | 95% | 0% | 2645 | -225
[5 empty] | 2019-03-12 | 16 | 1688 | 2539 | -226 | 1 | 0 | 2765 | 2210.6348 | 2210.6348 | 2210.6348 | 2184.0066 | 780 | 200 | 3164.0066 | 79.1% | 95% | 0% | -258.5812 | 1952.0536 | -3550 | -400 | -1997.9464 | 49.95% | 78.97% | 95% | 0% | 2765 | -226
[5 empty] | 2019-03-12 | 17 | 1688.5 | 2637 | -234 | 1 | 0 | 2871 | 2376.6694 | 2376.6694 | 2376.6694 | 2184.0066 | 780 | 200 | 3164.0066 | 79.1% | 95% | 0% | -267.7346 | 2108.9349 | -3550 | -400 | -1841.0651 | 46.03% | 78.96% | 95% | 0% | 2871 | -234
[5 empty] | 2019-03-12 | 18 | 1689 | 2665 | -237 | 1 | 0 | 2902 | 2425.2267 | 2425.2267 | 2425.2267 | 2184.0066 | 780 | 200 | 3164.0066 | 79.1% | 95% | 0% | -271.167 | 2154.0597 | -3550 | -400 | -1795.9403 | 44.9% | 78.96% | 95% | 0% | 2902 | -237
[5 empty] | 2019-03-12 | 19 | 1689.5 | 2700 | -248 | 1 | 0 | 2948 | 2497.2795 | 2497.2795 | 2497.2795 | 2184.0066 | 780 | 200 | 3164.0066 | 79.1% | 95% | 0% | -283.7529 | 2213.5266 | -3550 | -400 | -1736.4734 | 43.41% | 78.96% | 95% | 0% | 2948 | -248
[5 empty] | 2019-03-12 | 20 | 1690 | 2704 | -260 | 1 | 0 | 2964 | 2522.3413 | 2522.3413 | 2522.3413 | 2184.0066 | 780 | 200 | 3164.0066 | 79.1% | 95% | 0% | -297.4828 | 2224.8585 | -3550 | -400 | -1725.1415 | 43.13% | 78.96% | 95% | 0% | 2964 | -260
[5 empty] | 2019-03-12 | 21 | 1690.5 | 2722 | -276 | 1 | 0 | 2998 | 2575.5977 | 2575.5977 | 2575.5977 | 2184.0066 | 780 | 200 | 3164.0066 | 79.1% | 95% | 0% | -315.7895 | 2259.8082 | -3550 | -400 | -1690.1918 | 42.25% | 78.96% | 95% | 0% | 2998 | -276
[5 empty] | 2019-03-12 | 22 | 1691 | 2732 | -282 | 1 | 0 | 3014 | 2600.6595 | 2600.6595 | 2600.6595 | 2184.0066 | 780 | 200 | 3164.0066 | 79.1% | 95% | 0% | -322.6545 | 2278.0051 | -3550 | -400 | -1671.9949 | 41.8% | 78.96% | 95% | 0% | 3014 | -282
[5 empty] | 2019-03-12 | 23 | 1691.5 | 2727 | -288 | 1 | 0 | 3015 | 2602.2259 | 2602.2259 | 2602.2259 | 2184.0066 | 780 | 200 | 3164.0066 | 79.1% | 95% | 0% | -329.5195 | 2272.7064 | -3550 | -400 | -1677.2936 | 41.93% | 78.95% | 95% | 0% | 3015 | -288
[5 empty] | 2019-03-12 | 24 | 1692 | 2719 | -299 | 1 | 0 | 3018 | 2606.925 | 2606.925 | 2606.925 | 2184.0066 | 780 | 200 | 3164.0066 | 79.1% | 95% | 0% | -342.1053 | 2264.8197 | -3550 | -400 | -1685.1803 | 42.13% | 78.95% | 95% | 0% | 3018 | -299
[5 empty] | 2019-03-12 | 25 | 1692.5 | 2727 | -312 | 1 | 0 | 3039 | 2639.8186 | 2639.8186 | 2639.8186 | 2184.0066 | 780 | 200 | 3164.0066 | 79.1% | 95% | 0% | -356.9794 | 2282.8392 | -3550 | -400 | -1667.1608 | 41.68% | 78.95% | 95% | 0% | 3039 | -312
[5 empty] | 2019-03-12 | 26 | 1693 | 2702 | -320 | 1 | 0 | 3022 | 2613.1904 | 2613.1904 | 2613.1904 | 2184.0066 | 780 | 200 | 3164.0066 | 79.1% | 95% | 0% | -366.1327 | 2247.0577 | -3550 | -400 | -1702.9423 | 42.57% | 78.93% | 95% | 0% | 3022 | -320
[5 empty] | 2019-03-12 | 27 | 1693.5 | 2676 | -336 | 1 | 0 | 3012 | 2597.5268 | 2597.5268 | 2597.5268 | 2182.4402 | 780 | 200 | 3162.4402 | 79.06% | 95% | 0% | -384.4394 | 2213.0874 | -3550 | -400 | -1736.9126 | 43.42% | 78.93% | 95% | 0% | 3012 | -336
[5 empty] | 2019-03-12 | 28 | 1694 | 2603 | -362 | 1 | 0 | 2965 | 2523.9077 | 2523.9077 | 2523.9077 | 2182.4402 | 780 | 200 | 3162.4402 | 79.06% | 95% | 0% | -414.1876 | 2109.72 | -3550 | -400 | -1840.28 | 46.01% | 78.93% | 95% | 0% | 2965 | -362
[5 empty] | 2019-03-12 | 29 | 1694.5 | 2515 | -409 | 1 | 0 | 2924 | 2459.6867 | 2459.6867 | 2459.6867 | 2182.4402 | 780 | 200 | 3162.4402 | 79.06% | 95% | 0% | -467.9634 | 1991.7233 | -3550 | -400 | -1958.2767 | 48.96% | 78.93% | 95% | 0% | 2924 | -409
[5 empty] | 2019-03-12 | 30 | 1695 | 2405 | -451 | 1 | 0 | 2856 | 2353.1739 | 2353.1739 | 2353.1739 | 2180.8739 | 780 | 200 | 3160.8739 | 79.02% | 95% | 0% | -516.0183 | 1837.1556 | -3550 | -400 | -2112.8444 | 52.82% | 78.93% | 95% | 0% | 2856 | -451
[5 empty] | 2019-03-12 | 31 | 1695.5 | 2316 | -464 | 1 | 0 | 2780 | 2234.1303 | 2234.1303 | 2234.1303 | 2180.8739 | 780 | 200 | 3160.8739 | 79.02% | 95% | 0% | -530.8924 | 1703.2378 | -3550 | -400 | -2246.7622 | 56.17% | 78.93% | 95% | 0% | 2780 | -464
[5 empty] | 2019-03-12 | 32 | 1696 | 2376 | -446 | 1 | 0 | 2822 | 2299.9176 | 2299.9176 | 2299.9176 | 2180.8739 | 780 | 200 | 3160.8739 | 79.02% | 95% | 0% | -510.2975 | 1789.6201 | -3550 | -400 | -2160.3799 | 54.01% | 78.92% | 95% | 0% | 2822 | -446
[5 empty] | 2019-03-12 | 33 | 1696.5 | 2450 | -419 | 1 | 0 | 2869 | 2373.5367 | 2373.5367 | 2373.5367 | 2180.8739 | 780 | 200 | 3160.8739 | 79.02% | 95% | 0% | -479.405 | 1894.1317 | -3550 | -400 | -2055.8683 | 51.4% | 78.92% | 95% | 0% | 2869 | -419
[5 empty] | 2019-03-12 | 34 | 1697 | 2583 | -363 | 1 | 0 | 2946 | 2494.1467 | 2494.1467 | 2494.1467 | 2180.8739 | 780 | 200 | 3160.8739 | 79.02% | 95% | 0% | -415.3318 | 2078.8149 | -3550 | -400 | -1871.1851 | 46.78% | 78.91% | 95% | 0% | 2946 | -363
[5 empty] | 2019-03-12 | 35 | 1697.5 | 2740 | -291 | 1 | 0 | 3031 | 2627.2877 | 2627.2877 | 2627.2877 | 2180.8739 | 780 | 200 | 3160.8739 | 79.02% | 95% | 0% | -332.9519 | 2294.3358 | -3550 | -400 | -1655.6642 | 41.39% | 78.89% | 95% | 0% | 3031 | -291
[5 empty] | 2019-03-12 | 36 | 1698 | 2852 | -244 | 1 | 0 | 3096 | 2729.1014 | 2729.1014 | 2729.1014 | 2179.3075 | 780 | 200 | 3159.3075 | 78.98% | 95% | 0% | -279.1762 | 2449.9252 | -3550 | -400 | -1500.0748 | 37.5% | 78.89% | 95% | 0% | 3096 | -244
[5 empty] | 2019-03-12 | 37 | 1698.5 | 2935 | -233 | 1 | 0 | 3168 | 2841.8796 | 2841.8796 | 2841.8796 | 2179.3075 | 780 | 200 | 3159.3075 | 78.98% | 95% | 0% | -266.5904 | 2575.2892 | -3550 | -400 | -1374.7108 | 34.37% | 78.89% | 95% | 0% | 3168 | -233
[5 empty] | 2019-03-12 | 38 | 1699 | 2995 | -230 | 0 | 0 | 3225 | 2931.1624 | 2931.1624 | 2931.1624 | 2179.3075 | 780 | 200 | 3159.3075 | 78.98% | 95% | 0% | -263.1579 | 2668.0045 | -2750 | -200 | -281.9955 | 7.05% | 78.89% | 95% | 0% | 3225 | -230
[5 empty] | 2019-03-12 | 39 | 1699.5 | 2919 | -232 | 0 | 0 | 3151 | 2815.2514 | 2815.2514 | 2815.2514 | 2179.3075 | 780 | 200 | 3159.3075 | 78.98% | 95% | 0% | -265.4462 | 2549.8052 | -2750 | -200 | -400.1948 | 10% | 78.88% | 95% | 0% | 3151 | -232
[5 empty] | 2019-03-12 | 40 | 1700 | 2843 | -235 | 0 | 0 | 3078 | 2700.9068 | 2700.9068 | 2700.9068 | 2179.3075 | 780 | 200 | 3159.3075 | 78.98% | 95% | 0% | -268.8787 | 2432.0281 | -2750 | -200 | -517.9719 | 12.95% | 78.88% | 95% | 0% | 3078 | -235
[5 empty] | 2019-03-12 | 41 | 1700.5 | 2755 | -237 | 0 | 0 | 2992 | 2566.1995 | 2566.1995 | 2566.1995 | 2179.3075 | 780 | 200 | 3159.3075 | 78.98% | 95% | 0% | -271.167 | 2295.0325 | -2750 | -200 | -654.9675 | 16.37% | 78.88% | 95% | 0% | 2992 | -237
[5 empty] | 2019-03-12 | 42 | 1701 | 2618 | -239 | 0 | 0 | 2857 | 2354.7403 | 2354.7403 | 2354.7403 | 2179.3075 | 780 | 200 | 3159.3075 | 78.98% | 95% | 0% | -273.4554 | 2081.2849 | -2750 | -200 | -868.7151 | 21.72% | 78.88% | 95% | 0% | 2857 | -239
[5 empty] | 2019-03-12 | 43 | 1701.5 | 2463 | -234 | 0 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 2179.3075 | 780 | 200 | 3159.3075 | 78.98% | 95% | 0% | -267.7346 | 1836.3875 | -2750 | -200 | -1113.6125 | 27.84% | 78.87% | 95% | 0% | 2697 | -234
[5 empty] | 2019-03-12 | 44 | 1702 | 2293 | -230 | 0 | 0 | 2523 | 1831.5746 | 1831.5746 | 1831.5746 | 2179.3075 | 780 | 200 | 3159.3075 | 78.98% | 95% | 0% | -263.1579 | 1568.4167 | -2750 | -200 | -1381.5833 | 34.54% | 78.86% | 95% | 0% | 2523 | -230
[5 empty] | 2019-03-12 | 45 | 1702.5 | 2132 | -232 | 0 | 0 | 2364 | 1582.5227 | 1582.5227 | 1582.5227 | 2179.3075 | 780 | 200 | 3159.3075 | 78.98% | 95% | 0% | -265.4462 | 1317.0764 | -2750 | -200 | -1632.9236 | 40.82% | 78.85% | 95% | 0% | 2364 | -232
[5 empty] | 2019-03-12 | 46 | 1703 | 1989 | -233 | 0 | 0 | 2222 | 1360.0989 | 1360.0989 | 1360.0989 | 2177.7411 | 780 | 200 | 3157.7411 | 78.94% | 95% | 0% | -266.5904 | 1093.5085 | -2750 | -200 | -1856.4915 | 46.41% | 78.84% | 95% | 0% | 2222 | -233
[5 empty] | 2019-03-12 | 47 | 1703.5 | 1840 | -240 | 0 | 0 | 2080 | 1137.6752 | 1137.6752 | 1137.6752 | 2177.7411 | 780 | 200 | 3157.7411 | 78.94% | 95% | 0% | -274.5995 | 863.0756 | -2750 | -200 | -2086.9244 | 52.17% | 78.83% | 95% | 0% | 2080 | -240
[5 empty] | 2019-03-12 | 48 | 1704 | 1712 | -246 | 0 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 2177.7411 | 780 | 200 | 3157.7411 | 78.94% | 95% | 0% | -281.4645 | 665.1142 | -2750 | -200 | -2284.8858 | 57.12% | 78.82% | 95% | 0% | 1958 | -246
[5 empty] | 2019-03-13 | 1 | 1704.5 | 1682 | -244 | 0 | 0 | 1926 | 896.4551 | 896.4551 | 896.4551 | 2177.7411 | 780 | 200 | 3157.7411 | 78.94% | 95% | 0% | -279.1762 | 617.2789 | -2750 | -200 | -2332.7211 | 58.32% | 78.81% | 95% | 0% | 1926 | -244
[5 empty] | 2019-03-13 | 2 | 1705 | 1709 | -241 | 0 | 0 | 1950 | 934.0478 | 934.0478 | 934.0478 | 2176.1748 | 780 | 200 | 3156.1748 | 78.9% | 95% | 0% | -275.7437 | 658.3041 | -2750 | -200 | -2291.6959 | 57.29% | 78.8% | 95% | 0% | 1950 | -241
[5 empty] | 2019-03-13 | 3 | 1705.5 | 1677 | -244 | 0 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 2176.1748 | 780 | 200 | 3156.1748 | 78.9% | 95% | 0% | -279.1762 | 609.447 | -2750 | -200 | -2340.553 | 58.51% | 78.8% | 95% | 0% | 1921 | -244
[5 empty] | 2019-03-13 | 4 | 1706 | 1628 | -247 | 0 | 0 | 1875 | 816.5705 | 816.5705 | 816.5705 | 2176.1748 | 780 | 200 | 3156.1748 | 78.9% | 95% | 0% | -282.6087 | 533.9618 | -2750 | -200 | -2416.0382 | 60.4% | 78.78% | 95% | 0% | 1875 | -247
[5 empty] | 2019-03-13 | 5 | 1706.5 | 1593 | -250 | 0 | 0 | 1843 | 766.4468 | 766.4468 | 766.4468 | 2176.1748 | 780 | 200 | 3156.1748 | 78.9% | 95% | 0% | -286.0412 | 480.4056 | -2750 | -200 | -2469.5944 | 61.74% | 78.78% | 95% | 0% | 1843 | -250
[5 empty] | 2019-03-13 | 6 | 1707 | 1573 | -253 | 0 | 0 | 1826 | 739.8186 | 739.8186 | 739.8186 | 2174.6084 | 780 | 200 | 3154.6084 | 78.87% | 95% | 0% | -289.4737 | 450.3449 | -2750 | -200 | -2499.6551 | 62.49% | 78.75% | 95% | 0% | 1826 | -253
[5 empty] | 2019-03-13 | 7 | 1707.5 | 1533 | -257 | 0 | 0 | 1790 | 683.4295 | 683.4295 | 683.4295 | 2174.6084 | 780 | 200 | 3154.6084 | 78.87% | 95% | 0% | -294.0503 | 389.3792 | -2750 | -200 | -2560.6208 | 64.02% | 78.75% | 95% | 0% | 1790 | -257
[5 empty] | 2019-03-13 | 8 | 1708 | 1482 | -262 | 0 | 0 | 1744 | 611.3768 | 611.3768 | 611.3768 | 2174.6084 | 780 | 200 | 3154.6084 | 78.87% | 95% | 0% | -299.7712 | 311.6056 | -2750 | -200 | -2638.3944 | 65.96% | 78.74% | 95% | 0% | 1744 | -262
[5 empty] | 2019-03-13 | 9 | 1708.5 | 1461 | -264 | 0 | 0 | 1725 | 581.6158 | 581.6158 | 581.6158 | 2174.6084 | 780 | 200 | 3154.6084 | 78.87% | 95% | 0% | -302.0595 | 279.5563 | -2750 | -200 | -2670.4437 | 66.76% | 78.74% | 95% | 0% | 1725 | -264
[5 empty] | 2019-03-13 | 10 | 1709 | 1477 | -266 | 0 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 2174.6084 | 780 | 200 | 3154.6084 | 78.87% | 95% | 0% | -304.3478 | 305.4626 | -2750 | -200 | -2644.5374 | 66.11% | 78.74% | 95% | 0% | 1743 | -266
[5 empty] | 2019-03-13 | 11 | 1709.5 | 1543 | -268 | 0 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 2174.6084 | 780 | 200 | 3154.6084 | 78.87% | 95% | 0% | -306.6362 | 409.687 | -2750 | -200 | -2540.313 | 63.51% | 78.73% | 95% | 0% | 1811 | -268
[5 empty] | 2019-03-13 | 12 | 1710 | 1649 | -269 | 0 | 0 | 1918 | 883.9242 | 883.9242 | 883.9242 | 2174.6084 | 780 | 200 | 3154.6084 | 78.87% | 95% | 0% | -307.7803 | 576.1438 | -2750 | -200 | -2373.8562 | 59.35% | 78.73% | 95% | 0% | 1918 | -269
[5 empty] | 2019-03-13 | 13 | 1710.5 | 1900 | -267 | 0 | 0 | 2167 | 1273.9489 | 1273.9489 | 1273.9489 | 2174.6084 | 780 | 200 | 3154.6084 | 78.87% | 95% | 0% | -305.492 | 968.4569 | -2750 | -200 | -1981.5431 | 49.54% | 78.73% | 95% | 0% | 2167 | -267
[5 empty] | 2019-03-13 | 14 | 1711 | 2105 | -269 | 0 | 0 | 2374 | 1598.1863 | 1598.1863 | 1598.1863 | 2174.6084 | 780 | 200 | 3154.6084 | 78.87% | 95% | 0% | -307.7803 | 1290.406 | -2750 | -200 | -1659.594 | 41.49% | 78.72% | 95% | 0% | 2374 | -269
[5 empty] | 2019-03-13 | 15 | 1711.5 | 2311 | -305 | 0 | 0 | 2616 | 1977.2465 | 1977.2465 | 1977.2465 | 2174.6084 | 780 | 200 | 3154.6084 | 78.87% | 95% | 0% | -348.9703 | 1628.2762 | -2750 | -200 | -1321.7238 | 33.04% | 78.72% | 95% | 0% | 2616 | -305
[5 empty] | 2019-03-13 | 16 | 1712 | 2324 | -357 | 1 | 0 | 2681 | 2079.0602 | 2079.0602 | 2079.0602 | 2173.042 | 780 | 200 | 3153.042 | 78.83% | 95% | 0% | -408.4668 | 1670.5934 | -3550 | -400 | -2279.4066 | 56.99% | 78.72% | 95% | 0% | 2681 | -357
[5 empty] | 2019-03-13 | 17 | 1712.5 | 2280 | -415 | 1 | 0 | 2695 | 2100.9893 | 2100.9893 | 2100.9893 | 2173.042 | 780 | 200 | 3153.042 | 78.83% | 95% | 0% | -474.8284 | 1626.1609 | -3550 | -400 | -2323.8391 | 58.1% | 78.72% | 95% | 0% | 2695 | -415
[5 empty] | 2019-03-13 | 18 | 1713 | 2216 | -454 | 1 | 0 | 2670 | 2061.8302 | 2061.8302 | 2061.8302 | 2173.042 | 780 | 200 | 3153.042 | 78.83% | 95% | 0% | -519.4508 | 1542.3794 | -3550 | -400 | -2407.6206 | 60.19% | 78.72% | 95% | 0% | 2670 | -454
[5 empty] | 2019-03-13 | 19 | 1713.5 | 2111 | -531 | 1 | 0 | 2642 | 2017.972 | 2017.972 | 2017.972 | 2173.042 | 780 | 200 | 3153.042 | 78.83% | 95% | 0% | -607.5515 | 1410.4205 | -3550 | -400 | -2539.5795 | 63.49% | 78.71% | 95% | 0% | 2642 | -531
[5 empty] | 2019-03-13 | 20 | 1714 | 2015 | -594 | 1 | 0 | 2609 | 1966.2819 | 1966.2819 | 1966.2819 | 2173.042 | 780 | 200 | 3153.042 | 78.83% | 95% | 0% | -679.6339 | 1286.6481 | -3550 | -400 | -2663.3519 | 66.58% | 78.71% | 95% | 0% | 2609 | -594
[5 empty] | 2019-03-13 | 21 | 1714.5 | 1961 | -616 | 1 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 2173.042 | 780 | 200 | 3153.042 | 78.83% | 95% | 0% | -704.8055 | 1211.3528 | -3550 | -400 | -2738.6472 | 68.47% | 78.71% | 95% | 0% | 2577 | -616
[5 empty] | 2019-03-13 | 22 | 1715 | 1949 | -597 | 1 | 0 | 2546 | 1867.601 | 1867.601 | 1867.601 | 2173.042 | 780 | 200 | 3153.042 | 78.83% | 95% | 0% | -683.0664 | 1184.5346 | -3550 | -400 | -2765.4654 | 69.14% | 78.71% | 95% | 0% | 2546 | -597
[5 empty] | 2019-03-13 | 23 | 1715.5 | 1948 | -604 | 1 | 0 | 2552 | 1876.9992 | 1876.9992 | 1876.9992 | 2173.042 | 780 | 200 | 3153.042 | 78.83% | 95% | 0% | -691.0755 | 1185.9237 | -3550 | -400 | -2764.0763 | 69.1% | 78.7% | 95% | 0% | 2552 | -604
[5 empty] | 2019-03-13 | 24 | 1716 | 1963 | -598 | 1 | 0 | 2561 | 1891.0965 | 1891.0965 | 1891.0965 | 2171.4757 | 780 | 200 | 3151.4757 | 78.79% | 95% | 0% | -684.2105 | 1206.8859 | -3550 | -400 | -2743.1141 | 68.58% | 78.7% | 95% | 0% | 2561 | -598
[5 empty] | 2019-03-13 | 25 | 1716.5 | 1945 | -620 | 1 | 0 | 2565 | 1897.3619 | 1897.3619 | 1897.3619 | 2171.4757 | 780 | 200 | 3151.4757 | 78.79% | 95% | 0% | -709.3822 | 1187.9798 | -3550 | -400 | -2762.0202 | 69.05% | 78.69% | 95% | 0% | 2565 | -620
[5 empty] | 2019-03-13 | 26 | 1717 | 1946 | -613 | 1 | 0 | 2559 | 1887.9637 | 1887.9637 | 1887.9637 | 2171.4757 | 780 | 200 | 3151.4757 | 78.79% | 95% | 0% | -701.373 | 1186.5907 | -3550 | -400 | -2763.4093 | 69.09% | 78.69% | 95% | 0% | 2559 | -613
[5 empty] | 2019-03-13 | 27 | 1717.5 | 1963 | -601 | 1 | 0 | 2564 | 1895.7955 | 1895.7955 | 1895.7955 | 2171.4757 | 780 | 200 | 3151.4757 | 78.79% | 95% | 0% | -687.643 | 1208.1525 | -3550 | -400 | -2741.8475 | 68.55% | 78.69% | 95% | 0% | 2564 | -601
[5 empty] | 2019-03-13 | 28 | 1718 | 1956 | -595 | 1 | 0 | 2551 | 1875.4328 | 1875.4328 | 1875.4328 | 2171.4757 | 780 | 200 | 3151.4757 | 78.79% | 95% | 0% | -680.778 | 1194.6548 | -3550 | -400 | -2755.3452 | 68.88% | 78.68% | 95% | 0% | 2551 | -595
[5 empty] | 2019-03-13 | 29 | 1718.5 | 1999 | -570 | 1 | 0 | 2569 | 1903.6274 | 1903.6274 | 1903.6274 | 2171.4757 | 780 | 200 | 3151.4757 | 78.79% | 95% | 0% | -652.1739 | 1251.4535 | -3550 | -400 | -2698.5465 | 67.46% | 78.68% | 95% | 0% | 2569 | -570
[5 empty] | 2019-03-13 | 30 | 1719 | 2054 | -520 | 1 | 0 | 2574 | 1911.4592 | 1911.4592 | 1911.4592 | 2169.9093 | 780 | 200 | 3149.9093 | 78.75% | 95% | 0% | -594.9657 | 1316.4935 | -3550 | -400 | -2633.5065 | 65.84% | 78.68% | 95% | 0% | 2574 | -520
[5 empty] | 2019-03-13 | 31 | 1719.5 | 2135 | -462 | 1 | 0 | 2597 | 1947.4856 | 1947.4856 | 1947.4856 | 2169.9093 | 780 | 200 | 3149.9093 | 78.75% | 95% | 0% | -528.6041 | 1418.8815 | -3550 | -400 | -2531.1185 | 63.28% | 78.67% | 95% | 0% | 2597 | -462
[5 empty] | 2019-03-13 | 32 | 1720 | 2281 | -413 | 1 | 0 | 2694 | 2099.4229 | 2099.4229 | 2099.4229 | 2169.9093 | 780 | 200 | 3149.9093 | 78.75% | 95% | 0% | -472.54 | 1626.8829 | -3550 | -400 | -2323.1171 | 58.08% | 78.66% | 95% | 0% | 2694 | -413
[5 empty] | 2019-03-13 | 33 | 1720.5 | 2423 | -369 | 1 | 0 | 2792 | 2252.9266 | 2252.9266 | 2252.9266 | 2169.9093 | 780 | 200 | 3149.9093 | 78.75% | 95% | 0% | -422.1968 | 1830.7298 | -3550 | -400 | -2119.2702 | 52.98% | 78.66% | 95% | 0% | 2792 | -369
[5 empty] | 2019-03-13 | 34 | 1721 | 2605 | -300 | 1 | 0 | 2905 | 2429.9258 | 2429.9258 | 2429.9258 | 2169.9093 | 780 | 200 | 3149.9093 | 78.75% | 95% | 0% | -343.2494 | 2086.6764 | -3550 | -400 | -1863.3236 | 46.58% | 78.66% | 95% | 0% | 2905 | -300
[5 empty] | 2019-03-13 | 35 | 1721.5 | 2750 | -254 | 1 | 0 | 3004 | 2584.9959 | 2584.9959 | 2584.9959 | 2169.9093 | 780 | 200 | 3149.9093 | 78.75% | 95% | 0% | -290.6178 | 2294.378 | -3550 | -400 | -1655.622 | 41.39% | 78.66% | 95% | 0% | 3004 | -254
[5 empty] | 2019-03-13 | 36 | 1722 | 2831 | -224 | 1 | 0 | 3055 | 2664.8805 | 2664.8805 | 2664.8805 | 2168.343 | 780 | 200 | 3148.343 | 78.71% | 95% | 0% | -256.2929 | 2408.5876 | -3550 | -400 | -1541.4124 | 38.54% | 78.65% | 95% | 0% | 3055 | -224
[5 empty] | 2019-03-13 | 37 | 1722.5 | 2918 | -215 | 1 | 0 | 3133 | 2787.0569 | 2787.0569 | 2787.0569 | 2168.343 | 780 | 200 | 3148.343 | 78.71% | 95% | 0% | -245.9954 | 2541.0615 | -3550 | -400 | -1408.9385 | 35.22% | 78.65% | 95% | 0% | 3133 | -215
[5 empty] | 2019-03-13 | 38 | 1723 | 2966 | -209 | 1 | 0 | 3175 | 2852.8442 | 2852.8442 | 2852.8442 | 2168.343 | 780 | 200 | 3148.343 | 78.71% | 95% | 0% | -239.1304 | 2613.7138 | -3550 | -400 | -1336.2862 | 33.41% | 78.64% | 95% | 0% | 3175 | -209
[5 empty] | 2019-03-13 | 39 | 1723.5 | 2923 | -203 | 0 | 0 | 3126 | 2776.0923 | 2776.0923 | 2776.0923 | 2168.343 | 780 | 200 | 3148.343 | 78.71% | 95% | 0% | -232.2654 | 2543.8269 | -2750 | -200 | -406.1731 | 10.15% | 78.63% | 95% | 0% | 3126 | -203
[5 empty] | 2019-03-13 | 40 | 1724 | 2843 | -198 | 0 | 0 | 3041 | 2642.9514 | 2642.9514 | 2642.9514 | 2168.343 | 780 | 200 | 3148.343 | 78.71% | 95% | 0% | -226.5446 | 2416.4067 | -2750 | -200 | -533.5933 | 13.34% | 78.63% | 95% | 0% | 3041 | -198
[5 empty] | 2019-03-13 | 41 | 1724.5 | 2753 | -194 | 0 | 0 | 2947 | 2495.7131 | 2495.7131 | 2495.7131 | 2166.7766 | 780 | 200 | 3146.7766 | 78.67% | 95% | 0% | -221.968 | 2273.7451 | -2750 | -200 | -676.2549 | 16.91% | 78.63% | 95% | 0% | 2947 | -194
[5 empty] | 2019-03-13 | 42 | 1725 | 2642 | -190 | 0 | 0 | 2832 | 2315.5812 | 2315.5812 | 2315.5812 | 2166.7766 | 780 | 200 | 3146.7766 | 78.67% | 95% | 0% | -217.3913 | 2098.1899 | -2750 | -200 | -851.8101 | 21.3% | 78.63% | 95% | 0% | 2832 | -190
[5 empty] | 2019-03-13 | 43 | 1725.5 | 2498 | -192 | 0 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 2166.7766 | 780 | 200 | 3146.7766 | 78.67% | 95% | 0% | -219.6796 | 1873.4778 | -2750 | -200 | -1076.5222 | 26.91% | 78.62% | 95% | 0% | 2690 | -192
[5 empty] | 2019-03-13 | 44 | 1726 | 2326 | -194 | 0 | 0 | 2520 | 1826.8755 | 1826.8755 | 1826.8755 | 2166.7766 | 780 | 200 | 3146.7766 | 78.67% | 95% | 0% | -221.968 | 1604.9076 | -2750 | -200 | -1345.0924 | 33.63% | 78.62% | 95% | 0% | 2520 | -194
[5 empty] | 2019-03-13 | 45 | 1726.5 | 2146 | -201 | 0 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 2166.7766 | 780 | 200 | 3146.7766 | 78.67% | 95% | 0% | -229.9771 | 1325.9174 | -2750 | -200 | -1624.0826 | 40.6% | 78.61% | 95% | 0% | 2347 | -201
[5 empty] | 2019-03-13 | 46 | 1727 | 1986 | -207 | 0 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 2166.7766 | 780 | 200 | 3146.7766 | 78.67% | 95% | 0% | -236.8421 | 1077.8323 | -2750 | -200 | -1872.1677 | 46.8% | 78.61% | 95% | 0% | 2193 | -207
[5 empty] | 2019-03-13 | 47 | 1727.5 | 1817 | -216 | 0 | 0 | 2033 | 1064.0561 | 1064.0561 | 1064.0561 | 2166.7766 | 780 | 200 | 3146.7766 | 78.67% | 95% | 0% | -247.1396 | 816.9165 | -2750 | -200 | -2133.0835 | 53.33% | 78.61% | 95% | 0% | 2033 | -216
[5 empty] | 2019-03-13 | 48 | 1728 | 1701 | -225 | 0 | 0 | 1926 | 896.4551 | 896.4551 | 896.4551 | 2166.7766 | 780 | 200 | 3146.7766 | 78.67% | 95% | 0% | -257.4371 | 639.018 | -2750 | -200 | -2310.982 | 57.77% | 78.61% | 95% | 0% | 1926 | -225
[5 empty] | 2019-03-14 | 1 | 1728.5 | 1675 | -225 | 0 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 2165.2102 | 780 | 200 | 3145.2102 | 78.63% | 95% | 0% | -257.4371 | 598.2925 | -2750 | -200 | -2351.7075 | 58.79% | 78.6% | 95% | 0% | 1900 | -225
[5 empty] | 2019-03-14 | 2 | 1729 | 1700 | -225 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 2165.2102 | 780 | 200 | 3145.2102 | 78.63% | 95% | 0% | -257.4371 | 637.4516 | -2750 | -200 | -2312.5484 | 57.81% | 78.6% | 95% | 0% | 1925 | -225
[5 empty] | 2019-03-14 | 3 | 1729.5 | 1666 | -227 | 0 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 2165.2102 | 780 | 200 | 3145.2102 | 78.63% | 95% | 0% | -259.7254 | 585.0396 | -2750 | -200 | -2364.9604 | 59.12% | 78.6% | 95% | 0% | 1893 | -227
[5 empty] | 2019-03-14 | 4 | 1730 | 1611 | -230 | 0 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 2165.2102 | 780 | 200 | 3145.2102 | 78.63% | 95% | 0% | -263.1579 | 500.1562 | -2750 | -200 | -2449.8438 | 61.25% | 78.59% | 95% | 0% | 1841 | -230
[5 empty] | 2019-03-14 | 5 | 1730.5 | 1567 | -231 | 0 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 2165.2102 | 780 | 200 | 3145.2102 | 78.63% | 95% | 0% | -264.3021 | 431.6584 | -2750 | -200 | -2518.3416 | 62.96% | 78.58% | 95% | 0% | 1798 | -231
[5 empty] | 2019-03-14 | 6 | 1731 | 1556 | -232 | 0 | 0 | 1788 | 680.2968 | 680.2968 | 680.2968 | 2165.2102 | 780 | 200 | 3145.2102 | 78.63% | 95% | 0% | -265.4462 | 414.8506 | -2750 | -200 | -2535.1494 | 63.38% | 78.57% | 95% | 0% | 1788 | -232
[5 empty] | 2019-03-14 | 7 | 1731.5 | 1522 | -233 | 0 | 0 | 1755 | 628.6068 | 628.6068 | 628.6068 | 2165.2102 | 780 | 200 | 3145.2102 | 78.63% | 95% | 0% | -266.5904 | 362.0164 | -2750 | -200 | -2587.9836 | 64.7% | 78.57% | 95% | 0% | 1755 | -233
[5 empty] | 2019-03-14 | 8 | 1732 | 1490 | -234 | 0 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 2165.2102 | 780 | 200 | 3145.2102 | 78.63% | 95% | 0% | -267.7346 | 312.3149 | -2750 | -200 | -2637.6851 | 65.94% | 78.57% | 95% | 0% | 1724 | -234
[5 empty] | 2019-03-14 | 9 | 1732.5 | 1477 | -235 | 0 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 2165.2102 | 780 | 200 | 3145.2102 | 78.63% | 95% | 0% | -268.8787 | 292.3744 | -2750 | -200 | -2657.6256 | 66.44% | 78.57% | 95% | 0% | 1712 | -235
[5 empty] | 2019-03-14 | 10 | 1733 | 1477 | -237 | 0 | 0 | 1714 | 564.3858 | 564.3858 | 564.3858 | 2165.2102 | 780 | 200 | 3145.2102 | 78.63% | 95% | 0% | -271.167 | 293.2188 | -2750 | -200 | -2656.7812 | 66.42% | 78.56% | 95% | 0% | 1714 | -237
[5 empty] | 2019-03-14 | 11 | 1733.5 | 1547 | -238 | 1 | 0 | 1785 | 675.5977 | 675.5977 | 675.5977 | 2163.6439 | 780 | 200 | 3143.6439 | 78.59% | 95% | 0% | -272.3112 | 403.2865 | -3550 | -400 | -3546.7135 | 88.67% | 78.56% | 95% | 0% | 1785 | -238
[5 empty] | 2019-03-14 | 12 | 1734 | 1649 | -239 | 1 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 2163.6439 | 780 | 200 | 3143.6439 | 78.59% | 95% | 0% | -273.4554 | 563.4778 | -3550 | -400 | -3386.5222 | 84.66% | 78.54% | 95% | 0% | 1888 | -239
[5 empty] | 2019-03-14 | 13 | 1734.5 | 1896 | -243 | 1 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 2163.6439 | 780 | 200 | 3143.6439 | 78.59% | 95% | 0% | -278.032 | 952.0586 | -3550 | -400 | -2997.9414 | 74.95% | 78.54% | 95% | 0% | 2139 | -243
[5 empty] | 2019-03-14 | 14 | 1735 | 2105 | -247 | 1 | 0 | 2352 | 1563.7263 | 1563.7263 | 1563.7263 | 2163.6439 | 780 | 200 | 3143.6439 | 78.59% | 95% | 0% | -282.6087 | 1281.1176 | -3550 | -400 | -2668.8824 | 66.72% | 78.53% | 95% | 0% | 2352 | -247
[5 empty] | 2019-03-14 | 15 | 1735.5 | 2344 | -260 | 1 | 0 | 2604 | 1958.4501 | 1958.4501 | 1958.4501 | 2163.6439 | 780 | 200 | 3143.6439 | 78.59% | 95% | 0% | -297.4828 | 1660.9673 | -3550 | -400 | -2289.0327 | 57.23% | 78.51% | 95% | 0% | 2604 | -260
[5 empty] | 2019-03-14 | 16 | 1736 | 2387 | -306 | 1 | 0 | 2693 | 2097.8566 | 2097.8566 | 2097.8566 | 2163.6439 | 780 | 200 | 3143.6439 | 78.59% | 95% | 0% | -350.1144 | 1747.7421 | -3550 | -400 | -2202.2579 | 55.06% | 78.5% | 95% | 0% | 2693 | -306
[5 empty] | 2019-03-14 | 17 | 1736.5 | 2379 | -350 | 1 | 0 | 2729 | 2154.2457 | 2154.2457 | 2154.2457 | 2162.0775 | 780 | 200 | 3142.0775 | 78.55% | 95% | 0% | -400.4577 | 1753.788 | -3550 | -400 | -2196.212 | 54.91% | 78.49% | 95% | 0% | 2729 | -350
[5 empty] | 2019-03-14 | 18 | 1737 | 2326 | -384 | 1 | 0 | 2710 | 2124.4847 | 2124.4847 | 2124.4847 | 2162.0775 | 780 | 200 | 3142.0775 | 78.55% | 95% | 0% | -439.3593 | 1685.1255 | -3550 | -400 | -2264.8745 | 56.62% | 78.48% | 95% | 0% | 2710 | -384
[5 empty] | 2019-03-14 | 19 | 1737.5 | 2271 | -447 | 1 | 0 | 2718 | 2137.0157 | 2137.0157 | 2137.0157 | 2162.0775 | 780 | 200 | 3142.0775 | 78.55% | 95% | 0% | -511.4416 | 1625.574 | -3550 | -400 | -2324.426 | 58.11% | 78.48% | 95% | 0% | 2718 | -447
[5 empty] | 2019-03-14 | 20 | 1738 | 2172 | -518 | 1 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 2162.0775 | 780 | 200 | 3142.0775 | 78.55% | 95% | 0% | -592.6773 | 1500.4801 | -3550 | -400 | -2449.5199 | 61.24% | 78.47% | 95% | 0% | 2690 | -518
[5 empty] | 2019-03-14 | 21 | 1738.5 | 2046 | -573 | 1 | 0 | 2619 | 1981.9456 | 1981.9456 | 1981.9456 | 2162.0775 | 780 | 200 | 3142.0775 | 78.55% | 95% | 0% | -655.6064 | 1326.3392 | -3550 | -400 | -2623.6608 | 65.59% | 78.47% | 95% | 0% | 2619 | -573
[5 empty] | 2019-03-14 | 22 | 1739 | 1926 | -649 | 1 | 0 | 2575 | 1913.0256 | 1913.0256 | 1913.0256 | 2162.0775 | 780 | 200 | 3142.0775 | 78.55% | 95% | 0% | -742.5629 | 1170.4626 | -3550 | -400 | -2779.5374 | 69.49% | 78.47% | 95% | 0% | 2575 | -649
[5 empty] | 2019-03-14 | 23 | 1739.5 | 1836 | -709 | 1 | 0 | 2545 | 1866.0346 | 1866.0346 | 1866.0346 | 2160.5111 | 780 | 200 | 3140.5111 | 78.51% | 95% | 0% | -811.2128 | 1054.8218 | -3550 | -400 | -2895.1782 | 72.38% | 78.47% | 95% | 0% | 2545 | -709
[5 empty] | 2019-03-14 | 24 | 1740 | 1752 | -752 | 1 | 0 | 2504 | 1801.8137 | 1801.8137 | 1801.8137 | 2160.5111 | 780 | 200 | 3140.5111 | 78.51% | 95% | 0% | -860.4119 | 941.4018 | -3550 | -400 | -3008.5982 | 75.21% | 78.47% | 95% | 0% | 2504 | -752
[5 empty] | 2019-03-14 | 25 | 1740.5 | 1701 | -782 | 1 | 0 | 2483 | 1768.92 | 1768.92 | 1768.92 | 2160.5111 | 780 | 200 | 3140.5111 | 78.51% | 95% | 0% | -894.7368 | 874.1832 | -3550 | -400 | -3075.8168 | 76.9% | 78.46% | 95% | 0% | 2483 | -782
[5 empty] | 2019-03-14 | 26 | 1741 | 1666 | -772 | 1 | 0 | 2438 | 1698.4336 | 1698.4336 | 1698.4336 | 2160.5111 | 780 | 200 | 3140.5111 | 78.51% | 95% | 0% | -883.2952 | 815.1384 | -3550 | -400 | -3134.8616 | 78.37% | 78.46% | 95% | 0% | 2438 | -772
[5 empty] | 2019-03-14 | 27 | 1741.5 | 1678 | -733 | 1 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 2160.5111 | 780 | 200 | 3140.5111 | 78.51% | 95% | 0% | -838.6728 | 817.469 | -3550 | -400 | -3132.531 | 78.31% | 78.45% | 95% | 0% | 2411 | -733
[5 empty] | 2019-03-14 | 28 | 1742 | 1665 | -723 | 1 | 0 | 2388 | 1620.1154 | 1620.1154 | 1620.1154 | 2158.9448 | 780 | 200 | 3138.9448 | 78.47% | 95% | 0% | -827.2311 | 792.8843 | -3550 | -400 | -3157.1157 | 78.93% | 78.45% | 95% | 0% | 2388 | -723
[5 empty] | 2019-03-14 | 29 | 1742.5 | 1725 | -665 | 1 | 0 | 2390 | 1623.2481 | 1623.2481 | 1623.2481 | 2158.9448 | 780 | 200 | 3138.9448 | 78.47% | 95% | 0% | -760.8696 | 862.3786 | -3550 | -400 | -3087.6214 | 77.19% | 78.45% | 95% | 0% | 2390 | -665
[5 empty] | 2019-03-14 | 30 | 1743 | 1806 | -603 | 1 | 0 | 2409 | 1653.0091 | 1653.0091 | 1653.0091 | 2157.3784 | 780 | 200 | 3137.3784 | 78.43% | 95% | 0% | -689.9314 | 963.0777 | -3550 | -400 | -2986.9223 | 74.67% | 78.44% | 95% | 0% | 2409 | -603
[5 empty] | 2019-03-14 | 31 | 1743.5 | 1901 | -543 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 2157.3784 | 780 | 200 | 3137.3784 | 78.43% | 95% | 0% | -621.2815 | 1086.5504 | -3550 | -400 | -2863.4496 | 71.59% | 78.43% | 95% | 0% | 2444 | -543
[5 empty] | 2019-03-14 | 32 | 1744 | 2093 | -452 | 1 | 0 | 2545 | 1866.0346 | 1866.0346 | 1866.0346 | 2157.3784 | 780 | 200 | 3137.3784 | 78.43% | 95% | 0% | -517.1625 | 1348.8722 | -3550 | -400 | -2601.1278 | 65.03% | 78.43% | 95% | 0% | 2545 | -452
[5 empty] | 2019-03-14 | 33 | 1744.5 | 2263 | -383 | 1 | 0 | 2646 | 2024.2374 | 2024.2374 | 2024.2374 | 2157.3784 | 780 | 200 | 3137.3784 | 78.43% | 95% | 0% | -438.2151 | 1586.0223 | -3550 | -400 | -2363.9777 | 59.1% | 78.42% | 95% | 0% | 2646 | -383
[5 empty] | 2019-03-14 | 34 | 1745 | 2449 | -314 | 1 | 0 | 2763 | 2207.5021 | 2207.5021 | 2207.5021 | 2157.3784 | 780 | 200 | 3137.3784 | 78.43% | 95% | 0% | -359.2677 | 1848.2343 | -3550 | -400 | -2101.7657 | 52.54% | 78.42% | 95% | 0% | 2763 | -314
[5 empty] | 2019-03-14 | 35 | 1745.5 | 2625 | -245 | 1 | 0 | 2870 | 2375.1031 | 2375.1031 | 2375.1031 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -280.3204 | 2094.7827 | -3550 | -400 | -1855.2173 | 46.38% | 78.4% | 95% | 0% | 2870 | -245
[5 empty] | 2019-03-14 | 36 | 1746 | 2739 | -205 | 1 | 0 | 2944 | 2491.014 | 2491.014 | 2491.014 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -234.5538 | 2256.4602 | -3550 | -400 | -1693.5398 | 42.34% | 78.4% | 95% | 0% | 2944 | -205
[5 empty] | 2019-03-14 | 37 | 1746.5 | 2813 | -195 | 1 | 0 | 3008 | 2591.2613 | 2591.2613 | 2591.2613 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -223.1121 | 2368.1492 | -3550 | -400 | -1581.8508 | 39.55% | 78.4% | 95% | 0% | 3008 | -195
[5 empty] | 2019-03-14 | 38 | 1747 | 2883 | -189 | 1 | 0 | 3072 | 2691.5087 | 2691.5087 | 2691.5087 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -216.2471 | 2475.2615 | -3550 | -400 | -1474.7385 | 36.87% | 78.39% | 95% | 0% | 3072 | -189
[5 empty] | 2019-03-14 | 39 | 1747.5 | 2850 | -184 | 0 | 0 | 3034 | 2631.9868 | 2631.9868 | 2631.9868 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -210.5263 | 2421.4605 | -2750 | -200 | -528.5395 | 13.21% | 78.38% | 95% | 0% | 3034 | -184
[5 empty] | 2019-03-14 | 40 | 1748 | 2790 | -179 | 0 | 0 | 2969 | 2530.1731 | 2530.1731 | 2530.1731 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -204.8055 | 2325.3676 | -2750 | -200 | -624.6324 | 15.62% | 78.38% | 95% | 0% | 2969 | -179
[5 empty] | 2019-03-14 | 41 | 1748.5 | 2723 | -174 | 0 | 0 | 2897 | 2417.3949 | 2417.3949 | 2417.3949 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -199.0847 | 2218.3102 | -2750 | -200 | -731.6898 | 18.29% | 78.38% | 95% | 0% | 2897 | -174
[5 empty] | 2019-03-14 | 42 | 1749 | 2615 | -170 | 0 | 0 | 2785 | 2241.9621 | 2241.9621 | 2241.9621 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -194.508 | 2047.4541 | -2750 | -200 | -902.5459 | 22.56% | 78.37% | 95% | 0% | 2785 | -170
[5 empty] | 2019-03-14 | 43 | 1749.5 | 2491 | -168 | 0 | 0 | 2659 | 2044.6002 | 2044.6002 | 2044.6002 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -192.2197 | 1852.3805 | -2750 | -200 | -1097.6195 | 27.44% | 78.37% | 95% | 0% | 2659 | -168
[5 empty] | 2019-03-14 | 44 | 1750 | 2357 | -166 | 0 | 0 | 2523 | 1831.5746 | 1831.5746 | 1831.5746 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -189.9314 | 1641.6433 | -2750 | -200 | -1308.3567 | 32.71% | 78.37% | 95% | 0% | 2523 | -166
[5 empty] | 2019-03-14 | 45 | 1750.5 | 2210 | -164 | 0 | 0 | 2374 | 1598.1863 | 1598.1863 | 1598.1863 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -187.643 | 1410.5433 | -2750 | -200 | -1539.4567 | 38.49% | 78.37% | 95% | 0% | 2374 | -164
[5 empty] | 2019-03-14 | 46 | 1751 | 2061 | -162 | 0 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -185.3547 | 1176.3106 | -2750 | -200 | -1773.6894 | 44.34% | 78.36% | 95% | 0% | 2223 | -162
[5 empty] | 2019-03-14 | 47 | 1751.5 | 1909 | -160 | 0 | 0 | 2069 | 1120.4452 | 1120.4452 | 1120.4452 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -183.0664 | 937.3788 | -2750 | -200 | -2012.6212 | 50.32% | 78.36% | 95% | 0% | 2069 | -160
[5 empty] | 2019-03-14 | 48 | 1752 | 1825 | -158 | 0 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 2155.812 | 780 | 200 | 3135.812 | 78.4% | 95% | 0% | -180.778 | 804.9598 | -2750 | -200 | -2145.0402 | 53.63% | 78.34% | 95% | 0% | 1983 | -158
[5 empty] | 2019-03-15 | 1 | 1752.5 | 1798 | -157 | 0 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -179.6339 | 762.2458 | -2750 | -200 | -2187.7542 | 54.69% | 78.34% | 95% | 0% | 1955 | -157
[5 empty] | 2019-03-15 | 2 | 1753 | 1827 | -155 | 0 | 0 | 1982 | 984.1715 | 984.1715 | 984.1715 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -177.3455 | 806.8259 | -2750 | -200 | -2143.1741 | 53.58% | 78.34% | 95% | 0% | 1982 | -155
[5 empty] | 2019-03-15 | 3 | 1753.5 | 1788 | -158 | 0 | 0 | 1946 | 927.7824 | 927.7824 | 927.7824 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -180.778 | 747.0043 | -2750 | -200 | -2202.9957 | 55.07% | 78.34% | 95% | 0% | 1946 | -158
[5 empty] | 2019-03-15 | 4 | 1754 | 1738 | -162 | 0 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -185.3547 | 670.3749 | -2750 | -200 | -2279.6251 | 56.99% | 78.33% | 95% | 0% | 1900 | -162
[5 empty] | 2019-03-15 | 5 | 1754.5 | 1670 | -170 | 0 | 0 | 1840 | 761.7477 | 761.7477 | 761.7477 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -194.508 | 567.2397 | -2750 | -200 | -2382.7603 | 59.57% | 78.32% | 95% | 0% | 1840 | -170
[5 empty] | 2019-03-15 | 6 | 1755 | 1629 | -178 | 1 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -203.6613 | 506.3964 | -3550 | -400 | -3443.6036 | 86.09% | 78.31% | 95% | 0% | 1807 | -178
[5 empty] | 2019-03-15 | 7 | 1755.5 | 1560 | -193 | 1 | 0 | 1753 | 625.474 | 625.474 | 625.474 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -220.8238 | 404.6502 | -3550 | -400 | -3545.3498 | 88.63% | 78.31% | 95% | 0% | 1753 | -193
[5 empty] | 2019-03-15 | 8 | 1756 | 1488 | -207 | 1 | 0 | 1695 | 534.6249 | 534.6249 | 534.6249 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -236.8421 | 297.7828 | -3550 | -400 | -3652.2172 | 91.31% | 78.31% | 95% | 0% | 1695 | -207
[5 empty] | 2019-03-15 | 9 | 1756.5 | 1439 | -223 | 1 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -255.1487 | 227.7861 | -3550 | -400 | -3722.2139 | 93.06% | 78.3% | 95% | 0% | 1662 | -223
[5 empty] | 2019-03-15 | 10 | 1757 | 1414 | -239 | 1 | 0 | 1653 | 468.8376 | 468.8376 | 468.8376 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -273.4554 | 195.3822 | -3550 | -400 | -3754.6178 | 93.87% | 78.3% | 95% | 0% | 1653 | -239
[5 empty] | 2019-03-15 | 11 | 1757.5 | 1464 | -253 | 1 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -289.4737 | 279.6112 | -3550 | -400 | -3670.3888 | 91.76% | 78.29% | 95% | 0% | 1717 | -253
[5 empty] | 2019-03-15 | 12 | 1758 | 1541 | -266 | 1 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -304.3478 | 405.7099 | -3550 | -400 | -3544.2901 | 88.61% | 78.29% | 95% | 0% | 1807 | -266
[5 empty] | 2019-03-15 | 13 | 1758.5 | 1768 | -269 | 1 | 0 | 2037 | 1070.3215 | 1070.3215 | 1070.3215 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -307.7803 | 762.5412 | -3550 | -400 | -3187.4588 | 79.69% | 78.27% | 95% | 0% | 2037 | -269
[5 empty] | 2019-03-15 | 14 | 1759 | 1956 | -274 | 1 | 0 | 2230 | 1372.6298 | 1372.6298 | 1372.6298 | 2154.2457 | 780 | 200 | 3134.2457 | 78.36% | 95% | 0% | -313.5011 | 1059.1287 | -3550 | -400 | -2890.8713 | 72.27% | 78.26% | 95% | 0% | 2230 | -274
[5 empty] | 2019-03-15 | 15 | 1759.5 | 2156 | -297 | 1 | 0 | 2453 | 1721.9291 | 1721.9291 | 1721.9291 | 2152.6793 | 780 | 200 | 3132.6793 | 78.32% | 95% | 0% | -339.8169 | 1382.1122 | -3550 | -400 | -2567.8878 | 64.2% | 78.26% | 95% | 0% | 2453 | -297
[5 empty] | 2019-03-15 | 16 | 1760 | 2228 | -328 | 1 | 0 | 2556 | 1883.2646 | 1883.2646 | 1883.2646 | 2152.6793 | 780 | 200 | 3132.6793 | 78.32% | 95% | 0% | -375.286 | 1507.9786 | -3550 | -400 | -2442.0214 | 61.05% | 78.25% | 95% | 0% | 2556 | -328
[5 empty] | 2019-03-15 | 17 | 1760.5 | 2237 | -361 | 1 | 0 | 2598 | 1949.0519 | 1949.0519 | 1949.0519 | 2152.6793 | 780 | 200 | 3132.6793 | 78.32% | 95% | 0% | -413.0435 | 1536.0085 | -3550 | -400 | -2413.9915 | 60.35% | 78.25% | 95% | 0% | 2598 | -361
[5 empty] | 2019-03-15 | 18 | 1761 | 2201 | -400 | 1 | 0 | 2601 | 1953.751 | 1953.751 | 1953.751 | 2152.6793 | 780 | 200 | 3132.6793 | 78.32% | 95% | 0% | -457.6659 | 1496.0851 | -3550 | -400 | -2453.9149 | 61.35% | 78.24% | 95% | 0% | 2601 | -400
[5 empty] | 2019-03-15 | 19 | 1761.5 | 2168 | -447 | 1 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 2152.6793 | 780 | 200 | 3132.6793 | 78.32% | 95% | 0% | -511.4416 | 1464.2385 | -3550 | -400 | -2485.7615 | 62.14% | 78.23% | 95% | 0% | 2615 | -447
[5 empty] | 2019-03-15 | 20 | 1762 | 2115 | -486 | 1 | 0 | 2601 | 1953.751 | 1953.751 | 1953.751 | 2151.1129 | 780 | 200 | 3131.1129 | 78.28% | 95% | 0% | -556.0641 | 1397.687 | -3550 | -400 | -2552.313 | 63.81% | 78.22% | 95% | 0% | 2601 | -486
[5 empty] | 2019-03-15 | 21 | 1762.5 | 2078 | -503 | 1 | 0 | 2581 | 1922.4237 | 1922.4237 | 1922.4237 | 2151.1129 | 780 | 200 | 3131.1129 | 78.28% | 95% | 0% | -575.5149 | 1346.9089 | -3550 | -400 | -2603.0911 | 65.08% | 78.22% | 95% | 0% | 2581 | -503
[5 empty] | 2019-03-15 | 22 | 1763 | 2008 | -549 | 1 | 0 | 2557 | 1884.831 | 1884.831 | 1884.831 | 2151.1129 | 780 | 200 | 3131.1129 | 78.28% | 95% | 0% | -628.1465 | 1256.6845 | -3550 | -400 | -2693.3155 | 67.33% | 78.22% | 95% | 0% | 2557 | -549
[5 empty] | 2019-03-15 | 23 | 1763.5 | 1965 | -582 | 1 | 0 | 2547 | 1869.1674 | 1869.1674 | 1869.1674 | 2151.1129 | 780 | 200 | 3131.1129 | 78.28% | 95% | 0% | -665.9039 | 1203.2635 | -3550 | -400 | -2746.7365 | 68.67% | 78.21% | 95% | 0% | 2547 | -582
[5 empty] | 2019-03-15 | 24 | 1764 | 1996 | -551 | 1 | 0 | 2547 | 1869.1674 | 1869.1674 | 1869.1674 | 2151.1129 | 780 | 200 | 3131.1129 | 78.28% | 95% | 0% | -630.4348 | 1238.7326 | -3550 | -400 | -2711.2674 | 67.78% | 78.2% | 95% | 0% | 2547 | -551
[5 empty] | 2019-03-15 | 25 | 1764.5 | 1942 | -588 | 1 | 0 | 2530 | 1842.5392 | 1842.5392 | 1842.5392 | 2149.5466 | 780 | 200 | 3129.5466 | 78.24% | 95% | 0% | -672.7689 | 1169.7703 | -3550 | -400 | -2780.2297 | 69.51% | 78.2% | 95% | 0% | 2530 | -588
[5 empty] | 2019-03-15 | 26 | 1765 | 1953 | -569 | 1 | 0 | 2522 | 1830.0082 | 1830.0082 | 1830.0082 | 2149.5466 | 780 | 200 | 3129.5466 | 78.24% | 95% | 0% | -651.0297 | 1178.9785 | -3550 | -400 | -2771.0215 | 69.28% | 78.19% | 95% | 0% | 2522 | -569
[5 empty] | 2019-03-15 | 27 | 1765.5 | 1965 | -547 | 1 | 0 | 2512 | 1814.3446 | 1814.3446 | 1814.3446 | 2149.5466 | 780 | 200 | 3129.5466 | 78.24% | 95% | 0% | -625.8581 | 1188.4865 | -3550 | -400 | -2761.5135 | 69.04% | 78.19% | 95% | 0% | 2512 | -547
[5 empty] | 2019-03-15 | 28 | 1766 | 1943 | -544 | 1 | 0 | 2487 | 1775.1855 | 1775.1855 | 1775.1855 | 2149.5466 | 780 | 200 | 3129.5466 | 78.24% | 95% | 0% | -622.4256 | 1152.7599 | -3550 | -400 | -2797.2401 | 69.93% | 78.19% | 95% | 0% | 2487 | -544
[5 empty] | 2019-03-15 | 29 | 1766.5 | 1943 | -525 | 1 | 0 | 2468 | 1745.4246 | 1745.4246 | 1745.4246 | 2149.5466 | 780 | 200 | 3129.5466 | 78.24% | 95% | 0% | -600.6865 | 1144.7381 | -3550 | -400 | -2805.2619 | 70.13% | 78.18% | 95% | 0% | 2468 | -525
[5 empty] | 2019-03-15 | 30 | 1767 | 1960 | -488 | 1 | 0 | 2448 | 1714.0973 | 1714.0973 | 1714.0973 | 2149.5466 | 780 | 200 | 3129.5466 | 78.24% | 95% | 0% | -558.3524 | 1155.7449 | -3550 | -400 | -2794.2551 | 69.86% | 78.18% | 95% | 0% | 2448 | -488
[5 empty] | 2019-03-15 | 31 | 1767.5 | 1994 | -459 | 1 | 0 | 2453 | 1721.9291 | 1721.9291 | 1721.9291 | 2149.5466 | 780 | 200 | 3129.5466 | 78.24% | 95% | 0% | -525.1716 | 1196.7575 | -3550 | -400 | -2753.2425 | 68.83% | 78.18% | 95% | 0% | 2453 | -459
[5 empty] | 2019-03-15 | 32 | 1768 | 2090 | -406 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 2149.5466 | 780 | 200 | 3129.5466 | 78.24% | 95% | 0% | -464.5309 | 1324.7519 | -3550 | -400 | -2625.2481 | 65.63% | 78.17% | 95% | 0% | 2496 | -406
[5 empty] | 2019-03-15 | 33 | 1768.5 | 2220 | -352 | 1 | 0 | 2572 | 1908.3265 | 1908.3265 | 1908.3265 | 2149.5466 | 780 | 200 | 3129.5466 | 78.24% | 95% | 0% | -402.746 | 1505.5805 | -3550 | -400 | -2444.4195 | 61.11% | 78.17% | 95% | 0% | 2572 | -352
[5 empty] | 2019-03-15 | 34 | 1769 | 2376 | -302 | 1 | 0 | 2678 | 2074.3611 | 2074.3611 | 2074.3611 | 2147.9802 | 780 | 200 | 3127.9802 | 78.2% | 95% | 0% | -345.5378 | 1728.8233 | -3550 | -400 | -2221.1767 | 55.53% | 78.17% | 95% | 0% | 2678 | -302
[5 empty] | 2019-03-15 | 35 | 1769.5 | 2504 | -253 | 1 | 0 | 2757 | 2198.1039 | 2198.1039 | 2198.1039 | 2147.9802 | 780 | 200 | 3127.9802 | 78.2% | 95% | 0% | -289.4737 | 1908.6302 | -3550 | -400 | -2041.3698 | 51.03% | 78.16% | 95% | 0% | 2757 | -253
[5 empty] | 2019-03-15 | 36 | 1770 | 2599 | -218 | 1 | 0 | 2817 | 2292.0857 | 2292.0857 | 2292.0857 | 2147.9802 | 780 | 200 | 3127.9802 | 78.2% | 95% | 0% | -249.4279 | 2042.6578 | -3550 | -400 | -1907.3422 | 47.68% | 78.16% | 95% | 0% | 2817 | -218
[5 empty] | 2019-03-15 | 37 | 1770.5 | 2669 | -203 | 1 | 0 | 2872 | 2378.2358 | 2378.2358 | 2378.2358 | 2147.9802 | 780 | 200 | 3127.9802 | 78.2% | 95% | 0% | -232.2654 | 2145.9703 | -3550 | -400 | -1804.0297 | 45.1% | 78.15% | 95% | 0% | 2872 | -203
[5 empty] | 2019-03-15 | 38 | 1771 | 2734 | -193 | 1 | 0 | 2927 | 2464.3858 | 2464.3858 | 2464.3858 | 2146.4138 | 780 | 200 | 3126.4138 | 78.16% | 95% | 0% | -220.8238 | 2243.562 | -3550 | -400 | -1706.438 | 42.66% | 78.15% | 95% | 0% | 2927 | -193
[5 empty] | 2019-03-15 | 39 | 1771.5 | 2704 | -184 | 0 | 0 | 2888 | 2403.2976 | 2403.2976 | 2403.2976 | 2146.4138 | 780 | 200 | 3126.4138 | 78.16% | 95% | 0% | -210.5263 | 2192.7713 | -2750 | -200 | -757.2287 | 18.93% | 78.14% | 95% | 0% | 2888 | -184
[5 empty] | 2019-03-15 | 40 | 1772 | 2648 | -174 | 0 | 0 | 2822 | 2299.9176 | 2299.9176 | 2299.9176 | 2146.4138 | 780 | 200 | 3126.4138 | 78.16% | 95% | 0% | -199.0847 | 2100.8329 | -2750 | -200 | -849.1671 | 21.23% | 78.14% | 95% | 0% | 2822 | -174
[5 empty] | 2019-03-15 | 41 | 1772.5 | 2561 | -165 | 0 | 0 | 2726 | 2149.5466 | 2149.5466 | 2149.5466 | 2146.4138 | 780 | 200 | 3126.4138 | 78.16% | 95% | 0% | -188.7872 | 1960.7594 | -2750 | -200 | -989.2406 | 24.73% | 78.13% | 95% | 0% | 2726 | -165
[5 empty] | 2019-03-15 | 42 | 1773 | 2485 | -156 | 0 | 0 | 2641 | 2016.4056 | 2016.4056 | 2016.4056 | 2146.4138 | 780 | 200 | 3126.4138 | 78.16% | 95% | 0% | -178.4897 | 1837.9159 | -2750 | -200 | -1112.0841 | 27.8% | 78.13% | 95% | 0% | 2641 | -156
[5 empty] | 2019-03-15 | 43 | 1773.5 | 2410 | -152 | 0 | 0 | 2562 | 1892.6628 | 1892.6628 | 1892.6628 | 2146.4138 | 780 | 200 | 3126.4138 | 78.16% | 95% | 0% | -173.913 | 1718.7498 | -2750 | -200 | -1231.2502 | 30.78% | 78.12% | 95% | 0% | 2562 | -152
[5 empty] | 2019-03-15 | 44 | 1774 | 2320 | -148 | 0 | 0 | 2468 | 1745.4246 | 1745.4246 | 1745.4246 | 2146.4138 | 780 | 200 | 3126.4138 | 78.16% | 95% | 0% | -169.3364 | 1576.0882 | -2750 | -200 | -1373.9118 | 34.35% | 78.11% | 95% | 0% | 2468 | -148
[5 empty] | 2019-03-15 | 45 | 1774.5 | 2185 | -146 | 0 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 2144.8475 | 780 | 200 | 3124.8475 | 78.12% | 95% | 0% | -167.0481 | 1363.7846 | -2750 | -200 | -1586.2154 | 39.66% | 78.11% | 95% | 0% | 2331 | -146
[5 empty] | 2019-03-15 | 46 | 1775 | 2076 | -144 | 0 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 2144.8475 | 780 | 200 | 3124.8475 | 78.12% | 95% | 0% | -164.7597 | 1192.2065 | -2750 | -200 | -1757.7935 | 43.94% | 78.1% | 95% | 0% | 2220 | -144
[5 empty] | 2019-03-15 | 47 | 1775.5 | 1946 | -142 | 0 | 0 | 2088 | 1150.2061 | 1150.2061 | 1150.2061 | 2144.8475 | 780 | 200 | 3124.8475 | 78.12% | 95% | 0% | -162.4714 | 987.7347 | -2750 | -200 | -1962.2653 | 49.06% | 78.09% | 95% | 0% | 2088 | -142
[5 empty] | 2019-03-15 | 48 | 1776 | 1868 | -140 | 0 | 0 | 2008 | 1024.8969 | 1024.8969 | 1024.8969 | 2144.8475 | 780 | 200 | 3124.8475 | 78.12% | 95% | 0% | -160.1831 | 864.7139 | -2750 | -200 | -2085.2861 | 52.13% | 78.08% | 95% | 0% | 2008 | -140
[5 empty] | 2019-03-16 | 1 | 1776.5 | 1849 | -134 | 0 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 2144.8475 | 780 | 200 | 3124.8475 | 78.12% | 95% | 0% | -153.3181 | 832.4198 | -2750 | -200 | -2117.5802 | 52.94% | 78.08% | 95% | 0% | 1983 | -134
[5 empty] | 2019-03-16 | 2 | 1777 | 1847 | -128 | 0 | 0 | 1975 | 973.2069 | 973.2069 | 973.2069 | 2144.8475 | 780 | 200 | 3124.8475 | 78.12% | 95% | 0% | -146.4531 | 826.7538 | -2750 | -200 | -2123.2462 | 53.08% | 78.08% | 95% | 0% | 1975 | -128
[5 empty] | 2019-03-16 | 3 | 1777.5 | 1809 | -121 | 0 | 0 | 1930 | 902.7205 | 902.7205 | 902.7205 | 2144.8475 | 780 | 200 | 3124.8475 | 78.12% | 95% | 0% | -138.4439 | 764.2766 | -2750 | -200 | -2185.7234 | 54.64% | 78.07% | 95% | 0% | 1930 | -121
[5 empty] | 2019-03-16 | 4 | 1778 | 1771 | -113 | 0 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 2143.2811 | 780 | 200 | 3123.2811 | 78.08% | 95% | 0% | -129.2906 | 701.3771 | -2750 | -200 | -2248.6229 | 56.22% | 78.07% | 95% | 0% | 1884 | -113
[5 empty] | 2019-03-16 | 5 | 1778.5 | 1741 | -106 | 0 | 0 | 1847 | 772.7123 | 772.7123 | 772.7123 | 2143.2811 | 780 | 200 | 3123.2811 | 78.08% | 95% | 0% | -121.2815 | 651.4308 | -2750 | -200 | -2298.5692 | 57.46% | 78.07% | 95% | 0% | 1847 | -106
[5 empty] | 2019-03-16 | 6 | 1779 | 1723 | -100 | 0 | 0 | 1823 | 735.1195 | 735.1195 | 735.1195 | 2143.2811 | 780 | 200 | 3123.2811 | 78.08% | 95% | 0% | -114.4165 | 620.7031 | -2750 | -200 | -2329.2969 | 58.23% | 78.06% | 95% | 0% | 1823 | -100
[5 empty] | 2019-03-16 | 7 | 1779.5 | 1702 | -106 | 0 | 0 | 1808 | 711.6241 | 711.6241 | 711.6241 | 2143.2811 | 780 | 200 | 3123.2811 | 78.08% | 95% | 0% | -121.2815 | 590.3426 | -2750 | -200 | -2359.6574 | 58.99% | 78.05% | 95% | 0% | 1808 | -106
[5 empty] | 2019-03-16 | 8 | 1780 | 1658 | -113 | 1 | 0 | 1771 | 653.6686 | 653.6686 | 653.6686 | 2143.2811 | 780 | 200 | 3123.2811 | 78.08% | 95% | 0% | -129.2906 | 524.378 | -3550 | -400 | -3425.622 | 85.64% | 78.05% | 95% | 0% | 1771 | -113
[5 empty] | 2019-03-16 | 9 | 1780.5 | 1618 | -121 | 1 | 0 | 1739 | 603.5449 | 603.5449 | 603.5449 | 2141.7148 | 780 | 200 | 3121.7148 | 78.04% | 95% | 0% | -138.4439 | 465.101 | -3550 | -400 | -3484.899 | 87.12% | 78.04% | 95% | 0% | 1739 | -121
[5 empty] | 2019-03-16 | 10 | 1781 | 1589 | -128 | 1 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 2141.7148 | 780 | 200 | 3121.7148 | 78.04% | 95% | 0% | -146.4531 | 422.6318 | -3550 | -400 | -3527.3682 | 88.18% | 78.04% | 95% | 0% | 1717 | -128
[5 empty] | 2019-03-16 | 11 | 1781.5 | 1592 | -137 | 1 | 0 | 1729 | 587.8813 | 587.8813 | 587.8813 | 2141.7148 | 780 | 200 | 3121.7148 | 78.04% | 95% | 0% | -156.7506 | 431.1307 | -3550 | -400 | -3518.8693 | 87.97% | 78.03% | 95% | 0% | 1729 | -137
[5 empty] | 2019-03-16 | 12 | 1782 | 1608 | -145 | 1 | 0 | 1753 | 625.474 | 625.474 | 625.474 | 2141.7148 | 780 | 200 | 3121.7148 | 78.04% | 95% | 0% | -165.9039 | 459.5701 | -3550 | -400 | -3490.4299 | 87.26% | 78.03% | 95% | 0% | 1753 | -145
[5 empty] | 2019-03-16 | 13 | 1782.5 | 1691 | -146 | 1 | 0 | 1837 | 757.0486 | 757.0486 | 757.0486 | 2141.7148 | 780 | 200 | 3121.7148 | 78.04% | 95% | 0% | -167.0481 | 590.0006 | -3550 | -400 | -3359.9994 | 84% | 78.03% | 95% | 0% | 1837 | -146
[5 empty] | 2019-03-16 | 14 | 1783 | 1753 | -148 | 1 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 2141.7148 | 780 | 200 | 3121.7148 | 78.04% | 95% | 0% | -169.3364 | 687.9596 | -3550 | -400 | -3262.0404 | 81.55% | 78.02% | 95% | 0% | 1901 | -148
[5 empty] | 2019-03-16 | 15 | 1783.5 | 1856 | -163 | 1 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 2141.7148 | 780 | 200 | 3121.7148 | 78.04% | 95% | 0% | -186.4989 | 855.6281 | -3550 | -400 | -3094.3719 | 77.36% | 78.02% | 95% | 0% | 2019 | -163
[5 empty] | 2019-03-16 | 16 | 1784 | 1926 | -187 | 1 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 2141.7148 | 780 | 200 | 3121.7148 | 78.04% | 95% | 0% | -213.9588 | 975.4064 | -3550 | -400 | -2974.5936 | 74.36% | 78.02% | 95% | 0% | 2113 | -187
[5 empty] | 2019-03-16 | 17 | 1784.5 | 2046 | -211 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 2140.1484 | 780 | 200 | 3120.1484 | 78% | 95% | 0% | -241.4188 | 1173.5029 | -3550 | -400 | -2776.4971 | 69.41% | 78.02% | 95% | 0% | 2257 | -211
[5 empty] | 2019-03-16 | 18 | 1785 | 2135 | -228 | 1 | 0 | 2363 | 1580.9563 | 1580.9563 | 1580.9563 | 2140.1484 | 780 | 200 | 3120.1484 | 78% | 95% | 0% | -260.8696 | 1320.0867 | -3550 | -400 | -2629.9133 | 65.75% | 78.01% | 95% | 0% | 2363 | -228
[5 empty] | 2019-03-16 | 19 | 1785.5 | 2217 | -249 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 2140.1484 | 780 | 200 | 3120.1484 | 78% | 95% | 0% | -284.897 | 1457.3948 | -3550 | -400 | -2492.6052 | 62.32% | 78.01% | 95% | 0% | 2466 | -249
[5 empty] | 2019-03-16 | 20 | 1786 | 2221 | -268 | 1 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 2140.1484 | 780 | 200 | 3120.1484 | 78% | 95% | 0% | -306.6362 | 1471.6821 | -3550 | -400 | -2478.3179 | 61.96% | 78.01% | 95% | 0% | 2489 | -268
[5 empty] | 2019-03-16 | 21 | 1786.5 | 2201 | -293 | 1 | 0 | 2494 | 1786.15 | 1786.15 | 1786.15 | 2138.582 | 780 | 200 | 3118.582 | 77.96% | 95% | 0% | -335.2403 | 1450.9098 | -3550 | -400 | -2499.0902 | 62.48% | 78.01% | 95% | 0% | 2494 | -293
[5 empty] | 2019-03-16 | 22 | 1787 | 2173 | -315 | 1 | 0 | 2488 | 1776.7519 | 1776.7519 | 1776.7519 | 2138.582 | 780 | 200 | 3118.582 | 77.96% | 95% | 0% | -360.4119 | 1416.34 | -3550 | -400 | -2533.66 | 63.34% | 78% | 95% | 0% | 2488 | -315
[5 empty] | 2019-03-16 | 23 | 1787.5 | 2149 | -341 | 1 | 0 | 2490 | 1779.8846 | 1779.8846 | 1779.8846 | 2138.582 | 780 | 200 | 3118.582 | 77.96% | 95% | 0% | -390.1602 | 1389.7244 | -3550 | -400 | -2560.2756 | 64.01% | 78% | 95% | 0% | 2490 | -341
[5 empty] | 2019-03-16 | 24 | 1788 | 2122 | -362 | 1 | 0 | 2484 | 1770.4864 | 1770.4864 | 1770.4864 | 2138.582 | 780 | 200 | 3118.582 | 77.96% | 95% | 0% | -414.1876 | 1356.2988 | -3550 | -400 | -2593.7012 | 64.84% | 77.99% | 95% | 0% | 2484 | -362
[5 empty] | 2019-03-16 | 25 | 1788.5 | 2102 | -364 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 2138.582 | 780 | 200 | 3118.582 | 77.96% | 95% | 0% | -416.476 | 1325.8159 | -3550 | -400 | -2624.1841 | 65.6% | 77.99% | 95% | 0% | 2466 | -364
[5 empty] | 2019-03-16 | 26 | 1789 | 2106 | -338 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 2138.582 | 780 | 200 | 3118.582 | 77.96% | 95% | 0% | -386.7277 | 1321.1041 | -3550 | -400 | -2628.8959 | 65.72% | 77.98% | 95% | 0% | 2444 | -338
[5 empty] | 2019-03-16 | 27 | 1789.5 | 2098 | -328 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 2138.582 | 780 | 200 | 3118.582 | 77.96% | 95% | 0% | -375.286 | 1304.3512 | -3550 | -400 | -2645.6488 | 66.14% | 77.98% | 95% | 0% | 2426 | -328
[5 empty] | 2019-03-16 | 28 | 1790 | 2085 | -323 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 2138.582 | 780 | 200 | 3118.582 | 77.96% | 95% | 0% | -369.5652 | 1281.8775 | -3550 | -400 | -2668.1225 | 66.7% | 77.97% | 95% | 0% | 2408 | -323
[5 empty] | 2019-03-16 | 29 | 1790.5 | 2105 | -311 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 2138.582 | 780 | 200 | 3118.582 | 77.96% | 95% | 0% | -355.8352 | 1308.1384 | -3550 | -400 | -2641.8616 | 66.05% | 77.96% | 95% | 0% | 2416 | -311
[5 empty] | 2019-03-16 | 30 | 1791 | 2115 | -292 | 1 | 0 | 2407 | 1649.8763 | 1649.8763 | 1649.8763 | 2138.582 | 780 | 200 | 3118.582 | 77.96% | 95% | 0% | -334.0961 | 1315.7802 | -3550 | -400 | -2634.2198 | 65.86% | 77.96% | 95% | 0% | 2407 | -292
[5 empty] | 2019-03-16 | 31 | 1791.5 | 2134 | -286 | 1 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 2137.0157 | 780 | 200 | 3117.0157 | 77.93% | 95% | 0% | -327.2311 | 1343.008 | -3550 | -400 | -2606.992 | 65.17% | 77.96% | 95% | 0% | 2420 | -286
[5 empty] | 2019-03-16 | 32 | 1792 | 2168 | -270 | 1 | 0 | 2438 | 1698.4336 | 1698.4336 | 1698.4336 | 2137.0157 | 780 | 200 | 3117.0157 | 77.93% | 95% | 0% | -308.9245 | 1389.5092 | -3550 | -400 | -2560.4908 | 64.01% | 77.95% | 95% | 0% | 2438 | -270
[5 empty] | 2019-03-16 | 33 | 1792.5 | 2206 | -264 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 2137.0157 | 780 | 200 | 3117.0157 | 77.93% | 95% | 0% | -302.0595 | 1446.4978 | -3550 | -400 | -2503.5022 | 62.59% | 77.95% | 95% | 0% | 2470 | -264
[5 empty] | 2019-03-16 | 34 | 1793 | 2284 | -258 | 1 | 0 | 2542 | 1861.3355 | 1861.3355 | 1861.3355 | 2137.0157 | 780 | 200 | 3117.0157 | 77.93% | 95% | 0% | -295.1945 | 1566.141 | -3550 | -400 | -2383.859 | 59.6% | 77.93% | 95% | 0% | 2542 | -258
[5 empty] | 2019-03-16 | 35 | 1793.5 | 2384 | -241 | 1 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 2137.0157 | 780 | 200 | 3117.0157 | 77.93% | 95% | 0% | -275.7437 | 1715.6001 | -3550 | -400 | -2234.3999 | 55.86% | 77.92% | 95% | 0% | 2625 | -241
[5 empty] | 2019-03-16 | 36 | 1794 | 2429 | -229 | 1 | 0 | 2658 | 2043.0338 | 2043.0338 | 2043.0338 | 2137.0157 | 780 | 200 | 3117.0157 | 77.93% | 95% | 0% | -262.0137 | 1781.0201 | -3550 | -400 | -2168.9799 | 54.22% | 77.92% | 95% | 0% | 2658 | -229
[5 empty] | 2019-03-16 | 37 | 1794.5 | 2458 | -224 | 1 | 0 | 2682 | 2080.6265 | 2080.6265 | 2080.6265 | 2137.0157 | 780 | 200 | 3117.0157 | 77.93% | 95% | 0% | -256.2929 | 1824.3336 | -3550 | -400 | -2125.6664 | 53.14% | 77.92% | 95% | 0% | 2682 | -224
[5 empty] | 2019-03-16 | 38 | 1795 | 2479 | -219 | 1 | 0 | 2698 | 2105.6884 | 2105.6884 | 2105.6884 | 2137.0157 | 780 | 200 | 3117.0157 | 77.93% | 95% | 0% | -250.5721 | 1855.1163 | -3550 | -400 | -2094.8837 | 52.37% | 77.92% | 95% | 0% | 2698 | -219
[5 empty] | 2019-03-16 | 39 | 1795.5 | 2464 | -212 | 0 | 0 | 2676 | 2071.2284 | 2071.2284 | 2071.2284 | 2137.0157 | 780 | 200 | 3117.0157 | 77.93% | 95% | 0% | -242.5629 | 1828.6654 | -2750 | -200 | -1121.3346 | 28.03% | 77.92% | 95% | 0% | 2676 | -212
[5 empty] | 2019-03-16 | 40 | 1796 | 2400 | -206 | 0 | 0 | 2606 | 1961.5829 | 1961.5829 | 1961.5829 | 2137.0157 | 780 | 200 | 3117.0157 | 77.93% | 95% | 0% | -235.6979 | 1725.8849 | -2750 | -200 | -1224.1151 | 30.6% | 77.91% | 95% | 0% | 2606 | -206
[5 empty] | 2019-03-16 | 41 | 1796.5 | 2349 | -199 | 0 | 0 | 2548 | 1870.7337 | 1870.7337 | 1870.7337 | 2137.0157 | 780 | 200 | 3117.0157 | 77.93% | 95% | 0% | -227.6888 | 1643.0449 | -2750 | -200 | -1306.9551 | 32.67% | 77.91% | 95% | 0% | 2548 | -199
[5 empty] | 2019-03-16 | 42 | 1797 | 2257 | -192 | 0 | 0 | 2449 | 1715.6636 | 1715.6636 | 1715.6636 | 2137.0157 | 780 | 200 | 3117.0157 | 77.93% | 95% | 0% | -219.6796 | 1495.984 | -2750 | -200 | -1454.016 | 36.35% | 77.91% | 95% | 0% | 2449 | -192
[5 empty] | 2019-03-16 | 43 | 1797.5 | 2172 | -189 | 0 | 0 | 2361 | 1577.8236 | 1577.8236 | 1577.8236 | 2135.4493 | 780 | 200 | 3115.4493 | 77.89% | 95% | 0% | -216.2471 | 1361.5764 | -2750 | -200 | -1588.4236 | 39.71% | 77.91% | 95% | 0% | 2361 | -189
[5 empty] | 2019-03-16 | 44 | 1798 | 2093 | -185 | 0 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 2135.4493 | 780 | 200 | 3115.4493 | 77.89% | 95% | 0% | -211.6705 | 1236.1449 | -2750 | -200 | -1713.8551 | 42.85% | 77.91% | 95% | 0% | 2278 | -185
[5 empty] | 2019-03-16 | 45 | 1798.5 | 2004 | -183 | 0 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 2135.4493 | 780 | 200 | 3115.4493 | 77.89% | 95% | 0% | -209.3822 | 1095.894 | -2750 | -200 | -1854.106 | 46.35% | 77.9% | 95% | 0% | 2187 | -183
[5 empty] | 2019-03-16 | 46 | 1799 | 1923 | -181 | 0 | 0 | 2104 | 1175.2679 | 1175.2679 | 1175.2679 | 2135.4493 | 780 | 200 | 3115.4493 | 77.89% | 95% | 0% | -207.0938 | 968.1741 | -2750 | -200 | -1981.8259 | 49.55% | 77.9% | 95% | 0% | 2104 | -181
[5 empty] | 2019-03-16 | 47 | 1799.5 | 1804 | -181 | 0 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 2135.4493 | 780 | 200 | 3115.4493 | 77.89% | 95% | 0% | -207.0938 | 781.7767 | -2750 | -200 | -2168.2233 | 54.21% | 77.9% | 95% | 0% | 1985 | -181
[5 empty] | 2019-03-16 | 48 | 1800 | 1741 | -180 | 0 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 2135.4493 | 780 | 200 | 3115.4493 | 77.89% | 95% | 0% | -205.9497 | 682.6736 | -2750 | -200 | -2267.3264 | 56.68% | 77.89% | 95% | 0% | 1921 | -180
[5 empty] | 2019-03-17 | 1 | 1800.5 | 1724 | -181 | 0 | 0 | 1905 | 863.5614 | 863.5614 | 863.5614 | 2135.4493 | 780 | 200 | 3115.4493 | 77.89% | 95% | 0% | -207.0938 | 656.4676 | -2750 | -200 | -2293.5324 | 57.34% | 77.88% | 95% | 0% | 1905 | -181
[5 empty] | 2019-03-17 | 2 | 1801 | 1738 | -183 | 0 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 2135.4493 | 780 | 200 | 3115.4493 | 77.89% | 95% | 0% | -209.3822 | 679.2411 | -2750 | -200 | -2270.7589 | 56.77% | 77.88% | 95% | 0% | 1921 | -183
[5 empty] | 2019-03-17 | 3 | 1801.5 | 1700 | -184 | 0 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 2135.4493 | 780 | 200 | 3115.4493 | 77.89% | 95% | 0% | -210.5263 | 620.1415 | -2750 | -200 | -2329.8585 | 58.25% | 77.86% | 95% | 0% | 1884 | -184
[5 empty] | 2019-03-17 | 4 | 1802 | 1643 | -184 | 0 | 0 | 1827 | 741.385 | 741.385 | 741.385 | 2135.4493 | 780 | 200 | 3115.4493 | 77.89% | 95% | 0% | -210.5263 | 530.8587 | -2750 | -200 | -2419.1413 | 60.48% | 77.85% | 95% | 0% | 1827 | -184
[5 empty] | 2019-03-17 | 5 | 1802.5 | 1584 | -185 | 0 | 0 | 1769 | 650.5359 | 650.5359 | 650.5359 | 2135.4493 | 780 | 200 | 3115.4493 | 77.89% | 95% | 0% | -211.6705 | 438.8654 | -2750 | -200 | -2511.1346 | 62.78% | 77.85% | 95% | 0% | 1769 | -185
[5 empty] | 2019-03-17 | 6 | 1803 | 1559 | -187 | 0 | 0 | 1746 | 614.5095 | 614.5095 | 614.5095 | 2135.4493 | 780 | 200 | 3115.4493 | 77.89% | 95% | 0% | -213.9588 | 400.5507 | -2750 | -200 | -2549.4493 | 63.74% | 77.85% | 95% | 0% | 1746 | -187
[5 empty] | 2019-03-17 | 7 | 1803.5 | 1532 | -186 | 0 | 0 | 1718 | 570.6513 | 570.6513 | 570.6513 | 2133.8829 | 780 | 200 | 3113.8829 | 77.85% | 95% | 0% | -212.8146 | 357.8366 | -2750 | -200 | -2592.1634 | 64.8% | 77.85% | 95% | 0% | 1718 | -186
[5 empty] | 2019-03-17 | 8 | 1804 | 1491 | -184 | 0 | 0 | 1675 | 503.2976 | 503.2976 | 503.2976 | 2133.8829 | 780 | 200 | 3113.8829 | 77.85% | 95% | 0% | -210.5263 | 292.7713 | -2750 | -200 | -2657.2287 | 66.43% | 77.84% | 95% | 0% | 1675 | -184
[5 empty] | 2019-03-17 | 9 | 1804.5 | 1459 | -186 | 0 | 0 | 1645 | 456.3067 | 456.3067 | 456.3067 | 2133.8829 | 780 | 200 | 3113.8829 | 77.85% | 95% | 0% | -212.8146 | 243.492 | -2750 | -200 | -2706.508 | 67.66% | 77.84% | 95% | 0% | 1645 | -186
[5 empty] | 2019-03-17 | 10 | 1805 | 1466 | -187 | 0 | 0 | 1653 | 468.8376 | 468.8376 | 468.8376 | 2133.8829 | 780 | 200 | 3113.8829 | 77.85% | 95% | 0% | -213.9588 | 254.8788 | -2750 | -200 | -2695.1212 | 67.38% | 77.84% | 95% | 0% | 1653 | -187
[5 empty] | 2019-03-17 | 11 | 1805.5 | 1466 | -186 | 0 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 2133.8829 | 780 | 200 | 3113.8829 | 77.85% | 95% | 0% | -212.8146 | 254.4566 | -2750 | -200 | -2695.5434 | 67.39% | 77.84% | 95% | 0% | 1652 | -186
[5 empty] | 2019-03-17 | 12 | 1806 | 1503 | -186 | 0 | 0 | 1689 | 525.2267 | 525.2267 | 525.2267 | 2133.8829 | 780 | 200 | 3113.8829 | 77.85% | 95% | 0% | -212.8146 | 312.4121 | -2750 | -200 | -2637.5879 | 65.94% | 77.84% | 95% | 0% | 1689 | -186
[5 empty] | 2019-03-17 | 13 | 1806.5 | 1546 | -188 | 0 | 0 | 1734 | 595.7131 | 595.7131 | 595.7131 | 2133.8829 | 780 | 200 | 3113.8829 | 77.85% | 95% | 0% | -215.103 | 380.6101 | -2750 | -200 | -2569.3899 | 64.23% | 77.84% | 95% | 0% | 1734 | -188
[5 empty] | 2019-03-17 | 14 | 1807 | 1556 | -216 | 0 | 0 | 1772 | 655.235 | 655.235 | 655.235 | 2132.3166 | 780 | 200 | 3112.3166 | 77.81% | 95% | 0% | -247.1396 | 408.0954 | -2750 | -200 | -2541.9046 | 63.55% | 77.83% | 95% | 0% | 1772 | -216
[5 empty] | 2019-03-17 | 15 | 1807.5 | 1520 | -290 | 0 | 0 | 1810 | 714.7568 | 714.7568 | 714.7568 | 2132.3166 | 780 | 200 | 3112.3166 | 77.81% | 95% | 0% | -331.8078 | 382.949 | -2750 | -200 | -2567.051 | 64.18% | 77.83% | 95% | 0% | 1810 | -290
[5 empty] | 2019-03-17 | 16 | 1808 | 1428 | -376 | 1 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 2132.3166 | 780 | 200 | 3112.3166 | 77.81% | 95% | 0% | -430.2059 | 275.1527 | -3550 | -400 | -3674.8473 | 91.87% | 77.83% | 95% | 0% | 1804 | -376
[5 empty] | 2019-03-17 | 17 | 1808.5 | 1389 | -457 | 1 | 0 | 1846 | 771.1459 | 771.1459 | 771.1459 | 2132.3166 | 780 | 200 | 3112.3166 | 77.81% | 95% | 0% | -522.8833 | 248.2626 | -3550 | -400 | -3701.7374 | 92.54% | 77.81% | 95% | 0% | 1846 | -457
[5 empty] | 2019-03-17 | 18 | 1809 | 1344 | -537 | 1 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 2132.3166 | 780 | 200 | 3112.3166 | 77.81% | 95% | 0% | -614.4165 | 211.5522 | -3550 | -400 | -3738.4478 | 93.46% | 77.81% | 95% | 0% | 1881 | -537
[5 empty] | 2019-03-17 | 19 | 1809.5 | 1372 | -575 | 1 | 0 | 1947 | 929.3487 | 929.3487 | 929.3487 | 2132.3166 | 780 | 200 | 3112.3166 | 77.81% | 95% | 0% | -657.8947 | 271.454 | -3550 | -400 | -3678.546 | 91.96% | 77.8% | 95% | 0% | 1947 | -575
[5 empty] | 2019-03-17 | 20 | 1810 | 1340 | -628 | 1 | 0 | 1968 | 962.2424 | 962.2424 | 962.2424 | 2132.3166 | 780 | 200 | 3112.3166 | 77.81% | 95% | 0% | -718.5355 | 243.7069 | -3550 | -400 | -3706.2931 | 92.66% | 77.8% | 95% | 0% | 1968 | -628
[5 empty] | 2019-03-17 | 21 | 1810.5 | 1326 | -673 | 1 | 0 | 1999 | 1010.7997 | 1010.7997 | 1010.7997 | 2132.3166 | 780 | 200 | 3112.3166 | 77.81% | 95% | 0% | -770.0229 | 240.7768 | -3550 | -400 | -3709.2232 | 92.73% | 77.79% | 95% | 0% | 1999 | -673
[5 empty] | 2019-03-17 | 22 | 1811 | 1323 | -689 | 1 | 0 | 2012 | 1031.1624 | 1031.1624 | 1031.1624 | 2130.7502 | 780 | 200 | 3110.7502 | 77.77% | 95% | 0% | -788.3295 | 242.8329 | -3550 | -400 | -3707.1671 | 92.68% | 77.79% | 95% | 0% | 2012 | -689
[5 empty] | 2019-03-17 | 23 | 1811.5 | 1340 | -694 | 1 | 0 | 2034 | 1065.6224 | 1065.6224 | 1065.6224 | 2130.7502 | 780 | 200 | 3110.7502 | 77.77% | 95% | 0% | -794.0503 | 271.5721 | -3550 | -400 | -3678.4279 | 91.96% | 77.79% | 95% | 0% | 2034 | -694
[5 empty] | 2019-03-17 | 24 | 1812 | 1331 | -719 | 1 | 0 | 2050 | 1090.6843 | 1090.6843 | 1090.6843 | 2130.7502 | 780 | 200 | 3110.7502 | 77.77% | 95% | 0% | -822.6545 | 268.0298 | -3550 | -400 | -3681.9702 | 92.05% | 77.79% | 95% | 0% | 2050 | -719
[5 empty] | 2019-03-17 | 25 | 1812.5 | 1346 | -715 | 1 | 0 | 2061 | 1107.9143 | 1107.9143 | 1107.9143 | 2130.7502 | 780 | 200 | 3110.7502 | 77.77% | 95% | 0% | -818.0778 | 289.8365 | -3550 | -400 | -3660.1635 | 91.5% | 77.77% | 95% | 0% | 2061 | -715
[5 empty] | 2019-03-17 | 26 | 1813 | 1366 | -699 | 1 | 0 | 2065 | 1114.1797 | 1114.1797 | 1114.1797 | 2130.7502 | 780 | 200 | 3110.7502 | 77.77% | 95% | 0% | -799.7712 | 314.4086 | -3550 | -400 | -3635.5914 | 90.89% | 77.77% | 95% | 0% | 2065 | -699
[5 empty] | 2019-03-17 | 27 | 1813.5 | 1391 | -660 | 1 | 0 | 2051 | 1092.2506 | 1092.2506 | 1092.2506 | 2130.7502 | 780 | 200 | 3110.7502 | 77.77% | 95% | 0% | -755.1487 | 337.1019 | -3550 | -400 | -3612.8981 | 90.32% | 77.76% | 95% | 0% | 2051 | -660
[5 empty] | 2019-03-17 | 28 | 1814 | 1433 | -625 | 1 | 0 | 2058 | 1103.2152 | 1103.2152 | 1103.2152 | 2130.7502 | 780 | 200 | 3110.7502 | 77.77% | 95% | 0% | -715.103 | 388.1122 | -3550 | -400 | -3561.8878 | 89.05% | 77.76% | 95% | 0% | 2058 | -625
[5 empty] | 2019-03-17 | 29 | 1814.5 | 1518 | -560 | 1 | 0 | 2078 | 1134.5425 | 1134.5425 | 1134.5425 | 2129.1838 | 780 | 200 | 3109.1838 | 77.73% | 95% | 0% | -640.7323 | 493.8102 | -3550 | -400 | -3456.1898 | 86.4% | 77.76% | 95% | 0% | 2078 | -560
[5 empty] | 2019-03-17 | 30 | 1815 | 1617 | -505 | 1 | 0 | 2122 | 1203.4625 | 1203.4625 | 1203.4625 | 2129.1838 | 780 | 200 | 3109.1838 | 77.73% | 95% | 0% | -577.8032 | 625.6593 | -3550 | -400 | -3324.3407 | 83.11% | 77.75% | 95% | 0% | 2122 | -505
[5 empty] | 2019-03-17 | 31 | 1815.5 | 1708 | -482 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 2129.1838 | 780 | 200 | 3109.1838 | 77.73% | 95% | 0% | -551.4874 | 758.4879 | -3550 | -400 | -3191.5121 | 79.79% | 77.75% | 95% | 0% | 2190 | -482
[5 empty] | 2019-03-17 | 32 | 1816 | 1869 | -410 | 1 | 0 | 2279 | 1449.3817 | 1449.3817 | 1449.3817 | 2129.1838 | 780 | 200 | 3109.1838 | 77.73% | 95% | 0% | -469.1076 | 980.2741 | -3550 | -400 | -2969.7259 | 74.24% | 77.75% | 95% | 0% | 2279 | -410
[5 empty] | 2019-03-17 | 33 | 1816.5 | 2042 | -358 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 2129.1838 | 780 | 200 | 3109.1838 | 77.73% | 95% | 0% | -409.611 | 1229.3008 | -3550 | -400 | -2720.6992 | 68.02% | 77.74% | 95% | 0% | 2400 | -358
[5 empty] | 2019-03-17 | 34 | 1817 | 2248 | -296 | 1 | 0 | 2544 | 1864.4683 | 1864.4683 | 1864.4683 | 2129.1838 | 780 | 200 | 3109.1838 | 77.73% | 95% | 0% | -338.6728 | 1525.7955 | -3550 | -400 | -2424.2045 | 60.61% | 77.74% | 95% | 0% | 2544 | -296
[5 empty] | 2019-03-17 | 35 | 1817.5 | 2430 | -239 | 1 | 0 | 2669 | 2060.2638 | 2060.2638 | 2060.2638 | 2129.1838 | 780 | 200 | 3109.1838 | 77.73% | 95% | 0% | -273.4554 | 1786.8084 | -3550 | -400 | -2163.1916 | 54.08% | 77.73% | 95% | 0% | 2669 | -239
[5 empty] | 2019-03-17 | 36 | 1818 | 2569 | -185 | 1 | 0 | 2754 | 2193.4048 | 2193.4048 | 2193.4048 | 2129.1838 | 780 | 200 | 3109.1838 | 77.73% | 95% | 0% | -211.6705 | 1981.7343 | -3550 | -400 | -1968.2657 | 49.21% | 77.72% | 95% | 0% | 2754 | -185
[5 empty] | 2019-03-17 | 37 | 1818.5 | 2635 | -166 | 1 | 0 | 2801 | 2267.0239 | 2267.0239 | 2267.0239 | 2129.1838 | 780 | 200 | 3109.1838 | 77.73% | 95% | 0% | -189.9314 | 2077.0926 | -3550 | -400 | -1872.9074 | 46.82% | 77.72% | 95% | 0% | 2801 | -166
[5 empty] | 2019-03-17 | 38 | 1819 | 2723 | -162 | 0 | 0 | 2885 | 2398.5985 | 2398.5985 | 2398.5985 | 2127.6175 | 780 | 200 | 3107.6175 | 77.69% | 95% | 0% | -185.3547 | 2213.2438 | -2750 | -200 | -736.7562 | 18.42% | 77.71% | 95% | 0% | 2885 | -162
[5 empty] | 2019-03-17 | 39 | 1819.5 | 2706 | -159 | 0 | 0 | 2865 | 2367.2712 | 2367.2712 | 2367.2712 | 2127.6175 | 780 | 200 | 3107.6175 | 77.69% | 95% | 0% | -181.9222 | 2185.349 | -2750 | -200 | -764.651 | 19.12% | 77.71% | 95% | 0% | 2865 | -159
[5 empty] | 2019-03-17 | 40 | 1820 | 2622 | -156 | 0 | 0 | 2778 | 2230.9975 | 2230.9975 | 2230.9975 | 2127.6175 | 780 | 200 | 3107.6175 | 77.69% | 95% | 0% | -178.4897 | 2052.5078 | -2750 | -200 | -897.4922 | 22.44% | 77.71% | 95% | 0% | 2778 | -156
[5 empty] | 2019-03-17 | 41 | 1820.5 | 2565 | -154 | 0 | 0 | 2719 | 2138.582 | 2138.582 | 2138.582 | 2127.6175 | 780 | 200 | 3107.6175 | 77.69% | 95% | 0% | -176.2014 | 1962.3807 | -2750 | -200 | -987.6193 | 24.69% | 77.71% | 95% | 0% | 2719 | -154
[5 empty] | 2019-03-17 | 42 | 1821 | 2482 | -153 | 0 | 0 | 2635 | 2007.0074 | 2007.0074 | 2007.0074 | 2127.6175 | 780 | 200 | 3107.6175 | 77.69% | 95% | 0% | -175.0572 | 1831.9502 | -2750 | -200 | -1118.0498 | 27.95% | 77.71% | 95% | 0% | 2635 | -153
[5 empty] | 2019-03-17 | 43 | 1821.5 | 2387 | -149 | 0 | 0 | 2536 | 1851.9373 | 1851.9373 | 1851.9373 | 2127.6175 | 780 | 200 | 3107.6175 | 77.69% | 95% | 0% | -170.4805 | 1681.4568 | -2750 | -200 | -1268.5432 | 31.71% | 77.7% | 95% | 0% | 2536 | -149
[5 empty] | 2019-03-17 | 44 | 1822 | 2250 | -145 | 0 | 0 | 2395 | 1631.08 | 1631.08 | 1631.08 | 2126.0511 | 780 | 200 | 3106.0511 | 77.65% | 95% | 0% | -165.9039 | 1465.1761 | -2750 | -200 | -1484.8239 | 37.12% | 77.7% | 95% | 0% | 2395 | -145
[5 empty] | 2019-03-17 | 45 | 1822.5 | 2127 | -140 | 0 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 2126.0511 | 780 | 200 | 3106.0511 | 77.65% | 95% | 0% | -160.1831 | 1270.4023 | -2750 | -200 | -1679.5977 | 41.99% | 77.69% | 95% | 0% | 2267 | -140
[5 empty] | 2019-03-17 | 46 | 1823 | 2020 | -136 | 0 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 2126.0511 | 780 | 200 | 3106.0511 | 77.65% | 95% | 0% | -155.6064 | 1101.1125 | -2750 | -200 | -1848.8875 | 46.22% | 77.69% | 95% | 0% | 2156 | -136
[5 empty] | 2019-03-17 | 47 | 1823.5 | 1882 | -128 | 0 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 2126.0511 | 780 | 200 | 3106.0511 | 77.65% | 95% | 0% | -146.4531 | 881.5766 | -2750 | -200 | -2068.4234 | 51.71% | 77.68% | 95% | 0% | 2010 | -128
[5 empty] | 2019-03-17 | 48 | 1824 | 1809 | -120 | 1 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 2126.0511 | 780 | 200 | 3106.0511 | 77.65% | 95% | 0% | -137.2998 | 763.8544 | -3550 | -400 | -3186.1456 | 79.65% | 77.68% | 95% | 0% | 1929 | -120
[5 empty] | 2019-03-18 | 1 | 1824.5 | 1811 | -117 | 1 | 0 | 1928 | 899.5878 | 899.5878 | 899.5878 | 2126.0511 | 780 | 200 | 3106.0511 | 77.65% | 95% | 0% | -133.8673 | 765.7205 | -3550 | -400 | -3184.2795 | 79.61% | 77.67% | 95% | 0% | 1928 | -117
[5 empty] | 2019-03-18 | 2 | 1825 | 1857 | -113 | 1 | 0 | 1970 | 965.3751 | 965.3751 | 965.3751 | 2124.4847 | 780 | 200 | 3104.4847 | 77.61% | 95% | 0% | -129.2906 | 836.0845 | -3550 | -400 | -3113.9155 | 77.85% | 77.67% | 95% | 0% | 1970 | -113
[5 empty] | 2019-03-18 | 3 | 1825.5 | 1839 | -111 | 1 | 0 | 1950 | 934.0478 | 934.0478 | 934.0478 | 2124.4847 | 780 | 200 | 3104.4847 | 77.61% | 95% | 0% | -127.0023 | 807.0455 | -3550 | -400 | -3142.9545 | 78.57% | 77.66% | 95% | 0% | 1950 | -111
[5 empty] | 2019-03-18 | 4 | 1826 | 1813 | -109 | 1 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 2124.4847 | 780 | 200 | 3104.4847 | 77.61% | 95% | 0% | -124.714 | 765.4757 | -3550 | -400 | -3184.5243 | 79.61% | 77.66% | 95% | 0% | 1922 | -109
[5 empty] | 2019-03-18 | 5 | 1826.5 | 1793 | -107 | 1 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 2122.9184 | 780 | 200 | 3102.9184 | 77.57% | 95% | 0% | -122.4256 | 733.304 | -3550 | -400 | -3216.696 | 80.42% | 77.66% | 95% | 0% | 1900 | -107
[5 empty] | 2019-03-18 | 6 | 1827 | 1780 | -105 | 1 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 2122.9184 | 780 | 200 | 3102.9184 | 77.57% | 95% | 0% | -120.1373 | 712.0968 | -3550 | -400 | -3237.9032 | 80.95% | 77.66% | 95% | 0% | 1885 | -105
[5 empty] | 2019-03-18 | 7 | 1827.5 | 1775 | -102 | 1 | 0 | 1877 | 819.7032 | 819.7032 | 819.7032 | 2122.9184 | 780 | 200 | 3102.9184 | 77.57% | 95% | 0% | -116.7048 | 702.9984 | -3550 | -400 | -3247.0016 | 81.18% | 77.66% | 95% | 0% | 1877 | -102
[5 empty] | 2019-03-18 | 8 | 1828 | 1761 | -98 | 1 | 0 | 1859 | 791.5087 | 791.5087 | 791.5087 | 2122.9184 | 780 | 200 | 3102.9184 | 77.57% | 95% | 0% | -112.1281 | 679.3805 | -3550 | -400 | -3270.6195 | 81.77% | 77.65% | 95% | 0% | 1859 | -98
[5 empty] | 2019-03-18 | 9 | 1828.5 | 1762 | -94 | 1 | 0 | 1856 | 786.8096 | 786.8096 | 786.8096 | 2122.9184 | 780 | 200 | 3102.9184 | 77.57% | 95% | 0% | -107.5515 | 679.2581 | -3550 | -400 | -3270.7419 | 81.77% | 77.65% | 95% | 0% | 1856 | -94
[5 empty] | 2019-03-18 | 10 | 1829 | 1785 | -89 | 1 | 0 | 1874 | 815.0041 | 815.0041 | 815.0041 | 2122.9184 | 780 | 200 | 3102.9184 | 77.57% | 95% | 0% | -101.8307 | 713.1735 | -3550 | -400 | -3236.8265 | 80.92% | 77.64% | 95% | 0% | 1874 | -89
[5 empty] | 2019-03-18 | 11 | 1829.5 | 1871 | -86 | 1 | 0 | 1957 | 945.0124 | 945.0124 | 945.0124 | 2122.9184 | 780 | 200 | 3102.9184 | 77.57% | 95% | 0% | -98.3982 | 846.6142 | -3550 | -400 | -3103.3858 | 77.58% | 77.63% | 95% | 0% | 1957 | -86
[5 empty] | 2019-03-18 | 12 | 1830 | 1994 | -84 | 1 | 0 | 2078 | 1134.5425 | 1134.5425 | 1134.5425 | 2122.9184 | 780 | 200 | 3102.9184 | 77.57% | 95% | 0% | -96.1098 | 1038.4326 | -3550 | -400 | -2911.5674 | 72.79% | 77.63% | 95% | 0% | 2078 | -84
[5 empty] | 2019-03-18 | 13 | 1830.5 | 2216 | -80 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 2122.9184 | 780 | 200 | 3102.9184 | 77.57% | 95% | 0% | -91.5332 | 1384.4767 | -3550 | -400 | -2565.5233 | 64.14% | 77.63% | 95% | 0% | 2296 | -80
[5 empty] | 2019-03-18 | 14 | 1831 | 2428 | -90 | 1 | 0 | 2518 | 1823.7428 | 1823.7428 | 1823.7428 | 2121.352 | 780 | 200 | 3101.352 | 77.53% | 95% | 0% | -102.9748 | 1720.768 | -3550 | -400 | -2229.232 | 55.73% | 77.63% | 95% | 0% | 2518 | -90
[5 empty] | 2019-03-18 | 15 | 1831.5 | 2595 | -126 | 1 | 0 | 2721 | 2141.7148 | 2141.7148 | 2141.7148 | 2121.352 | 780 | 200 | 3101.352 | 77.53% | 95% | 0% | -144.1648 | 1997.55 | -3550 | -400 | -1952.45 | 48.81% | 77.62% | 95% | 0% | 2721 | -126
[5 empty] | 2019-03-18 | 16 | 1832 | 2608 | -182 | 1 | 0 | 2790 | 2249.7939 | 2249.7939 | 2249.7939 | 2121.352 | 780 | 200 | 3101.352 | 77.53% | 95% | 0% | -208.238 | 2041.5559 | -3550 | -400 | -1908.4441 | 47.71% | 77.62% | 95% | 0% | 2790 | -182
[5 empty] | 2019-03-18 | 17 | 1832.5 | 2599 | -236 | 1 | 0 | 2835 | 2320.2803 | 2320.2803 | 2320.2803 | 2121.352 | 780 | 200 | 3101.352 | 77.53% | 95% | 0% | -270.0229 | 2050.2574 | -3550 | -400 | -1899.7426 | 47.49% | 77.61% | 95% | 0% | 2835 | -236
[5 empty] | 2019-03-18 | 18 | 1833 | 2530 | -303 | 1 | 0 | 2833 | 2317.1476 | 2317.1476 | 2317.1476 | 2121.352 | 780 | 200 | 3101.352 | 77.53% | 95% | 0% | -346.6819 | 1970.4656 | -3550 | -400 | -1979.5344 | 49.49% | 77.61% | 95% | 0% | 2833 | -303
[5 empty] | 2019-03-18 | 19 | 1833.5 | 2499 | -347 | 1 | 0 | 2846 | 2337.5103 | 2337.5103 | 2337.5103 | 2121.352 | 780 | 200 | 3101.352 | 77.53% | 95% | 0% | -397.0252 | 1940.4851 | -3550 | -400 | -2009.5149 | 50.24% | 77.61% | 95% | 0% | 2846 | -347
[5 empty] | 2019-03-18 | 20 | 1834 | 2468 | -355 | 1 | 0 | 2823 | 2301.4839 | 2301.4839 | 2301.4839 | 2121.352 | 780 | 200 | 3101.352 | 77.53% | 95% | 0% | -406.1785 | 1895.3054 | -3550 | -400 | -2054.6946 | 51.37% | 77.6% | 95% | 0% | 2823 | -355
[5 empty] | 2019-03-18 | 21 | 1834.5 | 2428 | -377 | 1 | 0 | 2805 | 2273.2894 | 2273.2894 | 2273.2894 | 2119.7857 | 780 | 200 | 3099.7857 | 77.49% | 95% | 0% | -431.3501 | 1841.9393 | -3550 | -400 | -2108.0607 | 52.7% | 77.6% | 95% | 0% | 2805 | -377
[5 empty] | 2019-03-18 | 22 | 1835 | 2368 | -407 | 1 | 0 | 2775 | 2226.2984 | 2226.2984 | 2226.2984 | 2119.7857 | 780 | 200 | 3099.7857 | 77.49% | 95% | 0% | -465.6751 | 1760.6234 | -3550 | -400 | -2189.3766 | 54.73% | 77.6% | 95% | 0% | 2775 | -407
[5 empty] | 2019-03-18 | 23 | 1835.5 | 2388 | -383 | 1 | 0 | 2771 | 2220.033 | 2220.033 | 2220.033 | 2119.7857 | 780 | 200 | 3099.7857 | 77.49% | 95% | 0% | -438.2151 | 1781.8179 | -3550 | -400 | -2168.1821 | 54.2% | 77.6% | 95% | 0% | 2771 | -383
[5 empty] | 2019-03-18 | 24 | 1836 | 2398 | -397 | 1 | 0 | 2795 | 2257.6257 | 2257.6257 | 2257.6257 | 2118.2193 | 780 | 200 | 3098.2193 | 77.46% | 95% | 0% | -454.2334 | 1803.3923 | -3550 | -400 | -2146.6077 | 53.67% | 77.59% | 95% | 0% | 2795 | -397
[5 empty] | 2019-03-18 | 25 | 1836.5 | 2452 | -381 | 1 | 0 | 2833 | 2317.1476 | 2317.1476 | 2317.1476 | 2118.2193 | 780 | 200 | 3098.2193 | 77.46% | 95% | 0% | -435.9268 | 1881.2208 | -3550 | -400 | -2068.7792 | 51.72% | 77.59% | 95% | 0% | 2833 | -381
[5 empty] | 2019-03-18 | 26 | 1837 | 2487 | -342 | 1 | 0 | 2829 | 2310.8821 | 2310.8821 | 2310.8821 | 2118.2193 | 780 | 200 | 3098.2193 | 77.46% | 95% | 0% | -391.3043 | 1919.5778 | -3550 | -400 | -2030.4222 | 50.76% | 77.58% | 95% | 0% | 2829 | -342
[5 empty] | 2019-03-18 | 27 | 1837.5 | 2514 | -325 | 1 | 0 | 2839 | 2326.5458 | 2326.5458 | 2326.5458 | 2118.2193 | 780 | 200 | 3098.2193 | 77.46% | 95% | 0% | -371.8535 | 1954.6922 | -3550 | -400 | -1995.3078 | 49.88% | 77.58% | 95% | 0% | 2839 | -325
[5 empty] | 2019-03-18 | 28 | 1838 | 2519 | -308 | 1 | 0 | 2827 | 2307.7494 | 2307.7494 | 2307.7494 | 2118.2193 | 780 | 200 | 3098.2193 | 77.46% | 95% | 0% | -352.4027 | 1955.3466 | -3550 | -400 | -1994.6534 | 49.87% | 77.58% | 95% | 0% | 2827 | -308
[5 empty] | 2019-03-18 | 29 | 1838.5 | 2584 | -274 | 1 | 0 | 2858 | 2356.3067 | 2356.3067 | 2356.3067 | 2118.2193 | 780 | 200 | 3098.2193 | 77.46% | 95% | 0% | -313.5011 | 2042.8055 | -3550 | -400 | -1907.1945 | 47.68% | 77.57% | 95% | 0% | 2858 | -274
[5 empty] | 2019-03-18 | 30 | 1839 | 2617 | -252 | 1 | 0 | 2869 | 2373.5367 | 2373.5367 | 2373.5367 | 2118.2193 | 780 | 200 | 3098.2193 | 77.46% | 95% | 0% | -288.3295 | 2085.2072 | -3550 | -400 | -1864.7928 | 46.62% | 77.56% | 95% | 0% | 2869 | -252
[5 empty] | 2019-03-18 | 31 | 1839.5 | 2635 | -229 | 1 | 0 | 2864 | 2365.7049 | 2365.7049 | 2365.7049 | 2118.2193 | 780 | 200 | 3098.2193 | 77.46% | 95% | 0% | -262.0137 | 2103.6911 | -3550 | -400 | -1846.3089 | 46.16% | 77.54% | 95% | 0% | 2864 | -229
[5 empty] | 2019-03-18 | 32 | 1840 | 2722 | -184 | 1 | 0 | 2906 | 2431.4922 | 2431.4922 | 2431.4922 | 2118.2193 | 780 | 200 | 3098.2193 | 77.46% | 95% | 0% | -210.5263 | 2220.9659 | -3550 | -400 | -1729.0341 | 43.23% | 77.53% | 95% | 0% | 2906 | -184
[5 empty] | 2019-03-18 | 33 | 1840.5 | 2855 | -159 | 1 | 0 | 3014 | 2600.6595 | 2600.6595 | 2600.6595 | 2118.2193 | 780 | 200 | 3098.2193 | 77.46% | 95% | 0% | -181.9222 | 2418.7373 | -3550 | -400 | -1531.2627 | 38.28% | 77.52% | 95% | 0% | 3014 | -159
[5 empty] | 2019-03-18 | 34 | 1841 | 3009 | -117 | 1 | 0 | 3126 | 2776.0923 | 2776.0923 | 2776.0923 | 2116.6529 | 780 | 200 | 3096.6529 | 77.42% | 95% | 0% | -133.8673 | 2642.2251 | -3550 | -400 | -1307.7749 | 32.69% | 77.51% | 95% | 0% | 3126 | -117
[5 empty] | 2019-03-18 | 35 | 1841.5 | 3105 | -81 | 1 | 0 | 3186 | 2870.0742 | 2870.0742 | 2870.0742 | 2116.6529 | 780 | 200 | 3096.6529 | 77.42% | 95% | 0% | -92.6773 | 2777.3969 | -3550 | -400 | -1172.6031 | 29.32% | 77.5% | 95% | 0% | 3186 | -81
[5 empty] | 2019-03-18 | 36 | 1842 | 3171 | -49 | 1 | 0 | 3220 | 2923.3306 | 2923.3306 | 2923.3306 | 2116.6529 | 780 | 200 | 3096.6529 | 77.42% | 95% | 0% | -56.0641 | 2867.2665 | -3550 | -400 | -1082.7335 | 27.07% | 77.49% | 95% | 0% | 3220 | -49
[5 empty] | 2019-03-18 | 37 | 1842.5 | 3225 | -41 | 1 | 0 | 3266 | 2995.3833 | 2995.3833 | 2995.3833 | 2116.6529 | 780 | 200 | 3096.6529 | 77.42% | 95% | 0% | -46.9108 | 2948.4726 | -3550 | -400 | -1001.5274 | 25.04% | 77.49% | 95% | 0% | 3266 | -41
[5 empty] | 2019-03-18 | 38 | 1843 | 3288 | -41 | 1 | 0 | 3329 | 3094.0643 | 3094.0643 | 3094.0643 | 2116.6529 | 780 | 200 | 3096.6529 | 77.42% | 95% | 0% | -46.9108 | 3047.1535 | -3550 | -400 | -902.8465 | 22.57% | 77.47% | 95% | 0% | 3329 | -41
[5 empty] | 2019-03-18 | 39 | 1843.5 | 3250 | -41 | 0 | 0 | 3291 | 3034.5425 | 3034.5425 | 3034.5425 | 2116.6529 | 780 | 200 | 3096.6529 | 77.42% | 95% | 0% | -46.9108 | 2987.6317 | -2750 | -200 | 37.6317 | -0.9408% | 77.45% | 95% | 0% | 3291 | -41
[5 empty] | 2019-03-18 | 40 | 1844 | 3184 | -40 | 0 | 0 | 3224 | 2929.596 | 2929.596 | 2929.596 | 2116.6529 | 780 | 200 | 3096.6529 | 77.42% | 95% | 0% | -45.7666 | 2883.8295 | -2750 | -200 | -66.1705 | 1.654% | 77.45% | 95% | 0% | 3224 | -40
[5 empty] | 2019-03-18 | 41 | 1844.5 | 3072 | -40 | 0 | 0 | 3112 | 2754.1632 | 2754.1632 | 2754.1632 | 2116.6529 | 780 | 200 | 3096.6529 | 77.42% | 95% | 0% | -45.7666 | 2708.3966 | -2750 | -200 | -241.6034 | 6.04% | 77.45% | 95% | 0% | 3112 | -40
[5 empty] | 2019-03-18 | 42 | 1845 | 2969 | -40 | 0 | 0 | 3009 | 2592.8277 | 2592.8277 | 2592.8277 | 2116.6529 | 780 | 200 | 3096.6529 | 77.42% | 95% | 0% | -45.7666 | 2547.0611 | -2750 | -200 | -402.9389 | 10.07% | 77.45% | 95% | 0% | 3009 | -40
[5 empty] | 2019-03-18 | 43 | 1845.5 | 2861 | -41 | 0 | 0 | 2902 | 2425.2267 | 2425.2267 | 2425.2267 | 2115.0866 | 780 | 200 | 3095.0866 | 77.38% | 95% | 0% | -46.9108 | 2378.316 | -2750 | -200 | -571.684 | 14.29% | 77.45% | 95% | 0% | 2902 | -41
[5 empty] | 2019-03-18 | 44 | 1846 | 2694 | -41 | 0 | 0 | 2735 | 2163.6439 | 2163.6439 | 2163.6439 | 2115.0866 | 780 | 200 | 3095.0866 | 77.38% | 95% | 0% | -46.9108 | 2116.7331 | -2750 | -200 | -833.2669 | 20.83% | 77.44% | 95% | 0% | 2735 | -41
[5 empty] | 2019-03-18 | 45 | 1846.5 | 2519 | -41 | 0 | 0 | 2560 | 1889.5301 | 1889.5301 | 1889.5301 | 2115.0866 | 780 | 200 | 3095.0866 | 77.38% | 95% | 0% | -46.9108 | 1842.6193 | -2750 | -200 | -1107.3807 | 27.68% | 77.44% | 95% | 0% | 2560 | -41
[5 empty] | 2019-03-18 | 46 | 1847 | 2352 | -42 | 0 | 0 | 2394 | 1629.5136 | 1629.5136 | 1629.5136 | 2115.0866 | 780 | 200 | 3095.0866 | 77.38% | 95% | 0% | -48.0549 | 1581.4587 | -2750 | -200 | -1368.5413 | 34.21% | 77.43% | 95% | 0% | 2394 | -42
[5 empty] | 2019-03-18 | 47 | 1847.5 | 2206 | -43 | 0 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 2115.0866 | 780 | 200 | 3095.0866 | 77.38% | 95% | 0% | -49.1991 | 1353.1917 | -2750 | -200 | -1596.8083 | 39.92% | 77.42% | 95% | 0% | 2249 | -43
[5 empty] | 2019-03-18 | 48 | 1848 | 2116 | -44 | 0 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 2115.0866 | 780 | 200 | 3095.0866 | 77.38% | 95% | 0% | -50.3432 | 1212.6411 | -2750 | -200 | -1737.3589 | 43.43% | 77.42% | 95% | 0% | 2160 | -44
[5 empty] | 2019-03-19 | 1 | 1848.5 | 2087 | -44 | 0 | 0 | 2131 | 1217.5598 | 1217.5598 | 1217.5598 | 2115.0866 | 780 | 200 | 3095.0866 | 77.38% | 95% | 0% | -50.3432 | 1167.2165 | -2750 | -200 | -1782.7835 | 44.57% | 77.41% | 95% | 0% | 2131 | -44
[5 empty] | 2019-03-19 | 2 | 1849 | 2111 | -43 | 0 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 2115.0866 | 780 | 200 | 3095.0866 | 77.38% | 95% | 0% | -49.1991 | 1204.3871 | -2750 | -200 | -1745.6129 | 43.64% | 77.4% | 95% | 0% | 2154 | -43
[5 empty] | 2019-03-19 | 3 | 1849.5 | 2090 | -43 | 0 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 2113.5202 | 780 | 200 | 3093.5202 | 77.34% | 95% | 0% | -49.1991 | 1171.4934 | -2750 | -200 | -1778.5066 | 44.46% | 77.38% | 95% | 0% | 2133 | -43
[5 empty] | 2019-03-19 | 4 | 1850 | 2042 | -43 | 0 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 2113.5202 | 780 | 200 | 3093.5202 | 77.34% | 95% | 0% | -49.1991 | 1096.3079 | -2750 | -200 | -1853.6921 | 46.34% | 77.38% | 95% | 0% | 2085 | -43
[5 empty] | 2019-03-19 | 5 | 1850.5 | 2004 | -43 | 0 | 0 | 2047 | 1085.9852 | 1085.9852 | 1085.9852 | 2113.5202 | 780 | 200 | 3093.5202 | 77.34% | 95% | 0% | -49.1991 | 1036.7861 | -2750 | -200 | -1913.2139 | 47.83% | 77.38% | 95% | 0% | 2047 | -43
[5 empty] | 2019-03-19 | 6 | 1851 | 1989 | -43 | 0 | 0 | 2032 | 1062.4897 | 1062.4897 | 1062.4897 | 2113.5202 | 780 | 200 | 3093.5202 | 77.34% | 95% | 0% | -49.1991 | 1013.2906 | -2750 | -200 | -1936.7094 | 48.42% | 77.38% | 95% | 0% | 2032 | -43
[5 empty] | 2019-03-19 | 7 | 1851.5 | 1959 | -44 | 0 | 0 | 2003 | 1017.0651 | 1017.0651 | 1017.0651 | 2113.5202 | 780 | 200 | 3093.5202 | 77.34% | 95% | 0% | -50.3432 | 966.7219 | -2750 | -200 | -1983.2781 | 49.58% | 77.37% | 95% | 0% | 2003 | -44
[5 empty] | 2019-03-19 | 8 | 1852 | 1926 | -45 | 0 | 0 | 1971 | 966.9415 | 966.9415 | 966.9415 | 2111.9538 | 780 | 200 | 3091.9538 | 77.3% | 95% | 0% | -51.4874 | 915.4541 | -2750 | -200 | -2034.5459 | 50.86% | 77.37% | 95% | 0% | 1971 | -45
[5 empty] | 2019-03-19 | 9 | 1852.5 | 1915 | -47 | 0 | 0 | 1962 | 952.8442 | 952.8442 | 952.8442 | 2111.9538 | 780 | 200 | 3091.9538 | 77.3% | 95% | 0% | -53.7757 | 899.0684 | -2750 | -200 | -2050.9316 | 51.27% | 77.36% | 95% | 0% | 1962 | -47
[5 empty] | 2019-03-19 | 10 | 1853 | 1924 | -48 | 0 | 0 | 1972 | 968.5078 | 968.5078 | 968.5078 | 2111.9538 | 780 | 200 | 3091.9538 | 77.3% | 95% | 0% | -54.9199 | 913.5879 | -2750 | -200 | -2036.4121 | 50.91% | 77.36% | 95% | 0% | 1972 | -48
[5 empty] | 2019-03-19 | 11 | 1853.5 | 1982 | -51 | 0 | 0 | 2033 | 1064.0561 | 1064.0561 | 1064.0561 | 2111.9538 | 780 | 200 | 3091.9538 | 77.3% | 95% | 0% | -58.3524 | 1005.7037 | -2750 | -200 | -1944.2963 | 48.61% | 77.36% | 95% | 0% | 2033 | -51
[5 empty] | 2019-03-19 | 12 | 1854 | 2085 | -53 | 0 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 2111.9538 | 780 | 200 | 3091.9538 | 77.3% | 95% | 0% | -60.6407 | 1167.8836 | -2750 | -200 | -1782.1164 | 44.55% | 77.36% | 95% | 0% | 2138 | -53
[5 empty] | 2019-03-19 | 13 | 1854.5 | 2298 | -55 | 0 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 2111.9538 | 780 | 200 | 3091.9538 | 77.3% | 95% | 0% | -62.9291 | 1502.3636 | -2750 | -200 | -1447.6364 | 36.19% | 77.36% | 95% | 0% | 2353 | -55
[5 empty] | 2019-03-19 | 14 | 1855 | 2505 | -67 | 0 | 0 | 2572 | 1908.3265 | 1908.3265 | 1908.3265 | 2111.9538 | 780 | 200 | 3091.9538 | 77.3% | 95% | 0% | -76.659 | 1831.6674 | -2750 | -200 | -1118.3326 | 27.96% | 77.35% | 95% | 0% | 2572 | -67
[5 empty] | 2019-03-19 | 15 | 1855.5 | 2691 | -100 | 1 | 0 | 2791 | 2251.3603 | 2251.3603 | 2251.3603 | 2111.9538 | 780 | 200 | 3091.9538 | 77.3% | 95% | 0% | -114.4165 | 2136.9438 | -3550 | -400 | -1813.0562 | 45.33% | 77.35% | 95% | 0% | 2791 | -100
[5 empty] | 2019-03-19 | 16 | 1856 | 2749 | -126 | 1 | 0 | 2875 | 2382.9349 | 2382.9349 | 2382.9349 | 2111.9538 | 780 | 200 | 3091.9538 | 77.3% | 95% | 0% | -144.1648 | 2238.7701 | -3550 | -400 | -1711.2299 | 42.78% | 77.34% | 95% | 0% | 2875 | -126
[5 empty] | 2019-03-19 | 17 | 1856.5 | 2716 | -173 | 1 | 0 | 2889 | 2404.864 | 2404.864 | 2404.864 | 2111.9538 | 780 | 200 | 3091.9538 | 77.3% | 95% | 0% | -197.9405 | 2206.9235 | -3550 | -400 | -1743.0765 | 43.58% | 77.34% | 95% | 0% | 2889 | -173
[5 empty] | 2019-03-19 | 18 | 1857 | 2624 | -236 | 1 | 0 | 2860 | 2359.4394 | 2359.4394 | 2359.4394 | 2111.9538 | 780 | 200 | 3091.9538 | 77.3% | 95% | 0% | -270.0229 | 2089.4165 | -3550 | -400 | -1860.5835 | 46.51% | 77.34% | 95% | 0% | 2860 | -236
[5 empty] | 2019-03-19 | 19 | 1857.5 | 2534 | -307 | 1 | 0 | 2841 | 2329.6785 | 2329.6785 | 2329.6785 | 2110.3875 | 780 | 200 | 3090.3875 | 77.26% | 95% | 0% | -351.2586 | 1978.4199 | -3550 | -400 | -1971.5801 | 49.29% | 77.32% | 95% | 0% | 2841 | -307
[5 empty] | 2019-03-19 | 20 | 1858 | 2466 | -341 | 1 | 0 | 2807 | 2276.4221 | 2276.4221 | 2276.4221 | 2110.3875 | 780 | 200 | 3090.3875 | 77.26% | 95% | 0% | -390.1602 | 1886.2619 | -3550 | -400 | -2063.7381 | 51.59% | 77.32% | 95% | 0% | 2807 | -341
[5 empty] | 2019-03-19 | 21 | 1858.5 | 2410 | -343 | 1 | 0 | 2753 | 2191.8384 | 2191.8384 | 2191.8384 | 2110.3875 | 780 | 200 | 3090.3875 | 77.26% | 95% | 0% | -392.4485 | 1799.3899 | -3550 | -400 | -2150.6101 | 53.77% | 77.32% | 95% | 0% | 2753 | -343
[5 empty] | 2019-03-19 | 22 | 1859 | 2348 | -378 | 1 | 0 | 2726 | 2149.5466 | 2149.5466 | 2149.5466 | 2110.3875 | 780 | 200 | 3090.3875 | 77.26% | 95% | 0% | -432.4943 | 1717.0523 | -3550 | -400 | -2232.9477 | 55.82% | 77.3% | 95% | 0% | 2726 | -378
[5 empty] | 2019-03-19 | 23 | 1859.5 | 2330 | -388 | 1 | 0 | 2718 | 2137.0157 | 2137.0157 | 2137.0157 | 2108.8211 | 780 | 200 | 3088.8211 | 77.22% | 95% | 0% | -443.9359 | 1693.0797 | -3550 | -400 | -2256.9203 | 56.42% | 77.29% | 95% | 0% | 2718 | -388
[5 empty] | 2019-03-19 | 24 | 1860 | 2277 | -435 | 1 | 0 | 2712 | 2127.6175 | 2127.6175 | 2127.6175 | 2108.8211 | 780 | 200 | 3088.8211 | 77.22% | 95% | 0% | -497.7117 | 1629.9058 | -3550 | -400 | -2320.0942 | 58% | 77.29% | 95% | 0% | 2712 | -435
[5 empty] | 2019-03-19 | 25 | 1860.5 | 2331 | -395 | 1 | 0 | 2726 | 2149.5466 | 2149.5466 | 2149.5466 | 2108.8211 | 780 | 200 | 3088.8211 | 77.22% | 95% | 0% | -451.9451 | 1697.6015 | -3550 | -400 | -2252.3985 | 56.31% | 77.29% | 95% | 0% | 2726 | -395
[5 empty] | 2019-03-19 | 26 | 1861 | 2347 | -382 | 1 | 0 | 2729 | 2154.2457 | 2154.2457 | 2154.2457 | 2108.8211 | 780 | 200 | 3088.8211 | 77.22% | 95% | 0% | -437.0709 | 1717.1747 | -3550 | -400 | -2232.8253 | 55.82% | 77.29% | 95% | 0% | 2729 | -382
[5 empty] | 2019-03-19 | 27 | 1861.5 | 2394 | -345 | 1 | 0 | 2739 | 2169.9093 | 2169.9093 | 2169.9093 | 2108.8211 | 780 | 200 | 3088.8211 | 77.22% | 95% | 0% | -394.7368 | 1775.1725 | -3550 | -400 | -2174.8275 | 54.37% | 77.28% | 95% | 0% | 2739 | -345
[5 empty] | 2019-03-19 | 28 | 1862 | 2401 | -328 | 1 | 0 | 2729 | 2154.2457 | 2154.2457 | 2154.2457 | 2108.8211 | 780 | 200 | 3088.8211 | 77.22% | 95% | 0% | -375.286 | 1778.9596 | -3550 | -400 | -2171.0404 | 54.28% | 77.28% | 95% | 0% | 2729 | -328
[5 empty] | 2019-03-19 | 29 | 1862.5 | 2444 | -299 | 1 | 0 | 2743 | 2176.1748 | 2176.1748 | 2176.1748 | 2108.8211 | 780 | 200 | 3088.8211 | 77.22% | 95% | 0% | -342.1053 | 1834.0695 | -3550 | -400 | -2115.9305 | 52.9% | 77.26% | 95% | 0% | 2743 | -299
[5 empty] | 2019-03-19 | 30 | 1863 | 2438 | -291 | 1 | 0 | 2729 | 2154.2457 | 2154.2457 | 2154.2457 | 2108.8211 | 780 | 200 | 3088.8211 | 77.22% | 95% | 0% | -332.9519 | 1821.2937 | -3550 | -400 | -2128.7063 | 53.22% | 77.26% | 95% | 0% | 2729 | -291
[5 empty] | 2019-03-19 | 31 | 1863.5 | 2457 | -263 | 1 | 0 | 2720 | 2140.1484 | 2140.1484 | 2140.1484 | 2107.2547 | 780 | 200 | 3087.2547 | 77.18% | 95% | 0% | -300.9153 | 1839.2331 | -3550 | -400 | -2110.7669 | 52.77% | 77.26% | 95% | 0% | 2720 | -263
[5 empty] | 2019-03-19 | 32 | 1864 | 2539 | -243 | 1 | 0 | 2782 | 2237.263 | 2237.263 | 2237.263 | 2107.2547 | 780 | 200 | 3087.2547 | 77.18% | 95% | 0% | -278.032 | 1959.2309 | -3550 | -400 | -1990.7691 | 49.77% | 77.23% | 95% | 0% | 2782 | -243
[5 empty] | 2019-03-19 | 33 | 1864.5 | 2659 | -212 | 1 | 0 | 2871 | 2376.6694 | 2376.6694 | 2376.6694 | 2107.2547 | 780 | 200 | 3087.2547 | 77.18% | 95% | 0% | -242.5629 | 2134.1065 | -3550 | -400 | -1815.8935 | 45.4% | 77.23% | 95% | 0% | 2871 | -212
[5 empty] | 2019-03-19 | 34 | 1865 | 2795 | -168 | 1 | 0 | 2963 | 2520.7749 | 2520.7749 | 2520.7749 | 2107.2547 | 780 | 200 | 3087.2547 | 77.18% | 95% | 0% | -192.2197 | 2328.5553 | -3550 | -400 | -1621.4447 | 40.54% | 77.23% | 95% | 0% | 2963 | -168
[5 empty] | 2019-03-19 | 35 | 1865.5 | 2918 | -135 | 1 | 0 | 3053 | 2661.7477 | 2661.7477 | 2661.7477 | 2107.2547 | 780 | 200 | 3087.2547 | 77.18% | 95% | 0% | -154.4622 | 2507.2855 | -3550 | -400 | -1442.7145 | 36.07% | 77.21% | 95% | 0% | 3053 | -135
[5 empty] | 2019-03-19 | 36 | 1866 | 2994 | -116 | 1 | 0 | 3110 | 2751.0305 | 2751.0305 | 2751.0305 | 2107.2547 | 780 | 200 | 3087.2547 | 77.18% | 95% | 0% | -132.7231 | 2618.3074 | -3550 | -400 | -1331.6926 | 33.29% | 77.21% | 95% | 0% | 3110 | -116
[5 empty] | 2019-03-19 | 37 | 1866.5 | 3056 | -110 | 1 | 0 | 3166 | 2838.7469 | 2838.7469 | 2838.7469 | 2107.2547 | 780 | 200 | 3087.2547 | 77.18% | 95% | 0% | -125.8581 | 2712.8888 | -3550 | -400 | -1237.1112 | 30.93% | 77.21% | 95% | 0% | 3166 | -110
[5 empty] | 2019-03-19 | 38 | 1867 | 3111 | -110 | 1 | 0 | 3221 | 2924.8969 | 2924.8969 | 2924.8969 | 2105.6884 | 780 | 200 | 3085.6884 | 77.14% | 95% | 0% | -125.8581 | 2799.0388 | -3550 | -400 | -1150.9612 | 28.77% | 77.2% | 95% | 0% | 3221 | -110
[5 empty] | 2019-03-19 | 39 | 1867.5 | 3064 | -109 | 0 | 0 | 3173 | 2849.7115 | 2849.7115 | 2849.7115 | 2105.6884 | 780 | 200 | 3085.6884 | 77.14% | 95% | 0% | -124.714 | 2724.9975 | -2750 | -200 | -225.0025 | 5.625% | 77.19% | 95% | 0% | 3173 | -109
[5 empty] | 2019-03-19 | 40 | 1868 | 2967 | -109 | 0 | 0 | 3076 | 2697.7741 | 2697.7741 | 2697.7741 | 2105.6884 | 780 | 200 | 3085.6884 | 77.14% | 95% | 0% | -124.714 | 2573.0602 | -2750 | -200 | -376.9398 | 9.423% | 77.19% | 95% | 0% | 3076 | -109
[5 empty] | 2019-03-19 | 41 | 1868.5 | 2890 | -107 | 0 | 0 | 2997 | 2574.0313 | 2574.0313 | 2574.0313 | 2105.6884 | 780 | 200 | 3085.6884 | 77.14% | 95% | 0% | -122.4256 | 2451.6057 | -2750 | -200 | -498.3943 | 12.46% | 77.18% | 95% | 0% | 2997 | -107
[5 empty] | 2019-03-19 | 42 | 1869 | 2765 | -106 | 0 | 0 | 2871 | 2376.6694 | 2376.6694 | 2376.6694 | 2105.6884 | 780 | 200 | 3085.6884 | 77.14% | 95% | 0% | -121.2815 | 2255.388 | -2750 | -200 | -694.612 | 17.37% | 77.17% | 95% | 0% | 2871 | -106
[5 empty] | 2019-03-19 | 43 | 1869.5 | 2644 | -104 | 0 | 0 | 2748 | 2184.0066 | 2184.0066 | 2184.0066 | 2105.6884 | 780 | 200 | 3085.6884 | 77.14% | 95% | 0% | -118.9931 | 2065.0135 | -2750 | -200 | -884.9865 | 22.12% | 77.17% | 95% | 0% | 2748 | -104
[5 empty] | 2019-03-19 | 44 | 1870 | 2476 | -103 | 0 | 0 | 2579 | 1919.291 | 1919.291 | 1919.291 | 2105.6884 | 780 | 200 | 3085.6884 | 77.14% | 95% | 0% | -117.849 | 1801.442 | -2750 | -200 | -1148.558 | 28.71% | 77.16% | 95% | 0% | 2579 | -103
[5 empty] | 2019-03-19 | 45 | 1870.5 | 2314 | -101 | 0 | 0 | 2415 | 1662.4073 | 1662.4073 | 1662.4073 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -115.5606 | 1546.8466 | -2750 | -200 | -1403.1534 | 35.08% | 77.16% | 95% | 0% | 2415 | -101
[5 empty] | 2019-03-19 | 46 | 1871 | 2170 | -100 | 0 | 0 | 2270 | 1435.2844 | 1435.2844 | 1435.2844 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -114.4165 | 1320.8679 | -2750 | -200 | -1629.1321 | 40.73% | 77.15% | 95% | 0% | 2270 | -100
[5 empty] | 2019-03-19 | 47 | 1871.5 | 2016 | -99 | 0 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -113.2723 | 1079.2256 | -2750 | -200 | -1870.7744 | 46.77% | 77.15% | 95% | 0% | 2115 | -99
[5 empty] | 2019-03-19 | 48 | 1872 | 1922 | -98 | 0 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -112.1281 | 931.5652 | -2750 | -200 | -2018.4348 | 50.46% | 77.15% | 95% | 0% | 2020 | -98
[5 empty] | 2019-03-20 | 1 | 1872.5 | 1907 | -97 | 1 | 0 | 2004 | 1018.6315 | 1018.6315 | 1018.6315 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -110.984 | 907.6475 | -3550 | -400 | -3042.3525 | 76.06% | 77.15% | 95% | 0% | 2004 | -97
[5 empty] | 2019-03-20 | 2 | 1873 | 1932 | -97 | 1 | 0 | 2029 | 1057.7906 | 1057.7906 | 1057.7906 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -110.984 | 946.8066 | -3550 | -400 | -3003.1934 | 75.08% | 77.15% | 95% | 0% | 2029 | -97
[5 empty] | 2019-03-20 | 3 | 1873.5 | 1910 | -95 | 1 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -108.6957 | 911.5022 | -3550 | -400 | -3038.4978 | 75.96% | 77.13% | 95% | 0% | 2005 | -95
[5 empty] | 2019-03-20 | 4 | 1874 | 1860 | -94 | 1 | 0 | 1954 | 940.3133 | 940.3133 | 940.3133 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -107.5515 | 832.7618 | -3550 | -400 | -3117.2382 | 77.93% | 77.11% | 95% | 0% | 1954 | -94
[5 empty] | 2019-03-20 | 5 | 1874.5 | 1830 | -92 | 1 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -105.2632 | 784.9265 | -3550 | -400 | -3165.0735 | 79.13% | 77.11% | 95% | 0% | 1922 | -92
[5 empty] | 2019-03-20 | 6 | 1875 | 1805 | -90 | 1 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -102.9748 | 744.9229 | -3550 | -400 | -3205.0771 | 80.13% | 77.11% | 95% | 0% | 1895 | -90
[5 empty] | 2019-03-20 | 7 | 1875.5 | 1773 | -89 | 1 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -101.8307 | 694.3771 | -3550 | -400 | -3255.6229 | 81.39% | 77.1% | 95% | 0% | 1862 | -89
[5 empty] | 2019-03-20 | 8 | 1876 | 1746 | -88 | 1 | 0 | 1834 | 752.3495 | 752.3495 | 752.3495 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -100.6865 | 651.663 | -3550 | -400 | -3298.337 | 82.46% | 77.1% | 95% | 0% | 1834 | -88
[5 empty] | 2019-03-20 | 9 | 1876.5 | 1746 | -86 | 1 | 0 | 1832 | 749.2168 | 749.2168 | 749.2168 | 2104.122 | 780 | 200 | 3084.122 | 77.1% | 95% | 0% | -98.3982 | 650.8186 | -3550 | -400 | -3299.1814 | 82.48% | 77.1% | 95% | 0% | 1832 | -86
[5 empty] | 2019-03-20 | 10 | 1877 | 1773 | -83 | 1 | 0 | 1856 | 786.8096 | 786.8096 | 786.8096 | 2102.5556 | 780 | 200 | 3082.5556 | 77.06% | 95% | 0% | -94.9657 | 691.8439 | -3550 | -400 | -3258.1561 | 81.45% | 77.09% | 95% | 0% | 1856 | -83
[5 empty] | 2019-03-20 | 11 | 1877.5 | 1833 | -81 | 1 | 0 | 1914 | 877.6587 | 877.6587 | 877.6587 | 2102.5556 | 780 | 200 | 3082.5556 | 77.06% | 95% | 0% | -92.6773 | 784.9814 | -3550 | -400 | -3165.0186 | 79.13% | 77.09% | 95% | 0% | 1914 | -81
[5 empty] | 2019-03-20 | 12 | 1878 | 1954 | -79 | 1 | 0 | 2033 | 1064.0561 | 1064.0561 | 1064.0561 | 2102.5556 | 780 | 200 | 3082.5556 | 77.06% | 95% | 0% | -90.389 | 973.667 | -3550 | -400 | -2976.333 | 74.41% | 77.09% | 95% | 0% | 2033 | -79
[5 empty] | 2019-03-20 | 13 | 1878.5 | 2174 | -76 | 1 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 2100.9893 | 780 | 200 | 3080.9893 | 77.02% | 95% | 0% | -86.9565 | 1317.0006 | -3550 | -400 | -2632.9994 | 65.82% | 77.08% | 95% | 0% | 2250 | -76
[5 empty] | 2019-03-20 | 14 | 1879 | 2383 | -79 | 1 | 0 | 2462 | 1736.0264 | 1736.0264 | 1736.0264 | 2100.9893 | 780 | 200 | 3080.9893 | 77.02% | 95% | 0% | -90.389 | 1645.6374 | -3550 | -400 | -2304.3626 | 57.61% | 77.06% | 95% | 0% | 2462 | -79
[5 empty] | 2019-03-20 | 15 | 1879.5 | 2594 | -97 | 1 | 0 | 2691 | 2094.7238 | 2094.7238 | 2094.7238 | 2100.9893 | 780 | 200 | 3080.9893 | 77.02% | 95% | 0% | -110.984 | 1983.7398 | -3550 | -400 | -1966.2602 | 49.16% | 77.06% | 95% | 0% | 2691 | -97
[5 empty] | 2019-03-20 | 16 | 1880 | 2651 | -123 | 1 | 0 | 2774 | 2224.7321 | 2224.7321 | 2224.7321 | 2099.4229 | 780 | 200 | 3079.4229 | 76.99% | 95% | 0% | -140.7323 | 2083.9998 | -3550 | -400 | -1866.0002 | 46.65% | 77.06% | 95% | 0% | 2774 | -123
[5 empty] | 2019-03-20 | 17 | 1880.5 | 2650 | -156 | 1 | 0 | 2806 | 2274.8557 | 2274.8557 | 2274.8557 | 2099.4229 | 780 | 200 | 3079.4229 | 76.99% | 95% | 0% | -178.4897 | 2096.366 | -3550 | -400 | -1853.634 | 46.34% | 77.05% | 95% | 0% | 2806 | -156
[5 empty] | 2019-03-20 | 18 | 1881 | 2603 | -192 | 1 | 0 | 2795 | 2257.6257 | 2257.6257 | 2257.6257 | 2099.4229 | 780 | 200 | 3079.4229 | 76.99% | 95% | 0% | -219.6796 | 2037.9461 | -3550 | -400 | -1912.0539 | 47.8% | 77.05% | 95% | 0% | 2795 | -192
[5 empty] | 2019-03-20 | 19 | 1881.5 | 2561 | -241 | 1 | 0 | 2802 | 2268.5903 | 2268.5903 | 2268.5903 | 2099.4229 | 780 | 200 | 3079.4229 | 76.99% | 95% | 0% | -275.7437 | 1992.8466 | -3550 | -400 | -1957.1534 | 48.93% | 77.05% | 95% | 0% | 2802 | -241
[5 empty] | 2019-03-20 | 20 | 1882 | 2457 | -304 | 1 | 0 | 2761 | 2204.3693 | 2204.3693 | 2204.3693 | 2099.4229 | 780 | 200 | 3079.4229 | 76.99% | 95% | 0% | -347.8261 | 1856.5432 | -3550 | -400 | -2093.4568 | 52.34% | 77.04% | 95% | 0% | 2761 | -304
[5 empty] | 2019-03-20 | 21 | 1882.5 | 2377 | -363 | 1 | 0 | 2740 | 2171.4757 | 2171.4757 | 2171.4757 | 2099.4229 | 780 | 200 | 3079.4229 | 76.99% | 95% | 0% | -415.3318 | 1756.1439 | -3550 | -400 | -2193.8561 | 54.85% | 77.03% | 95% | 0% | 2740 | -363
[5 empty] | 2019-03-20 | 22 | 1883 | 2332 | -377 | 1 | 0 | 2709 | 2122.9184 | 2122.9184 | 2122.9184 | 2099.4229 | 780 | 200 | 3079.4229 | 76.99% | 95% | 0% | -431.3501 | 1691.5683 | -3550 | -400 | -2258.4317 | 56.46% | 77.03% | 95% | 0% | 2709 | -377
[5 empty] | 2019-03-20 | 23 | 1883.5 | 2301 | -392 | 1 | 0 | 2693 | 2097.8566 | 2097.8566 | 2097.8566 | 2099.4229 | 780 | 200 | 3079.4229 | 76.99% | 95% | 0% | -448.5126 | 1649.344 | -3550 | -400 | -2300.656 | 57.52% | 77.03% | 95% | 0% | 2693 | -392
[5 empty] | 2019-03-20 | 24 | 1884 | 2268 | -403 | 1 | 0 | 2671 | 2063.3965 | 2063.3965 | 2063.3965 | 2097.8566 | 780 | 200 | 3077.8566 | 76.95% | 95% | 0% | -461.0984 | 1602.2981 | -3550 | -400 | -2347.7019 | 58.69% | 77.03% | 95% | 0% | 2671 | -403
[5 empty] | 2019-03-20 | 25 | 1884.5 | 2234 | -431 | 1 | 0 | 2665 | 2053.9984 | 2053.9984 | 2053.9984 | 2097.8566 | 780 | 200 | 3077.8566 | 76.95% | 95% | 0% | -493.135 | 1560.8633 | -3550 | -400 | -2389.1367 | 59.73% | 77.02% | 95% | 0% | 2665 | -431
[5 empty] | 2019-03-20 | 26 | 1885 | 2187 | -449 | 1 | 0 | 2636 | 2008.5738 | 2008.5738 | 2008.5738 | 2097.8566 | 780 | 200 | 3077.8566 | 76.95% | 95% | 0% | -513.73 | 1494.8438 | -3550 | -400 | -2455.1562 | 61.38% | 77.02% | 95% | 0% | 2636 | -449
[5 empty] | 2019-03-20 | 27 | 1885.5 | 2192 | -426 | 1 | 0 | 2618 | 1980.3792 | 1980.3792 | 1980.3792 | 2097.8566 | 780 | 200 | 3077.8566 | 76.95% | 95% | 0% | -487.4142 | 1492.965 | -3550 | -400 | -2457.035 | 61.43% | 77.02% | 95% | 0% | 2618 | -426
[5 empty] | 2019-03-20 | 28 | 1886 | 2202 | -393 | 1 | 0 | 2595 | 1944.3528 | 1944.3528 | 1944.3528 | 2097.8566 | 780 | 200 | 3077.8566 | 76.95% | 95% | 0% | -449.6568 | 1494.6961 | -3550 | -400 | -2455.3039 | 61.38% | 77.02% | 95% | 0% | 2595 | -393
[5 empty] | 2019-03-20 | 29 | 1886.5 | 2204 | -389 | 1 | 0 | 2593 | 1941.2201 | 1941.2201 | 1941.2201 | 2097.8566 | 780 | 200 | 3077.8566 | 76.95% | 95% | 0% | -445.0801 | 1496.14 | -3550 | -400 | -2453.86 | 61.35% | 77.02% | 95% | 0% | 2593 | -389
[5 empty] | 2019-03-20 | 30 | 1887 | 2219 | -364 | 1 | 0 | 2583 | 1925.5565 | 1925.5565 | 1925.5565 | 2097.8566 | 780 | 200 | 3077.8566 | 76.95% | 95% | 0% | -416.476 | 1509.0805 | -3550 | -400 | -2440.9195 | 61.02% | 77% | 95% | 0% | 2583 | -364
[5 empty] | 2019-03-20 | 31 | 1887.5 | 2266 | -336 | 1 | 0 | 2602 | 1955.3174 | 1955.3174 | 1955.3174 | 2097.8566 | 780 | 200 | 3077.8566 | 76.95% | 95% | 0% | -384.4394 | 1570.878 | -3550 | -400 | -2379.122 | 59.48% | 76.99% | 95% | 0% | 2602 | -336
[5 empty] | 2019-03-20 | 32 | 1888 | 2364 | -297 | 1 | 0 | 2661 | 2047.7329 | 2047.7329 | 2047.7329 | 2097.8566 | 780 | 200 | 3077.8566 | 76.95% | 95% | 0% | -339.8169 | 1707.916 | -3550 | -400 | -2242.084 | 56.05% | 76.99% | 95% | 0% | 2661 | -297
[5 empty] | 2019-03-20 | 33 | 1888.5 | 2515 | -243 | 1 | 0 | 2758 | 2199.6702 | 2199.6702 | 2199.6702 | 2097.8566 | 780 | 200 | 3077.8566 | 76.95% | 95% | 0% | -278.032 | 1921.6382 | -3550 | -400 | -2028.3618 | 50.71% | 76.98% | 95% | 0% | 2758 | -243
[5 empty] | 2019-03-20 | 34 | 1889 | 2638 | -204 | 1 | 0 | 2842 | 2331.2448 | 2331.2448 | 2331.2448 | 2096.2902 | 780 | 200 | 3076.2902 | 76.91% | 95% | 0% | -233.4096 | 2097.8352 | -3550 | -400 | -1852.1648 | 46.3% | 76.98% | 95% | 0% | 2842 | -204
[5 empty] | 2019-03-20 | 35 | 1889.5 | 2762 | -168 | 1 | 0 | 2930 | 2469.0849 | 2469.0849 | 2469.0849 | 2096.2902 | 780 | 200 | 3076.2902 | 76.91% | 95% | 0% | -192.2197 | 2276.8652 | -3550 | -400 | -1673.1348 | 41.83% | 76.98% | 95% | 0% | 2930 | -168
[5 empty] | 2019-03-20 | 36 | 1890 | 2842 | -140 | 1 | 0 | 2982 | 2550.5359 | 2550.5359 | 2550.5359 | 2096.2902 | 780 | 200 | 3076.2902 | 76.91% | 95% | 0% | -160.1831 | 2390.3528 | -3550 | -400 | -1559.6472 | 38.99% | 76.97% | 95% | 0% | 2982 | -140
[5 empty] | 2019-03-20 | 37 | 1890.5 | 2921 | -129 | 1 | 0 | 3050 | 2657.0486 | 2657.0486 | 2657.0486 | 2096.2902 | 780 | 200 | 3076.2902 | 76.91% | 95% | 0% | -147.5973 | 2509.4514 | -3550 | -400 | -1440.5486 | 36.01% | 76.97% | 95% | 0% | 3050 | -129
[5 empty] | 2019-03-20 | 38 | 1891 | 3007 | -130 | 1 | 0 | 3137 | 2793.3223 | 2793.3223 | 2793.3223 | 2096.2902 | 780 | 200 | 3076.2902 | 76.91% | 95% | 0% | -148.7414 | 2644.5809 | -3550 | -400 | -1305.4191 | 32.64% | 76.96% | 95% | 0% | 3137 | -130
[5 empty] | 2019-03-20 | 39 | 1891.5 | 2993 | -132 | 1 | 0 | 3125 | 2774.526 | 2774.526 | 2774.526 | 2096.2902 | 780 | 200 | 3076.2902 | 76.91% | 95% | 0% | -151.0297 | 2623.4962 | -3550 | -400 | -1326.5038 | 33.16% | 76.93% | 95% | 0% | 3125 | -132
[5 empty] | 2019-03-20 | 40 | 1892 | 2897 | -133 | 0 | 0 | 3030 | 2625.7214 | 2625.7214 | 2625.7214 | 2094.7238 | 780 | 200 | 3074.7238 | 76.87% | 95% | 0% | -152.1739 | 2473.5474 | -2750 | -200 | -476.4526 | 11.91% | 76.93% | 95% | 0% | 3030 | -133
[5 empty] | 2019-03-20 | 41 | 1892.5 | 2810 | -135 | 0 | 0 | 2945 | 2492.5804 | 2492.5804 | 2492.5804 | 2094.7238 | 780 | 200 | 3074.7238 | 76.87% | 95% | 0% | -154.4622 | 2338.1181 | -2750 | -200 | -611.8819 | 15.3% | 76.93% | 95% | 0% | 2945 | -135
[5 empty] | 2019-03-20 | 42 | 1893 | 2660 | -137 | 0 | 0 | 2797 | 2260.7585 | 2260.7585 | 2260.7585 | 2094.7238 | 780 | 200 | 3074.7238 | 76.87% | 95% | 0% | -156.7506 | 2104.0079 | -2750 | -200 | -845.9921 | 21.15% | 76.91% | 95% | 0% | 2797 | -137
[5 empty] | 2019-03-20 | 43 | 1893.5 | 2529 | -139 | 0 | 0 | 2668 | 2058.6974 | 2058.6974 | 2058.6974 | 2094.7238 | 780 | 200 | 3074.7238 | 76.87% | 95% | 0% | -159.0389 | 1899.6585 | -2750 | -200 | -1050.3415 | 26.26% | 76.9% | 95% | 0% | 2668 | -139
[5 empty] | 2019-03-20 | 44 | 1894 | 2368 | -139 | 0 | 0 | 2507 | 1806.5128 | 1806.5128 | 1806.5128 | 2094.7238 | 780 | 200 | 3074.7238 | 76.87% | 95% | 0% | -159.0389 | 1647.4739 | -2750 | -200 | -1302.5261 | 32.56% | 76.9% | 95% | 0% | 2507 | -139
[5 empty] | 2019-03-20 | 45 | 1894.5 | 2202 | -139 | 0 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 2094.7238 | 780 | 200 | 3074.7238 | 76.87% | 95% | 0% | -159.0389 | 1387.4574 | -2750 | -200 | -1562.5426 | 39.06% | 76.9% | 95% | 0% | 2341 | -139
[5 empty] | 2019-03-20 | 46 | 1895 | 2059 | -138 | 0 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 2094.7238 | 780 | 200 | 3074.7238 | 76.87% | 95% | 0% | -157.8947 | 1163.0451 | -2750 | -200 | -1786.9549 | 44.67% | 76.9% | 95% | 0% | 2197 | -138
[5 empty] | 2019-03-20 | 47 | 1895.5 | 1916 | -138 | 0 | 0 | 2054 | 1096.9497 | 1096.9497 | 1096.9497 | 2094.7238 | 780 | 200 | 3074.7238 | 76.87% | 95% | 0% | -157.8947 | 939.055 | -2750 | -200 | -2010.945 | 50.27% | 76.89% | 95% | 0% | 2054 | -138
[5 empty] | 2019-03-20 | 48 | 1896 | 1820 | -138 | 0 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 2094.7238 | 780 | 200 | 3074.7238 | 76.87% | 95% | 0% | -157.8947 | 788.684 | -2750 | -200 | -2161.316 | 54.03% | 76.87% | 95% | 0% | 1958 | -138
[5 empty] | 2019-03-21 | 1 | 1896.5 | 1809 | -137 | 0 | 0 | 1946 | 927.7824 | 927.7824 | 927.7824 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -156.7506 | 771.0318 | -2750 | -200 | -2178.9682 | 54.47% | 76.87% | 95% | 0% | 1946 | -137
[5 empty] | 2019-03-21 | 2 | 1897 | 1826 | -136 | 0 | 0 | 1962 | 952.8442 | 952.8442 | 952.8442 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -155.6064 | 797.2378 | -2750 | -200 | -2152.7622 | 53.82% | 76.87% | 95% | 0% | 1962 | -136
[5 empty] | 2019-03-21 | 3 | 1897.5 | 1802 | -134 | 0 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -153.3181 | 758.8006 | -2750 | -200 | -2191.1994 | 54.78% | 76.86% | 95% | 0% | 1936 | -134
[5 empty] | 2019-03-21 | 4 | 1898 | 1746 | -132 | 0 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -151.0297 | 670.2398 | -2750 | -200 | -2279.7602 | 56.99% | 76.86% | 95% | 0% | 1878 | -132
[5 empty] | 2019-03-21 | 5 | 1898.5 | 1715 | -131 | 0 | 0 | 1846 | 771.1459 | 771.1459 | 771.1459 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -149.8856 | 621.2603 | -2750 | -200 | -2328.7397 | 58.22% | 76.86% | 95% | 0% | 1846 | -131
[5 empty] | 2019-03-21 | 6 | 1899 | 1695 | -129 | 0 | 0 | 1824 | 736.6859 | 736.6859 | 736.6859 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -147.5973 | 589.0886 | -2750 | -200 | -2360.9114 | 59.02% | 76.86% | 95% | 0% | 1824 | -129
[5 empty] | 2019-03-21 | 7 | 1899.5 | 1677 | -125 | 0 | 0 | 1802 | 702.2259 | 702.2259 | 702.2259 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -143.0206 | 559.2053 | -2750 | -200 | -2390.7947 | 59.77% | 76.85% | 95% | 0% | 1802 | -125
[5 empty] | 2019-03-21 | 8 | 1900 | 1647 | -121 | 0 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -138.4439 | 510.5256 | -2750 | -200 | -2439.4744 | 60.99% | 76.85% | 95% | 0% | 1768 | -121
[5 empty] | 2019-03-21 | 9 | 1900.5 | 1639 | -119 | 0 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -136.1556 | 497.1502 | -2750 | -200 | -2452.8498 | 61.32% | 76.84% | 95% | 0% | 1758 | -119
[5 empty] | 2019-03-21 | 10 | 1901 | 1677 | -118 | 0 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -135.0114 | 556.2499 | -2750 | -200 | -2393.7501 | 59.84% | 76.83% | 95% | 0% | 1795 | -118
[5 empty] | 2019-03-21 | 11 | 1901.5 | 1753 | -116 | 0 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -132.7231 | 674.4492 | -2750 | -200 | -2275.5508 | 56.89% | 76.83% | 95% | 0% | 1869 | -116
[5 empty] | 2019-03-21 | 12 | 1902 | 1873 | -114 | 0 | 0 | 1987 | 992.0033 | 992.0033 | 992.0033 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -130.4348 | 861.5685 | -2750 | -200 | -2088.4315 | 52.21% | 76.83% | 95% | 0% | 1987 | -114
[5 empty] | 2019-03-21 | 13 | 1902.5 | 2079 | -112 | 0 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -128.1465 | 1183.3952 | -2750 | -200 | -1766.6048 | 44.17% | 76.82% | 95% | 0% | 2191 | -112
[5 empty] | 2019-03-21 | 14 | 1903 | 2283 | -121 | 0 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -138.4439 | 1506.7333 | -2750 | -200 | -1443.2667 | 36.08% | 76.82% | 95% | 0% | 2404 | -121
[5 empty] | 2019-03-21 | 15 | 1903.5 | 2473 | -147 | 0 | 0 | 2620 | 1983.512 | 1983.512 | 1983.512 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -168.1922 | 1815.3197 | -2750 | -200 | -1134.6803 | 28.37% | 76.82% | 95% | 0% | 2620 | -147
[5 empty] | 2019-03-21 | 16 | 1904 | 2540 | -179 | 1 | 0 | 2719 | 2138.582 | 2138.582 | 2138.582 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -204.8055 | 1933.7765 | -3550 | -400 | -2016.2235 | 50.41% | 76.82% | 95% | 0% | 2719 | -179
[5 empty] | 2019-03-21 | 17 | 1904.5 | 2553 | -214 | 1 | 0 | 2767 | 2213.7675 | 2213.7675 | 2213.7675 | 2093.1575 | 780 | 200 | 3073.1575 | 76.83% | 95% | 0% | -244.8513 | 1968.9163 | -3550 | -400 | -1981.0837 | 49.53% | 76.82% | 95% | 0% | 2767 | -214
[5 empty] | 2019-03-21 | 18 | 1905 | 2510 | -251 | 1 | 0 | 2761 | 2204.3693 | 2204.3693 | 2204.3693 | 2091.5911 | 780 | 200 | 3071.5911 | 76.79% | 95% | 0% | -287.1854 | 1917.184 | -3550 | -400 | -2032.816 | 50.82% | 76.82% | 95% | 0% | 2761 | -251
[5 empty] | 2019-03-21 | 19 | 1905.5 | 2489 | -283 | 1 | 0 | 2772 | 2221.5993 | 2221.5993 | 2221.5993 | 2091.5911 | 780 | 200 | 3071.5911 | 76.79% | 95% | 0% | -323.7986 | 1897.8007 | -3550 | -400 | -2052.1993 | 51.3% | 76.79% | 95% | 0% | 2772 | -283
[5 empty] | 2019-03-21 | 20 | 1906 | 2432 | -304 | 1 | 0 | 2736 | 2165.2102 | 2165.2102 | 2165.2102 | 2091.5911 | 780 | 200 | 3071.5911 | 76.79% | 95% | 0% | -347.8261 | 1817.3841 | -3550 | -400 | -2132.6159 | 53.32% | 76.77% | 95% | 0% | 2736 | -304
[5 empty] | 2019-03-21 | 21 | 1906.5 | 2382 | -330 | 1 | 0 | 2712 | 2127.6175 | 2127.6175 | 2127.6175 | 2091.5911 | 780 | 200 | 3071.5911 | 76.79% | 95% | 0% | -377.5744 | 1750.0431 | -3550 | -400 | -2199.9569 | 55% | 76.77% | 95% | 0% | 2712 | -330
[5 empty] | 2019-03-21 | 22 | 1907 | 2380 | -323 | 1 | 0 | 2703 | 2113.5202 | 2113.5202 | 2113.5202 | 2091.5911 | 780 | 200 | 3071.5911 | 76.79% | 95% | 0% | -369.5652 | 1743.955 | -3550 | -400 | -2206.045 | 55.15% | 76.75% | 95% | 0% | 2703 | -323
[5 empty] | 2019-03-21 | 23 | 1907.5 | 2422 | -312 | 1 | 0 | 2734 | 2162.0775 | 2162.0775 | 2162.0775 | 2091.5911 | 780 | 200 | 3071.5911 | 76.79% | 95% | 0% | -356.9794 | 1805.0981 | -3550 | -400 | -2144.9019 | 53.62% | 76.75% | 95% | 0% | 2734 | -312
[5 empty] | 2019-03-21 | 24 | 1908 | 2444 | -298 | 1 | 0 | 2742 | 2174.6084 | 2174.6084 | 2174.6084 | 2091.5911 | 780 | 200 | 3071.5911 | 76.79% | 95% | 0% | -340.9611 | 1833.6473 | -3550 | -400 | -2116.3527 | 52.91% | 76.75% | 95% | 0% | 2742 | -298
[5 empty] | 2019-03-21 | 25 | 1908.5 | 2449 | -305 | 1 | 0 | 2754 | 2193.4048 | 2193.4048 | 2193.4048 | 2090.0247 | 780 | 200 | 3070.0247 | 76.75% | 95% | 0% | -348.9703 | 1844.4345 | -3550 | -400 | -2105.5655 | 52.64% | 76.74% | 95% | 0% | 2754 | -305
[5 empty] | 2019-03-21 | 26 | 1909 | 2451 | -294 | 1 | 0 | 2745 | 2179.3075 | 2179.3075 | 2179.3075 | 2090.0247 | 780 | 200 | 3070.0247 | 76.75% | 95% | 0% | -336.3844 | 1842.9231 | -3550 | -400 | -2107.0769 | 52.68% | 76.74% | 95% | 0% | 2745 | -294
[5 empty] | 2019-03-21 | 27 | 1909.5 | 2459 | -273 | 1 | 0 | 2732 | 2158.9448 | 2158.9448 | 2158.9448 | 2090.0247 | 780 | 200 | 3070.0247 | 76.75% | 95% | 0% | -312.357 | 1846.5878 | -3550 | -400 | -2103.4122 | 52.59% | 76.74% | 95% | 0% | 2732 | -273
[5 empty] | 2019-03-21 | 28 | 1910 | 2495 | -236 | 1 | 0 | 2731 | 2157.3784 | 2157.3784 | 2157.3784 | 2090.0247 | 780 | 200 | 3070.0247 | 76.75% | 95% | 0% | -270.0229 | 1887.3555 | -3550 | -400 | -2062.6445 | 51.57% | 76.72% | 95% | 0% | 2731 | -236
[5 empty] | 2019-03-21 | 29 | 1910.5 | 2518 | -218 | 1 | 0 | 2736 | 2165.2102 | 2165.2102 | 2165.2102 | 2090.0247 | 780 | 200 | 3070.0247 | 76.75% | 95% | 0% | -249.4279 | 1915.7823 | -3550 | -400 | -2034.2177 | 50.86% | 76.72% | 95% | 0% | 2736 | -218
[5 empty] | 2019-03-21 | 30 | 1911 | 2546 | -198 | 1 | 0 | 2744 | 2177.7411 | 2177.7411 | 2177.7411 | 2090.0247 | 780 | 200 | 3070.0247 | 76.75% | 95% | 0% | -226.5446 | 1951.1965 | -3550 | -400 | -1998.8035 | 49.97% | 76.72% | 95% | 0% | 2744 | -198
[5 empty] | 2019-03-21 | 31 | 1911.5 | 2560 | -188 | 1 | 0 | 2748 | 2184.0066 | 2184.0066 | 2184.0066 | 2090.0247 | 780 | 200 | 3070.0247 | 76.75% | 95% | 0% | -215.103 | 1968.9036 | -3550 | -400 | -1981.0964 | 49.53% | 76.71% | 95% | 0% | 2748 | -188
[5 empty] | 2019-03-21 | 32 | 1912 | 2616 | -162 | 1 | 0 | 2778 | 2230.9975 | 2230.9975 | 2230.9975 | 2090.0247 | 780 | 200 | 3070.0247 | 76.75% | 95% | 0% | -185.3547 | 2045.6428 | -3550 | -400 | -1904.3572 | 47.61% | 76.71% | 95% | 0% | 2778 | -162
[5 empty] | 2019-03-21 | 33 | 1912.5 | 2692 | -128 | 1 | 0 | 2820 | 2296.7848 | 2296.7848 | 2296.7848 | 2090.0247 | 780 | 200 | 3070.0247 | 76.75% | 95% | 0% | -146.4531 | 2150.3317 | -3550 | -400 | -1799.6683 | 44.99% | 76.69% | 95% | 0% | 2820 | -128
[5 empty] | 2019-03-21 | 34 | 1913 | 2804 | -96 | 1 | 0 | 2900 | 2422.094 | 2422.094 | 2422.094 | 2088.4584 | 780 | 200 | 3068.4584 | 76.71% | 95% | 0% | -109.8398 | 2312.2542 | -3550 | -400 | -1637.7458 | 40.94% | 76.67% | 95% | 0% | 2900 | -96
[5 empty] | 2019-03-21 | 35 | 1913.5 | 2897 | -73 | 1 | 0 | 2970 | 2531.7395 | 2531.7395 | 2531.7395 | 2088.4584 | 780 | 200 | 3068.4584 | 76.71% | 95% | 0% | -83.524 | 2448.2155 | -3550 | -400 | -1501.7845 | 37.54% | 76.67% | 95% | 0% | 2970 | -73
[5 empty] | 2019-03-21 | 36 | 1914 | 2934 | -62 | 1 | 0 | 2996 | 2572.465 | 2572.465 | 2572.465 | 2088.4584 | 780 | 200 | 3068.4584 | 76.71% | 95% | 0% | -70.9382 | 2501.5267 | -3550 | -400 | -1448.4733 | 36.21% | 76.66% | 95% | 0% | 2996 | -62
[5 empty] | 2019-03-21 | 37 | 1914.5 | 2984 | -62 | 1 | 0 | 3046 | 2650.7832 | 2650.7832 | 2650.7832 | 2088.4584 | 780 | 200 | 3068.4584 | 76.71% | 95% | 0% | -70.9382 | 2579.845 | -3550 | -400 | -1370.155 | 34.25% | 76.66% | 95% | 0% | 3046 | -62
[5 empty] | 2019-03-21 | 38 | 1915 | 3045 | -68 | 1 | 0 | 3113 | 2755.7296 | 2755.7296 | 2755.7296 | 2088.4584 | 780 | 200 | 3068.4584 | 76.71% | 95% | 0% | -77.8032 | 2677.9264 | -3550 | -400 | -1272.0736 | 31.8% | 76.64% | 95% | 0% | 3113 | -68
[5 empty] | 2019-03-21 | 39 | 1915.5 | 3003 | -73 | 1 | 0 | 3076 | 2697.7741 | 2697.7741 | 2697.7741 | 2088.4584 | 780 | 200 | 3068.4584 | 76.71% | 95% | 0% | -83.524 | 2614.2501 | -3550 | -400 | -1335.7499 | 33.39% | 76.64% | 95% | 0% | 3076 | -73
[5 empty] | 2019-03-21 | 40 | 1916 | 2944 | -79 | 0 | 0 | 3023 | 2614.7568 | 2614.7568 | 2614.7568 | 2086.892 | 780 | 200 | 3066.892 | 76.67% | 95% | 0% | -90.389 | 2524.3678 | -2750 | -200 | -425.6322 | 10.64% | 76.64% | 95% | 0% | 3023 | -79
[5 empty] | 2019-03-21 | 41 | 1916.5 | 2854 | -84 | 0 | 0 | 2938 | 2481.6158 | 2481.6158 | 2481.6158 | 2086.892 | 780 | 200 | 3066.892 | 76.67% | 95% | 0% | -96.1098 | 2385.506 | -2750 | -200 | -564.494 | 14.11% | 76.63% | 95% | 0% | 2938 | -84
[5 empty] | 2019-03-21 | 42 | 1917 | 2730 | -89 | 0 | 0 | 2819 | 2295.2185 | 2295.2185 | 2295.2185 | 2086.892 | 780 | 200 | 3066.892 | 76.67% | 95% | 0% | -101.8307 | 2193.3878 | -2750 | -200 | -756.6122 | 18.92% | 76.63% | 95% | 0% | 2819 | -89
[5 empty] | 2019-03-21 | 43 | 1917.5 | 2574 | -93 | 0 | 0 | 2667 | 2057.1311 | 2057.1311 | 2057.1311 | 2086.892 | 780 | 200 | 3066.892 | 76.67% | 95% | 0% | -106.4073 | 1950.7238 | -2750 | -200 | -999.2762 | 24.98% | 76.63% | 95% | 0% | 2667 | -93
[5 empty] | 2019-03-21 | 44 | 1918 | 2433 | -98 | 0 | 0 | 2531 | 1844.1055 | 1844.1055 | 1844.1055 | 2086.892 | 780 | 200 | 3066.892 | 76.67% | 95% | 0% | -112.1281 | 1731.9774 | -2750 | -200 | -1218.0226 | 30.45% | 76.62% | 95% | 0% | 2531 | -98
[5 empty] | 2019-03-21 | 45 | 1918.5 | 2258 | -103 | 0 | 0 | 2361 | 1577.8236 | 1577.8236 | 1577.8236 | 2086.892 | 780 | 200 | 3066.892 | 76.67% | 95% | 0% | -117.849 | 1459.9746 | -2750 | -200 | -1490.0254 | 37.25% | 76.62% | 95% | 0% | 2361 | -103
[5 empty] | 2019-03-21 | 46 | 1919 | 2120 | -108 | 0 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 2086.892 | 780 | 200 | 3066.892 | 76.67% | 95% | 0% | -123.5698 | 1245.9273 | -2750 | -200 | -1704.0727 | 42.6% | 76.62% | 95% | 0% | 2228 | -108
[5 empty] | 2019-03-21 | 47 | 1919.5 | 1976 | -112 | 0 | 0 | 2088 | 1150.2061 | 1150.2061 | 1150.2061 | 2086.892 | 780 | 200 | 3066.892 | 76.67% | 95% | 0% | -128.1465 | 1022.0596 | -2750 | -200 | -1927.9404 | 48.2% | 76.62% | 95% | 0% | 2088 | -112
[5 empty] | 2019-03-21 | 48 | 1920 | 1878 | -116 | 0 | 0 | 1994 | 1002.9678 | 1002.9678 | 1002.9678 | 2086.892 | 780 | 200 | 3066.892 | 76.67% | 95% | 0% | -132.7231 | 870.2447 | -2750 | -200 | -2079.7553 | 51.99% | 76.6% | 95% | 0% | 1994 | -116
[5 empty] | 2019-03-22 | 1 | 1920.5 | 1845 | -120 | 0 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 2086.892 | 780 | 200 | 3066.892 | 76.67% | 95% | 0% | -137.2998 | 820.2435 | -2750 | -200 | -2129.7565 | 53.24% | 76.6% | 95% | 0% | 1965 | -120
[5 empty] | 2019-03-22 | 2 | 1921 | 1837 | -125 | 0 | 0 | 1962 | 952.8442 | 952.8442 | 952.8442 | 2085.3256 | 780 | 200 | 3065.3256 | 76.63% | 95% | 0% | -143.0206 | 809.8236 | -2750 | -200 | -2140.1764 | 53.5% | 76.6% | 95% | 0% | 1962 | -125
[5 empty] | 2019-03-22 | 3 | 1921.5 | 1792 | -130 | 0 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 2085.3256 | 780 | 200 | 3065.3256 | 76.63% | 95% | 0% | -148.7414 | 741.4482 | -2750 | -200 | -2208.5518 | 55.21% | 76.6% | 95% | 0% | 1922 | -130
[5 empty] | 2019-03-22 | 4 | 1922 | 1726 | -135 | 0 | 0 | 1861 | 794.6414 | 794.6414 | 794.6414 | 2085.3256 | 780 | 200 | 3065.3256 | 76.63% | 95% | 0% | -154.4622 | 640.1791 | -2750 | -200 | -2309.8209 | 57.75% | 76.6% | 95% | 0% | 1861 | -135
[5 empty] | 2019-03-22 | 5 | 1922.5 | 1675 | -138 | 0 | 0 | 1813 | 719.4559 | 719.4559 | 719.4559 | 2085.3256 | 780 | 200 | 3065.3256 | 76.63% | 95% | 0% | -157.8947 | 561.5612 | -2750 | -200 | -2388.4388 | 59.71% | 76.6% | 95% | 0% | 1813 | -138
[5 empty] | 2019-03-22 | 6 | 1923 | 1645 | -142 | 0 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 2085.3256 | 780 | 200 | 3065.3256 | 76.63% | 95% | 0% | -162.4714 | 516.259 | -2750 | -200 | -2433.741 | 60.84% | 76.59% | 95% | 0% | 1787 | -142
[5 empty] | 2019-03-22 | 7 | 1923.5 | 1600 | -145 | 0 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 2085.3256 | 780 | 200 | 3065.3256 | 76.63% | 95% | 0% | -165.9039 | 447.0392 | -2750 | -200 | -2502.9608 | 62.57% | 76.59% | 95% | 0% | 1745 | -145
[5 empty] | 2019-03-22 | 8 | 1924 | 1574 | -147 | 0 | 0 | 1721 | 575.3504 | 575.3504 | 575.3504 | 2083.7593 | 780 | 200 | 3063.7593 | 76.59% | 95% | 0% | -168.1922 | 407.1582 | -2750 | -200 | -2542.8418 | 63.57% | 76.59% | 95% | 0% | 1721 | -147
[5 empty] | 2019-03-22 | 9 | 1924.5 | 1564 | -149 | 0 | 0 | 1713 | 562.8195 | 562.8195 | 562.8195 | 2083.7593 | 780 | 200 | 3063.7593 | 76.59% | 95% | 0% | -170.4805 | 392.3389 | -2750 | -200 | -2557.6611 | 63.94% | 76.59% | 95% | 0% | 1713 | -149
[5 empty] | 2019-03-22 | 10 | 1925 | 1577 | -152 | 0 | 0 | 1729 | 587.8813 | 587.8813 | 587.8813 | 2083.7593 | 780 | 200 | 3063.7593 | 76.59% | 95% | 0% | -173.913 | 413.9682 | -2750 | -200 | -2536.0318 | 63.4% | 76.58% | 95% | 0% | 1729 | -152
[5 empty] | 2019-03-22 | 11 | 1925.5 | 1638 | -154 | 0 | 0 | 1792 | 686.5622 | 686.5622 | 686.5622 | 2083.7593 | 780 | 200 | 3063.7593 | 76.59% | 95% | 0% | -176.2014 | 510.3609 | -2750 | -200 | -2439.6391 | 60.99% | 76.58% | 95% | 0% | 1792 | -154
[5 empty] | 2019-03-22 | 12 | 1926 | 1736 | -157 | 0 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 2083.7593 | 780 | 200 | 3063.7593 | 76.59% | 95% | 0% | -179.6339 | 665.1312 | -2750 | -200 | -2284.8688 | 57.12% | 76.58% | 95% | 0% | 1893 | -157
[5 empty] | 2019-03-22 | 13 | 1926.5 | 1926 | -158 | 0 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 2083.7593 | 780 | 200 | 3063.7593 | 76.59% | 95% | 0% | -180.778 | 963.1626 | -2750 | -200 | -1986.8374 | 49.67% | 76.57% | 95% | 0% | 2084 | -158
[5 empty] | 2019-03-22 | 14 | 1927 | 2122 | -163 | 0 | 0 | 2285 | 1458.7799 | 1458.7799 | 1458.7799 | 2082.1929 | 780 | 200 | 3062.1929 | 76.55% | 95% | 0% | -186.4989 | 1272.281 | -2750 | -200 | -1677.719 | 41.94% | 76.57% | 95% | 0% | 2285 | -163
[5 empty] | 2019-03-22 | 15 | 1927.5 | 2336 | -178 | 1 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 2082.1929 | 780 | 200 | 3062.1929 | 76.55% | 95% | 0% | -203.6613 | 1613.816 | -3550 | -400 | -2336.184 | 58.4% | 76.56% | 95% | 0% | 2514 | -178
[5 empty] | 2019-03-22 | 16 | 1928 | 2413 | -201 | 1 | 0 | 2614 | 1974.1138 | 1974.1138 | 1974.1138 | 2082.1929 | 780 | 200 | 3062.1929 | 76.55% | 95% | 0% | -229.9771 | 1744.1367 | -3550 | -400 | -2205.8633 | 55.15% | 76.55% | 95% | 0% | 2614 | -201
[5 empty] | 2019-03-22 | 17 | 1928.5 | 2461 | -223 | 1 | 0 | 2684 | 2083.7593 | 2083.7593 | 2083.7593 | 2082.1929 | 780 | 200 | 3062.1929 | 76.55% | 95% | 0% | -255.1487 | 1828.6105 | -3550 | -400 | -2121.3895 | 53.03% | 76.55% | 95% | 0% | 2684 | -223
[5 empty] | 2019-03-22 | 18 | 1929 | 2432 | -246 | 1 | 0 | 2678 | 2074.3611 | 2074.3611 | 2074.3611 | 2082.1929 | 780 | 200 | 3062.1929 | 76.55% | 95% | 0% | -281.4645 | 1792.8966 | -3550 | -400 | -2157.1034 | 53.93% | 76.55% | 95% | 0% | 2678 | -246
[5 empty] | 2019-03-22 | 19 | 1929.5 | 2420 | -269 | 1 | 0 | 2689 | 2091.5911 | 2091.5911 | 2091.5911 | 2082.1929 | 780 | 200 | 3062.1929 | 76.55% | 95% | 0% | -307.7803 | 1783.8108 | -3550 | -400 | -2166.1892 | 54.15% | 76.54% | 95% | 0% | 2689 | -269
[5 empty] | 2019-03-22 | 20 | 1930 | 2398 | -292 | 1 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 2082.1929 | 780 | 200 | 3062.1929 | 76.55% | 95% | 0% | -334.0961 | 1759.0614 | -3550 | -400 | -2190.9386 | 54.77% | 76.54% | 95% | 0% | 2690 | -292
[5 empty] | 2019-03-22 | 21 | 1930.5 | 2351 | -312 | 1 | 0 | 2663 | 2050.8656 | 2050.8656 | 2050.8656 | 2080.6265 | 780 | 200 | 3060.6265 | 76.52% | 95% | 0% | -356.9794 | 1693.8862 | -3550 | -400 | -2256.1138 | 56.4% | 76.54% | 95% | 0% | 2663 | -312
[5 empty] | 2019-03-22 | 22 | 1931 | 2317 | -349 | 1 | 0 | 2666 | 2055.5647 | 2055.5647 | 2055.5647 | 2080.6265 | 780 | 200 | 3060.6265 | 76.52% | 95% | 0% | -399.3135 | 1656.2512 | -3550 | -400 | -2293.7488 | 57.34% | 76.54% | 95% | 0% | 2666 | -349
[5 empty] | 2019-03-22 | 23 | 1931.5 | 2286 | -374 | 1 | 0 | 2660 | 2046.1665 | 2046.1665 | 2046.1665 | 2080.6265 | 780 | 200 | 3060.6265 | 76.52% | 95% | 0% | -427.9176 | 1618.2489 | -3550 | -400 | -2331.7511 | 58.29% | 76.54% | 95% | 0% | 2660 | -374
[5 empty] | 2019-03-22 | 24 | 1932 | 2292 | -373 | 1 | 0 | 2665 | 2053.9984 | 2053.9984 | 2053.9984 | 2080.6265 | 780 | 200 | 3060.6265 | 76.52% | 95% | 0% | -426.7735 | 1627.2249 | -3550 | -400 | -2322.7751 | 58.07% | 76.53% | 95% | 0% | 2665 | -373
[5 empty] | 2019-03-22 | 25 | 1932.5 | 2267 | -382 | 1 | 0 | 2649 | 2028.9365 | 2028.9365 | 2028.9365 | 2079.0602 | 780 | 200 | 3059.0602 | 76.48% | 95% | 0% | -437.0709 | 1591.8656 | -3550 | -400 | -2358.1344 | 58.95% | 76.53% | 95% | 0% | 2649 | -382
[5 empty] | 2019-03-22 | 26 | 1933 | 2250 | -366 | 1 | 0 | 2616 | 1977.2465 | 1977.2465 | 1977.2465 | 2079.0602 | 780 | 200 | 3059.0602 | 76.48% | 95% | 0% | -418.7643 | 1558.4822 | -3550 | -400 | -2391.5178 | 59.79% | 76.52% | 95% | 0% | 2616 | -366
[5 empty] | 2019-03-22 | 27 | 1933.5 | 2227 | -364 | 1 | 0 | 2591 | 1938.0874 | 1938.0874 | 1938.0874 | 2079.0602 | 780 | 200 | 3059.0602 | 76.48% | 95% | 0% | -416.476 | 1521.6114 | -3550 | -400 | -2428.3886 | 60.71% | 76.52% | 95% | 0% | 2591 | -364
[5 empty] | 2019-03-22 | 28 | 1934 | 2222 | -343 | 1 | 0 | 2565 | 1897.3619 | 1897.3619 | 1897.3619 | 2079.0602 | 780 | 200 | 3059.0602 | 76.48% | 95% | 0% | -392.4485 | 1504.9134 | -3550 | -400 | -2445.0866 | 61.13% | 76.52% | 95% | 0% | 2565 | -343
[5 empty] | 2019-03-22 | 29 | 1934.5 | 2230 | -341 | 1 | 0 | 2571 | 1906.7601 | 1906.7601 | 1906.7601 | 2079.0602 | 780 | 200 | 3059.0602 | 76.48% | 95% | 0% | -390.1602 | 1516.5999 | -3550 | -400 | -2433.4001 | 60.84% | 76.52% | 95% | 0% | 2571 | -341
[5 empty] | 2019-03-22 | 30 | 1935 | 2243 | -317 | 1 | 0 | 2560 | 1889.5301 | 1889.5301 | 1889.5301 | 2079.0602 | 780 | 200 | 3059.0602 | 76.48% | 95% | 0% | -362.7002 | 1526.8299 | -3550 | -400 | -2423.1701 | 60.58% | 76.51% | 95% | 0% | 2560 | -317
[5 empty] | 2019-03-22 | 31 | 1935.5 | 2265 | -284 | 1 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 2077.4938 | 780 | 200 | 3057.4938 | 76.44% | 95% | 0% | -324.9428 | 1547.3573 | -3550 | -400 | -2402.6427 | 60.07% | 76.5% | 95% | 0% | 2549 | -284
[5 empty] | 2019-03-22 | 32 | 1936 | 2352 | -254 | 1 | 0 | 2606 | 1961.5829 | 1961.5829 | 1961.5829 | 2077.4938 | 780 | 200 | 3057.4938 | 76.44% | 95% | 0% | -290.6178 | 1670.965 | -3550 | -400 | -2279.035 | 56.98% | 76.5% | 95% | 0% | 2606 | -254
[5 empty] | 2019-03-22 | 33 | 1936.5 | 2452 | -223 | 1 | 0 | 2675 | 2069.662 | 2069.662 | 2069.662 | 2077.4938 | 780 | 200 | 3057.4938 | 76.44% | 95% | 0% | -255.1487 | 1814.5133 | -3550 | -400 | -2135.4867 | 53.39% | 76.5% | 95% | 0% | 2675 | -223
[5 empty] | 2019-03-22 | 34 | 1937 | 2571 | -197 | 1 | 0 | 2768 | 2215.3339 | 2215.3339 | 2215.3339 | 2077.4938 | 780 | 200 | 3057.4938 | 76.44% | 95% | 0% | -225.4005 | 1989.9334 | -3550 | -400 | -1960.0666 | 49% | 76.49% | 95% | 0% | 2768 | -197
[5 empty] | 2019-03-22 | 35 | 1937.5 | 2685 | -170 | 1 | 0 | 2855 | 2351.6076 | 2351.6076 | 2351.6076 | 2077.4938 | 780 | 200 | 3057.4938 | 76.44% | 95% | 0% | -194.508 | 2157.0996 | -3550 | -400 | -1792.9004 | 44.82% | 76.49% | 95% | 0% | 2855 | -170
[5 empty] | 2019-03-22 | 36 | 1938 | 2745 | -151 | 1 | 0 | 2896 | 2415.8285 | 2415.8285 | 2415.8285 | 2075.9275 | 780 | 200 | 3055.9275 | 76.4% | 95% | 0% | -172.7689 | 2243.0596 | -3550 | -400 | -1706.9404 | 42.67% | 76.49% | 95% | 0% | 2896 | -151
[5 empty] | 2019-03-22 | 37 | 1938.5 | 2788 | -144 | 1 | 0 | 2932 | 2472.2176 | 2472.2176 | 2472.2176 | 2075.9275 | 780 | 200 | 3055.9275 | 76.4% | 95% | 0% | -164.7597 | 2307.4579 | -3550 | -400 | -1642.5421 | 41.06% | 76.49% | 95% | 0% | 2932 | -144
[5 empty] | 2019-03-22 | 38 | 1939 | 2812 | -140 | 1 | 0 | 2952 | 2503.5449 | 2503.5449 | 2503.5449 | 2075.9275 | 780 | 200 | 3055.9275 | 76.4% | 95% | 0% | -160.1831 | 2343.3619 | -3550 | -400 | -1606.6381 | 40.17% | 76.47% | 95% | 0% | 2952 | -140
[5 empty] | 2019-03-22 | 39 | 1939.5 | 2787 | -135 | 1 | 0 | 2922 | 2456.554 | 2456.554 | 2456.554 | 2075.9275 | 780 | 200 | 3055.9275 | 76.4% | 95% | 0% | -154.4622 | 2302.0918 | -3550 | -400 | -1647.9082 | 41.2% | 76.47% | 95% | 0% | 2922 | -135
[5 empty] | 2019-03-22 | 40 | 1940 | 2737 | -130 | 0 | 0 | 2867 | 2370.404 | 2370.404 | 2370.404 | 2075.9275 | 780 | 200 | 3055.9275 | 76.4% | 95% | 0% | -148.7414 | 2221.6625 | -2750 | -200 | -728.3375 | 18.21% | 76.46% | 95% | 0% | 2867 | -130
[5 empty] | 2019-03-22 | 41 | 1940.5 | 2656 | -128 | 0 | 0 | 2784 | 2240.3957 | 2240.3957 | 2240.3957 | 2074.3611 | 780 | 200 | 3054.3611 | 76.36% | 95% | 0% | -146.4531 | 2093.9426 | -2750 | -200 | -856.0574 | 21.4% | 76.46% | 95% | 0% | 2784 | -128
[5 empty] | 2019-03-22 | 42 | 1941 | 2563 | -125 | 0 | 0 | 2688 | 2090.0247 | 2090.0247 | 2090.0247 | 2074.3611 | 780 | 200 | 3054.3611 | 76.36% | 95% | 0% | -143.0206 | 1947.0041 | -2750 | -200 | -1002.9959 | 25.07% | 76.45% | 95% | 0% | 2688 | -125
[5 empty] | 2019-03-22 | 43 | 1941.5 | 2447 | -124 | 0 | 0 | 2571 | 1906.7601 | 1906.7601 | 1906.7601 | 2074.3611 | 780 | 200 | 3054.3611 | 76.36% | 95% | 0% | -141.8764 | 1764.8837 | -2750 | -200 | -1185.1163 | 29.63% | 76.45% | 95% | 0% | 2571 | -124
[5 empty] | 2019-03-22 | 44 | 1942 | 2324 | -123 | 0 | 0 | 2447 | 1712.5309 | 1712.5309 | 1712.5309 | 2074.3611 | 780 | 200 | 3054.3611 | 76.36% | 95% | 0% | -140.7323 | 1571.7986 | -2750 | -200 | -1378.2014 | 34.46% | 76.44% | 95% | 0% | 2447 | -123
[5 empty] | 2019-03-22 | 45 | 1942.5 | 2182 | -121 | 0 | 0 | 2303 | 1486.9744 | 1486.9744 | 1486.9744 | 2074.3611 | 780 | 200 | 3054.3611 | 76.36% | 95% | 0% | -138.4439 | 1348.5305 | -2750 | -200 | -1601.4695 | 40.04% | 76.43% | 95% | 0% | 2303 | -121
[5 empty] | 2019-03-22 | 46 | 1943 | 2085 | -120 | 0 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 2074.3611 | 780 | 200 | 3054.3611 | 76.36% | 95% | 0% | -137.2998 | 1196.171 | -2750 | -200 | -1753.829 | 43.85% | 76.42% | 95% | 0% | 2205 | -120
[5 empty] | 2019-03-22 | 47 | 1943.5 | 1963 | -121 | 0 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 2074.3611 | 780 | 200 | 3054.3611 | 76.36% | 95% | 0% | -138.4439 | 1005.4967 | -2750 | -200 | -1944.5033 | 48.61% | 76.42% | 95% | 0% | 2084 | -121
[5 empty] | 2019-03-22 | 48 | 1944 | 1871 | -122 | 0 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 2074.3611 | 780 | 200 | 3054.3611 | 76.36% | 95% | 0% | -139.5881 | 861.8134 | -2750 | -200 | -2088.1866 | 52.2% | 76.41% | 95% | 0% | 1993 | -122
[5 empty] | 2019-03-23 | 1 | 1944.5 | 1852 | -120 | 0 | 0 | 1972 | 968.5078 | 968.5078 | 968.5078 | 2074.3611 | 780 | 200 | 3054.3611 | 76.36% | 95% | 0% | -137.2998 | 831.2081 | -2750 | -200 | -2118.7919 | 52.97% | 76.4% | 95% | 0% | 1972 | -120
[5 empty] | 2019-03-23 | 2 | 1945 | 1862 | -119 | 0 | 0 | 1981 | 982.6051 | 982.6051 | 982.6051 | 2074.3611 | 780 | 200 | 3054.3611 | 76.36% | 95% | 0% | -136.1556 | 846.4495 | -2750 | -200 | -2103.5505 | 52.59% | 76.39% | 95% | 0% | 1981 | -119
[5 empty] | 2019-03-23 | 3 | 1945.5 | 1822 | -118 | 0 | 0 | 1940 | 918.3842 | 918.3842 | 918.3842 | 2074.3611 | 780 | 200 | 3054.3611 | 76.36% | 95% | 0% | -135.0114 | 783.3727 | -2750 | -200 | -2166.6273 | 54.17% | 76.39% | 95% | 0% | 1940 | -118
[5 empty] | 2019-03-23 | 4 | 1946 | 1765 | -117 | 0 | 0 | 1882 | 827.535 | 827.535 | 827.535 | 2074.3611 | 780 | 200 | 3054.3611 | 76.36% | 95% | 0% | -133.8673 | 693.6678 | -2750 | -200 | -2256.3322 | 56.41% | 76.38% | 95% | 0% | 1882 | -117
[5 empty] | 2019-03-23 | 5 | 1946.5 | 1714 | -117 | 0 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 2072.7947 | 780 | 200 | 3052.7947 | 76.32% | 95% | 0% | -133.8673 | 613.7832 | -2750 | -200 | -2336.2168 | 58.41% | 76.38% | 95% | 0% | 1831 | -117
[5 empty] | 2019-03-23 | 6 | 1947 | 1684 | -116 | 0 | 0 | 1800 | 699.0932 | 699.0932 | 699.0932 | 2072.7947 | 780 | 200 | 3052.7947 | 76.32% | 95% | 0% | -132.7231 | 566.37 | -2750 | -200 | -2383.63 | 59.59% | 76.38% | 95% | 0% | 1800 | -116
[5 empty] | 2019-03-23 | 7 | 1947.5 | 1658 | -113 | 0 | 0 | 1771 | 653.6686 | 653.6686 | 653.6686 | 2072.7947 | 780 | 200 | 3052.7947 | 76.32% | 95% | 0% | -129.2906 | 524.378 | -2750 | -200 | -2425.622 | 60.64% | 76.36% | 95% | 0% | 1771 | -113
[5 empty] | 2019-03-23 | 8 | 1948 | 1633 | -110 | 0 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 2071.2284 | 780 | 200 | 3051.2284 | 76.28% | 95% | 0% | -125.8581 | 483.9523 | -2750 | -200 | -2466.0477 | 61.65% | 76.36% | 95% | 0% | 1743 | -110
[5 empty] | 2019-03-23 | 9 | 1948.5 | 1619 | -109 | 0 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 2071.2284 | 780 | 200 | 3051.2284 | 76.28% | 95% | 0% | -124.714 | 461.601 | -2750 | -200 | -2488.399 | 62.21% | 76.35% | 95% | 0% | 1728 | -109
[5 empty] | 2019-03-23 | 10 | 1949 | 1612 | -108 | 0 | 0 | 1720 | 573.784 | 573.784 | 573.784 | 2071.2284 | 780 | 200 | 3051.2284 | 76.28% | 95% | 0% | -123.5698 | 450.2142 | -2750 | -200 | -2499.7858 | 62.49% | 76.35% | 95% | 0% | 1720 | -108
[5 empty] | 2019-03-23 | 11 | 1949.5 | 1628 | -107 | 0 | 0 | 1735 | 597.2795 | 597.2795 | 597.2795 | 2071.2284 | 780 | 200 | 3051.2284 | 76.28% | 95% | 0% | -122.4256 | 474.8538 | -2750 | -200 | -2475.1462 | 61.88% | 76.35% | 95% | 0% | 1735 | -107
[5 empty] | 2019-03-23 | 12 | 1950 | 1683 | -106 | 0 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 2071.2284 | 780 | 200 | 3051.2284 | 76.28% | 95% | 0% | -121.2815 | 560.5817 | -2750 | -200 | -2389.4183 | 59.74% | 76.34% | 95% | 0% | 1789 | -106
[5 empty] | 2019-03-23 | 13 | 1950.5 | 1774 | -105 | 0 | 0 | 1879 | 822.8359 | 822.8359 | 822.8359 | 2071.2284 | 780 | 200 | 3051.2284 | 76.28% | 95% | 0% | -120.1373 | 702.6986 | -2750 | -200 | -2247.3014 | 56.18% | 76.33% | 95% | 0% | 1879 | -105
[5 empty] | 2019-03-23 | 14 | 1951 | 1849 | -118 | 0 | 0 | 1967 | 960.676 | 960.676 | 960.676 | 2071.2284 | 780 | 200 | 3051.2284 | 76.28% | 95% | 0% | -135.0114 | 825.6646 | -2750 | -200 | -2124.3354 | 53.11% | 76.32% | 95% | 0% | 1967 | -118
[5 empty] | 2019-03-23 | 15 | 1951.5 | 1946 | -148 | 0 | 0 | 2094 | 1159.6043 | 1159.6043 | 1159.6043 | 2071.2284 | 780 | 200 | 3051.2284 | 76.28% | 95% | 0% | -169.3364 | 990.2679 | -2750 | -200 | -1959.7321 | 48.99% | 76.32% | 95% | 0% | 2094 | -148
[5 empty] | 2019-03-23 | 16 | 1952 | 1972 | -190 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 2071.2284 | 780 | 200 | 3051.2284 | 76.28% | 95% | 0% | -217.3913 | 1048.7258 | -3550 | -400 | -2901.2742 | 72.53% | 76.32% | 95% | 0% | 2162 | -190
[5 empty] | 2019-03-23 | 17 | 1952.5 | 2001 | -251 | 1 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 2069.662 | 780 | 200 | 3049.662 | 76.24% | 95% | 0% | -287.1854 | 1119.9045 | -3550 | -400 | -2830.0955 | 70.75% | 76.31% | 95% | 0% | 2252 | -251
[5 empty] | 2019-03-23 | 18 | 1953 | 2032 | -283 | 1 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 2069.662 | 780 | 200 | 3049.662 | 76.24% | 95% | 0% | -323.7986 | 1181.9722 | -3550 | -400 | -2768.0278 | 69.2% | 76.3% | 95% | 0% | 2315 | -283
[5 empty] | 2019-03-23 | 19 | 1953.5 | 1980 | -340 | 1 | 0 | 2320 | 1513.6026 | 1513.6026 | 1513.6026 | 2069.662 | 780 | 200 | 3049.662 | 76.24% | 95% | 0% | -389.016 | 1124.5866 | -3550 | -400 | -2825.4134 | 70.64% | 76.3% | 95% | 0% | 2320 | -340
[5 empty] | 2019-03-23 | 20 | 1954 | 1871 | -417 | 1 | 0 | 2288 | 1463.479 | 1463.479 | 1463.479 | 2069.662 | 780 | 200 | 3049.662 | 76.24% | 95% | 0% | -477.1167 | 986.3623 | -3550 | -400 | -2963.6377 | 74.09% | 76.28% | 95% | 0% | 2288 | -417
[5 empty] | 2019-03-23 | 21 | 1954.5 | 1819 | -453 | 1 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 2069.662 | 780 | 200 | 3049.662 | 76.24% | 95% | 0% | -518.3066 | 920.1105 | -3550 | -400 | -3029.8895 | 75.75% | 76.27% | 95% | 0% | 2272 | -453
[5 empty] | 2019-03-23 | 22 | 1955 | 1810 | -445 | 1 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 2069.662 | 780 | 200 | 3049.662 | 76.24% | 95% | 0% | -509.1533 | 902.6356 | -3550 | -400 | -3047.3644 | 76.18% | 76.26% | 95% | 0% | 2255 | -445
[5 empty] | 2019-03-23 | 23 | 1955.5 | 1773 | -464 | 1 | 0 | 2237 | 1383.5944 | 1383.5944 | 1383.5944 | 2068.0956 | 780 | 200 | 3048.0956 | 76.2% | 95% | 0% | -530.8924 | 852.7019 | -3550 | -400 | -3097.2981 | 77.43% | 76.24% | 95% | 0% | 2237 | -464
[5 empty] | 2019-03-23 | 24 | 1956 | 1765 | -462 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 2068.0956 | 780 | 200 | 3048.0956 | 76.2% | 95% | 0% | -528.6041 | 839.3266 | -3550 | -400 | -3110.6734 | 77.77% | 76.24% | 95% | 0% | 2227 | -462
[5 empty] | 2019-03-23 | 25 | 1956.5 | 1740 | -470 | 1 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 2068.0956 | 780 | 200 | 3048.0956 | 76.2% | 95% | 0% | -537.7574 | 803.5451 | -3550 | -400 | -3146.4549 | 78.66% | 76.24% | 95% | 0% | 2210 | -470
[5 empty] | 2019-03-23 | 26 | 1957 | 1744 | -458 | 1 | 0 | 2202 | 1328.7716 | 1328.7716 | 1328.7716 | 2068.0956 | 780 | 200 | 3048.0956 | 76.2% | 95% | 0% | -524.0275 | 804.7442 | -3550 | -400 | -3145.2558 | 78.63% | 76.22% | 95% | 0% | 2202 | -458
[5 empty] | 2019-03-23 | 27 | 1957.5 | 1736 | -452 | 1 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 2068.0956 | 780 | 200 | 3048.0956 | 76.2% | 95% | 0% | -517.1625 | 789.6801 | -3550 | -400 | -3160.3199 | 79.01% | 76.21% | 95% | 0% | 2188 | -452
[5 empty] | 2019-03-23 | 28 | 1958 | 1727 | -448 | 1 | 0 | 2175 | 1286.4798 | 1286.4798 | 1286.4798 | 2068.0956 | 780 | 200 | 3048.0956 | 76.2% | 95% | 0% | -512.5858 | 773.894 | -3550 | -400 | -3176.106 | 79.4% | 76.21% | 95% | 0% | 2175 | -448
[5 empty] | 2019-03-23 | 29 | 1958.5 | 1727 | -438 | 1 | 0 | 2165 | 1270.8162 | 1270.8162 | 1270.8162 | 2068.0956 | 780 | 200 | 3048.0956 | 76.2% | 95% | 0% | -501.1442 | 769.672 | -3550 | -400 | -3180.328 | 79.51% | 76.21% | 95% | 0% | 2165 | -438
[5 empty] | 2019-03-23 | 30 | 1959 | 1792 | -392 | 1 | 0 | 2184 | 1300.5771 | 1300.5771 | 1300.5771 | 2068.0956 | 780 | 200 | 3048.0956 | 76.2% | 95% | 0% | -448.5126 | 852.0645 | -3550 | -400 | -3097.9355 | 77.45% | 76.2% | 95% | 0% | 2184 | -392
[5 empty] | 2019-03-23 | 31 | 1959.5 | 1906 | -321 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 2068.0956 | 780 | 200 | 3048.0956 | 76.2% | 95% | 0% | -367.2769 | 1000.6539 | -3550 | -400 | -2949.3461 | 73.73% | 76.2% | 95% | 0% | 2227 | -321
[5 empty] | 2019-03-23 | 32 | 1960 | 2009 | -275 | 1 | 0 | 2284 | 1457.2135 | 1457.2135 | 1457.2135 | 2066.5293 | 780 | 200 | 3046.5293 | 76.16% | 95% | 0% | -314.6453 | 1142.5682 | -3550 | -400 | -2807.4318 | 70.19% | 76.18% | 95% | 0% | 2284 | -275
[5 empty] | 2019-03-23 | 33 | 1960.5 | 2143 | -222 | 1 | 0 | 2365 | 1584.089 | 1584.089 | 1584.089 | 2066.5293 | 780 | 200 | 3046.5293 | 76.16% | 95% | 0% | -254.0046 | 1330.0845 | -3550 | -400 | -2619.9155 | 65.5% | 76.18% | 95% | 0% | 2365 | -222
[5 empty] | 2019-03-23 | 34 | 1961 | 2307 | -171 | 1 | 0 | 2478 | 1761.0882 | 1761.0882 | 1761.0882 | 2066.5293 | 780 | 200 | 3046.5293 | 76.16% | 95% | 0% | -195.6522 | 1565.436 | -3550 | -400 | -2384.564 | 59.61% | 76.18% | 95% | 0% | 2478 | -171
[5 empty] | 2019-03-23 | 35 | 1961.5 | 2489 | -118 | 1 | 0 | 2607 | 1963.1492 | 1963.1492 | 1963.1492 | 2066.5293 | 780 | 200 | 3046.5293 | 76.16% | 95% | 0% | -135.0114 | 1828.1378 | -3550 | -400 | -2121.8622 | 53.05% | 76.18% | 95% | 0% | 2607 | -118
[5 empty] | 2019-03-23 | 36 | 1962 | 2605 | -81 | 1 | 0 | 2686 | 2086.892 | 2086.892 | 2086.892 | 2066.5293 | 780 | 200 | 3046.5293 | 76.16% | 95% | 0% | -92.6773 | 1994.2147 | -3550 | -400 | -1955.7853 | 48.89% | 76.17% | 95% | 0% | 2686 | -81
[5 empty] | 2019-03-23 | 37 | 1962.5 | 2681 | -66 | 1 | 0 | 2747 | 2182.4402 | 2182.4402 | 2182.4402 | 2066.5293 | 780 | 200 | 3046.5293 | 76.16% | 95% | 0% | -75.5149 | 2106.9254 | -3550 | -400 | -1843.0746 | 46.08% | 76.16% | 95% | 0% | 2747 | -66
[5 empty] | 2019-03-23 | 38 | 1963 | 2743 | -66 | 1 | 0 | 2809 | 2279.5548 | 2279.5548 | 2279.5548 | 2066.5293 | 780 | 200 | 3046.5293 | 76.16% | 95% | 0% | -75.5149 | 2204.0399 | -3550 | -400 | -1745.9601 | 43.65% | 76.16% | 95% | 0% | 2809 | -66
[5 empty] | 2019-03-23 | 39 | 1963.5 | 2727 | -67 | 1 | 0 | 2794 | 2256.0594 | 2256.0594 | 2256.0594 | 2066.5293 | 780 | 200 | 3046.5293 | 76.16% | 95% | 0% | -76.659 | 2179.4003 | -3550 | -400 | -1770.5997 | 44.26% | 76.14% | 95% | 0% | 2794 | -67
[5 empty] | 2019-03-23 | 40 | 1964 | 2649 | -67 | 0 | 0 | 2716 | 2133.8829 | 2133.8829 | 2133.8829 | 2064.9629 | 780 | 200 | 3044.9629 | 76.12% | 95% | 0% | -76.659 | 2057.2239 | -2750 | -200 | -892.7761 | 22.32% | 76.14% | 95% | 0% | 2716 | -67
[5 empty] | 2019-03-23 | 41 | 1964.5 | 2603 | -67 | 0 | 0 | 2670 | 2061.8302 | 2061.8302 | 2061.8302 | 2064.9629 | 780 | 200 | 3044.9629 | 76.12% | 95% | 0% | -76.659 | 1985.1711 | -2750 | -200 | -964.8289 | 24.12% | 76.14% | 95% | 0% | 2670 | -67
[5 empty] | 2019-03-23 | 42 | 1965 | 2540 | -68 | 0 | 0 | 2608 | 1964.7156 | 1964.7156 | 1964.7156 | 2064.9629 | 780 | 200 | 3044.9629 | 76.12% | 95% | 0% | -77.8032 | 1886.9124 | -2750 | -200 | -1063.0876 | 26.58% | 76.13% | 95% | 0% | 2608 | -68
[5 empty] | 2019-03-23 | 43 | 1965.5 | 2436 | -67 | 0 | 0 | 2503 | 1800.2473 | 1800.2473 | 1800.2473 | 2064.9629 | 780 | 200 | 3044.9629 | 76.12% | 95% | 0% | -76.659 | 1723.5883 | -2750 | -200 | -1226.4117 | 30.66% | 76.13% | 95% | 0% | 2503 | -67
[5 empty] | 2019-03-23 | 44 | 1966 | 2326 | -67 | 0 | 0 | 2393 | 1627.9472 | 1627.9472 | 1627.9472 | 2064.9629 | 780 | 200 | 3044.9629 | 76.12% | 95% | 0% | -76.659 | 1551.2882 | -2750 | -200 | -1398.7118 | 34.97% | 76.13% | 95% | 0% | 2393 | -67
[5 empty] | 2019-03-23 | 45 | 1966.5 | 2226 | -68 | 0 | 0 | 2294 | 1472.8772 | 1472.8772 | 1472.8772 | 2064.9629 | 780 | 200 | 3044.9629 | 76.12% | 95% | 0% | -77.8032 | 1395.074 | -2750 | -200 | -1554.926 | 38.87% | 76.13% | 95% | 0% | 2294 | -68
[5 empty] | 2019-03-23 | 46 | 1967 | 2131 | -68 | 0 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 2064.9629 | 780 | 200 | 3044.9629 | 76.12% | 95% | 0% | -77.8032 | 1246.2693 | -2750 | -200 | -1703.7307 | 42.59% | 76.11% | 95% | 0% | 2199 | -68
[5 empty] | 2019-03-23 | 47 | 1967.5 | 2023 | -68 | 0 | 0 | 2091 | 1154.9052 | 1154.9052 | 1154.9052 | 2063.3965 | 780 | 200 | 3043.3965 | 76.08% | 95% | 0% | -77.8032 | 1077.102 | -2750 | -200 | -1872.898 | 46.82% | 76.11% | 95% | 0% | 2091 | -68
[5 empty] | 2019-03-23 | 48 | 1968 | 1944 | -69 | 0 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 2063.3965 | 780 | 200 | 3043.3965 | 76.08% | 95% | 0% | -78.9474 | 953.7814 | -2750 | -200 | -1996.2186 | 49.91% | 76.11% | 95% | 0% | 2013 | -69
[5 empty] | 2019-03-24 | 1 | 1968.5 | 1910 | -71 | 0 | 0 | 1981 | 982.6051 | 982.6051 | 982.6051 | 2063.3965 | 780 | 200 | 3043.3965 | 76.08% | 95% | 0% | -81.2357 | 901.3694 | -2750 | -200 | -2048.6306 | 51.22% | 76.1% | 95% | 0% | 1981 | -71
[5 empty] | 2019-03-24 | 2 | 1969 | 1915 | -74 | 0 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 2063.3965 | 780 | 200 | 3043.3965 | 76.08% | 95% | 0% | -84.6682 | 910.4678 | -2750 | -200 | -2039.5322 | 50.99% | 76.09% | 95% | 0% | 1989 | -74
[5 empty] | 2019-03-24 | 3 | 1969.5 | 1874 | -76 | 0 | 0 | 1950 | 934.0478 | 934.0478 | 934.0478 | 2061.8302 | 780 | 200 | 3041.8302 | 76.05% | 95% | 0% | -86.9565 | 847.0913 | -2750 | -200 | -2102.9087 | 52.57% | 76.09% | 95% | 0% | 1950 | -76
[5 empty] | 2019-03-24 | 4 | 1970 | 1814 | -79 | 0 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 2061.8302 | 780 | 200 | 3041.8302 | 76.05% | 95% | 0% | -90.389 | 754.376 | -2750 | -200 | -2195.624 | 54.89% | 76.09% | 95% | 0% | 1893 | -79
[5 empty] | 2019-03-24 | 5 | 1970.5 | 1768 | -81 | 0 | 0 | 1849 | 775.845 | 775.845 | 775.845 | 2061.8302 | 780 | 200 | 3041.8302 | 76.05% | 95% | 0% | -92.6773 | 683.1677 | -2750 | -200 | -2266.8323 | 56.67% | 76.09% | 95% | 0% | 1849 | -81
[5 empty] | 2019-03-24 | 6 | 1971 | 1736 | -84 | 0 | 0 | 1820 | 730.4204 | 730.4204 | 730.4204 | 2060.2638 | 780 | 200 | 3040.2638 | 76.01% | 95% | 0% | -96.1098 | 634.3106 | -2750 | -200 | -2315.6894 | 57.89% | 76.09% | 95% | 0% | 1820 | -84
[5 empty] | 2019-03-24 | 7 | 1971.5 | 1689 | -87 | 0 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 2060.2638 | 780 | 200 | 3040.2638 | 76.01% | 95% | 0% | -99.5423 | 561.9581 | -2750 | -200 | -2388.0419 | 59.7% | 76.08% | 95% | 0% | 1776 | -87
[5 empty] | 2019-03-24 | 8 | 1972 | 1650 | -91 | 0 | 0 | 1741 | 606.6777 | 606.6777 | 606.6777 | 2060.2638 | 780 | 200 | 3040.2638 | 76.01% | 95% | 0% | -104.119 | 502.5587 | -2750 | -200 | -2447.4413 | 61.19% | 76.08% | 95% | 0% | 1741 | -91
[5 empty] | 2019-03-24 | 9 | 1972.5 | 1620 | -94 | 0 | 0 | 1714 | 564.3858 | 564.3858 | 564.3858 | 2060.2638 | 780 | 200 | 3040.2638 | 76.01% | 95% | 0% | -107.5515 | 456.8343 | -2750 | -200 | -2493.1657 | 62.33% | 76.06% | 95% | 0% | 1714 | -94
[5 empty] | 2019-03-24 | 10 | 1973 | 1595 | -97 | 1 | 0 | 1692 | 529.9258 | 529.9258 | 529.9258 | 2058.6974 | 780 | 200 | 3038.6974 | 75.97% | 95% | 0% | -110.984 | 418.9418 | -3550 | -400 | -3531.0582 | 88.28% | 76.06% | 95% | 0% | 1692 | -97
[5 empty] | 2019-03-24 | 11 | 1973.5 | 1610 | -101 | 1 | 0 | 1711 | 559.6867 | 559.6867 | 559.6867 | 2058.6974 | 780 | 200 | 3038.6974 | 75.97% | 95% | 0% | -115.5606 | 444.1261 | -3550 | -400 | -3505.8739 | 87.65% | 76.05% | 95% | 0% | 1711 | -101
[5 empty] | 2019-03-24 | 12 | 1974 | 1615 | -104 | 1 | 0 | 1719 | 572.2176 | 572.2176 | 572.2176 | 2058.6974 | 780 | 200 | 3038.6974 | 75.97% | 95% | 0% | -118.9931 | 453.2245 | -3550 | -400 | -3496.7755 | 87.42% | 76.05% | 95% | 0% | 1719 | -104
[5 empty] | 2019-03-24 | 13 | 1974.5 | 1636 | -115 | 1 | 0 | 1751 | 622.3413 | 622.3413 | 622.3413 | 2058.6974 | 780 | 200 | 3038.6974 | 75.97% | 95% | 0% | -131.5789 | 490.7624 | -3550 | -400 | -3459.2376 | 86.48% | 76.05% | 95% | 0% | 1751 | -115
[5 empty] | 2019-03-24 | 14 | 1975 | 1622 | -157 | 1 | 0 | 1779 | 666.1995 | 666.1995 | 666.1995 | 2058.6974 | 780 | 200 | 3038.6974 | 75.97% | 95% | 0% | -179.6339 | 486.5656 | -3550 | -400 | -3463.4344 | 86.59% | 76.04% | 95% | 0% | 1779 | -157
[5 empty] | 2019-03-24 | 15 | 1975.5 | 1581 | -228 | 1 | 0 | 1809 | 713.1904 | 713.1904 | 713.1904 | 2058.6974 | 780 | 200 | 3038.6974 | 75.97% | 95% | 0% | -260.8696 | 452.3209 | -3550 | -400 | -3497.6791 | 87.44% | 76.04% | 95% | 0% | 1809 | -228
[5 empty] | 2019-03-24 | 16 | 1976 | 1500 | -321 | 1 | 0 | 1821 | 731.9868 | 731.9868 | 731.9868 | 2058.6974 | 780 | 200 | 3038.6974 | 75.97% | 95% | 0% | -367.2769 | 364.7099 | -3550 | -400 | -3585.2901 | 89.63% | 76.03% | 95% | 0% | 1821 | -321
[5 empty] | 2019-03-24 | 17 | 1976.5 | 1460 | -401 | 1 | 0 | 1861 | 794.6414 | 794.6414 | 794.6414 | 2058.6974 | 780 | 200 | 3038.6974 | 75.97% | 95% | 0% | -458.8101 | 335.8313 | -3550 | -400 | -3614.1687 | 90.35% | 76.02% | 95% | 0% | 1861 | -401
[5 empty] | 2019-03-24 | 18 | 1977 | 1381 | -500 | 1 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 2058.6974 | 780 | 200 | 3038.6974 | 75.97% | 95% | 0% | -572.0824 | 253.8863 | -3550 | -400 | -3696.1137 | 92.4% | 76.01% | 95% | 0% | 1881 | -500
[5 empty] | 2019-03-24 | 19 | 1977.5 | 1296 | -585 | 1 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 2057.1311 | 780 | 200 | 3037.1311 | 75.93% | 95% | 0% | -669.3364 | 156.6323 | -3550 | -400 | -3793.3677 | 94.83% | 76% | 95% | 0% | 1881 | -585
[5 empty] | 2019-03-24 | 20 | 1978 | 1196 | -668 | 1 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 2057.1311 | 780 | 200 | 3037.1311 | 75.93% | 95% | 0% | -764.3021 | 35.0384 | -3550 | -400 | -3914.9616 | 97.87% | 76% | 95% | 0% | 1864 | -668
[5 empty] | 2019-03-24 | 21 | 1978.5 | 1117 | -726 | 1 | 0 | 1843 | 766.4468 | 766.4468 | 766.4468 | 2057.1311 | 780 | 200 | 3037.1311 | 75.93% | 95% | 0% | -830.6636 | -64.2168 | -3550 | -400 | -4014.2168 | 100.4% | 76% | 95% | 0% | 1843 | -726
[5 empty] | 2019-03-24 | 22 | 1979 | 1036 | -769 | 1 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 2057.1311 | 780 | 200 | 3037.1311 | 75.93% | 95% | 0% | -879.8627 | -172.9377 | -3550 | -400 | -4122.9377 | 103.1% | 75.99% | 95% | 0% | 1805 | -769
[5 empty] | 2019-03-24 | 23 | 1979.5 | 985 | -806 | 1 | 0 | 1791 | 684.9959 | 684.9959 | 684.9959 | 2057.1311 | 780 | 200 | 3037.1311 | 75.93% | 95% | 0% | -922.1968 | -237.2009 | -3550 | -400 | -4187.2009 | 104.7% | 75.99% | 95% | 0% | 1791 | -806
[5 empty] | 2019-03-24 | 24 | 1980 | 940 | -830 | 1 | 0 | 1770 | 652.1022 | 652.1022 | 652.1022 | 2057.1311 | 780 | 200 | 3037.1311 | 75.93% | 95% | 0% | -949.6568 | -297.5545 | -3550 | -400 | -4247.5545 | 106.2% | 75.99% | 95% | 0% | 1770 | -830
[5 empty] | 2019-03-24 | 25 | 1980.5 | 956 | -826 | 1 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 2055.5647 | 780 | 200 | 3035.5647 | 75.89% | 95% | 0% | -945.0801 | -274.1815 | -3550 | -400 | -4224.1815 | 105.6% | 75.99% | 95% | 0% | 1782 | -826
[5 empty] | 2019-03-24 | 26 | 1981 | 953 | -818 | 1 | 0 | 1771 | 653.6686 | 653.6686 | 653.6686 | 2055.5647 | 780 | 200 | 3035.5647 | 75.89% | 95% | 0% | -935.9268 | -282.2582 | -3550 | -400 | -4232.2582 | 105.8% | 75.97% | 95% | 0% | 1771 | -818
[5 empty] | 2019-03-24 | 27 | 1981.5 | 928 | -815 | 1 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 2055.5647 | 780 | 200 | 3035.5647 | 75.89% | 95% | 0% | -932.4943 | -322.6839 | -3550 | -400 | -4272.6839 | 106.8% | 75.96% | 95% | 0% | 1743 | -815
[5 empty] | 2019-03-24 | 28 | 1982 | 936 | -778 | 1 | 0 | 1714 | 564.3858 | 564.3858 | 564.3858 | 2055.5647 | 780 | 200 | 3035.5647 | 75.89% | 95% | 0% | -890.1602 | -325.7744 | -3550 | -400 | -4275.7744 | 106.9% | 75.96% | 95% | 0% | 1714 | -778
[5 empty] | 2019-03-24 | 29 | 1982.5 | 1018 | -711 | 1 | 0 | 1729 | 587.8813 | 587.8813 | 587.8813 | 2055.5647 | 780 | 200 | 3035.5647 | 75.89% | 95% | 0% | -813.5011 | -225.6199 | -3550 | -400 | -4175.6199 | 104.4% | 75.96% | 95% | 0% | 1729 | -711
[5 empty] | 2019-03-24 | 30 | 1983 | 1120 | -645 | 1 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 2055.5647 | 780 | 200 | 3035.5647 | 75.89% | 95% | 0% | -737.9863 | -93.7159 | -3550 | -400 | -4043.7159 | 101.1% | 75.95% | 95% | 0% | 1765 | -645
[5 empty] | 2019-03-24 | 31 | 1983.5 | 1242 | -587 | 1 | 0 | 1829 | 744.5177 | 744.5177 | 744.5177 | 2053.9984 | 780 | 200 | 3033.9984 | 75.85% | 95% | 0% | -671.6247 | 72.893 | -3550 | -400 | -3877.107 | 96.93% | 75.94% | 95% | 0% | 1829 | -587
[5 empty] | 2019-03-24 | 32 | 1984 | 1402 | -524 | 1 | 0 | 1926 | 896.4551 | 896.4551 | 896.4551 | 2053.9984 | 780 | 200 | 3033.9984 | 75.85% | 95% | 0% | -599.5423 | 296.9127 | -3550 | -400 | -3653.0873 | 91.33% | 75.94% | 95% | 0% | 1926 | -524
[5 empty] | 2019-03-24 | 33 | 1984.5 | 1608 | -446 | 1 | 0 | 2054 | 1096.9497 | 1096.9497 | 1096.9497 | 2053.9984 | 780 | 200 | 3033.9984 | 75.85% | 95% | 0% | -510.2975 | 586.6522 | -3550 | -400 | -3363.3478 | 84.08% | 75.93% | 95% | 0% | 2054 | -446
[5 empty] | 2019-03-24 | 34 | 1985 | 1859 | -362 | 1 | 0 | 2221 | 1358.5326 | 1358.5326 | 1358.5326 | 2053.9984 | 780 | 200 | 3033.9984 | 75.85% | 95% | 0% | -414.1876 | 944.3449 | -3550 | -400 | -3005.6551 | 75.14% | 75.93% | 95% | 0% | 2221 | -362
[5 empty] | 2019-03-24 | 35 | 1985.5 | 2102 | -282 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 2053.9984 | 780 | 200 | 3033.9984 | 75.85% | 95% | 0% | -322.6545 | 1291.1955 | -3550 | -400 | -2658.8045 | 66.47% | 75.92% | 95% | 0% | 2384 | -282
[5 empty] | 2019-03-24 | 36 | 1986 | 2272 | -212 | 1 | 0 | 2484 | 1770.4864 | 1770.4864 | 1770.4864 | 2053.9984 | 780 | 200 | 3033.9984 | 75.85% | 95% | 0% | -242.5629 | 1527.9235 | -3550 | -400 | -2422.0765 | 60.55% | 75.91% | 95% | 0% | 2484 | -212
[5 empty] | 2019-03-24 | 37 | 1986.5 | 2383 | -182 | 1 | 0 | 2565 | 1897.3619 | 1897.3619 | 1897.3619 | 2053.9984 | 780 | 200 | 3033.9984 | 75.85% | 95% | 0% | -208.238 | 1689.1239 | -3550 | -400 | -2260.8761 | 56.52% | 75.9% | 95% | 0% | 2565 | -182
[5 empty] | 2019-03-24 | 38 | 1987 | 2477 | -176 | 1 | 0 | 2653 | 2035.202 | 2035.202 | 2035.202 | 2053.9984 | 780 | 200 | 3033.9984 | 75.85% | 95% | 0% | -201.373 | 1833.829 | -3550 | -400 | -2116.171 | 52.9% | 75.9% | 95% | 0% | 2653 | -176
[5 empty] | 2019-03-24 | 39 | 1987.5 | 2493 | -175 | 1 | 0 | 2668 | 2058.6974 | 2058.6974 | 2058.6974 | 2053.9984 | 780 | 200 | 3033.9984 | 75.85% | 95% | 0% | -200.2288 | 1858.4686 | -3550 | -400 | -2091.5314 | 52.29% | 75.9% | 95% | 0% | 2668 | -175
[5 empty] | 2019-03-24 | 40 | 1988 | 2440 | -174 | 0 | 0 | 2614 | 1974.1138 | 1974.1138 | 1974.1138 | 2053.9984 | 780 | 200 | 3033.9984 | 75.85% | 95% | 0% | -199.0847 | 1775.0291 | -2750 | -200 | -1174.9709 | 29.37% | 75.9% | 95% | 0% | 2614 | -174
[5 empty] | 2019-03-24 | 41 | 1988.5 | 2391 | -174 | 0 | 0 | 2565 | 1897.3619 | 1897.3619 | 1897.3619 | 2052.432 | 780 | 200 | 3032.432 | 75.81% | 95% | 0% | -199.0847 | 1698.2772 | -2750 | -200 | -1251.7228 | 31.29% | 75.89% | 95% | 0% | 2565 | -174
[5 empty] | 2019-03-24 | 42 | 1989 | 2280 | -174 | 0 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 2052.432 | 780 | 200 | 3032.432 | 75.81% | 95% | 0% | -199.0847 | 1524.4108 | -2750 | -200 | -1425.5892 | 35.64% | 75.89% | 95% | 0% | 2454 | -174
[5 empty] | 2019-03-24 | 43 | 1989.5 | 2171 | -174 | 0 | 0 | 2345 | 1552.7617 | 1552.7617 | 1552.7617 | 2052.432 | 780 | 200 | 3032.432 | 75.81% | 95% | 0% | -199.0847 | 1353.6771 | -2750 | -200 | -1596.3229 | 39.91% | 75.89% | 95% | 0% | 2345 | -174
[5 empty] | 2019-03-24 | 44 | 1990 | 2038 | -174 | 0 | 0 | 2212 | 1344.4353 | 1344.4353 | 1344.4353 | 2052.432 | 780 | 200 | 3032.432 | 75.81% | 95% | 0% | -199.0847 | 1145.3506 | -2750 | -200 | -1804.6494 | 45.12% | 75.89% | 95% | 0% | 2212 | -174
[5 empty] | 2019-03-24 | 45 | 1990.5 | 1910 | -176 | 0 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 2052.432 | 780 | 200 | 3032.432 | 75.81% | 95% | 0% | -201.373 | 945.7004 | -2750 | -200 | -2004.2996 | 50.11% | 75.87% | 95% | 0% | 2086 | -176
[5 empty] | 2019-03-24 | 46 | 1991 | 1786 | -177 | 0 | 0 | 1963 | 954.4106 | 954.4106 | 954.4106 | 2052.432 | 780 | 200 | 3032.432 | 75.81% | 95% | 0% | -202.5172 | 751.8934 | -2750 | -200 | -2198.1066 | 54.95% | 75.86% | 95% | 0% | 1963 | -177
[5 empty] | 2019-03-24 | 47 | 1991.5 | 1652 | -176 | 0 | 0 | 1828 | 742.9514 | 742.9514 | 742.9514 | 2052.432 | 780 | 200 | 3032.432 | 75.81% | 95% | 0% | -201.373 | 541.5784 | -2750 | -200 | -2408.4216 | 60.21% | 75.86% | 95% | 0% | 1828 | -176
[5 empty] | 2019-03-24 | 48 | 1992 | 1565 | -176 | 0 | 0 | 1741 | 606.6777 | 606.6777 | 606.6777 | 2052.432 | 780 | 200 | 3032.432 | 75.81% | 95% | 0% | -201.373 | 405.3047 | -2750 | -200 | -2544.6953 | 63.62% | 75.85% | 95% | 0% | 1741 | -176
[5 empty] | 2019-03-25 | 1 | 1992.5 | 1551 | -177 | 0 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 2050.8656 | 780 | 200 | 3030.8656 | 75.77% | 95% | 0% | -202.5172 | 383.7978 | -2750 | -200 | -2566.2022 | 64.16% | 75.84% | 95% | 0% | 1728 | -177
[5 empty] | 2019-03-25 | 2 | 1993 | 1583 | -178 | 0 | 0 | 1761 | 638.0049 | 638.0049 | 638.0049 | 2050.8656 | 780 | 200 | 3030.8656 | 75.77% | 95% | 0% | -203.6613 | 434.3436 | -2750 | -200 | -2515.6564 | 62.89% | 75.84% | 95% | 0% | 1761 | -178
[5 empty] | 2019-03-25 | 3 | 1993.5 | 1565 | -175 | 0 | 0 | 1740 | 605.1113 | 605.1113 | 605.1113 | 2050.8656 | 780 | 200 | 3030.8656 | 75.77% | 95% | 0% | -200.2288 | 404.8825 | -2750 | -200 | -2545.1175 | 63.63% | 75.84% | 95% | 0% | 1740 | -175
[5 empty] | 2019-03-25 | 4 | 1994 | 1527 | -173 | 0 | 0 | 1700 | 542.4567 | 542.4567 | 542.4567 | 2050.8656 | 780 | 200 | 3030.8656 | 75.77% | 95% | 0% | -197.9405 | 344.5162 | -2750 | -200 | -2605.4838 | 65.14% | 75.83% | 95% | 0% | 1700 | -173
[5 empty] | 2019-03-25 | 5 | 1994.5 | 1496 | -170 | 0 | 0 | 1666 | 489.2003 | 489.2003 | 489.2003 | 2050.8656 | 780 | 200 | 3030.8656 | 75.77% | 95% | 0% | -194.508 | 294.6923 | -2750 | -200 | -2655.3077 | 66.38% | 75.83% | 95% | 0% | 1666 | -170
[5 empty] | 2019-03-25 | 6 | 1995 | 1486 | -168 | 0 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 2050.8656 | 780 | 200 | 3030.8656 | 75.77% | 95% | 0% | -192.2197 | 278.1843 | -2750 | -200 | -2671.8157 | 66.8% | 75.83% | 95% | 0% | 1654 | -168
[5 empty] | 2019-03-25 | 7 | 1995.5 | 1484 | -163 | 0 | 0 | 1647 | 459.4394 | 459.4394 | 459.4394 | 2050.8656 | 780 | 200 | 3030.8656 | 75.77% | 95% | 0% | -186.4989 | 272.9406 | -2750 | -200 | -2677.0594 | 66.93% | 75.82% | 95% | 0% | 1647 | -163
[5 empty] | 2019-03-25 | 8 | 1996 | 1478 | -159 | 0 | 0 | 1637 | 443.7758 | 443.7758 | 443.7758 | 2050.8656 | 780 | 200 | 3030.8656 | 75.77% | 95% | 0% | -181.9222 | 261.8536 | -2750 | -200 | -2688.1464 | 67.2% | 75.82% | 95% | 0% | 1637 | -159
[5 empty] | 2019-03-25 | 9 | 1996.5 | 1488 | -157 | 0 | 0 | 1645 | 456.3067 | 456.3067 | 456.3067 | 2050.8656 | 780 | 200 | 3030.8656 | 75.77% | 95% | 0% | -179.6339 | 276.6728 | -2750 | -200 | -2673.3272 | 66.83% | 75.82% | 95% | 0% | 1645 | -157
[5 empty] | 2019-03-25 | 10 | 1997 | 1509 | -154 | 0 | 0 | 1663 | 484.5012 | 484.5012 | 484.5012 | 2049.2993 | 780 | 200 | 3029.2993 | 75.73% | 95% | 0% | -176.2014 | 308.2999 | -2750 | -200 | -2641.7001 | 66.04% | 75.82% | 95% | 0% | 1663 | -154
[5 empty] | 2019-03-25 | 11 | 1997.5 | 1598 | -150 | 0 | 0 | 1748 | 617.6422 | 617.6422 | 617.6422 | 2049.2993 | 780 | 200 | 3029.2993 | 75.73% | 95% | 0% | -171.6247 | 446.0175 | -2750 | -200 | -2503.9825 | 62.6% | 75.81% | 95% | 0% | 1748 | -150
[5 empty] | 2019-03-25 | 12 | 1998 | 1705 | -146 | 0 | 0 | 1851 | 778.9777 | 778.9777 | 778.9777 | 2049.2993 | 780 | 200 | 3029.2993 | 75.73% | 95% | 0% | -167.0481 | 611.9297 | -2750 | -200 | -2338.0703 | 58.45% | 75.81% | 95% | 0% | 1851 | -146
[5 empty] | 2019-03-25 | 13 | 1998.5 | 1940 | -153 | 0 | 0 | 2093 | 1158.0379 | 1158.0379 | 1158.0379 | 2049.2993 | 780 | 200 | 3029.2993 | 75.73% | 95% | 0% | -175.0572 | 982.9807 | -2750 | -200 | -1967.0193 | 49.18% | 75.81% | 95% | 0% | 2093 | -153
[5 empty] | 2019-03-25 | 14 | 1999 | 2097 | -203 | 0 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 2049.2993 | 780 | 200 | 3029.2993 | 75.73% | 95% | 0% | -232.2654 | 1250.0099 | -2750 | -200 | -1699.9901 | 42.5% | 75.81% | 95% | 0% | 2300 | -203
[5 empty] | 2019-03-25 | 15 | 1999.5 | 2222 | -282 | 1 | 0 | 2504 | 1801.8137 | 1801.8137 | 1801.8137 | 2049.2993 | 780 | 200 | 3029.2993 | 75.73% | 95% | 0% | -322.6545 | 1479.1592 | -3550 | -400 | -2470.8408 | 61.77% | 75.8% | 95% | 0% | 2504 | -282
[5 empty] | 2019-03-25 | 16 | 2000 | 2181 | -363 | 1 | 0 | 2544 | 1864.4683 | 1864.4683 | 1864.4683 | 2047.7329 | 780 | 200 | 3027.7329 | 75.69% | 95% | 0% | -415.3318 | 1449.1365 | -3550 | -400 | -2500.8635 | 62.52% | 75.8% | 95% | 0% | 2544 | -363
[5 empty] | 2019-03-25 | 17 | 2000.5 | 2087 | -444 | 1 | 0 | 2531 | 1844.1055 | 1844.1055 | 1844.1055 | 2047.7329 | 780 | 200 | 3027.7329 | 75.69% | 95% | 0% | -508.0092 | 1336.0964 | -3550 | -400 | -2613.9036 | 65.35% | 75.79% | 95% | 0% | 2531 | -444
[5 empty] | 2019-03-25 | 18 | 2001 | 1934 | -529 | 1 | 0 | 2463 | 1737.5927 | 1737.5927 | 1737.5927 | 2047.7329 | 780 | 200 | 3027.7329 | 75.69% | 95% | 0% | -605.2632 | 1132.3296 | -3550 | -400 | -2817.6704 | 70.44% | 75.79% | 95% | 0% | 2463 | -529
[5 empty] | 2019-03-25 | 19 | 2001.5 | 1838 | -592 | 1 | 0 | 2430 | 1685.9027 | 1685.9027 | 1685.9027 | 2047.7329 | 780 | 200 | 3027.7329 | 75.69% | 95% | 0% | -677.3455 | 1008.5572 | -3550 | -400 | -2941.4428 | 73.54% | 75.79% | 95% | 0% | 2430 | -592
[5 empty] | 2019-03-25 | 20 | 2002 | 1735 | -643 | 1 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 2047.7329 | 780 | 200 | 3027.7329 | 75.69% | 95% | 0% | -735.6979 | 868.7538 | -3550 | -400 | -3081.2462 | 77.03% | 75.78% | 95% | 0% | 2378 | -643
[5 empty] | 2019-03-25 | 21 | 2002.5 | 1660 | -682 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 2047.7329 | 780 | 200 | 3027.7329 | 75.69% | 95% | 0% | -780.3204 | 767.7423 | -3550 | -400 | -3182.2577 | 79.56% | 75.78% | 95% | 0% | 2342 | -682
[5 empty] | 2019-03-25 | 22 | 2003 | 1608 | -720 | 1 | 0 | 2328 | 1526.1336 | 1526.1336 | 1526.1336 | 2047.7329 | 780 | 200 | 3027.7329 | 75.69% | 95% | 0% | -823.7986 | 702.3349 | -3550 | -400 | -3247.6651 | 81.19% | 75.78% | 95% | 0% | 2328 | -720
[5 empty] | 2019-03-25 | 23 | 2003.5 | 1592 | -740 | 1 | 0 | 2332 | 1532.399 | 1532.399 | 1532.399 | 2046.1665 | 780 | 200 | 3026.1665 | 75.65% | 95% | 0% | -846.6819 | 685.7171 | -3550 | -400 | -3264.2829 | 81.61% | 75.77% | 95% | 0% | 2332 | -740
[5 empty] | 2019-03-25 | 24 | 2004 | 1577 | -754 | 1 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 2046.1665 | 780 | 200 | 3026.1665 | 75.65% | 95% | 0% | -862.7002 | 668.1324 | -3550 | -400 | -3281.8676 | 82.05% | 75.77% | 95% | 0% | 2331 | -754
[5 empty] | 2019-03-25 | 25 | 2004.5 | 1586 | -744 | 1 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 2046.1665 | 780 | 200 | 3026.1665 | 75.65% | 95% | 0% | -851.2586 | 678.0077 | -3550 | -400 | -3271.9923 | 81.8% | 75.77% | 95% | 0% | 2330 | -744
[5 empty] | 2019-03-25 | 26 | 2005 | 1568 | -743 | 1 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 2046.1665 | 780 | 200 | 3026.1665 | 75.65% | 95% | 0% | -850.1144 | 649.3909 | -3550 | -400 | -3300.6091 | 82.52% | 75.77% | 95% | 0% | 2311 | -743
[5 empty] | 2019-03-25 | 27 | 2005.5 | 1590 | -704 | 1 | 0 | 2294 | 1472.8772 | 1472.8772 | 1472.8772 | 2046.1665 | 780 | 200 | 3026.1665 | 75.65% | 95% | 0% | -805.492 | 667.3852 | -3550 | -400 | -3282.6148 | 82.07% | 75.76% | 95% | 0% | 2294 | -704
[5 empty] | 2019-03-25 | 28 | 2006 | 1594 | -678 | 1 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 2046.1665 | 780 | 200 | 3026.1665 | 75.65% | 95% | 0% | -775.7437 | 662.6734 | -3550 | -400 | -3287.3266 | 82.18% | 75.76% | 95% | 0% | 2272 | -678
[5 empty] | 2019-03-25 | 29 | 2006.5 | 1668 | -624 | 1 | 0 | 2292 | 1469.7444 | 1469.7444 | 1469.7444 | 2046.1665 | 780 | 200 | 3026.1665 | 75.65% | 95% | 0% | -713.9588 | 755.7856 | -3550 | -400 | -3194.2144 | 79.86% | 75.76% | 95% | 0% | 2292 | -624
[5 empty] | 2019-03-25 | 30 | 2007 | 1737 | -581 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 2044.6002 | 780 | 200 | 3024.6002 | 75.62% | 95% | 0% | -664.7597 | 845.7102 | -3550 | -400 | -3104.2898 | 77.61% | 75.75% | 95% | 0% | 2318 | -581
[5 empty] | 2019-03-25 | 31 | 2007.5 | 1857 | -514 | 1 | 0 | 2371 | 1593.4872 | 1593.4872 | 1593.4872 | 2044.6002 | 780 | 200 | 3024.6002 | 75.62% | 95% | 0% | -588.1007 | 1005.3865 | -3550 | -400 | -2944.6135 | 73.62% | 75.75% | 95% | 0% | 2371 | -514
[5 empty] | 2019-03-25 | 32 | 2008 | 2035 | -442 | 1 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 2044.6002 | 780 | 200 | 3024.6002 | 75.62% | 95% | 0% | -505.7208 | 1253.801 | -3550 | -400 | -2696.199 | 67.4% | 75.74% | 95% | 0% | 2477 | -442
[5 empty] | 2019-03-25 | 33 | 2008.5 | 2244 | -356 | 1 | 0 | 2600 | 1952.1847 | 1952.1847 | 1952.1847 | 2044.6002 | 780 | 200 | 3024.6002 | 75.62% | 95% | 0% | -407.3227 | 1544.862 | -3550 | -400 | -2405.138 | 60.13% | 75.73% | 95% | 0% | 2600 | -356
[5 empty] | 2019-03-25 | 34 | 2009 | 2468 | -273 | 1 | 0 | 2741 | 2173.042 | 2173.042 | 2173.042 | 2044.6002 | 780 | 200 | 3024.6002 | 75.62% | 95% | 0% | -312.357 | 1860.6851 | -3550 | -400 | -2089.3149 | 52.23% | 75.73% | 95% | 0% | 2741 | -273
[5 empty] | 2019-03-25 | 35 | 2009.5 | 2685 | -195 | 1 | 0 | 2880 | 2390.7667 | 2390.7667 | 2390.7667 | 2044.6002 | 780 | 200 | 3024.6002 | 75.62% | 95% | 0% | -223.1121 | 2167.6546 | -3550 | -400 | -1782.3454 | 44.56% | 75.72% | 95% | 0% | 2880 | -195
[5 empty] | 2019-03-25 | 36 | 2010 | 2858 | -117 | 1 | 0 | 2975 | 2539.5713 | 2539.5713 | 2539.5713 | 2043.0338 | 780 | 200 | 3023.0338 | 75.58% | 95% | 0% | -133.8673 | 2405.704 | -3550 | -400 | -1544.296 | 38.61% | 75.71% | 95% | 0% | 2975 | -117
[5 empty] | 2019-03-25 | 37 | 2010.5 | 2952 | -73 | 1 | 0 | 3025 | 2617.8895 | 2617.8895 | 2617.8895 | 2043.0338 | 780 | 200 | 3023.0338 | 75.58% | 95% | 0% | -83.524 | 2534.3655 | -3550 | -400 | -1415.6345 | 35.39% | 75.71% | 95% | 0% | 3025 | -73
[5 empty] | 2019-03-25 | 38 | 2011 | 3080 | -65 | 1 | 0 | 3145 | 2805.8533 | 2805.8533 | 2805.8533 | 2043.0338 | 780 | 200 | 3023.0338 | 75.58% | 95% | 0% | -74.3707 | 2731.4825 | -3550 | -400 | -1218.5175 | 30.46% | 75.7% | 95% | 0% | 3145 | -65
[5 empty] | 2019-03-25 | 39 | 2011.5 | 3121 | -63 | 1 | 0 | 3184 | 2866.9415 | 2866.9415 | 2866.9415 | 2043.0338 | 780 | 200 | 3023.0338 | 75.58% | 95% | 0% | -72.0824 | 2794.8591 | -3550 | -400 | -1155.1409 | 28.88% | 75.69% | 95% | 0% | 3184 | -63
[5 empty] | 2019-03-25 | 40 | 2012 | 3081 | -61 | 0 | 0 | 3142 | 2801.1542 | 2801.1542 | 2801.1542 | 2043.0338 | 780 | 200 | 3023.0338 | 75.58% | 95% | 0% | -69.7941 | 2731.3601 | -2750 | -200 | -218.6399 | 5.466% | 75.69% | 95% | 0% | 3142 | -61
[5 empty] | 2019-03-25 | 41 | 2012.5 | 2977 | -60 | 0 | 0 | 3037 | 2636.6859 | 2636.6859 | 2636.6859 | 2043.0338 | 780 | 200 | 3023.0338 | 75.58% | 95% | 0% | -68.6499 | 2568.036 | -2750 | -200 | -381.964 | 9.549% | 75.68% | 95% | 0% | 3037 | -60
[5 empty] | 2019-03-25 | 42 | 2013 | 2876 | -59 | 0 | 0 | 2935 | 2476.9167 | 2476.9167 | 2476.9167 | 2043.0338 | 780 | 200 | 3023.0338 | 75.58% | 95% | 0% | -67.5057 | 2409.411 | -2750 | -200 | -540.589 | 13.51% | 75.68% | 95% | 0% | 2935 | -59
[5 empty] | 2019-03-25 | 43 | 2013.5 | 2750 | -57 | 0 | 0 | 2807 | 2276.4221 | 2276.4221 | 2276.4221 | 2043.0338 | 780 | 200 | 3023.0338 | 75.58% | 95% | 0% | -65.2174 | 2211.2047 | -2750 | -200 | -738.7953 | 18.47% | 75.66% | 95% | 0% | 2807 | -57
[5 empty] | 2019-03-25 | 44 | 2014 | 2597 | -56 | 0 | 0 | 2653 | 2035.202 | 2035.202 | 2035.202 | 2041.4674 | 780 | 200 | 3021.4674 | 75.54% | 95% | 0% | -64.0732 | 1971.1288 | -2750 | -200 | -978.8712 | 24.47% | 75.66% | 95% | 0% | 2653 | -56
[5 empty] | 2019-03-25 | 45 | 2014.5 | 2421 | -55 | 0 | 0 | 2476 | 1757.9555 | 1757.9555 | 1757.9555 | 2041.4674 | 780 | 200 | 3021.4674 | 75.54% | 95% | 0% | -62.9291 | 1695.0264 | -2750 | -200 | -1254.9736 | 31.37% | 75.65% | 95% | 0% | 2476 | -55
[5 empty] | 2019-03-25 | 46 | 2015 | 2274 | -54 | 0 | 0 | 2328 | 1526.1336 | 1526.1336 | 1526.1336 | 2041.4674 | 780 | 200 | 3021.4674 | 75.54% | 95% | 0% | -61.7849 | 1464.3487 | -2750 | -200 | -1485.6513 | 37.14% | 75.64% | 95% | 0% | 2328 | -54
[5 empty] | 2019-03-25 | 47 | 2015.5 | 2139 | -54 | 0 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 2041.4674 | 780 | 200 | 3021.4674 | 75.54% | 95% | 0% | -61.7849 | 1252.8895 | -2750 | -200 | -1697.1105 | 42.43% | 75.64% | 95% | 0% | 2193 | -54
[5 empty] | 2019-03-25 | 48 | 2016 | 2053 | -54 | 0 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 2039.9011 | 780 | 200 | 3019.9011 | 75.5% | 95% | 0% | -61.7849 | 1118.1821 | -2750 | -200 | -1831.8179 | 45.8% | 75.64% | 95% | 0% | 2107 | -54
[5 empty] | 2019-03-26 | 1 | 2016.5 | 2017 | -56 | 0 | 0 | 2073 | 1126.7106 | 1126.7106 | 1126.7106 | 2039.9011 | 780 | 200 | 3019.9011 | 75.5% | 95% | 0% | -64.0732 | 1062.6374 | -2750 | -200 | -1887.3626 | 47.18% | 75.63% | 95% | 0% | 2073 | -56
[5 empty] | 2019-03-26 | 2 | 2017 | 2032 | -58 | 0 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 2039.9011 | 780 | 200 | 3019.9011 | 75.5% | 95% | 0% | -66.3616 | 1086.9773 | -2750 | -200 | -1863.0227 | 46.58% | 75.63% | 95% | 0% | 2090 | -58
[5 empty] | 2019-03-26 | 3 | 2017.5 | 1997 | -61 | 0 | 0 | 2058 | 1103.2152 | 1103.2152 | 1103.2152 | 2038.3347 | 780 | 200 | 3018.3347 | 75.46% | 95% | 0% | -69.7941 | 1033.4211 | -2750 | -200 | -1916.5789 | 47.91% | 75.62% | 95% | 0% | 2058 | -61
[5 empty] | 2019-03-26 | 4 | 2018 | 1945 | -64 | 0 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 2038.3347 | 780 | 200 | 3018.3347 | 75.46% | 95% | 0% | -73.2265 | 953.2368 | -2750 | -200 | -1996.7632 | 49.92% | 75.62% | 95% | 0% | 2009 | -64
[5 empty] | 2019-03-26 | 5 | 2018.5 | 1898 | -67 | 0 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 2038.3347 | 780 | 200 | 3018.3347 | 75.46% | 95% | 0% | -76.659 | 880.8842 | -2750 | -200 | -2069.1158 | 51.73% | 75.62% | 95% | 0% | 1965 | -67
[5 empty] | 2019-03-26 | 6 | 2019 | 1877 | -69 | 0 | 0 | 1946 | 927.7824 | 927.7824 | 927.7824 | 2038.3347 | 780 | 200 | 3018.3347 | 75.46% | 95% | 0% | -78.9474 | 848.835 | -2750 | -200 | -2101.165 | 52.53% | 75.61% | 95% | 0% | 1946 | -69
[5 empty] | 2019-03-26 | 7 | 2019.5 | 1836 | -72 | 0 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 2038.3347 | 780 | 200 | 3018.3347 | 75.46% | 95% | 0% | -82.3799 | 785.8806 | -2750 | -200 | -2164.1194 | 54.1% | 75.6% | 95% | 0% | 1908 | -72
[5 empty] | 2019-03-26 | 8 | 2020 | 1812 | -74 | 0 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 2038.3347 | 780 | 200 | 3018.3347 | 75.46% | 95% | 0% | -84.6682 | 749.1323 | -2750 | -200 | -2200.8677 | 55.02% | 75.59% | 95% | 0% | 1886 | -74
[5 empty] | 2019-03-26 | 9 | 2020.5 | 1812 | -76 | 1 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 2036.7683 | 780 | 200 | 3016.7683 | 75.42% | 95% | 0% | -86.9565 | 749.9767 | -3550 | -400 | -3200.0233 | 80% | 75.59% | 95% | 0% | 1888 | -76
[5 empty] | 2019-03-26 | 10 | 2021 | 1822 | -77 | 1 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 2036.7683 | 780 | 200 | 3016.7683 | 75.42% | 95% | 0% | -88.1007 | 766.0625 | -3550 | -400 | -3183.9375 | 79.6% | 75.58% | 95% | 0% | 1899 | -77
[5 empty] | 2019-03-26 | 11 | 2021.5 | 1900 | -80 | 1 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 2036.7683 | 780 | 200 | 3016.7683 | 75.42% | 95% | 0% | -91.5332 | 889.5056 | -3550 | -400 | -3060.4944 | 76.51% | 75.58% | 95% | 0% | 1980 | -80
[5 empty] | 2019-03-26 | 12 | 2022 | 1994 | -82 | 1 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 2036.7683 | 780 | 200 | 3016.7683 | 75.42% | 95% | 0% | -93.8215 | 1037.5882 | -3550 | -400 | -2912.4118 | 72.81% | 75.56% | 95% | 0% | 2076 | -82
[5 empty] | 2019-03-26 | 13 | 2022.5 | 2205 | -89 | 1 | 0 | 2294 | 1472.8772 | 1472.8772 | 1472.8772 | 2036.7683 | 780 | 200 | 3016.7683 | 75.42% | 95% | 0% | -101.8307 | 1371.0465 | -3550 | -400 | -2578.9535 | 64.47% | 75.55% | 95% | 0% | 2294 | -89
[5 empty] | 2019-03-26 | 14 | 2023 | 2363 | -119 | 1 | 0 | 2482 | 1767.3537 | 1767.3537 | 1767.3537 | 2036.7683 | 780 | 200 | 3016.7683 | 75.42% | 95% | 0% | -136.1556 | 1631.1981 | -3550 | -400 | -2318.8019 | 57.97% | 75.55% | 95% | 0% | 2482 | -119
[5 empty] | 2019-03-26 | 15 | 2023.5 | 2494 | -177 | 1 | 0 | 2671 | 2063.3965 | 2063.3965 | 2063.3965 | 2036.7683 | 780 | 200 | 3016.7683 | 75.42% | 95% | 0% | -202.5172 | 1860.8794 | -3550 | -400 | -2089.1206 | 52.23% | 75.55% | 95% | 0% | 2671 | -177
[5 empty] | 2019-03-26 | 16 | 2024 | 2464 | -251 | 1 | 0 | 2715 | 2132.3166 | 2132.3166 | 2132.3166 | 2035.202 | 780 | 200 | 3015.202 | 75.38% | 95% | 0% | -287.1854 | 1845.1312 | -3550 | -400 | -2104.8688 | 52.62% | 75.54% | 95% | 0% | 2715 | -251
[5 empty] | 2019-03-26 | 17 | 2024.5 | 2399 | -316 | 1 | 0 | 2715 | 2132.3166 | 2132.3166 | 2132.3166 | 2035.202 | 780 | 200 | 3015.202 | 75.38% | 95% | 0% | -361.5561 | 1770.7605 | -3550 | -400 | -2179.2395 | 54.48% | 75.54% | 95% | 0% | 2715 | -316
[5 empty] | 2019-03-26 | 18 | 2025 | 2261 | -392 | 1 | 0 | 2653 | 2035.202 | 2035.202 | 2035.202 | 2035.202 | 780 | 200 | 3015.202 | 75.38% | 95% | 0% | -448.5126 | 1586.6894 | -3550 | -400 | -2363.3106 | 59.08% | 75.53% | 95% | 0% | 2653 | -392
[5 empty] | 2019-03-26 | 19 | 2025.5 | 2143 | -475 | 1 | 0 | 2618 | 1980.3792 | 1980.3792 | 1980.3792 | 2035.202 | 780 | 200 | 3015.202 | 75.38% | 95% | 0% | -543.4783 | 1436.901 | -3550 | -400 | -2513.099 | 62.83% | 75.53% | 95% | 0% | 2618 | -475
[5 empty] | 2019-03-26 | 20 | 2026 | 2013 | -539 | 1 | 0 | 2552 | 1876.9992 | 1876.9992 | 1876.9992 | 2035.202 | 780 | 200 | 3015.202 | 75.38% | 95% | 0% | -616.7048 | 1260.2944 | -3550 | -400 | -2689.7056 | 67.24% | 75.53% | 95% | 0% | 2552 | -539
[5 empty] | 2019-03-26 | 21 | 2026.5 | 1951 | -537 | 1 | 0 | 2488 | 1776.7519 | 1776.7519 | 1776.7519 | 2035.202 | 780 | 200 | 3015.202 | 75.38% | 95% | 0% | -614.4165 | 1162.3354 | -3550 | -400 | -2787.6646 | 69.69% | 75.53% | 95% | 0% | 2488 | -537
[5 empty] | 2019-03-26 | 22 | 2027 | 1940 | -529 | 1 | 0 | 2469 | 1746.9909 | 1746.9909 | 1746.9909 | 2035.202 | 780 | 200 | 3015.202 | 75.38% | 95% | 0% | -605.2632 | 1141.7278 | -3550 | -400 | -2808.2722 | 70.21% | 75.53% | 95% | 0% | 2469 | -529
[5 empty] | 2019-03-26 | 23 | 2027.5 | 1954 | -538 | 1 | 0 | 2492 | 1783.0173 | 1783.0173 | 1783.0173 | 2035.202 | 780 | 200 | 3015.202 | 75.38% | 95% | 0% | -615.5606 | 1167.4567 | -3550 | -400 | -2782.5433 | 69.56% | 75.52% | 95% | 0% | 2492 | -538
[5 empty] | 2019-03-26 | 24 | 2028 | 1934 | -578 | 1 | 0 | 2512 | 1814.3446 | 1814.3446 | 1814.3446 | 2033.6356 | 780 | 200 | 3013.6356 | 75.34% | 95% | 0% | -661.3272 | 1153.0174 | -3550 | -400 | -2796.9826 | 69.92% | 75.5% | 95% | 0% | 2512 | -578
[5 empty] | 2019-03-26 | 25 | 2028.5 | 1911 | -607 | 1 | 0 | 2518 | 1823.7428 | 1823.7428 | 1823.7428 | 2033.6356 | 780 | 200 | 3013.6356 | 75.34% | 95% | 0% | -694.508 | 1129.2348 | -3550 | -400 | -2820.7652 | 70.52% | 75.48% | 95% | 0% | 2518 | -607
[5 empty] | 2019-03-26 | 26 | 2029 | 1865 | -618 | 1 | 0 | 2483 | 1768.92 | 1768.92 | 1768.92 | 2033.6356 | 780 | 200 | 3013.6356 | 75.34% | 95% | 0% | -707.0938 | 1061.8262 | -3550 | -400 | -2888.1738 | 72.2% | 75.48% | 95% | 0% | 2483 | -618
[5 empty] | 2019-03-26 | 27 | 2029.5 | 1858 | -601 | 1 | 0 | 2459 | 1731.3273 | 1731.3273 | 1731.3273 | 2033.6356 | 780 | 200 | 3013.6356 | 75.34% | 95% | 0% | -687.643 | 1043.6843 | -3550 | -400 | -2906.3157 | 72.66% | 75.48% | 95% | 0% | 2459 | -601
[5 empty] | 2019-03-26 | 28 | 2030 | 1872 | -563 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 2033.6356 | 780 | 200 | 3013.6356 | 75.34% | 95% | 0% | -644.1648 | 1049.5698 | -3550 | -400 | -2900.4302 | 72.51% | 75.48% | 95% | 0% | 2435 | -563
[5 empty] | 2019-03-26 | 29 | 2030.5 | 1886 | -546 | 1 | 0 | 2432 | 1689.0354 | 1689.0354 | 1689.0354 | 2033.6356 | 780 | 200 | 3013.6356 | 75.34% | 95% | 0% | -624.714 | 1064.3215 | -3550 | -400 | -2885.6785 | 72.14% | 75.48% | 95% | 0% | 2432 | -546
[5 empty] | 2019-03-26 | 30 | 2031 | 1905 | -521 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 2033.6356 | 780 | 200 | 3013.6356 | 75.34% | 95% | 0% | -596.1098 | 1083.5274 | -3550 | -400 | -2866.4726 | 71.66% | 75.47% | 95% | 0% | 2426 | -521
[5 empty] | 2019-03-26 | 31 | 2031.5 | 1983 | -459 | 1 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 2033.6356 | 780 | 200 | 3013.6356 | 75.34% | 95% | 0% | -525.1716 | 1179.5275 | -3550 | -400 | -2770.4725 | 69.26% | 75.47% | 95% | 0% | 2442 | -459
[5 empty] | 2019-03-26 | 32 | 2032 | 2132 | -398 | 1 | 0 | 2530 | 1842.5392 | 1842.5392 | 1842.5392 | 2032.0692 | 780 | 200 | 3012.0692 | 75.3% | 95% | 0% | -455.3776 | 1387.1616 | -3550 | -400 | -2562.8384 | 64.07% | 75.47% | 95% | 0% | 2530 | -398
[5 empty] | 2019-03-26 | 33 | 2032.5 | 2298 | -329 | 1 | 0 | 2627 | 1994.4765 | 1994.4765 | 1994.4765 | 2032.0692 | 780 | 200 | 3012.0692 | 75.3% | 95% | 0% | -376.4302 | 1618.0463 | -3550 | -400 | -2331.9537 | 58.3% | 75.47% | 95% | 0% | 2627 | -329
[5 empty] | 2019-03-26 | 34 | 2033 | 2519 | -251 | 1 | 0 | 2770 | 2218.4666 | 2218.4666 | 2218.4666 | 2032.0692 | 780 | 200 | 3012.0692 | 75.3% | 95% | 0% | -287.1854 | 1931.2813 | -3550 | -400 | -2018.7187 | 50.47% | 75.47% | 95% | 0% | 2770 | -251
[5 empty] | 2019-03-26 | 35 | 2033.5 | 2711 | -189 | 1 | 0 | 2900 | 2422.094 | 2422.094 | 2422.094 | 2032.0692 | 780 | 200 | 3012.0692 | 75.3% | 95% | 0% | -216.2471 | 2205.8468 | -3550 | -400 | -1744.1532 | 43.6% | 75.46% | 95% | 0% | 2900 | -189
[5 empty] | 2019-03-26 | 36 | 2034 | 2843 | -126 | 1 | 0 | 2969 | 2530.1731 | 2530.1731 | 2530.1731 | 2032.0692 | 780 | 200 | 3012.0692 | 75.3% | 95% | 0% | -144.1648 | 2386.0084 | -3550 | -400 | -1563.9916 | 39.1% | 75.46% | 95% | 0% | 2969 | -126
[5 empty] | 2019-03-26 | 37 | 2034.5 | 2933 | -94 | 1 | 0 | 3027 | 2621.0223 | 2621.0223 | 2621.0223 | 2030.5029 | 780 | 200 | 3010.5029 | 75.26% | 95% | 0% | -107.5515 | 2513.4708 | -3550 | -400 | -1436.5292 | 35.91% | 75.46% | 95% | 0% | 3027 | -94
[5 empty] | 2019-03-26 | 38 | 2035 | 3046 | -87 | 1 | 0 | 3133 | 2787.0569 | 2787.0569 | 2787.0569 | 2030.5029 | 780 | 200 | 3010.5029 | 75.26% | 95% | 0% | -99.5423 | 2687.5145 | -3550 | -400 | -1262.4855 | 31.56% | 75.45% | 95% | 0% | 3133 | -87
[5 empty] | 2019-03-26 | 39 | 2035.5 | 3068 | -85 | 1 | 0 | 3153 | 2818.3842 | 2818.3842 | 2818.3842 | 2030.5029 | 780 | 200 | 3010.5029 | 75.26% | 95% | 0% | -97.254 | 2721.1302 | -3550 | -400 | -1228.8698 | 30.72% | 75.44% | 95% | 0% | 3153 | -85
[5 empty] | 2019-03-26 | 40 | 2036 | 3021 | -84 | 0 | 0 | 3105 | 2743.1987 | 2743.1987 | 2743.1987 | 2030.5029 | 780 | 200 | 3010.5029 | 75.26% | 95% | 0% | -96.1098 | 2647.0888 | -2750 | -200 | -302.9112 | 7.573% | 75.44% | 95% | 0% | 3105 | -84
[5 empty] | 2019-03-26 | 41 | 2036.5 | 2934 | -83 | 0 | 0 | 3017 | 2605.3586 | 2605.3586 | 2605.3586 | 2030.5029 | 780 | 200 | 3010.5029 | 75.26% | 95% | 0% | -94.9657 | 2510.3929 | -2750 | -200 | -439.6071 | 10.99% | 75.44% | 95% | 0% | 3017 | -83
[5 empty] | 2019-03-26 | 42 | 2037 | 2815 | -83 | 0 | 0 | 2898 | 2418.9613 | 2418.9613 | 2418.9613 | 2030.5029 | 780 | 200 | 3010.5029 | 75.26% | 95% | 0% | -94.9657 | 2323.9956 | -2750 | -200 | -626.0044 | 15.65% | 75.44% | 95% | 0% | 2898 | -83
[5 empty] | 2019-03-26 | 43 | 2037.5 | 2694 | -83 | 0 | 0 | 2777 | 2229.4312 | 2229.4312 | 2229.4312 | 2030.5029 | 780 | 200 | 3010.5029 | 75.26% | 95% | 0% | -94.9657 | 2134.4655 | -2750 | -200 | -815.5345 | 20.39% | 75.44% | 95% | 0% | 2777 | -83
[5 empty] | 2019-03-26 | 44 | 2038 | 2526 | -83 | 0 | 0 | 2609 | 1966.2819 | 1966.2819 | 1966.2819 | 2030.5029 | 780 | 200 | 3010.5029 | 75.26% | 95% | 0% | -94.9657 | 1871.3163 | -2750 | -200 | -1078.6837 | 26.97% | 75.44% | 95% | 0% | 2609 | -83
[5 empty] | 2019-03-26 | 45 | 2038.5 | 2353 | -84 | 0 | 0 | 2437 | 1696.8673 | 1696.8673 | 1696.8673 | 2030.5029 | 780 | 200 | 3010.5029 | 75.26% | 95% | 0% | -96.1098 | 1600.7574 | -2750 | -200 | -1349.2426 | 33.73% | 75.43% | 95% | 0% | 2437 | -84
[5 empty] | 2019-03-26 | 46 | 2039 | 2207 | -85 | 0 | 0 | 2292 | 1469.7444 | 1469.7444 | 1469.7444 | 2028.9365 | 780 | 200 | 3008.9365 | 75.22% | 95% | 0% | -97.254 | 1372.4904 | -2750 | -200 | -1577.5096 | 39.44% | 75.43% | 95% | 0% | 2292 | -85
[5 empty] | 2019-03-26 | 47 | 2039.5 | 2054 | -84 | 0 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 2028.9365 | 780 | 200 | 3008.9365 | 75.22% | 95% | 0% | -96.1098 | 1132.4145 | -2750 | -200 | -1817.5855 | 45.44% | 75.43% | 95% | 0% | 2138 | -84
[5 empty] | 2019-03-26 | 48 | 2040 | 1958 | -83 | 0 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 2028.9365 | 780 | 200 | 3008.9365 | 75.22% | 95% | 0% | -94.9657 | 981.6213 | -2750 | -200 | -1968.3787 | 49.21% | 75.42% | 95% | 0% | 2041 | -83
[5 empty] | 2019-03-27 | 1 | 2040.5 | 1932 | -83 | 0 | 0 | 2015 | 1035.8615 | 1035.8615 | 1035.8615 | 2028.9365 | 780 | 200 | 3008.9365 | 75.22% | 95% | 0% | -94.9657 | 940.8958 | -2750 | -200 | -2009.1042 | 50.23% | 75.42% | 95% | 0% | 2015 | -83
[5 empty] | 2019-03-27 | 2 | 2041 | 1957 | -82 | 0 | 0 | 2039 | 1073.4542 | 1073.4542 | 1073.4542 | 2028.9365 | 780 | 200 | 3008.9365 | 75.22% | 95% | 0% | -93.8215 | 979.6327 | -2750 | -200 | -1970.3673 | 49.26% | 75.42% | 95% | 0% | 2039 | -82
[5 empty] | 2019-03-27 | 3 | 2041.5 | 1926 | -83 | 0 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 2028.9365 | 780 | 200 | 3008.9365 | 75.22% | 95% | 0% | -94.9657 | 931.4976 | -2750 | -200 | -2018.5024 | 50.46% | 75.42% | 95% | 0% | 2009 | -83
[5 empty] | 2019-03-27 | 4 | 2042 | 1869 | -83 | 0 | 0 | 1952 | 937.1805 | 937.1805 | 937.1805 | 2027.3702 | 780 | 200 | 3007.3702 | 75.18% | 95% | 0% | -94.9657 | 842.2149 | -2750 | -200 | -2107.7851 | 52.69% | 75.41% | 95% | 0% | 1952 | -83
[5 empty] | 2019-03-27 | 5 | 2042.5 | 1833 | -82 | 0 | 0 | 1915 | 879.2251 | 879.2251 | 879.2251 | 2027.3702 | 780 | 200 | 3007.3702 | 75.18% | 95% | 0% | -93.8215 | 785.4036 | -2750 | -200 | -2164.5964 | 54.11% | 75.41% | 95% | 0% | 1915 | -82
[5 empty] | 2019-03-27 | 6 | 2043 | 1817 | -82 | 0 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 2027.3702 | 780 | 200 | 3007.3702 | 75.18% | 95% | 0% | -93.8215 | 760.3417 | -2750 | -200 | -2189.6583 | 54.74% | 75.4% | 95% | 0% | 1899 | -82
[5 empty] | 2019-03-27 | 7 | 2043.5 | 1791 | -82 | 0 | 0 | 1873 | 813.4378 | 813.4378 | 813.4378 | 2027.3702 | 780 | 200 | 3007.3702 | 75.18% | 95% | 0% | -93.8215 | 719.6162 | -2750 | -200 | -2230.3838 | 55.76% | 75.39% | 95% | 0% | 1873 | -82
[5 empty] | 2019-03-27 | 8 | 2044 | 1768 | -82 | 0 | 0 | 1850 | 777.4114 | 777.4114 | 777.4114 | 2027.3702 | 780 | 200 | 3007.3702 | 75.18% | 95% | 0% | -93.8215 | 683.5899 | -2750 | -200 | -2266.4101 | 56.66% | 75.39% | 95% | 0% | 1850 | -82
[5 empty] | 2019-03-27 | 9 | 2044.5 | 1764 | -82 | 0 | 0 | 1846 | 771.1459 | 771.1459 | 771.1459 | 2027.3702 | 780 | 200 | 3007.3702 | 75.18% | 95% | 0% | -93.8215 | 677.3244 | -2750 | -200 | -2272.6756 | 56.82% | 75.39% | 95% | 0% | 1846 | -82
[5 empty] | 2019-03-27 | 10 | 2045 | 1785 | -82 | 0 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 2027.3702 | 780 | 200 | 3007.3702 | 75.18% | 95% | 0% | -93.8215 | 710.2181 | -2750 | -200 | -2239.7819 | 55.99% | 75.39% | 95% | 0% | 1867 | -82
[5 empty] | 2019-03-27 | 11 | 2045.5 | 1861 | -82 | 0 | 0 | 1943 | 923.0833 | 923.0833 | 923.0833 | 2027.3702 | 780 | 200 | 3007.3702 | 75.18% | 95% | 0% | -93.8215 | 829.2618 | -2750 | -200 | -2120.7382 | 53.02% | 75.38% | 95% | 0% | 1943 | -82
[5 empty] | 2019-03-27 | 12 | 2046 | 1963 | -81 | 0 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 2025.8038 | 780 | 200 | 3005.8038 | 75.15% | 95% | 0% | -92.6773 | 988.6087 | -2750 | -200 | -1961.3913 | 49.03% | 75.38% | 95% | 0% | 2044 | -81
[5 empty] | 2019-03-27 | 13 | 2046.5 | 2185 | -83 | 0 | 0 | 2268 | 1432.1517 | 1432.1517 | 1432.1517 | 2025.8038 | 780 | 200 | 3005.8038 | 75.15% | 95% | 0% | -94.9657 | 1337.186 | -2750 | -200 | -1612.814 | 40.32% | 75.38% | 95% | 0% | 2268 | -83
[5 empty] | 2019-03-27 | 14 | 2047 | 2367 | -102 | 0 | 0 | 2469 | 1746.9909 | 1746.9909 | 1746.9909 | 2025.8038 | 780 | 200 | 3005.8038 | 75.15% | 95% | 0% | -116.7048 | 1630.2861 | -2750 | -200 | -1319.7139 | 32.99% | 75.37% | 95% | 0% | 2469 | -102
[5 empty] | 2019-03-27 | 15 | 2047.5 | 2530 | -138 | 0 | 0 | 2668 | 2058.6974 | 2058.6974 | 2058.6974 | 2025.8038 | 780 | 200 | 3005.8038 | 75.15% | 95% | 0% | -157.8947 | 1900.8027 | -2750 | -200 | -1049.1973 | 26.23% | 75.37% | 95% | 0% | 2668 | -138
[5 empty] | 2019-03-27 | 16 | 2048 | 2547 | -184 | 1 | 0 | 2731 | 2157.3784 | 2157.3784 | 2157.3784 | 2025.8038 | 780 | 200 | 3005.8038 | 75.15% | 95% | 0% | -210.5263 | 1946.8521 | -3550 | -400 | -2003.1479 | 50.08% | 75.35% | 95% | 0% | 2731 | -184
[5 empty] | 2019-03-27 | 17 | 2048.5 | 2503 | -230 | 1 | 0 | 2733 | 2160.5111 | 2160.5111 | 2160.5111 | 2025.8038 | 780 | 200 | 3005.8038 | 75.15% | 95% | 0% | -263.1579 | 1897.3532 | -3550 | -400 | -2052.6468 | 51.32% | 75.35% | 95% | 0% | 2733 | -230
[5 empty] | 2019-03-27 | 18 | 2049 | 2441 | -274 | 1 | 0 | 2715 | 2132.3166 | 2132.3166 | 2132.3166 | 2025.8038 | 780 | 200 | 3005.8038 | 75.15% | 95% | 0% | -313.5011 | 1818.8154 | -3550 | -400 | -2131.1846 | 53.28% | 75.34% | 95% | 0% | 2715 | -274
[5 empty] | 2019-03-27 | 19 | 2049.5 | 2394 | -317 | 1 | 0 | 2711 | 2126.0511 | 2126.0511 | 2126.0511 | 2025.8038 | 780 | 200 | 3005.8038 | 75.15% | 95% | 0% | -362.7002 | 1763.3509 | -3550 | -400 | -2186.6491 | 54.67% | 75.34% | 95% | 0% | 2711 | -317
[5 empty] | 2019-03-27 | 20 | 2050 | 2344 | -353 | 1 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 2025.8038 | 780 | 200 | 3005.8038 | 75.15% | 95% | 0% | -403.8902 | 1700.2319 | -3550 | -400 | -2249.7681 | 56.24% | 75.33% | 95% | 0% | 2697 | -353
[5 empty] | 2019-03-27 | 21 | 2050.5 | 2290 | -388 | 1 | 0 | 2678 | 2074.3611 | 2074.3611 | 2074.3611 | 2024.2374 | 780 | 200 | 3004.2374 | 75.11% | 95% | 0% | -443.9359 | 1630.4252 | -3550 | -400 | -2319.5748 | 57.99% | 75.33% | 95% | 0% | 2678 | -388
[5 empty] | 2019-03-27 | 22 | 2051 | 2239 | -425 | 1 | 0 | 2664 | 2052.432 | 2052.432 | 2052.432 | 2024.2374 | 780 | 200 | 3004.2374 | 75.11% | 95% | 0% | -486.27 | 1566.162 | -3550 | -400 | -2383.838 | 59.6% | 75.33% | 95% | 0% | 2664 | -425
[5 empty] | 2019-03-27 | 23 | 2051.5 | 2236 | -426 | 1 | 0 | 2662 | 2049.2993 | 2049.2993 | 2049.2993 | 2024.2374 | 780 | 200 | 3004.2374 | 75.11% | 95% | 0% | -487.4142 | 1561.8851 | -3550 | -400 | -2388.1149 | 59.7% | 75.33% | 95% | 0% | 2662 | -426
[5 empty] | 2019-03-27 | 24 | 2052 | 2227 | -423 | 1 | 0 | 2650 | 2030.5029 | 2030.5029 | 2030.5029 | 2024.2374 | 780 | 200 | 3004.2374 | 75.11% | 95% | 0% | -483.9817 | 1546.5212 | -3550 | -400 | -2403.4788 | 60.09% | 75.32% | 95% | 0% | 2650 | -423
[5 empty] | 2019-03-27 | 25 | 2052.5 | 2229 | -425 | 1 | 0 | 2654 | 2036.7683 | 2036.7683 | 2036.7683 | 2024.2374 | 780 | 200 | 3004.2374 | 75.11% | 95% | 0% | -486.27 | 1550.4983 | -3550 | -400 | -2399.5017 | 59.99% | 75.31% | 95% | 0% | 2654 | -425
[5 empty] | 2019-03-27 | 26 | 2053 | 2184 | -441 | 1 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 2024.2374 | 780 | 200 | 3004.2374 | 75.11% | 95% | 0% | -504.5767 | 1486.7671 | -3550 | -400 | -2463.2329 | 61.58% | 75.31% | 95% | 0% | 2625 | -441
[5 empty] | 2019-03-27 | 27 | 2053.5 | 2137 | -458 | 1 | 0 | 2595 | 1944.3528 | 1944.3528 | 1944.3528 | 2024.2374 | 780 | 200 | 3004.2374 | 75.11% | 95% | 0% | -524.0275 | 1420.3254 | -3550 | -400 | -2529.6746 | 63.24% | 75.31% | 95% | 0% | 2595 | -458
[5 empty] | 2019-03-27 | 28 | 2054 | 2088 | -463 | 1 | 0 | 2551 | 1875.4328 | 1875.4328 | 1875.4328 | 2024.2374 | 780 | 200 | 3004.2374 | 75.11% | 95% | 0% | -529.7483 | 1345.6845 | -3550 | -400 | -2604.3155 | 65.11% | 75.29% | 95% | 0% | 2551 | -463
[5 empty] | 2019-03-27 | 29 | 2054.5 | 2094 | -440 | 1 | 0 | 2534 | 1848.8046 | 1848.8046 | 1848.8046 | 2022.6711 | 780 | 200 | 3002.6711 | 75.07% | 95% | 0% | -503.4325 | 1345.3721 | -3550 | -400 | -2604.6279 | 65.12% | 75.28% | 95% | 0% | 2534 | -440
[5 empty] | 2019-03-27 | 30 | 2055 | 2111 | -418 | 1 | 0 | 2529 | 1840.9728 | 1840.9728 | 1840.9728 | 2022.6711 | 780 | 200 | 3002.6711 | 75.07% | 95% | 0% | -478.2609 | 1362.7119 | -3550 | -400 | -2587.2881 | 64.68% | 75.28% | 95% | 0% | 2529 | -418
[5 empty] | 2019-03-27 | 31 | 2055.5 | 2161 | -385 | 1 | 0 | 2546 | 1867.601 | 1867.601 | 1867.601 | 2022.6711 | 780 | 200 | 3002.6711 | 75.07% | 95% | 0% | -440.5034 | 1427.0976 | -3550 | -400 | -2522.9024 | 63.07% | 75.27% | 95% | 0% | 2546 | -385
[5 empty] | 2019-03-27 | 32 | 2056 | 2274 | -339 | 1 | 0 | 2613 | 1972.5474 | 1972.5474 | 1972.5474 | 2022.6711 | 780 | 200 | 3002.6711 | 75.07% | 95% | 0% | -387.8719 | 1584.6755 | -3550 | -400 | -2365.3245 | 59.13% | 75.27% | 95% | 0% | 2613 | -339
[5 empty] | 2019-03-27 | 33 | 2056.5 | 2422 | -277 | 1 | 0 | 2699 | 2107.2547 | 2107.2547 | 2107.2547 | 2022.6711 | 780 | 200 | 3002.6711 | 75.07% | 95% | 0% | -316.9336 | 1790.3211 | -3550 | -400 | -2159.6789 | 53.99% | 75.27% | 95% | 0% | 2699 | -277
[5 empty] | 2019-03-27 | 34 | 2057 | 2598 | -222 | 1 | 0 | 2820 | 2296.7848 | 2296.7848 | 2296.7848 | 2022.6711 | 780 | 200 | 3002.6711 | 75.07% | 95% | 0% | -254.0046 | 2042.7803 | -3550 | -400 | -1907.2197 | 47.68% | 75.26% | 95% | 0% | 2820 | -222
[5 empty] | 2019-03-27 | 35 | 2057.5 | 2752 | -165 | 1 | 0 | 2917 | 2448.7222 | 2448.7222 | 2448.7222 | 2021.1047 | 780 | 200 | 3001.1047 | 75.03% | 95% | 0% | -188.7872 | 2259.935 | -3550 | -400 | -1690.065 | 42.25% | 75.25% | 95% | 0% | 2917 | -165
[5 empty] | 2019-03-27 | 36 | 2058 | 2870 | -110 | 1 | 0 | 2980 | 2547.4031 | 2547.4031 | 2547.4031 | 2021.1047 | 780 | 200 | 3001.1047 | 75.03% | 95% | 0% | -125.8581 | 2421.545 | -3550 | -400 | -1528.455 | 38.21% | 75.25% | 95% | 0% | 2980 | -110
[5 empty] | 2019-03-27 | 37 | 2058.5 | 2964 | -73 | 1 | 0 | 3037 | 2636.6859 | 2636.6859 | 2636.6859 | 2021.1047 | 780 | 200 | 3001.1047 | 75.03% | 95% | 0% | -83.524 | 2553.1619 | -3550 | -400 | -1396.8381 | 34.92% | 75.25% | 95% | 0% | 3037 | -73
[5 empty] | 2019-03-27 | 38 | 2059 | 3050 | -65 | 1 | 0 | 3115 | 2758.8623 | 2758.8623 | 2758.8623 | 2021.1047 | 780 | 200 | 3001.1047 | 75.03% | 95% | 0% | -74.3707 | 2684.4916 | -3550 | -400 | -1265.5084 | 31.64% | 75.25% | 95% | 0% | 3115 | -65
[5 empty] | 2019-03-27 | 39 | 2059.5 | 3091 | -63 | 1 | 0 | 3154 | 2819.9505 | 2819.9505 | 2819.9505 | 2021.1047 | 780 | 200 | 3001.1047 | 75.03% | 95% | 0% | -72.0824 | 2747.8682 | -3550 | -400 | -1202.1318 | 30.05% | 75.25% | 95% | 0% | 3154 | -63
[5 empty] | 2019-03-27 | 40 | 2060 | 3039 | -61 | 0 | 0 | 3100 | 2735.3669 | 2735.3669 | 2735.3669 | 2021.1047 | 780 | 200 | 3001.1047 | 75.03% | 95% | 0% | -69.7941 | 2665.5728 | -2750 | -200 | -284.4272 | 7.111% | 75.24% | 95% | 0% | 3100 | -61
[5 empty] | 2019-03-27 | 41 | 2060.5 | 2951 | -60 | 0 | 0 | 3011 | 2595.9604 | 2595.9604 | 2595.9604 | 2021.1047 | 780 | 200 | 3001.1047 | 75.03% | 95% | 0% | -68.6499 | 2527.3105 | -2750 | -200 | -422.6895 | 10.57% | 75.24% | 95% | 0% | 3011 | -60
[5 empty] | 2019-03-27 | 42 | 2061 | 2865 | -59 | 0 | 0 | 2924 | 2459.6867 | 2459.6867 | 2459.6867 | 2021.1047 | 780 | 200 | 3001.1047 | 75.03% | 95% | 0% | -67.5057 | 2392.181 | -2750 | -200 | -557.819 | 13.95% | 75.23% | 95% | 0% | 2924 | -59
[5 empty] | 2019-03-27 | 43 | 2061.5 | 2739 | -59 | 0 | 0 | 2798 | 2262.3248 | 2262.3248 | 2262.3248 | 2021.1047 | 780 | 200 | 3001.1047 | 75.03% | 95% | 0% | -67.5057 | 2194.8191 | -2750 | -200 | -755.1809 | 18.88% | 75.23% | 95% | 0% | 2798 | -59
[5 empty] | 2019-03-27 | 44 | 2062 | 2579 | -60 | 0 | 0 | 2639 | 2013.2729 | 2013.2729 | 2013.2729 | 2021.1047 | 780 | 200 | 3001.1047 | 75.03% | 95% | 0% | -68.6499 | 1944.623 | -2750 | -200 | -1005.377 | 25.13% | 75.23% | 95% | 0% | 2639 | -60
[5 empty] | 2019-03-27 | 45 | 2062.5 | 2435 | -60 | 0 | 0 | 2495 | 1787.7164 | 1787.7164 | 1787.7164 | 2021.1047 | 780 | 200 | 3001.1047 | 75.03% | 95% | 0% | -68.6499 | 1719.0665 | -2750 | -200 | -1230.9335 | 30.77% | 75.22% | 95% | 0% | 2495 | -60
[5 empty] | 2019-03-27 | 46 | 2063 | 2292 | -61 | 0 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 2021.1047 | 780 | 200 | 3001.1047 | 75.03% | 95% | 0% | -69.7941 | 1495.4986 | -2750 | -200 | -1454.5014 | 36.36% | 75.22% | 95% | 0% | 2353 | -61
[5 empty] | 2019-03-27 | 47 | 2063.5 | 2131 | -60 | 0 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -68.6499 | 1242.8917 | -2750 | -200 | -1707.1083 | 42.68% | 75.22% | 95% | 0% | 2191 | -60
[5 empty] | 2019-03-27 | 48 | 2064 | 2035 | -58 | 0 | 0 | 2093 | 1158.0379 | 1158.0379 | 1158.0379 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -66.3616 | 1091.6764 | -2750 | -200 | -1858.3236 | 46.46% | 75.21% | 95% | 0% | 2093 | -58
[5 empty] | 2019-03-28 | 1 | 2064.5 | 2011 | -57 | 0 | 0 | 2068 | 1118.8788 | 1118.8788 | 1118.8788 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -65.2174 | 1053.6614 | -2750 | -200 | -1896.3386 | 47.41% | 75.21% | 95% | 0% | 2068 | -57
[5 empty] | 2019-03-28 | 2 | 2065 | 2027 | -55 | 0 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -62.9291 | 1077.8789 | -2750 | -200 | -1872.1211 | 46.8% | 75.21% | 95% | 0% | 2082 | -55
[5 empty] | 2019-03-28 | 3 | 2065.5 | 1982 | -54 | 0 | 0 | 2036 | 1068.7552 | 1068.7552 | 1068.7552 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -61.7849 | 1006.9703 | -2750 | -200 | -1943.0297 | 48.58% | 75.21% | 95% | 0% | 2036 | -54
[5 empty] | 2019-03-28 | 4 | 2066 | 1943 | -53 | 0 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -60.6407 | 945.4598 | -2750 | -200 | -2004.5402 | 50.11% | 75.2% | 95% | 0% | 1996 | -53
[5 empty] | 2019-03-28 | 5 | 2066.5 | 1908 | -52 | 0 | 0 | 1960 | 949.7115 | 949.7115 | 949.7115 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -59.4966 | 890.2149 | -2750 | -200 | -2059.7851 | 51.49% | 75.19% | 95% | 0% | 1960 | -52
[5 empty] | 2019-03-28 | 6 | 2067 | 1898 | -50 | 0 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -57.2082 | 873.7068 | -2750 | -200 | -2076.2932 | 51.91% | 75.19% | 95% | 0% | 1948 | -50
[5 empty] | 2019-03-28 | 7 | 2067.5 | 1865 | -52 | 0 | 0 | 1917 | 882.3578 | 882.3578 | 882.3578 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -59.4966 | 822.8612 | -2750 | -200 | -2127.1388 | 53.18% | 75.19% | 95% | 0% | 1917 | -52
[5 empty] | 2019-03-28 | 8 | 2068 | 1843 | -54 | 0 | 0 | 1897 | 851.0305 | 851.0305 | 851.0305 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -61.7849 | 789.2456 | -2750 | -200 | -2160.7544 | 54.02% | 75.18% | 95% | 0% | 1897 | -54
[5 empty] | 2019-03-28 | 9 | 2068.5 | 1847 | -54 | 0 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -61.7849 | 795.5111 | -2750 | -200 | -2154.4889 | 53.86% | 75.18% | 95% | 0% | 1901 | -54
[5 empty] | 2019-03-28 | 10 | 2069 | 1859 | -54 | 0 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -61.7849 | 814.3074 | -2750 | -200 | -2135.6926 | 53.39% | 75.18% | 95% | 0% | 1913 | -54
[5 empty] | 2019-03-28 | 11 | 2069.5 | 1931 | -55 | 0 | 0 | 1986 | 990.4369 | 990.4369 | 990.4369 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -62.9291 | 927.5079 | -2750 | -200 | -2022.4921 | 50.56% | 75.18% | 95% | 0% | 1986 | -55
[5 empty] | 2019-03-28 | 12 | 2070 | 2021 | -55 | 0 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -62.9291 | 1068.4807 | -2750 | -200 | -1881.5193 | 47.04% | 75.17% | 95% | 0% | 2076 | -55
[5 empty] | 2019-03-28 | 13 | 2070.5 | 2240 | -60 | 0 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 2019.5383 | 780 | 200 | 2999.5383 | 74.99% | 95% | 0% | -68.6499 | 1413.6255 | -2750 | -200 | -1536.3745 | 38.41% | 75.17% | 95% | 0% | 2300 | -60
[5 empty] | 2019-03-28 | 14 | 2071 | 2409 | -94 | 0 | 0 | 2503 | 1800.2473 | 1800.2473 | 1800.2473 | 2017.972 | 780 | 200 | 2997.972 | 74.95% | 95% | 0% | -107.5515 | 1692.6958 | -2750 | -200 | -1257.3042 | 31.43% | 75.17% | 95% | 0% | 2503 | -94
[5 empty] | 2019-03-28 | 15 | 2071.5 | 2543 | -150 | 0 | 0 | 2693 | 2097.8566 | 2097.8566 | 2097.8566 | 2017.972 | 780 | 200 | 2997.972 | 74.95% | 95% | 0% | -171.6247 | 1926.2318 | -2750 | -200 | -1023.7682 | 25.59% | 75.17% | 95% | 0% | 2693 | -150
[5 empty] | 2019-03-28 | 16 | 2072 | 2506 | -209 | 1 | 0 | 2715 | 2132.3166 | 2132.3166 | 2132.3166 | 2017.972 | 780 | 200 | 2997.972 | 74.95% | 95% | 0% | -239.1304 | 1893.1861 | -3550 | -400 | -2056.8139 | 51.42% | 75.16% | 95% | 0% | 2715 | -209
[5 empty] | 2019-03-28 | 17 | 2072.5 | 2421 | -285 | 1 | 0 | 2706 | 2118.2193 | 2118.2193 | 2118.2193 | 2017.972 | 780 | 200 | 2997.972 | 74.95% | 95% | 0% | -326.087 | 1792.1323 | -3550 | -400 | -2157.8677 | 53.95% | 75.16% | 95% | 0% | 2706 | -285
[5 empty] | 2019-03-28 | 18 | 2073 | 2307 | -360 | 1 | 0 | 2667 | 2057.1311 | 2057.1311 | 2057.1311 | 2017.972 | 780 | 200 | 2997.972 | 74.95% | 95% | 0% | -411.8993 | 1645.2318 | -3550 | -400 | -2304.7682 | 57.62% | 75.16% | 95% | 0% | 2667 | -360
[5 empty] | 2019-03-28 | 19 | 2073.5 | 2210 | -441 | 1 | 0 | 2651 | 2032.0692 | 2032.0692 | 2032.0692 | 2017.972 | 780 | 200 | 2997.972 | 74.95% | 95% | 0% | -504.5767 | 1527.4926 | -3550 | -400 | -2422.5074 | 60.56% | 75.15% | 95% | 0% | 2651 | -441
[5 empty] | 2019-03-28 | 20 | 2074 | 2075 | -507 | 1 | 0 | 2582 | 1923.9901 | 1923.9901 | 1923.9901 | 2016.4056 | 780 | 200 | 2996.4056 | 74.91% | 95% | 0% | -580.0915 | 1343.8986 | -3550 | -400 | -2606.1014 | 65.15% | 75.15% | 95% | 0% | 2582 | -507
[5 empty] | 2019-03-28 | 21 | 2074.5 | 1946 | -568 | 1 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 2016.4056 | 780 | 200 | 2996.4056 | 74.91% | 95% | 0% | -649.8856 | 1167.5917 | -3550 | -400 | -2782.4083 | 69.56% | 75.14% | 95% | 0% | 2514 | -568
[5 empty] | 2019-03-28 | 22 | 2075 | 1855 | -609 | 1 | 0 | 2464 | 1739.1591 | 1739.1591 | 1739.1591 | 2016.4056 | 780 | 200 | 2996.4056 | 74.91% | 95% | 0% | -696.7963 | 1042.3628 | -3550 | -400 | -2907.6372 | 72.69% | 75.14% | 95% | 0% | 2464 | -609
[5 empty] | 2019-03-28 | 23 | 2075.5 | 1775 | -645 | 1 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 2016.4056 | 780 | 200 | 2996.4056 | 74.91% | 95% | 0% | -737.9863 | 932.2528 | -3550 | -400 | -3017.7472 | 75.44% | 75.12% | 95% | 0% | 2420 | -645
[5 empty] | 2019-03-28 | 24 | 2076 | 1745 | -656 | 1 | 0 | 2401 | 1640.4782 | 1640.4782 | 1640.4782 | 2016.4056 | 780 | 200 | 2996.4056 | 74.91% | 95% | 0% | -750.5721 | 889.9061 | -3550 | -400 | -3060.0939 | 76.5% | 75.12% | 95% | 0% | 2401 | -656
[5 empty] | 2019-03-28 | 25 | 2076.5 | 1704 | -678 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 2016.4056 | 780 | 200 | 2996.4056 | 74.91% | 95% | 0% | -775.7437 | 834.9735 | -3550 | -400 | -3115.0265 | 77.88% | 75.12% | 95% | 0% | 2382 | -678
[5 empty] | 2019-03-28 | 26 | 2077 | 1674 | -674 | 1 | 0 | 2348 | 1557.4608 | 1557.4608 | 1557.4608 | 2016.4056 | 780 | 200 | 2996.4056 | 74.91% | 95% | 0% | -771.167 | 786.2938 | -3550 | -400 | -3163.7062 | 79.09% | 75.12% | 95% | 0% | 2348 | -674
[5 empty] | 2019-03-28 | 27 | 2077.5 | 1647 | -669 | 1 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 2016.4056 | 780 | 200 | 2996.4056 | 74.91% | 95% | 0% | -765.4462 | 741.891 | -3550 | -400 | -3208.109 | 80.2% | 75.12% | 95% | 0% | 2316 | -669
[5 empty] | 2019-03-28 | 28 | 2078 | 1638 | -652 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 2016.4056 | 780 | 200 | 2996.4056 | 74.91% | 95% | 0% | -745.9954 | 720.6163 | -3550 | -400 | -3229.3837 | 80.73% | 75.11% | 95% | 0% | 2290 | -652
[5 empty] | 2019-03-28 | 29 | 2078.5 | 1677 | -618 | 1 | 0 | 2295 | 1474.4435 | 1474.4435 | 1474.4435 | 2016.4056 | 780 | 200 | 2996.4056 | 74.91% | 95% | 0% | -707.0938 | 767.3497 | -3550 | -400 | -3182.6503 | 79.57% | 75.1% | 95% | 0% | 2295 | -618
[5 empty] | 2019-03-28 | 30 | 2079 | 1721 | -565 | 1 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 2014.8392 | 780 | 200 | 2994.8392 | 74.87% | 95% | 0% | -646.4531 | 813.8932 | -3550 | -400 | -3136.1068 | 78.4% | 75.09% | 95% | 0% | 2286 | -565
[5 empty] | 2019-03-28 | 31 | 2079.5 | 1805 | -502 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 2014.8392 | 780 | 200 | 2994.8392 | 74.87% | 95% | 0% | -574.3707 | 918.8692 | -3550 | -400 | -3031.1308 | 75.78% | 75.09% | 95% | 0% | 2307 | -502
[5 empty] | 2019-03-28 | 32 | 2080 | 1943 | -440 | 1 | 0 | 2383 | 1612.2836 | 1612.2836 | 1612.2836 | 2014.8392 | 780 | 200 | 2994.8392 | 74.87% | 95% | 0% | -503.4325 | 1108.8511 | -3550 | -400 | -2841.1489 | 71.03% | 75.09% | 95% | 0% | 2383 | -440
[5 empty] | 2019-03-28 | 33 | 2080.5 | 2124 | -363 | 1 | 0 | 2487 | 1775.1855 | 1775.1855 | 1775.1855 | 2014.8392 | 780 | 200 | 2994.8392 | 74.87% | 95% | 0% | -415.3318 | 1359.8537 | -3550 | -400 | -2590.1463 | 64.75% | 75.09% | 95% | 0% | 2487 | -363
[5 empty] | 2019-03-28 | 34 | 2081 | 2345 | -279 | 1 | 0 | 2624 | 1989.7774 | 1989.7774 | 1989.7774 | 2014.8392 | 780 | 200 | 2994.8392 | 74.87% | 95% | 0% | -319.222 | 1670.5554 | -3550 | -400 | -2279.4446 | 56.99% | 75.08% | 95% | 0% | 2624 | -279
[5 empty] | 2019-03-28 | 35 | 2081.5 | 2528 | -201 | 1 | 0 | 2729 | 2154.2457 | 2154.2457 | 2154.2457 | 2013.2729 | 780 | 200 | 2993.2729 | 74.83% | 95% | 0% | -229.9771 | 1924.2686 | -3550 | -400 | -2025.7314 | 50.64% | 75.08% | 95% | 0% | 2729 | -201
[5 empty] | 2019-03-28 | 36 | 2082 | 2622 | -134 | 1 | 0 | 2756 | 2196.5375 | 2196.5375 | 2196.5375 | 2013.2729 | 780 | 200 | 2993.2729 | 74.83% | 95% | 0% | -153.3181 | 2043.2194 | -3550 | -400 | -1906.7806 | 47.67% | 75.08% | 95% | 0% | 2756 | -134
[5 empty] | 2019-03-28 | 37 | 2082.5 | 2740 | -91 | 1 | 0 | 2831 | 2314.0148 | 2314.0148 | 2314.0148 | 2013.2729 | 780 | 200 | 2993.2729 | 74.83% | 95% | 0% | -104.119 | 2209.8958 | -3550 | -400 | -1740.1042 | 43.5% | 75.08% | 95% | 0% | 2831 | -91
[5 empty] | 2019-03-28 | 38 | 2083 | 2865 | -82 | 1 | 0 | 2947 | 2495.7131 | 2495.7131 | 2495.7131 | 2013.2729 | 780 | 200 | 2993.2729 | 74.83% | 95% | 0% | -93.8215 | 2401.8916 | -3550 | -400 | -1548.1084 | 38.7% | 75.08% | 95% | 0% | 2947 | -82
[5 empty] | 2019-03-28 | 39 | 2083.5 | 2924 | -84 | 1 | 0 | 3008 | 2591.2613 | 2591.2613 | 2591.2613 | 2013.2729 | 780 | 200 | 2993.2729 | 74.83% | 95% | 0% | -96.1098 | 2495.1515 | -3550 | -400 | -1454.8485 | 36.37% | 75.07% | 95% | 0% | 3008 | -84
[5 empty] | 2019-03-28 | 40 | 2084 | 2873 | -85 | 0 | 0 | 2958 | 2512.9431 | 2512.9431 | 2512.9431 | 2013.2729 | 780 | 200 | 2993.2729 | 74.83% | 95% | 0% | -97.254 | 2415.6891 | -2750 | -200 | -534.3109 | 13.36% | 75.06% | 95% | 0% | 2958 | -85
[5 empty] | 2019-03-28 | 41 | 2084.5 | 2799 | -87 | 0 | 0 | 2886 | 2400.1649 | 2400.1649 | 2400.1649 | 2013.2729 | 780 | 200 | 2993.2729 | 74.83% | 95% | 0% | -99.5423 | 2300.6225 | -2750 | -200 | -649.3775 | 16.23% | 75.06% | 95% | 0% | 2886 | -87
[5 empty] | 2019-03-28 | 42 | 2085 | 2722 | -89 | 0 | 0 | 2811 | 2282.6876 | 2282.6876 | 2282.6876 | 2013.2729 | 780 | 200 | 2993.2729 | 74.83% | 95% | 0% | -101.8307 | 2180.8569 | -2750 | -200 | -769.1431 | 19.23% | 75.05% | 95% | 0% | 2811 | -89
[5 empty] | 2019-03-28 | 43 | 2085.5 | 2601 | -90 | 0 | 0 | 2691 | 2094.7238 | 2094.7238 | 2094.7238 | 2011.7065 | 780 | 200 | 2991.7065 | 74.79% | 95% | 0% | -102.9748 | 1991.749 | -2750 | -200 | -958.251 | 23.96% | 75.05% | 95% | 0% | 2691 | -90
[5 empty] | 2019-03-28 | 44 | 2086 | 2442 | -90 | 0 | 0 | 2532 | 1845.6719 | 1845.6719 | 1845.6719 | 2011.7065 | 780 | 200 | 2991.7065 | 74.79% | 95% | 0% | -102.9748 | 1742.6971 | -2750 | -200 | -1207.3029 | 30.18% | 75.03% | 95% | 0% | 2532 | -90
[5 empty] | 2019-03-28 | 45 | 2086.5 | 2284 | -91 | 0 | 0 | 2375 | 1599.7527 | 1599.7527 | 1599.7527 | 2011.7065 | 780 | 200 | 2991.7065 | 74.79% | 95% | 0% | -104.119 | 1495.6337 | -2750 | -200 | -1454.3663 | 36.36% | 75.03% | 95% | 0% | 2375 | -91
[5 empty] | 2019-03-28 | 46 | 2087 | 2159 | -91 | 0 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 2011.7065 | 780 | 200 | 2991.7065 | 74.79% | 95% | 0% | -104.119 | 1299.8381 | -2750 | -200 | -1650.1619 | 41.25% | 75.03% | 95% | 0% | 2250 | -91
[5 empty] | 2019-03-28 | 47 | 2087.5 | 2012 | -93 | 0 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 2011.7065 | 780 | 200 | 2991.7065 | 74.79% | 95% | 0% | -106.4073 | 1070.427 | -2750 | -200 | -1879.573 | 46.99% | 75.03% | 95% | 0% | 2105 | -93
[5 empty] | 2019-03-28 | 48 | 2088 | 1904 | -94 | 0 | 0 | 1998 | 1009.2333 | 1009.2333 | 1009.2333 | 2011.7065 | 780 | 200 | 2991.7065 | 74.79% | 95% | 0% | -107.5515 | 901.6818 | -2750 | -200 | -2048.3182 | 51.21% | 75.03% | 95% | 0% | 1998 | -94
[5 empty] | 2019-03-29 | 1 | 2088.5 | 1870 | -95 | 0 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 2011.7065 | 780 | 200 | 2991.7065 | 74.79% | 95% | 0% | -108.6957 | 848.8476 | -2750 | -200 | -2101.1524 | 52.53% | 75.02% | 95% | 0% | 1965 | -95
[5 empty] | 2019-03-29 | 2 | 2089 | 1889 | -95 | 0 | 0 | 1984 | 987.3042 | 987.3042 | 987.3042 | 2011.7065 | 780 | 200 | 2991.7065 | 74.79% | 95% | 0% | -108.6957 | 878.6086 | -2750 | -200 | -2071.3914 | 51.78% | 75.02% | 95% | 0% | 1984 | -95
[5 empty] | 2019-03-29 | 3 | 2089.5 | 1856 | -95 | 0 | 0 | 1951 | 935.6142 | 935.6142 | 935.6142 | 2011.7065 | 780 | 200 | 2991.7065 | 74.79% | 95% | 0% | -108.6957 | 826.9185 | -2750 | -200 | -2123.0815 | 53.08% | 75.02% | 95% | 0% | 1951 | -95
[5 empty] | 2019-03-29 | 4 | 2090 | 1811 | -95 | 0 | 0 | 1906 | 865.1278 | 865.1278 | 865.1278 | 2011.7065 | 780 | 200 | 2991.7065 | 74.79% | 95% | 0% | -108.6957 | 756.4321 | -2750 | -200 | -2193.5679 | 54.84% | 75.01% | 95% | 0% | 1906 | -95
[5 empty] | 2019-03-29 | 5 | 2090.5 | 1773 | -94 | 0 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 2011.7065 | 780 | 200 | 2991.7065 | 74.79% | 95% | 0% | -107.5515 | 696.4881 | -2750 | -200 | -2253.5119 | 56.34% | 75.01% | 95% | 0% | 1867 | -94
[5 empty] | 2019-03-29 | 6 | 2091 | 1748 | -94 | 1 | 0 | 1842 | 764.8805 | 764.8805 | 764.8805 | 2010.1401 | 780 | 200 | 2990.1401 | 74.75% | 95% | 0% | -107.5515 | 657.329 | -3550 | -400 | -3292.671 | 82.32% | 75.01% | 95% | 0% | 1842 | -94
[5 empty] | 2019-03-29 | 7 | 2091.5 | 1717 | -93 | 1 | 0 | 1810 | 714.7568 | 714.7568 | 714.7568 | 2010.1401 | 780 | 200 | 2990.1401 | 74.75% | 95% | 0% | -106.4073 | 608.3495 | -3550 | -400 | -3341.6505 | 83.54% | 75% | 95% | 0% | 1810 | -93
[5 empty] | 2019-03-29 | 8 | 2092 | 1704 | -91 | 1 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 2010.1401 | 780 | 200 | 2990.1401 | 74.75% | 95% | 0% | -104.119 | 587.1423 | -3550 | -400 | -3362.8577 | 84.07% | 75% | 95% | 0% | 1795 | -91
[5 empty] | 2019-03-29 | 9 | 2092.5 | 1703 | -91 | 1 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 2010.1401 | 780 | 200 | 2990.1401 | 74.75% | 95% | 0% | -104.119 | 585.576 | -3550 | -400 | -3364.424 | 84.11% | 75% | 95% | 0% | 1794 | -91
[5 empty] | 2019-03-29 | 10 | 2093 | 1725 | -91 | 1 | 0 | 1816 | 724.155 | 724.155 | 724.155 | 2010.1401 | 780 | 200 | 2990.1401 | 74.75% | 95% | 0% | -104.119 | 620.036 | -3550 | -400 | -3329.964 | 83.25% | 74.99% | 95% | 0% | 1816 | -91
[5 empty] | 2019-03-29 | 11 | 2093.5 | 1802 | -90 | 1 | 0 | 1892 | 843.1987 | 843.1987 | 843.1987 | 2010.1401 | 780 | 200 | 2990.1401 | 74.75% | 95% | 0% | -102.9748 | 740.2239 | -3550 | -400 | -3209.7761 | 80.24% | 74.99% | 95% | 0% | 1892 | -90
[5 empty] | 2019-03-29 | 12 | 2094 | 1882 | -90 | 1 | 0 | 1972 | 968.5078 | 968.5078 | 968.5078 | 2010.1401 | 780 | 200 | 2990.1401 | 74.75% | 95% | 0% | -102.9748 | 865.533 | -3550 | -400 | -3084.467 | 77.11% | 74.99% | 95% | 0% | 1972 | -90
[5 empty] | 2019-03-29 | 13 | 2094.5 | 2089 | -104 | 1 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 2008.5738 | 780 | 200 | 2988.5738 | 74.71% | 95% | 0% | -118.9931 | 1195.6812 | -3550 | -400 | -2754.3188 | 68.86% | 74.98% | 95% | 0% | 2193 | -104
[5 empty] | 2019-03-29 | 14 | 2095 | 2233 | -151 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 2008.5738 | 780 | 200 | 2988.5738 | 74.71% | 95% | 0% | -172.7689 | 1441.0811 | -3550 | -400 | -2508.9189 | 62.72% | 74.97% | 95% | 0% | 2384 | -151
[5 empty] | 2019-03-29 | 15 | 2095.5 | 2347 | -214 | 1 | 0 | 2561 | 1891.0965 | 1891.0965 | 1891.0965 | 2008.5738 | 780 | 200 | 2988.5738 | 74.71% | 95% | 0% | -244.8513 | 1646.2452 | -3550 | -400 | -2303.7548 | 57.59% | 74.96% | 95% | 0% | 2561 | -214
[5 empty] | 2019-03-29 | 16 | 2096 | 2318 | -284 | 1 | 0 | 2602 | 1955.3174 | 1955.3174 | 1955.3174 | 2008.5738 | 780 | 200 | 2988.5738 | 74.71% | 95% | 0% | -324.9428 | 1630.3746 | -3550 | -400 | -2319.6254 | 57.99% | 74.96% | 95% | 0% | 2602 | -284
[5 empty] | 2019-03-29 | 17 | 2096.5 | 2267 | -356 | 1 | 0 | 2623 | 1988.211 | 1988.211 | 1988.211 | 2008.5738 | 780 | 200 | 2988.5738 | 74.71% | 95% | 0% | -407.3227 | 1580.8884 | -3550 | -400 | -2369.1116 | 59.23% | 74.96% | 95% | 0% | 2623 | -356
[5 empty] | 2019-03-29 | 18 | 2097 | 2124 | -433 | 1 | 0 | 2557 | 1884.831 | 1884.831 | 1884.831 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -495.4233 | 1389.4077 | -3550 | -400 | -2560.5923 | 64.01% | 74.96% | 95% | 0% | 2557 | -433
[5 empty] | 2019-03-29 | 19 | 2097.5 | 2000 | -507 | 1 | 0 | 2507 | 1806.5128 | 1806.5128 | 1806.5128 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -580.0915 | 1226.4212 | -3550 | -400 | -2723.5788 | 68.09% | 74.95% | 95% | 0% | 2507 | -507
[5 empty] | 2019-03-29 | 20 | 2098 | 1852 | -577 | 1 | 0 | 2429 | 1684.3364 | 1684.3364 | 1684.3364 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -660.1831 | 1024.1533 | -3550 | -400 | -2925.8467 | 73.15% | 74.95% | 95% | 0% | 2429 | -577
[5 empty] | 2019-03-29 | 21 | 2098.5 | 1707 | -641 | 1 | 0 | 2348 | 1557.4608 | 1557.4608 | 1557.4608 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -733.4096 | 824.0512 | -3550 | -400 | -3125.9488 | 78.15% | 74.95% | 95% | 0% | 2348 | -641
[5 empty] | 2019-03-29 | 22 | 2099 | 1589 | -694 | 1 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -794.0503 | 661.5968 | -3550 | -400 | -3288.4032 | 82.21% | 74.94% | 95% | 0% | 2283 | -694
[5 empty] | 2019-03-29 | 23 | 2099.5 | 1521 | -731 | 1 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -836.3844 | 570.7054 | -3550 | -400 | -3379.2946 | 84.48% | 74.94% | 95% | 0% | 2252 | -731
[5 empty] | 2019-03-29 | 24 | 2100 | 1468 | -747 | 1 | 0 | 2215 | 1349.1344 | 1349.1344 | 1349.1344 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -854.6911 | 494.4433 | -3550 | -400 | -3455.5567 | 86.39% | 74.94% | 95% | 0% | 2215 | -747
[5 empty] | 2019-03-29 | 25 | 2100.5 | 1444 | -753 | 1 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -861.5561 | 459.3838 | -3550 | -400 | -3490.6162 | 87.27% | 74.9% | 95% | 0% | 2197 | -753
[5 empty] | 2019-03-29 | 26 | 2101 | 1426 | -743 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -850.1144 | 426.9672 | -3550 | -400 | -3523.0328 | 88.08% | 74.9% | 95% | 0% | 2169 | -743
[5 empty] | 2019-03-29 | 27 | 2101.5 | 1424 | -716 | 1 | 0 | 2140 | 1231.657 | 1231.657 | 1231.657 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -819.222 | 412.4351 | -3550 | -400 | -3537.5649 | 88.44% | 74.9% | 95% | 0% | 2140 | -716
[5 empty] | 2019-03-29 | 28 | 2102 | 1451 | -676 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -773.4554 | 437.8389 | -3550 | -400 | -3512.1611 | 87.8% | 74.89% | 95% | 0% | 2127 | -676
[5 empty] | 2019-03-29 | 29 | 2102.5 | 1518 | -626 | 1 | 0 | 2144 | 1237.9225 | 1237.9225 | 1237.9225 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -716.2471 | 521.6754 | -3550 | -400 | -3428.3246 | 85.71% | 74.89% | 95% | 0% | 2144 | -626
[5 empty] | 2019-03-29 | 30 | 2103 | 1601 | -567 | 1 | 0 | 2168 | 1275.5153 | 1275.5153 | 1275.5153 | 2007.0074 | 780 | 200 | 2987.0074 | 74.68% | 95% | 0% | -648.7414 | 626.7738 | -3550 | -400 | -3323.2262 | 83.08% | 74.89% | 95% | 0% | 2168 | -567
[5 empty] | 2019-03-29 | 31 | 2103.5 | 1706 | -497 | 1 | 0 | 2203 | 1330.338 | 1330.338 | 1330.338 | 2005.4411 | 780 | 200 | 2985.4411 | 74.64% | 95% | 0% | -568.6499 | 761.6881 | -3550 | -400 | -3188.3119 | 79.71% | 74.89% | 95% | 0% | 2203 | -497
[5 empty] | 2019-03-29 | 32 | 2104 | 1868 | -419 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 2005.4411 | 780 | 200 | 2985.4411 | 74.64% | 95% | 0% | -479.405 | 982.5076 | -3550 | -400 | -2967.4924 | 74.19% | 74.89% | 95% | 0% | 2287 | -419
[5 empty] | 2019-03-29 | 33 | 2104.5 | 2061 | -339 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 2005.4411 | 780 | 200 | 2985.4411 | 74.64% | 95% | 0% | -387.8719 | 1251.0399 | -3550 | -400 | -2698.9601 | 67.47% | 74.88% | 95% | 0% | 2400 | -339
[5 empty] | 2019-03-29 | 34 | 2105 | 2278 | -256 | 1 | 0 | 2534 | 1848.8046 | 1848.8046 | 1848.8046 | 2005.4411 | 780 | 200 | 2985.4411 | 74.64% | 95% | 0% | -292.9062 | 1555.8984 | -3550 | -400 | -2394.1016 | 59.85% | 74.87% | 95% | 0% | 2534 | -256
[5 empty] | 2019-03-29 | 35 | 2105.5 | 2472 | -179 | 1 | 0 | 2651 | 2032.0692 | 2032.0692 | 2032.0692 | 2005.4411 | 780 | 200 | 2985.4411 | 74.64% | 95% | 0% | -204.8055 | 1827.2638 | -3550 | -400 | -2122.7362 | 53.07% | 74.86% | 95% | 0% | 2651 | -179
[5 empty] | 2019-03-29 | 36 | 2106 | 2617 | -110 | 1 | 0 | 2727 | 2151.1129 | 2151.1129 | 2151.1129 | 2005.4411 | 780 | 200 | 2985.4411 | 74.64% | 95% | 0% | -125.8581 | 2025.2548 | -3550 | -400 | -1924.7452 | 48.12% | 74.86% | 95% | 0% | 2727 | -110
[5 empty] | 2019-03-29 | 37 | 2106.5 | 2724 | -71 | 1 | 0 | 2795 | 2257.6257 | 2257.6257 | 2257.6257 | 2005.4411 | 780 | 200 | 2985.4411 | 74.64% | 95% | 0% | -81.2357 | 2176.39 | -3550 | -400 | -1773.61 | 44.34% | 74.85% | 95% | 0% | 2795 | -71
[5 empty] | 2019-03-29 | 38 | 2107 | 2799 | -62 | 1 | 0 | 2861 | 2361.0058 | 2361.0058 | 2361.0058 | 2003.8747 | 780 | 200 | 2983.8747 | 74.6% | 95% | 0% | -70.9382 | 2290.0676 | -3550 | -400 | -1659.9324 | 41.5% | 74.85% | 95% | 0% | 2861 | -62
[5 empty] | 2019-03-29 | 39 | 2107.5 | 2829 | -60 | 1 | 0 | 2889 | 2404.864 | 2404.864 | 2404.864 | 2003.8747 | 780 | 200 | 2983.8747 | 74.6% | 95% | 0% | -68.6499 | 2336.2141 | -3550 | -400 | -1613.7859 | 40.34% | 74.85% | 95% | 0% | 2889 | -60
[5 empty] | 2019-03-29 | 40 | 2108 | 2779 | -59 | 0 | 0 | 2838 | 2324.9794 | 2324.9794 | 2324.9794 | 2003.8747 | 780 | 200 | 2983.8747 | 74.6% | 95% | 0% | -67.5057 | 2257.4737 | -2750 | -200 | -692.5263 | 17.31% | 74.84% | 95% | 0% | 2838 | -59
[5 empty] | 2019-03-29 | 41 | 2108.5 | 2729 | -57 | 0 | 0 | 2786 | 2243.5284 | 2243.5284 | 2243.5284 | 2003.8747 | 780 | 200 | 2983.8747 | 74.6% | 95% | 0% | -65.2174 | 2178.3111 | -2750 | -200 | -771.6889 | 19.29% | 74.84% | 95% | 0% | 2786 | -57
[5 empty] | 2019-03-29 | 42 | 2109 | 2662 | -55 | 0 | 0 | 2717 | 2135.4493 | 2135.4493 | 2135.4493 | 2003.8747 | 780 | 200 | 2983.8747 | 74.6% | 95% | 0% | -62.9291 | 2072.5202 | -2750 | -200 | -877.4798 | 21.94% | 74.83% | 95% | 0% | 2717 | -55
[5 empty] | 2019-03-29 | 43 | 2109.5 | 2569 | -54 | 0 | 0 | 2623 | 1988.211 | 1988.211 | 1988.211 | 2003.8747 | 780 | 200 | 2983.8747 | 74.6% | 95% | 0% | -61.7849 | 1926.4261 | -2750 | -200 | -1023.5739 | 25.59% | 74.83% | 95% | 0% | 2623 | -54
[5 empty] | 2019-03-29 | 44 | 2110 | 2442 | -52 | 0 | 0 | 2494 | 1786.15 | 1786.15 | 1786.15 | 2002.3083 | 780 | 200 | 2982.3083 | 74.56% | 95% | 0% | -59.4966 | 1726.6535 | -2750 | -200 | -1223.3465 | 30.58% | 74.82% | 95% | 0% | 2494 | -52
[5 empty] | 2019-03-29 | 45 | 2110.5 | 2312 | -51 | 0 | 0 | 2363 | 1580.9563 | 1580.9563 | 1580.9563 | 2002.3083 | 780 | 200 | 2982.3083 | 74.56% | 95% | 0% | -58.3524 | 1522.6039 | -2750 | -200 | -1427.3961 | 35.68% | 74.81% | 95% | 0% | 2363 | -51
[5 empty] | 2019-03-29 | 46 | 2111 | 2204 | -50 | 0 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 2002.3083 | 780 | 200 | 2982.3083 | 74.56% | 95% | 0% | -57.2082 | 1353.0144 | -2750 | -200 | -1596.9856 | 39.92% | 74.8% | 95% | 0% | 2254 | -50
[5 empty] | 2019-03-29 | 47 | 2111.5 | 2081 | -50 | 0 | 0 | 2131 | 1217.5598 | 1217.5598 | 1217.5598 | 2002.3083 | 780 | 200 | 2982.3083 | 74.56% | 95% | 0% | -57.2082 | 1160.3515 | -2750 | -200 | -1789.6485 | 44.74% | 74.8% | 95% | 0% | 2131 | -50
[5 empty] | 2019-03-29 | 48 | 2112 | 2001 | -50 | 0 | 0 | 2051 | 1092.2506 | 1092.2506 | 1092.2506 | 2002.3083 | 780 | 200 | 2982.3083 | 74.56% | 95% | 0% | -57.2082 | 1035.0424 | -2750 | -200 | -1914.9576 | 47.87% | 74.79% | 95% | 0% | 2051 | -50
[5 empty] | 2019-03-30 | 1 | 2112.5 | 1968 | -50 | 0 | 0 | 2018 | 1040.5606 | 1040.5606 | 1040.5606 | 2000.742 | 780 | 200 | 2980.742 | 74.52% | 95% | 0% | -57.2082 | 983.3524 | -2750 | -200 | -1966.6476 | 49.17% | 74.79% | 95% | 0% | 2018 | -50
[5 empty] | 2019-03-30 | 2 | 2113 | 1975 | -50 | 0 | 0 | 2025 | 1051.5251 | 1051.5251 | 1051.5251 | 2000.742 | 780 | 200 | 2980.742 | 74.52% | 95% | 0% | -57.2082 | 994.3169 | -2750 | -200 | -1955.6831 | 48.89% | 74.78% | 95% | 0% | 2025 | -50
[5 empty] | 2019-03-30 | 3 | 2113.5 | 1937 | -49 | 0 | 0 | 1986 | 990.4369 | 990.4369 | 990.4369 | 2000.742 | 780 | 200 | 2980.742 | 74.52% | 95% | 0% | -56.0641 | 934.3729 | -2750 | -200 | -2015.6271 | 50.39% | 74.78% | 95% | 0% | 1986 | -49
[5 empty] | 2019-03-30 | 4 | 2114 | 1871 | -48 | 0 | 0 | 1919 | 885.4905 | 885.4905 | 885.4905 | 2000.742 | 780 | 200 | 2980.742 | 74.52% | 95% | 0% | -54.9199 | 830.5706 | -2750 | -200 | -2119.4294 | 52.99% | 74.77% | 95% | 0% | 1919 | -48
[5 empty] | 2019-03-30 | 5 | 2114.5 | 1840 | -48 | 0 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 2000.742 | 780 | 200 | 2980.742 | 74.52% | 95% | 0% | -54.9199 | 782.0133 | -2750 | -200 | -2167.9867 | 54.2% | 74.76% | 95% | 0% | 1888 | -48
[5 empty] | 2019-03-30 | 6 | 2115 | 1812 | -48 | 0 | 0 | 1860 | 793.075 | 793.075 | 793.075 | 1999.1756 | 780 | 200 | 2979.1756 | 74.48% | 95% | 0% | -54.9199 | 738.1551 | -2750 | -200 | -2211.8449 | 55.3% | 74.76% | 95% | 0% | 1860 | -48
[5 empty] | 2019-03-30 | 7 | 2115.5 | 1780 | -49 | 0 | 0 | 1829 | 744.5177 | 744.5177 | 744.5177 | 1999.1756 | 780 | 200 | 2979.1756 | 74.48% | 95% | 0% | -56.0641 | 688.4537 | -2750 | -200 | -2261.5463 | 56.54% | 74.76% | 95% | 0% | 1829 | -49
[5 empty] | 2019-03-30 | 8 | 2116 | 1746 | -51 | 0 | 0 | 1797 | 694.3941 | 694.3941 | 694.3941 | 1999.1756 | 780 | 200 | 2979.1756 | 74.48% | 95% | 0% | -58.3524 | 636.0417 | -2750 | -200 | -2313.9583 | 57.85% | 74.75% | 95% | 0% | 1797 | -51
[5 empty] | 2019-03-30 | 9 | 2116.5 | 1735 | -52 | 0 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 1997.6092 | 780 | 200 | 2977.6092 | 74.44% | 95% | 0% | -59.4966 | 619.2339 | -2750 | -200 | -2330.7661 | 58.27% | 74.75% | 95% | 0% | 1787 | -52
[5 empty] | 2019-03-30 | 10 | 2117 | 1723 | -53 | 0 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 1997.6092 | 780 | 200 | 2977.6092 | 74.44% | 95% | 0% | -60.6407 | 600.8597 | -2750 | -200 | -2349.1403 | 58.73% | 74.75% | 95% | 0% | 1776 | -53
[5 empty] | 2019-03-30 | 11 | 2117.5 | 1754 | -54 | 1 | 0 | 1808 | 711.6241 | 711.6241 | 711.6241 | 1997.6092 | 780 | 200 | 2977.6092 | 74.44% | 95% | 0% | -61.7849 | 649.8392 | -3550 | -400 | -3300.1608 | 82.5% | 74.75% | 95% | 0% | 1808 | -54
[5 empty] | 2019-03-30 | 12 | 2118 | 1774 | -55 | 1 | 0 | 1829 | 744.5177 | 744.5177 | 744.5177 | 1997.6092 | 780 | 200 | 2977.6092 | 74.44% | 95% | 0% | -62.9291 | 681.5887 | -3550 | -400 | -3268.4113 | 81.71% | 74.73% | 95% | 0% | 1829 | -55
[5 empty] | 2019-03-30 | 13 | 2118.5 | 1852 | -64 | 1 | 0 | 1916 | 880.7914 | 880.7914 | 880.7914 | 1997.6092 | 780 | 200 | 2977.6092 | 74.44% | 95% | 0% | -73.2265 | 807.5649 | -3550 | -400 | -3142.4351 | 78.56% | 74.72% | 95% | 0% | 1916 | -64
[5 empty] | 2019-03-30 | 14 | 2119 | 1893 | -98 | 1 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1997.6092 | 780 | 200 | 2977.6092 | 74.44% | 95% | 0% | -112.1281 | 886.1406 | -3550 | -400 | -3063.8594 | 76.6% | 74.71% | 95% | 0% | 1991 | -98
[5 empty] | 2019-03-30 | 15 | 2119.5 | 1932 | -146 | 1 | 0 | 2078 | 1134.5425 | 1134.5425 | 1134.5425 | 1997.6092 | 780 | 200 | 2977.6092 | 74.44% | 95% | 0% | -167.0481 | 967.4944 | -3550 | -400 | -2982.5056 | 74.56% | 74.71% | 95% | 0% | 2078 | -146
[5 empty] | 2019-03-30 | 16 | 2120 | 1923 | -203 | 1 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 1997.6092 | 780 | 200 | 2977.6092 | 74.44% | 95% | 0% | -232.2654 | 977.4625 | -3550 | -400 | -2972.5375 | 74.31% | 74.7% | 95% | 0% | 2126 | -203
[5 empty] | 2019-03-30 | 17 | 2120.5 | 1904 | -259 | 1 | 0 | 2163 | 1267.6834 | 1267.6834 | 1267.6834 | 1997.6092 | 780 | 200 | 2977.6092 | 74.44% | 95% | 0% | -296.3387 | 971.3448 | -3550 | -400 | -2978.6552 | 74.47% | 74.69% | 95% | 0% | 2163 | -259
[5 empty] | 2019-03-30 | 18 | 2121 | 1872 | -316 | 1 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 1997.6092 | 780 | 200 | 2977.6092 | 74.44% | 95% | 0% | -361.5561 | 945.2865 | -3550 | -400 | -3004.7135 | 75.12% | 74.69% | 95% | 0% | 2188 | -316
[5 empty] | 2019-03-30 | 19 | 2121.5 | 1819 | -378 | 1 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 1996.0429 | 780 | 200 | 2976.0429 | 74.4% | 95% | 0% | -432.4943 | 888.4455 | -3550 | -400 | -3061.5545 | 76.54% | 74.69% | 95% | 0% | 2197 | -378
[5 empty] | 2019-03-30 | 20 | 2122 | 1708 | -471 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 1996.0429 | 780 | 200 | 2976.0429 | 74.4% | 95% | 0% | -538.9016 | 753.8437 | -3550 | -400 | -3196.1563 | 79.9% | 74.68% | 95% | 0% | 2179 | -471
[5 empty] | 2019-03-30 | 21 | 2122.5 | 1637 | -523 | 1 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1996.0429 | 780 | 200 | 2976.0429 | 74.4% | 95% | 0% | -598.3982 | 664.5862 | -3550 | -400 | -3285.4138 | 82.14% | 74.67% | 95% | 0% | 2160 | -523
[5 empty] | 2019-03-30 | 22 | 2123 | 1552 | -564 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1996.0429 | 780 | 200 | 2976.0429 | 74.4% | 95% | 0% | -645.3089 | 548.7554 | -3550 | -400 | -3401.2446 | 85.03% | 74.67% | 95% | 0% | 2116 | -564
[5 empty] | 2019-03-30 | 23 | 2123.5 | 1466 | -606 | 1 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 1996.0429 | 780 | 200 | 2976.0429 | 74.4% | 95% | 0% | -693.3638 | 431.7804 | -3550 | -400 | -3518.2196 | 87.96% | 74.67% | 95% | 0% | 2072 | -606
[5 empty] | 2019-03-30 | 24 | 2124 | 1389 | -641 | 1 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 1996.0429 | 780 | 200 | 2976.0429 | 74.4% | 95% | 0% | -733.4096 | 325.9474 | -3550 | -400 | -3624.0526 | 90.6% | 74.67% | 95% | 0% | 2030 | -641
[5 empty] | 2019-03-30 | 25 | 2124.5 | 1355 | -648 | 1 | 0 | 2003 | 1017.0651 | 1017.0651 | 1017.0651 | 1996.0429 | 780 | 200 | 2976.0429 | 74.4% | 95% | 0% | -741.4188 | 275.6464 | -3550 | -400 | -3674.3536 | 91.86% | 74.64% | 95% | 0% | 2003 | -648
[5 empty] | 2019-03-30 | 26 | 2125 | 1334 | -634 | 1 | 0 | 1968 | 962.2424 | 962.2424 | 962.2424 | 1996.0429 | 780 | 200 | 2976.0429 | 74.4% | 95% | 0% | -725.4005 | 236.8419 | -3550 | -400 | -3713.1581 | 92.83% | 74.64% | 95% | 0% | 1968 | -634
[5 empty] | 2019-03-30 | 27 | 2125.5 | 1350 | -591 | 1 | 0 | 1941 | 919.9505 | 919.9505 | 919.9505 | 1996.0429 | 780 | 200 | 2976.0429 | 74.4% | 95% | 0% | -676.2014 | 243.7492 | -3550 | -400 | -3706.2508 | 92.66% | 74.63% | 95% | 0% | 1941 | -591
[5 empty] | 2019-03-30 | 28 | 2126 | 1369 | -560 | 1 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 1994.4765 | 780 | 200 | 2974.4765 | 74.36% | 95% | 0% | -640.7323 | 260.4219 | -3550 | -400 | -3689.5781 | 92.24% | 74.63% | 95% | 0% | 1929 | -560
[5 empty] | 2019-03-30 | 29 | 2126.5 | 1388 | -533 | 1 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 1994.4765 | 780 | 200 | 2974.4765 | 74.36% | 95% | 0% | -609.8398 | 278.7834 | -3550 | -400 | -3671.2166 | 91.78% | 74.59% | 95% | 0% | 1921 | -533
[5 empty] | 2019-03-30 | 30 | 2127 | 1451 | -491 | 1 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 1994.4765 | 780 | 200 | 2974.4765 | 74.36% | 95% | 0% | -561.7849 | 359.732 | -3550 | -400 | -3590.268 | 89.76% | 74.58% | 95% | 0% | 1942 | -491
[5 empty] | 2019-03-30 | 31 | 2127.5 | 1559 | -430 | 1 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 1994.4765 | 780 | 200 | 2974.4765 | 74.36% | 95% | 0% | -491.9908 | 503.1452 | -3550 | -400 | -3446.8548 | 86.17% | 74.58% | 95% | 0% | 1989 | -430
[5 empty] | 2019-03-30 | 32 | 2128 | 1692 | -371 | 1 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 1994.4765 | 780 | 200 | 2974.4765 | 74.36% | 95% | 0% | -424.4851 | 686.5619 | -3550 | -400 | -3263.4381 | 81.59% | 74.58% | 95% | 0% | 2063 | -371
[5 empty] | 2019-03-30 | 33 | 2128.5 | 1854 | -308 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 1994.4765 | 780 | 200 | 2974.4765 | 74.36% | 95% | 0% | -352.4027 | 913.7143 | -3550 | -400 | -3036.2857 | 75.91% | 74.57% | 95% | 0% | 2162 | -308
[5 empty] | 2019-03-30 | 34 | 2129 | 2031 | -236 | 1 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 1992.9101 | 780 | 200 | 2972.9101 | 74.32% | 95% | 0% | -270.0229 | 1160.5624 | -3550 | -400 | -2789.4376 | 69.74% | 74.57% | 95% | 0% | 2267 | -236
[5 empty] | 2019-03-30 | 35 | 2129.5 | 2229 | -167 | 1 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 1992.9101 | 780 | 200 | 2972.9101 | 74.32% | 95% | 0% | -191.0755 | 1441.5708 | -3550 | -400 | -2508.4292 | 62.71% | 74.56% | 95% | 0% | 2396 | -167
[5 empty] | 2019-03-30 | 36 | 2130 | 2388 | -108 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 1992.9101 | 780 | 200 | 2972.9101 | 74.32% | 95% | 0% | -123.5698 | 1665.713 | -3550 | -400 | -2284.287 | 57.11% | 74.54% | 95% | 0% | 2496 | -108
[5 empty] | 2019-03-30 | 37 | 2130.5 | 2496 | -73 | 1 | 0 | 2569 | 1903.6274 | 1903.6274 | 1903.6274 | 1992.9101 | 780 | 200 | 2972.9101 | 74.32% | 95% | 0% | -83.524 | 1820.1033 | -3550 | -400 | -2129.8967 | 53.25% | 74.53% | 95% | 0% | 2569 | -73
[5 empty] | 2019-03-30 | 38 | 2131 | 2580 | -64 | 1 | 0 | 2644 | 2021.1047 | 2021.1047 | 2021.1047 | 1992.9101 | 780 | 200 | 2972.9101 | 74.32% | 95% | 0% | -73.2265 | 1947.8782 | -3550 | -400 | -2002.1218 | 50.05% | 74.52% | 95% | 0% | 2644 | -64
[5 empty] | 2019-03-30 | 39 | 2131.5 | 2596 | -64 | 1 | 0 | 2660 | 2046.1665 | 2046.1665 | 2046.1665 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -73.2265 | 1972.94 | -3550 | -400 | -1977.06 | 49.43% | 74.52% | 95% | 0% | 2660 | -64
[5 empty] | 2019-03-30 | 40 | 2132 | 2550 | -64 | 0 | 0 | 2614 | 1974.1138 | 1974.1138 | 1974.1138 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -73.2265 | 1900.8872 | -2750 | -200 | -1049.1128 | 26.23% | 74.51% | 95% | 0% | 2614 | -64
[5 empty] | 2019-03-30 | 41 | 2132.5 | 2481 | -65 | 0 | 0 | 2546 | 1867.601 | 1867.601 | 1867.601 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -74.3707 | 1793.2303 | -2750 | -200 | -1156.7697 | 28.92% | 74.51% | 95% | 0% | 2546 | -65
[5 empty] | 2019-03-30 | 42 | 2133 | 2417 | -66 | 0 | 0 | 2483 | 1768.92 | 1768.92 | 1768.92 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -75.5149 | 1693.4052 | -2750 | -200 | -1256.5948 | 31.41% | 74.51% | 95% | 0% | 2483 | -66
[5 empty] | 2019-03-30 | 43 | 2133.5 | 2352 | -66 | 0 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -75.5149 | 1591.5915 | -2750 | -200 | -1358.4085 | 33.96% | 74.51% | 95% | 0% | 2418 | -66
[5 empty] | 2019-03-30 | 44 | 2134 | 2260 | -66 | 0 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -75.5149 | 1447.486 | -2750 | -200 | -1502.514 | 37.56% | 74.5% | 95% | 0% | 2326 | -66
[5 empty] | 2019-03-30 | 45 | 2134.5 | 2151 | -66 | 1 | 0 | 2217 | 1352.2671 | 1352.2671 | 1352.2671 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -75.5149 | 1276.7522 | -3550 | -400 | -2673.2478 | 66.83% | 74.49% | 95% | 0% | 2217 | -66
[5 empty] | 2019-03-30 | 46 | 2135 | 2068 | -66 | 1 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -75.5149 | 1146.744 | -3550 | -400 | -2803.256 | 70.08% | 74.49% | 95% | 0% | 2134 | -66
[5 empty] | 2019-03-30 | 47 | 2135.5 | 1952 | -64 | 1 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -73.2265 | 964.2013 | -3550 | -400 | -2985.7987 | 74.64% | 74.48% | 95% | 0% | 2016 | -64
[5 empty] | 2019-03-30 | 48 | 2136 | 1875 | -63 | 1 | 0 | 1938 | 915.2514 | 915.2514 | 915.2514 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -72.0824 | 843.1691 | -3550 | -400 | -3106.8309 | 77.67% | 74.48% | 95% | 0% | 1938 | -63
[5 empty] | 2019-03-31 | 1 | 2136.5 | 1842 | -64 | 1 | 0 | 1906 | 865.1278 | 865.1278 | 865.1278 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -73.2265 | 791.9012 | -3550 | -400 | -3158.0988 | 78.95% | 74.48% | 95% | 0% | 1906 | -64
[5 empty] | 2019-03-31 | 2 | 2137 | 1847 | -65 | 1 | 0 | 1912 | 874.526 | 874.526 | 874.526 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -74.3707 | 800.1553 | -3550 | -400 | -3149.8447 | 78.75% | 74.48% | 95% | 0% | 1912 | -65
[5 empty] | 2019-03-31 | 3 | 2137.5 | 1816 | -66 | 1 | 0 | 1882 | 827.535 | 827.535 | 827.535 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -75.5149 | 752.0202 | -3550 | -400 | -3197.9798 | 79.95% | 74.47% | 95% | 0% | 1882 | -66
[5 empty] | 2019-03-31 | 4 | 2138 | 1748 | -68 | 1 | 0 | 1816 | 724.155 | 724.155 | 724.155 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -77.8032 | 646.3518 | -3550 | -400 | -3303.6482 | 82.59% | 74.47% | 95% | 0% | 1816 | -68
[5 empty] | 2019-03-31 | 5 | 2138.5 | 1701 | -69 | 1 | 0 | 1770 | 652.1022 | 652.1022 | 652.1022 | 1991.3438 | 780 | 200 | 2971.3438 | 74.28% | 95% | 0% | -78.9474 | 573.1549 | -3550 | -400 | -3376.8451 | 84.42% | 74.47% | 95% | 0% | 1770 | -69
[5 empty] | 2019-03-31 | 6 | 2139 | 1671 | -69 | 1 | 0 | 1740 | 605.1113 | 605.1113 | 605.1113 | 1989.7774 | 780 | 200 | 2969.7774 | 74.24% | 95% | 0% | -78.9474 | 526.1639 | -3550 | -400 | -3423.8361 | 85.6% | 74.47% | 95% | 0% | 1740 | -69
[5 empty] | 2019-03-31 | 7 | 2139.5 | 1633 | -71 | 1 | 0 | 1704 | 548.7222 | 548.7222 | 548.7222 | 1989.7774 | 780 | 200 | 2969.7774 | 74.24% | 95% | 0% | -81.2357 | 467.4865 | -3550 | -400 | -3482.5135 | 87.06% | 74.46% | 95% | 0% | 1704 | -71
[5 empty] | 2019-03-31 | 8 | 2140 | 1603 | -73 | 1 | 0 | 1676 | 504.864 | 504.864 | 504.864 | 1989.7774 | 780 | 200 | 2969.7774 | 74.24% | 95% | 0% | -83.524 | 421.3399 | -3550 | -400 | -3528.6601 | 88.22% | 74.46% | 95% | 0% | 1676 | -73
[5 empty] | 2019-03-31 | 9 | 2140.5 | 1599 | -74 | 1 | 0 | 1673 | 500.1649 | 500.1649 | 500.1649 | 1989.7774 | 780 | 200 | 2969.7774 | 74.24% | 95% | 0% | -84.6682 | 415.4967 | -3550 | -400 | -3534.5033 | 88.36% | 74.46% | 95% | 0% | 1673 | -74
[5 empty] | 2019-03-31 | 10 | 2141 | 1601 | -74 | 1 | 0 | 1675 | 503.2976 | 503.2976 | 503.2976 | 1989.7774 | 780 | 200 | 2969.7774 | 74.24% | 95% | 0% | -84.6682 | 418.6294 | -3550 | -400 | -3531.3706 | 88.28% | 74.46% | 95% | 0% | 1675 | -74
[5 empty] | 2019-03-31 | 11 | 2141.5 | 1656 | -76 | 1 | 0 | 1732 | 592.5804 | 592.5804 | 592.5804 | 1989.7774 | 780 | 200 | 2969.7774 | 74.24% | 95% | 0% | -86.9565 | 505.6239 | -3550 | -400 | -3444.3761 | 86.11% | 74.45% | 95% | 0% | 1732 | -76
[5 empty] | 2019-03-31 | 12 | 2142 | 1672 | -77 | 1 | 0 | 1749 | 619.2086 | 619.2086 | 619.2086 | 1989.7774 | 780 | 200 | 2969.7774 | 74.24% | 95% | 0% | -88.1007 | 531.1079 | -3550 | -400 | -3418.8921 | 85.47% | 74.45% | 95% | 0% | 1749 | -77
[5 empty] | 2019-03-31 | 13 | 2142.5 | 1740 | -83 | 1 | 0 | 1823 | 735.1195 | 735.1195 | 735.1195 | 1988.211 | 780 | 200 | 2968.211 | 74.21% | 95% | 0% | -94.9657 | 640.1539 | -3550 | -400 | -3309.8461 | 82.75% | 74.45% | 95% | 0% | 1823 | -83
[5 empty] | 2019-03-31 | 14 | 2143 | 1794 | -102 | 1 | 0 | 1896 | 849.4641 | 849.4641 | 849.4641 | 1988.211 | 780 | 200 | 2968.211 | 74.21% | 95% | 0% | -116.7048 | 732.7593 | -3550 | -400 | -3217.2407 | 80.43% | 74.44% | 95% | 0% | 1896 | -102
[5 empty] | 2019-03-31 | 15 | 2143.5 | 1852 | -132 | 1 | 0 | 1984 | 987.3042 | 987.3042 | 987.3042 | 1988.211 | 780 | 200 | 2968.211 | 74.21% | 95% | 0% | -151.0297 | 836.2745 | -3550 | -400 | -3113.7255 | 77.84% | 74.44% | 95% | 0% | 1984 | -132
[5 empty] | 2019-03-31 | 16 | 2144 | 1865 | -173 | 1 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 1988.211 | 780 | 200 | 2968.211 | 74.21% | 95% | 0% | -197.9405 | 873.9474 | -3550 | -400 | -3076.0526 | 76.9% | 74.43% | 95% | 0% | 2038 | -173
[5 empty] | 2019-03-31 | 17 | 2144.5 | 1891 | -221 | 1 | 0 | 2112 | 1187.7988 | 1187.7988 | 1187.7988 | 1986.6447 | 780 | 200 | 2966.6447 | 74.17% | 95% | 0% | -252.8604 | 934.9384 | -3550 | -400 | -3015.0616 | 75.38% | 74.42% | 95% | 0% | 2112 | -221
[5 empty] | 2019-03-31 | 18 | 2145 | 1866 | -272 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1986.6447 | 780 | 200 | 2966.6447 | 74.17% | 95% | 0% | -311.2128 | 917.3115 | -3550 | -400 | -3032.6885 | 75.82% | 74.42% | 95% | 0% | 2138 | -272
[5 empty] | 2019-03-31 | 19 | 2145.5 | 1831 | -325 | 1 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 1986.6447 | 780 | 200 | 2966.6447 | 74.17% | 95% | 0% | -371.8535 | 884.8653 | -3550 | -400 | -3065.1347 | 76.63% | 74.42% | 95% | 0% | 2156 | -325
[5 empty] | 2019-03-31 | 20 | 2146 | 1777 | -368 | 1 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 1986.6447 | 780 | 200 | 2966.6447 | 74.17% | 95% | 0% | -421.0526 | 818.4362 | -3550 | -400 | -3131.5638 | 78.29% | 74.42% | 95% | 0% | 2145 | -368
[5 empty] | 2019-03-31 | 21 | 2146.5 | 1726 | -405 | 1 | 0 | 2131 | 1217.5598 | 1217.5598 | 1217.5598 | 1986.6447 | 780 | 200 | 2966.6447 | 74.17% | 95% | 0% | -463.3867 | 754.173 | -3550 | -400 | -3195.827 | 79.9% | 74.41% | 95% | 0% | 2131 | -405
[5 empty] | 2019-03-31 | 22 | 2147 | 1672 | -443 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 1986.6447 | 780 | 200 | 2966.6447 | 74.17% | 95% | 0% | -506.865 | 685.633 | -3550 | -400 | -3264.367 | 81.61% | 74.41% | 95% | 0% | 2115 | -443
[5 empty] | 2019-03-31 | 23 | 2147.5 | 1630 | -466 | 1 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 1986.6447 | 780 | 200 | 2966.6447 | 74.17% | 95% | 0% | -533.1808 | 629.5562 | -3550 | -400 | -3320.4438 | 83.01% | 74.41% | 95% | 0% | 2096 | -466
[5 empty] | 2019-03-31 | 24 | 2148 | 1604 | -479 | 1 | 0 | 2083 | 1142.3743 | 1142.3743 | 1142.3743 | 1986.6447 | 780 | 200 | 2966.6447 | 74.17% | 95% | 0% | -548.0549 | 594.3194 | -3550 | -400 | -3355.6806 | 83.89% | 74.4% | 95% | 0% | 2083 | -479
[5 empty] | 2019-03-31 | 25 | 2148.5 | 1569 | -481 | 1 | 0 | 2050 | 1090.6843 | 1090.6843 | 1090.6843 | 1986.6447 | 780 | 200 | 2966.6447 | 74.17% | 95% | 0% | -550.3432 | 540.341 | -3550 | -400 | -3409.659 | 85.24% | 74.4% | 95% | 0% | 2050 | -481
[5 empty] | 2019-03-31 | 26 | 2149 | 1551 | -473 | 1 | 0 | 2024 | 1049.9588 | 1049.9588 | 1049.9588 | 1985.0783 | 780 | 200 | 2965.0783 | 74.13% | 95% | 0% | -541.1899 | 508.7688 | -3550 | -400 | -3441.2312 | 86.03% | 74.39% | 95% | 0% | 2024 | -473
[5 empty] | 2019-03-31 | 27 | 2149.5 | 1555 | -463 | 1 | 0 | 2018 | 1040.5606 | 1040.5606 | 1040.5606 | 1985.0783 | 780 | 200 | 2965.0783 | 74.13% | 95% | 0% | -529.7483 | 510.8123 | -3550 | -400 | -3439.1877 | 85.98% | 74.39% | 95% | 0% | 2018 | -463
[5 empty] | 2019-03-31 | 28 | 2150 | 1550 | -447 | 1 | 0 | 1997 | 1007.6669 | 1007.6669 | 1007.6669 | 1985.0783 | 780 | 200 | 2965.0783 | 74.13% | 95% | 0% | -511.4416 | 496.2253 | -3550 | -400 | -3453.7747 | 86.34% | 74.39% | 95% | 0% | 1997 | -447
[5 empty] | 2019-03-31 | 29 | 2150.5 | 1581 | -427 | 1 | 0 | 2008 | 1024.8969 | 1024.8969 | 1024.8969 | 1985.0783 | 780 | 200 | 2965.0783 | 74.13% | 95% | 0% | -488.5584 | 536.3386 | -3550 | -400 | -3413.6614 | 85.34% | 74.39% | 95% | 0% | 2008 | -427
[5 empty] | 2019-03-31 | 30 | 2151 | 1638 | -400 | 1 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 1985.0783 | 780 | 200 | 2965.0783 | 74.13% | 95% | 0% | -457.6659 | 614.222 | -3550 | -400 | -3335.778 | 83.39% | 74.39% | 95% | 0% | 2038 | -400
[5 empty] | 2019-03-31 | 31 | 2151.5 | 1718 | -368 | 1 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 1985.0783 | 780 | 200 | 2965.0783 | 74.13% | 95% | 0% | -421.0526 | 726.0207 | -3550 | -400 | -3223.9793 | 80.6% | 74.38% | 95% | 0% | 2086 | -368
[5 empty] | 2019-03-31 | 32 | 2152 | 1834 | -327 | 1 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 1983.512 | 780 | 200 | 2963.512 | 74.09% | 95% | 0% | -374.1419 | 890.4088 | -3550 | -400 | -3059.5912 | 76.49% | 74.37% | 95% | 0% | 2161 | -327
[5 empty] | 2019-03-31 | 33 | 2152.5 | 1963 | -279 | 1 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 1983.512 | 780 | 200 | 2963.512 | 74.09% | 95% | 0% | -319.222 | 1072.2042 | -3550 | -400 | -2877.7958 | 71.94% | 74.36% | 95% | 0% | 2242 | -279
[5 empty] | 2019-03-31 | 34 | 2153 | 2082 | -230 | 1 | 0 | 2312 | 1501.0717 | 1501.0717 | 1501.0717 | 1983.512 | 780 | 200 | 2963.512 | 74.09% | 95% | 0% | -263.1579 | 1237.9138 | -3550 | -400 | -2712.0862 | 67.8% | 74.36% | 95% | 0% | 2312 | -230
[5 empty] | 2019-03-31 | 35 | 2153.5 | 2212 | -173 | 1 | 0 | 2385 | 1615.4163 | 1615.4163 | 1615.4163 | 1983.512 | 780 | 200 | 2963.512 | 74.09% | 95% | 0% | -197.9405 | 1417.4758 | -3550 | -400 | -2532.5242 | 63.31% | 74.36% | 95% | 0% | 2385 | -173
[5 empty] | 2019-03-31 | 36 | 2154 | 2327 | -125 | 1 | 0 | 2452 | 1720.3627 | 1720.3627 | 1720.3627 | 1983.512 | 780 | 200 | 2963.512 | 74.09% | 95% | 0% | -143.0206 | 1577.3421 | -3550 | -400 | -2372.6579 | 59.32% | 74.35% | 95% | 0% | 2452 | -125
[5 empty] | 2019-03-31 | 37 | 2154.5 | 2410 | -93 | 1 | 0 | 2503 | 1800.2473 | 1800.2473 | 1800.2473 | 1983.512 | 780 | 200 | 2963.512 | 74.09% | 95% | 0% | -106.4073 | 1693.84 | -3550 | -400 | -2256.16 | 56.4% | 74.35% | 95% | 0% | 2503 | -93
[5 empty] | 2019-03-31 | 38 | 2155 | 2497 | -85 | 1 | 0 | 2582 | 1923.9901 | 1923.9901 | 1923.9901 | 1983.512 | 780 | 200 | 2963.512 | 74.09% | 95% | 0% | -97.254 | 1826.7361 | -3550 | -400 | -2123.2639 | 53.08% | 74.35% | 95% | 0% | 2582 | -85
[5 empty] | 2019-03-31 | 39 | 2155.5 | 2588 | -86 | 1 | 0 | 2674 | 2068.0956 | 2068.0956 | 2068.0956 | 1983.512 | 780 | 200 | 2963.512 | 74.09% | 95% | 0% | -98.3982 | 1969.6975 | -3550 | -400 | -1980.3025 | 49.51% | 74.35% | 95% | 0% | 2674 | -86
[5 empty] | 2019-03-31 | 40 | 2156 | 2525 | -87 | 0 | 0 | 2612 | 1970.981 | 1970.981 | 1970.981 | 1983.512 | 780 | 200 | 2963.512 | 74.09% | 95% | 0% | -99.5423 | 1871.4387 | -2750 | -200 | -1078.5613 | 26.96% | 74.35% | 95% | 0% | 2612 | -87
[5 empty] | 2019-03-31 | 41 | 2156.5 | 2452 | -88 | 0 | 0 | 2540 | 1858.2028 | 1858.2028 | 1858.2028 | 1983.512 | 780 | 200 | 2963.512 | 74.09% | 95% | 0% | -100.6865 | 1757.5163 | -2750 | -200 | -1192.4837 | 29.81% | 74.34% | 95% | 0% | 2540 | -88
[5 empty] | 2019-03-31 | 42 | 2157 | 2330 | -90 | 0 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 1983.512 | 780 | 200 | 2963.512 | 74.09% | 95% | 0% | -102.9748 | 1567.2642 | -2750 | -200 | -1382.7358 | 34.57% | 74.34% | 95% | 0% | 2420 | -90
[5 empty] | 2019-03-31 | 43 | 2157.5 | 2205 | -91 | 0 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1981.9456 | 780 | 200 | 2961.9456 | 74.05% | 95% | 0% | -104.119 | 1371.8909 | -2750 | -200 | -1578.1091 | 39.45% | 74.33% | 95% | 0% | 2296 | -91
[5 empty] | 2019-03-31 | 44 | 2158 | 2063 | -93 | 0 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 1981.9456 | 780 | 200 | 2961.9456 | 74.05% | 95% | 0% | -106.4073 | 1150.3116 | -2750 | -200 | -1799.6884 | 44.99% | 74.32% | 95% | 0% | 2156 | -93
[5 empty] | 2019-03-31 | 45 | 2158.5 | 1903 | -95 | 0 | 0 | 1998 | 1009.2333 | 1009.2333 | 1009.2333 | 1981.9456 | 780 | 200 | 2961.9456 | 74.05% | 95% | 0% | -108.6957 | 900.5377 | -2750 | -200 | -2049.4623 | 51.24% | 74.31% | 95% | 0% | 1998 | -95
[5 empty] | 2019-03-31 | 46 | 2159 | 1795 | -97 | 0 | 0 | 1892 | 843.1987 | 843.1987 | 843.1987 | 1981.9456 | 780 | 200 | 2961.9456 | 74.05% | 95% | 0% | -110.984 | 732.2147 | -2750 | -200 | -2217.7853 | 55.44% | 74.31% | 95% | 0% | 1892 | -97
[5 empty] | 2019-04-01 | 1 | 2159.5 | 1708 | -99 | 0 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 1981.9456 | 780 | 200 | 2961.9456 | 74.05% | 95% | 0% | -113.2723 | 596.7854 | -2750 | -200 | -2353.2146 | 58.83% | 74.3% | 95% | 0% | 1807 | -99
[5 empty] | 2019-04-01 | 2 | 2160 | 1662 | -101 | 0 | 0 | 1763 | 641.1377 | 641.1377 | 641.1377 | 1981.9456 | 780 | 200 | 2961.9456 | 74.05% | 95% | 0% | -115.5606 | 525.577 | -2750 | -200 | -2424.423 | 60.61% | 74.3% | 95% | 0% | 1763 | -101
[5 empty] | 2019-04-01 | 3 | 2160.5 | 1673 | -100 | 0 | 0 | 1773 | 656.8013 | 656.8013 | 656.8013 | 1980.3792 | 780 | 200 | 2960.3792 | 74.01% | 95% | 0% | -114.4165 | 542.3848 | -2750 | -200 | -2407.6152 | 60.19% | 74.29% | 95% | 0% | 1773 | -100
[5 empty] | 2019-04-01 | 4 | 2161 | 1730 | -100 | 0 | 0 | 1830 | 746.0841 | 746.0841 | 746.0841 | 1980.3792 | 780 | 200 | 2960.3792 | 74.01% | 95% | 0% | -114.4165 | 631.6676 | -2750 | -200 | -2318.3324 | 57.96% | 74.29% | 95% | 0% | 1830 | -100
[5 empty] | 2019-04-01 | 5 | 2161.5 | 1732 | -100 | 0 | 0 | 1832 | 749.2168 | 749.2168 | 749.2168 | 1980.3792 | 780 | 200 | 2960.3792 | 74.01% | 95% | 0% | -114.4165 | 634.8003 | -2750 | -200 | -2315.1997 | 57.88% | 74.29% | 95% | 0% | 1832 | -100
[5 empty] | 2019-04-01 | 6 | 2162 | 1711 | -100 | 0 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1980.3792 | 780 | 200 | 2960.3792 | 74.01% | 95% | 0% | -114.4165 | 601.9067 | -2750 | -200 | -2348.0933 | 58.7% | 74.28% | 95% | 0% | 1811 | -100
[5 empty] | 2019-04-01 | 7 | 2162.5 | 1690 | -99 | 0 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 1978.8129 | 780 | 200 | 2958.8129 | 73.97% | 95% | 0% | -113.2723 | 568.5908 | -2750 | -200 | -2381.4092 | 59.54% | 74.28% | 95% | 0% | 1789 | -99
[5 empty] | 2019-04-01 | 8 | 2163 | 1673 | -98 | 0 | 0 | 1771 | 653.6686 | 653.6686 | 653.6686 | 1978.8129 | 780 | 200 | 2958.8129 | 73.97% | 95% | 0% | -112.1281 | 541.5404 | -2750 | -200 | -2408.4596 | 60.21% | 74.27% | 95% | 0% | 1771 | -98
[5 empty] | 2019-04-01 | 9 | 2163.5 | 1674 | -99 | 0 | 0 | 1773 | 656.8013 | 656.8013 | 656.8013 | 1978.8129 | 780 | 200 | 2958.8129 | 73.97% | 95% | 0% | -113.2723 | 543.529 | -2750 | -200 | -2406.471 | 60.16% | 74.26% | 95% | 0% | 1773 | -99
[5 empty] | 2019-04-01 | 10 | 2164 | 1695 | -100 | 0 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 1978.8129 | 780 | 200 | 2958.8129 | 73.97% | 95% | 0% | -114.4165 | 576.8449 | -2750 | -200 | -2373.1551 | 59.33% | 74.26% | 95% | 0% | 1795 | -100
[5 empty] | 2019-04-01 | 11 | 2164.5 | 1742 | -100 | 0 | 0 | 1842 | 764.8805 | 764.8805 | 764.8805 | 1978.8129 | 780 | 200 | 2958.8129 | 73.97% | 95% | 0% | -114.4165 | 650.464 | -2750 | -200 | -2299.536 | 57.49% | 74.25% | 95% | 0% | 1842 | -100
[5 empty] | 2019-04-01 | 12 | 2165 | 1847 | -100 | 0 | 0 | 1947 | 929.3487 | 929.3487 | 929.3487 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -114.4165 | 814.9322 | -2750 | -200 | -2135.0678 | 53.38% | 74.24% | 95% | 0% | 1947 | -100
[5 empty] | 2019-04-01 | 13 | 2165.5 | 2086 | -100 | 0 | 0 | 2186 | 1303.7098 | 1303.7098 | 1303.7098 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -114.4165 | 1189.2933 | -2750 | -200 | -1760.7067 | 44.02% | 74.24% | 95% | 0% | 2186 | -100
[5 empty] | 2019-04-01 | 14 | 2166 | 2291 | -104 | 0 | 0 | 2395 | 1631.08 | 1631.08 | 1631.08 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -118.9931 | 1512.0868 | -2750 | -200 | -1437.9132 | 35.95% | 74.24% | 95% | 0% | 2395 | -104
[5 empty] | 2019-04-01 | 15 | 2166.5 | 2511 | -136 | 0 | 0 | 2647 | 2025.8038 | 2025.8038 | 2025.8038 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -155.6064 | 1870.1974 | -2750 | -200 | -1079.8026 | 27% | 74.23% | 95% | 0% | 2647 | -136
[5 empty] | 2019-04-01 | 16 | 2167 | 2595 | -176 | 1 | 0 | 2771 | 2220.033 | 2220.033 | 2220.033 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -201.373 | 2018.66 | -3550 | -400 | -1931.34 | 48.28% | 74.22% | 95% | 0% | 2771 | -176
[5 empty] | 2019-04-01 | 17 | 2167.5 | 2550 | -234 | 1 | 0 | 2784 | 2240.3957 | 2240.3957 | 2240.3957 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -267.7346 | 1972.6612 | -3550 | -400 | -1977.3388 | 49.43% | 74.22% | 95% | 0% | 2784 | -234
[5 empty] | 2019-04-01 | 18 | 2168 | 2460 | -306 | 1 | 0 | 2766 | 2212.2012 | 2212.2012 | 2212.2012 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -350.1144 | 1862.0867 | -3550 | -400 | -2087.9133 | 52.2% | 74.22% | 95% | 0% | 2766 | -306
[5 empty] | 2019-04-01 | 19 | 2168.5 | 2361 | -376 | 1 | 0 | 2737 | 2166.7766 | 2166.7766 | 2166.7766 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -430.2059 | 1736.5706 | -3550 | -400 | -2213.4294 | 55.34% | 74.21% | 95% | 0% | 2737 | -376
[5 empty] | 2019-04-01 | 20 | 2169 | 2208 | -455 | 1 | 0 | 2663 | 2050.8656 | 2050.8656 | 2050.8656 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -520.595 | 1530.2707 | -3550 | -400 | -2419.7293 | 60.49% | 74.21% | 95% | 0% | 2663 | -455
[5 empty] | 2019-04-01 | 21 | 2169.5 | 2058 | -519 | 1 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -593.8215 | 1322.3368 | -3550 | -400 | -2627.6632 | 65.69% | 74.2% | 95% | 0% | 2577 | -519
[5 empty] | 2019-04-01 | 22 | 2170 | 1907 | -594 | 1 | 0 | 2501 | 1797.1146 | 1797.1146 | 1797.1146 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -679.6339 | 1117.4807 | -3550 | -400 | -2832.5193 | 70.81% | 74.19% | 95% | 0% | 2501 | -594
[5 empty] | 2019-04-01 | 23 | 2170.5 | 1819 | -643 | 1 | 0 | 2462 | 1736.0264 | 1736.0264 | 1736.0264 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -735.6979 | 1000.3284 | -3550 | -400 | -2949.6716 | 73.74% | 74.18% | 95% | 0% | 2462 | -643
[5 empty] | 2019-04-01 | 24 | 2171 | 1736 | -682 | 1 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 1977.2465 | 780 | 200 | 2957.2465 | 73.93% | 95% | 0% | -780.3204 | 886.786 | -3550 | -400 | -3063.214 | 76.58% | 74.18% | 95% | 0% | 2418 | -682
[5 empty] | 2019-04-01 | 25 | 2171.5 | 1673 | -723 | 1 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -827.2311 | 805.4152 | -3550 | -400 | -3144.5848 | 78.61% | 74.18% | 95% | 0% | 2396 | -723
[5 empty] | 2019-04-01 | 26 | 2172 | 1614 | -741 | 1 | 0 | 2355 | 1568.4254 | 1568.4254 | 1568.4254 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -847.8261 | 720.5993 | -3550 | -400 | -3229.4007 | 80.74% | 74.18% | 95% | 0% | 2355 | -741
[5 empty] | 2019-04-01 | 27 | 2172.5 | 1555 | -762 | 1 | 0 | 2317 | 1508.9035 | 1508.9035 | 1508.9035 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -871.8535 | 637.05 | -3550 | -400 | -3312.95 | 82.82% | 74.17% | 95% | 0% | 2317 | -762
[5 empty] | 2019-04-01 | 28 | 2173 | 1601 | -680 | 1 | 0 | 2281 | 1452.5144 | 1452.5144 | 1452.5144 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -778.032 | 674.4824 | -3550 | -400 | -3275.5176 | 81.89% | 74.17% | 95% | 0% | 2281 | -680
[5 empty] | 2019-04-01 | 29 | 2173.5 | 1626 | -654 | 1 | 0 | 2280 | 1450.9481 | 1450.9481 | 1450.9481 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -748.2838 | 702.6643 | -3550 | -400 | -3247.3357 | 81.18% | 74.17% | 95% | 0% | 2280 | -654
[5 empty] | 2019-04-01 | 30 | 2174 | 1650 | -630 | 1 | 0 | 2280 | 1450.9481 | 1450.9481 | 1450.9481 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -720.8238 | 730.1243 | -3550 | -400 | -3219.8757 | 80.5% | 74.16% | 95% | 0% | 2280 | -630
[5 empty] | 2019-04-01 | 31 | 2174.5 | 1689 | -593 | 1 | 0 | 2282 | 1454.0808 | 1454.0808 | 1454.0808 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -678.4897 | 775.5911 | -3550 | -400 | -3174.4089 | 79.36% | 74.16% | 95% | 0% | 2282 | -593
[5 empty] | 2019-04-01 | 32 | 2175 | 1819 | -534 | 1 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -610.984 | 954.3087 | -3550 | -400 | -2995.6913 | 74.89% | 74.16% | 95% | 0% | 2353 | -534
[5 empty] | 2019-04-01 | 33 | 2175.5 | 1967 | -476 | 1 | 0 | 2443 | 1706.2655 | 1706.2655 | 1706.2655 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -544.6224 | 1161.643 | -3550 | -400 | -2788.357 | 69.71% | 74.15% | 95% | 0% | 2443 | -476
[5 empty] | 2019-04-01 | 34 | 2176 | 2143 | -412 | 1 | 0 | 2555 | 1881.6983 | 1881.6983 | 1881.6983 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -471.3959 | 1410.3024 | -3550 | -400 | -2539.6976 | 63.49% | 74.15% | 95% | 0% | 2555 | -412
[5 empty] | 2019-04-01 | 35 | 2176.5 | 2312 | -342 | 1 | 0 | 2654 | 2036.7683 | 2036.7683 | 2036.7683 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -391.3043 | 1645.464 | -3550 | -400 | -2304.536 | 57.61% | 74.14% | 95% | 0% | 2654 | -342
[5 empty] | 2019-04-01 | 36 | 2177 | 2441 | -270 | 1 | 0 | 2711 | 2126.0511 | 2126.0511 | 2126.0511 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -308.9245 | 1817.1266 | -3550 | -400 | -2132.8734 | 53.32% | 74.14% | 95% | 0% | 2711 | -270
[5 empty] | 2019-04-01 | 37 | 2177.5 | 2579 | -202 | 1 | 0 | 2781 | 2235.6966 | 2235.6966 | 2235.6966 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -231.1213 | 2004.5753 | -3550 | -400 | -1945.4247 | 48.64% | 74.14% | 95% | 0% | 2781 | -202
[5 empty] | 2019-04-01 | 38 | 2178 | 2675 | -146 | 1 | 0 | 2821 | 2298.3512 | 2298.3512 | 2298.3512 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -167.0481 | 2131.3031 | -3550 | -400 | -1818.6969 | 45.47% | 74.14% | 95% | 0% | 2821 | -146
[5 empty] | 2019-04-01 | 39 | 2178.5 | 2758 | -112 | 1 | 0 | 2870 | 2375.1031 | 2375.1031 | 2375.1031 | 1975.6801 | 780 | 200 | 2955.6801 | 73.89% | 95% | 0% | -128.1465 | 2246.9566 | -3550 | -400 | -1703.0434 | 42.58% | 74.14% | 95% | 0% | 2870 | -112
[5 empty] | 2019-04-01 | 40 | 2179 | 2802 | -100 | 1 | 0 | 2902 | 2425.2267 | 2425.2267 | 2425.2267 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -114.4165 | 2310.8102 | -3550 | -400 | -1639.1898 | 40.98% | 74.14% | 95% | 0% | 2902 | -100
[5 empty] | 2019-04-01 | 41 | 2179.5 | 2795 | -99 | 1 | 0 | 2894 | 2412.6958 | 2412.6958 | 2412.6958 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -113.2723 | 2299.4235 | -3550 | -400 | -1650.5765 | 41.26% | 74.14% | 95% | 0% | 2894 | -99
[5 empty] | 2019-04-01 | 42 | 2180 | 2744 | -98 | 0 | 0 | 2842 | 2331.2448 | 2331.2448 | 2331.2448 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -112.1281 | 2219.1167 | -2750 | -200 | -730.8833 | 18.27% | 74.14% | 95% | 0% | 2842 | -98
[5 empty] | 2019-04-01 | 43 | 2180.5 | 2659 | -98 | 0 | 0 | 2757 | 2198.1039 | 2198.1039 | 2198.1039 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -112.1281 | 2085.9757 | -2750 | -200 | -864.0243 | 21.6% | 74.13% | 95% | 0% | 2757 | -98
[5 empty] | 2019-04-01 | 44 | 2181 | 2505 | -99 | 0 | 0 | 2604 | 1958.4501 | 1958.4501 | 1958.4501 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -113.2723 | 1845.1778 | -2750 | -200 | -1104.8222 | 27.62% | 74.13% | 95% | 0% | 2604 | -99
[5 empty] | 2019-04-01 | 45 | 2181.5 | 2340 | -99 | 0 | 0 | 2439 | 1700 | 1700 | 1700 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -113.2723 | 1586.7277 | -2750 | -200 | -1363.2723 | 34.08% | 74.13% | 95% | 0% | 2439 | -99
[5 empty] | 2019-04-01 | 46 | 2182 | 2181 | -99 | 0 | 0 | 2280 | 1450.9481 | 1450.9481 | 1450.9481 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -113.2723 | 1337.6758 | -2750 | -200 | -1612.3242 | 40.31% | 74.13% | 95% | 0% | 2280 | -99
[5 empty] | 2019-04-01 | 47 | 2182.5 | 2018 | -99 | 0 | 0 | 2117 | 1195.6307 | 1195.6307 | 1195.6307 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -113.2723 | 1082.3584 | -2750 | -200 | -1867.6416 | 46.69% | 74.12% | 95% | 0% | 2117 | -99
[5 empty] | 2019-04-01 | 48 | 2183 | 1910 | -98 | 0 | 0 | 2008 | 1024.8969 | 1024.8969 | 1024.8969 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -112.1281 | 912.7688 | -2750 | -200 | -2037.2312 | 50.93% | 74.12% | 95% | 0% | 2008 | -98
[5 empty] | 2019-04-02 | 1 | 2183.5 | 1817 | -93 | 0 | 0 | 1910 | 871.3932 | 871.3932 | 871.3932 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -106.4073 | 764.9859 | -2750 | -200 | -2185.0141 | 54.63% | 74.11% | 95% | 0% | 1910 | -93
[5 empty] | 2019-04-02 | 2 | 2184 | 1777 | -87 | 0 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -99.5423 | 699.7981 | -2750 | -200 | -2250.2019 | 56.26% | 74.11% | 95% | 0% | 1864 | -87
[5 empty] | 2019-04-02 | 3 | 2184.5 | 1800 | -84 | 0 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -96.1098 | 734.5579 | -2750 | -200 | -2215.4421 | 55.39% | 74.1% | 95% | 0% | 1884 | -84
[5 empty] | 2019-04-02 | 4 | 2185 | 1851 | -81 | 0 | 0 | 1932 | 905.8533 | 905.8533 | 905.8533 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -92.6773 | 813.1759 | -2750 | -200 | -2136.8241 | 53.42% | 74.1% | 95% | 0% | 1932 | -81
[5 empty] | 2019-04-02 | 5 | 2185.5 | 1862 | -78 | 1 | 0 | 1940 | 918.3842 | 918.3842 | 918.3842 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -89.2449 | 829.1393 | -3550 | -400 | -3120.8607 | 78.02% | 74.1% | 95% | 0% | 1940 | -78
[5 empty] | 2019-04-02 | 6 | 2186 | 1845 | -75 | 1 | 0 | 1920 | 887.0569 | 887.0569 | 887.0569 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -85.8124 | 801.2445 | -3550 | -400 | -3148.7555 | 78.72% | 74.09% | 95% | 0% | 1920 | -75
[5 empty] | 2019-04-02 | 7 | 2186.5 | 1840 | -74 | 1 | 0 | 1914 | 877.6587 | 877.6587 | 877.6587 | 1974.1138 | 780 | 200 | 2954.1138 | 73.85% | 95% | 0% | -84.6682 | 792.9905 | -3550 | -400 | -3157.0095 | 78.93% | 74.08% | 95% | 0% | 1914 | -74
[5 empty] | 2019-04-02 | 8 | 2187 | 1835 | -72 | 1 | 0 | 1907 | 866.6941 | 866.6941 | 866.6941 | 1972.5474 | 780 | 200 | 2952.5474 | 73.81% | 95% | 0% | -82.3799 | 784.3143 | -3550 | -400 | -3165.6857 | 79.14% | 74.08% | 95% | 0% | 1907 | -72
[5 empty] | 2019-04-02 | 9 | 2187.5 | 1828 | -72 | 1 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 1972.5474 | 780 | 200 | 2952.5474 | 73.81% | 95% | 0% | -82.3799 | 773.3497 | -3550 | -400 | -3176.6503 | 79.42% | 74.07% | 95% | 0% | 1900 | -72
[5 empty] | 2019-04-02 | 10 | 2188 | 1828 | -72 | 1 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 1972.5474 | 780 | 200 | 2952.5474 | 73.81% | 95% | 0% | -82.3799 | 773.3497 | -3550 | -400 | -3176.6503 | 79.42% | 74.07% | 95% | 0% | 1900 | -72
[5 empty] | 2019-04-02 | 11 | 2188.5 | 1873 | -74 | 1 | 0 | 1947 | 929.3487 | 929.3487 | 929.3487 | 1972.5474 | 780 | 200 | 2952.5474 | 73.81% | 95% | 0% | -84.6682 | 844.6805 | -3550 | -400 | -3105.3195 | 77.63% | 74.07% | 95% | 0% | 1947 | -74
[5 empty] | 2019-04-02 | 12 | 2189 | 1967 | -74 | 1 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 1972.5474 | 780 | 200 | 2952.5474 | 73.81% | 95% | 0% | -84.6682 | 991.9188 | -3550 | -400 | -2958.0812 | 73.95% | 74.07% | 95% | 0% | 2041 | -74
[5 empty] | 2019-04-02 | 13 | 2189.5 | 2189 | -74 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 1972.5474 | 780 | 200 | 2952.5474 | 73.81% | 95% | 0% | -84.6682 | 1339.6517 | -3550 | -400 | -2610.3483 | 65.26% | 74.07% | 95% | 0% | 2263 | -74
[5 empty] | 2019-04-02 | 14 | 2190 | 2367 | -79 | 1 | 0 | 2446 | 1710.9646 | 1710.9646 | 1710.9646 | 1970.981 | 780 | 200 | 2950.981 | 73.77% | 95% | 0% | -90.389 | 1620.5755 | -3550 | -400 | -2329.4245 | 58.24% | 74.07% | 95% | 0% | 2446 | -79
[5 empty] | 2019-04-02 | 15 | 2190.5 | 2605 | -104 | 1 | 0 | 2709 | 2122.9184 | 2122.9184 | 2122.9184 | 1970.981 | 780 | 200 | 2950.981 | 73.77% | 95% | 0% | -118.9931 | 2003.9252 | -3550 | -400 | -1946.0748 | 48.65% | 74.07% | 95% | 0% | 2709 | -104
[5 empty] | 2019-04-02 | 16 | 2191 | 2704 | -142 | 1 | 0 | 2846 | 2337.5103 | 2337.5103 | 2337.5103 | 1970.981 | 780 | 200 | 2950.981 | 73.77% | 95% | 0% | -162.4714 | 2175.0389 | -3550 | -400 | -1774.9611 | 44.37% | 74.06% | 95% | 0% | 2846 | -142
[5 empty] | 2019-04-02 | 17 | 2191.5 | 2725 | -189 | 1 | 0 | 2914 | 2444.0231 | 2444.0231 | 2444.0231 | 1970.981 | 780 | 200 | 2950.981 | 73.77% | 95% | 0% | -216.2471 | 2227.7759 | -3550 | -400 | -1722.2241 | 43.06% | 74.06% | 95% | 0% | 2914 | -189
[5 empty] | 2019-04-02 | 18 | 2192 | 2659 | -238 | 1 | 0 | 2897 | 2417.3949 | 2417.3949 | 2417.3949 | 1970.981 | 780 | 200 | 2950.981 | 73.77% | 95% | 0% | -272.3112 | 2145.0837 | -3550 | -400 | -1804.9163 | 45.12% | 74.05% | 95% | 0% | 2897 | -238
[5 empty] | 2019-04-02 | 19 | 2192.5 | 2638 | -284 | 1 | 0 | 2922 | 2456.554 | 2456.554 | 2456.554 | 1970.981 | 780 | 200 | 2950.981 | 73.77% | 95% | 0% | -324.9428 | 2131.6112 | -3550 | -400 | -1818.3888 | 45.46% | 74.05% | 95% | 0% | 2922 | -284
[5 empty] | 2019-04-02 | 20 | 2193 | 2587 | -329 | 1 | 0 | 2916 | 2447.1558 | 2447.1558 | 2447.1558 | 1970.981 | 780 | 200 | 2950.981 | 73.77% | 95% | 0% | -376.4302 | 2070.7256 | -3550 | -400 | -1879.2744 | 46.98% | 74.05% | 95% | 0% | 2916 | -329
[5 empty] | 2019-04-02 | 21 | 2193.5 | 2505 | -377 | 1 | 0 | 2882 | 2393.8994 | 2393.8994 | 2393.8994 | 1970.981 | 780 | 200 | 2950.981 | 73.77% | 95% | 0% | -431.3501 | 1962.5493 | -3550 | -400 | -1987.4507 | 49.69% | 74.05% | 95% | 0% | 2882 | -377
[5 empty] | 2019-04-02 | 22 | 2194 | 2458 | -418 | 1 | 0 | 2876 | 2384.5012 | 2384.5012 | 2384.5012 | 1970.981 | 780 | 200 | 2950.981 | 73.77% | 95% | 0% | -478.2609 | 1906.2404 | -3550 | -400 | -2043.7596 | 51.09% | 74.05% | 95% | 0% | 2876 | -418
[5 empty] | 2019-04-02 | 23 | 2194.5 | 2426 | -445 | 1 | 0 | 2871 | 2376.6694 | 2376.6694 | 2376.6694 | 1970.981 | 780 | 200 | 2950.981 | 73.77% | 95% | 0% | -509.1533 | 1867.5161 | -3550 | -400 | -2082.4839 | 52.06% | 74.05% | 95% | 0% | 2871 | -445
[5 empty] | 2019-04-02 | 24 | 2195 | 2386 | -464 | 1 | 0 | 2850 | 2343.7758 | 2343.7758 | 2343.7758 | 1969.4147 | 780 | 200 | 2949.4147 | 73.74% | 95% | 0% | -530.8924 | 1812.8833 | -3550 | -400 | -2137.1167 | 53.43% | 74.05% | 95% | 0% | 2850 | -464
[5 empty] | 2019-04-02 | 25 | 2195.5 | 2366 | -479 | 1 | 0 | 2845 | 2335.9439 | 2335.9439 | 2335.9439 | 1969.4147 | 780 | 200 | 2949.4147 | 73.74% | 95% | 0% | -548.0549 | 1787.889 | -3550 | -400 | -2162.111 | 54.05% | 74.04% | 95% | 0% | 2845 | -479
[5 empty] | 2019-04-02 | 26 | 2196 | 2329 | -490 | 1 | 0 | 2819 | 2295.2185 | 2295.2185 | 2295.2185 | 1969.4147 | 780 | 200 | 2949.4147 | 73.74% | 95% | 0% | -560.6407 | 1734.5777 | -3550 | -400 | -2215.4223 | 55.39% | 74.04% | 95% | 0% | 2819 | -490
[5 empty] | 2019-04-02 | 27 | 2196.5 | 2276 | -491 | 1 | 0 | 2767 | 2213.7675 | 2213.7675 | 2213.7675 | 1969.4147 | 780 | 200 | 2949.4147 | 73.74% | 95% | 0% | -561.7849 | 1651.9826 | -3550 | -400 | -2298.0174 | 57.45% | 74.04% | 95% | 0% | 2767 | -491
[5 empty] | 2019-04-02 | 28 | 2197 | 2228 | -485 | 1 | 0 | 2713 | 2129.1838 | 2129.1838 | 2129.1838 | 1969.4147 | 780 | 200 | 2949.4147 | 73.74% | 95% | 0% | -554.9199 | 1574.2639 | -3550 | -400 | -2375.7361 | 59.39% | 74.04% | 95% | 0% | 2713 | -485
[5 empty] | 2019-04-02 | 29 | 2197.5 | 2252 | -432 | 1 | 0 | 2684 | 2083.7593 | 2083.7593 | 2083.7593 | 1969.4147 | 780 | 200 | 2949.4147 | 73.74% | 95% | 0% | -494.2792 | 1589.4801 | -3550 | -400 | -2360.5199 | 59.01% | 74.04% | 95% | 0% | 2684 | -432
[5 empty] | 2019-04-02 | 30 | 2198 | 2211 | -450 | 1 | 0 | 2661 | 2047.7329 | 2047.7329 | 2047.7329 | 1969.4147 | 780 | 200 | 2949.4147 | 73.74% | 95% | 0% | -514.8741 | 1532.8588 | -3550 | -400 | -2417.1412 | 60.43% | 74.03% | 95% | 0% | 2661 | -450
[5 empty] | 2019-04-02 | 31 | 2198.5 | 2204 | -431 | 1 | 0 | 2635 | 2007.0074 | 2007.0074 | 2007.0074 | 1969.4147 | 780 | 200 | 2949.4147 | 73.74% | 95% | 0% | -493.135 | 1513.8724 | -3550 | -400 | -2436.1276 | 60.9% | 74.03% | 95% | 0% | 2635 | -431
[5 empty] | 2019-04-02 | 32 | 2199 | 2269 | -425 | 1 | 0 | 2694 | 2099.4229 | 2099.4229 | 2099.4229 | 1969.4147 | 780 | 200 | 2949.4147 | 73.74% | 95% | 0% | -486.27 | 1613.1529 | -3550 | -400 | -2336.8471 | 58.42% | 74.02% | 95% | 0% | 2694 | -425
[5 empty] | 2019-04-02 | 33 | 2199.5 | 2391 | -363 | 1 | 0 | 2754 | 2193.4048 | 2193.4048 | 2193.4048 | 1969.4147 | 780 | 200 | 2949.4147 | 73.74% | 95% | 0% | -415.3318 | 1778.073 | -3550 | -400 | -2171.927 | 54.3% | 74% | 95% | 0% | 2754 | -363
[5 empty] | 2019-04-02 | 34 | 2200 | 2529 | -321 | 1 | 0 | 2850 | 2343.7758 | 2343.7758 | 2343.7758 | 1967.8483 | 780 | 200 | 2947.8483 | 73.7% | 95% | 0% | -367.2769 | 1976.4989 | -3550 | -400 | -1973.5011 | 49.34% | 74% | 95% | 0% | 2850 | -321
[5 empty] | 2019-04-02 | 35 | 2200.5 | 2643 | -256 | 1 | 0 | 2899 | 2420.5276 | 2420.5276 | 2420.5276 | 1967.8483 | 780 | 200 | 2947.8483 | 73.7% | 95% | 0% | -292.9062 | 2127.6214 | -3550 | -400 | -1822.3786 | 45.56% | 74% | 95% | 0% | 2899 | -256
[5 empty] | 2019-04-02 | 36 | 2201 | 2761 | -190 | 1 | 0 | 2951 | 2501.9786 | 2501.9786 | 2501.9786 | 1967.8483 | 780 | 200 | 2947.8483 | 73.7% | 95% | 0% | -217.3913 | 2284.5873 | -3550 | -400 | -1665.4127 | 41.64% | 73.99% | 95% | 0% | 2951 | -190
[5 empty] | 2019-04-02 | 37 | 2201.5 | 2810 | -159 | 1 | 0 | 2969 | 2530.1731 | 2530.1731 | 2530.1731 | 1967.8483 | 780 | 200 | 2947.8483 | 73.7% | 95% | 0% | -181.9222 | 2348.2509 | -3550 | -400 | -1601.7491 | 40.04% | 73.99% | 95% | 0% | 2969 | -159
[5 empty] | 2019-04-02 | 38 | 2202 | 2873 | -123 | 1 | 0 | 2996 | 2572.465 | 2572.465 | 2572.465 | 1967.8483 | 780 | 200 | 2947.8483 | 73.7% | 95% | 0% | -140.7323 | 2431.7327 | -3550 | -400 | -1518.2673 | 37.96% | 73.98% | 95% | 0% | 2996 | -123
[5 empty] | 2019-04-02 | 39 | 2202.5 | 2935 | -86 | 1 | 0 | 3021 | 2611.6241 | 2611.6241 | 2611.6241 | 1967.8483 | 780 | 200 | 2947.8483 | 73.7% | 95% | 0% | -98.3982 | 2513.2259 | -3550 | -400 | -1436.7741 | 35.92% | 73.97% | 95% | 0% | 3021 | -86
[5 empty] | 2019-04-02 | 40 | 2203 | 2995 | -75 | 1 | 0 | 3070 | 2688.3759 | 2688.3759 | 2688.3759 | 1967.8483 | 780 | 200 | 2947.8483 | 73.7% | 95% | 0% | -85.8124 | 2602.5636 | -3550 | -400 | -1347.4364 | 33.69% | 73.96% | 95% | 0% | 3070 | -75
[5 empty] | 2019-04-02 | 41 | 2203.5 | 3007 | -75 | 0 | 0 | 3082 | 2707.1723 | 2707.1723 | 2707.1723 | 1967.8483 | 780 | 200 | 2947.8483 | 73.7% | 95% | 0% | -85.8124 | 2621.3599 | -2750 | -200 | -328.6401 | 8.216% | 73.96% | 95% | 0% | 3082 | -75
[5 empty] | 2019-04-02 | 42 | 2204 | 2925 | -74 | 0 | 0 | 2999 | 2577.1641 | 2577.1641 | 2577.1641 | 1967.8483 | 780 | 200 | 2947.8483 | 73.7% | 95% | 0% | -84.6682 | 2492.4959 | -2750 | -200 | -457.5041 | 11.44% | 73.96% | 95% | 0% | 2999 | -74
[5 empty] | 2019-04-02 | 43 | 2204.5 | 2814 | -75 | 0 | 0 | 2889 | 2404.864 | 2404.864 | 2404.864 | 1967.8483 | 780 | 200 | 2947.8483 | 73.7% | 95% | 0% | -85.8124 | 2319.0516 | -2750 | -200 | -630.9484 | 15.77% | 73.95% | 95% | 0% | 2889 | -75
[5 empty] | 2019-04-02 | 44 | 2205 | 2657 | -76 | 0 | 0 | 2733 | 2160.5111 | 2160.5111 | 2160.5111 | 1966.2819 | 780 | 200 | 2946.2819 | 73.66% | 95% | 0% | -86.9565 | 2073.5546 | -2750 | -200 | -876.4454 | 21.91% | 73.95% | 95% | 0% | 2733 | -76
[5 empty] | 2019-04-02 | 45 | 2205.5 | 2479 | -79 | 0 | 0 | 2558 | 1886.3974 | 1886.3974 | 1886.3974 | 1966.2819 | 780 | 200 | 2946.2819 | 73.66% | 95% | 0% | -90.389 | 1796.0083 | -2750 | -200 | -1153.9917 | 28.85% | 73.95% | 95% | 0% | 2558 | -79
[5 empty] | 2019-04-02 | 46 | 2206 | 2303 | -82 | 0 | 0 | 2385 | 1615.4163 | 1615.4163 | 1615.4163 | 1966.2819 | 780 | 200 | 2946.2819 | 73.66% | 95% | 0% | -93.8215 | 1521.5948 | -2750 | -200 | -1428.4052 | 35.71% | 73.94% | 95% | 0% | 2385 | -82
[5 empty] | 2019-04-02 | 47 | 2206.5 | 2134 | -86 | 0 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 1966.2819 | 780 | 200 | 2946.2819 | 73.66% | 95% | 0% | -98.3982 | 1258.568 | -2750 | -200 | -1691.432 | 42.29% | 73.94% | 95% | 0% | 2220 | -86
[5 empty] | 2019-04-02 | 48 | 2207 | 1999 | -90 | 0 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1966.2819 | 780 | 200 | 2946.2819 | 73.66% | 95% | 0% | -102.9748 | 1048.7976 | -2750 | -200 | -1901.2024 | 47.53% | 73.94% | 95% | 0% | 2089 | -90
[5 empty] | 2019-04-03 | 1 | 2207.5 | 1900 | -91 | 0 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1964.7156 | 780 | 200 | 2944.7156 | 73.62% | 95% | 0% | -104.119 | 894.1498 | -2750 | -200 | -2055.8502 | 51.4% | 73.93% | 95% | 0% | 1991 | -91
[5 empty] | 2019-04-03 | 2 | 2208 | 1848 | -91 | 0 | 0 | 1939 | 916.8178 | 916.8178 | 916.8178 | 1964.7156 | 780 | 200 | 2944.7156 | 73.62% | 95% | 0% | -104.119 | 812.6988 | -2750 | -200 | -2137.3012 | 53.43% | 73.93% | 95% | 0% | 1939 | -91
[5 empty] | 2019-04-03 | 3 | 2208.5 | 1852 | -94 | 0 | 0 | 1946 | 927.7824 | 927.7824 | 927.7824 | 1964.7156 | 780 | 200 | 2944.7156 | 73.62% | 95% | 0% | -107.5515 | 820.2309 | -2750 | -200 | -2129.7691 | 53.24% | 73.91% | 95% | 0% | 1946 | -94
[5 empty] | 2019-04-03 | 4 | 2209 | 1891 | -98 | 0 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 1964.7156 | 780 | 200 | 2944.7156 | 73.62% | 95% | 0% | -112.1281 | 883.0079 | -2750 | -200 | -2066.9921 | 51.67% | 73.9% | 95% | 0% | 1989 | -98
[5 empty] | 2019-04-03 | 5 | 2209.5 | 1890 | -101 | 0 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1964.7156 | 780 | 200 | 2944.7156 | 73.62% | 95% | 0% | -115.5606 | 882.7081 | -2750 | -200 | -2067.2919 | 51.68% | 73.9% | 95% | 0% | 1991 | -101
[5 empty] | 2019-04-03 | 6 | 2210 | 1866 | -104 | 0 | 0 | 1970 | 965.3751 | 965.3751 | 965.3751 | 1964.7156 | 780 | 200 | 2944.7156 | 73.62% | 95% | 0% | -118.9931 | 846.382 | -2750 | -200 | -2103.618 | 52.59% | 73.89% | 95% | 0% | 1970 | -104
[5 empty] | 2019-04-03 | 7 | 2210.5 | 1842 | -106 | 0 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 1964.7156 | 780 | 200 | 2944.7156 | 73.62% | 95% | 0% | -121.2815 | 809.6336 | -2750 | -200 | -2140.3664 | 53.51% | 73.88% | 95% | 0% | 1948 | -106
[5 empty] | 2019-04-03 | 8 | 2211 | 1822 | -108 | 0 | 0 | 1930 | 902.7205 | 902.7205 | 902.7205 | 1964.7156 | 780 | 200 | 2944.7156 | 73.62% | 95% | 0% | -123.5698 | 779.1507 | -2750 | -200 | -2170.8493 | 54.27% | 73.87% | 95% | 0% | 1930 | -108
[5 empty] | 2019-04-03 | 9 | 2211.5 | 1795 | -108 | 0 | 0 | 1903 | 860.4287 | 860.4287 | 860.4287 | 1964.7156 | 780 | 200 | 2944.7156 | 73.62% | 95% | 0% | -123.5698 | 736.8589 | -2750 | -200 | -2213.1411 | 55.33% | 73.87% | 95% | 0% | 1903 | -108
[5 empty] | 2019-04-03 | 10 | 2212 | 1795 | -109 | 0 | 0 | 1904 | 861.9951 | 861.9951 | 861.9951 | 1964.7156 | 780 | 200 | 2944.7156 | 73.62% | 95% | 0% | -124.714 | 737.2811 | -2750 | -200 | -2212.7189 | 55.32% | 73.86% | 95% | 0% | 1904 | -109
[5 empty] | 2019-04-03 | 11 | 2212.5 | 1855 | -110 | 0 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 1964.7156 | 780 | 200 | 2944.7156 | 73.62% | 95% | 0% | -125.8581 | 831.6852 | -2750 | -200 | -2118.3148 | 52.96% | 73.84% | 95% | 0% | 1965 | -110
[5 empty] | 2019-04-03 | 12 | 2213 | 1955 | -111 | 0 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 1963.1492 | 780 | 200 | 2943.1492 | 73.58% | 95% | 0% | -127.0023 | 988.7438 | -2750 | -200 | -1961.2562 | 49.03% | 73.84% | 95% | 0% | 2066 | -111
[5 empty] | 2019-04-03 | 13 | 2213.5 | 2192 | -112 | 0 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 1963.1492 | 780 | 200 | 2943.1492 | 73.58% | 95% | 0% | -128.1465 | 1360.3944 | -2750 | -200 | -1589.6056 | 39.74% | 73.82% | 95% | 0% | 2304 | -112
[5 empty] | 2019-04-03 | 14 | 2214 | 2401 | -114 | 0 | 0 | 2515 | 1819.0437 | 1819.0437 | 1819.0437 | 1963.1492 | 780 | 200 | 2943.1492 | 73.58% | 95% | 0% | -130.4348 | 1688.6089 | -2750 | -200 | -1261.3911 | 31.53% | 73.82% | 95% | 0% | 2515 | -114
[5 empty] | 2019-04-03 | 15 | 2214.5 | 2644 | -128 | 0 | 0 | 2772 | 2221.5993 | 2221.5993 | 2221.5993 | 1963.1492 | 780 | 200 | 2943.1492 | 73.58% | 95% | 0% | -146.4531 | 2075.1463 | -2750 | -200 | -874.8537 | 21.87% | 73.82% | 95% | 0% | 2772 | -128
[5 empty] | 2019-04-03 | 16 | 2215 | 2713 | -160 | 0 | 0 | 2873 | 2379.8021 | 2379.8021 | 2379.8021 | 1963.1492 | 780 | 200 | 2943.1492 | 73.58% | 95% | 0% | -183.0664 | 2196.7358 | -2750 | -200 | -753.2642 | 18.83% | 73.81% | 95% | 0% | 2873 | -160
[5 empty] | 2019-04-03 | 17 | 2215.5 | 2703 | -204 | 1 | 0 | 2907 | 2433.0585 | 2433.0585 | 2433.0585 | 1963.1492 | 780 | 200 | 2943.1492 | 73.58% | 95% | 0% | -233.4096 | 2199.6489 | -3550 | -400 | -1750.3511 | 43.76% | 73.8% | 95% | 0% | 2907 | -204
[5 empty] | 2019-04-03 | 18 | 2216 | 2633 | -242 | 1 | 0 | 2875 | 2382.9349 | 2382.9349 | 2382.9349 | 1963.1492 | 780 | 200 | 2943.1492 | 73.58% | 95% | 0% | -276.8879 | 2106.047 | -3550 | -400 | -1843.953 | 46.1% | 73.8% | 95% | 0% | 2875 | -242
[5 empty] | 2019-04-03 | 19 | 2216.5 | 2586 | -291 | 1 | 0 | 2877 | 2386.0676 | 2386.0676 | 2386.0676 | 1961.5829 | 780 | 200 | 2941.5829 | 73.54% | 95% | 0% | -332.9519 | 2053.1157 | -3550 | -400 | -1896.8843 | 47.42% | 73.8% | 95% | 0% | 2877 | -291
[5 empty] | 2019-04-03 | 20 | 2217 | 2581 | -329 | 1 | 0 | 2910 | 2437.7576 | 2437.7576 | 2437.7576 | 1961.5829 | 780 | 200 | 2941.5829 | 73.54% | 95% | 0% | -376.4302 | 2061.3274 | -3550 | -400 | -1888.6726 | 47.22% | 73.79% | 95% | 0% | 2910 | -329
[5 empty] | 2019-04-03 | 21 | 2217.5 | 2503 | -353 | 1 | 0 | 2856 | 2353.1739 | 2353.1739 | 2353.1739 | 1961.5829 | 780 | 200 | 2941.5829 | 73.54% | 95% | 0% | -403.8902 | 1949.2838 | -3550 | -400 | -2000.7162 | 50.02% | 73.79% | 95% | 0% | 2856 | -353
[5 empty] | 2019-04-03 | 22 | 2218 | 2475 | -361 | 1 | 0 | 2836 | 2321.8467 | 2321.8467 | 2321.8467 | 1961.5829 | 780 | 200 | 2941.5829 | 73.54% | 95% | 0% | -413.0435 | 1908.8032 | -3550 | -400 | -2041.1968 | 51.03% | 73.77% | 95% | 0% | 2836 | -361
[5 empty] | 2019-04-03 | 23 | 2218.5 | 2431 | -394 | 1 | 0 | 2825 | 2304.6167 | 2304.6167 | 2304.6167 | 1961.5829 | 780 | 200 | 2941.5829 | 73.54% | 95% | 0% | -450.8009 | 1853.8157 | -3550 | -400 | -2096.1843 | 52.4% | 73.77% | 95% | 0% | 2825 | -394
[5 empty] | 2019-04-03 | 24 | 2219 | 2417 | -407 | 1 | 0 | 2824 | 2303.0503 | 2303.0503 | 2303.0503 | 1961.5829 | 780 | 200 | 2941.5829 | 73.54% | 95% | 0% | -465.6751 | 1837.3752 | -3550 | -400 | -2112.6248 | 52.82% | 73.76% | 95% | 0% | 2824 | -407
[5 empty] | 2019-04-03 | 25 | 2219.5 | 2418 | -389 | 1 | 0 | 2807 | 2276.4221 | 2276.4221 | 2276.4221 | 1961.5829 | 780 | 200 | 2941.5829 | 73.54% | 95% | 0% | -445.0801 | 1831.342 | -3550 | -400 | -2118.658 | 52.97% | 73.76% | 95% | 0% | 2807 | -389
[5 empty] | 2019-04-03 | 26 | 2220 | 2416 | -383 | 1 | 0 | 2799 | 2263.8912 | 2263.8912 | 2263.8912 | 1961.5829 | 780 | 200 | 2941.5829 | 73.54% | 95% | 0% | -438.2151 | 1825.6761 | -3550 | -400 | -2124.3239 | 53.11% | 73.76% | 95% | 0% | 2799 | -383
[5 empty] | 2019-04-03 | 27 | 2220.5 | 2353 | -392 | 1 | 0 | 2745 | 2179.3075 | 2179.3075 | 2179.3075 | 1961.5829 | 780 | 200 | 2941.5829 | 73.54% | 95% | 0% | -448.5126 | 1730.7949 | -3550 | -400 | -2219.2051 | 55.48% | 73.76% | 95% | 0% | 2745 | -392
[5 empty] | 2019-04-03 | 28 | 2221 | 2275 | -425 | 1 | 0 | 2700 | 2108.8211 | 2108.8211 | 2108.8211 | 1960.0165 | 780 | 200 | 2940.0165 | 73.5% | 95% | 0% | -486.27 | 1622.5511 | -3550 | -400 | -2327.4489 | 58.19% | 73.76% | 95% | 0% | 2700 | -425
[5 empty] | 2019-04-03 | 29 | 2221.5 | 2215 | -458 | 1 | 0 | 2673 | 2066.5293 | 2066.5293 | 2066.5293 | 1960.0165 | 780 | 200 | 2940.0165 | 73.5% | 95% | 0% | -524.0275 | 1542.5018 | -3550 | -400 | -2407.4982 | 60.19% | 73.75% | 95% | 0% | 2673 | -458
[5 empty] | 2019-04-03 | 30 | 2222 | 2209 | -443 | 1 | 0 | 2652 | 2033.6356 | 2033.6356 | 2033.6356 | 1960.0165 | 780 | 200 | 2940.0165 | 73.5% | 95% | 0% | -506.865 | 1526.7706 | -3550 | -400 | -2423.2294 | 60.58% | 73.74% | 95% | 0% | 2652 | -443
[5 empty] | 2019-04-03 | 31 | 2222.5 | 2232 | -418 | 1 | 0 | 2650 | 2030.5029 | 2030.5029 | 2030.5029 | 1960.0165 | 780 | 200 | 2940.0165 | 73.5% | 95% | 0% | -478.2609 | 1552.242 | -3550 | -400 | -2397.758 | 59.94% | 73.74% | 95% | 0% | 2650 | -418
[5 empty] | 2019-04-03 | 32 | 2223 | 2298 | -394 | 1 | 0 | 2692 | 2096.2902 | 2096.2902 | 2096.2902 | 1960.0165 | 780 | 200 | 2940.0165 | 73.5% | 95% | 0% | -450.8009 | 1645.4893 | -3550 | -400 | -2304.5107 | 57.61% | 73.74% | 95% | 0% | 2692 | -394
[5 empty] | 2019-04-03 | 33 | 2223.5 | 2409 | -345 | 1 | 0 | 2754 | 2193.4048 | 2193.4048 | 2193.4048 | 1960.0165 | 780 | 200 | 2940.0165 | 73.5% | 95% | 0% | -394.7368 | 1798.6679 | -3550 | -400 | -2151.3321 | 53.78% | 73.74% | 95% | 0% | 2754 | -345
[5 empty] | 2019-04-03 | 34 | 2224 | 2508 | -314 | 1 | 0 | 2822 | 2299.9176 | 2299.9176 | 2299.9176 | 1958.4501 | 780 | 200 | 2938.4501 | 73.46% | 95% | 0% | -359.2677 | 1940.6498 | -3550 | -400 | -2009.3502 | 50.23% | 73.73% | 95% | 0% | 2822 | -314
[5 empty] | 2019-04-03 | 35 | 2224.5 | 2597 | -273 | 1 | 0 | 2870 | 2375.1031 | 2375.1031 | 2375.1031 | 1958.4501 | 780 | 200 | 2938.4501 | 73.46% | 95% | 0% | -312.357 | 2062.7461 | -3550 | -400 | -1887.2539 | 47.18% | 73.73% | 95% | 0% | 2870 | -273
[5 empty] | 2019-04-03 | 36 | 2225 | 2702 | -223 | 1 | 0 | 2925 | 2461.2531 | 2461.2531 | 2461.2531 | 1958.4501 | 780 | 200 | 2938.4501 | 73.46% | 95% | 0% | -255.1487 | 2206.1044 | -3550 | -400 | -1743.8956 | 43.6% | 73.72% | 95% | 0% | 2925 | -223
[5 empty] | 2019-04-03 | 37 | 2225.5 | 2817 | -165 | 1 | 0 | 2982 | 2550.5359 | 2550.5359 | 2550.5359 | 1958.4501 | 780 | 200 | 2938.4501 | 73.46% | 95% | 0% | -188.7872 | 2361.7487 | -3550 | -400 | -1588.2513 | 39.71% | 73.72% | 95% | 0% | 2982 | -165
[5 empty] | 2019-04-03 | 38 | 2226 | 2880 | -127 | 1 | 0 | 3007 | 2589.695 | 2589.695 | 2589.695 | 1958.4501 | 780 | 200 | 2938.4501 | 73.46% | 95% | 0% | -145.3089 | 2444.386 | -3550 | -400 | -1505.614 | 37.64% | 73.71% | 95% | 0% | 3007 | -127
[5 empty] | 2019-04-03 | 39 | 2226.5 | 2882 | -105 | 1 | 0 | 2987 | 2558.3677 | 2558.3677 | 2558.3677 | 1958.4501 | 780 | 200 | 2938.4501 | 73.46% | 95% | 0% | -120.1373 | 2438.2304 | -3550 | -400 | -1511.7696 | 37.79% | 73.71% | 95% | 0% | 2987 | -105
[5 empty] | 2019-04-03 | 40 | 2227 | 2896 | -99 | 1 | 0 | 2995 | 2570.8986 | 2570.8986 | 2570.8986 | 1958.4501 | 780 | 200 | 2938.4501 | 73.46% | 95% | 0% | -113.2723 | 2457.6263 | -3550 | -400 | -1492.3737 | 37.31% | 73.71% | 95% | 0% | 2995 | -99
[5 empty] | 2019-04-03 | 41 | 2227.5 | 2931 | -100 | 1 | 0 | 3031 | 2627.2877 | 2627.2877 | 2627.2877 | 1958.4501 | 780 | 200 | 2938.4501 | 73.46% | 95% | 0% | -114.4165 | 2512.8712 | -3550 | -400 | -1437.1288 | 35.93% | 73.71% | 95% | 0% | 3031 | -100
[5 empty] | 2019-04-03 | 42 | 2228 | 2851 | -100 | 0 | 0 | 2951 | 2501.9786 | 2501.9786 | 2501.9786 | 1958.4501 | 780 | 200 | 2938.4501 | 73.46% | 95% | 0% | -114.4165 | 2387.5621 | -2750 | -200 | -562.4379 | 14.06% | 73.71% | 95% | 0% | 2951 | -100
[5 empty] | 2019-04-03 | 43 | 2228.5 | 2747 | -101 | 0 | 0 | 2848 | 2340.643 | 2340.643 | 2340.643 | 1956.8838 | 780 | 200 | 2936.8838 | 73.42% | 95% | 0% | -115.5606 | 2225.0824 | -2750 | -200 | -724.9176 | 18.12% | 73.7% | 95% | 0% | 2848 | -101
[5 empty] | 2019-04-03 | 44 | 2229 | 2612 | -102 | 0 | 0 | 2714 | 2130.7502 | 2130.7502 | 2130.7502 | 1956.8838 | 780 | 200 | 2936.8838 | 73.42% | 95% | 0% | -116.7048 | 2014.0454 | -2750 | -200 | -935.9546 | 23.4% | 73.7% | 95% | 0% | 2714 | -102
[5 empty] | 2019-04-03 | 45 | 2229.5 | 2473 | -103 | 0 | 0 | 2576 | 1914.5919 | 1914.5919 | 1914.5919 | 1956.8838 | 780 | 200 | 2936.8838 | 73.42% | 95% | 0% | -117.849 | 1796.743 | -2750 | -200 | -1153.257 | 28.83% | 73.7% | 95% | 0% | 2576 | -103
[5 empty] | 2019-04-03 | 46 | 2230 | 2308 | -104 | 0 | 0 | 2412 | 1657.7082 | 1657.7082 | 1657.7082 | 1955.3174 | 780 | 200 | 2935.3174 | 73.38% | 95% | 0% | -118.9931 | 1538.715 | -2750 | -200 | -1411.285 | 35.28% | 73.68% | 95% | 0% | 2412 | -104
[5 empty] | 2019-04-03 | 47 | 2230.5 | 2130 | -104 | 0 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 1955.3174 | 780 | 200 | 2935.3174 | 73.38% | 95% | 0% | -118.9931 | 1259.9022 | -2750 | -200 | -1690.0978 | 42.25% | 73.68% | 95% | 0% | 2234 | -104
[5 empty] | 2019-04-03 | 48 | 2231 | 1994 | -105 | 0 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 1955.3174 | 780 | 200 | 2935.3174 | 73.38% | 95% | 0% | -120.1373 | 1047.2988 | -2750 | -200 | -1902.7012 | 47.57% | 73.68% | 95% | 0% | 2099 | -105
[5 empty] | 2019-04-04 | 1 | 2231.5 | 1896 | -104 | 0 | 0 | 2000 | 1012.366 | 1012.366 | 1012.366 | 1955.3174 | 780 | 200 | 2935.3174 | 73.38% | 95% | 0% | -118.9931 | 893.3729 | -2750 | -200 | -2056.6271 | 51.42% | 73.67% | 95% | 0% | 2000 | -104
[5 empty] | 2019-04-04 | 2 | 2232 | 1848 | -104 | 0 | 0 | 1952 | 937.1805 | 937.1805 | 937.1805 | 1955.3174 | 780 | 200 | 2935.3174 | 73.38% | 95% | 0% | -118.9931 | 818.1874 | -2750 | -200 | -2131.8126 | 53.3% | 73.67% | 95% | 0% | 1952 | -104
[5 empty] | 2019-04-04 | 3 | 2232.5 | 1858 | -106 | 0 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 1955.3174 | 780 | 200 | 2935.3174 | 73.38% | 95% | 0% | -121.2815 | 834.6955 | -2750 | -200 | -2115.3045 | 52.88% | 73.67% | 95% | 0% | 1964 | -106
[5 empty] | 2019-04-04 | 4 | 2233 | 1912 | -107 | 0 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 1955.3174 | 780 | 200 | 2935.3174 | 73.38% | 95% | 0% | -122.4256 | 919.7013 | -2750 | -200 | -2030.2987 | 50.76% | 73.67% | 95% | 0% | 2019 | -107
[5 empty] | 2019-04-04 | 5 | 2233.5 | 1917 | -108 | 0 | 0 | 2025 | 1051.5251 | 1051.5251 | 1051.5251 | 1955.3174 | 780 | 200 | 2935.3174 | 73.38% | 95% | 0% | -123.5698 | 927.9554 | -2750 | -200 | -2022.0446 | 50.55% | 73.67% | 95% | 0% | 2025 | -108
[5 empty] | 2019-04-04 | 6 | 2234 | 1901 | -109 | 0 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 1955.3174 | 780 | 200 | 2935.3174 | 73.38% | 95% | 0% | -124.714 | 903.3157 | -2750 | -200 | -2046.6843 | 51.17% | 73.66% | 95% | 0% | 2010 | -109
[5 empty] | 2019-04-04 | 7 | 2234.5 | 1882 | -109 | 0 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1955.3174 | 780 | 200 | 2935.3174 | 73.38% | 95% | 0% | -124.714 | 873.5548 | -2750 | -200 | -2076.4452 | 51.91% | 73.66% | 95% | 0% | 1991 | -109
[5 empty] | 2019-04-04 | 8 | 2235 | 1877 | -110 | 0 | 0 | 1987 | 992.0033 | 992.0033 | 992.0033 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -125.8581 | 866.1452 | -2750 | -200 | -2083.8548 | 52.1% | 73.66% | 95% | 0% | 1987 | -110
[5 empty] | 2019-04-04 | 9 | 2235.5 | 1872 | -108 | 0 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -123.5698 | 857.469 | -2750 | -200 | -2092.531 | 52.31% | 73.65% | 95% | 0% | 1980 | -108
[5 empty] | 2019-04-04 | 10 | 2236 | 1866 | -106 | 0 | 0 | 1972 | 968.5078 | 968.5078 | 968.5078 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -121.2815 | 847.2264 | -2750 | -200 | -2102.7736 | 52.57% | 73.65% | 95% | 0% | 1972 | -106
[5 empty] | 2019-04-04 | 11 | 2236.5 | 1933 | -106 | 0 | 0 | 2039 | 1073.4542 | 1073.4542 | 1073.4542 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -121.2815 | 952.1728 | -2750 | -200 | -1997.8272 | 49.95% | 73.64% | 95% | 0% | 2039 | -106
[5 empty] | 2019-04-04 | 12 | 2237 | 2023 | -107 | 0 | 0 | 2130 | 1215.9934 | 1215.9934 | 1215.9934 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -122.4256 | 1093.5678 | -2750 | -200 | -1856.4322 | 46.41% | 73.64% | 95% | 0% | 2130 | -107
[5 empty] | 2019-04-04 | 13 | 2237.5 | 2243 | -107 | 0 | 0 | 2350 | 1560.5936 | 1560.5936 | 1560.5936 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -122.4256 | 1438.1679 | -2750 | -200 | -1511.8321 | 37.8% | 73.64% | 95% | 0% | 2350 | -107
[5 empty] | 2019-04-04 | 14 | 2238 | 2437 | -110 | 0 | 0 | 2547 | 1869.1674 | 1869.1674 | 1869.1674 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -125.8581 | 1743.3092 | -2750 | -200 | -1206.6908 | 30.17% | 73.64% | 95% | 0% | 2547 | -110
[5 empty] | 2019-04-04 | 15 | 2238.5 | 2658 | -126 | 0 | 0 | 2784 | 2240.3957 | 2240.3957 | 2240.3957 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -144.1648 | 2096.231 | -2750 | -200 | -853.769 | 21.34% | 73.64% | 95% | 0% | 2784 | -126
[5 empty] | 2019-04-04 | 16 | 2239 | 2748 | -155 | 0 | 0 | 2903 | 2426.7931 | 2426.7931 | 2426.7931 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -177.3455 | 2249.4475 | -2750 | -200 | -700.5525 | 17.51% | 73.63% | 95% | 0% | 2903 | -155
[5 empty] | 2019-04-04 | 17 | 2239.5 | 2751 | -191 | 1 | 0 | 2942 | 2487.8813 | 2487.8813 | 2487.8813 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -218.5355 | 2269.3458 | -3550 | -400 | -1680.6542 | 42.02% | 73.63% | 95% | 0% | 2942 | -191
[5 empty] | 2019-04-04 | 18 | 2240 | 2678 | -235 | 1 | 0 | 2913 | 2442.4567 | 2442.4567 | 2442.4567 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -268.8787 | 2173.578 | -3550 | -400 | -1776.422 | 44.41% | 73.62% | 95% | 0% | 2913 | -235
[5 empty] | 2019-04-04 | 19 | 2240.5 | 2639 | -284 | 1 | 0 | 2923 | 2458.1204 | 2458.1204 | 2458.1204 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -324.9428 | 2133.1776 | -3550 | -400 | -1816.8224 | 45.42% | 73.62% | 95% | 0% | 2923 | -284
[5 empty] | 2019-04-04 | 20 | 2241 | 2567 | -326 | 1 | 0 | 2893 | 2411.1294 | 2411.1294 | 2411.1294 | 1953.751 | 780 | 200 | 2933.751 | 73.34% | 95% | 0% | -372.9977 | 2038.1317 | -3550 | -400 | -1911.8683 | 47.8% | 73.6% | 95% | 0% | 2893 | -326
[5 empty] | 2019-04-04 | 21 | 2241.5 | 2528 | -334 | 1 | 0 | 2862 | 2362.5721 | 2362.5721 | 2362.5721 | 1952.1847 | 780 | 200 | 2932.1847 | 73.3% | 95% | 0% | -382.151 | 1980.4211 | -3550 | -400 | -1969.5789 | 49.24% | 73.6% | 95% | 0% | 2862 | -334
[5 empty] | 2019-04-04 | 22 | 2242 | 2473 | -389 | 1 | 0 | 2862 | 2362.5721 | 2362.5721 | 2362.5721 | 1952.1847 | 780 | 200 | 2932.1847 | 73.3% | 95% | 0% | -445.0801 | 1917.492 | -3550 | -400 | -2032.508 | 50.81% | 73.6% | 95% | 0% | 2862 | -389
[5 empty] | 2019-04-04 | 23 | 2242.5 | 2437 | -424 | 1 | 0 | 2861 | 2361.0058 | 2361.0058 | 2361.0058 | 1952.1847 | 780 | 200 | 2932.1847 | 73.3% | 95% | 0% | -485.1259 | 1875.8799 | -3550 | -400 | -2074.1201 | 51.85% | 73.6% | 95% | 0% | 2861 | -424
[5 empty] | 2019-04-04 | 24 | 2243 | 2391 | -450 | 1 | 0 | 2841 | 2329.6785 | 2329.6785 | 2329.6785 | 1952.1847 | 780 | 200 | 2932.1847 | 73.3% | 95% | 0% | -514.8741 | 1814.8043 | -3550 | -400 | -2135.1957 | 53.38% | 73.6% | 95% | 0% | 2841 | -450
[5 empty] | 2019-04-04 | 25 | 2243.5 | 2411 | -424 | 1 | 0 | 2835 | 2320.2803 | 2320.2803 | 2320.2803 | 1952.1847 | 780 | 200 | 2932.1847 | 73.3% | 95% | 0% | -485.1259 | 1835.1544 | -3550 | -400 | -2114.8456 | 52.87% | 73.59% | 95% | 0% | 2835 | -424
[5 empty] | 2019-04-04 | 26 | 2244 | 2335 | -466 | 1 | 0 | 2801 | 2267.0239 | 2267.0239 | 2267.0239 | 1952.1847 | 780 | 200 | 2932.1847 | 73.3% | 95% | 0% | -533.1808 | 1733.8431 | -3550 | -400 | -2216.1569 | 55.4% | 73.59% | 95% | 0% | 2801 | -466
[5 empty] | 2019-04-04 | 27 | 2244.5 | 2277 | -479 | 1 | 0 | 2756 | 2196.5375 | 2196.5375 | 2196.5375 | 1950.6183 | 780 | 200 | 2930.6183 | 73.27% | 95% | 0% | -548.0549 | 1648.4826 | -3550 | -400 | -2301.5174 | 57.54% | 73.58% | 95% | 0% | 2756 | -479
[5 empty] | 2019-04-04 | 28 | 2245 | 2265 | -444 | 1 | 0 | 2709 | 2122.9184 | 2122.9184 | 2122.9184 | 1950.6183 | 780 | 200 | 2930.6183 | 73.27% | 95% | 0% | -508.0092 | 1614.9092 | -3550 | -400 | -2335.0908 | 58.38% | 73.58% | 95% | 0% | 2709 | -444
[5 empty] | 2019-04-04 | 29 | 2245.5 | 2281 | -436 | 1 | 0 | 2717 | 2135.4493 | 2135.4493 | 2135.4493 | 1950.6183 | 780 | 200 | 2930.6183 | 73.27% | 95% | 0% | -498.8558 | 1636.5935 | -3550 | -400 | -2313.4065 | 57.84% | 73.57% | 95% | 0% | 2717 | -436
[5 empty] | 2019-04-04 | 30 | 2246 | 2277 | -432 | 1 | 0 | 2709 | 2122.9184 | 2122.9184 | 2122.9184 | 1950.6183 | 780 | 200 | 2930.6183 | 73.27% | 95% | 0% | -494.2792 | 1628.6392 | -3550 | -400 | -2321.3608 | 58.03% | 73.57% | 95% | 0% | 2709 | -432
[5 empty] | 2019-04-04 | 31 | 2246.5 | 2313 | -405 | 1 | 0 | 2718 | 2137.0157 | 2137.0157 | 2137.0157 | 1950.6183 | 780 | 200 | 2930.6183 | 73.27% | 95% | 0% | -463.3867 | 1673.6289 | -3550 | -400 | -2276.3711 | 56.91% | 73.56% | 95% | 0% | 2718 | -405
[5 empty] | 2019-04-04 | 32 | 2247 | 2355 | -390 | 1 | 0 | 2745 | 2179.3075 | 2179.3075 | 2179.3075 | 1949.0519 | 780 | 200 | 2929.0519 | 73.23% | 95% | 0% | -446.2243 | 1733.0832 | -3550 | -400 | -2216.9168 | 55.42% | 73.56% | 95% | 0% | 2745 | -390
[5 empty] | 2019-04-04 | 33 | 2247.5 | 2428 | -352 | 1 | 0 | 2780 | 2234.1303 | 2234.1303 | 2234.1303 | 1949.0519 | 780 | 200 | 2929.0519 | 73.23% | 95% | 0% | -402.746 | 1831.3843 | -3550 | -400 | -2118.6157 | 52.97% | 73.56% | 95% | 0% | 2780 | -352
[5 empty] | 2019-04-04 | 34 | 2248 | 2487 | -327 | 1 | 0 | 2814 | 2287.3866 | 2287.3866 | 2287.3866 | 1949.0519 | 780 | 200 | 2929.0519 | 73.23% | 95% | 0% | -374.1419 | 1913.2448 | -3550 | -400 | -2036.7552 | 50.92% | 73.56% | 95% | 0% | 2814 | -327
[5 empty] | 2019-04-04 | 35 | 2248.5 | 2577 | -301 | 1 | 0 | 2878 | 2387.634 | 2387.634 | 2387.634 | 1949.0519 | 780 | 200 | 2929.0519 | 73.23% | 95% | 0% | -344.3936 | 2043.2404 | -3550 | -400 | -1906.7596 | 47.67% | 73.56% | 95% | 0% | 2878 | -301
[5 empty] | 2019-04-04 | 36 | 2249 | 2627 | -270 | 1 | 0 | 2897 | 2417.3949 | 2417.3949 | 2417.3949 | 1949.0519 | 780 | 200 | 2929.0519 | 73.23% | 95% | 0% | -308.9245 | 2108.4704 | -3550 | -400 | -1841.5296 | 46.04% | 73.56% | 95% | 0% | 2897 | -270
[5 empty] | 2019-04-04 | 37 | 2249.5 | 2697 | -225 | 1 | 0 | 2922 | 2456.554 | 2456.554 | 2456.554 | 1949.0519 | 780 | 200 | 2929.0519 | 73.23% | 95% | 0% | -257.4371 | 2199.1169 | -3550 | -400 | -1750.8831 | 43.77% | 73.56% | 95% | 0% | 2922 | -225
[5 empty] | 2019-04-04 | 38 | 2250 | 2752 | -195 | 1 | 0 | 2947 | 2495.7131 | 2495.7131 | 2495.7131 | 1949.0519 | 780 | 200 | 2929.0519 | 73.23% | 95% | 0% | -223.1121 | 2272.601 | -3550 | -400 | -1677.399 | 41.93% | 73.55% | 95% | 0% | 2947 | -195
[5 empty] | 2019-04-04 | 39 | 2250.5 | 2785 | -179 | 1 | 0 | 2964 | 2522.3413 | 2522.3413 | 2522.3413 | 1949.0519 | 780 | 200 | 2929.0519 | 73.23% | 95% | 0% | -204.8055 | 2317.5358 | -3550 | -400 | -1632.4642 | 40.81% | 73.55% | 95% | 0% | 2964 | -179
[5 empty] | 2019-04-04 | 40 | 2251 | 2781 | -171 | 1 | 0 | 2952 | 2503.5449 | 2503.5449 | 2503.5449 | 1949.0519 | 780 | 200 | 2929.0519 | 73.23% | 95% | 0% | -195.6522 | 2307.8928 | -3550 | -400 | -1642.1072 | 41.05% | 73.55% | 95% | 0% | 2952 | -171
[5 empty] | 2019-04-04 | 41 | 2251.5 | 2783 | -169 | 1 | 0 | 2952 | 2503.5449 | 2503.5449 | 2503.5449 | 1947.4856 | 780 | 200 | 2927.4856 | 73.19% | 95% | 0% | -193.3638 | 2310.1811 | -3550 | -400 | -1639.8189 | 41% | 73.54% | 95% | 0% | 2952 | -169
[5 empty] | 2019-04-04 | 42 | 2252 | 2714 | -168 | 0 | 0 | 2882 | 2393.8994 | 2393.8994 | 2393.8994 | 1947.4856 | 780 | 200 | 2927.4856 | 73.19% | 95% | 0% | -192.2197 | 2201.6797 | -2750 | -200 | -748.3203 | 18.71% | 73.54% | 95% | 0% | 2882 | -168
[5 empty] | 2019-04-04 | 43 | 2252.5 | 2589 | -166 | 0 | 0 | 2755 | 2194.9711 | 2194.9711 | 2194.9711 | 1947.4856 | 780 | 200 | 2927.4856 | 73.19% | 95% | 0% | -189.9314 | 2005.0398 | -2750 | -200 | -944.9602 | 23.62% | 73.51% | 95% | 0% | 2755 | -166
[5 empty] | 2019-04-04 | 44 | 2253 | 2437 | -165 | 0 | 0 | 2602 | 1955.3174 | 1955.3174 | 1955.3174 | 1947.4856 | 780 | 200 | 2927.4856 | 73.19% | 95% | 0% | -188.7872 | 1766.5302 | -2750 | -200 | -1183.4698 | 29.59% | 73.51% | 95% | 0% | 2602 | -165
[5 empty] | 2019-04-04 | 45 | 2253.5 | 2266 | -163 | 0 | 0 | 2429 | 1684.3364 | 1684.3364 | 1684.3364 | 1947.4856 | 780 | 200 | 2927.4856 | 73.19% | 95% | 0% | -186.4989 | 1497.8375 | -2750 | -200 | -1452.1625 | 36.3% | 73.51% | 95% | 0% | 2429 | -163
[5 empty] | 2019-04-04 | 46 | 2254 | 2104 | -161 | 0 | 0 | 2265 | 1427.4526 | 1427.4526 | 1427.4526 | 1947.4856 | 780 | 200 | 2927.4856 | 73.19% | 95% | 0% | -184.2105 | 1243.2421 | -2750 | -200 | -1706.7579 | 42.67% | 73.51% | 95% | 0% | 2265 | -161
[5 empty] | 2019-04-04 | 47 | 2254.5 | 1946 | -158 | 0 | 0 | 2104 | 1175.2679 | 1175.2679 | 1175.2679 | 1947.4856 | 780 | 200 | 2927.4856 | 73.19% | 95% | 0% | -180.778 | 994.4899 | -2750 | -200 | -1955.5101 | 48.89% | 73.51% | 95% | 0% | 2104 | -158
[5 empty] | 2019-04-04 | 48 | 2255 | 1832 | -155 | 0 | 0 | 1987 | 992.0033 | 992.0033 | 992.0033 | 1947.4856 | 780 | 200 | 2927.4856 | 73.19% | 95% | 0% | -177.3455 | 814.6578 | -2750 | -200 | -2135.3422 | 53.38% | 73.5% | 95% | 0% | 1987 | -155
[5 empty] | 2019-04-05 | 1 | 2255.5 | 1734 | -154 | 0 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 1947.4856 | 780 | 200 | 2927.4856 | 73.19% | 95% | 0% | -176.2014 | 660.7319 | -2750 | -200 | -2289.2681 | 57.23% | 73.5% | 95% | 0% | 1888 | -154
[5 empty] | 2019-04-05 | 2 | 2256 | 1687 | -153 | 0 | 0 | 1840 | 761.7477 | 761.7477 | 761.7477 | 1947.4856 | 780 | 200 | 2927.4856 | 73.19% | 95% | 0% | -175.0572 | 586.6905 | -2750 | -200 | -2363.3095 | 59.08% | 73.5% | 95% | 0% | 1840 | -153
[5 empty] | 2019-04-05 | 3 | 2256.5 | 1709 | -151 | 0 | 0 | 1860 | 793.075 | 793.075 | 793.075 | 1945.9192 | 780 | 200 | 2925.9192 | 73.15% | 95% | 0% | -172.7689 | 620.3061 | -2750 | -200 | -2329.6939 | 58.24% | 73.5% | 95% | 0% | 1860 | -151
[5 empty] | 2019-04-05 | 4 | 2257 | 1782 | -149 | 0 | 0 | 1931 | 904.2869 | 904.2869 | 904.2869 | 1945.9192 | 780 | 200 | 2925.9192 | 73.15% | 95% | 0% | -170.4805 | 733.8063 | -2750 | -200 | -2216.1937 | 55.4% | 73.49% | 95% | 0% | 1931 | -149
[5 empty] | 2019-04-05 | 5 | 2257.5 | 1787 | -148 | 0 | 0 | 1935 | 910.5523 | 910.5523 | 910.5523 | 1945.9192 | 780 | 200 | 2925.9192 | 73.15% | 95% | 0% | -169.3364 | 741.216 | -2750 | -200 | -2208.784 | 55.22% | 73.49% | 95% | 0% | 1935 | -148
[5 empty] | 2019-04-05 | 6 | 2258 | 1766 | -148 | 0 | 0 | 1914 | 877.6587 | 877.6587 | 877.6587 | 1945.9192 | 780 | 200 | 2925.9192 | 73.15% | 95% | 0% | -169.3364 | 708.3223 | -2750 | -200 | -2241.6777 | 56.04% | 73.49% | 95% | 0% | 1914 | -148
[5 empty] | 2019-04-05 | 7 | 2258.5 | 1742 | -148 | 0 | 0 | 1890 | 840.066 | 840.066 | 840.066 | 1945.9192 | 780 | 200 | 2925.9192 | 73.15% | 95% | 0% | -169.3364 | 670.7296 | -2750 | -200 | -2279.2704 | 56.98% | 73.49% | 95% | 0% | 1890 | -148
[5 empty] | 2019-04-05 | 8 | 2259 | 1733 | -147 | 0 | 0 | 1880 | 824.4023 | 824.4023 | 824.4023 | 1945.9192 | 780 | 200 | 2925.9192 | 73.15% | 95% | 0% | -168.1922 | 656.2101 | -2750 | -200 | -2293.7899 | 57.34% | 73.49% | 95% | 0% | 1880 | -147
[5 empty] | 2019-04-05 | 9 | 2259.5 | 1729 | -148 | 0 | 0 | 1877 | 819.7032 | 819.7032 | 819.7032 | 1944.3528 | 780 | 200 | 2924.3528 | 73.11% | 95% | 0% | -169.3364 | 650.3668 | -2750 | -200 | -2299.6332 | 57.49% | 73.49% | 95% | 0% | 1877 | -148
[5 empty] | 2019-04-05 | 10 | 2260 | 1730 | -148 | 0 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 1944.3528 | 780 | 200 | 2924.3528 | 73.11% | 95% | 0% | -169.3364 | 651.9332 | -2750 | -200 | -2298.0668 | 57.45% | 73.48% | 95% | 0% | 1878 | -148
[5 empty] | 2019-04-05 | 11 | 2260.5 | 1776 | -149 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 1944.3528 | 780 | 200 | 2924.3528 | 73.11% | 95% | 0% | -170.4805 | 724.4082 | -2750 | -200 | -2225.5918 | 55.64% | 73.48% | 95% | 0% | 1925 | -149
[5 empty] | 2019-04-05 | 12 | 2261 | 1855 | -150 | 0 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 1944.3528 | 780 | 200 | 2924.3528 | 73.11% | 95% | 0% | -171.6247 | 848.5731 | -2750 | -200 | -2101.4269 | 52.54% | 73.48% | 95% | 0% | 2005 | -150
[5 empty] | 2019-04-05 | 13 | 2261.5 | 2052 | -150 | 0 | 0 | 2202 | 1328.7716 | 1328.7716 | 1328.7716 | 1944.3528 | 780 | 200 | 2924.3528 | 73.11% | 95% | 0% | -171.6247 | 1157.1469 | -2750 | -200 | -1792.8531 | 44.82% | 73.47% | 95% | 0% | 2202 | -150
[5 empty] | 2019-04-05 | 14 | 2262 | 2245 | -152 | 0 | 0 | 2397 | 1634.2127 | 1634.2127 | 1634.2127 | 1944.3528 | 780 | 200 | 2924.3528 | 73.11% | 95% | 0% | -173.913 | 1460.2997 | -2750 | -200 | -1489.7003 | 37.24% | 73.47% | 95% | 0% | 2397 | -152
[5 empty] | 2019-04-05 | 15 | 2262.5 | 2475 | -150 | 0 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 1944.3528 | 780 | 200 | 2924.3528 | 73.11% | 95% | 0% | -171.6247 | 1819.7191 | -2750 | -200 | -1130.2809 | 28.26% | 73.47% | 95% | 0% | 2625 | -150
[5 empty] | 2019-04-05 | 16 | 2263 | 2578 | -149 | 1 | 0 | 2727 | 2151.1129 | 2151.1129 | 2151.1129 | 1944.3528 | 780 | 200 | 2924.3528 | 73.11% | 95% | 0% | -170.4805 | 1980.6324 | -3550 | -400 | -1969.3676 | 49.23% | 73.46% | 95% | 0% | 2727 | -149
[5 empty] | 2019-04-05 | 17 | 2263.5 | 2496 | -272 | 1 | 0 | 2768 | 2215.3339 | 2215.3339 | 2215.3339 | 1944.3528 | 780 | 200 | 2924.3528 | 73.11% | 95% | 0% | -311.2128 | 1904.1211 | -3550 | -400 | -2045.8789 | 51.15% | 73.46% | 95% | 0% | 2768 | -272
[5 empty] | 2019-04-05 | 18 | 2264 | 2410 | -306 | 1 | 0 | 2716 | 2133.8829 | 2133.8829 | 2133.8829 | 1944.3528 | 780 | 200 | 2924.3528 | 73.11% | 95% | 0% | -350.1144 | 1783.7685 | -3550 | -400 | -2166.2315 | 54.16% | 73.46% | 95% | 0% | 2716 | -306
[5 empty] | 2019-04-05 | 19 | 2264.5 | 2362 | -340 | 1 | 0 | 2702 | 2111.9538 | 2111.9538 | 2111.9538 | 1944.3528 | 780 | 200 | 2924.3528 | 73.11% | 95% | 0% | -389.016 | 1722.9378 | -3550 | -400 | -2227.0622 | 55.68% | 73.45% | 95% | 0% | 2702 | -340
[5 empty] | 2019-04-05 | 20 | 2265 | 2309 | -382 | 1 | 0 | 2691 | 2094.7238 | 2094.7238 | 2094.7238 | 1942.7865 | 780 | 200 | 2922.7865 | 73.07% | 95% | 0% | -437.0709 | 1657.6529 | -3550 | -400 | -2292.3471 | 57.31% | 73.45% | 95% | 0% | 2691 | -382
[5 empty] | 2019-04-05 | 21 | 2265.5 | 2208 | -426 | 1 | 0 | 2634 | 2005.4411 | 2005.4411 | 2005.4411 | 1942.7865 | 780 | 200 | 2922.7865 | 73.07% | 95% | 0% | -487.4142 | 1518.0269 | -3550 | -400 | -2431.9731 | 60.8% | 73.45% | 95% | 0% | 2634 | -426
[5 empty] | 2019-04-05 | 22 | 2266 | 2120 | -477 | 1 | 0 | 2597 | 1947.4856 | 1947.4856 | 1947.4856 | 1942.7865 | 780 | 200 | 2922.7865 | 73.07% | 95% | 0% | -545.7666 | 1401.719 | -3550 | -400 | -2548.281 | 63.71% | 73.45% | 95% | 0% | 2597 | -477
[5 empty] | 2019-04-05 | 23 | 2266.5 | 2106 | -475 | 1 | 0 | 2581 | 1922.4237 | 1922.4237 | 1922.4237 | 1942.7865 | 780 | 200 | 2922.7865 | 73.07% | 95% | 0% | -543.4783 | 1378.9455 | -3550 | -400 | -2571.0545 | 64.28% | 73.44% | 95% | 0% | 2581 | -475
[5 empty] | 2019-04-05 | 24 | 2267 | 2067 | -498 | 1 | 0 | 2565 | 1897.3619 | 1897.3619 | 1897.3619 | 1942.7865 | 780 | 200 | 2922.7865 | 73.07% | 95% | 0% | -569.7941 | 1327.5679 | -3550 | -400 | -2622.4321 | 65.56% | 73.44% | 95% | 0% | 2565 | -498
[5 empty] | 2019-04-05 | 25 | 2267.5 | 2020 | -539 | 1 | 0 | 2559 | 1887.9637 | 1887.9637 | 1887.9637 | 1941.2201 | 780 | 200 | 2921.2201 | 73.03% | 95% | 0% | -616.7048 | 1271.2589 | -3550 | -400 | -2678.7411 | 66.97% | 73.43% | 95% | 0% | 2559 | -539
[5 empty] | 2019-04-05 | 26 | 2268 | 1971 | -560 | 1 | 0 | 2531 | 1844.1055 | 1844.1055 | 1844.1055 | 1941.2201 | 780 | 200 | 2921.2201 | 73.03% | 95% | 0% | -640.7323 | 1203.3733 | -3550 | -400 | -2746.6267 | 68.67% | 73.43% | 95% | 0% | 2531 | -560
[5 empty] | 2019-04-05 | 27 | 2268.5 | 1896 | -563 | 1 | 0 | 2459 | 1731.3273 | 1731.3273 | 1731.3273 | 1941.2201 | 780 | 200 | 2921.2201 | 73.03% | 95% | 0% | -644.1648 | 1087.1625 | -3550 | -400 | -2862.8375 | 71.57% | 73.43% | 95% | 0% | 2459 | -563
[5 empty] | 2019-04-05 | 28 | 2269 | 1909 | -548 | 1 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 1941.2201 | 780 | 200 | 2921.2201 | 73.03% | 95% | 0% | -627.0023 | 1101.1923 | -3550 | -400 | -2848.8077 | 71.22% | 73.42% | 95% | 0% | 2457 | -548
[5 empty] | 2019-04-05 | 29 | 2269.5 | 1905 | -538 | 1 | 0 | 2443 | 1706.2655 | 1706.2655 | 1706.2655 | 1941.2201 | 780 | 200 | 2921.2201 | 73.03% | 95% | 0% | -615.5606 | 1090.7048 | -3550 | -400 | -2859.2952 | 71.48% | 73.41% | 95% | 0% | 2443 | -538
[5 empty] | 2019-04-05 | 30 | 2270 | 1964 | -480 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 1941.2201 | 780 | 200 | 2921.2201 | 73.03% | 95% | 0% | -549.1991 | 1158.6327 | -3550 | -400 | -2791.3673 | 69.78% | 73.41% | 95% | 0% | 2444 | -480
[5 empty] | 2019-04-05 | 31 | 2270.5 | 2027 | -425 | 1 | 0 | 2452 | 1720.3627 | 1720.3627 | 1720.3627 | 1941.2201 | 780 | 200 | 2921.2201 | 73.03% | 95% | 0% | -486.27 | 1234.0927 | -3550 | -400 | -2715.9073 | 67.9% | 73.4% | 95% | 0% | 2452 | -425
[5 empty] | 2019-04-05 | 32 | 2271 | 2076 | -392 | 1 | 0 | 2468 | 1745.4246 | 1745.4246 | 1745.4246 | 1941.2201 | 780 | 200 | 2921.2201 | 73.03% | 95% | 0% | -448.5126 | 1296.912 | -3550 | -400 | -2653.088 | 66.33% | 73.4% | 95% | 0% | 2468 | -392
[5 empty] | 2019-04-05 | 33 | 2271.5 | 2195 | -352 | 1 | 0 | 2547 | 1869.1674 | 1869.1674 | 1869.1674 | 1941.2201 | 780 | 200 | 2921.2201 | 73.03% | 95% | 0% | -402.746 | 1466.4214 | -3550 | -400 | -2483.5786 | 62.09% | 73.4% | 95% | 0% | 2547 | -352
[5 empty] | 2019-04-05 | 34 | 2272 | 2296 | -320 | 1 | 0 | 2616 | 1977.2465 | 1977.2465 | 1977.2465 | 1941.2201 | 780 | 200 | 2921.2201 | 73.03% | 95% | 0% | -366.1327 | 1611.1138 | -3550 | -400 | -2338.8862 | 58.47% | 73.4% | 95% | 0% | 2616 | -320
[5 empty] | 2019-04-05 | 35 | 2272.5 | 2393 | -281 | 1 | 0 | 2674 | 2068.0956 | 2068.0956 | 2068.0956 | 1941.2201 | 780 | 200 | 2921.2201 | 73.03% | 95% | 0% | -321.5103 | 1746.5853 | -3550 | -400 | -2203.4147 | 55.09% | 73.4% | 95% | 0% | 2674 | -281
[5 empty] | 2019-04-05 | 36 | 2273 | 2493 | -229 | 1 | 0 | 2722 | 2143.2811 | 2143.2811 | 2143.2811 | 1941.2201 | 780 | 200 | 2921.2201 | 73.03% | 95% | 0% | -262.0137 | 1881.2674 | -3550 | -400 | -2068.7326 | 51.72% | 73.39% | 95% | 0% | 2722 | -229
[5 empty] | 2019-04-05 | 37 | 2273.5 | 2515 | -191 | 1 | 0 | 2706 | 2118.2193 | 2118.2193 | 2118.2193 | 1939.6538 | 780 | 200 | 2919.6538 | 72.99% | 95% | 0% | -218.5355 | 1899.6838 | -3550 | -400 | -2050.3162 | 51.26% | 73.39% | 95% | 0% | 2706 | -191
[5 empty] | 2019-04-05 | 38 | 2274 | 2548 | -156 | 1 | 0 | 2704 | 2115.0866 | 2115.0866 | 2115.0866 | 1939.6538 | 780 | 200 | 2919.6538 | 72.99% | 95% | 0% | -178.4897 | 1936.5969 | -3550 | -400 | -2013.4031 | 50.34% | 73.38% | 95% | 0% | 2704 | -156
[5 empty] | 2019-04-05 | 39 | 2274.5 | 2578 | -134 | 1 | 0 | 2712 | 2127.6175 | 2127.6175 | 2127.6175 | 1939.6538 | 780 | 200 | 2919.6538 | 72.99% | 95% | 0% | -153.3181 | 1974.2994 | -3550 | -400 | -1975.7006 | 49.39% | 73.38% | 95% | 0% | 2712 | -134
[5 empty] | 2019-04-05 | 40 | 2275 | 2610 | -126 | 1 | 0 | 2736 | 2165.2102 | 2165.2102 | 2165.2102 | 1939.6538 | 780 | 200 | 2919.6538 | 72.99% | 95% | 0% | -144.1648 | 2021.0455 | -3550 | -400 | -1928.9545 | 48.22% | 73.36% | 95% | 0% | 2736 | -126
[5 empty] | 2019-04-05 | 41 | 2275.5 | 2621 | -124 | 1 | 0 | 2745 | 2179.3075 | 2179.3075 | 2179.3075 | 1939.6538 | 780 | 200 | 2919.6538 | 72.99% | 95% | 0% | -141.8764 | 2037.4311 | -3550 | -400 | -1912.5689 | 47.81% | 73.35% | 95% | 0% | 2745 | -124
[5 empty] | 2019-04-05 | 42 | 2276 | 2605 | -122 | 1 | 0 | 2727 | 2151.1129 | 2151.1129 | 2151.1129 | 1939.6538 | 780 | 200 | 2919.6538 | 72.99% | 95% | 0% | -139.5881 | 2011.5248 | -3550 | -400 | -1938.4752 | 48.46% | 73.34% | 95% | 0% | 2727 | -122
[5 empty] | 2019-04-05 | 43 | 2276.5 | 2555 | -120 | 0 | 0 | 2675 | 2069.662 | 2069.662 | 2069.662 | 1939.6538 | 780 | 200 | 2919.6538 | 72.99% | 95% | 0% | -137.2998 | 1932.3622 | -2750 | -200 | -1017.6378 | 25.44% | 73.34% | 95% | 0% | 2675 | -120
[5 empty] | 2019-04-05 | 44 | 2277 | 2417 | -118 | 0 | 0 | 2535 | 1850.371 | 1850.371 | 1850.371 | 1939.6538 | 780 | 200 | 2919.6538 | 72.99% | 95% | 0% | -135.0114 | 1715.3595 | -2750 | -200 | -1234.6405 | 30.87% | 73.32% | 95% | 0% | 2535 | -118
[5 empty] | 2019-04-05 | 45 | 2277.5 | 2276 | -115 | 0 | 0 | 2391 | 1624.8145 | 1624.8145 | 1624.8145 | 1938.0874 | 780 | 200 | 2918.0874 | 72.95% | 95% | 0% | -131.5789 | 1493.2356 | -2750 | -200 | -1456.7644 | 36.42% | 73.32% | 95% | 0% | 2391 | -115
[5 empty] | 2019-04-05 | 46 | 2278 | 2154 | -112 | 0 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 1938.0874 | 780 | 200 | 2918.0874 | 72.95% | 95% | 0% | -128.1465 | 1300.8725 | -2750 | -200 | -1649.1275 | 41.23% | 73.32% | 95% | 0% | 2266 | -112
[5 empty] | 2019-04-05 | 47 | 2278.5 | 2014 | -108 | 0 | 0 | 2122 | 1203.4625 | 1203.4625 | 1203.4625 | 1938.0874 | 780 | 200 | 2918.0874 | 72.95% | 95% | 0% | -123.5698 | 1079.8927 | -2750 | -200 | -1870.1073 | 46.75% | 73.32% | 95% | 0% | 2122 | -108
[5 empty] | 2019-04-05 | 48 | 2279 | 1906 | -105 | 0 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 1938.0874 | 780 | 200 | 2918.0874 | 72.95% | 95% | 0% | -120.1373 | 909.4587 | -2750 | -200 | -2040.5413 | 51.01% | 73.31% | 95% | 0% | 2011 | -105
[5 empty] | 2019-04-06 | 1 | 2279.5 | 1819 | -101 | 0 | 0 | 1920 | 887.0569 | 887.0569 | 887.0569 | 1938.0874 | 780 | 200 | 2918.0874 | 72.95% | 95% | 0% | -115.5606 | 771.4962 | -2750 | -200 | -2178.5038 | 54.46% | 73.3% | 95% | 0% | 1920 | -101
[5 empty] | 2019-04-06 | 2 | 2280 | 1774 | -97 | 1 | 0 | 1871 | 810.305 | 810.305 | 810.305 | 1938.0874 | 780 | 200 | 2918.0874 | 72.95% | 95% | 0% | -110.984 | 699.321 | -3550 | -400 | -3250.679 | 81.27% | 73.3% | 95% | 0% | 1871 | -97
[5 empty] | 2019-04-06 | 3 | 2280.5 | 1802 | -93 | 1 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 1938.0874 | 780 | 200 | 2918.0874 | 72.95% | 95% | 0% | -106.4073 | 741.4905 | -3550 | -400 | -3208.5095 | 80.21% | 73.29% | 95% | 0% | 1895 | -93
[5 empty] | 2019-04-06 | 4 | 2281 | 1850 | -89 | 1 | 0 | 1939 | 916.8178 | 916.8178 | 916.8178 | 1938.0874 | 780 | 200 | 2918.0874 | 72.95% | 95% | 0% | -101.8307 | 814.9871 | -3550 | -400 | -3135.0129 | 78.38% | 73.28% | 95% | 0% | 1939 | -89
[5 empty] | 2019-04-06 | 5 | 2281.5 | 1850 | -87 | 1 | 0 | 1937 | 913.6851 | 913.6851 | 913.6851 | 1938.0874 | 780 | 200 | 2918.0874 | 72.95% | 95% | 0% | -99.5423 | 814.1427 | -3550 | -400 | -3135.8573 | 78.4% | 73.27% | 95% | 0% | 1937 | -87
[5 empty] | 2019-04-06 | 6 | 2282 | 1820 | -84 | 1 | 0 | 1904 | 861.9951 | 861.9951 | 861.9951 | 1938.0874 | 780 | 200 | 2918.0874 | 72.95% | 95% | 0% | -96.1098 | 765.8852 | -3550 | -400 | -3184.1148 | 79.6% | 73.27% | 95% | 0% | 1904 | -84
[5 empty] | 2019-04-06 | 7 | 2282.5 | 1789 | -81 | 1 | 0 | 1870 | 808.7387 | 808.7387 | 808.7387 | 1936.521 | 780 | 200 | 2916.521 | 72.91% | 95% | 0% | -92.6773 | 716.0613 | -3550 | -400 | -3233.9387 | 80.85% | 73.27% | 95% | 0% | 1870 | -81
[5 empty] | 2019-04-06 | 8 | 2283 | 1775 | -79 | 1 | 0 | 1854 | 783.6768 | 783.6768 | 783.6768 | 1936.521 | 780 | 200 | 2916.521 | 72.91% | 95% | 0% | -90.389 | 693.2878 | -3550 | -400 | -3256.7122 | 81.42% | 73.27% | 95% | 0% | 1854 | -79
[5 empty] | 2019-04-06 | 9 | 2283.5 | 1760 | -78 | 1 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 1936.521 | 780 | 200 | 2916.521 | 72.91% | 95% | 0% | -89.2449 | 669.3702 | -3550 | -400 | -3280.6298 | 82.02% | 73.27% | 95% | 0% | 1838 | -78
[5 empty] | 2019-04-06 | 10 | 2284 | 1754 | -78 | 1 | 0 | 1832 | 749.2168 | 749.2168 | 749.2168 | 1936.521 | 780 | 200 | 2916.521 | 72.91% | 95% | 0% | -89.2449 | 659.972 | -3550 | -400 | -3290.028 | 82.25% | 73.27% | 95% | 0% | 1832 | -78
[5 empty] | 2019-04-06 | 11 | 2284.5 | 1764 | -77 | 1 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 1936.521 | 780 | 200 | 2916.521 | 72.91% | 95% | 0% | -88.1007 | 675.2134 | -3550 | -400 | -3274.7866 | 81.87% | 73.26% | 95% | 0% | 1841 | -77
[5 empty] | 2019-04-06 | 12 | 2285 | 1801 | -76 | 1 | 0 | 1877 | 819.7032 | 819.7032 | 819.7032 | 1936.521 | 780 | 200 | 2916.521 | 72.91% | 95% | 0% | -86.9565 | 732.7467 | -3550 | -400 | -3217.2533 | 80.43% | 73.26% | 95% | 0% | 1877 | -76
[5 empty] | 2019-04-06 | 13 | 2285.5 | 1899 | -75 | 1 | 0 | 1974 | 971.6406 | 971.6406 | 971.6406 | 1936.521 | 780 | 200 | 2916.521 | 72.91% | 95% | 0% | -85.8124 | 885.8282 | -3550 | -400 | -3064.1718 | 76.6% | 73.24% | 95% | 0% | 1974 | -75
[5 empty] | 2019-04-06 | 14 | 2286 | 1960 | -75 | 1 | 0 | 2035 | 1067.1888 | 1067.1888 | 1067.1888 | 1936.521 | 780 | 200 | 2916.521 | 72.91% | 95% | 0% | -85.8124 | 981.3764 | -3550 | -400 | -2968.6236 | 74.22% | 73.24% | 95% | 0% | 2035 | -75
[5 empty] | 2019-04-06 | 15 | 2286.5 | 2076 | -88 | 1 | 0 | 2164 | 1269.2498 | 1269.2498 | 1269.2498 | 1936.521 | 780 | 200 | 2916.521 | 72.91% | 95% | 0% | -100.6865 | 1168.5633 | -3550 | -400 | -2781.4367 | 69.54% | 73.24% | 95% | 0% | 2164 | -88
[5 empty] | 2019-04-06 | 16 | 2287 | 2146 | -112 | 1 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 1936.521 | 780 | 200 | 2916.521 | 72.91% | 95% | 0% | -128.1465 | 1288.3416 | -3550 | -400 | -2661.6584 | 66.54% | 73.23% | 95% | 0% | 2258 | -112
[5 empty] | 2019-04-06 | 17 | 2287.5 | 2206 | -147 | 1 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 1936.521 | 780 | 200 | 2916.521 | 72.91% | 95% | 0% | -168.1922 | 1397.1004 | -3550 | -400 | -2552.8996 | 63.82% | 73.23% | 95% | 0% | 2353 | -147
[5 empty] | 2019-04-06 | 18 | 2288 | 2215 | -189 | 1 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 1936.521 | 780 | 200 | 2916.521 | 72.91% | 95% | 0% | -216.2471 | 1428.9301 | -3550 | -400 | -2521.0699 | 63.03% | 73.23% | 95% | 0% | 2404 | -189
[5 empty] | 2019-04-06 | 19 | 2288.5 | 2203 | -235 | 1 | 0 | 2438 | 1698.4336 | 1698.4336 | 1698.4336 | 1934.9547 | 780 | 200 | 2914.9547 | 72.87% | 95% | 0% | -268.8787 | 1429.5549 | -3550 | -400 | -2520.4451 | 63.01% | 73.22% | 95% | 0% | 2438 | -235
[5 empty] | 2019-04-06 | 20 | 2289 | 2144 | -282 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1934.9547 | 780 | 200 | 2914.9547 | 72.87% | 95% | 0% | -322.6545 | 1356.9828 | -3550 | -400 | -2593.0172 | 64.83% | 73.21% | 95% | 0% | 2426 | -282
[5 empty] | 2019-04-06 | 21 | 2289.5 | 2098 | -314 | 1 | 0 | 2412 | 1657.7082 | 1657.7082 | 1657.7082 | 1934.9547 | 780 | 200 | 2914.9547 | 72.87% | 95% | 0% | -359.2677 | 1298.4404 | -3550 | -400 | -2651.5596 | 66.29% | 73.21% | 95% | 0% | 2412 | -314
[5 empty] | 2019-04-06 | 22 | 2290 | 1993 | -389 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 1934.9547 | 780 | 200 | 2914.9547 | 72.87% | 95% | 0% | -445.0801 | 1165.6371 | -3550 | -400 | -2784.3629 | 69.61% | 73.21% | 95% | 0% | 2382 | -389
[5 empty] | 2019-04-06 | 23 | 2290.5 | 1936 | -423 | 1 | 0 | 2359 | 1574.6908 | 1574.6908 | 1574.6908 | 1934.9547 | 780 | 200 | 2914.9547 | 72.87% | 95% | 0% | -483.9817 | 1090.7092 | -3550 | -400 | -2859.2908 | 71.48% | 73.2% | 95% | 0% | 2359 | -423
[5 empty] | 2019-04-06 | 24 | 2291 | 1879 | -443 | 1 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 1933.3883 | 780 | 200 | 2913.3883 | 72.83% | 95% | 0% | -506.865 | 1009.8704 | -3550 | -400 | -2940.1296 | 73.5% | 73.2% | 95% | 0% | 2322 | -443
[5 empty] | 2019-04-06 | 25 | 2291.5 | 1827 | -472 | 1 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 1933.3883 | 780 | 200 | 2913.3883 | 72.83% | 95% | 0% | -540.0458 | 940.6632 | -3550 | -400 | -3009.3368 | 75.23% | 73.2% | 95% | 0% | 2299 | -472
[5 empty] | 2019-04-06 | 26 | 2292 | 1792 | -480 | 1 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 1933.3883 | 780 | 200 | 2913.3883 | 72.83% | 95% | 0% | -549.1991 | 889.2181 | -3550 | -400 | -3060.7819 | 76.52% | 73.19% | 95% | 0% | 2272 | -480
[5 empty] | 2019-04-06 | 27 | 2292.5 | 1750 | -483 | 1 | 0 | 2233 | 1377.3289 | 1377.3289 | 1377.3289 | 1933.3883 | 780 | 200 | 2913.3883 | 72.83% | 95% | 0% | -552.6316 | 824.6974 | -3550 | -400 | -3125.3026 | 78.13% | 73.19% | 95% | 0% | 2233 | -483
[5 empty] | 2019-04-06 | 28 | 2293 | 1713 | -482 | 1 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 1931.8219 | 780 | 200 | 2911.8219 | 72.8% | 95% | 0% | -551.4874 | 766.3197 | -3550 | -400 | -3183.6803 | 79.59% | 73.18% | 95% | 0% | 2195 | -482
[5 empty] | 2019-04-06 | 29 | 2293.5 | 1734 | -446 | 1 | 0 | 2180 | 1294.3116 | 1294.3116 | 1294.3116 | 1931.8219 | 780 | 200 | 2911.8219 | 72.8% | 95% | 0% | -510.2975 | 784.0141 | -3550 | -400 | -3165.9859 | 79.15% | 73.18% | 95% | 0% | 2180 | -446
[5 empty] | 2019-04-06 | 30 | 2294 | 1783 | -408 | 1 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 1931.8219 | 780 | 200 | 2911.8219 | 72.8% | 95% | 0% | -466.8192 | 844.7224 | -3550 | -400 | -3105.2776 | 77.63% | 73.17% | 95% | 0% | 2191 | -408
[5 empty] | 2019-04-06 | 31 | 2294.5 | 1849 | -360 | 1 | 0 | 2209 | 1339.7362 | 1339.7362 | 1339.7362 | 1930.2556 | 780 | 200 | 2910.2556 | 72.76% | 95% | 0% | -411.8993 | 927.8369 | -3550 | -400 | -3022.1631 | 75.55% | 73.17% | 95% | 0% | 2209 | -360
[5 empty] | 2019-04-06 | 32 | 2295 | 1908 | -330 | 1 | 0 | 2238 | 1385.1608 | 1385.1608 | 1385.1608 | 1930.2556 | 780 | 200 | 2910.2556 | 72.76% | 95% | 0% | -377.5744 | 1007.5864 | -3550 | -400 | -2942.4136 | 73.56% | 73.16% | 95% | 0% | 2238 | -330
[5 empty] | 2019-04-06 | 33 | 2295.5 | 2020 | -289 | 1 | 0 | 2309 | 1496.3726 | 1496.3726 | 1496.3726 | 1928.6892 | 780 | 200 | 2908.6892 | 72.72% | 95% | 0% | -330.6636 | 1165.709 | -3550 | -400 | -2784.291 | 69.61% | 73.16% | 95% | 0% | 2309 | -289
[5 empty] | 2019-04-06 | 34 | 2296 | 2114 | -255 | 1 | 0 | 2369 | 1590.3545 | 1590.3545 | 1590.3545 | 1928.6892 | 780 | 200 | 2908.6892 | 72.72% | 95% | 0% | -291.762 | 1298.5925 | -3550 | -400 | -2651.4075 | 66.29% | 73.16% | 95% | 0% | 2369 | -255
[5 empty] | 2019-04-06 | 35 | 2296.5 | 2211 | -219 | 1 | 0 | 2430 | 1685.9027 | 1685.9027 | 1685.9027 | 1928.6892 | 780 | 200 | 2908.6892 | 72.72% | 95% | 0% | -250.5721 | 1435.3306 | -3550 | -400 | -2514.6694 | 62.87% | 73.16% | 95% | 0% | 2430 | -219
[5 empty] | 2019-04-06 | 36 | 2297 | 2308 | -182 | 1 | 0 | 2490 | 1779.8846 | 1779.8846 | 1779.8846 | 1928.6892 | 780 | 200 | 2908.6892 | 72.72% | 95% | 0% | -208.238 | 1571.6466 | -3550 | -400 | -2378.3534 | 59.46% | 73.16% | 95% | 0% | 2490 | -182
[5 empty] | 2019-04-06 | 37 | 2297.5 | 2382 | -147 | 1 | 0 | 2529 | 1840.9728 | 1840.9728 | 1840.9728 | 1928.6892 | 780 | 200 | 2908.6892 | 72.72% | 95% | 0% | -168.1922 | 1672.7806 | -3550 | -400 | -2277.2194 | 56.93% | 73.15% | 95% | 0% | 2529 | -147
[5 empty] | 2019-04-06 | 38 | 2298 | 2436 | -113 | 1 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 1928.6892 | 780 | 200 | 2908.6892 | 72.72% | 95% | 0% | -129.2906 | 1743.0095 | -3550 | -400 | -2206.9905 | 55.17% | 73.15% | 95% | 0% | 2549 | -113
[5 empty] | 2019-04-06 | 39 | 2298.5 | 2447 | -91 | 1 | 0 | 2538 | 1855.0701 | 1855.0701 | 1855.0701 | 1928.6892 | 780 | 200 | 2908.6892 | 72.72% | 95% | 0% | -104.119 | 1750.9511 | -3550 | -400 | -2199.0489 | 54.98% | 73.14% | 95% | 0% | 2538 | -91
[5 empty] | 2019-04-06 | 40 | 2299 | 2454 | -84 | 1 | 0 | 2538 | 1855.0701 | 1855.0701 | 1855.0701 | 1927.1228 | 780 | 200 | 2907.1228 | 72.68% | 95% | 0% | -96.1098 | 1758.9602 | -3550 | -400 | -2191.0398 | 54.78% | 73.14% | 95% | 0% | 2538 | -84
[5 empty] | 2019-04-06 | 41 | 2299.5 | 2471 | -84 | 1 | 0 | 2555 | 1881.6983 | 1881.6983 | 1881.6983 | 1927.1228 | 780 | 200 | 2907.1228 | 72.68% | 95% | 0% | -96.1098 | 1785.5884 | -3550 | -400 | -2164.4116 | 54.11% | 73.13% | 95% | 0% | 2555 | -84
[5 empty] | 2019-04-06 | 42 | 2300 | 2423 | -84 | 1 | 0 | 2507 | 1806.5128 | 1806.5128 | 1806.5128 | 1927.1228 | 780 | 200 | 2907.1228 | 72.68% | 95% | 0% | -96.1098 | 1710.4029 | -3550 | -400 | -2239.5971 | 55.99% | 73.13% | 95% | 0% | 2507 | -84
[5 empty] | 2019-04-06 | 43 | 2300.5 | 2372 | -85 | 1 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 1927.1228 | 780 | 200 | 2907.1228 | 72.68% | 95% | 0% | -97.254 | 1630.9406 | -3550 | -400 | -2319.0594 | 57.98% | 73.12% | 95% | 0% | 2457 | -85
[5 empty] | 2019-04-06 | 44 | 2301 | 2298 | -85 | 1 | 0 | 2383 | 1612.2836 | 1612.2836 | 1612.2836 | 1927.1228 | 780 | 200 | 2907.1228 | 72.68% | 95% | 0% | -97.254 | 1515.0296 | -3550 | -400 | -2434.9704 | 60.87% | 73.12% | 95% | 0% | 2383 | -85
[5 empty] | 2019-04-06 | 45 | 2301.5 | 2210 | -85 | 1 | 0 | 2295 | 1474.4435 | 1474.4435 | 1474.4435 | 1925.5565 | 780 | 200 | 2905.5565 | 72.64% | 95% | 0% | -97.254 | 1377.1895 | -3550 | -400 | -2572.8105 | 64.32% | 73.09% | 95% | 0% | 2295 | -85
[5 empty] | 2019-04-06 | 46 | 2302 | 2105 | -85 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1925.5565 | 780 | 200 | 2905.5565 | 72.64% | 95% | 0% | -97.254 | 1212.7213 | -3550 | -400 | -2737.2787 | 68.43% | 73.09% | 95% | 0% | 2190 | -85
[5 empty] | 2019-04-06 | 47 | 2302.5 | 1973 | -85 | 1 | 0 | 2058 | 1103.2152 | 1103.2152 | 1103.2152 | 1925.5565 | 780 | 200 | 2905.5565 | 72.64% | 95% | 0% | -97.254 | 1005.9612 | -3550 | -400 | -2944.0388 | 73.6% | 73.09% | 95% | 0% | 2058 | -85
[5 empty] | 2019-04-06 | 48 | 2303 | 1868 | -85 | 1 | 0 | 1953 | 938.7469 | 938.7469 | 938.7469 | 1925.5565 | 780 | 200 | 2905.5565 | 72.64% | 95% | 0% | -97.254 | 841.4929 | -3550 | -400 | -3108.5071 | 77.71% | 73.09% | 95% | 0% | 1953 | -85
[5 empty] | 2019-04-07 | 1 | 2303.5 | 1780 | -86 | 1 | 0 | 1866 | 802.4732 | 802.4732 | 802.4732 | 1925.5565 | 780 | 200 | 2905.5565 | 72.64% | 95% | 0% | -98.3982 | 704.075 | -3550 | -400 | -3245.925 | 81.15% | 73.09% | 95% | 0% | 1866 | -86
[5 empty] | 2019-04-07 | 2 | 2304 | 1739 | -86 | 1 | 0 | 1825 | 738.2523 | 738.2523 | 738.2523 | 1925.5565 | 780 | 200 | 2905.5565 | 72.64% | 95% | 0% | -98.3982 | 639.8541 | -3550 | -400 | -3310.1459 | 82.75% | 73.08% | 95% | 0% | 1825 | -86
[5 empty] | 2019-04-07 | 3 | 2304.5 | 1750 | -86 | 1 | 0 | 1836 | 755.4823 | 755.4823 | 755.4823 | 1925.5565 | 780 | 200 | 2905.5565 | 72.64% | 95% | 0% | -98.3982 | 657.0841 | -3550 | -400 | -3292.9159 | 82.32% | 73.07% | 95% | 0% | 1836 | -86
[5 empty] | 2019-04-07 | 4 | 2305 | 1781 | -86 | 1 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 1925.5565 | 780 | 200 | 2905.5565 | 72.64% | 95% | 0% | -98.3982 | 705.6414 | -3550 | -400 | -3244.3586 | 81.11% | 73.06% | 95% | 0% | 1867 | -86
[5 empty] | 2019-04-07 | 5 | 2305.5 | 1772 | -86 | 1 | 0 | 1858 | 789.9423 | 789.9423 | 789.9423 | 1925.5565 | 780 | 200 | 2905.5565 | 72.64% | 95% | 0% | -98.3982 | 691.5441 | -3550 | -400 | -3258.4559 | 81.46% | 73.06% | 95% | 0% | 1858 | -86
[5 empty] | 2019-04-07 | 6 | 2306 | 1744 | -86 | 1 | 0 | 1830 | 746.0841 | 746.0841 | 746.0841 | 1925.5565 | 780 | 200 | 2905.5565 | 72.64% | 95% | 0% | -98.3982 | 647.6859 | -3550 | -400 | -3302.3141 | 82.56% | 73.06% | 95% | 0% | 1830 | -86
[5 empty] | 2019-04-07 | 7 | 2306.5 | 1708 | -86 | 1 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 1925.5565 | 780 | 200 | 2905.5565 | 72.64% | 95% | 0% | -98.3982 | 591.2968 | -3550 | -400 | -3358.7032 | 83.97% | 73.05% | 95% | 0% | 1794 | -86
[5 empty] | 2019-04-07 | 8 | 2307 | 1690 | -85 | 1 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 1923.9901 | 780 | 200 | 2903.9901 | 72.6% | 95% | 0% | -97.254 | 562.68 | -3550 | -400 | -3387.32 | 84.68% | 73.05% | 95% | 0% | 1775 | -85
[5 empty] | 2019-04-07 | 9 | 2307.5 | 1663 | -87 | 0 | 0 | 1750 | 620.7749 | 620.7749 | 620.7749 | 1923.9901 | 780 | 200 | 2903.9901 | 72.6% | 95% | 0% | -99.5423 | 521.2326 | -2750 | -200 | -2428.7674 | 60.72% | 73.05% | 95% | 0% | 1750 | -87
[5 empty] | 2019-04-07 | 10 | 2308 | 1636 | -89 | 0 | 0 | 1725 | 581.6158 | 581.6158 | 581.6158 | 1923.9901 | 780 | 200 | 2903.9901 | 72.6% | 95% | 0% | -101.8307 | 479.7852 | -2750 | -200 | -2470.2148 | 61.76% | 73.04% | 95% | 0% | 1725 | -89
[5 empty] | 2019-04-07 | 11 | 2308.5 | 1636 | -91 | 0 | 0 | 1727 | 584.7486 | 584.7486 | 584.7486 | 1923.9901 | 780 | 200 | 2903.9901 | 72.6% | 95% | 0% | -104.119 | 480.6296 | -2750 | -200 | -2469.3704 | 61.73% | 73.04% | 95% | 0% | 1727 | -91
[5 empty] | 2019-04-07 | 12 | 2309 | 1642 | -93 | 0 | 0 | 1735 | 597.2795 | 597.2795 | 597.2795 | 1923.9901 | 780 | 200 | 2903.9901 | 72.6% | 95% | 0% | -106.4073 | 490.8721 | -2750 | -200 | -2459.1279 | 61.48% | 73.04% | 95% | 0% | 1735 | -93
[5 empty] | 2019-04-07 | 13 | 2309.5 | 1694 | -94 | 0 | 0 | 1788 | 680.2968 | 680.2968 | 680.2968 | 1923.9901 | 780 | 200 | 2903.9901 | 72.6% | 95% | 0% | -107.5515 | 572.7453 | -2750 | -200 | -2377.2547 | 59.43% | 73.03% | 95% | 0% | 1788 | -94
[5 empty] | 2019-04-07 | 14 | 2310 | 1721 | -95 | 0 | 0 | 1816 | 724.155 | 724.155 | 724.155 | 1923.9901 | 780 | 200 | 2903.9901 | 72.6% | 95% | 0% | -108.6957 | 615.4593 | -2750 | -200 | -2334.5407 | 58.36% | 73.03% | 95% | 0% | 1816 | -95
[5 empty] | 2019-04-07 | 15 | 2310.5 | 1809 | -101 | 0 | 0 | 1910 | 871.3932 | 871.3932 | 871.3932 | 1923.9901 | 780 | 200 | 2903.9901 | 72.6% | 95% | 0% | -115.5606 | 755.8326 | -2750 | -200 | -2194.1674 | 54.85% | 73.03% | 95% | 0% | 1910 | -101
[5 empty] | 2019-04-07 | 16 | 2311 | 1875 | -114 | 1 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 1923.9901 | 780 | 200 | 2903.9901 | 72.6% | 95% | 0% | -130.4348 | 864.7012 | -3550 | -400 | -3085.2988 | 77.13% | 73.02% | 95% | 0% | 1989 | -114
[5 empty] | 2019-04-07 | 17 | 2311.5 | 1960 | -133 | 1 | 0 | 2093 | 1158.0379 | 1158.0379 | 1158.0379 | 1922.4237 | 780 | 200 | 2902.4237 | 72.56% | 95% | 0% | -152.1739 | 1005.864 | -3550 | -400 | -2944.136 | 73.6% | 73.01% | 95% | 0% | 2093 | -133
[5 empty] | 2019-04-07 | 18 | 2312 | 2018 | -154 | 1 | 0 | 2172 | 1281.7807 | 1281.7807 | 1281.7807 | 1922.4237 | 780 | 200 | 2902.4237 | 72.56% | 95% | 0% | -176.2014 | 1105.5793 | -3550 | -400 | -2844.4207 | 71.11% | 73.01% | 95% | 0% | 2172 | -154
[5 empty] | 2019-04-07 | 19 | 2312.5 | 2058 | -182 | 1 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 1922.4237 | 780 | 200 | 2902.4237 | 72.56% | 95% | 0% | -208.238 | 1180.0555 | -3550 | -400 | -2769.9445 | 69.25% | 73.01% | 95% | 0% | 2240 | -182
[5 empty] | 2019-04-07 | 20 | 2313 | 2065 | -211 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1922.4237 | 780 | 200 | 2902.4237 | 72.56% | 95% | 0% | -241.4188 | 1203.2638 | -3550 | -400 | -2746.7362 | 68.67% | 73.01% | 95% | 0% | 2276 | -211
[5 empty] | 2019-04-07 | 21 | 2313.5 | 2059 | -245 | 1 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 1922.4237 | 780 | 200 | 2902.4237 | 72.56% | 95% | 0% | -280.3204 | 1208.2204 | -3550 | -400 | -2741.7796 | 68.54% | 73% | 95% | 0% | 2304 | -245
[5 empty] | 2019-04-07 | 22 | 2314 | 2006 | -311 | 1 | 0 | 2317 | 1508.9035 | 1508.9035 | 1508.9035 | 1922.4237 | 780 | 200 | 2902.4237 | 72.56% | 95% | 0% | -355.8352 | 1153.0683 | -3550 | -400 | -2796.9317 | 69.92% | 72.99% | 95% | 0% | 2317 | -311
[5 empty] | 2019-04-07 | 23 | 2314.5 | 1971 | -357 | 1 | 0 | 2328 | 1526.1336 | 1526.1336 | 1526.1336 | 1922.4237 | 780 | 200 | 2902.4237 | 72.56% | 95% | 0% | -408.4668 | 1117.6667 | -3550 | -400 | -2832.3333 | 70.81% | 72.99% | 95% | 0% | 2328 | -357
[5 empty] | 2019-04-07 | 24 | 2315 | 1940 | -382 | 1 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 1920.8574 | 780 | 200 | 2900.8574 | 72.52% | 95% | 0% | -437.0709 | 1079.6644 | -3550 | -400 | -2870.3356 | 71.76% | 72.99% | 95% | 0% | 2322 | -382
[5 empty] | 2019-04-07 | 25 | 2315.5 | 1924 | -394 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 1920.8574 | 780 | 200 | 2900.8574 | 72.52% | 95% | 0% | -450.8009 | 1059.669 | -3550 | -400 | -2890.331 | 72.26% | 72.98% | 95% | 0% | 2318 | -394
[5 empty] | 2019-04-07 | 26 | 2316 | 1897 | -413 | 1 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 1920.8574 | 780 | 200 | 2900.8574 | 72.52% | 95% | 0% | -472.54 | 1025.3989 | -3550 | -400 | -2924.6011 | 73.12% | 72.98% | 95% | 0% | 2310 | -413
[5 empty] | 2019-04-07 | 27 | 2316.5 | 1835 | -442 | 1 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 1920.8574 | 780 | 200 | 2900.8574 | 72.52% | 95% | 0% | -505.7208 | 940.5281 | -3550 | -400 | -3009.4719 | 75.24% | 72.98% | 95% | 0% | 2277 | -442
[5 empty] | 2019-04-07 | 28 | 2317 | 1805 | -447 | 1 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 1920.8574 | 780 | 200 | 2900.8574 | 72.52% | 95% | 0% | -511.4416 | 895.6482 | -3550 | -400 | -3054.3518 | 76.36% | 72.98% | 95% | 0% | 2252 | -447
[5 empty] | 2019-04-07 | 29 | 2317.5 | 1833 | -419 | 1 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 1920.8574 | 780 | 200 | 2900.8574 | 72.52% | 95% | 0% | -479.405 | 927.6848 | -3550 | -400 | -3022.3152 | 75.56% | 72.98% | 95% | 0% | 2252 | -419
[5 empty] | 2019-04-07 | 30 | 2318 | 1839 | -389 | 1 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 1919.291 | 780 | 200 | 2899.291 | 72.48% | 95% | 0% | -445.0801 | 924.417 | -3550 | -400 | -3025.583 | 75.64% | 72.97% | 95% | 0% | 2228 | -389
[5 empty] | 2019-04-07 | 31 | 2318.5 | 1874 | -370 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1919.291 | 780 | 200 | 2899.291 | 72.48% | 95% | 0% | -423.341 | 971.218 | -3550 | -400 | -2978.782 | 74.47% | 72.97% | 95% | 0% | 2244 | -370
[5 empty] | 2019-04-07 | 32 | 2319 | 1924 | -340 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 1919.291 | 780 | 200 | 2899.291 | 72.48% | 95% | 0% | -389.016 | 1036.8702 | -3550 | -400 | -2913.1298 | 72.83% | 72.96% | 95% | 0% | 2264 | -340
[5 empty] | 2019-04-07 | 33 | 2319.5 | 2005 | -302 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1919.291 | 780 | 200 | 2899.291 | 72.48% | 95% | 0% | -345.5378 | 1147.7021 | -3550 | -400 | -2802.2979 | 70.06% | 72.95% | 95% | 0% | 2307 | -302
[5 empty] | 2019-04-07 | 34 | 2320 | 2121 | -261 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 1919.291 | 780 | 200 | 2899.291 | 72.48% | 95% | 0% | -298.627 | 1312.0902 | -3550 | -400 | -2637.9098 | 65.95% | 72.95% | 95% | 0% | 2382 | -261
[5 empty] | 2019-04-07 | 35 | 2320.5 | 2232 | -224 | 1 | 0 | 2456 | 1726.6282 | 1726.6282 | 1726.6282 | 1917.7246 | 780 | 200 | 2897.7246 | 72.44% | 95% | 0% | -256.2929 | 1470.3353 | -3550 | -400 | -2479.6647 | 61.99% | 72.94% | 95% | 0% | 2456 | -224
[5 empty] | 2019-04-07 | 36 | 2321 | 2302 | -187 | 1 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 1917.7246 | 780 | 200 | 2897.7246 | 72.44% | 95% | 0% | -213.9588 | 1564.3594 | -3550 | -400 | -2385.6406 | 59.64% | 72.94% | 95% | 0% | 2489 | -187
[5 empty] | 2019-04-07 | 37 | 2321.5 | 2358 | -153 | 1 | 0 | 2511 | 1812.7782 | 1812.7782 | 1812.7782 | 1917.7246 | 780 | 200 | 2897.7246 | 72.44% | 95% | 0% | -175.0572 | 1637.721 | -3550 | -400 | -2312.279 | 57.81% | 72.94% | 95% | 0% | 2511 | -153
[5 empty] | 2019-04-07 | 38 | 2322 | 2389 | -130 | 1 | 0 | 2519 | 1825.3092 | 1825.3092 | 1825.3092 | 1917.7246 | 780 | 200 | 2897.7246 | 72.44% | 95% | 0% | -148.7414 | 1676.5677 | -3550 | -400 | -2273.4323 | 56.84% | 72.94% | 95% | 0% | 2519 | -130
[5 empty] | 2019-04-07 | 39 | 2322.5 | 2427 | -106 | 1 | 0 | 2533 | 1847.2383 | 1847.2383 | 1847.2383 | 1917.7246 | 780 | 200 | 2897.7246 | 72.44% | 95% | 0% | -121.2815 | 1725.9568 | -3550 | -400 | -2224.0432 | 55.6% | 72.93% | 95% | 0% | 2533 | -106
[5 empty] | 2019-04-07 | 40 | 2323 | 2450 | -95 | 1 | 0 | 2545 | 1866.0346 | 1866.0346 | 1866.0346 | 1917.7246 | 780 | 200 | 2897.7246 | 72.44% | 95% | 0% | -108.6957 | 1757.339 | -3550 | -400 | -2192.661 | 54.82% | 72.92% | 95% | 0% | 2545 | -95
[5 empty] | 2019-04-07 | 41 | 2323.5 | 2482 | -93 | 0 | 0 | 2575 | 1913.0256 | 1913.0256 | 1913.0256 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -106.4073 | 1806.6182 | -2750 | -200 | -1143.3818 | 28.58% | 72.91% | 95% | 0% | 2575 | -93
[5 empty] | 2019-04-07 | 42 | 2324 | 2431 | -93 | 1 | 0 | 2524 | 1833.141 | 1833.141 | 1833.141 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -106.4073 | 1726.7337 | -3550 | -400 | -2223.2663 | 55.58% | 72.91% | 95% | 0% | 2524 | -93
[5 empty] | 2019-04-07 | 43 | 2324.5 | 2355 | -93 | 0 | 0 | 2448 | 1714.0973 | 1714.0973 | 1714.0973 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -106.4073 | 1607.69 | -2750 | -200 | -1342.31 | 33.56% | 72.91% | 95% | 0% | 2448 | -93
[5 empty] | 2019-04-07 | 44 | 2325 | 2251 | -93 | 0 | 0 | 2344 | 1551.1954 | 1551.1954 | 1551.1954 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -106.4073 | 1444.7881 | -2750 | -200 | -1505.2119 | 37.63% | 72.91% | 95% | 0% | 2344 | -93
[5 empty] | 2019-04-07 | 45 | 2325.5 | 2154 | -93 | 0 | 0 | 2247 | 1399.258 | 1399.258 | 1399.258 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -106.4073 | 1292.8507 | -2750 | -200 | -1657.1493 | 41.43% | 72.9% | 95% | 0% | 2247 | -93
[5 empty] | 2019-04-07 | 46 | 2326 | 2012 | -93 | 0 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -106.4073 | 1070.427 | -2750 | -200 | -1879.573 | 46.99% | 72.9% | 95% | 0% | 2105 | -93
[5 empty] | 2019-04-07 | 47 | 2326.5 | 1870 | -92 | 0 | 0 | 1962 | 952.8442 | 952.8442 | 952.8442 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -105.2632 | 847.581 | -2750 | -200 | -2102.419 | 52.56% | 72.9% | 95% | 0% | 1962 | -92
[5 empty] | 2019-04-07 | 48 | 2327 | 1770 | -92 | 0 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -105.2632 | 690.9446 | -2750 | -200 | -2259.0554 | 56.48% | 72.9% | 95% | 0% | 1862 | -92
[5 empty] | 2019-04-08 | 1 | 2327.5 | 1693 | -91 | 0 | 0 | 1784 | 674.0313 | 674.0313 | 674.0313 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -104.119 | 569.9123 | -2750 | -200 | -2380.0877 | 59.5% | 72.89% | 95% | 0% | 1784 | -91
[5 empty] | 2019-04-08 | 2 | 2328 | 1654 | -91 | 0 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -104.119 | 508.8241 | -2750 | -200 | -2441.1759 | 61.03% | 72.89% | 95% | 0% | 1745 | -91
[5 empty] | 2019-04-08 | 3 | 2328.5 | 1677 | -90 | 0 | 0 | 1767 | 647.4031 | 647.4031 | 647.4031 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -102.9748 | 544.4283 | -2750 | -200 | -2405.5717 | 60.14% | 72.89% | 95% | 0% | 1767 | -90
[5 empty] | 2019-04-08 | 4 | 2329 | 1721 | -88 | 0 | 0 | 1809 | 713.1904 | 713.1904 | 713.1904 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -100.6865 | 612.5039 | -2750 | -200 | -2337.4961 | 58.44% | 72.88% | 95% | 0% | 1809 | -88
[5 empty] | 2019-04-08 | 5 | 2329.5 | 1727 | -87 | 0 | 0 | 1814 | 721.0223 | 721.0223 | 721.0223 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -99.5423 | 621.4799 | -2750 | -200 | -2328.5201 | 58.21% | 72.88% | 95% | 0% | 1814 | -87
[5 empty] | 2019-04-08 | 6 | 2330 | 1714 | -85 | 0 | 0 | 1799 | 697.5268 | 697.5268 | 697.5268 | 1916.1583 | 780 | 200 | 2896.1583 | 72.4% | 95% | 0% | -97.254 | 600.2728 | -2750 | -200 | -2349.7272 | 58.74% | 72.87% | 95% | 0% | 1799 | -85
[5 empty] | 2019-04-08 | 7 | 2330.5 | 1689 | -84 | 0 | 0 | 1773 | 656.8013 | 656.8013 | 656.8013 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -96.1098 | 560.6915 | -2750 | -200 | -2389.3085 | 59.73% | 72.87% | 95% | 0% | 1773 | -84
[5 empty] | 2019-04-08 | 8 | 2331 | 1673 | -83 | 0 | 0 | 1756 | 630.1731 | 630.1731 | 630.1731 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -94.9657 | 535.2074 | -2750 | -200 | -2414.7926 | 60.37% | 72.87% | 95% | 0% | 1756 | -83
[5 empty] | 2019-04-08 | 9 | 2331.5 | 1667 | -83 | 0 | 0 | 1750 | 620.7749 | 620.7749 | 620.7749 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -94.9657 | 525.8093 | -2750 | -200 | -2424.1907 | 60.6% | 72.86% | 95% | 0% | 1750 | -83
[5 empty] | 2019-04-08 | 10 | 2332 | 1671 | -83 | 0 | 0 | 1754 | 627.0404 | 627.0404 | 627.0404 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -94.9657 | 532.0747 | -2750 | -200 | -2417.9253 | 60.45% | 72.86% | 95% | 0% | 1754 | -83
[5 empty] | 2019-04-08 | 11 | 2332.5 | 1733 | -82 | 0 | 0 | 1815 | 722.5886 | 722.5886 | 722.5886 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -93.8215 | 628.7671 | -2750 | -200 | -2321.2329 | 58.03% | 72.86% | 95% | 0% | 1815 | -82
[5 empty] | 2019-04-08 | 12 | 2333 | 1826 | -82 | 0 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -93.8215 | 774.439 | -2750 | -200 | -2175.561 | 54.39% | 72.85% | 95% | 0% | 1908 | -82
[5 empty] | 2019-04-08 | 13 | 2333.5 | 2043 | -82 | 0 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -93.8215 | 1114.3401 | -2750 | -200 | -1835.6599 | 45.89% | 72.85% | 95% | 0% | 2125 | -82
[5 empty] | 2019-04-08 | 14 | 2334 | 2224 | -83 | 0 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -94.9657 | 1398.2742 | -2750 | -200 | -1551.7258 | 38.79% | 72.84% | 95% | 0% | 2307 | -83
[5 empty] | 2019-04-08 | 15 | 2334.5 | 2439 | -91 | 0 | 0 | 2530 | 1842.5392 | 1842.5392 | 1842.5392 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -104.119 | 1738.4202 | -2750 | -200 | -1211.5798 | 30.29% | 72.83% | 95% | 0% | 2530 | -91
[5 empty] | 2019-04-08 | 16 | 2335 | 2537 | -107 | 0 | 0 | 2644 | 2021.1047 | 2021.1047 | 2021.1047 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -122.4256 | 1898.6791 | -2750 | -200 | -1051.3209 | 26.28% | 72.82% | 95% | 0% | 2644 | -107
[5 empty] | 2019-04-08 | 17 | 2335.5 | 2586 | -132 | 1 | 0 | 2718 | 2137.0157 | 2137.0157 | 2137.0157 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -151.0297 | 1985.9859 | -3550 | -400 | -1964.0141 | 49.1% | 72.82% | 95% | 0% | 2718 | -132
[5 empty] | 2019-04-08 | 18 | 2336 | 2576 | -164 | 1 | 0 | 2740 | 2171.4757 | 2171.4757 | 2171.4757 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -187.643 | 1983.8327 | -3550 | -400 | -1966.1673 | 49.15% | 72.82% | 95% | 0% | 2740 | -164
[5 empty] | 2019-04-08 | 19 | 2336.5 | 2536 | -203 | 1 | 0 | 2739 | 2169.9093 | 2169.9093 | 2169.9093 | 1914.5919 | 780 | 200 | 2894.5919 | 72.36% | 95% | 0% | -232.2654 | 1937.6439 | -3550 | -400 | -2012.3561 | 50.31% | 72.81% | 95% | 0% | 2739 | -203
[5 empty] | 2019-04-08 | 20 | 2337 | 2489 | -242 | 1 | 0 | 2731 | 2157.3784 | 2157.3784 | 2157.3784 | 1913.0256 | 780 | 200 | 2893.0256 | 72.33% | 95% | 0% | -276.8879 | 1880.4905 | -3550 | -400 | -2069.5095 | 51.74% | 72.81% | 95% | 0% | 2731 | -242
[5 empty] | 2019-04-08 | 21 | 2337.5 | 2406 | -291 | 1 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 1913.0256 | 780 | 200 | 2893.0256 | 72.33% | 95% | 0% | -332.9519 | 1771.1701 | -3550 | -400 | -2178.8299 | 54.47% | 72.8% | 95% | 0% | 2697 | -291
[5 empty] | 2019-04-08 | 22 | 2338 | 2328 | -360 | 1 | 0 | 2688 | 2090.0247 | 2090.0247 | 2090.0247 | 1913.0256 | 780 | 200 | 2893.0256 | 72.33% | 95% | 0% | -411.8993 | 1678.1254 | -3550 | -400 | -2271.8746 | 56.8% | 72.8% | 95% | 0% | 2688 | -360
[5 empty] | 2019-04-08 | 23 | 2338.5 | 2285 | -397 | 1 | 0 | 2682 | 2080.6265 | 2080.6265 | 2080.6265 | 1913.0256 | 780 | 200 | 2893.0256 | 72.33% | 95% | 0% | -454.2334 | 1626.3931 | -3550 | -400 | -2323.6069 | 58.09% | 72.8% | 95% | 0% | 2682 | -397
[5 empty] | 2019-04-08 | 24 | 2339 | 2202 | -434 | 1 | 0 | 2636 | 2008.5738 | 2008.5738 | 2008.5738 | 1913.0256 | 780 | 200 | 2893.0256 | 72.33% | 95% | 0% | -496.5675 | 1512.0063 | -3550 | -400 | -2437.9937 | 60.95% | 72.8% | 95% | 0% | 2636 | -434
[5 empty] | 2019-04-08 | 25 | 2339.5 | 2126 | -465 | 1 | 0 | 2591 | 1938.0874 | 1938.0874 | 1938.0874 | 1913.0256 | 780 | 200 | 2893.0256 | 72.33% | 95% | 0% | -532.0366 | 1406.0508 | -3550 | -400 | -2543.9492 | 63.6% | 72.79% | 95% | 0% | 2591 | -465
[5 empty] | 2019-04-08 | 26 | 2340 | 2064 | -485 | 1 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 1913.0256 | 780 | 200 | 2893.0256 | 72.33% | 95% | 0% | -554.9199 | 1317.3802 | -3550 | -400 | -2632.6198 | 65.82% | 72.79% | 95% | 0% | 2549 | -485
[5 empty] | 2019-04-08 | 27 | 2340.5 | 2007 | -502 | 1 | 0 | 2509 | 1809.6455 | 1809.6455 | 1809.6455 | 1913.0256 | 780 | 200 | 2893.0256 | 72.33% | 95% | 0% | -574.3707 | 1235.2748 | -3550 | -400 | -2714.7252 | 67.87% | 72.79% | 95% | 0% | 2509 | -502
[5 empty] | 2019-04-08 | 28 | 2341 | 1954 | -505 | 1 | 0 | 2459 | 1731.3273 | 1731.3273 | 1731.3273 | 1913.0256 | 780 | 200 | 2893.0256 | 72.33% | 95% | 0% | -577.8032 | 1153.5241 | -3550 | -400 | -2796.4759 | 69.91% | 72.79% | 95% | 0% | 2459 | -505
[5 empty] | 2019-04-08 | 29 | 2341.5 | 1948 | -503 | 1 | 0 | 2451 | 1718.7964 | 1718.7964 | 1718.7964 | 1913.0256 | 780 | 200 | 2893.0256 | 72.33% | 95% | 0% | -575.5149 | 1143.2815 | -3550 | -400 | -2806.7185 | 70.17% | 72.78% | 95% | 0% | 2451 | -503
[5 empty] | 2019-04-08 | 30 | 2342 | 1936 | -497 | 1 | 0 | 2433 | 1690.6018 | 1690.6018 | 1690.6018 | 1913.0256 | 780 | 200 | 2893.0256 | 72.33% | 95% | 0% | -568.6499 | 1121.9519 | -3550 | -400 | -2828.0481 | 70.7% | 72.78% | 95% | 0% | 2433 | -497
[5 empty] | 2019-04-08 | 31 | 2342.5 | 1956 | -468 | 1 | 0 | 2424 | 1676.5045 | 1676.5045 | 1676.5045 | 1913.0256 | 780 | 200 | 2893.0256 | 72.33% | 95% | 0% | -535.4691 | 1141.0354 | -3550 | -400 | -2808.9646 | 70.22% | 72.77% | 95% | 0% | 2424 | -468
[5 empty] | 2019-04-08 | 32 | 2343 | 2023 | -433 | 1 | 0 | 2456 | 1726.6282 | 1726.6282 | 1726.6282 | 1911.4592 | 780 | 200 | 2891.4592 | 72.29% | 95% | 0% | -495.4233 | 1231.2049 | -3550 | -400 | -2718.7951 | 67.97% | 72.77% | 95% | 0% | 2456 | -433
[5 empty] | 2019-04-08 | 33 | 2343.5 | 2130 | -382 | 1 | 0 | 2512 | 1814.3446 | 1814.3446 | 1814.3446 | 1911.4592 | 780 | 200 | 2891.4592 | 72.29% | 95% | 0% | -437.0709 | 1377.2737 | -3550 | -400 | -2572.7263 | 64.32% | 72.76% | 95% | 0% | 2512 | -382
[5 empty] | 2019-04-08 | 34 | 2344 | 2270 | -327 | 1 | 0 | 2597 | 1947.4856 | 1947.4856 | 1947.4856 | 1911.4592 | 780 | 200 | 2891.4592 | 72.29% | 95% | 0% | -374.1419 | 1573.3437 | -3550 | -400 | -2376.6563 | 59.42% | 72.76% | 95% | 0% | 2597 | -327
[5 empty] | 2019-04-08 | 35 | 2344.5 | 2383 | -290 | 1 | 0 | 2673 | 2066.5293 | 2066.5293 | 2066.5293 | 1911.4592 | 780 | 200 | 2891.4592 | 72.29% | 95% | 0% | -331.8078 | 1734.7215 | -3550 | -400 | -2215.2785 | 55.38% | 72.76% | 95% | 0% | 2673 | -290
[5 empty] | 2019-04-08 | 36 | 2345 | 2500 | -229 | 1 | 0 | 2729 | 2154.2457 | 2154.2457 | 2154.2457 | 1911.4592 | 780 | 200 | 2891.4592 | 72.29% | 95% | 0% | -262.0137 | 1892.2319 | -3550 | -400 | -2057.7681 | 51.44% | 72.75% | 95% | 0% | 2729 | -229
[5 empty] | 2019-04-08 | 37 | 2345.5 | 2590 | -187 | 1 | 0 | 2777 | 2229.4312 | 2229.4312 | 2229.4312 | 1911.4592 | 780 | 200 | 2891.4592 | 72.29% | 95% | 0% | -213.9588 | 2015.4724 | -3550 | -400 | -1934.5276 | 48.36% | 72.75% | 95% | 0% | 2777 | -187
[5 empty] | 2019-04-08 | 38 | 2346 | 2666 | -139 | 1 | 0 | 2805 | 2273.2894 | 2273.2894 | 2273.2894 | 1911.4592 | 780 | 200 | 2891.4592 | 72.29% | 95% | 0% | -159.0389 | 2114.2505 | -3550 | -400 | -1835.7495 | 45.89% | 72.75% | 95% | 0% | 2805 | -139
[5 empty] | 2019-04-08 | 39 | 2346.5 | 2717 | -107 | 1 | 0 | 2824 | 2303.0503 | 2303.0503 | 2303.0503 | 1909.8928 | 780 | 200 | 2889.8928 | 72.25% | 95% | 0% | -122.4256 | 2180.6247 | -3550 | -400 | -1769.3753 | 44.23% | 72.75% | 95% | 0% | 2824 | -107
[5 empty] | 2019-04-08 | 40 | 2347 | 2742 | -91 | 1 | 0 | 2833 | 2317.1476 | 2317.1476 | 2317.1476 | 1909.8928 | 780 | 200 | 2889.8928 | 72.25% | 95% | 0% | -104.119 | 2213.0286 | -3550 | -400 | -1736.9714 | 43.42% | 72.74% | 95% | 0% | 2833 | -91
[5 empty] | 2019-04-08 | 41 | 2347.5 | 2745 | -90 | 1 | 0 | 2835 | 2320.2803 | 2320.2803 | 2320.2803 | 1909.8928 | 780 | 200 | 2889.8928 | 72.25% | 95% | 0% | -102.9748 | 2217.3055 | -3550 | -400 | -1732.6945 | 43.32% | 72.74% | 95% | 0% | 2835 | -90
[5 empty] | 2019-04-08 | 42 | 2348 | 2704 | -90 | 0 | 0 | 2794 | 2256.0594 | 2256.0594 | 2256.0594 | 1909.8928 | 780 | 200 | 2889.8928 | 72.25% | 95% | 0% | -102.9748 | 2153.0845 | -2750 | -200 | -796.9155 | 19.92% | 72.74% | 95% | 0% | 2794 | -90
[5 empty] | 2019-04-08 | 43 | 2348.5 | 2613 | -92 | 0 | 0 | 2705 | 2116.6529 | 2116.6529 | 2116.6529 | 1909.8928 | 780 | 200 | 2889.8928 | 72.25% | 95% | 0% | -105.2632 | 2011.3898 | -2750 | -200 | -938.6102 | 23.47% | 72.74% | 95% | 0% | 2705 | -92
[5 empty] | 2019-04-08 | 44 | 2349 | 2458 | -93 | 0 | 0 | 2551 | 1875.4328 | 1875.4328 | 1875.4328 | 1909.8928 | 780 | 200 | 2889.8928 | 72.25% | 95% | 0% | -106.4073 | 1769.0255 | -2750 | -200 | -1180.9745 | 29.52% | 72.73% | 95% | 0% | 2551 | -93
[5 empty] | 2019-04-08 | 45 | 2349.5 | 2311 | -94 | 0 | 0 | 2405 | 1646.7436 | 1646.7436 | 1646.7436 | 1909.8928 | 780 | 200 | 2889.8928 | 72.25% | 95% | 0% | -107.5515 | 1539.1921 | -2750 | -200 | -1410.8079 | 35.27% | 72.72% | 95% | 0% | 2405 | -94
[5 empty] | 2019-04-08 | 46 | 2350 | 2150 | -95 | 0 | 0 | 2245 | 1396.1253 | 1396.1253 | 1396.1253 | 1908.3265 | 780 | 200 | 2888.3265 | 72.21% | 95% | 0% | -108.6957 | 1287.4297 | -2750 | -200 | -1662.5703 | 41.56% | 72.72% | 95% | 0% | 2245 | -95
[5 empty] | 2019-04-08 | 47 | 2350.5 | 1994 | -96 | 0 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 1908.3265 | 780 | 200 | 2888.3265 | 72.21% | 95% | 0% | -109.8398 | 1043.499 | -2750 | -200 | -1906.501 | 47.66% | 72.72% | 95% | 0% | 2090 | -96
[5 empty] | 2019-04-08 | 48 | 2351 | 1864 | -97 | 0 | 0 | 1961 | 951.2778 | 951.2778 | 951.2778 | 1908.3265 | 780 | 200 | 2888.3265 | 72.21% | 95% | 0% | -110.984 | 840.2938 | -2750 | -200 | -2109.7062 | 52.74% | 72.72% | 95% | 0% | 1961 | -97
[5 empty] | 2019-04-09 | 1 | 2351.5 | 1785 | -96 | 0 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 1908.3265 | 780 | 200 | 2888.3265 | 72.21% | 95% | 0% | -109.8398 | 716.1289 | -2750 | -200 | -2233.8711 | 55.85% | 72.72% | 95% | 0% | 1881 | -96
[5 empty] | 2019-04-09 | 2 | 2352 | 1746 | -95 | 0 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 1908.3265 | 780 | 200 | 2888.3265 | 72.21% | 95% | 0% | -108.6957 | 654.6184 | -2750 | -200 | -2295.3816 | 57.38% | 72.71% | 95% | 0% | 1841 | -95
[5 empty] | 2019-04-09 | 3 | 2352.5 | 1747 | -95 | 0 | 0 | 1842 | 764.8805 | 764.8805 | 764.8805 | 1908.3265 | 780 | 200 | 2888.3265 | 72.21% | 95% | 0% | -108.6957 | 656.1848 | -2750 | -200 | -2293.8152 | 57.35% | 72.7% | 95% | 0% | 1842 | -95
[5 empty] | 2019-04-09 | 4 | 2353 | 1790 | -95 | 0 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 1908.3265 | 780 | 200 | 2888.3265 | 72.21% | 95% | 0% | -108.6957 | 723.5385 | -2750 | -200 | -2226.4615 | 55.66% | 72.7% | 95% | 0% | 1885 | -95
[5 empty] | 2019-04-09 | 5 | 2353.5 | 1781 | -96 | 0 | 0 | 1877 | 819.7032 | 819.7032 | 819.7032 | 1908.3265 | 780 | 200 | 2888.3265 | 72.21% | 95% | 0% | -109.8398 | 709.8634 | -2750 | -200 | -2240.1366 | 56% | 72.7% | 95% | 0% | 1877 | -96
[5 empty] | 2019-04-09 | 6 | 2354 | 1747 | -97 | 0 | 0 | 1844 | 768.0132 | 768.0132 | 768.0132 | 1908.3265 | 780 | 200 | 2888.3265 | 72.21% | 95% | 0% | -110.984 | 657.0292 | -2750 | -200 | -2292.9708 | 57.32% | 72.7% | 95% | 0% | 1844 | -97
[5 empty] | 2019-04-09 | 7 | 2354.5 | 1719 | -98 | 0 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 1906.7601 | 780 | 200 | 2886.7601 | 72.17% | 95% | 0% | -112.1281 | 613.5932 | -2750 | -200 | -2336.4068 | 58.41% | 72.7% | 95% | 0% | 1817 | -98
[5 empty] | 2019-04-09 | 8 | 2355 | 1698 | -99 | 0 | 0 | 1797 | 694.3941 | 694.3941 | 694.3941 | 1906.7601 | 780 | 200 | 2886.7601 | 72.17% | 95% | 0% | -113.2723 | 581.1218 | -2750 | -200 | -2368.8782 | 59.22% | 72.7% | 95% | 0% | 1797 | -99
[5 empty] | 2019-04-09 | 9 | 2355.5 | 1690 | -100 | 0 | 0 | 1790 | 683.4295 | 683.4295 | 683.4295 | 1906.7601 | 780 | 200 | 2886.7601 | 72.17% | 95% | 0% | -114.4165 | 569.013 | -2750 | -200 | -2380.987 | 59.52% | 72.69% | 95% | 0% | 1790 | -100
[5 empty] | 2019-04-09 | 10 | 2356 | 1692 | -101 | 0 | 0 | 1793 | 688.1286 | 688.1286 | 688.1286 | 1906.7601 | 780 | 200 | 2886.7601 | 72.17% | 95% | 0% | -115.5606 | 572.568 | -2750 | -200 | -2377.432 | 59.44% | 72.69% | 95% | 0% | 1793 | -101
[5 empty] | 2019-04-09 | 11 | 2356.5 | 1738 | -104 | 0 | 0 | 1842 | 764.8805 | 764.8805 | 764.8805 | 1906.7601 | 780 | 200 | 2886.7601 | 72.17% | 95% | 0% | -118.9931 | 645.8873 | -2750 | -200 | -2304.1127 | 57.6% | 72.69% | 95% | 0% | 1842 | -104
[5 empty] | 2019-04-09 | 12 | 2357 | 1827 | -106 | 0 | 0 | 1933 | 907.4196 | 907.4196 | 907.4196 | 1906.7601 | 780 | 200 | 2886.7601 | 72.17% | 95% | 0% | -121.2815 | 786.1382 | -2750 | -200 | -2163.8618 | 54.1% | 72.69% | 95% | 0% | 1933 | -106
[5 empty] | 2019-04-09 | 13 | 2357.5 | 2023 | -109 | 0 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 1906.7601 | 780 | 200 | 2886.7601 | 72.17% | 95% | 0% | -124.714 | 1094.4122 | -2750 | -200 | -1855.5878 | 46.39% | 72.68% | 95% | 0% | 2132 | -109
[5 empty] | 2019-04-09 | 14 | 2358 | 2190 | -114 | 0 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 1905.1937 | 780 | 200 | 2885.1937 | 72.13% | 95% | 0% | -130.4348 | 1358.106 | -2750 | -200 | -1591.894 | 39.8% | 72.68% | 95% | 0% | 2304 | -114
[5 empty] | 2019-04-09 | 15 | 2358.5 | 2398 | -127 | 0 | 0 | 2525 | 1834.7073 | 1834.7073 | 1834.7073 | 1905.1937 | 780 | 200 | 2885.1937 | 72.13% | 95% | 0% | -145.3089 | 1689.3984 | -2750 | -200 | -1260.6016 | 31.52% | 72.68% | 95% | 0% | 2525 | -127
[5 empty] | 2019-04-09 | 16 | 2359 | 2499 | -147 | 0 | 0 | 2646 | 2024.2374 | 2024.2374 | 2024.2374 | 1905.1937 | 780 | 200 | 2885.1937 | 72.13% | 95% | 0% | -168.1922 | 1856.0452 | -2750 | -200 | -1093.9548 | 27.35% | 72.68% | 95% | 0% | 2646 | -147
[5 empty] | 2019-04-09 | 17 | 2359.5 | 2571 | -175 | 1 | 0 | 2746 | 2180.8739 | 2180.8739 | 2180.8739 | 1905.1937 | 780 | 200 | 2885.1937 | 72.13% | 95% | 0% | -200.2288 | 1980.645 | -3550 | -400 | -1969.355 | 49.23% | 72.68% | 95% | 0% | 2746 | -175
[5 empty] | 2019-04-09 | 18 | 2360 | 2528 | -209 | 1 | 0 | 2737 | 2166.7766 | 2166.7766 | 2166.7766 | 1905.1937 | 780 | 200 | 2885.1937 | 72.13% | 95% | 0% | -239.1304 | 1927.6462 | -3550 | -400 | -2022.3538 | 50.56% | 72.67% | 95% | 0% | 2737 | -209
[5 empty] | 2019-04-09 | 19 | 2360.5 | 2487 | -251 | 1 | 0 | 2738 | 2168.343 | 2168.343 | 2168.343 | 1905.1937 | 780 | 200 | 2885.1937 | 72.13% | 95% | 0% | -287.1854 | 1881.1576 | -3550 | -400 | -2068.8424 | 51.72% | 72.67% | 95% | 0% | 2738 | -251
[5 empty] | 2019-04-09 | 20 | 2361 | 2428 | -291 | 1 | 0 | 2719 | 2138.582 | 2138.582 | 2138.582 | 1905.1937 | 780 | 200 | 2885.1937 | 72.13% | 95% | 0% | -332.9519 | 1805.6301 | -3550 | -400 | -2144.3699 | 53.61% | 72.67% | 95% | 0% | 2719 | -291
[5 empty] | 2019-04-09 | 21 | 2361.5 | 2381 | -324 | 1 | 0 | 2705 | 2116.6529 | 2116.6529 | 2116.6529 | 1905.1937 | 780 | 200 | 2885.1937 | 72.13% | 95% | 0% | -370.7094 | 1745.9435 | -3550 | -400 | -2204.0565 | 55.1% | 72.67% | 95% | 0% | 2705 | -324
[5 empty] | 2019-04-09 | 22 | 2362 | 2329 | -358 | 1 | 0 | 2687 | 2088.4584 | 2088.4584 | 2088.4584 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -409.611 | 1678.8474 | -3550 | -400 | -2271.1526 | 56.78% | 72.67% | 95% | 0% | 2687 | -358
[5 empty] | 2019-04-09 | 23 | 2362.5 | 2270 | -389 | 1 | 0 | 2659 | 2044.6002 | 2044.6002 | 2044.6002 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -445.0801 | 1599.5201 | -3550 | -400 | -2350.4799 | 58.76% | 72.66% | 95% | 0% | 2659 | -389
[5 empty] | 2019-04-09 | 24 | 2363 | 2228 | -410 | 1 | 0 | 2638 | 2011.7065 | 2011.7065 | 2011.7065 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -469.1076 | 1542.599 | -3550 | -400 | -2407.401 | 60.19% | 72.66% | 95% | 0% | 2638 | -410
[5 empty] | 2019-04-09 | 25 | 2363.5 | 2205 | -427 | 1 | 0 | 2632 | 2002.3083 | 2002.3083 | 2002.3083 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -488.5584 | 1513.75 | -3550 | -400 | -2436.25 | 60.91% | 72.66% | 95% | 0% | 2632 | -427
[5 empty] | 2019-04-09 | 26 | 2364 | 2151 | -452 | 1 | 0 | 2603 | 1956.8838 | 1956.8838 | 1956.8838 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -517.1625 | 1439.7213 | -3550 | -400 | -2510.2787 | 62.76% | 72.66% | 95% | 0% | 2603 | -452
[5 empty] | 2019-04-09 | 27 | 2364.5 | 2127 | -449 | 1 | 0 | 2576 | 1914.5919 | 1914.5919 | 1914.5919 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -513.73 | 1400.8619 | -3550 | -400 | -2549.1381 | 63.73% | 72.66% | 95% | 0% | 2576 | -449
[5 empty] | 2019-04-09 | 28 | 2365 | 2111 | -449 | 1 | 0 | 2560 | 1889.5301 | 1889.5301 | 1889.5301 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -513.73 | 1375.8001 | -3550 | -400 | -2574.1999 | 64.35% | 72.66% | 95% | 0% | 2560 | -449
[5 empty] | 2019-04-09 | 29 | 2365.5 | 2117 | -433 | 1 | 0 | 2550 | 1873.8664 | 1873.8664 | 1873.8664 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -495.4233 | 1378.4431 | -3550 | -400 | -2571.5569 | 64.29% | 72.65% | 95% | 0% | 2550 | -433
[5 empty] | 2019-04-09 | 30 | 2366 | 2100 | -439 | 1 | 0 | 2539 | 1856.6364 | 1856.6364 | 1856.6364 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -502.2883 | 1354.3481 | -3550 | -400 | -2595.6519 | 64.89% | 72.65% | 95% | 0% | 2539 | -439
[5 empty] | 2019-04-09 | 31 | 2366.5 | 2130 | -428 | 1 | 0 | 2558 | 1886.3974 | 1886.3974 | 1886.3974 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -489.7025 | 1396.6948 | -3550 | -400 | -2553.3052 | 63.83% | 72.65% | 95% | 0% | 2558 | -428
[5 empty] | 2019-04-09 | 32 | 2367 | 2190 | -403 | 1 | 0 | 2593 | 1941.2201 | 1941.2201 | 1941.2201 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -461.0984 | 1480.1217 | -3550 | -400 | -2469.8783 | 61.75% | 72.64% | 95% | 0% | 2593 | -403
[5 empty] | 2019-04-09 | 33 | 2367.5 | 2252 | -371 | 1 | 0 | 2623 | 1988.211 | 1988.211 | 1988.211 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -424.4851 | 1563.7259 | -3550 | -400 | -2386.2741 | 59.66% | 72.64% | 95% | 0% | 2623 | -371
[5 empty] | 2019-04-09 | 34 | 2368 | 2356 | -334 | 1 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 1903.6274 | 780 | 200 | 2883.6274 | 72.09% | 95% | 0% | -382.151 | 1711.0064 | -3550 | -400 | -2238.9936 | 55.97% | 72.64% | 95% | 0% | 2690 | -334
[5 empty] | 2019-04-09 | 35 | 2368.5 | 2452 | -301 | 1 | 0 | 2753 | 2191.8384 | 2191.8384 | 2191.8384 | 1902.061 | 780 | 200 | 2882.061 | 72.05% | 95% | 0% | -344.3936 | 1847.4448 | -3550 | -400 | -2102.5552 | 52.56% | 72.64% | 95% | 0% | 2753 | -301
[5 empty] | 2019-04-09 | 36 | 2369 | 2538 | -257 | 1 | 0 | 2795 | 2257.6257 | 2257.6257 | 2257.6257 | 1902.061 | 780 | 200 | 2882.061 | 72.05% | 95% | 0% | -294.0503 | 1963.5754 | -3550 | -400 | -1986.4246 | 49.66% | 72.64% | 95% | 0% | 2795 | -257
[5 empty] | 2019-04-09 | 37 | 2369.5 | 2605 | -207 | 1 | 0 | 2812 | 2284.2539 | 2284.2539 | 2284.2539 | 1902.061 | 780 | 200 | 2882.061 | 72.05% | 95% | 0% | -236.8421 | 2047.4118 | -3550 | -400 | -1902.5882 | 47.56% | 72.64% | 95% | 0% | 2812 | -207
[5 empty] | 2019-04-09 | 38 | 2370 | 2666 | -161 | 1 | 0 | 2827 | 2307.7494 | 2307.7494 | 2307.7494 | 1902.061 | 780 | 200 | 2882.061 | 72.05% | 95% | 0% | -184.2105 | 2123.5389 | -3550 | -400 | -1826.4611 | 45.66% | 72.64% | 95% | 0% | 2827 | -161
[5 empty] | 2019-04-09 | 39 | 2370.5 | 2714 | -129 | 1 | 0 | 2843 | 2332.8112 | 2332.8112 | 2332.8112 | 1902.061 | 780 | 200 | 2882.061 | 72.05% | 95% | 0% | -147.5973 | 2185.214 | -3550 | -400 | -1764.786 | 44.12% | 72.63% | 95% | 0% | 2843 | -129
[5 empty] | 2019-04-09 | 40 | 2371 | 2757 | -112 | 1 | 0 | 2869 | 2373.5367 | 2373.5367 | 2373.5367 | 1902.061 | 780 | 200 | 2882.061 | 72.05% | 95% | 0% | -128.1465 | 2245.3902 | -3550 | -400 | -1704.6098 | 42.62% | 72.63% | 95% | 0% | 2869 | -112
[5 empty] | 2019-04-09 | 41 | 2371.5 | 2769 | -110 | 1 | 0 | 2879 | 2389.2003 | 2389.2003 | 2389.2003 | 1902.061 | 780 | 200 | 2882.061 | 72.05% | 95% | 0% | -125.8581 | 2263.3422 | -3550 | -400 | -1686.6578 | 42.17% | 72.63% | 95% | 0% | 2879 | -110
[5 empty] | 2019-04-09 | 42 | 2372 | 2732 | -110 | 1 | 0 | 2842 | 2331.2448 | 2331.2448 | 2331.2448 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -125.8581 | 2205.3867 | -3550 | -400 | -1744.6133 | 43.62% | 72.63% | 95% | 0% | 2842 | -110
[5 empty] | 2019-04-09 | 43 | 2372.5 | 2639 | -109 | 0 | 0 | 2748 | 2184.0066 | 2184.0066 | 2184.0066 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -124.714 | 2059.2926 | -2750 | -200 | -890.7074 | 22.27% | 72.63% | 95% | 0% | 2748 | -109
[5 empty] | 2019-04-09 | 44 | 2373 | 2474 | -107 | 0 | 0 | 2581 | 1922.4237 | 1922.4237 | 1922.4237 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -122.4256 | 1799.9981 | -2750 | -200 | -1150.0019 | 28.75% | 72.63% | 95% | 0% | 2581 | -107
[5 empty] | 2019-04-09 | 45 | 2373.5 | 2339 | -105 | 0 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -120.1373 | 1587.6945 | -2750 | -200 | -1362.3055 | 34.06% | 72.63% | 95% | 0% | 2444 | -105
[5 empty] | 2019-04-09 | 46 | 2374 | 2189 | -103 | 0 | 0 | 2292 | 1469.7444 | 1469.7444 | 1469.7444 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -117.849 | 1351.8955 | -2750 | -200 | -1598.1045 | 39.95% | 72.63% | 95% | 0% | 2292 | -103
[5 empty] | 2019-04-09 | 47 | 2374.5 | 2034 | -100 | 0 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -114.4165 | 1107.8424 | -2750 | -200 | -1842.1576 | 46.05% | 72.63% | 95% | 0% | 2134 | -100
[5 empty] | 2019-04-09 | 48 | 2375 | 1914 | -97 | 0 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -110.984 | 918.6121 | -2750 | -200 | -2031.3879 | 50.78% | 72.62% | 95% | 0% | 2011 | -97
[5 empty] | 2019-04-10 | 1 | 2375.5 | 1832 | -93 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -106.4073 | 788.4814 | -2750 | -200 | -2161.5186 | 54.04% | 72.61% | 95% | 0% | 1925 | -93
[5 empty] | 2019-04-10 | 2 | 2376 | 1796 | -90 | 0 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -102.9748 | 730.8257 | -2750 | -200 | -2219.1743 | 55.48% | 72.61% | 95% | 0% | 1886 | -90
[5 empty] | 2019-04-10 | 3 | 2376.5 | 1815 | -87 | 0 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -99.5423 | 759.32 | -2750 | -200 | -2190.68 | 54.77% | 72.61% | 95% | 0% | 1902 | -87
[5 empty] | 2019-04-10 | 4 | 2377 | 1863 | -84 | 0 | 0 | 1947 | 929.3487 | 929.3487 | 929.3487 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -96.1098 | 833.2389 | -2750 | -200 | -2116.7611 | 52.92% | 72.6% | 95% | 0% | 1947 | -84
[5 empty] | 2019-04-10 | 5 | 2377.5 | 1862 | -83 | 0 | 0 | 1945 | 926.216 | 926.216 | 926.216 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -94.9657 | 831.2503 | -2750 | -200 | -2118.7497 | 52.97% | 72.6% | 95% | 0% | 1945 | -83
[5 empty] | 2019-04-10 | 6 | 2378 | 1840 | -81 | 0 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 1900.4946 | 780 | 200 | 2880.4946 | 72.01% | 95% | 0% | -92.6773 | 795.9459 | -2750 | -200 | -2154.0541 | 53.85% | 72.6% | 95% | 0% | 1921 | -81
[5 empty] | 2019-04-10 | 7 | 2378.5 | 1821 | -80 | 0 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 1898.9283 | 780 | 200 | 2878.9283 | 71.97% | 95% | 0% | -91.5332 | 765.7628 | -2750 | -200 | -2184.2372 | 54.61% | 72.6% | 95% | 0% | 1901 | -80
[5 empty] | 2019-04-10 | 8 | 2379 | 1817 | -79 | 0 | 0 | 1896 | 849.4641 | 849.4641 | 849.4641 | 1898.9283 | 780 | 200 | 2878.9283 | 71.97% | 95% | 0% | -90.389 | 759.0751 | -2750 | -200 | -2190.9249 | 54.77% | 72.58% | 95% | 0% | 1896 | -79
[5 empty] | 2019-04-10 | 9 | 2379.5 | 1811 | -78 | 0 | 0 | 1889 | 838.4996 | 838.4996 | 838.4996 | 1898.9283 | 780 | 200 | 2878.9283 | 71.97% | 95% | 0% | -89.2449 | 749.2547 | -2750 | -200 | -2200.7453 | 55.02% | 72.58% | 95% | 0% | 1889 | -78
[5 empty] | 2019-04-10 | 10 | 2380 | 1820 | -77 | 0 | 0 | 1897 | 851.0305 | 851.0305 | 851.0305 | 1898.9283 | 780 | 200 | 2878.9283 | 71.97% | 95% | 0% | -88.1007 | 762.9298 | -2750 | -200 | -2187.0702 | 54.68% | 72.58% | 95% | 0% | 1897 | -77
[5 empty] | 2019-04-10 | 11 | 2380.5 | 1870 | -76 | 0 | 0 | 1946 | 927.7824 | 927.7824 | 927.7824 | 1898.9283 | 780 | 200 | 2878.9283 | 71.97% | 95% | 0% | -86.9565 | 840.8258 | -2750 | -200 | -2109.1742 | 52.73% | 72.57% | 95% | 0% | 1946 | -76
[5 empty] | 2019-04-10 | 12 | 2381 | 1945 | -75 | 0 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 1898.9283 | 780 | 200 | 2878.9283 | 71.97% | 95% | 0% | -85.8124 | 957.881 | -2750 | -200 | -1992.119 | 49.8% | 72.56% | 95% | 0% | 2020 | -75
[5 empty] | 2019-04-10 | 13 | 2381.5 | 2117 | -74 | 0 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 1898.9283 | 780 | 200 | 2878.9283 | 71.97% | 95% | 0% | -84.6682 | 1226.8734 | -2750 | -200 | -1723.1266 | 43.08% | 72.56% | 95% | 0% | 2191 | -74
[5 empty] | 2019-04-10 | 14 | 2382 | 2304 | -81 | 0 | 0 | 2385 | 1615.4163 | 1615.4163 | 1615.4163 | 1898.9283 | 780 | 200 | 2878.9283 | 71.97% | 95% | 0% | -92.6773 | 1522.739 | -2750 | -200 | -1427.261 | 35.68% | 72.56% | 95% | 0% | 2385 | -81
[5 empty] | 2019-04-10 | 15 | 2382.5 | 2510 | -106 | 0 | 0 | 2616 | 1977.2465 | 1977.2465 | 1977.2465 | 1898.9283 | 780 | 200 | 2878.9283 | 71.97% | 95% | 0% | -121.2815 | 1855.965 | -2750 | -200 | -1094.035 | 27.35% | 72.55% | 95% | 0% | 2616 | -106
[5 empty] | 2019-04-10 | 16 | 2383 | 2549 | -143 | 1 | 0 | 2692 | 2096.2902 | 2096.2902 | 2096.2902 | 1898.9283 | 780 | 200 | 2878.9283 | 71.97% | 95% | 0% | -163.6156 | 1932.6746 | -3550 | -400 | -2017.3254 | 50.43% | 72.55% | 95% | 0% | 2692 | -143
[5 empty] | 2019-04-10 | 17 | 2383.5 | 2552 | -187 | 1 | 0 | 2739 | 2169.9093 | 2169.9093 | 2169.9093 | 1898.9283 | 780 | 200 | 2878.9283 | 71.97% | 95% | 0% | -213.9588 | 1955.9505 | -3550 | -400 | -1994.0495 | 49.85% | 72.54% | 95% | 0% | 2739 | -187
[5 empty] | 2019-04-10 | 18 | 2384 | 2493 | -237 | 1 | 0 | 2730 | 2155.812 | 2155.812 | 2155.812 | 1897.3619 | 780 | 200 | 2877.3619 | 71.93% | 95% | 0% | -271.167 | 1884.645 | -3550 | -400 | -2065.355 | 51.63% | 72.54% | 95% | 0% | 2730 | -237
[5 empty] | 2019-04-10 | 19 | 2384.5 | 2420 | -295 | 1 | 0 | 2715 | 2132.3166 | 2132.3166 | 2132.3166 | 1897.3619 | 780 | 200 | 2877.3619 | 71.93% | 95% | 0% | -337.5286 | 1794.788 | -3550 | -400 | -2155.212 | 53.88% | 72.54% | 95% | 0% | 2715 | -295
[5 empty] | 2019-04-10 | 20 | 2385 | 2358 | -342 | 1 | 0 | 2700 | 2108.8211 | 2108.8211 | 2108.8211 | 1897.3619 | 780 | 200 | 2877.3619 | 71.93% | 95% | 0% | -391.3043 | 1717.5168 | -3550 | -400 | -2232.4832 | 55.81% | 72.54% | 95% | 0% | 2700 | -342
[5 empty] | 2019-04-10 | 21 | 2385.5 | 2266 | -397 | 1 | 0 | 2663 | 2050.8656 | 2050.8656 | 2050.8656 | 1897.3619 | 780 | 200 | 2877.3619 | 71.93% | 95% | 0% | -454.2334 | 1596.6322 | -3550 | -400 | -2353.3678 | 58.83% | 72.54% | 95% | 0% | 2663 | -397
[5 empty] | 2019-04-10 | 22 | 2386 | 2091 | -516 | 1 | 0 | 2607 | 1963.1492 | 1963.1492 | 1963.1492 | 1897.3619 | 780 | 200 | 2877.3619 | 71.93% | 95% | 0% | -590.389 | 1372.7602 | -3550 | -400 | -2577.2398 | 64.43% | 72.54% | 95% | 0% | 2607 | -516
[5 empty] | 2019-04-10 | 23 | 2386.5 | 1990 | -565 | 1 | 0 | 2555 | 1881.6983 | 1881.6983 | 1881.6983 | 1897.3619 | 780 | 200 | 2877.3619 | 71.93% | 95% | 0% | -646.4531 | 1235.2452 | -3550 | -400 | -2714.7548 | 67.87% | 72.53% | 95% | 0% | 2555 | -565
[5 empty] | 2019-04-10 | 24 | 2387 | 1883 | -628 | 1 | 0 | 2511 | 1812.7782 | 1812.7782 | 1812.7782 | 1897.3619 | 780 | 200 | 2877.3619 | 71.93% | 95% | 0% | -718.5355 | 1094.2428 | -3550 | -400 | -2855.7572 | 71.39% | 72.53% | 95% | 0% | 2511 | -628
[5 empty] | 2019-04-10 | 25 | 2387.5 | 1811 | -668 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 1897.3619 | 780 | 200 | 2877.3619 | 71.93% | 95% | 0% | -764.3021 | 998.3525 | -3550 | -400 | -2951.6475 | 73.79% | 72.53% | 95% | 0% | 2479 | -668
[5 empty] | 2019-04-10 | 26 | 2388 | 1675 | -726 | 1 | 0 | 2401 | 1640.4782 | 1640.4782 | 1640.4782 | 1897.3619 | 780 | 200 | 2877.3619 | 71.93% | 95% | 0% | -830.6636 | 809.8145 | -3550 | -400 | -3140.1855 | 78.5% | 72.53% | 95% | 0% | 2401 | -726
[5 empty] | 2019-04-10 | 27 | 2388.5 | 1590 | -751 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -859.2677 | 687.2286 | -3550 | -400 | -3262.7714 | 81.57% | 72.53% | 95% | 0% | 2341 | -751
[5 empty] | 2019-04-10 | 28 | 2389 | 1535 | -741 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -847.8261 | 596.8565 | -3550 | -400 | -3353.1435 | 83.83% | 72.53% | 95% | 0% | 2276 | -741
[5 empty] | 2019-04-10 | 29 | 2389.5 | 1520 | -729 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -834.0961 | 568.2947 | -3550 | -400 | -3381.7053 | 84.54% | 72.52% | 95% | 0% | 2249 | -729
[5 empty] | 2019-04-10 | 30 | 2390 | 1511 | -717 | 1 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -820.3661 | 549.131 | -3550 | -400 | -3400.869 | 85.02% | 72.51% | 95% | 0% | 2228 | -717
[5 empty] | 2019-04-10 | 31 | 2390.5 | 1556 | -670 | 1 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -766.5904 | 599.774 | -3550 | -400 | -3350.226 | 83.76% | 72.51% | 95% | 0% | 2226 | -670
[5 empty] | 2019-04-10 | 32 | 2391 | 1664 | -606 | 1 | 0 | 2270 | 1435.2844 | 1435.2844 | 1435.2844 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -693.3638 | 741.9206 | -3550 | -400 | -3208.0794 | 80.2% | 72.51% | 95% | 0% | 2270 | -606
[5 empty] | 2019-04-10 | 33 | 2391.5 | 1790 | -536 | 1 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -613.2723 | 909.7285 | -3550 | -400 | -3040.2715 | 76.01% | 72.51% | 95% | 0% | 2326 | -536
[5 empty] | 2019-04-10 | 34 | 2392 | 1944 | -468 | 1 | 0 | 2412 | 1657.7082 | 1657.7082 | 1657.7082 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -535.4691 | 1122.2391 | -3550 | -400 | -2827.7609 | 70.69% | 72.51% | 95% | 0% | 2412 | -468
[5 empty] | 2019-04-10 | 35 | 2392.5 | 2142 | -393 | 1 | 0 | 2535 | 1850.371 | 1850.371 | 1850.371 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -449.6568 | 1400.7142 | -3550 | -400 | -2549.2858 | 63.73% | 72.5% | 95% | 0% | 2535 | -393
[5 empty] | 2019-04-10 | 36 | 2393 | 2303 | -314 | 1 | 0 | 2617 | 1978.8129 | 1978.8129 | 1978.8129 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -359.2677 | 1619.5451 | -3550 | -400 | -2330.4549 | 58.26% | 72.49% | 95% | 0% | 2617 | -314
[5 empty] | 2019-04-10 | 37 | 2393.5 | 2460 | -233 | 1 | 0 | 2693 | 2097.8566 | 2097.8566 | 2097.8566 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -266.5904 | 1831.2662 | -3550 | -400 | -2118.7338 | 52.97% | 72.49% | 95% | 0% | 2693 | -233
[5 empty] | 2019-04-10 | 38 | 2394 | 2561 | -159 | 1 | 0 | 2720 | 2140.1484 | 2140.1484 | 2140.1484 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -181.9222 | 1958.2262 | -3550 | -400 | -1991.7738 | 49.79% | 72.48% | 95% | 0% | 2720 | -159
[5 empty] | 2019-04-10 | 39 | 2394.5 | 2662 | -96 | 1 | 0 | 2758 | 2199.6702 | 2199.6702 | 2199.6702 | 1895.7955 | 780 | 200 | 2875.7955 | 71.89% | 95% | 0% | -109.8398 | 2089.8304 | -3550 | -400 | -1860.1696 | 46.5% | 72.48% | 95% | 0% | 2758 | -96
[5 empty] | 2019-04-10 | 40 | 2395 | 2708 | -65 | 1 | 0 | 2773 | 2223.1657 | 2223.1657 | 2223.1657 | 1894.2292 | 780 | 200 | 2874.2292 | 71.86% | 95% | 0% | -74.3707 | 2148.795 | -3550 | -400 | -1801.205 | 45.03% | 72.48% | 95% | 0% | 2773 | -65
[5 empty] | 2019-04-10 | 41 | 2395.5 | 2749 | -63 | 1 | 0 | 2812 | 2284.2539 | 2284.2539 | 2284.2539 | 1894.2292 | 780 | 200 | 2874.2292 | 71.86% | 95% | 0% | -72.0824 | 2212.1715 | -3550 | -400 | -1737.8285 | 43.45% | 72.47% | 95% | 0% | 2812 | -63
[5 empty] | 2019-04-10 | 42 | 2396 | 2722 | -63 | 1 | 0 | 2785 | 2241.9621 | 2241.9621 | 2241.9621 | 1894.2292 | 780 | 200 | 2874.2292 | 71.86% | 95% | 0% | -72.0824 | 2169.8797 | -3550 | -400 | -1780.1203 | 44.5% | 72.47% | 95% | 0% | 2785 | -63
[5 empty] | 2019-04-10 | 43 | 2396.5 | 2666 | -64 | 0 | 0 | 2730 | 2155.812 | 2155.812 | 2155.812 | 1894.2292 | 780 | 200 | 2874.2292 | 71.86% | 95% | 0% | -73.2265 | 2082.5855 | -2750 | -200 | -867.4145 | 21.69% | 72.46% | 95% | 0% | 2730 | -64
[5 empty] | 2019-04-10 | 44 | 2397 | 2561 | -64 | 0 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 1894.2292 | 780 | 200 | 2874.2292 | 71.86% | 95% | 0% | -73.2265 | 1918.1172 | -2750 | -200 | -1031.8828 | 25.8% | 72.46% | 95% | 0% | 2625 | -64
[5 empty] | 2019-04-10 | 45 | 2397.5 | 2415 | -65 | 0 | 0 | 2480 | 1764.2209 | 1764.2209 | 1764.2209 | 1894.2292 | 780 | 200 | 2874.2292 | 71.86% | 95% | 0% | -74.3707 | 1689.8502 | -2750 | -200 | -1260.1498 | 31.5% | 72.46% | 95% | 0% | 2480 | -65
[5 empty] | 2019-04-10 | 46 | 2398 | 2291 | -65 | 0 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 1894.2292 | 780 | 200 | 2874.2292 | 71.86% | 95% | 0% | -74.3707 | 1495.621 | -2750 | -200 | -1454.379 | 36.36% | 72.45% | 95% | 0% | 2356 | -65
[5 empty] | 2019-04-10 | 47 | 2398.5 | 2135 | -66 | 0 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 1892.6628 | 780 | 200 | 2872.6628 | 71.82% | 95% | 0% | -75.5149 | 1251.6904 | -2750 | -200 | -1698.3096 | 42.46% | 72.45% | 95% | 0% | 2201 | -66
[5 empty] | 2019-04-10 | 48 | 2399 | 2018 | -67 | 0 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 1892.6628 | 780 | 200 | 2872.6628 | 71.82% | 95% | 0% | -76.659 | 1068.848 | -2750 | -200 | -1881.152 | 47.03% | 72.44% | 95% | 0% | 2085 | -67
[5 empty] | 2019-04-11 | 1 | 2399.5 | 1921 | -66 | 0 | 0 | 1987 | 992.0033 | 992.0033 | 992.0033 | 1892.6628 | 780 | 200 | 2872.6628 | 71.82% | 95% | 0% | -75.5149 | 916.4884 | -2750 | -200 | -2033.5116 | 50.84% | 72.44% | 95% | 0% | 1987 | -66
[5 empty] | 2019-04-11 | 2 | 2400 | 1885 | -65 | 0 | 0 | 1950 | 934.0478 | 934.0478 | 934.0478 | 1892.6628 | 780 | 200 | 2872.6628 | 71.82% | 95% | 0% | -74.3707 | 859.6771 | -2750 | -200 | -2090.3229 | 52.26% | 72.42% | 95% | 0% | 1950 | -65
[5 empty] | 2019-04-11 | 3 | 2400.5 | 1897 | -63 | 0 | 0 | 1960 | 949.7115 | 949.7115 | 949.7115 | 1892.6628 | 780 | 200 | 2872.6628 | 71.82% | 95% | 0% | -72.0824 | 877.6291 | -2750 | -200 | -2072.3709 | 51.81% | 72.42% | 95% | 0% | 1960 | -63
[5 empty] | 2019-04-11 | 4 | 2401 | 1943 | -61 | 0 | 0 | 2004 | 1018.6315 | 1018.6315 | 1018.6315 | 1892.6628 | 780 | 200 | 2872.6628 | 71.82% | 95% | 0% | -69.7941 | 948.8374 | -2750 | -200 | -2001.1626 | 50.03% | 72.41% | 95% | 0% | 2004 | -61
[5 empty] | 2019-04-11 | 5 | 2401.5 | 1937 | -60 | 0 | 0 | 1997 | 1007.6669 | 1007.6669 | 1007.6669 | 1892.6628 | 780 | 200 | 2872.6628 | 71.82% | 95% | 0% | -68.6499 | 939.0171 | -2750 | -200 | -2010.9829 | 50.27% | 72.39% | 95% | 0% | 1997 | -60
[5 empty] | 2019-04-11 | 6 | 2402 | 1932 | -59 | 0 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1892.6628 | 780 | 200 | 2872.6628 | 71.82% | 95% | 0% | -67.5057 | 930.763 | -2750 | -200 | -2019.237 | 50.48% | 72.39% | 95% | 0% | 1991 | -59
[5 empty] | 2019-04-11 | 7 | 2402.5 | 1914 | -57 | 0 | 0 | 1971 | 966.9415 | 966.9415 | 966.9415 | 1891.0965 | 780 | 200 | 2871.0965 | 71.78% | 95% | 0% | -65.2174 | 901.7241 | -2750 | -200 | -2048.2759 | 51.21% | 72.39% | 95% | 0% | 1971 | -57
[5 empty] | 2019-04-11 | 8 | 2403 | 1906 | -55 | 0 | 0 | 1961 | 951.2778 | 951.2778 | 951.2778 | 1891.0965 | 780 | 200 | 2871.0965 | 71.78% | 95% | 0% | -62.9291 | 888.3488 | -2750 | -200 | -2061.6512 | 51.54% | 72.38% | 95% | 0% | 1961 | -55
[5 empty] | 2019-04-11 | 9 | 2403.5 | 1907 | -55 | 0 | 0 | 1962 | 952.8442 | 952.8442 | 952.8442 | 1891.0965 | 780 | 200 | 2871.0965 | 71.78% | 95% | 0% | -62.9291 | 889.9151 | -2750 | -200 | -2060.0849 | 51.5% | 72.38% | 95% | 0% | 1962 | -55
[5 empty] | 2019-04-11 | 10 | 2404 | 1910 | -55 | 0 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 1891.0965 | 780 | 200 | 2871.0965 | 71.78% | 95% | 0% | -62.9291 | 894.6142 | -2750 | -200 | -2055.3858 | 51.38% | 72.37% | 95% | 0% | 1965 | -55
[5 empty] | 2019-04-11 | 11 | 2404.5 | 1971 | -55 | 0 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 1891.0965 | 780 | 200 | 2871.0965 | 71.78% | 95% | 0% | -62.9291 | 990.1624 | -2750 | -200 | -1959.8376 | 49% | 72.37% | 95% | 0% | 2026 | -55
[5 empty] | 2019-04-11 | 12 | 2405 | 2077 | -54 | 0 | 0 | 2131 | 1217.5598 | 1217.5598 | 1217.5598 | 1891.0965 | 780 | 200 | 2871.0965 | 71.78% | 95% | 0% | -61.7849 | 1155.7749 | -2750 | -200 | -1794.2251 | 44.86% | 72.37% | 95% | 0% | 2131 | -54
[5 empty] | 2019-04-11 | 13 | 2405.5 | 2263 | -54 | 0 | 0 | 2317 | 1508.9035 | 1508.9035 | 1508.9035 | 1891.0965 | 780 | 200 | 2871.0965 | 71.78% | 95% | 0% | -61.7849 | 1447.1186 | -2750 | -200 | -1502.8814 | 37.57% | 72.36% | 95% | 0% | 2317 | -54
[5 empty] | 2019-04-11 | 14 | 2406 | 2446 | -59 | 0 | 0 | 2505 | 1803.38 | 1803.38 | 1803.38 | 1891.0965 | 780 | 200 | 2871.0965 | 71.78% | 95% | 0% | -67.5057 | 1735.8743 | -2750 | -200 | -1214.1257 | 30.35% | 72.35% | 95% | 0% | 2505 | -59
[5 empty] | 2019-04-11 | 15 | 2406.5 | 2607 | -103 | 0 | 0 | 2710 | 2124.4847 | 2124.4847 | 2124.4847 | 1891.0965 | 780 | 200 | 2871.0965 | 71.78% | 95% | 0% | -117.849 | 2006.6358 | -2750 | -200 | -943.3642 | 23.58% | 72.35% | 95% | 0% | 2710 | -103
[5 empty] | 2019-04-11 | 16 | 2407 | 2649 | -154 | 1 | 0 | 2803 | 2270.1566 | 2270.1566 | 2270.1566 | 1889.5301 | 780 | 200 | 2869.5301 | 71.74% | 95% | 0% | -176.2014 | 2093.9553 | -3550 | -400 | -1856.0447 | 46.4% | 72.35% | 95% | 0% | 2803 | -154
[5 empty] | 2019-04-11 | 17 | 2407.5 | 2640 | -216 | 1 | 0 | 2856 | 2353.1739 | 2353.1739 | 2353.1739 | 1889.5301 | 780 | 200 | 2869.5301 | 71.74% | 95% | 0% | -247.1396 | 2106.0344 | -3550 | -400 | -1843.9656 | 46.1% | 72.35% | 95% | 0% | 2856 | -216
[5 empty] | 2019-04-11 | 18 | 2408 | 2501 | -285 | 1 | 0 | 2786 | 2243.5284 | 2243.5284 | 2243.5284 | 1889.5301 | 780 | 200 | 2869.5301 | 71.74% | 95% | 0% | -326.087 | 1917.4415 | -3550 | -400 | -2032.5585 | 50.81% | 72.35% | 95% | 0% | 2786 | -285
[5 empty] | 2019-04-11 | 19 | 2408.5 | 2408 | -347 | 1 | 0 | 2755 | 2194.9711 | 2194.9711 | 2194.9711 | 1889.5301 | 780 | 200 | 2869.5301 | 71.74% | 95% | 0% | -397.0252 | 1797.946 | -3550 | -400 | -2152.054 | 53.8% | 72.35% | 95% | 0% | 2755 | -347
[5 empty] | 2019-04-11 | 20 | 2409 | 2295 | -407 | 1 | 0 | 2702 | 2111.9538 | 2111.9538 | 2111.9538 | 1889.5301 | 780 | 200 | 2869.5301 | 71.74% | 95% | 0% | -465.6751 | 1646.2788 | -3550 | -400 | -2303.7212 | 57.59% | 72.35% | 95% | 0% | 2702 | -407
[5 empty] | 2019-04-11 | 21 | 2409.5 | 2187 | -457 | 1 | 0 | 2644 | 2021.1047 | 2021.1047 | 2021.1047 | 1889.5301 | 780 | 200 | 2869.5301 | 71.74% | 95% | 0% | -522.8833 | 1498.2214 | -3550 | -400 | -2451.7786 | 61.29% | 72.34% | 95% | 0% | 2644 | -457
[5 empty] | 2019-04-11 | 22 | 2410 | 2037 | -555 | 1 | 0 | 2592 | 1939.6538 | 1939.6538 | 1939.6538 | 1889.5301 | 780 | 200 | 2869.5301 | 71.74% | 95% | 0% | -635.0114 | 1304.6423 | -3550 | -400 | -2645.3577 | 66.13% | 72.34% | 95% | 0% | 2592 | -555
[5 empty] | 2019-04-11 | 23 | 2410.5 | 1954 | -592 | 1 | 0 | 2546 | 1867.601 | 1867.601 | 1867.601 | 1889.5301 | 780 | 200 | 2869.5301 | 71.74% | 95% | 0% | -677.3455 | 1190.2555 | -3550 | -400 | -2759.7445 | 68.99% | 72.33% | 95% | 0% | 2546 | -592
[5 empty] | 2019-04-11 | 24 | 2411 | 1841 | -658 | 1 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 1887.9637 | 780 | 200 | 2867.9637 | 71.7% | 95% | 0% | -752.8604 | 1041.1215 | -3550 | -400 | -2908.8785 | 72.72% | 72.33% | 95% | 0% | 2499 | -658
[5 empty] | 2019-04-11 | 25 | 2411.5 | 1748 | -710 | 1 | 0 | 2458 | 1729.7609 | 1729.7609 | 1729.7609 | 1887.9637 | 780 | 200 | 2867.9637 | 71.7% | 95% | 0% | -812.357 | 917.4039 | -3550 | -400 | -3032.5961 | 75.81% | 72.32% | 95% | 0% | 2458 | -710
[5 empty] | 2019-04-11 | 26 | 2412 | 1671 | -731 | 1 | 0 | 2402 | 1642.0445 | 1642.0445 | 1642.0445 | 1887.9637 | 780 | 200 | 2867.9637 | 71.7% | 95% | 0% | -836.3844 | 805.6601 | -3550 | -400 | -3144.3399 | 78.61% | 72.32% | 95% | 0% | 2402 | -731
[5 empty] | 2019-04-11 | 27 | 2412.5 | 1615 | -731 | 1 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 1887.9637 | 780 | 200 | 2867.9637 | 71.7% | 95% | 0% | -836.3844 | 717.9437 | -3550 | -400 | -3232.0563 | 80.8% | 72.32% | 95% | 0% | 2346 | -731
[5 empty] | 2019-04-11 | 28 | 2413 | 1574 | -726 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 1887.9637 | 780 | 200 | 2867.9637 | 71.7% | 95% | 0% | -830.6636 | 651.6117 | -3550 | -400 | -3298.3883 | 82.46% | 72.32% | 95% | 0% | 2300 | -726
[5 empty] | 2019-04-11 | 29 | 2413.5 | 1590 | -700 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 1887.9637 | 780 | 200 | 2867.9637 | 71.7% | 95% | 0% | -800.9153 | 665.6964 | -3550 | -400 | -3284.3036 | 82.11% | 72.32% | 95% | 0% | 2290 | -700
[5 empty] | 2019-04-11 | 30 | 2414 | 1608 | -664 | 1 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 1887.9637 | 780 | 200 | 2867.9637 | 71.7% | 95% | 0% | -759.7254 | 678.6917 | -3550 | -400 | -3271.3083 | 81.78% | 72.31% | 95% | 0% | 2272 | -664
[5 empty] | 2019-04-11 | 31 | 2414.5 | 1654 | -622 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1887.9637 | 780 | 200 | 2867.9637 | 71.7% | 95% | 0% | -711.6705 | 733.0121 | -3550 | -400 | -3216.9879 | 80.42% | 72.31% | 95% | 0% | 2276 | -622
[5 empty] | 2019-04-11 | 32 | 2415 | 1754 | -567 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 1887.9637 | 780 | 200 | 2867.9637 | 71.7% | 95% | 0% | -648.7414 | 866.4276 | -3550 | -400 | -3083.5724 | 77.09% | 72.31% | 95% | 0% | 2321 | -567
[5 empty] | 2019-04-11 | 33 | 2415.5 | 1889 | -496 | 1 | 0 | 2385 | 1615.4163 | 1615.4163 | 1615.4163 | 1886.3974 | 780 | 200 | 2866.3974 | 71.66% | 95% | 0% | -567.5057 | 1047.9106 | -3550 | -400 | -2902.0894 | 72.55% | 72.3% | 95% | 0% | 2385 | -496
[5 empty] | 2019-04-11 | 34 | 2416 | 2058 | -421 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 1886.3974 | 780 | 200 | 2866.3974 | 71.66% | 95% | 0% | -481.6934 | 1280.9612 | -3550 | -400 | -2669.0388 | 66.73% | 72.3% | 95% | 0% | 2479 | -421
[5 empty] | 2019-04-11 | 35 | 2416.5 | 2235 | -343 | 1 | 0 | 2578 | 1917.7246 | 1917.7246 | 1917.7246 | 1886.3974 | 780 | 200 | 2866.3974 | 71.66% | 95% | 0% | -392.4485 | 1525.2761 | -3550 | -400 | -2424.7239 | 60.62% | 72.29% | 95% | 0% | 2578 | -343
[5 empty] | 2019-04-11 | 36 | 2417 | 2392 | -267 | 1 | 0 | 2659 | 2044.6002 | 2044.6002 | 2044.6002 | 1886.3974 | 780 | 200 | 2866.3974 | 71.66% | 95% | 0% | -305.492 | 1739.1082 | -3550 | -400 | -2210.8918 | 55.27% | 72.28% | 95% | 0% | 2659 | -267
[5 empty] | 2019-04-11 | 37 | 2417.5 | 2538 | -195 | 1 | 0 | 2733 | 2160.5111 | 2160.5111 | 2160.5111 | 1886.3974 | 780 | 200 | 2866.3974 | 71.66% | 95% | 0% | -223.1121 | 1937.399 | -3550 | -400 | -2012.601 | 50.32% | 72.27% | 95% | 0% | 2733 | -195
[5 empty] | 2019-04-11 | 38 | 2418 | 2656 | -129 | 1 | 0 | 2785 | 2241.9621 | 2241.9621 | 2241.9621 | 1886.3974 | 780 | 200 | 2866.3974 | 71.66% | 95% | 0% | -147.5973 | 2094.3648 | -3550 | -400 | -1855.6352 | 46.39% | 72.27% | 95% | 0% | 2785 | -129
[5 empty] | 2019-04-11 | 39 | 2418.5 | 2726 | -74 | 1 | 0 | 2800 | 2265.4575 | 2265.4575 | 2265.4575 | 1886.3974 | 780 | 200 | 2866.3974 | 71.66% | 95% | 0% | -84.6682 | 2180.7894 | -3550 | -400 | -1769.2106 | 44.23% | 72.27% | 95% | 0% | 2800 | -74
[5 empty] | 2019-04-11 | 40 | 2419 | 2781 | -45 | 1 | 0 | 2826 | 2306.183 | 2306.183 | 2306.183 | 1886.3974 | 780 | 200 | 2866.3974 | 71.66% | 95% | 0% | -51.4874 | 2254.6956 | -3550 | -400 | -1695.3044 | 42.38% | 72.26% | 95% | 0% | 2826 | -45
[5 empty] | 2019-04-11 | 41 | 2419.5 | 2823 | -43 | 1 | 0 | 2866 | 2368.8376 | 2368.8376 | 2368.8376 | 1886.3974 | 780 | 200 | 2866.3974 | 71.66% | 95% | 0% | -49.1991 | 2319.6385 | -3550 | -400 | -1630.3615 | 40.76% | 72.25% | 95% | 0% | 2866 | -43
[5 empty] | 2019-04-11 | 42 | 2420 | 2823 | -44 | 0 | 0 | 2867 | 2370.404 | 2370.404 | 2370.404 | 1886.3974 | 780 | 200 | 2866.3974 | 71.66% | 95% | 0% | -50.3432 | 2320.0607 | -2750 | -200 | -629.9393 | 15.75% | 72.25% | 95% | 0% | 2867 | -44
[5 empty] | 2019-04-11 | 43 | 2420.5 | 2737 | -44 | 0 | 0 | 2781 | 2235.6966 | 2235.6966 | 2235.6966 | 1886.3974 | 780 | 200 | 2866.3974 | 71.66% | 95% | 0% | -50.3432 | 2185.3534 | -2750 | -200 | -764.6466 | 19.12% | 72.25% | 95% | 0% | 2781 | -44
[5 empty] | 2019-04-11 | 44 | 2421 | 2617 | -44 | 0 | 0 | 2661 | 2047.7329 | 2047.7329 | 2047.7329 | 1884.831 | 780 | 200 | 2864.831 | 71.62% | 95% | 0% | -50.3432 | 1997.3896 | -2750 | -200 | -952.6104 | 23.82% | 72.24% | 95% | 0% | 2661 | -44
[5 empty] | 2019-04-11 | 45 | 2421.5 | 2468 | -44 | 0 | 0 | 2512 | 1814.3446 | 1814.3446 | 1814.3446 | 1884.831 | 780 | 200 | 2864.831 | 71.62% | 95% | 0% | -50.3432 | 1764.0014 | -2750 | -200 | -1185.9986 | 29.65% | 72.24% | 95% | 0% | 2512 | -44
[5 empty] | 2019-04-11 | 46 | 2422 | 2327 | -44 | 0 | 0 | 2371 | 1593.4872 | 1593.4872 | 1593.4872 | 1884.831 | 780 | 200 | 2864.831 | 71.62% | 95% | 0% | -50.3432 | 1543.144 | -2750 | -200 | -1406.856 | 35.17% | 72.23% | 95% | 0% | 2371 | -44
[5 empty] | 2019-04-11 | 47 | 2422.5 | 2165 | -45 | 0 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 1884.831 | 780 | 200 | 2864.831 | 71.62% | 95% | 0% | -51.4874 | 1289.8151 | -2750 | -200 | -1660.1849 | 41.5% | 72.23% | 95% | 0% | 2210 | -45
[5 empty] | 2019-04-11 | 48 | 2423 | 2051 | -45 | 0 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 1884.831 | 780 | 200 | 2864.831 | 71.62% | 95% | 0% | -51.4874 | 1111.2496 | -2750 | -200 | -1838.7504 | 45.97% | 72.23% | 95% | 0% | 2096 | -45
[5 empty] | 2019-04-12 | 1 | 2423.5 | 1946 | -47 | 0 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 1884.831 | 780 | 200 | 2864.831 | 71.62% | 95% | 0% | -53.7757 | 947.6257 | -2750 | -200 | -2002.3743 | 50.06% | 72.23% | 95% | 0% | 1993 | -47
[5 empty] | 2019-04-12 | 2 | 2424 | 1908 | -48 | 0 | 0 | 1956 | 943.446 | 943.446 | 943.446 | 1884.831 | 780 | 200 | 2864.831 | 71.62% | 95% | 0% | -54.9199 | 888.5261 | -2750 | -200 | -2061.4739 | 51.54% | 72.23% | 95% | 0% | 1956 | -48
[5 empty] | 2019-04-12 | 3 | 2424.5 | 1922 | -48 | 0 | 0 | 1970 | 965.3751 | 965.3751 | 965.3751 | 1884.831 | 780 | 200 | 2864.831 | 71.62% | 95% | 0% | -54.9199 | 910.4552 | -2750 | -200 | -2039.5448 | 50.99% | 72.22% | 95% | 0% | 1970 | -48
[5 empty] | 2019-04-12 | 4 | 2425 | 1958 | -49 | 0 | 0 | 2007 | 1023.3306 | 1023.3306 | 1023.3306 | 1883.2646 | 780 | 200 | 2863.2646 | 71.58% | 95% | 0% | -56.0641 | 967.2665 | -2750 | -200 | -1982.7335 | 49.57% | 72.22% | 95% | 0% | 2007 | -49
[5 empty] | 2019-04-12 | 5 | 2425.5 | 1951 | -50 | 0 | 0 | 2001 | 1013.9324 | 1013.9324 | 1013.9324 | 1883.2646 | 780 | 200 | 2863.2646 | 71.58% | 95% | 0% | -57.2082 | 956.7242 | -2750 | -200 | -1993.2758 | 49.83% | 72.21% | 95% | 0% | 2001 | -50
[5 empty] | 2019-04-12 | 6 | 2426 | 1932 | -52 | 0 | 0 | 1984 | 987.3042 | 987.3042 | 987.3042 | 1883.2646 | 780 | 200 | 2863.2646 | 71.58% | 95% | 0% | -59.4966 | 927.8076 | -2750 | -200 | -2022.1924 | 50.55% | 72.2% | 95% | 0% | 1984 | -52
[5 empty] | 2019-04-12 | 7 | 2426.5 | 1902 | -53 | 0 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 1883.2646 | 780 | 200 | 2863.2646 | 71.58% | 95% | 0% | -60.6407 | 881.2389 | -2750 | -200 | -2068.7611 | 51.72% | 72.2% | 95% | 0% | 1955 | -53
[5 empty] | 2019-04-12 | 8 | 2427 | 1887 | -53 | 0 | 0 | 1940 | 918.3842 | 918.3842 | 918.3842 | 1883.2646 | 780 | 200 | 2863.2646 | 71.58% | 95% | 0% | -60.6407 | 857.7434 | -2750 | -200 | -2092.2566 | 52.31% | 72.2% | 95% | 0% | 1940 | -53
[5 empty] | 2019-04-12 | 9 | 2427.5 | 1885 | -55 | 0 | 0 | 1940 | 918.3842 | 918.3842 | 918.3842 | 1883.2646 | 780 | 200 | 2863.2646 | 71.58% | 95% | 0% | -62.9291 | 855.4551 | -2750 | -200 | -2094.5449 | 52.36% | 72.2% | 95% | 0% | 1940 | -55
[5 empty] | 2019-04-12 | 10 | 2428 | 1888 | -57 | 0 | 0 | 1945 | 926.216 | 926.216 | 926.216 | 1883.2646 | 780 | 200 | 2863.2646 | 71.58% | 95% | 0% | -65.2174 | 860.9986 | -2750 | -200 | -2089.0014 | 52.23% | 72.19% | 95% | 0% | 1945 | -57
[5 empty] | 2019-04-12 | 11 | 2428.5 | 1953 | -60 | 0 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 1883.2646 | 780 | 200 | 2863.2646 | 71.58% | 95% | 0% | -68.6499 | 964.0789 | -2750 | -200 | -1985.9211 | 49.65% | 72.19% | 95% | 0% | 2013 | -60
[5 empty] | 2019-04-12 | 12 | 2429 | 2043 | -63 | 0 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 1881.6983 | 780 | 200 | 2861.6983 | 71.54% | 95% | 0% | -72.0824 | 1106.3183 | -2750 | -200 | -1843.6817 | 46.09% | 72.18% | 95% | 0% | 2106 | -63
[5 empty] | 2019-04-12 | 13 | 2429.5 | 2214 | -65 | 0 | 0 | 2279 | 1449.3817 | 1449.3817 | 1449.3817 | 1881.6983 | 780 | 200 | 2861.6983 | 71.54% | 95% | 0% | -74.3707 | 1375.011 | -2750 | -200 | -1574.989 | 39.37% | 72.18% | 95% | 0% | 2279 | -65
[5 empty] | 2019-04-12 | 14 | 2430 | 2361 | -80 | 0 | 0 | 2441 | 1703.1327 | 1703.1327 | 1703.1327 | 1881.6983 | 780 | 200 | 2861.6983 | 71.54% | 95% | 0% | -91.5332 | 1611.5995 | -2750 | -200 | -1338.4005 | 33.46% | 72.17% | 95% | 0% | 2441 | -80
[5 empty] | 2019-04-12 | 15 | 2430.5 | 2517 | -114 | 0 | 0 | 2631 | 2000.742 | 2000.742 | 2000.742 | 1881.6983 | 780 | 200 | 2861.6983 | 71.54% | 95% | 0% | -130.4348 | 1870.3072 | -2750 | -200 | -1079.6928 | 26.99% | 72.17% | 95% | 0% | 2631 | -114
[5 empty] | 2019-04-12 | 16 | 2431 | 2534 | -164 | 1 | 0 | 2698 | 2105.6884 | 2105.6884 | 2105.6884 | 1881.6983 | 780 | 200 | 2861.6983 | 71.54% | 95% | 0% | -187.643 | 1918.0454 | -3550 | -400 | -2031.9546 | 50.8% | 72.17% | 95% | 0% | 2698 | -164
[5 empty] | 2019-04-12 | 17 | 2431.5 | 2526 | -222 | 1 | 0 | 2748 | 2184.0066 | 2184.0066 | 2184.0066 | 1881.6983 | 780 | 200 | 2861.6983 | 71.54% | 95% | 0% | -254.0046 | 1930.002 | -3550 | -400 | -2019.998 | 50.5% | 72.17% | 95% | 0% | 2748 | -222
[5 empty] | 2019-04-12 | 18 | 2432 | 2472 | -281 | 1 | 0 | 2753 | 2191.8384 | 2191.8384 | 2191.8384 | 1881.6983 | 780 | 200 | 2861.6983 | 71.54% | 95% | 0% | -321.5103 | 1870.3281 | -3550 | -400 | -2079.6719 | 51.99% | 72.16% | 95% | 0% | 2753 | -281
[5 empty] | 2019-04-12 | 19 | 2432.5 | 2391 | -347 | 1 | 0 | 2738 | 2168.343 | 2168.343 | 2168.343 | 1881.6983 | 780 | 200 | 2861.6983 | 71.54% | 95% | 0% | -397.0252 | 1771.3178 | -3550 | -400 | -2178.6822 | 54.47% | 72.16% | 95% | 0% | 2738 | -347
[5 empty] | 2019-04-12 | 20 | 2433 | 2243 | -422 | 1 | 0 | 2665 | 2053.9984 | 2053.9984 | 2053.9984 | 1881.6983 | 780 | 200 | 2861.6983 | 71.54% | 95% | 0% | -482.8375 | 1571.1608 | -3550 | -400 | -2378.8392 | 59.47% | 72.15% | 95% | 0% | 2665 | -422
[5 empty] | 2019-04-12 | 21 | 2433.5 | 2131 | -476 | 1 | 0 | 2607 | 1963.1492 | 1963.1492 | 1963.1492 | 1881.6983 | 780 | 200 | 2861.6983 | 71.54% | 95% | 0% | -544.6224 | 1418.5268 | -3550 | -400 | -2531.4732 | 63.29% | 72.15% | 95% | 0% | 2607 | -476
[5 empty] | 2019-04-12 | 22 | 2434 | 2047 | -536 | 1 | 0 | 2583 | 1925.5565 | 1925.5565 | 1925.5565 | 1881.6983 | 780 | 200 | 2861.6983 | 71.54% | 95% | 0% | -613.2723 | 1312.2842 | -3550 | -400 | -2637.7158 | 65.94% | 72.15% | 95% | 0% | 2583 | -536
[5 empty] | 2019-04-12 | 23 | 2434.5 | 2010 | -552 | 1 | 0 | 2562 | 1892.6628 | 1892.6628 | 1892.6628 | 1880.1319 | 780 | 200 | 2860.1319 | 71.5% | 95% | 0% | -631.5789 | 1261.0839 | -3550 | -400 | -2688.9161 | 67.22% | 72.14% | 95% | 0% | 2562 | -552
[5 empty] | 2019-04-12 | 24 | 2435 | 2004 | -562 | 1 | 0 | 2566 | 1898.9283 | 1898.9283 | 1898.9283 | 1880.1319 | 780 | 200 | 2860.1319 | 71.5% | 95% | 0% | -643.0206 | 1255.9077 | -3550 | -400 | -2694.0923 | 67.35% | 72.14% | 95% | 0% | 2566 | -562
[5 empty] | 2019-04-12 | 25 | 2435.5 | 2026 | -546 | 1 | 0 | 2572 | 1908.3265 | 1908.3265 | 1908.3265 | 1880.1319 | 780 | 200 | 2860.1319 | 71.5% | 95% | 0% | -624.714 | 1283.6125 | -3550 | -400 | -2666.3875 | 66.66% | 72.14% | 95% | 0% | 2572 | -546
[5 empty] | 2019-04-12 | 26 | 2436 | 2000 | -540 | 1 | 0 | 2540 | 1858.2028 | 1858.2028 | 1858.2028 | 1880.1319 | 780 | 200 | 2860.1319 | 71.5% | 95% | 0% | -617.849 | 1240.3538 | -3550 | -400 | -2709.6462 | 67.74% | 72.13% | 95% | 0% | 2540 | -540
[5 empty] | 2019-04-12 | 27 | 2436.5 | 2000 | -507 | 1 | 0 | 2507 | 1806.5128 | 1806.5128 | 1806.5128 | 1880.1319 | 780 | 200 | 2860.1319 | 71.5% | 95% | 0% | -580.0915 | 1226.4212 | -3550 | -400 | -2723.5788 | 68.09% | 72.13% | 95% | 0% | 2507 | -507
[5 empty] | 2019-04-12 | 28 | 2437 | 1992 | -481 | 1 | 0 | 2473 | 1753.2564 | 1753.2564 | 1753.2564 | 1880.1319 | 780 | 200 | 2860.1319 | 71.5% | 95% | 0% | -550.3432 | 1202.9131 | -3550 | -400 | -2747.0869 | 68.68% | 72.12% | 95% | 0% | 2473 | -481
[5 empty] | 2019-04-12 | 29 | 2437.5 | 2036 | -441 | 1 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 1880.1319 | 780 | 200 | 2860.1319 | 71.5% | 95% | 0% | -504.5767 | 1254.9452 | -3550 | -400 | -2695.0548 | 67.38% | 72.12% | 95% | 0% | 2477 | -441
[5 empty] | 2019-04-12 | 30 | 2438 | 2060 | -411 | 1 | 0 | 2471 | 1750.1237 | 1750.1237 | 1750.1237 | 1880.1319 | 780 | 200 | 2860.1319 | 71.5% | 95% | 0% | -470.2517 | 1279.8719 | -3550 | -400 | -2670.1281 | 66.75% | 72.11% | 95% | 0% | 2471 | -411
[5 empty] | 2019-04-12 | 31 | 2438.5 | 2091 | -388 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 1880.1319 | 780 | 200 | 2860.1319 | 71.5% | 95% | 0% | -443.9359 | 1318.7186 | -3550 | -400 | -2631.2814 | 65.78% | 72.11% | 95% | 0% | 2479 | -388
[5 empty] | 2019-04-12 | 32 | 2439 | 2136 | -366 | 1 | 0 | 2502 | 1798.681 | 1798.681 | 1798.681 | 1878.5655 | 780 | 200 | 2858.5655 | 71.46% | 95% | 0% | -418.7643 | 1379.9167 | -3550 | -400 | -2570.0833 | 64.25% | 72.1% | 95% | 0% | 2502 | -366
[5 empty] | 2019-04-12 | 33 | 2439.5 | 2228 | -322 | 1 | 0 | 2550 | 1873.8664 | 1873.8664 | 1873.8664 | 1878.5655 | 780 | 200 | 2858.5655 | 71.46% | 95% | 0% | -368.4211 | 1505.4454 | -3550 | -400 | -2444.5546 | 61.11% | 72.1% | 95% | 0% | 2550 | -322
[5 empty] | 2019-04-12 | 34 | 2440 | 2353 | -278 | 1 | 0 | 2631 | 2000.742 | 2000.742 | 2000.742 | 1878.5655 | 780 | 200 | 2858.5655 | 71.46% | 95% | 0% | -318.0778 | 1682.6642 | -3550 | -400 | -2267.3358 | 56.68% | 72.1% | 95% | 0% | 2631 | -278
[5 empty] | 2019-04-12 | 35 | 2440.5 | 2450 | -246 | 1 | 0 | 2696 | 2102.5556 | 2102.5556 | 2102.5556 | 1878.5655 | 780 | 200 | 2858.5655 | 71.46% | 95% | 0% | -281.4645 | 1821.0911 | -3550 | -400 | -2128.9089 | 53.22% | 72.09% | 95% | 0% | 2696 | -246
[5 empty] | 2019-04-12 | 36 | 2441 | 2526 | -213 | 1 | 0 | 2739 | 2169.9093 | 2169.9093 | 2169.9093 | 1878.5655 | 780 | 200 | 2858.5655 | 71.46% | 95% | 0% | -243.7071 | 1926.2022 | -3550 | -400 | -2023.7978 | 50.59% | 72.09% | 95% | 0% | 2739 | -213
[5 empty] | 2019-04-12 | 37 | 2441.5 | 2596 | -172 | 1 | 0 | 2768 | 2215.3339 | 2215.3339 | 2215.3339 | 1878.5655 | 780 | 200 | 2858.5655 | 71.46% | 95% | 0% | -196.7963 | 2018.5375 | -3550 | -400 | -1931.4625 | 48.29% | 72.09% | 95% | 0% | 2768 | -172
[5 empty] | 2019-04-12 | 38 | 2442 | 2627 | -137 | 1 | 0 | 2764 | 2209.0684 | 2209.0684 | 2209.0684 | 1878.5655 | 780 | 200 | 2858.5655 | 71.46% | 95% | 0% | -156.7506 | 2052.3179 | -3550 | -400 | -1897.6821 | 47.44% | 72.09% | 95% | 0% | 2764 | -137
[5 empty] | 2019-04-12 | 39 | 2442.5 | 2656 | -115 | 1 | 0 | 2771 | 2220.033 | 2220.033 | 2220.033 | 1876.9992 | 780 | 200 | 2856.9992 | 71.42% | 95% | 0% | -131.5789 | 2088.454 | -3550 | -400 | -1861.546 | 46.54% | 72.09% | 95% | 0% | 2771 | -115
[5 empty] | 2019-04-12 | 40 | 2443 | 2682 | -103 | 1 | 0 | 2785 | 2241.9621 | 2241.9621 | 2241.9621 | 1876.9992 | 780 | 200 | 2856.9992 | 71.42% | 95% | 0% | -117.849 | 2124.1131 | -3550 | -400 | -1825.8869 | 45.65% | 72.08% | 95% | 0% | 2785 | -103
[5 empty] | 2019-04-12 | 41 | 2443.5 | 2698 | -104 | 1 | 0 | 2802 | 2268.5903 | 2268.5903 | 2268.5903 | 1876.9992 | 780 | 200 | 2856.9992 | 71.42% | 95% | 0% | -118.9931 | 2149.5971 | -3550 | -400 | -1800.4029 | 45.01% | 72.08% | 95% | 0% | 2802 | -104
[5 empty] | 2019-04-12 | 42 | 2444 | 2667 | -106 | 1 | 0 | 2773 | 2223.1657 | 2223.1657 | 2223.1657 | 1876.9992 | 780 | 200 | 2856.9992 | 71.42% | 95% | 0% | -121.2815 | 2101.8842 | -3550 | -400 | -1848.1158 | 46.2% | 72.07% | 95% | 0% | 2773 | -106
[5 empty] | 2019-04-12 | 43 | 2444.5 | 2545 | -108 | 0 | 0 | 2653 | 2035.202 | 2035.202 | 2035.202 | 1876.9992 | 780 | 200 | 2856.9992 | 71.42% | 95% | 0% | -123.5698 | 1911.6322 | -2750 | -200 | -1038.3678 | 25.96% | 72.07% | 95% | 0% | 2653 | -108
[5 empty] | 2019-04-12 | 44 | 2445 | 2428 | -109 | 0 | 0 | 2537 | 1853.5037 | 1853.5037 | 1853.5037 | 1876.9992 | 780 | 200 | 2856.9992 | 71.42% | 95% | 0% | -124.714 | 1728.7898 | -2750 | -200 | -1221.2102 | 30.53% | 72.06% | 95% | 0% | 2537 | -109
[5 empty] | 2019-04-12 | 45 | 2445.5 | 2305 | -110 | 0 | 0 | 2415 | 1662.4073 | 1662.4073 | 1662.4073 | 1876.9992 | 780 | 200 | 2856.9992 | 71.42% | 95% | 0% | -125.8581 | 1536.5491 | -2750 | -200 | -1413.4509 | 35.34% | 72.06% | 95% | 0% | 2415 | -110
[5 empty] | 2019-04-12 | 46 | 2446 | 2169 | -110 | 0 | 0 | 2279 | 1449.3817 | 1449.3817 | 1449.3817 | 1875.4328 | 780 | 200 | 2855.4328 | 71.39% | 95% | 0% | -125.8581 | 1323.5236 | -2750 | -200 | -1626.4764 | 40.66% | 72.06% | 95% | 0% | 2279 | -110
[5 empty] | 2019-04-12 | 47 | 2446.5 | 2023 | -109 | 0 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 1875.4328 | 780 | 200 | 2855.4328 | 71.39% | 95% | 0% | -124.714 | 1094.4122 | -2750 | -200 | -1855.5878 | 46.39% | 72.06% | 95% | 0% | 2132 | -109
[5 empty] | 2019-04-12 | 48 | 2447 | 1904 | -109 | 0 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 1875.4328 | 780 | 200 | 2855.4328 | 71.39% | 95% | 0% | -124.714 | 908.0148 | -2750 | -200 | -2041.9852 | 51.05% | 72.06% | 95% | 0% | 2013 | -109
[5 empty] | 2019-04-13 | 1 | 2447.5 | 1819 | -107 | 0 | 0 | 1926 | 896.4551 | 896.4551 | 896.4551 | 1875.4328 | 780 | 200 | 2855.4328 | 71.39% | 95% | 0% | -122.4256 | 774.0294 | -2750 | -200 | -2175.9706 | 54.4% | 72.05% | 95% | 0% | 1926 | -107
[5 empty] | 2019-04-13 | 2 | 2448 | 1774 | -104 | 0 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 1875.4328 | 780 | 200 | 2855.4328 | 71.39% | 95% | 0% | -118.9931 | 702.2764 | -2750 | -200 | -2247.7236 | 56.19% | 72.05% | 95% | 0% | 1878 | -104
[5 empty] | 2019-04-13 | 3 | 2448.5 | 1787 | -103 | 1 | 0 | 1890 | 840.066 | 840.066 | 840.066 | 1875.4328 | 780 | 200 | 2855.4328 | 71.39% | 95% | 0% | -117.849 | 722.217 | -3550 | -400 | -3227.783 | 80.69% | 72.05% | 95% | 0% | 1890 | -103
[5 empty] | 2019-04-13 | 4 | 2449 | 1831 | -102 | 1 | 0 | 1933 | 907.4196 | 907.4196 | 907.4196 | 1875.4328 | 780 | 200 | 2855.4328 | 71.39% | 95% | 0% | -116.7048 | 790.7148 | -3550 | -400 | -3159.2852 | 78.98% | 72.05% | 95% | 0% | 1933 | -102
[5 empty] | 2019-04-13 | 5 | 2449.5 | 1826 | -100 | 1 | 0 | 1926 | 896.4551 | 896.4551 | 896.4551 | 1875.4328 | 780 | 200 | 2855.4328 | 71.39% | 95% | 0% | -114.4165 | 782.0386 | -3550 | -400 | -3167.9614 | 79.2% | 72.04% | 95% | 0% | 1926 | -100
[5 empty] | 2019-04-13 | 6 | 2450 | 1810 | -98 | 1 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 1875.4328 | 780 | 200 | 2855.4328 | 71.39% | 95% | 0% | -112.1281 | 756.1324 | -3550 | -400 | -3193.8676 | 79.85% | 72.04% | 95% | 0% | 1908 | -98
[5 empty] | 2019-04-13 | 7 | 2450.5 | 1781 | -97 | 1 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 1875.4328 | 780 | 200 | 2855.4328 | 71.39% | 95% | 0% | -110.984 | 710.2856 | -3550 | -400 | -3239.7144 | 80.99% | 72.04% | 95% | 0% | 1878 | -97
[5 empty] | 2019-04-13 | 8 | 2451 | 1772 | -96 | 1 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 1875.4328 | 780 | 200 | 2855.4328 | 71.39% | 95% | 0% | -109.8398 | 695.7661 | -3550 | -400 | -3254.2339 | 81.36% | 72.04% | 95% | 0% | 1868 | -96
[5 empty] | 2019-04-13 | 9 | 2451.5 | 1757 | -95 | 1 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 1875.4328 | 780 | 200 | 2855.4328 | 71.39% | 95% | 0% | -108.6957 | 671.8485 | -3550 | -400 | -3278.1515 | 81.95% | 72.03% | 95% | 0% | 1852 | -95
[5 empty] | 2019-04-13 | 10 | 2452 | 1749 | -94 | 1 | 0 | 1843 | 766.4468 | 766.4468 | 766.4468 | 1873.8664 | 780 | 200 | 2853.8664 | 71.35% | 95% | 0% | -107.5515 | 658.8953 | -3550 | -400 | -3291.1047 | 82.28% | 72.03% | 95% | 0% | 1843 | -94
[5 empty] | 2019-04-13 | 11 | 2452.5 | 1762 | -95 | 1 | 0 | 1857 | 788.3759 | 788.3759 | 788.3759 | 1873.8664 | 780 | 200 | 2853.8664 | 71.35% | 95% | 0% | -108.6957 | 679.6803 | -3550 | -400 | -3270.3197 | 81.76% | 72.03% | 95% | 0% | 1857 | -95
[5 empty] | 2019-04-13 | 12 | 2453 | 1790 | -96 | 1 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 1873.8664 | 780 | 200 | 2853.8664 | 71.35% | 95% | 0% | -109.8398 | 723.9607 | -3550 | -400 | -3226.0393 | 80.65% | 72.03% | 95% | 0% | 1886 | -96
[5 empty] | 2019-04-13 | 13 | 2453.5 | 1855 | -98 | 1 | 0 | 1953 | 938.7469 | 938.7469 | 938.7469 | 1873.8664 | 780 | 200 | 2853.8664 | 71.35% | 95% | 0% | -112.1281 | 826.6188 | -3550 | -400 | -3123.3812 | 78.08% | 72.02% | 95% | 0% | 1953 | -98
[5 empty] | 2019-04-13 | 14 | 2454 | 1918 | -115 | 1 | 0 | 2033 | 1064.0561 | 1064.0561 | 1064.0561 | 1873.8664 | 780 | 200 | 2853.8664 | 71.35% | 95% | 0% | -131.5789 | 932.4771 | -3550 | -400 | -3017.5229 | 75.44% | 72.02% | 95% | 0% | 2033 | -115
[5 empty] | 2019-04-13 | 15 | 2454.5 | 1990 | -160 | 1 | 0 | 2150 | 1247.3207 | 1247.3207 | 1247.3207 | 1873.8664 | 780 | 200 | 2853.8664 | 71.35% | 95% | 0% | -183.0664 | 1064.2543 | -3550 | -400 | -2885.7457 | 72.14% | 72.02% | 95% | 0% | 2150 | -160
[5 empty] | 2019-04-13 | 16 | 2455 | 1967 | -216 | 1 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 1873.8664 | 780 | 200 | 2853.8664 | 71.35% | 95% | 0% | -247.1396 | 1051.8711 | -3550 | -400 | -2898.1289 | 72.45% | 72.01% | 95% | 0% | 2183 | -216
[5 empty] | 2019-04-13 | 17 | 2455.5 | 1953 | -288 | 1 | 0 | 2241 | 1389.8599 | 1389.8599 | 1389.8599 | 1873.8664 | 780 | 200 | 2853.8664 | 71.35% | 95% | 0% | -329.5195 | 1060.3404 | -3550 | -400 | -2889.6596 | 72.24% | 72.01% | 95% | 0% | 2241 | -288
[5 empty] | 2019-04-13 | 18 | 2456 | 1889 | -360 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1873.8664 | 780 | 200 | 2853.8664 | 71.35% | 95% | 0% | -411.8993 | 990.4915 | -3550 | -400 | -2959.5085 | 73.99% | 72% | 95% | 0% | 2249 | -360
[5 empty] | 2019-04-13 | 19 | 2456.5 | 1804 | -435 | 1 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -497.7117 | 889.0155 | -3550 | -400 | -3060.9845 | 76.52% | 72% | 95% | 0% | 2239 | -435
[5 empty] | 2019-04-13 | 20 | 2457 | 1683 | -495 | 1 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -566.3616 | 724.8173 | -3550 | -400 | -3225.1827 | 80.63% | 71.99% | 95% | 0% | 2178 | -495
[5 empty] | 2019-04-13 | 21 | 2457.5 | 1599 | -537 | 1 | 0 | 2136 | 1225.3916 | 1225.3916 | 1225.3916 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -614.4165 | 610.9751 | -3550 | -400 | -3339.0249 | 83.48% | 71.99% | 95% | 0% | 2136 | -537
[5 empty] | 2019-04-13 | 22 | 2458 | 1452 | -645 | 1 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -737.9863 | 426.3171 | -3550 | -400 | -3523.6829 | 88.09% | 71.98% | 95% | 0% | 2097 | -645
[5 empty] | 2019-04-13 | 23 | 2458.5 | 1428 | -646 | 1 | 0 | 2074 | 1128.277 | 1128.277 | 1128.277 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -739.1304 | 389.1466 | -3550 | -400 | -3560.8534 | 89.02% | 71.98% | 95% | 0% | 2074 | -646
[5 empty] | 2019-04-13 | 24 | 2459 | 1403 | -649 | 1 | 0 | 2052 | 1093.817 | 1093.817 | 1093.817 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -742.5629 | 351.2541 | -3550 | -400 | -3598.7459 | 89.97% | 71.97% | 95% | 0% | 2052 | -649
[5 empty] | 2019-04-13 | 25 | 2459.5 | 1335 | -695 | 1 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -795.1945 | 264.1625 | -3550 | -400 | -3685.8375 | 92.15% | 71.97% | 95% | 0% | 2030 | -695
[5 empty] | 2019-04-13 | 26 | 2460 | 1278 | -718 | 1 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -821.5103 | 184.5903 | -3550 | -400 | -3765.4097 | 94.14% | 71.96% | 95% | 0% | 1996 | -718
[5 empty] | 2019-04-13 | 27 | 2460.5 | 1272 | -703 | 1 | 0 | 1975 | 973.2069 | 973.2069 | 973.2069 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -804.3478 | 168.8591 | -3550 | -400 | -3781.1409 | 94.53% | 71.96% | 95% | 0% | 1975 | -703
[5 empty] | 2019-04-13 | 28 | 2461 | 1213 | -716 | 1 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -819.222 | 81.9322 | -3550 | -400 | -3868.0678 | 96.7% | 71.96% | 95% | 0% | 1929 | -716
[5 empty] | 2019-04-13 | 29 | 2461.5 | 1215 | -693 | 1 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -792.9062 | 75.3543 | -3550 | -400 | -3874.6457 | 96.87% | 71.96% | 95% | 0% | 1908 | -693
[5 empty] | 2019-04-13 | 30 | 2462 | 1230 | -666 | 1 | 0 | 1896 | 849.4641 | 849.4641 | 849.4641 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -762.0137 | 87.4504 | -3550 | -400 | -3862.5496 | 96.56% | 71.96% | 95% | 0% | 1896 | -666
[5 empty] | 2019-04-13 | 31 | 2462.5 | 1251 | -630 | 1 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -720.8238 | 105.1449 | -3550 | -400 | -3844.8551 | 96.12% | 71.96% | 95% | 0% | 1881 | -630
[5 empty] | 2019-04-13 | 32 | 2463 | 1321 | -594 | 1 | 0 | 1915 | 879.2251 | 879.2251 | 879.2251 | 1872.3001 | 780 | 200 | 2852.3001 | 71.31% | 95% | 0% | -679.6339 | 199.5912 | -3550 | -400 | -3750.4088 | 93.76% | 71.95% | 95% | 0% | 1915 | -594
[5 empty] | 2019-04-13 | 33 | 2463.5 | 1454 | -521 | 1 | 0 | 1975 | 973.2069 | 973.2069 | 973.2069 | 1870.7337 | 780 | 200 | 2850.7337 | 71.27% | 95% | 0% | -596.1098 | 377.0971 | -3550 | -400 | -3572.9029 | 89.32% | 71.94% | 95% | 0% | 1975 | -521
[5 empty] | 2019-04-13 | 34 | 2464 | 1605 | -465 | 1 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 1870.7337 | 780 | 200 | 2850.7337 | 71.27% | 95% | 0% | -532.0366 | 589.9749 | -3550 | -400 | -3360.0251 | 84% | 71.94% | 95% | 0% | 2070 | -465
[5 empty] | 2019-04-13 | 35 | 2464.5 | 1804 | -393 | 1 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 1870.7337 | 780 | 200 | 2850.7337 | 71.27% | 95% | 0% | -449.6568 | 871.2831 | -3550 | -400 | -3078.7169 | 76.97% | 71.93% | 95% | 0% | 2197 | -393
[5 empty] | 2019-04-13 | 36 | 2465 | 1961 | -342 | 1 | 0 | 2303 | 1486.9744 | 1486.9744 | 1486.9744 | 1870.7337 | 780 | 200 | 2850.7337 | 71.27% | 95% | 0% | -391.3043 | 1095.6701 | -3550 | -400 | -2854.3299 | 71.36% | 71.93% | 95% | 0% | 2303 | -342
[5 empty] | 2019-04-13 | 37 | 2465.5 | 2083 | -285 | 1 | 0 | 2368 | 1588.7881 | 1588.7881 | 1588.7881 | 1870.7337 | 780 | 200 | 2850.7337 | 71.27% | 95% | 0% | -326.087 | 1262.7012 | -3550 | -400 | -2687.2988 | 67.18% | 71.92% | 95% | 0% | 2368 | -285
[5 empty] | 2019-04-13 | 38 | 2466 | 2190 | -229 | 1 | 0 | 2419 | 1668.6727 | 1668.6727 | 1668.6727 | 1870.7337 | 780 | 200 | 2850.7337 | 71.27% | 95% | 0% | -262.0137 | 1406.659 | -3550 | -400 | -2543.341 | 63.58% | 71.92% | 95% | 0% | 2419 | -229
[5 empty] | 2019-04-13 | 39 | 2466.5 | 2272 | -182 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 1870.7337 | 780 | 200 | 2850.7337 | 71.27% | 95% | 0% | -208.238 | 1515.2575 | -3550 | -400 | -2434.7425 | 60.87% | 71.92% | 95% | 0% | 2454 | -182
[5 empty] | 2019-04-13 | 40 | 2467 | 2328 | -151 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 1870.7337 | 780 | 200 | 2850.7337 | 71.27% | 95% | 0% | -172.7689 | 1589.8857 | -3550 | -400 | -2360.1143 | 59% | 71.91% | 95% | 0% | 2479 | -151
[5 empty] | 2019-04-13 | 41 | 2467.5 | 2379 | -148 | 1 | 0 | 2527 | 1837.8401 | 1837.8401 | 1837.8401 | 1870.7337 | 780 | 200 | 2850.7337 | 71.27% | 95% | 0% | -169.3364 | 1668.5037 | -3550 | -400 | -2281.4963 | 57.04% | 71.91% | 95% | 0% | 2527 | -148
[5 empty] | 2019-04-13 | 42 | 2468 | 2351 | -148 | 1 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 1870.7337 | 780 | 200 | 2850.7337 | 71.27% | 95% | 0% | -169.3364 | 1624.6455 | -3550 | -400 | -2325.3545 | 58.13% | 71.9% | 95% | 0% | 2499 | -148
[5 empty] | 2019-04-13 | 43 | 2468.5 | 2298 | -147 | 0 | 0 | 2445 | 1709.3982 | 1709.3982 | 1709.3982 | 1869.1674 | 780 | 200 | 2849.1674 | 71.23% | 95% | 0% | -168.1922 | 1541.206 | -2750 | -200 | -1408.794 | 35.22% | 71.89% | 95% | 0% | 2445 | -147
[5 empty] | 2019-04-13 | 44 | 2469 | 2220 | -146 | 0 | 0 | 2366 | 1585.6554 | 1585.6554 | 1585.6554 | 1869.1674 | 780 | 200 | 2849.1674 | 71.23% | 95% | 0% | -167.0481 | 1418.6073 | -2750 | -200 | -1531.3927 | 38.28% | 71.87% | 95% | 0% | 2366 | -146
[5 empty] | 2019-04-13 | 45 | 2469.5 | 2107 | -146 | 0 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 1869.1674 | 780 | 200 | 2849.1674 | 71.23% | 95% | 0% | -167.0481 | 1241.6082 | -2750 | -200 | -1708.3918 | 42.71% | 71.86% | 95% | 0% | 2253 | -146
[5 empty] | 2019-04-13 | 46 | 2470 | 1993 | -146 | 0 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 1869.1674 | 780 | 200 | 2849.1674 | 71.23% | 95% | 0% | -167.0481 | 1063.0426 | -2750 | -200 | -1886.9574 | 47.17% | 71.85% | 95% | 0% | 2139 | -146
[5 empty] | 2019-04-13 | 47 | 2470.5 | 1871 | -146 | 0 | 0 | 2017 | 1038.9942 | 1038.9942 | 1038.9942 | 1869.1674 | 780 | 200 | 2849.1674 | 71.23% | 95% | 0% | -167.0481 | 871.9462 | -2750 | -200 | -2078.0538 | 51.95% | 71.85% | 95% | 0% | 2017 | -146
[5 empty] | 2019-04-13 | 48 | 2471 | 1772 | -146 | 0 | 0 | 1918 | 883.9242 | 883.9242 | 883.9242 | 1869.1674 | 780 | 200 | 2849.1674 | 71.23% | 95% | 0% | -167.0481 | 716.8761 | -2750 | -200 | -2233.1239 | 55.83% | 71.85% | 95% | 0% | 1918 | -146
[5 empty] | 2019-04-14 | 1 | 2471.5 | 1677 | -144 | 0 | 0 | 1821 | 731.9868 | 731.9868 | 731.9868 | 1869.1674 | 780 | 200 | 2849.1674 | 71.23% | 95% | 0% | -164.7597 | 567.2271 | -2750 | -200 | -2382.7729 | 59.57% | 71.85% | 95% | 0% | 1821 | -144
[5 empty] | 2019-04-14 | 2 | 2472 | 1638 | -142 | 0 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 1869.1674 | 780 | 200 | 2849.1674 | 71.23% | 95% | 0% | -162.4714 | 505.2945 | -2750 | -200 | -2444.7055 | 61.12% | 71.84% | 95% | 0% | 1780 | -142
[5 empty] | 2019-04-14 | 3 | 2472.5 | 1667 | -141 | 0 | 0 | 1808 | 711.6241 | 711.6241 | 711.6241 | 1869.1674 | 780 | 200 | 2849.1674 | 71.23% | 95% | 0% | -161.3272 | 550.2968 | -2750 | -200 | -2399.7032 | 59.99% | 71.84% | 95% | 0% | 1808 | -141
[5 empty] | 2019-04-14 | 4 | 2473 | 1693 | -141 | 0 | 0 | 1834 | 752.3495 | 752.3495 | 752.3495 | 1869.1674 | 780 | 200 | 2849.1674 | 71.23% | 95% | 0% | -161.3272 | 591.0223 | -2750 | -200 | -2358.9777 | 58.97% | 71.84% | 95% | 0% | 1834 | -141
[5 empty] | 2019-04-14 | 5 | 2473.5 | 1687 | -139 | 0 | 0 | 1826 | 739.8186 | 739.8186 | 739.8186 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -159.0389 | 580.7797 | -2750 | -200 | -2369.2203 | 59.23% | 71.84% | 95% | 0% | 1826 | -139
[5 empty] | 2019-04-14 | 6 | 2474 | 1668 | -138 | 0 | 0 | 1806 | 708.4913 | 708.4913 | 708.4913 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -157.8947 | 550.5966 | -2750 | -200 | -2399.4034 | 59.99% | 71.84% | 95% | 0% | 1806 | -138
[5 empty] | 2019-04-14 | 7 | 2474.5 | 1632 | -135 | 0 | 0 | 1767 | 647.4031 | 647.4031 | 647.4031 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -154.4622 | 492.9409 | -2750 | -200 | -2457.0591 | 61.43% | 71.83% | 95% | 0% | 1767 | -135
[5 empty] | 2019-04-14 | 8 | 2475 | 1631 | -133 | 0 | 0 | 1764 | 642.704 | 642.704 | 642.704 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -152.1739 | 490.5301 | -2750 | -200 | -2459.4699 | 61.49% | 71.83% | 95% | 0% | 1764 | -133
[5 empty] | 2019-04-14 | 9 | 2475.5 | 1621 | -130 | 0 | 0 | 1751 | 622.3413 | 622.3413 | 622.3413 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -148.7414 | 473.5999 | -2750 | -200 | -2476.4001 | 61.91% | 71.83% | 95% | 0% | 1751 | -130
[5 empty] | 2019-04-14 | 10 | 2476 | 1617 | -126 | 1 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -144.1648 | 465.6456 | -3550 | -400 | -3484.3544 | 87.11% | 71.81% | 95% | 0% | 1743 | -126
[5 empty] | 2019-04-14 | 11 | 2476.5 | 1623 | -126 | 1 | 0 | 1749 | 619.2086 | 619.2086 | 619.2086 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -144.1648 | 475.0438 | -3550 | -400 | -3474.9562 | 86.87% | 71.81% | 95% | 0% | 1749 | -126
[5 empty] | 2019-04-14 | 12 | 2477 | 1626 | -126 | 1 | 0 | 1752 | 623.9077 | 623.9077 | 623.9077 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -144.1648 | 479.7429 | -3550 | -400 | -3470.2571 | 86.76% | 71.81% | 95% | 0% | 1752 | -126
[5 empty] | 2019-04-14 | 13 | 2477.5 | 1642 | -128 | 1 | 0 | 1770 | 652.1022 | 652.1022 | 652.1022 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -146.4531 | 505.6491 | -3550 | -400 | -3444.3509 | 86.11% | 71.8% | 95% | 0% | 1770 | -128
[5 empty] | 2019-04-14 | 14 | 2478 | 1670 | -147 | 1 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -168.1922 | 557.5291 | -3550 | -400 | -3392.4709 | 84.81% | 71.8% | 95% | 0% | 1817 | -147
[5 empty] | 2019-04-14 | 15 | 2478.5 | 1702 | -189 | 1 | 0 | 1891 | 841.6323 | 841.6323 | 841.6323 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -216.2471 | 625.3852 | -3550 | -400 | -3324.6148 | 83.12% | 71.8% | 95% | 0% | 1891 | -189
[5 empty] | 2019-04-14 | 16 | 2479 | 1714 | -235 | 1 | 0 | 1949 | 932.4815 | 932.4815 | 932.4815 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -268.8787 | 663.6027 | -3550 | -400 | -3286.3973 | 82.16% | 71.79% | 95% | 0% | 1949 | -235
[5 empty] | 2019-04-14 | 17 | 2479.5 | 1731 | -289 | 1 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 1867.601 | 780 | 200 | 2847.601 | 71.19% | 95% | 0% | -330.6636 | 713.0297 | -3550 | -400 | -3236.9703 | 80.92% | 71.79% | 95% | 0% | 2020 | -289
[5 empty] | 2019-04-14 | 18 | 2480 | 1686 | -345 | 1 | 0 | 2031 | 1060.9233 | 1060.9233 | 1060.9233 | 1866.0346 | 780 | 200 | 2846.0346 | 71.15% | 95% | 0% | -394.7368 | 666.1865 | -3550 | -400 | -3283.8135 | 82.1% | 71.79% | 95% | 0% | 2031 | -345
[5 empty] | 2019-04-14 | 19 | 2480.5 | 1642 | -424 | 1 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 1866.0346 | 780 | 200 | 2846.0346 | 71.15% | 95% | 0% | -485.1259 | 630.6202 | -3550 | -400 | -3319.3798 | 82.98% | 71.79% | 95% | 0% | 2066 | -424
[5 empty] | 2019-04-14 | 20 | 2481 | 1609 | -465 | 1 | 0 | 2074 | 1128.277 | 1128.277 | 1128.277 | 1866.0346 | 780 | 200 | 2846.0346 | 71.15% | 95% | 0% | -532.0366 | 596.2404 | -3550 | -400 | -3353.7596 | 83.84% | 71.79% | 95% | 0% | 2074 | -465
[5 empty] | 2019-04-14 | 21 | 2481.5 | 1598 | -501 | 1 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 1866.0346 | 780 | 200 | 2846.0346 | 71.15% | 95% | 0% | -573.2265 | 594.2096 | -3550 | -400 | -3355.7904 | 83.89% | 71.77% | 95% | 0% | 2099 | -501
[5 empty] | 2019-04-14 | 22 | 2482 | 1551 | -554 | 1 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 1866.0346 | 780 | 200 | 2846.0346 | 71.15% | 95% | 0% | -633.8673 | 542.967 | -3550 | -400 | -3407.033 | 85.18% | 71.77% | 95% | 0% | 2105 | -554
[5 empty] | 2019-04-14 | 23 | 2482.5 | 1585 | -525 | 1 | 0 | 2110 | 1184.6661 | 1184.6661 | 1184.6661 | 1866.0346 | 780 | 200 | 2846.0346 | 71.15% | 95% | 0% | -600.6865 | 583.9796 | -3550 | -400 | -3366.0204 | 84.15% | 71.77% | 95% | 0% | 2110 | -525
[5 empty] | 2019-04-14 | 24 | 2483 | 1612 | -516 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1866.0346 | 780 | 200 | 2846.0346 | 71.15% | 95% | 0% | -590.389 | 622.4717 | -3550 | -400 | -3327.5283 | 83.19% | 71.77% | 95% | 0% | 2128 | -516
[5 empty] | 2019-04-14 | 25 | 2483.5 | 1649 | -505 | 1 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 1866.0346 | 780 | 200 | 2846.0346 | 71.15% | 95% | 0% | -577.8032 | 675.7829 | -3550 | -400 | -3274.2171 | 81.86% | 71.76% | 95% | 0% | 2154 | -505
[5 empty] | 2019-04-14 | 26 | 2484 | 1636 | -524 | 1 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1866.0346 | 780 | 200 | 2846.0346 | 71.15% | 95% | 0% | -599.5423 | 663.442 | -3550 | -400 | -3286.558 | 82.16% | 71.76% | 95% | 0% | 2160 | -524
[5 empty] | 2019-04-14 | 27 | 2484.5 | 1627 | -516 | 1 | 0 | 2143 | 1236.3561 | 1236.3561 | 1236.3561 | 1864.4683 | 780 | 200 | 2844.4683 | 71.11% | 95% | 0% | -590.389 | 645.9671 | -3550 | -400 | -3304.0329 | 82.6% | 71.76% | 95% | 0% | 2143 | -516
[5 empty] | 2019-04-14 | 28 | 2485 | 1588 | -540 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1864.4683 | 780 | 200 | 2844.4683 | 71.11% | 95% | 0% | -617.849 | 595.0117 | -3550 | -400 | -3354.9883 | 83.87% | 71.76% | 95% | 0% | 2128 | -540
[5 empty] | 2019-04-14 | 29 | 2485.5 | 1707 | -453 | 1 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1864.4683 | 780 | 200 | 2844.4683 | 71.11% | 95% | 0% | -518.3066 | 744.6777 | -3550 | -400 | -3205.3223 | 80.13% | 71.76% | 95% | 0% | 2160 | -453
[5 empty] | 2019-04-14 | 30 | 2486 | 1735 | -434 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 1864.4683 | 780 | 200 | 2844.4683 | 71.11% | 95% | 0% | -496.5675 | 780.5141 | -3550 | -400 | -3169.4859 | 79.24% | 71.75% | 95% | 0% | 2169 | -434
[5 empty] | 2019-04-14 | 31 | 2486.5 | 1783 | -405 | 1 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 1864.4683 | 780 | 200 | 2844.4683 | 71.11% | 95% | 0% | -463.3867 | 843.4558 | -3550 | -400 | -3106.5442 | 77.66% | 71.75% | 95% | 0% | 2188 | -405
[5 empty] | 2019-04-14 | 32 | 2487 | 1812 | -404 | 1 | 0 | 2216 | 1350.7007 | 1350.7007 | 1350.7007 | 1864.4683 | 780 | 200 | 2844.4683 | 71.11% | 95% | 0% | -462.2426 | 888.4582 | -3550 | -400 | -3061.5418 | 76.54% | 71.75% | 95% | 0% | 2216 | -404
[5 empty] | 2019-04-14 | 33 | 2487.5 | 1862 | -394 | 1 | 0 | 2256 | 1413.3553 | 1413.3553 | 1413.3553 | 1864.4683 | 780 | 200 | 2844.4683 | 71.11% | 95% | 0% | -450.8009 | 962.5544 | -3550 | -400 | -2987.4456 | 74.69% | 71.73% | 95% | 0% | 2256 | -394
[5 empty] | 2019-04-14 | 34 | 2488 | 1958 | -362 | 1 | 0 | 2320 | 1513.6026 | 1513.6026 | 1513.6026 | 1862.9019 | 780 | 200 | 2842.9019 | 71.07% | 95% | 0% | -414.1876 | 1099.415 | -3550 | -400 | -2850.585 | 71.26% | 71.73% | 95% | 0% | 2320 | -362
[5 empty] | 2019-04-14 | 35 | 2488.5 | 2088 | -328 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 1862.9019 | 780 | 200 | 2842.9019 | 71.07% | 95% | 0% | -375.286 | 1288.6876 | -3550 | -400 | -2661.3124 | 66.53% | 71.73% | 95% | 0% | 2416 | -328
[5 empty] | 2019-04-14 | 36 | 2489 | 2170 | -293 | 1 | 0 | 2463 | 1737.5927 | 1737.5927 | 1737.5927 | 1862.9019 | 780 | 200 | 2842.9019 | 71.07% | 95% | 0% | -335.2403 | 1402.3525 | -3550 | -400 | -2547.6475 | 63.69% | 71.73% | 95% | 0% | 2463 | -293
[5 empty] | 2019-04-14 | 37 | 2489.5 | 2243 | -239 | 1 | 0 | 2482 | 1767.3537 | 1767.3537 | 1767.3537 | 1862.9019 | 780 | 200 | 2842.9019 | 71.07% | 95% | 0% | -273.4554 | 1493.8983 | -3550 | -400 | -2456.1017 | 61.4% | 71.72% | 95% | 0% | 2482 | -239
[5 empty] | 2019-04-14 | 38 | 2490 | 2312 | -200 | 1 | 0 | 2512 | 1814.3446 | 1814.3446 | 1814.3446 | 1862.9019 | 780 | 200 | 2842.9019 | 71.07% | 95% | 0% | -228.833 | 1585.5116 | -3550 | -400 | -2364.4884 | 59.11% | 71.72% | 95% | 0% | 2512 | -200
[5 empty] | 2019-04-14 | 39 | 2490.5 | 2361 | -169 | 1 | 0 | 2530 | 1842.5392 | 1842.5392 | 1842.5392 | 1862.9019 | 780 | 200 | 2842.9019 | 71.07% | 95% | 0% | -193.3638 | 1649.1753 | -3550 | -400 | -2300.8247 | 57.52% | 71.71% | 95% | 0% | 2530 | -169
[5 empty] | 2019-04-14 | 40 | 2491 | 2396 | -147 | 1 | 0 | 2543 | 1862.9019 | 1862.9019 | 1862.9019 | 1862.9019 | 780 | 200 | 2842.9019 | 71.07% | 95% | 0% | -168.1922 | 1694.7097 | -3550 | -400 | -2255.2903 | 56.38% | 71.71% | 95% | 0% | 2543 | -147
[5 empty] | 2019-04-14 | 41 | 2491.5 | 2418 | -144 | 0 | 0 | 2562 | 1892.6628 | 1892.6628 | 1892.6628 | 1862.9019 | 780 | 200 | 2842.9019 | 71.07% | 95% | 0% | -164.7597 | 1727.9031 | -2750 | -200 | -1222.0969 | 30.55% | 71.71% | 95% | 0% | 2562 | -144
[5 empty] | 2019-04-14 | 42 | 2492 | 2410 | -144 | 0 | 0 | 2554 | 1880.1319 | 1880.1319 | 1880.1319 | 1862.9019 | 780 | 200 | 2842.9019 | 71.07% | 95% | 0% | -164.7597 | 1715.3722 | -2750 | -200 | -1234.6278 | 30.87% | 71.7% | 95% | 0% | 2554 | -144
[5 empty] | 2019-04-14 | 43 | 2492.5 | 2371 | -144 | 0 | 0 | 2515 | 1819.0437 | 1819.0437 | 1819.0437 | 1861.3355 | 780 | 200 | 2841.3355 | 71.03% | 95% | 0% | -164.7597 | 1654.284 | -2750 | -200 | -1295.716 | 32.39% | 71.7% | 95% | 0% | 2515 | -144
[5 empty] | 2019-04-14 | 44 | 2493 | 2237 | -144 | 0 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 1861.3355 | 780 | 200 | 2841.3355 | 71.03% | 95% | 0% | -164.7597 | 1444.3911 | -2750 | -200 | -1505.6089 | 37.64% | 71.7% | 95% | 0% | 2381 | -144
[5 empty] | 2019-04-14 | 45 | 2493.5 | 2115 | -144 | 0 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 1861.3355 | 780 | 200 | 2841.3355 | 71.03% | 95% | 0% | -164.7597 | 1253.2947 | -2750 | -200 | -1696.7053 | 42.42% | 71.7% | 95% | 0% | 2259 | -144
[5 empty] | 2019-04-14 | 46 | 2494 | 1975 | -145 | 0 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1861.3355 | 780 | 200 | 2841.3355 | 71.03% | 95% | 0% | -165.9039 | 1034.4259 | -2750 | -200 | -1915.5741 | 47.89% | 71.69% | 95% | 0% | 2120 | -145
[5 empty] | 2019-04-14 | 47 | 2494.5 | 1829 | -146 | 0 | 0 | 1975 | 973.2069 | 973.2069 | 973.2069 | 1859.7692 | 780 | 200 | 2839.7692 | 70.99% | 95% | 0% | -167.0481 | 806.1589 | -2750 | -200 | -2143.8411 | 53.6% | 71.66% | 95% | 0% | 1975 | -146
[5 empty] | 2019-04-14 | 48 | 2495 | 1718 | -146 | 0 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 1859.7692 | 780 | 200 | 2839.7692 | 70.99% | 95% | 0% | -167.0481 | 632.2924 | -2750 | -200 | -2317.7076 | 57.94% | 71.66% | 95% | 0% | 1864 | -146
[5 empty] | 2019-04-15 | 1 | 2495.5 | 1627 | -147 | 0 | 0 | 1774 | 658.3677 | 658.3677 | 658.3677 | 1859.7692 | 780 | 200 | 2839.7692 | 70.99% | 95% | 0% | -168.1922 | 490.1755 | -2750 | -200 | -2459.8245 | 61.5% | 71.65% | 95% | 0% | 1774 | -147
[5 empty] | 2019-04-15 | 2 | 2496 | 1587 | -147 | 0 | 0 | 1734 | 595.7131 | 595.7131 | 595.7131 | 1859.7692 | 780 | 200 | 2839.7692 | 70.99% | 95% | 0% | -168.1922 | 427.5209 | -2750 | -200 | -2522.4791 | 63.06% | 71.63% | 95% | 0% | 1734 | -147
[5 empty] | 2019-04-15 | 3 | 2496.5 | 1604 | -149 | 0 | 0 | 1753 | 625.474 | 625.474 | 625.474 | 1859.7692 | 780 | 200 | 2839.7692 | 70.99% | 95% | 0% | -170.4805 | 454.9935 | -2750 | -200 | -2495.0065 | 62.38% | 71.63% | 95% | 0% | 1753 | -149
[5 empty] | 2019-04-15 | 4 | 2497 | 1643 | -151 | 0 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 1859.7692 | 780 | 200 | 2839.7692 | 70.99% | 95% | 0% | -172.7689 | 516.9261 | -2750 | -200 | -2433.0739 | 60.83% | 71.63% | 95% | 0% | 1794 | -151
[5 empty] | 2019-04-15 | 5 | 2497.5 | 1648 | -152 | 0 | 0 | 1800 | 699.0932 | 699.0932 | 699.0932 | 1859.7692 | 780 | 200 | 2839.7692 | 70.99% | 95% | 0% | -173.913 | 525.1801 | -2750 | -200 | -2424.8199 | 60.62% | 71.63% | 95% | 0% | 1800 | -152
[5 empty] | 2019-04-15 | 6 | 2498 | 1623 | -153 | 0 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 1859.7692 | 780 | 200 | 2839.7692 | 70.99% | 95% | 0% | -175.0572 | 486.4432 | -2750 | -200 | -2463.5568 | 61.59% | 71.62% | 95% | 0% | 1776 | -153
[5 empty] | 2019-04-15 | 7 | 2498.5 | 1596 | -154 | 0 | 0 | 1750 | 620.7749 | 620.7749 | 620.7749 | 1858.2028 | 780 | 200 | 2838.2028 | 70.96% | 95% | 0% | -176.2014 | 444.5736 | -2750 | -200 | -2505.4264 | 62.64% | 71.62% | 95% | 0% | 1750 | -154
[5 empty] | 2019-04-15 | 8 | 2499 | 1581 | -155 | 0 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 1858.2028 | 780 | 200 | 2838.2028 | 70.96% | 95% | 0% | -177.3455 | 421.5003 | -2750 | -200 | -2528.4997 | 63.21% | 71.62% | 95% | 0% | 1736 | -155
[5 empty] | 2019-04-15 | 9 | 2499.5 | 1578 | -157 | 0 | 0 | 1735 | 597.2795 | 597.2795 | 597.2795 | 1858.2028 | 780 | 200 | 2838.2028 | 70.96% | 95% | 0% | -179.6339 | 417.6456 | -2750 | -200 | -2532.3544 | 63.31% | 71.62% | 95% | 0% | 1735 | -157
[5 empty] | 2019-04-15 | 10 | 2500 | 1558 | -159 | 0 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 1858.2028 | 780 | 200 | 2838.2028 | 70.96% | 95% | 0% | -181.9222 | 387.1627 | -2750 | -200 | -2562.8373 | 64.07% | 71.62% | 95% | 0% | 1717 | -159
[5 empty] | 2019-04-15 | 11 | 2500.5 | 1617 | -161 | 0 | 0 | 1778 | 664.6331 | 664.6331 | 664.6331 | 1858.2028 | 780 | 200 | 2838.2028 | 70.96% | 95% | 0% | -184.2105 | 480.4226 | -2750 | -200 | -2469.5774 | 61.74% | 71.62% | 95% | 0% | 1778 | -161
[5 empty] | 2019-04-15 | 12 | 2501 | 1705 | -163 | 0 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 1858.2028 | 780 | 200 | 2838.2028 | 70.96% | 95% | 0% | -186.4989 | 619.1071 | -2750 | -200 | -2330.8929 | 58.27% | 71.61% | 95% | 0% | 1868 | -163
[5 empty] | 2019-04-15 | 13 | 2501.5 | 1879 | -166 | 0 | 0 | 2045 | 1082.8524 | 1082.8524 | 1082.8524 | 1858.2028 | 780 | 200 | 2838.2028 | 70.96% | 95% | 0% | -189.9314 | 892.9211 | -2750 | -200 | -2057.0789 | 51.43% | 71.6% | 95% | 0% | 2045 | -166
[5 empty] | 2019-04-15 | 14 | 2502 | 2036 | -182 | 0 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 1858.2028 | 780 | 200 | 2838.2028 | 70.96% | 95% | 0% | -208.238 | 1145.5955 | -2750 | -200 | -1804.4045 | 45.11% | 71.6% | 95% | 0% | 2218 | -182
[5 empty] | 2019-04-15 | 15 | 2502.5 | 2217 | -218 | 0 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1858.2028 | 780 | 200 | 2838.2028 | 70.96% | 95% | 0% | -249.4279 | 1444.3066 | -2750 | -200 | -1505.6934 | 37.64% | 71.59% | 95% | 0% | 2435 | -218
[5 empty] | 2019-04-15 | 16 | 2503 | 2277 | -261 | 0 | 0 | 2538 | 1855.0701 | 1855.0701 | 1855.0701 | 1858.2028 | 780 | 200 | 2838.2028 | 70.96% | 95% | 0% | -298.627 | 1556.4431 | -2750 | -200 | -1393.5569 | 34.84% | 71.59% | 95% | 0% | 2538 | -261
[5 empty] | 2019-04-15 | 17 | 2503.5 | 2274 | -330 | 1 | 0 | 2604 | 1958.4501 | 1958.4501 | 1958.4501 | 1856.6364 | 780 | 200 | 2836.6364 | 70.92% | 95% | 0% | -377.5744 | 1580.8758 | -3550 | -400 | -2369.1242 | 59.23% | 71.59% | 95% | 0% | 2604 | -330
[5 empty] | 2019-04-15 | 18 | 2504 | 2208 | -394 | 1 | 0 | 2602 | 1955.3174 | 1955.3174 | 1955.3174 | 1856.6364 | 780 | 200 | 2836.6364 | 70.92% | 95% | 0% | -450.8009 | 1504.5165 | -3550 | -400 | -2445.4835 | 61.14% | 71.59% | 95% | 0% | 2602 | -394
[5 empty] | 2019-04-15 | 19 | 2504.5 | 2061 | -506 | 1 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 1856.6364 | 780 | 200 | 2836.6364 | 70.92% | 95% | 0% | -578.9474 | 1321.5473 | -3550 | -400 | -2628.4527 | 65.71% | 71.58% | 95% | 0% | 2567 | -506
[5 empty] | 2019-04-15 | 20 | 2505 | 1954 | -537 | 1 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 1856.6364 | 780 | 200 | 2836.6364 | 70.92% | 95% | 0% | -614.4165 | 1167.0345 | -3550 | -400 | -2782.9655 | 69.57% | 71.58% | 95% | 0% | 2491 | -537
[5 empty] | 2019-04-15 | 21 | 2505.5 | 1800 | -608 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 1856.6364 | 780 | 200 | 2836.6364 | 70.92% | 95% | 0% | -695.6522 | 955.7905 | -3550 | -400 | -2994.2095 | 74.86% | 71.57% | 95% | 0% | 2408 | -608
[5 empty] | 2019-04-15 | 22 | 2506 | 1594 | -739 | 1 | 0 | 2333 | 1533.9654 | 1533.9654 | 1533.9654 | 1856.6364 | 780 | 200 | 2836.6364 | 70.92% | 95% | 0% | -845.5378 | 688.4276 | -3550 | -400 | -3261.5724 | 81.54% | 71.57% | 95% | 0% | 2333 | -739
[5 empty] | 2019-04-15 | 23 | 2506.5 | 1472 | -798 | 1 | 0 | 2270 | 1435.2844 | 1435.2844 | 1435.2844 | 1856.6364 | 780 | 200 | 2836.6364 | 70.92% | 95% | 0% | -913.0435 | 522.2409 | -3550 | -400 | -3427.7591 | 85.69% | 71.56% | 95% | 0% | 2270 | -798
[5 empty] | 2019-04-15 | 24 | 2507 | 1373 | -854 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1856.6364 | 780 | 200 | 2836.6364 | 70.92% | 95% | 0% | -977.1167 | 390.814 | -3550 | -400 | -3559.186 | 88.98% | 71.56% | 95% | 0% | 2227 | -854
[5 empty] | 2019-04-15 | 25 | 2507.5 | 1338 | -873 | 1 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 1856.6364 | 780 | 200 | 2836.6364 | 70.92% | 95% | 0% | -998.8558 | 344.0131 | -3550 | -400 | -3605.9869 | 90.15% | 71.56% | 95% | 0% | 2211 | -873
[5 empty] | 2019-04-15 | 26 | 2508 | 1314 | -863 | 1 | 0 | 2177 | 1289.6125 | 1289.6125 | 1289.6125 | 1856.6364 | 780 | 200 | 2836.6364 | 70.92% | 95% | 0% | -987.4142 | 302.1983 | -3550 | -400 | -3647.8017 | 91.2% | 71.55% | 95% | 0% | 2177 | -863
[5 empty] | 2019-04-15 | 27 | 2508.5 | 1271 | -874 | 1 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 1856.6364 | 780 | 200 | 2836.6364 | 70.92% | 95% | 0% | -1000 | 239.4889 | -3550 | -400 | -3710.5111 | 92.76% | 71.55% | 95% | 0% | 2145 | -874
[5 empty] | 2019-04-15 | 28 | 2509 | 1249 | -857 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 1855.0701 | 780 | 200 | 2835.0701 | 70.88% | 95% | 0% | -980.5492 | 197.8515 | -3550 | -400 | -3752.1485 | 93.8% | 71.55% | 95% | 0% | 2106 | -857
[5 empty] | 2019-04-15 | 29 | 2509.5 | 1308 | -812 | 1 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1855.0701 | 780 | 200 | 2835.0701 | 70.88% | 95% | 0% | -929.0618 | 271.268 | -3550 | -400 | -3678.732 | 91.97% | 71.54% | 95% | 0% | 2120 | -812
[5 empty] | 2019-04-15 | 30 | 2510 | 1378 | -751 | 1 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 1855.0701 | 780 | 200 | 2835.0701 | 70.88% | 95% | 0% | -859.2677 | 355.1593 | -3550 | -400 | -3594.8407 | 89.87% | 71.54% | 95% | 0% | 2129 | -751
[5 empty] | 2019-04-15 | 31 | 2510.5 | 1469 | -688 | 1 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 1855.0701 | 780 | 200 | 2835.0701 | 70.88% | 95% | 0% | -787.1854 | 471.0999 | -3550 | -400 | -3478.9001 | 86.97% | 71.53% | 95% | 0% | 2157 | -688
[5 empty] | 2019-04-15 | 32 | 2511 | 1595 | -618 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 1855.0701 | 780 | 200 | 2835.0701 | 70.88% | 95% | 0% | -707.0938 | 638.9078 | -3550 | -400 | -3311.0922 | 82.78% | 71.53% | 95% | 0% | 2213 | -618
[5 empty] | 2019-04-15 | 33 | 2511.5 | 1740 | -549 | 1 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 1855.0701 | 780 | 200 | 2835.0701 | 70.88% | 95% | 0% | -628.1465 | 836.8989 | -3550 | -400 | -3113.1011 | 77.83% | 71.52% | 95% | 0% | 2289 | -549
[5 empty] | 2019-04-15 | 34 | 2512 | 1887 | -494 | 1 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 1855.0701 | 780 | 200 | 2835.0701 | 70.88% | 95% | 0% | -565.2174 | 1043.9335 | -3550 | -400 | -2906.0665 | 72.65% | 71.52% | 95% | 0% | 2381 | -494
[5 empty] | 2019-04-15 | 35 | 2512.5 | 2050 | -429 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 1855.0701 | 780 | 200 | 2835.0701 | 70.88% | 95% | 0% | -490.8467 | 1271.8079 | -3550 | -400 | -2678.1921 | 66.95% | 71.52% | 95% | 0% | 2479 | -429
[5 empty] | 2019-04-15 | 36 | 2513 | 2177 | -368 | 1 | 0 | 2545 | 1866.0346 | 1866.0346 | 1866.0346 | 1853.5037 | 780 | 200 | 2833.5037 | 70.84% | 95% | 0% | -421.0526 | 1444.982 | -3550 | -400 | -2505.018 | 62.63% | 71.51% | 95% | 0% | 2545 | -368
[5 empty] | 2019-04-15 | 37 | 2513.5 | 2275 | -306 | 1 | 0 | 2581 | 1922.4237 | 1922.4237 | 1922.4237 | 1853.5037 | 780 | 200 | 2833.5037 | 70.84% | 95% | 0% | -350.1144 | 1572.3093 | -3550 | -400 | -2377.6907 | 59.44% | 71.51% | 95% | 0% | 2581 | -306
[5 empty] | 2019-04-15 | 38 | 2514 | 2359 | -251 | 1 | 0 | 2610 | 1967.8483 | 1967.8483 | 1967.8483 | 1853.5037 | 780 | 200 | 2833.5037 | 70.84% | 95% | 0% | -287.1854 | 1680.663 | -3550 | -400 | -2269.337 | 56.73% | 71.51% | 95% | 0% | 2610 | -251
[5 empty] | 2019-04-15 | 39 | 2514.5 | 2437 | -207 | 1 | 0 | 2644 | 2021.1047 | 2021.1047 | 2021.1047 | 1853.5037 | 780 | 200 | 2833.5037 | 70.84% | 95% | 0% | -236.8421 | 1784.2626 | -3550 | -400 | -2165.7374 | 54.14% | 71.5% | 95% | 0% | 2644 | -207
[5 empty] | 2019-04-15 | 40 | 2515 | 2469 | -183 | 1 | 0 | 2652 | 2033.6356 | 2033.6356 | 2033.6356 | 1853.5037 | 780 | 200 | 2833.5037 | 70.84% | 95% | 0% | -209.3822 | 1824.2535 | -3550 | -400 | -2125.7465 | 53.14% | 71.49% | 95% | 0% | 2652 | -183
[5 empty] | 2019-04-15 | 41 | 2515.5 | 2495 | -177 | 1 | 0 | 2672 | 2064.9629 | 2064.9629 | 2064.9629 | 1853.5037 | 780 | 200 | 2833.5037 | 70.84% | 95% | 0% | -202.5172 | 1862.4457 | -3550 | -400 | -2087.5543 | 52.19% | 71.48% | 95% | 0% | 2672 | -177
[5 empty] | 2019-04-15 | 42 | 2516 | 2507 | -172 | 1 | 0 | 2679 | 2075.9275 | 2075.9275 | 2075.9275 | 1853.5037 | 780 | 200 | 2833.5037 | 70.84% | 95% | 0% | -196.7963 | 1879.1311 | -3550 | -400 | -2070.8689 | 51.77% | 71.48% | 95% | 0% | 2679 | -172
[5 empty] | 2019-04-15 | 43 | 2516.5 | 2442 | -169 | 0 | 0 | 2611 | 1969.4147 | 1969.4147 | 1969.4147 | 1853.5037 | 780 | 200 | 2833.5037 | 70.84% | 95% | 0% | -193.3638 | 1776.0508 | -2750 | -200 | -1173.9492 | 29.35% | 71.48% | 95% | 0% | 2611 | -169
[5 empty] | 2019-04-15 | 44 | 2517 | 2316 | -166 | 0 | 0 | 2482 | 1767.3537 | 1767.3537 | 1767.3537 | 1853.5037 | 780 | 200 | 2833.5037 | 70.84% | 95% | 0% | -189.9314 | 1577.4223 | -2750 | -200 | -1372.5777 | 34.31% | 71.48% | 95% | 0% | 2482 | -166
[5 empty] | 2019-04-15 | 45 | 2517.5 | 2180 | -163 | 0 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 1851.9373 | 780 | 200 | 2831.9373 | 70.8% | 95% | 0% | -186.4989 | 1363.1302 | -2750 | -200 | -1586.8698 | 39.67% | 71.47% | 95% | 0% | 2343 | -163
[5 empty] | 2019-04-15 | 46 | 2518 | 2044 | -160 | 0 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 1851.9373 | 780 | 200 | 2831.9373 | 70.8% | 95% | 0% | -183.0664 | 1148.838 | -2750 | -200 | -1801.162 | 45.03% | 71.47% | 95% | 0% | 2204 | -160
[5 empty] | 2019-04-15 | 47 | 2518.5 | 1890 | -156 | 0 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1851.9373 | 780 | 200 | 2831.9373 | 70.8% | 95% | 0% | -178.4897 | 905.9291 | -2750 | -200 | -2044.0709 | 51.1% | 71.47% | 95% | 0% | 2046 | -156
[5 empty] | 2019-04-15 | 48 | 2519 | 1792 | -152 | 0 | 0 | 1944 | 924.6496 | 924.6496 | 924.6496 | 1851.9373 | 780 | 200 | 2831.9373 | 70.8% | 95% | 0% | -173.913 | 750.7366 | -2750 | -200 | -2199.2634 | 54.98% | 71.47% | 95% | 0% | 1944 | -152
[5 empty] | 2019-04-16 | 1 | 2519.5 | 1717 | -145 | 0 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 1851.9373 | 780 | 200 | 2831.9373 | 70.8% | 95% | 0% | -165.9039 | 630.3039 | -2750 | -200 | -2319.6961 | 57.99% | 71.47% | 95% | 0% | 1862 | -145
[5 empty] | 2019-04-16 | 2 | 2520 | 1679 | -138 | 0 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 1851.9373 | 780 | 200 | 2831.9373 | 70.8% | 95% | 0% | -157.8947 | 567.8266 | -2750 | -200 | -2382.1734 | 59.55% | 71.47% | 95% | 0% | 1817 | -138
[5 empty] | 2019-04-16 | 3 | 2520.5 | 1697 | -134 | 0 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 1851.9373 | 780 | 200 | 2831.9373 | 70.8% | 95% | 0% | -153.3181 | 594.3324 | -2750 | -200 | -2355.6676 | 58.89% | 71.46% | 95% | 0% | 1831 | -134
[5 empty] | 2019-04-16 | 4 | 2521 | 1754 | -131 | 0 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 1851.9373 | 780 | 200 | 2831.9373 | 70.8% | 95% | 0% | -149.8856 | 682.3485 | -2750 | -200 | -2267.6515 | 56.69% | 71.46% | 95% | 0% | 1885 | -131
[5 empty] | 2019-04-16 | 5 | 2521.5 | 1748 | -127 | 0 | 0 | 1875 | 816.5705 | 816.5705 | 816.5705 | 1851.9373 | 780 | 200 | 2831.9373 | 70.8% | 95% | 0% | -145.3089 | 671.2616 | -2750 | -200 | -2278.7384 | 56.97% | 71.45% | 95% | 0% | 1875 | -127
[5 empty] | 2019-04-16 | 6 | 2522 | 1747 | -122 | 0 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 1851.9373 | 780 | 200 | 2831.9373 | 70.8% | 95% | 0% | -139.5881 | 667.5842 | -2750 | -200 | -2282.4158 | 57.06% | 71.45% | 95% | 0% | 1869 | -122
[5 empty] | 2019-04-16 | 7 | 2522.5 | 1744 | -118 | 0 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 1851.9373 | 780 | 200 | 2831.9373 | 70.8% | 95% | 0% | -135.0114 | 661.1963 | -2750 | -200 | -2288.8037 | 57.22% | 71.45% | 95% | 0% | 1862 | -118
[5 empty] | 2019-04-16 | 8 | 2523 | 1742 | -114 | 0 | 0 | 1856 | 786.8096 | 786.8096 | 786.8096 | 1850.371 | 780 | 200 | 2830.371 | 70.76% | 95% | 0% | -130.4348 | 656.3748 | -2750 | -200 | -2293.6252 | 57.34% | 71.44% | 95% | 0% | 1856 | -114
[5 empty] | 2019-04-16 | 9 | 2523.5 | 1734 | -110 | 0 | 0 | 1844 | 768.0132 | 768.0132 | 768.0132 | 1850.371 | 780 | 200 | 2830.371 | 70.76% | 95% | 0% | -125.8581 | 642.1551 | -2750 | -200 | -2307.8449 | 57.7% | 71.44% | 95% | 0% | 1844 | -110
[5 empty] | 2019-04-16 | 10 | 2524 | 1754 | -105 | 0 | 0 | 1859 | 791.5087 | 791.5087 | 791.5087 | 1850.371 | 780 | 200 | 2830.371 | 70.76% | 95% | 0% | -120.1373 | 671.3714 | -2750 | -200 | -2278.6286 | 56.97% | 71.44% | 95% | 0% | 1859 | -105
[5 empty] | 2019-04-16 | 11 | 2524.5 | 1820 | -103 | 0 | 0 | 1923 | 891.756 | 891.756 | 891.756 | 1850.371 | 780 | 200 | 2830.371 | 70.76% | 95% | 0% | -117.849 | 773.907 | -2750 | -200 | -2176.093 | 54.4% | 71.43% | 95% | 0% | 1923 | -103
[5 empty] | 2019-04-16 | 12 | 2525 | 1899 | -100 | 0 | 0 | 1999 | 1010.7997 | 1010.7997 | 1010.7997 | 1850.371 | 780 | 200 | 2830.371 | 70.76% | 95% | 0% | -114.4165 | 896.3832 | -2750 | -200 | -2053.6168 | 51.34% | 71.43% | 95% | 0% | 1999 | -100
[5 empty] | 2019-04-16 | 13 | 2525.5 | 2057 | -99 | 0 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 1850.371 | 780 | 200 | 2830.371 | 70.76% | 95% | 0% | -113.2723 | 1143.4466 | -2750 | -200 | -1806.5534 | 45.16% | 71.43% | 95% | 0% | 2156 | -99
[5 empty] | 2019-04-16 | 14 | 2526 | 2211 | -108 | 0 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 1850.371 | 780 | 200 | 2830.371 | 70.76% | 95% | 0% | -123.5698 | 1388.4665 | -2750 | -200 | -1561.5335 | 39.04% | 71.43% | 95% | 0% | 2319 | -108
[5 empty] | 2019-04-16 | 15 | 2526.5 | 2381 | -124 | 0 | 0 | 2505 | 1803.38 | 1803.38 | 1803.38 | 1850.371 | 780 | 200 | 2830.371 | 70.76% | 95% | 0% | -141.8764 | 1661.5036 | -2750 | -200 | -1288.4964 | 32.21% | 71.43% | 95% | 0% | 2505 | -124
[5 empty] | 2019-04-16 | 16 | 2527 | 2460 | -146 | 0 | 0 | 2606 | 1961.5829 | 1961.5829 | 1961.5829 | 1850.371 | 780 | 200 | 2830.371 | 70.76% | 95% | 0% | -167.0481 | 1794.5348 | -2750 | -200 | -1155.4652 | 28.89% | 71.43% | 95% | 0% | 2606 | -146
[5 empty] | 2019-04-16 | 17 | 2527.5 | 2534 | -179 | 1 | 0 | 2713 | 2129.1838 | 2129.1838 | 2129.1838 | 1848.8046 | 780 | 200 | 2828.8046 | 70.72% | 95% | 0% | -204.8055 | 1924.3783 | -3550 | -400 | -2025.6217 | 50.64% | 71.42% | 95% | 0% | 2713 | -179
[5 empty] | 2019-04-16 | 18 | 2528 | 2506 | -213 | 1 | 0 | 2719 | 2138.582 | 2138.582 | 2138.582 | 1848.8046 | 780 | 200 | 2828.8046 | 70.72% | 95% | 0% | -243.7071 | 1894.8749 | -3550 | -400 | -2055.1251 | 51.38% | 71.42% | 95% | 0% | 2719 | -213
[5 empty] | 2019-04-16 | 19 | 2528.5 | 2472 | -249 | 1 | 0 | 2721 | 2141.7148 | 2141.7148 | 2141.7148 | 1848.8046 | 780 | 200 | 2828.8046 | 70.72% | 95% | 0% | -284.897 | 1856.8177 | -3550 | -400 | -2093.1823 | 52.33% | 71.42% | 95% | 0% | 2721 | -249
[5 empty] | 2019-04-16 | 20 | 2529 | 2400 | -287 | 1 | 0 | 2687 | 2088.4584 | 2088.4584 | 2088.4584 | 1848.8046 | 780 | 200 | 2828.8046 | 70.72% | 95% | 0% | -328.3753 | 1760.0831 | -3550 | -400 | -2189.9169 | 54.75% | 71.42% | 95% | 0% | 2687 | -287
[5 empty] | 2019-04-16 | 21 | 2529.5 | 2337 | -312 | 1 | 0 | 2649 | 2028.9365 | 2028.9365 | 2028.9365 | 1848.8046 | 780 | 200 | 2828.8046 | 70.72% | 95% | 0% | -356.9794 | 1671.9571 | -3550 | -400 | -2278.0429 | 56.95% | 71.41% | 95% | 0% | 2649 | -312
[5 empty] | 2019-04-16 | 22 | 2530 | 2286 | -358 | 1 | 0 | 2644 | 2021.1047 | 2021.1047 | 2021.1047 | 1848.8046 | 780 | 200 | 2828.8046 | 70.72% | 95% | 0% | -409.611 | 1611.4937 | -3550 | -400 | -2338.5063 | 58.46% | 71.41% | 95% | 0% | 2644 | -358
[5 empty] | 2019-04-16 | 23 | 2530.5 | 2244 | -388 | 1 | 0 | 2632 | 2002.3083 | 2002.3083 | 2002.3083 | 1848.8046 | 780 | 200 | 2828.8046 | 70.72% | 95% | 0% | -443.9359 | 1558.3724 | -3550 | -400 | -2391.6276 | 59.79% | 71.41% | 95% | 0% | 2632 | -388
[5 empty] | 2019-04-16 | 24 | 2531 | 2202 | -416 | 1 | 0 | 2618 | 1980.3792 | 1980.3792 | 1980.3792 | 1848.8046 | 780 | 200 | 2828.8046 | 70.72% | 95% | 0% | -475.9725 | 1504.4067 | -3550 | -400 | -2445.5933 | 61.14% | 71.39% | 95% | 0% | 2618 | -416
[5 empty] | 2019-04-16 | 25 | 2531.5 | 2196 | -413 | 1 | 0 | 2609 | 1966.2819 | 1966.2819 | 1966.2819 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -472.54 | 1493.7419 | -3550 | -400 | -2456.2581 | 61.41% | 71.39% | 95% | 0% | 2609 | -413
[5 empty] | 2019-04-16 | 26 | 2532 | 2157 | -410 | 1 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -469.1076 | 1431.3871 | -3550 | -400 | -2518.6129 | 62.97% | 71.39% | 95% | 0% | 2567 | -410
[5 empty] | 2019-04-16 | 27 | 2532.5 | 2130 | -421 | 1 | 0 | 2551 | 1875.4328 | 1875.4328 | 1875.4328 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -481.6934 | 1393.7394 | -3550 | -400 | -2556.2606 | 63.91% | 71.38% | 95% | 0% | 2551 | -421
[5 empty] | 2019-04-16 | 28 | 2533 | 2099 | -423 | 1 | 0 | 2522 | 1830.0082 | 1830.0082 | 1830.0082 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -483.9817 | 1346.0266 | -3550 | -400 | -2603.9734 | 65.1% | 71.38% | 95% | 0% | 2522 | -423
[5 empty] | 2019-04-16 | 29 | 2533.5 | 2115 | -398 | 1 | 0 | 2513 | 1815.911 | 1815.911 | 1815.911 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -455.3776 | 1360.5334 | -3550 | -400 | -2589.4666 | 64.74% | 71.38% | 95% | 0% | 2513 | -398
[5 empty] | 2019-04-16 | 30 | 2534 | 2148 | -370 | 1 | 0 | 2518 | 1823.7428 | 1823.7428 | 1823.7428 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -423.341 | 1400.4018 | -3550 | -400 | -2549.5982 | 63.74% | 71.37% | 95% | 0% | 2518 | -370
[5 empty] | 2019-04-16 | 31 | 2534.5 | 2171 | -365 | 1 | 0 | 2536 | 1851.9373 | 1851.9373 | 1851.9373 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -417.6201 | 1434.3172 | -3550 | -400 | -2515.6828 | 62.89% | 71.37% | 95% | 0% | 2536 | -365
[5 empty] | 2019-04-16 | 32 | 2535 | 2247 | -330 | 1 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -377.5744 | 1538.5839 | -3550 | -400 | -2411.4161 | 60.29% | 71.37% | 95% | 0% | 2577 | -330
[5 empty] | 2019-04-16 | 33 | 2535.5 | 2329 | -285 | 1 | 0 | 2614 | 1974.1138 | 1974.1138 | 1974.1138 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -326.087 | 1648.0268 | -3550 | -400 | -2301.9732 | 57.55% | 71.36% | 95% | 0% | 2614 | -285
[5 empty] | 2019-04-16 | 34 | 2536 | 2409 | -255 | 1 | 0 | 2664 | 2052.432 | 2052.432 | 2052.432 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -291.762 | 1760.67 | -3550 | -400 | -2189.33 | 54.73% | 71.36% | 95% | 0% | 2664 | -255
[5 empty] | 2019-04-16 | 35 | 2536.5 | 2514 | -224 | 1 | 0 | 2738 | 2168.343 | 2168.343 | 2168.343 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -256.2929 | 1912.05 | -3550 | -400 | -2037.95 | 50.95% | 71.35% | 95% | 0% | 2738 | -224
[5 empty] | 2019-04-16 | 36 | 2537 | 2572 | -197 | 1 | 0 | 2769 | 2216.9002 | 2216.9002 | 2216.9002 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -225.4005 | 1991.4998 | -3550 | -400 | -1958.5002 | 48.96% | 71.35% | 95% | 0% | 2769 | -197
[5 empty] | 2019-04-16 | 37 | 2537.5 | 2633 | -168 | 1 | 0 | 2801 | 2267.0239 | 2267.0239 | 2267.0239 | 1847.2383 | 780 | 200 | 2827.2383 | 70.68% | 95% | 0% | -192.2197 | 2074.8042 | -3550 | -400 | -1875.1958 | 46.88% | 71.35% | 95% | 0% | 2801 | -168
[5 empty] | 2019-04-16 | 38 | 2538 | 2683 | -134 | 1 | 0 | 2817 | 2292.0857 | 2292.0857 | 2292.0857 | 1845.6719 | 780 | 200 | 2825.6719 | 70.64% | 95% | 0% | -153.3181 | 2138.7677 | -3550 | -400 | -1811.2323 | 45.28% | 71.35% | 95% | 0% | 2817 | -134
[5 empty] | 2019-04-16 | 39 | 2538.5 | 2712 | -111 | 1 | 0 | 2823 | 2301.4839 | 2301.4839 | 2301.4839 | 1845.6719 | 780 | 200 | 2825.6719 | 70.64% | 95% | 0% | -127.0023 | 2174.4816 | -3550 | -400 | -1775.5184 | 44.39% | 71.35% | 95% | 0% | 2823 | -111
[5 empty] | 2019-04-16 | 40 | 2539 | 2742 | -97 | 1 | 0 | 2839 | 2326.5458 | 2326.5458 | 2326.5458 | 1845.6719 | 780 | 200 | 2825.6719 | 70.64% | 95% | 0% | -110.984 | 2215.5618 | -3550 | -400 | -1734.4382 | 43.36% | 71.35% | 95% | 0% | 2839 | -97
[5 empty] | 2019-04-16 | 41 | 2539.5 | 2733 | -94 | 1 | 0 | 2827 | 2307.7494 | 2307.7494 | 2307.7494 | 1845.6719 | 780 | 200 | 2825.6719 | 70.64% | 95% | 0% | -107.5515 | 2200.1979 | -3550 | -400 | -1749.8021 | 43.75% | 71.35% | 95% | 0% | 2827 | -94
[5 empty] | 2019-04-16 | 42 | 2540 | 2717 | -94 | 1 | 0 | 2811 | 2282.6876 | 2282.6876 | 2282.6876 | 1845.6719 | 780 | 200 | 2825.6719 | 70.64% | 95% | 0% | -107.5515 | 2175.1361 | -3550 | -400 | -1774.8639 | 44.37% | 71.34% | 95% | 0% | 2811 | -94
[5 empty] | 2019-04-16 | 43 | 2540.5 | 2625 | -93 | 0 | 0 | 2718 | 2137.0157 | 2137.0157 | 2137.0157 | 1845.6719 | 780 | 200 | 2825.6719 | 70.64% | 95% | 0% | -106.4073 | 2030.6083 | -2750 | -200 | -919.3917 | 22.98% | 71.33% | 95% | 0% | 2718 | -93
[5 empty] | 2019-04-16 | 44 | 2541 | 2475 | -92 | 0 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 1845.6719 | 780 | 200 | 2825.6719 | 70.64% | 95% | 0% | -105.2632 | 1795.2315 | -2750 | -200 | -1154.7685 | 28.87% | 71.33% | 95% | 0% | 2567 | -92
[5 empty] | 2019-04-16 | 45 | 2541.5 | 2342 | -91 | 0 | 0 | 2433 | 1690.6018 | 1690.6018 | 1690.6018 | 1845.6719 | 780 | 200 | 2825.6719 | 70.64% | 95% | 0% | -104.119 | 1586.4828 | -2750 | -200 | -1363.5172 | 34.09% | 71.33% | 95% | 0% | 2433 | -91
[5 empty] | 2019-04-16 | 46 | 2542 | 2177 | -89 | 0 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -101.8307 | 1327.1883 | -2750 | -200 | -1622.8117 | 40.57% | 71.33% | 95% | 0% | 2266 | -89
[5 empty] | 2019-04-16 | 47 | 2542.5 | 2030 | -86 | 0 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -98.3982 | 1095.6661 | -2750 | -200 | -1854.3339 | 46.36% | 71.33% | 95% | 0% | 2116 | -86
[5 empty] | 2019-04-16 | 48 | 2543 | 1915 | -83 | 0 | 0 | 1998 | 1009.2333 | 1009.2333 | 1009.2333 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -94.9657 | 914.2676 | -2750 | -200 | -2035.7324 | 50.89% | 71.32% | 95% | 0% | 1998 | -83
[5 empty] | 2019-04-17 | 1 | 2543.5 | 1833 | -79 | 0 | 0 | 1912 | 874.526 | 874.526 | 874.526 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -90.389 | 784.137 | -2750 | -200 | -2165.863 | 54.15% | 71.32% | 95% | 0% | 1912 | -79
[5 empty] | 2019-04-17 | 2 | 2544 | 1795 | -76 | 0 | 0 | 1871 | 810.305 | 810.305 | 810.305 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -86.9565 | 723.3485 | -2750 | -200 | -2226.6515 | 55.67% | 71.32% | 95% | 0% | 1871 | -76
[5 empty] | 2019-04-17 | 3 | 2544.5 | 1812 | -73 | 0 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -83.524 | 748.7101 | -2750 | -200 | -2201.2899 | 55.03% | 71.32% | 95% | 0% | 1885 | -73
[5 empty] | 2019-04-17 | 4 | 2545 | 1857 | -71 | 0 | 0 | 1928 | 899.5878 | 899.5878 | 899.5878 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -81.2357 | 818.3521 | -2750 | -200 | -2131.6479 | 53.29% | 71.32% | 95% | 0% | 1928 | -71
[5 empty] | 2019-04-17 | 5 | 2545.5 | 1867 | -69 | 0 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -78.9474 | 833.1713 | -2750 | -200 | -2116.8287 | 52.92% | 71.31% | 95% | 0% | 1936 | -69
[5 empty] | 2019-04-17 | 6 | 2546 | 1845 | -67 | 0 | 0 | 1912 | 874.526 | 874.526 | 874.526 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -76.659 | 797.8669 | -2750 | -200 | -2152.1331 | 53.8% | 71.31% | 95% | 0% | 1912 | -67
[5 empty] | 2019-04-17 | 7 | 2546.5 | 1833 | -65 | 0 | 0 | 1898 | 852.5969 | 852.5969 | 852.5969 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -74.3707 | 778.2262 | -2750 | -200 | -2171.7738 | 54.29% | 71.3% | 95% | 0% | 1898 | -65
[5 empty] | 2019-04-17 | 8 | 2547 | 1819 | -64 | 0 | 0 | 1883 | 829.1014 | 829.1014 | 829.1014 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -73.2265 | 755.8749 | -2750 | -200 | -2194.1251 | 54.85% | 71.29% | 95% | 0% | 1883 | -64
[5 empty] | 2019-04-17 | 9 | 2547.5 | 1805 | -64 | 0 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -73.2265 | 733.9458 | -2750 | -200 | -2216.0542 | 55.4% | 71.29% | 95% | 0% | 1869 | -64
[5 empty] | 2019-04-17 | 10 | 2548 | 1803 | -64 | 0 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 1844.1055 | 780 | 200 | 2824.1055 | 70.6% | 95% | 0% | -73.2265 | 730.813 | -2750 | -200 | -2219.187 | 55.48% | 71.29% | 95% | 0% | 1867 | -64
[5 empty] | 2019-04-17 | 11 | 2548.5 | 1860 | -66 | 1 | 0 | 1926 | 896.4551 | 896.4551 | 896.4551 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -75.5149 | 820.9402 | -3550 | -400 | -3129.0598 | 78.23% | 71.28% | 95% | 0% | 1926 | -66
[5 empty] | 2019-04-17 | 12 | 2549 | 1938 | -67 | 1 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -76.659 | 943.5388 | -3550 | -400 | -3006.4612 | 75.16% | 71.28% | 95% | 0% | 2005 | -67
[5 empty] | 2019-04-17 | 13 | 2549.5 | 2109 | -70 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -80.0915 | 1212.6537 | -3550 | -400 | -2737.3463 | 68.43% | 71.28% | 95% | 0% | 2179 | -70
[5 empty] | 2019-04-17 | 14 | 2550 | 2247 | -84 | 1 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -96.1098 | 1434.7228 | -3550 | -400 | -2515.2772 | 62.88% | 71.28% | 95% | 0% | 2331 | -84
[5 empty] | 2019-04-17 | 15 | 2550.5 | 2394 | -110 | 1 | 0 | 2504 | 1801.8137 | 1801.8137 | 1801.8137 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -125.8581 | 1675.9556 | -3550 | -400 | -2274.0444 | 56.85% | 71.28% | 95% | 0% | 2504 | -110
[5 empty] | 2019-04-17 | 16 | 2551 | 2401 | -144 | 1 | 0 | 2545 | 1866.0346 | 1866.0346 | 1866.0346 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -164.7597 | 1701.2749 | -3550 | -400 | -2248.7251 | 56.22% | 71.27% | 95% | 0% | 2545 | -144
[5 empty] | 2019-04-17 | 17 | 2551.5 | 2406 | -190 | 1 | 0 | 2596 | 1945.9192 | 1945.9192 | 1945.9192 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -217.3913 | 1728.5279 | -3550 | -400 | -2221.4721 | 55.54% | 71.27% | 95% | 0% | 2596 | -190
[5 empty] | 2019-04-17 | 18 | 2552 | 2340 | -243 | 1 | 0 | 2583 | 1925.5565 | 1925.5565 | 1925.5565 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -278.032 | 1647.5244 | -3550 | -400 | -2302.4756 | 57.56% | 71.27% | 95% | 0% | 2583 | -243
[5 empty] | 2019-04-17 | 19 | 2552.5 | 2264 | -304 | 1 | 0 | 2568 | 1902.061 | 1902.061 | 1902.061 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -347.8261 | 1554.2349 | -3550 | -400 | -2395.7651 | 59.89% | 71.27% | 95% | 0% | 2568 | -304
[5 empty] | 2019-04-17 | 20 | 2553 | 2123 | -368 | 1 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -421.0526 | 1360.3983 | -3550 | -400 | -2589.6017 | 64.74% | 71.26% | 95% | 0% | 2491 | -368
[5 empty] | 2019-04-17 | 21 | 2553.5 | 1986 | -440 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -503.4325 | 1176.2048 | -3550 | -400 | -2773.7952 | 69.34% | 71.26% | 95% | 0% | 2426 | -440
[5 empty] | 2019-04-17 | 22 | 2554 | 1890 | -515 | 1 | 0 | 2405 | 1646.7436 | 1646.7436 | 1646.7436 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -589.2449 | 1057.4988 | -3550 | -400 | -2892.5012 | 72.31% | 71.25% | 95% | 0% | 2405 | -515
[5 empty] | 2019-04-17 | 23 | 2554.5 | 1801 | -569 | 1 | 0 | 2370 | 1591.9209 | 1591.9209 | 1591.9209 | 1842.5392 | 780 | 200 | 2822.5392 | 70.56% | 95% | 0% | -651.0297 | 940.8911 | -3550 | -400 | -3009.1089 | 75.23% | 71.25% | 95% | 0% | 2370 | -569
[5 empty] | 2019-04-17 | 24 | 2555 | 1701 | -612 | 1 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 1840.9728 | 780 | 200 | 2820.9728 | 70.52% | 95% | 0% | -700.2288 | 802.4093 | -3550 | -400 | -3147.5907 | 78.69% | 71.23% | 95% | 0% | 2313 | -612
[5 empty] | 2019-04-17 | 25 | 2555.5 | 1654 | -632 | 1 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 1840.9728 | 780 | 200 | 2820.9728 | 70.52% | 95% | 0% | -723.1121 | 737.2341 | -3550 | -400 | -3212.7659 | 80.32% | 71.23% | 95% | 0% | 2286 | -632
[5 empty] | 2019-04-17 | 26 | 2556 | 1604 | -647 | 1 | 0 | 2251 | 1405.5235 | 1405.5235 | 1405.5235 | 1840.9728 | 780 | 200 | 2820.9728 | 70.52% | 95% | 0% | -740.2746 | 665.2489 | -3550 | -400 | -3284.7511 | 82.12% | 71.22% | 95% | 0% | 2251 | -647
[5 empty] | 2019-04-17 | 27 | 2556.5 | 1550 | -652 | 1 | 0 | 2202 | 1328.7716 | 1328.7716 | 1328.7716 | 1840.9728 | 780 | 200 | 2820.9728 | 70.52% | 95% | 0% | -745.9954 | 582.7762 | -3550 | -400 | -3367.2238 | 84.18% | 71.22% | 95% | 0% | 2202 | -652
[5 empty] | 2019-04-17 | 28 | 2557 | 1535 | -643 | 1 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 1840.9728 | 780 | 200 | 2820.9728 | 70.52% | 95% | 0% | -735.6979 | 555.481 | -3550 | -400 | -3394.519 | 84.86% | 71.22% | 95% | 0% | 2178 | -643
[5 empty] | 2019-04-17 | 29 | 2557.5 | 1552 | -624 | 1 | 0 | 2176 | 1288.0462 | 1288.0462 | 1288.0462 | 1840.9728 | 780 | 200 | 2820.9728 | 70.52% | 95% | 0% | -713.9588 | 574.0874 | -3550 | -400 | -3375.9126 | 84.4% | 71.22% | 95% | 0% | 2176 | -624
[5 empty] | 2019-04-17 | 30 | 2558 | 1575 | -605 | 1 | 0 | 2180 | 1294.3116 | 1294.3116 | 1294.3116 | 1840.9728 | 780 | 200 | 2820.9728 | 70.52% | 95% | 0% | -692.2197 | 602.0919 | -3550 | -400 | -3347.9081 | 83.7% | 71.22% | 95% | 0% | 2180 | -605
[5 empty] | 2019-04-17 | 31 | 2558.5 | 1632 | -569 | 1 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 1839.4064 | 780 | 200 | 2819.4064 | 70.49% | 95% | 0% | -651.0297 | 676.1755 | -3550 | -400 | -3273.8245 | 81.85% | 71.22% | 95% | 0% | 2201 | -569
[5 empty] | 2019-04-17 | 32 | 2559 | 1726 | -515 | 1 | 0 | 2241 | 1389.8599 | 1389.8599 | 1389.8599 | 1839.4064 | 780 | 200 | 2819.4064 | 70.49% | 95% | 0% | -589.2449 | 800.615 | -3550 | -400 | -3149.385 | 78.73% | 71.21% | 95% | 0% | 2241 | -515
[5 empty] | 2019-04-17 | 33 | 2559.5 | 1834 | -459 | 1 | 0 | 2293 | 1471.3108 | 1471.3108 | 1471.3108 | 1839.4064 | 780 | 200 | 2819.4064 | 70.49% | 95% | 0% | -525.1716 | 946.1392 | -3550 | -400 | -3003.8608 | 75.1% | 71.21% | 95% | 0% | 2293 | -459
[5 empty] | 2019-04-17 | 34 | 2560 | 1977 | -397 | 1 | 0 | 2374 | 1598.1863 | 1598.1863 | 1598.1863 | 1839.4064 | 780 | 200 | 2819.4064 | 70.49% | 95% | 0% | -454.2334 | 1143.9529 | -3550 | -400 | -2806.0471 | 70.15% | 71.21% | 95% | 0% | 2374 | -397
[5 empty] | 2019-04-17 | 35 | 2560.5 | 2125 | -335 | 1 | 0 | 2460 | 1732.8937 | 1732.8937 | 1732.8937 | 1839.4064 | 780 | 200 | 2819.4064 | 70.49% | 95% | 0% | -383.2952 | 1349.5985 | -3550 | -400 | -2600.4015 | 65.01% | 71.19% | 95% | 0% | 2460 | -335
[5 empty] | 2019-04-17 | 36 | 2561 | 2219 | -270 | 1 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 1839.4064 | 780 | 200 | 2819.4064 | 70.49% | 95% | 0% | -308.9245 | 1469.3937 | -3550 | -400 | -2480.6063 | 62.02% | 71.19% | 95% | 0% | 2489 | -270
[5 empty] | 2019-04-17 | 37 | 2561.5 | 2321 | -212 | 1 | 0 | 2533 | 1847.2383 | 1847.2383 | 1847.2383 | 1839.4064 | 780 | 200 | 2819.4064 | 70.49% | 95% | 0% | -242.5629 | 1604.6753 | -3550 | -400 | -2345.3247 | 58.63% | 71.19% | 95% | 0% | 2533 | -212
[5 empty] | 2019-04-17 | 38 | 2562 | 2402 | -159 | 1 | 0 | 2561 | 1891.0965 | 1891.0965 | 1891.0965 | 1839.4064 | 780 | 200 | 2819.4064 | 70.49% | 95% | 0% | -181.9222 | 1709.1743 | -3550 | -400 | -2240.8257 | 56.02% | 71.19% | 95% | 0% | 2561 | -159
[5 empty] | 2019-04-17 | 39 | 2562.5 | 2488 | -120 | 1 | 0 | 2608 | 1964.7156 | 1964.7156 | 1964.7156 | 1839.4064 | 780 | 200 | 2819.4064 | 70.49% | 95% | 0% | -137.2998 | 1827.4158 | -3550 | -400 | -2122.5842 | 53.06% | 71.19% | 95% | 0% | 2608 | -120
[5 empty] | 2019-04-17 | 40 | 2563 | 2535 | -98 | 1 | 0 | 2633 | 2003.8747 | 2003.8747 | 2003.8747 | 1837.8401 | 780 | 200 | 2817.8401 | 70.45% | 95% | 0% | -112.1281 | 1891.7465 | -3550 | -400 | -2058.2535 | 51.46% | 71.18% | 95% | 0% | 2633 | -98
[5 empty] | 2019-04-17 | 41 | 2563.5 | 2583 | -96 | 1 | 0 | 2679 | 2075.9275 | 2075.9275 | 2075.9275 | 1837.8401 | 780 | 200 | 2817.8401 | 70.45% | 95% | 0% | -109.8398 | 1966.0876 | -3550 | -400 | -1983.9124 | 49.6% | 71.18% | 95% | 0% | 2679 | -96
[5 empty] | 2019-04-17 | 42 | 2564 | 2584 | -98 | 1 | 0 | 2682 | 2080.6265 | 2080.6265 | 2080.6265 | 1837.8401 | 780 | 200 | 2817.8401 | 70.45% | 95% | 0% | -112.1281 | 1968.4984 | -3550 | -400 | -1981.5016 | 49.54% | 71.15% | 95% | 0% | 2682 | -98
[5 empty] | 2019-04-17 | 43 | 2564.5 | 2492 | -99 | 0 | 0 | 2591 | 1938.0874 | 1938.0874 | 1938.0874 | 1837.8401 | 780 | 200 | 2817.8401 | 70.45% | 95% | 0% | -113.2723 | 1824.8151 | -2750 | -200 | -1125.1849 | 28.13% | 71.15% | 95% | 0% | 2591 | -99
[5 empty] | 2019-04-17 | 44 | 2565 | 2371 | -100 | 0 | 0 | 2471 | 1750.1237 | 1750.1237 | 1750.1237 | 1837.8401 | 780 | 200 | 2817.8401 | 70.45% | 95% | 0% | -114.4165 | 1635.7072 | -2750 | -200 | -1314.2928 | 32.86% | 71.14% | 95% | 0% | 2471 | -100
[5 empty] | 2019-04-17 | 45 | 2565.5 | 2259 | -100 | 0 | 0 | 2359 | 1574.6908 | 1574.6908 | 1574.6908 | 1837.8401 | 780 | 200 | 2817.8401 | 70.45% | 95% | 0% | -114.4165 | 1460.2744 | -2750 | -200 | -1489.7256 | 37.24% | 71.14% | 95% | 0% | 2359 | -100
[5 empty] | 2019-04-17 | 46 | 2566 | 2116 | -100 | 0 | 0 | 2216 | 1350.7007 | 1350.7007 | 1350.7007 | 1837.8401 | 780 | 200 | 2817.8401 | 70.45% | 95% | 0% | -114.4165 | 1236.2843 | -2750 | -200 | -1713.7157 | 42.84% | 71.13% | 95% | 0% | 2216 | -100
[5 empty] | 2019-04-17 | 47 | 2566.5 | 1968 | -100 | 0 | 0 | 2068 | 1118.8788 | 1118.8788 | 1118.8788 | 1836.2737 | 780 | 200 | 2816.2737 | 70.41% | 95% | 0% | -114.4165 | 1004.4623 | -2750 | -200 | -1945.5377 | 48.64% | 71.13% | 95% | 0% | 2068 | -100
[5 empty] | 2019-04-17 | 48 | 2567 | 1860 | -100 | 0 | 0 | 1960 | 949.7115 | 949.7115 | 949.7115 | 1836.2737 | 780 | 200 | 2816.2737 | 70.41% | 95% | 0% | -114.4165 | 835.295 | -2750 | -200 | -2114.705 | 52.87% | 71.13% | 95% | 0% | 1960 | -100
[5 empty] | 2019-04-18 | 1 | 2567.5 | 1765 | -98 | 0 | 0 | 1863 | 797.7741 | 797.7741 | 797.7741 | 1836.2737 | 780 | 200 | 2816.2737 | 70.41% | 95% | 0% | -112.1281 | 685.646 | -2750 | -200 | -2264.354 | 56.61% | 71.13% | 95% | 0% | 1863 | -98
[5 empty] | 2019-04-18 | 2 | 2568 | 1726 | -96 | 0 | 0 | 1822 | 733.5532 | 733.5532 | 733.5532 | 1836.2737 | 780 | 200 | 2816.2737 | 70.41% | 95% | 0% | -109.8398 | 623.7134 | -2750 | -200 | -2326.2866 | 58.16% | 71.13% | 95% | 0% | 1822 | -96
[5 empty] | 2019-04-18 | 3 | 2568.5 | 1729 | -96 | 0 | 0 | 1825 | 738.2523 | 738.2523 | 738.2523 | 1836.2737 | 780 | 200 | 2816.2737 | 70.41% | 95% | 0% | -109.8398 | 628.4125 | -2750 | -200 | -2321.5875 | 58.04% | 71.12% | 95% | 0% | 1825 | -96
[5 empty] | 2019-04-18 | 4 | 2569 | 1747 | -96 | 0 | 0 | 1843 | 766.4468 | 766.4468 | 766.4468 | 1836.2737 | 780 | 200 | 2816.2737 | 70.41% | 95% | 0% | -109.8398 | 656.607 | -2750 | -200 | -2293.393 | 57.33% | 71.11% | 95% | 0% | 1843 | -96
[5 empty] | 2019-04-18 | 5 | 2569.5 | 1742 | -96 | 0 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 1836.2737 | 780 | 200 | 2816.2737 | 70.41% | 95% | 0% | -109.8398 | 648.7752 | -2750 | -200 | -2301.2248 | 57.53% | 71.11% | 95% | 0% | 1838 | -96
[5 empty] | 2019-04-18 | 6 | 2570 | 1705 | -96 | 0 | 0 | 1801 | 700.6595 | 700.6595 | 700.6595 | 1836.2737 | 780 | 200 | 2816.2737 | 70.41% | 95% | 0% | -109.8398 | 590.8197 | -2750 | -200 | -2359.1803 | 58.98% | 71.11% | 95% | 0% | 1801 | -96
[5 empty] | 2019-04-18 | 7 | 2570.5 | 1685 | -95 | 0 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 1836.2737 | 780 | 200 | 2816.2737 | 70.41% | 95% | 0% | -108.6957 | 559.0702 | -2750 | -200 | -2390.9298 | 59.77% | 71.11% | 95% | 0% | 1780 | -95
[5 empty] | 2019-04-18 | 8 | 2571 | 1671 | -94 | 0 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 1836.2737 | 780 | 200 | 2816.2737 | 70.41% | 95% | 0% | -107.5515 | 536.7189 | -2750 | -200 | -2413.2811 | 60.33% | 71.11% | 95% | 0% | 1765 | -94
[5 empty] | 2019-04-18 | 9 | 2571.5 | 1675 | -94 | 0 | 0 | 1769 | 650.5359 | 650.5359 | 650.5359 | 1834.7073 | 780 | 200 | 2814.7073 | 70.37% | 95% | 0% | -107.5515 | 542.9844 | -2750 | -200 | -2407.0156 | 60.18% | 71.11% | 95% | 0% | 1769 | -94
[5 empty] | 2019-04-18 | 10 | 2572 | 1689 | -95 | 1 | 0 | 1784 | 674.0313 | 674.0313 | 674.0313 | 1834.7073 | 780 | 200 | 2814.7073 | 70.37% | 95% | 0% | -108.6957 | 565.3357 | -3550 | -400 | -3384.6643 | 84.62% | 71.11% | 95% | 0% | 1784 | -95
[5 empty] | 2019-04-18 | 11 | 2572.5 | 1747 | -96 | 1 | 0 | 1843 | 766.4468 | 766.4468 | 766.4468 | 1834.7073 | 780 | 200 | 2814.7073 | 70.37% | 95% | 0% | -109.8398 | 656.607 | -3550 | -400 | -3293.393 | 82.33% | 71.11% | 95% | 0% | 1843 | -96
[5 empty] | 2019-04-18 | 12 | 2573 | 1820 | -98 | 1 | 0 | 1918 | 883.9242 | 883.9242 | 883.9242 | 1834.7073 | 780 | 200 | 2814.7073 | 70.37% | 95% | 0% | -112.1281 | 771.796 | -3550 | -400 | -3178.204 | 79.46% | 71.1% | 95% | 0% | 1918 | -98
[5 empty] | 2019-04-18 | 13 | 2573.5 | 1957 | -102 | 1 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 1834.7073 | 780 | 200 | 2814.7073 | 70.37% | 95% | 0% | -116.7048 | 988.0767 | -3550 | -400 | -2961.9233 | 74.05% | 71.1% | 95% | 0% | 2059 | -102
[5 empty] | 2019-04-18 | 14 | 2574 | 2093 | -121 | 1 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 1834.7073 | 780 | 200 | 2814.7073 | 70.37% | 95% | 0% | -138.4439 | 1209.1241 | -3550 | -400 | -2740.8759 | 68.52% | 71.1% | 95% | 0% | 2214 | -121
[5 empty] | 2019-04-18 | 15 | 2574.5 | 2260 | -148 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 1834.7073 | 780 | 200 | 2814.7073 | 70.37% | 95% | 0% | -169.3364 | 1482.1063 | -3550 | -400 | -2467.8937 | 61.7% | 71.1% | 95% | 0% | 2408 | -148
[5 empty] | 2019-04-18 | 16 | 2575 | 2292 | -183 | 1 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 1833.141 | 780 | 200 | 2813.141 | 70.33% | 95% | 0% | -209.3822 | 1547.007 | -3550 | -400 | -2402.993 | 60.07% | 71.1% | 95% | 0% | 2475 | -183
[5 empty] | 2019-04-18 | 17 | 2575.5 | 2273 | -233 | 1 | 0 | 2506 | 1804.9464 | 1804.9464 | 1804.9464 | 1833.141 | 780 | 200 | 2813.141 | 70.33% | 95% | 0% | -266.5904 | 1538.356 | -3550 | -400 | -2411.644 | 60.29% | 71.1% | 95% | 0% | 2506 | -233
[5 empty] | 2019-04-18 | 18 | 2576 | 2179 | -292 | 1 | 0 | 2471 | 1750.1237 | 1750.1237 | 1750.1237 | 1833.141 | 780 | 200 | 2813.141 | 70.33% | 95% | 0% | -334.0961 | 1416.0276 | -3550 | -400 | -2533.9724 | 63.35% | 71.1% | 95% | 0% | 2471 | -292
[5 empty] | 2019-04-18 | 19 | 2576.5 | 2083 | -353 | 1 | 0 | 2436 | 1695.3009 | 1695.3009 | 1695.3009 | 1833.141 | 780 | 200 | 2813.141 | 70.33% | 95% | 0% | -403.8902 | 1291.4107 | -3550 | -400 | -2658.5893 | 66.46% | 71.09% | 95% | 0% | 2436 | -353
[5 empty] | 2019-04-18 | 20 | 2577 | 1964 | -418 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 1833.141 | 780 | 200 | 2813.141 | 70.33% | 95% | 0% | -478.2609 | 1132.4564 | -3550 | -400 | -2817.5436 | 70.44% | 71.09% | 95% | 0% | 2382 | -418
[5 empty] | 2019-04-18 | 21 | 2577.5 | 1842 | -490 | 1 | 0 | 2332 | 1532.399 | 1532.399 | 1532.399 | 1833.141 | 780 | 200 | 2813.141 | 70.33% | 95% | 0% | -560.6407 | 971.7583 | -3550 | -400 | -2978.2417 | 74.46% | 71.09% | 95% | 0% | 2332 | -490
[5 empty] | 2019-04-18 | 22 | 2578 | 1674 | -607 | 1 | 0 | 2281 | 1452.5144 | 1452.5144 | 1452.5144 | 1833.141 | 780 | 200 | 2813.141 | 70.33% | 95% | 0% | -694.508 | 758.0064 | -3550 | -400 | -3191.9936 | 79.8% | 71.08% | 95% | 0% | 2281 | -607
[5 empty] | 2019-04-18 | 23 | 2578.5 | 1581 | -663 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1833.141 | 780 | 200 | 2813.141 | 70.33% | 95% | 0% | -758.5812 | 635.9777 | -3550 | -400 | -3314.0223 | 82.85% | 71.07% | 95% | 0% | 2244 | -663
[5 empty] | 2019-04-18 | 24 | 2579 | 1508 | -690 | 1 | 0 | 2198 | 1322.5062 | 1322.5062 | 1322.5062 | 1833.141 | 780 | 200 | 2813.141 | 70.33% | 95% | 0% | -789.4737 | 533.0325 | -3550 | -400 | -3416.9675 | 85.42% | 71.07% | 95% | 0% | 2198 | -690
[5 empty] | 2019-04-18 | 25 | 2579.5 | 1459 | -712 | 1 | 0 | 2171 | 1280.2143 | 1280.2143 | 1280.2143 | 1831.5746 | 780 | 200 | 2811.5746 | 70.29% | 95% | 0% | -814.6453 | 465.569 | -3550 | -400 | -3484.431 | 87.11% | 71.07% | 95% | 0% | 2171 | -712
[5 empty] | 2019-04-18 | 26 | 2580 | 1391 | -732 | 1 | 0 | 2123 | 1205.0289 | 1205.0289 | 1205.0289 | 1831.5746 | 780 | 200 | 2811.5746 | 70.29% | 95% | 0% | -837.5286 | 367.5002 | -3550 | -400 | -3582.4998 | 89.56% | 71.06% | 95% | 0% | 2123 | -732
[5 empty] | 2019-04-18 | 27 | 2580.5 | 1357 | -733 | 1 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 1831.5746 | 780 | 200 | 2811.5746 | 70.29% | 95% | 0% | -838.6728 | 314.6661 | -3550 | -400 | -3635.3339 | 90.88% | 71.06% | 95% | 0% | 2090 | -733
[5 empty] | 2019-04-18 | 28 | 2581 | 1347 | -722 | 1 | 0 | 2069 | 1120.4452 | 1120.4452 | 1120.4452 | 1831.5746 | 780 | 200 | 2811.5746 | 70.29% | 95% | 0% | -826.087 | 294.3582 | -3550 | -400 | -3655.6418 | 91.39% | 71.05% | 95% | 0% | 2069 | -722
[5 empty] | 2019-04-18 | 29 | 2581.5 | 1356 | -688 | 1 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 1831.5746 | 780 | 200 | 2811.5746 | 70.29% | 95% | 0% | -787.1854 | 294.1007 | -3550 | -400 | -3655.8993 | 91.4% | 71.05% | 95% | 0% | 2044 | -688
[5 empty] | 2019-04-18 | 30 | 2582 | 1416 | -633 | 1 | 0 | 2049 | 1089.1179 | 1089.1179 | 1089.1179 | 1831.5746 | 780 | 200 | 2811.5746 | 70.29% | 95% | 0% | -724.2563 | 364.8616 | -3550 | -400 | -3585.1384 | 89.63% | 71.04% | 95% | 0% | 2049 | -633
[5 empty] | 2019-04-18 | 31 | 2582.5 | 1489 | -600 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1831.5746 | 780 | 200 | 2811.5746 | 70.29% | 95% | 0% | -686.4989 | 465.2736 | -3550 | -400 | -3484.7264 | 87.12% | 71.04% | 95% | 0% | 2089 | -600
[5 empty] | 2019-04-18 | 32 | 2583 | 1563 | -545 | 1 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -623.5698 | 557.9636 | -3550 | -400 | -3392.0364 | 84.8% | 71.04% | 95% | 0% | 2108 | -545
[5 empty] | 2019-04-18 | 33 | 2583.5 | 1691 | -482 | 1 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -551.4874 | 731.8597 | -3550 | -400 | -3218.1403 | 80.45% | 71.04% | 95% | 0% | 2173 | -482
[5 empty] | 2019-04-18 | 34 | 2584 | 1831 | -415 | 1 | 0 | 2246 | 1397.6917 | 1397.6917 | 1397.6917 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -474.8284 | 922.8633 | -3550 | -400 | -3027.1367 | 75.68% | 71.04% | 95% | 0% | 2246 | -415
[5 empty] | 2019-04-18 | 35 | 2584.5 | 1979 | -346 | 1 | 0 | 2325 | 1521.4345 | 1521.4345 | 1521.4345 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -395.881 | 1125.5535 | -3550 | -400 | -2824.4465 | 70.61% | 71.03% | 95% | 0% | 2325 | -346
[5 empty] | 2019-04-18 | 36 | 2585 | 2069 | -285 | 1 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -326.087 | 1240.7721 | -3550 | -400 | -2709.2279 | 67.73% | 71.03% | 95% | 0% | 2354 | -285
[5 empty] | 2019-04-18 | 37 | 2585.5 | 2178 | -226 | 1 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -258.5812 | 1386.596 | -3550 | -400 | -2563.404 | 64.09% | 71.03% | 95% | 0% | 2404 | -226
[5 empty] | 2019-04-18 | 38 | 2586 | 2259 | -177 | 1 | 0 | 2436 | 1695.3009 | 1695.3009 | 1695.3009 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -202.5172 | 1492.7837 | -3550 | -400 | -2457.2163 | 61.43% | 71.03% | 95% | 0% | 2436 | -177
[5 empty] | 2019-04-18 | 39 | 2586.5 | 2288 | -142 | 1 | 0 | 2430 | 1685.9027 | 1685.9027 | 1685.9027 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -162.4714 | 1523.4313 | -3550 | -400 | -2426.5687 | 60.66% | 71.03% | 95% | 0% | 2430 | -142
[5 empty] | 2019-04-18 | 40 | 2587 | 2327 | -118 | 1 | 0 | 2445 | 1709.3982 | 1709.3982 | 1709.3982 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -135.0114 | 1574.3867 | -3550 | -400 | -2375.6133 | 59.39% | 71.03% | 95% | 0% | 2445 | -118
[5 empty] | 2019-04-18 | 41 | 2587.5 | 2353 | -115 | 1 | 0 | 2468 | 1745.4246 | 1745.4246 | 1745.4246 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -131.5789 | 1613.8456 | -3550 | -400 | -2336.1544 | 58.4% | 71.02% | 95% | 0% | 2468 | -115
[5 empty] | 2019-04-18 | 42 | 2588 | 2365 | -117 | 1 | 0 | 2482 | 1767.3537 | 1767.3537 | 1767.3537 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -133.8673 | 1633.4864 | -3550 | -400 | -2316.5136 | 57.91% | 71.02% | 95% | 0% | 2482 | -117
[5 empty] | 2019-04-18 | 43 | 2588.5 | 2328 | -118 | 0 | 0 | 2446 | 1710.9646 | 1710.9646 | 1710.9646 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -135.0114 | 1575.9531 | -2750 | -200 | -1374.0469 | 34.35% | 71.02% | 95% | 0% | 2446 | -118
[5 empty] | 2019-04-18 | 44 | 2589 | 2244 | -118 | 0 | 0 | 2362 | 1579.3899 | 1579.3899 | 1579.3899 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -135.0114 | 1444.3785 | -2750 | -200 | -1505.6215 | 37.64% | 71.01% | 95% | 0% | 2362 | -118
[5 empty] | 2019-04-18 | 45 | 2589.5 | 2141 | -117 | 0 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 1830.0082 | 780 | 200 | 2810.0082 | 70.25% | 95% | 0% | -133.8673 | 1282.6208 | -2750 | -200 | -1667.3792 | 41.68% | 71.01% | 95% | 0% | 2258 | -117
[5 empty] | 2019-04-18 | 46 | 2590 | 2014 | -115 | 0 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -131.5789 | 1082.8481 | -2750 | -200 | -1867.1519 | 46.68% | 71.01% | 95% | 0% | 2129 | -115
[5 empty] | 2019-04-18 | 47 | 2590.5 | 1877 | -114 | 0 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -130.4348 | 867.834 | -2750 | -200 | -2082.166 | 52.05% | 71.01% | 95% | 0% | 1991 | -114
[5 empty] | 2019-04-18 | 48 | 2591 | 1770 | -112 | 0 | 0 | 1882 | 827.535 | 827.535 | 827.535 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -128.1465 | 699.3886 | -2750 | -200 | -2250.6114 | 56.27% | 71.01% | 95% | 0% | 1882 | -112
[5 empty] | 2019-04-19 | 1 | 2591.5 | 1680 | -108 | 0 | 0 | 1788 | 680.2968 | 680.2968 | 680.2968 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -123.5698 | 556.727 | -2750 | -200 | -2393.273 | 59.83% | 71% | 95% | 0% | 1788 | -108
[5 empty] | 2019-04-19 | 2 | 2592 | 1644 | -105 | 0 | 0 | 1749 | 619.2086 | 619.2086 | 619.2086 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -120.1373 | 499.0713 | -2750 | -200 | -2450.9287 | 61.27% | 71% | 95% | 0% | 1749 | -105
[5 empty] | 2019-04-19 | 3 | 2592.5 | 1642 | -102 | 0 | 0 | 1744 | 611.3768 | 611.3768 | 611.3768 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -116.7048 | 494.6719 | -2750 | -200 | -2455.3281 | 61.38% | 71% | 95% | 0% | 1744 | -102
[5 empty] | 2019-04-19 | 4 | 2593 | 1660 | -99 | 0 | 0 | 1759 | 634.8722 | 634.8722 | 634.8722 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -113.2723 | 521.5999 | -2750 | -200 | -2428.4001 | 60.71% | 70.99% | 95% | 0% | 1759 | -99
[5 empty] | 2019-04-19 | 5 | 2593.5 | 1649 | -96 | 0 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -109.8398 | 503.1033 | -2750 | -200 | -2446.8967 | 61.17% | 70.99% | 95% | 0% | 1745 | -96
[5 empty] | 2019-04-19 | 6 | 2594 | 1622 | -94 | 0 | 0 | 1716 | 567.5185 | 567.5185 | 567.5185 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -107.5515 | 459.9671 | -2750 | -200 | -2490.0329 | 62.25% | 70.98% | 95% | 0% | 1716 | -94
[5 empty] | 2019-04-19 | 7 | 2594.5 | 1597 | -91 | 0 | 0 | 1688 | 523.6603 | 523.6603 | 523.6603 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -104.119 | 419.5414 | -2750 | -200 | -2530.4586 | 63.26% | 70.98% | 95% | 0% | 1688 | -91
[5 empty] | 2019-04-19 | 8 | 2595 | 1579 | -87 | 0 | 0 | 1666 | 489.2003 | 489.2003 | 489.2003 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -99.5423 | 389.658 | -2750 | -200 | -2560.342 | 64.01% | 70.98% | 95% | 0% | 1666 | -87
[5 empty] | 2019-04-19 | 9 | 2595.5 | 1565 | -87 | 0 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -99.5423 | 367.7289 | -2750 | -200 | -2582.2711 | 64.56% | 70.98% | 95% | 0% | 1652 | -87
[5 empty] | 2019-04-19 | 10 | 2596 | 1559 | -86 | 0 | 0 | 1645 | 456.3067 | 456.3067 | 456.3067 | 1828.4419 | 780 | 200 | 2808.4419 | 70.21% | 95% | 0% | -98.3982 | 357.9085 | -2750 | -200 | -2592.0915 | 64.8% | 70.98% | 95% | 0% | 1645 | -86
[5 empty] | 2019-04-19 | 11 | 2596.5 | 1598 | -85 | 0 | 0 | 1683 | 515.8285 | 515.8285 | 515.8285 | 1826.8755 | 780 | 200 | 2806.8755 | 70.17% | 95% | 0% | -97.254 | 418.5745 | -2750 | -200 | -2531.4255 | 63.29% | 70.98% | 95% | 0% | 1683 | -85
[5 empty] | 2019-04-19 | 12 | 2597 | 1632 | -85 | 0 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 1826.8755 | 780 | 200 | 2806.8755 | 70.17% | 95% | 0% | -97.254 | 471.8309 | -2750 | -200 | -2478.1691 | 61.95% | 70.98% | 95% | 0% | 1717 | -85
[5 empty] | 2019-04-19 | 13 | 2597.5 | 1699 | -88 | 0 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 1826.8755 | 780 | 200 | 2806.8755 | 70.17% | 95% | 0% | -100.6865 | 578.0439 | -2750 | -200 | -2371.9561 | 59.3% | 70.97% | 95% | 0% | 1787 | -88
[5 empty] | 2019-04-19 | 14 | 2598 | 1754 | -110 | 0 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 1826.8755 | 780 | 200 | 2806.8755 | 70.17% | 95% | 0% | -125.8581 | 673.4824 | -2750 | -200 | -2276.5176 | 56.91% | 70.96% | 95% | 0% | 1864 | -110
[5 empty] | 2019-04-19 | 15 | 2598.5 | 1819 | -149 | 1 | 0 | 1968 | 962.2424 | 962.2424 | 962.2424 | 1826.8755 | 780 | 200 | 2806.8755 | 70.17% | 95% | 0% | -170.4805 | 791.7618 | -3550 | -400 | -3158.2382 | 78.96% | 70.96% | 95% | 0% | 1968 | -149
[5 empty] | 2019-04-19 | 16 | 2599 | 1824 | -197 | 1 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 1825.3092 | 780 | 200 | 2805.3092 | 70.13% | 95% | 0% | -225.4005 | 819.8592 | -3550 | -400 | -3130.1408 | 78.25% | 70.94% | 95% | 0% | 2021 | -197
[5 empty] | 2019-04-19 | 17 | 2599.5 | 1789 | -255 | 1 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 1825.3092 | 780 | 200 | 2805.3092 | 70.13% | 95% | 0% | -291.762 | 789.5241 | -3550 | -400 | -3160.4759 | 79.01% | 70.94% | 95% | 0% | 2044 | -255
[5 empty] | 2019-04-19 | 18 | 2600 | 1713 | -319 | 1 | 0 | 2032 | 1062.4897 | 1062.4897 | 1062.4897 | 1825.3092 | 780 | 200 | 2805.3092 | 70.13% | 95% | 0% | -364.9886 | 697.5011 | -3550 | -400 | -3252.4989 | 81.31% | 70.94% | 95% | 0% | 2032 | -319
[5 empty] | 2019-04-19 | 19 | 2600.5 | 1615 | -385 | 1 | 0 | 2000 | 1012.366 | 1012.366 | 1012.366 | 1825.3092 | 780 | 200 | 2805.3092 | 70.13% | 95% | 0% | -440.5034 | 571.8626 | -3550 | -400 | -3378.1374 | 84.45% | 70.93% | 95% | 0% | 2000 | -385
[5 empty] | 2019-04-19 | 20 | 2601 | 1515 | -456 | 1 | 0 | 1971 | 966.9415 | 966.9415 | 966.9415 | 1825.3092 | 780 | 200 | 2805.3092 | 70.13% | 95% | 0% | -521.7391 | 445.2023 | -3550 | -400 | -3504.7977 | 87.62% | 70.92% | 95% | 0% | 1971 | -456
[5 empty] | 2019-04-19 | 21 | 2601.5 | 1447 | -522 | 1 | 0 | 1969 | 963.8087 | 963.8087 | 963.8087 | 1825.3092 | 780 | 200 | 2805.3092 | 70.13% | 95% | 0% | -597.254 | 366.5547 | -3550 | -400 | -3583.4453 | 89.59% | 70.91% | 95% | 0% | 1969 | -522
[5 empty] | 2019-04-19 | 22 | 2602 | 1333 | -617 | 1 | 0 | 1950 | 934.0478 | 934.0478 | 934.0478 | 1825.3092 | 780 | 200 | 2805.3092 | 70.13% | 95% | 0% | -705.9497 | 228.0982 | -3550 | -400 | -3721.9018 | 93.05% | 70.91% | 95% | 0% | 1950 | -617
[5 empty] | 2019-04-19 | 23 | 2602.5 | 1250 | -650 | 1 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 1825.3092 | 780 | 200 | 2805.3092 | 70.13% | 95% | 0% | -743.7071 | 112.0225 | -3550 | -400 | -3837.9775 | 95.95% | 70.91% | 95% | 0% | 1900 | -650
[5 empty] | 2019-04-19 | 24 | 2603 | 1170 | -688 | 1 | 0 | 1858 | 789.9423 | 789.9423 | 789.9423 | 1825.3092 | 780 | 200 | 2805.3092 | 70.13% | 95% | 0% | -787.1854 | 2.7569 | -3550 | -400 | -3947.2431 | 98.68% | 70.9% | 95% | 0% | 1858 | -688
[5 empty] | 2019-04-19 | 25 | 2603.5 | 1107 | -713 | 1 | 0 | 1820 | 730.4204 | 730.4204 | 730.4204 | 1825.3092 | 780 | 200 | 2805.3092 | 70.13% | 95% | 0% | -815.7895 | -85.369 | -3550 | -400 | -4035.369 | 100.9% | 70.9% | 95% | 0% | 1820 | -713
[5 empty] | 2019-04-19 | 26 | 2604 | 1050 | -734 | 1 | 0 | 1784 | 674.0313 | 674.0313 | 674.0313 | 1823.7428 | 780 | 200 | 2803.7428 | 70.09% | 95% | 0% | -839.8169 | -165.7856 | -3550 | -400 | -4115.7856 | 102.9% | 70.89% | 95% | 0% | 1784 | -734
[5 empty] | 2019-04-19 | 27 | 2604.5 | 978 | -746 | 1 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 1823.7428 | 780 | 200 | 2803.7428 | 70.09% | 95% | 0% | -853.5469 | -273.4974 | -3550 | -400 | -4223.4974 | 105.6% | 70.89% | 95% | 0% | 1724 | -746
[5 empty] | 2019-04-19 | 28 | 2605 | 924 | -756 | 1 | 0 | 1680 | 511.1294 | 511.1294 | 511.1294 | 1823.7428 | 780 | 200 | 2803.7428 | 70.09% | 95% | 0% | -864.9886 | -353.8591 | -3550 | -400 | -4303.8591 | 107.6% | 70.89% | 95% | 0% | 1680 | -756
[5 empty] | 2019-04-19 | 29 | 2605.5 | 955 | -732 | 1 | 0 | 1687 | 522.094 | 522.094 | 522.094 | 1823.7428 | 780 | 200 | 2803.7428 | 70.09% | 95% | 0% | -837.5286 | -315.4346 | -3550 | -400 | -4265.4346 | 106.6% | 70.88% | 95% | 0% | 1687 | -732
[5 empty] | 2019-04-19 | 30 | 2606 | 977 | -699 | 1 | 0 | 1676 | 504.864 | 504.864 | 504.864 | 1823.7428 | 780 | 200 | 2803.7428 | 70.09% | 95% | 0% | -799.7712 | -294.9072 | -3550 | -400 | -4244.9072 | 106.1% | 70.88% | 95% | 0% | 1676 | -699
[5 empty] | 2019-04-19 | 31 | 2606.5 | 1044 | -653 | 1 | 0 | 1697 | 537.7576 | 537.7576 | 537.7576 | 1823.7428 | 780 | 200 | 2803.7428 | 70.09% | 95% | 0% | -747.1396 | -209.382 | -3550 | -400 | -4159.382 | 104% | 70.87% | 95% | 0% | 1697 | -653
[5 empty] | 2019-04-19 | 32 | 2607 | 1146 | -590 | 1 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 1823.7428 | 780 | 200 | 2803.7428 | 70.09% | 95% | 0% | -675.0572 | -76.2114 | -3550 | -400 | -4026.2114 | 100.7% | 70.87% | 95% | 0% | 1736 | -590
[5 empty] | 2019-04-19 | 33 | 2607.5 | 1301 | -515 | 1 | 0 | 1816 | 724.155 | 724.155 | 724.155 | 1823.7428 | 780 | 200 | 2803.7428 | 70.09% | 95% | 0% | -589.2449 | 134.9101 | -3550 | -400 | -3815.0899 | 95.38% | 70.87% | 95% | 0% | 1816 | -515
[5 empty] | 2019-04-19 | 34 | 2608 | 1493 | -443 | 1 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 1822.1764 | 780 | 200 | 2802.1764 | 70.05% | 95% | 0% | -506.865 | 405.2537 | -3550 | -400 | -3544.7463 | 88.62% | 70.86% | 95% | 0% | 1936 | -443
[5 empty] | 2019-04-19 | 35 | 2608.5 | 1683 | -365 | 1 | 0 | 2048 | 1087.5515 | 1087.5515 | 1087.5515 | 1822.1764 | 780 | 200 | 2802.1764 | 70.05% | 95% | 0% | -417.6201 | 669.9314 | -3550 | -400 | -3280.0686 | 82% | 70.86% | 95% | 0% | 2048 | -365
[5 empty] | 2019-04-19 | 36 | 2609 | 1848 | -285 | 1 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 1822.1764 | 780 | 200 | 2802.1764 | 70.05% | 95% | 0% | -326.087 | 894.6055 | -3550 | -400 | -3055.3945 | 76.38% | 70.86% | 95% | 0% | 2133 | -285
[5 empty] | 2019-04-19 | 37 | 2609.5 | 1977 | -213 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1822.1764 | 780 | 200 | 2802.1764 | 70.05% | 95% | 0% | -243.7071 | 1066.2682 | -3550 | -400 | -2883.7318 | 72.09% | 70.84% | 95% | 0% | 2190 | -213
[5 empty] | 2019-04-19 | 38 | 2610 | 2086 | -148 | 1 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 1822.1764 | 780 | 200 | 2802.1764 | 70.05% | 95% | 0% | -169.3364 | 1209.5589 | -3550 | -400 | -2740.4411 | 68.51% | 70.84% | 95% | 0% | 2234 | -148
[5 empty] | 2019-04-19 | 39 | 2610.5 | 2149 | -100 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1822.1764 | 780 | 200 | 2802.1764 | 70.05% | 95% | 0% | -114.4165 | 1287.9743 | -3550 | -400 | -2662.0257 | 66.55% | 70.83% | 95% | 0% | 2249 | -100
[5 empty] | 2019-04-19 | 40 | 2611 | 2193 | -70 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 1822.1764 | 780 | 200 | 2802.1764 | 70.05% | 95% | 0% | -80.0915 | 1344.2283 | -3550 | -400 | -2605.7717 | 65.14% | 70.83% | 95% | 0% | 2263 | -70
[5 empty] | 2019-04-19 | 41 | 2611.5 | 2236 | -64 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 1822.1764 | 780 | 200 | 2802.1764 | 70.05% | 95% | 0% | -73.2265 | 1409.0488 | -3550 | -400 | -2540.9512 | 63.52% | 70.83% | 95% | 0% | 2300 | -64
[5 empty] | 2019-04-19 | 42 | 2612 | 2249 | -64 | 1 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 1820.6101 | 780 | 200 | 2800.6101 | 70.02% | 95% | 0% | -73.2265 | 1429.4115 | -3550 | -400 | -2520.5885 | 63.01% | 70.83% | 95% | 0% | 2313 | -64
[5 empty] | 2019-04-19 | 43 | 2612.5 | 2209 | -65 | 1 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 1820.6101 | 780 | 200 | 2800.6101 | 70.02% | 95% | 0% | -74.3707 | 1367.1792 | -3550 | -400 | -2582.8208 | 64.57% | 70.83% | 95% | 0% | 2274 | -65
[5 empty] | 2019-04-19 | 44 | 2613 | 2138 | -66 | 0 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 1820.6101 | 780 | 200 | 2800.6101 | 70.02% | 95% | 0% | -75.5149 | 1256.3895 | -2750 | -200 | -1693.6105 | 42.34% | 70.82% | 95% | 0% | 2204 | -66
[5 empty] | 2019-04-19 | 45 | 2613.5 | 2088 | -66 | 0 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 1820.6101 | 780 | 200 | 2800.6101 | 70.02% | 95% | 0% | -75.5149 | 1178.0713 | -2750 | -200 | -1771.9287 | 44.3% | 70.82% | 95% | 0% | 2154 | -66
[5 empty] | 2019-04-19 | 46 | 2614 | 1991 | -66 | 0 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 1820.6101 | 780 | 200 | 2800.6101 | 70.02% | 95% | 0% | -75.5149 | 1026.1339 | -2750 | -200 | -1923.8661 | 48.1% | 70.82% | 95% | 0% | 2057 | -66
[5 empty] | 2019-04-19 | 47 | 2614.5 | 1866 | -66 | 0 | 0 | 1932 | 905.8533 | 905.8533 | 905.8533 | 1820.6101 | 780 | 200 | 2800.6101 | 70.02% | 95% | 0% | -75.5149 | 830.3384 | -2750 | -200 | -2119.6616 | 52.99% | 70.82% | 95% | 0% | 1932 | -66
[5 empty] | 2019-04-19 | 48 | 2615 | 1756 | -67 | 0 | 0 | 1823 | 735.1195 | 735.1195 | 735.1195 | 1820.6101 | 780 | 200 | 2800.6101 | 70.02% | 95% | 0% | -76.659 | 658.4605 | -2750 | -200 | -2291.5395 | 57.29% | 70.82% | 95% | 0% | 1823 | -67
[5 empty] | 2019-04-20 | 1 | 2615.5 | 1688 | -66 | 0 | 0 | 1754 | 627.0404 | 627.0404 | 627.0404 | 1820.6101 | 780 | 200 | 2800.6101 | 70.02% | 95% | 0% | -75.5149 | 551.5255 | -2750 | -200 | -2398.4745 | 59.96% | 70.81% | 95% | 0% | 1754 | -66
[5 empty] | 2019-04-20 | 2 | 2616 | 1646 | -65 | 0 | 0 | 1711 | 559.6867 | 559.6867 | 559.6867 | 1820.6101 | 780 | 200 | 2800.6101 | 70.02% | 95% | 0% | -74.3707 | 485.316 | -2750 | -200 | -2464.684 | 61.62% | 70.81% | 95% | 0% | 1711 | -65
[5 empty] | 2019-04-20 | 3 | 2616.5 | 1625 | -64 | 0 | 0 | 1689 | 525.2267 | 525.2267 | 525.2267 | 1820.6101 | 780 | 200 | 2800.6101 | 70.02% | 95% | 0% | -73.2265 | 452.0002 | -2750 | -200 | -2497.9998 | 62.45% | 70.81% | 95% | 0% | 1689 | -64
[5 empty] | 2019-04-20 | 4 | 2617 | 1631 | -63 | 1 | 0 | 1694 | 533.0585 | 533.0585 | 533.0585 | 1819.0437 | 780 | 200 | 2799.0437 | 69.98% | 95% | 0% | -72.0824 | 460.9762 | -3550 | -400 | -3489.0238 | 87.23% | 70.81% | 95% | 0% | 1694 | -63
[5 empty] | 2019-04-20 | 5 | 2617.5 | 1611 | -62 | 1 | 0 | 1673 | 500.1649 | 500.1649 | 500.1649 | 1819.0437 | 780 | 200 | 2799.0437 | 69.98% | 95% | 0% | -70.9382 | 429.2267 | -3550 | -400 | -3520.7733 | 88.02% | 70.8% | 95% | 0% | 1673 | -62
[5 empty] | 2019-04-20 | 6 | 2618 | 1583 | -61 | 1 | 0 | 1644 | 454.7403 | 454.7403 | 454.7403 | 1819.0437 | 780 | 200 | 2799.0437 | 69.98% | 95% | 0% | -69.7941 | 384.9463 | -3550 | -400 | -3565.0537 | 89.13% | 70.8% | 95% | 0% | 1644 | -61
[5 empty] | 2019-04-20 | 7 | 2618.5 | 1559 | -59 | 1 | 0 | 1618 | 414.0148 | 414.0148 | 414.0148 | 1819.0437 | 780 | 200 | 2799.0437 | 69.98% | 95% | 0% | -67.5057 | 346.5091 | -3550 | -400 | -3603.4909 | 90.09% | 70.79% | 95% | 0% | 1618 | -59
[5 empty] | 2019-04-20 | 8 | 2619 | 1550 | -57 | 1 | 0 | 1607 | 396.7848 | 396.7848 | 396.7848 | 1819.0437 | 780 | 200 | 2799.0437 | 69.98% | 95% | 0% | -65.2174 | 331.5674 | -3550 | -400 | -3618.4326 | 90.46% | 70.79% | 95% | 0% | 1607 | -57
[5 empty] | 2019-04-20 | 9 | 2619.5 | 1530 | -57 | 1 | 0 | 1587 | 365.4575 | 365.4575 | 365.4575 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -65.2174 | 300.2402 | -3550 | -400 | -3649.7598 | 91.24% | 70.79% | 95% | 0% | 1587 | -57
[5 empty] | 2019-04-20 | 10 | 2620 | 1517 | -58 | 1 | 0 | 1575 | 346.6612 | 346.6612 | 346.6612 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -66.3616 | 280.2996 | -3550 | -400 | -3669.7004 | 91.74% | 70.78% | 95% | 0% | 1575 | -58
[5 empty] | 2019-04-20 | 11 | 2620.5 | 1552 | -57 | 1 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -65.2174 | 334.7002 | -3550 | -400 | -3615.2998 | 90.38% | 70.77% | 95% | 0% | 1609 | -57
[5 empty] | 2019-04-20 | 12 | 2621 | 1572 | -55 | 1 | 0 | 1627 | 428.1121 | 428.1121 | 428.1121 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -62.9291 | 365.1831 | -3550 | -400 | -3584.8169 | 89.62% | 70.77% | 95% | 0% | 1627 | -55
[5 empty] | 2019-04-20 | 13 | 2621.5 | 1624 | -60 | 1 | 0 | 1684 | 517.3949 | 517.3949 | 517.3949 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -68.6499 | 448.745 | -3550 | -400 | -3501.255 | 87.53% | 70.77% | 95% | 0% | 1684 | -60
[5 empty] | 2019-04-20 | 14 | 2622 | 1648 | -87 | 1 | 0 | 1735 | 597.2795 | 597.2795 | 597.2795 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -99.5423 | 497.7371 | -3550 | -400 | -3452.2629 | 86.31% | 70.76% | 95% | 0% | 1735 | -87
[5 empty] | 2019-04-20 | 15 | 2622.5 | 1722 | -125 | 1 | 0 | 1847 | 772.7123 | 772.7123 | 772.7123 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -143.0206 | 629.6917 | -3550 | -400 | -3320.3083 | 83.01% | 70.76% | 95% | 0% | 1847 | -125
[5 empty] | 2019-04-20 | 16 | 2623 | 1725 | -172 | 1 | 0 | 1897 | 851.0305 | 851.0305 | 851.0305 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -196.7963 | 654.2342 | -3550 | -400 | -3295.7658 | 82.39% | 70.76% | 95% | 0% | 1897 | -172
[5 empty] | 2019-04-20 | 17 | 2623.5 | 1719 | -230 | 1 | 0 | 1949 | 932.4815 | 932.4815 | 932.4815 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -263.1579 | 669.3236 | -3550 | -400 | -3280.6764 | 82.02% | 70.75% | 95% | 0% | 1949 | -230
[5 empty] | 2019-04-20 | 18 | 2624 | 1657 | -297 | 1 | 0 | 1954 | 940.3133 | 940.3133 | 940.3133 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -339.8169 | 600.4963 | -3550 | -400 | -3349.5037 | 83.74% | 70.75% | 95% | 0% | 1954 | -297
[5 empty] | 2019-04-20 | 19 | 2624.5 | 1592 | -364 | 1 | 0 | 1956 | 943.446 | 943.446 | 943.446 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -416.476 | 526.97 | -3550 | -400 | -3423.03 | 85.58% | 70.74% | 95% | 0% | 1956 | -364
[5 empty] | 2019-04-20 | 20 | 2625 | 1505 | -431 | 1 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -493.135 | 418.9837 | -3550 | -400 | -3531.0163 | 88.28% | 70.74% | 95% | 0% | 1936 | -431
[5 empty] | 2019-04-20 | 21 | 2625.5 | 1379 | -496 | 1 | 0 | 1875 | 816.5705 | 816.5705 | 816.5705 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -567.5057 | 249.0648 | -3550 | -400 | -3700.9352 | 92.52% | 70.73% | 95% | 0% | 1875 | -496
[5 empty] | 2019-04-20 | 22 | 2626 | 1216 | -609 | 1 | 0 | 1825 | 738.2523 | 738.2523 | 738.2523 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -696.7963 | 41.4559 | -3550 | -400 | -3908.5441 | 97.71% | 70.73% | 95% | 0% | 1825 | -609
[5 empty] | 2019-04-20 | 23 | 2626.5 | 1126 | -658 | 1 | 0 | 1784 | 674.0313 | 674.0313 | 674.0313 | 1817.4773 | 780 | 200 | 2797.4773 | 69.94% | 95% | 0% | -752.8604 | -78.8291 | -3550 | -400 | -4028.8291 | 100.7% | 70.73% | 95% | 0% | 1784 | -658
[5 empty] | 2019-04-20 | 24 | 2627 | 1051 | -696 | 1 | 0 | 1747 | 616.0758 | 616.0758 | 616.0758 | 1815.911 | 780 | 200 | 2795.911 | 69.9% | 95% | 0% | -796.3387 | -180.2628 | -3550 | -400 | -4130.2628 | 103.3% | 70.72% | 95% | 0% | 1747 | -696
[5 empty] | 2019-04-20 | 25 | 2627.5 | 993 | -721 | 1 | 0 | 1714 | 564.3858 | 564.3858 | 564.3858 | 1815.911 | 780 | 200 | 2795.911 | 69.9% | 95% | 0% | -824.9428 | -260.557 | -3550 | -400 | -4210.557 | 105.3% | 70.72% | 95% | 0% | 1714 | -721
[5 empty] | 2019-04-20 | 26 | 2628 | 950 | -730 | 1 | 0 | 1680 | 511.1294 | 511.1294 | 511.1294 | 1815.911 | 780 | 200 | 2795.911 | 69.9% | 95% | 0% | -835.2403 | -324.1108 | -3550 | -400 | -4274.1108 | 106.9% | 70.71% | 95% | 0% | 1680 | -730
[5 empty] | 2019-04-20 | 27 | 2628.5 | 904 | -731 | 1 | 0 | 1635 | 440.643 | 440.643 | 440.643 | 1815.911 | 780 | 200 | 2795.911 | 69.9% | 95% | 0% | -836.3844 | -395.7414 | -3550 | -400 | -4345.7414 | 108.6% | 70.71% | 95% | 0% | 1635 | -731
[5 empty] | 2019-04-20 | 28 | 2629 | 886 | -720 | 1 | 0 | 1606 | 395.2185 | 395.2185 | 395.2185 | 1815.911 | 780 | 200 | 2795.911 | 69.9% | 95% | 0% | -823.7986 | -428.5802 | -3550 | -400 | -4378.5802 | 109.5% | 70.71% | 95% | 0% | 1606 | -720
[5 empty] | 2019-04-20 | 29 | 2629.5 | 895 | -697 | 1 | 0 | 1592 | 373.2894 | 373.2894 | 373.2894 | 1815.911 | 780 | 200 | 2795.911 | 69.9% | 95% | 0% | -797.4828 | -424.1935 | -3550 | -400 | -4374.1935 | 109.4% | 70.71% | 95% | 0% | 1592 | -697
[5 empty] | 2019-04-20 | 30 | 2630 | 935 | -661 | 1 | 0 | 1596 | 379.5548 | 379.5548 | 379.5548 | 1815.911 | 780 | 200 | 2795.911 | 69.9% | 95% | 0% | -756.2929 | -376.7381 | -3550 | -400 | -4326.7381 | 108.2% | 70.7% | 95% | 0% | 1596 | -661
[5 empty] | 2019-04-20 | 31 | 2630.5 | 1005 | -612 | 1 | 0 | 1617 | 412.4485 | 412.4485 | 412.4485 | 1815.911 | 780 | 200 | 2795.911 | 69.9% | 95% | 0% | -700.2288 | -287.7804 | -3550 | -400 | -4237.7804 | 105.9% | 70.7% | 95% | 0% | 1617 | -612
[5 empty] | 2019-04-20 | 32 | 2631 | 1089 | -555 | 1 | 0 | 1644 | 454.7403 | 454.7403 | 454.7403 | 1815.911 | 780 | 200 | 2795.911 | 69.9% | 95% | 0% | -635.0114 | -180.2711 | -3550 | -400 | -4130.2711 | 103.3% | 70.69% | 95% | 0% | 1644 | -555
[5 empty] | 2019-04-20 | 33 | 2631.5 | 1226 | -490 | 1 | 0 | 1716 | 567.5185 | 567.5185 | 567.5185 | 1815.911 | 780 | 200 | 2795.911 | 69.9% | 95% | 0% | -560.6407 | 6.8778 | -3550 | -400 | -3943.1222 | 98.58% | 70.69% | 95% | 0% | 1716 | -490
[5 empty] | 2019-04-20 | 34 | 2632 | 1394 | -418 | 1 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 1815.911 | 780 | 200 | 2795.911 | 69.9% | 95% | 0% | -478.2609 | 239.6287 | -3550 | -400 | -3710.3713 | 92.76% | 70.69% | 95% | 0% | 1812 | -418
[5 empty] | 2019-04-20 | 35 | 2632.5 | 1592 | -342 | 1 | 0 | 1934 | 908.986 | 908.986 | 908.986 | 1815.911 | 780 | 200 | 2795.911 | 69.9% | 95% | 0% | -391.3043 | 517.6816 | -3550 | -400 | -3432.3184 | 85.81% | 70.69% | 95% | 0% | 1934 | -342
[5 empty] | 2019-04-20 | 36 | 2633 | 1740 | -269 | 1 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 1814.3446 | 780 | 200 | 2794.3446 | 69.86% | 95% | 0% | -307.7803 | 718.683 | -3550 | -400 | -3231.317 | 80.78% | 70.68% | 95% | 0% | 2009 | -269
[5 empty] | 2019-04-20 | 37 | 2633.5 | 1858 | -199 | 1 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 1814.3446 | 780 | 200 | 2794.3446 | 69.86% | 95% | 0% | -227.6888 | 873.96 | -3550 | -400 | -3076.04 | 76.9% | 70.67% | 95% | 0% | 2057 | -199
[5 empty] | 2019-04-20 | 38 | 2634 | 1975 | -136 | 1 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 1814.3446 | 780 | 200 | 2794.3446 | 69.86% | 95% | 0% | -155.6064 | 1030.6261 | -3550 | -400 | -2919.3739 | 72.98% | 70.66% | 95% | 0% | 2111 | -136
[5 empty] | 2019-04-20 | 39 | 2634.5 | 2060 | -81 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1814.3446 | 780 | 200 | 2794.3446 | 69.86% | 95% | 0% | -92.6773 | 1140.5461 | -3550 | -400 | -2809.4539 | 70.24% | 70.66% | 95% | 0% | 2141 | -81
[5 empty] | 2019-04-20 | 40 | 2635 | 2100 | -46 | 1 | 0 | 2146 | 1241.0552 | 1241.0552 | 1241.0552 | 1814.3446 | 780 | 200 | 2794.3446 | 69.86% | 95% | 0% | -52.6316 | 1188.4237 | -3550 | -400 | -2761.5763 | 69.04% | 70.65% | 95% | 0% | 2146 | -46
[5 empty] | 2019-04-20 | 41 | 2635.5 | 2144 | -38 | 1 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 1814.3446 | 780 | 200 | 2794.3446 | 69.86% | 95% | 0% | -43.4783 | 1253.9661 | -3550 | -400 | -2696.0339 | 67.4% | 70.65% | 95% | 0% | 2182 | -38
[5 empty] | 2019-04-20 | 42 | 2636 | 2175 | -38 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 1814.3446 | 780 | 200 | 2794.3446 | 69.86% | 95% | 0% | -43.4783 | 1302.5234 | -3550 | -400 | -2647.4766 | 66.19% | 70.65% | 95% | 0% | 2213 | -38
[5 empty] | 2019-04-20 | 43 | 2636.5 | 2146 | -37 | 1 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 1814.3446 | 780 | 200 | 2794.3446 | 69.86% | 95% | 0% | -42.3341 | 1256.6766 | -3550 | -400 | -2693.3234 | 67.33% | 70.64% | 95% | 0% | 2183 | -37
[5 empty] | 2019-04-20 | 44 | 2637 | 2105 | -37 | 0 | 0 | 2142 | 1234.7898 | 1234.7898 | 1234.7898 | 1814.3446 | 780 | 200 | 2794.3446 | 69.86% | 95% | 0% | -42.3341 | 1192.4557 | -2750 | -200 | -1757.5443 | 43.94% | 70.64% | 95% | 0% | 2142 | -37
[5 empty] | 2019-04-20 | 45 | 2637.5 | 2035 | -37 | 0 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 1814.3446 | 780 | 200 | 2794.3446 | 69.86% | 95% | 0% | -42.3341 | 1082.8102 | -2750 | -200 | -1867.1898 | 46.68% | 70.64% | 95% | 0% | 2072 | -37
[5 empty] | 2019-04-20 | 46 | 2638 | 1955 | -36 | 0 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1814.3446 | 780 | 200 | 2794.3446 | 69.86% | 95% | 0% | -41.1899 | 957.0788 | -2750 | -200 | -1992.9212 | 49.82% | 70.64% | 95% | 0% | 1991 | -36
[5 empty] | 2019-04-20 | 47 | 2638.5 | 1831 | -36 | 0 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 1814.3446 | 780 | 200 | 2794.3446 | 69.86% | 95% | 0% | -41.1899 | 762.8496 | -2750 | -200 | -2187.1504 | 54.68% | 70.63% | 95% | 0% | 1867 | -36
[5 empty] | 2019-04-20 | 48 | 2639 | 1726 | -36 | 0 | 0 | 1762 | 639.5713 | 639.5713 | 639.5713 | 1812.7782 | 780 | 200 | 2792.7782 | 69.82% | 95% | 0% | -41.1899 | 598.3814 | -2750 | -200 | -2351.6186 | 58.79% | 70.63% | 95% | 0% | 1762 | -36
[5 empty] | 2019-04-21 | 1 | 2639.5 | 1642 | -38 | 0 | 0 | 1680 | 511.1294 | 511.1294 | 511.1294 | 1812.7782 | 780 | 200 | 2792.7782 | 69.82% | 95% | 0% | -43.4783 | 467.6512 | -2750 | -200 | -2482.3488 | 62.06% | 70.63% | 95% | 0% | 1680 | -38
[5 empty] | 2019-04-21 | 2 | 2640 | 1592 | -40 | 0 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 1812.7782 | 780 | 200 | 2792.7782 | 69.82% | 95% | 0% | -45.7666 | 390.1774 | -2750 | -200 | -2559.8226 | 64% | 70.63% | 95% | 0% | 1632 | -40
[5 empty] | 2019-04-21 | 3 | 2640.5 | 1572 | -41 | 0 | 0 | 1613 | 406.183 | 406.183 | 406.183 | 1812.7782 | 780 | 200 | 2792.7782 | 69.82% | 95% | 0% | -46.9108 | 359.2723 | -2750 | -200 | -2590.7277 | 64.77% | 70.63% | 95% | 0% | 1613 | -41
[5 empty] | 2019-04-21 | 4 | 2641 | 1568 | -42 | 0 | 0 | 1610 | 401.4839 | 401.4839 | 401.4839 | 1812.7782 | 780 | 200 | 2792.7782 | 69.82% | 95% | 0% | -48.0549 | 353.429 | -2750 | -200 | -2596.571 | 64.91% | 70.62% | 95% | 0% | 1610 | -42
[5 empty] | 2019-04-21 | 5 | 2641.5 | 1543 | -43 | 0 | 0 | 1586 | 363.8912 | 363.8912 | 363.8912 | 1812.7782 | 780 | 200 | 2792.7782 | 69.82% | 95% | 0% | -49.1991 | 314.6921 | -2750 | -200 | -2635.3079 | 65.88% | 70.62% | 95% | 0% | 1586 | -43
[5 empty] | 2019-04-21 | 6 | 2642 | 1505 | -44 | 0 | 0 | 1549 | 305.9357 | 305.9357 | 305.9357 | 1812.7782 | 780 | 200 | 2792.7782 | 69.82% | 95% | 0% | -50.3432 | 255.5924 | -2750 | -200 | -2694.4076 | 67.36% | 70.62% | 95% | 0% | 1549 | -44
[5 empty] | 2019-04-21 | 7 | 2642.5 | 1478 | -45 | 0 | 0 | 1523 | 265.2102 | 265.2102 | 265.2102 | 1812.7782 | 780 | 200 | 2792.7782 | 69.82% | 95% | 0% | -51.4874 | 213.7228 | -2750 | -200 | -2736.2772 | 68.41% | 70.62% | 95% | 0% | 1523 | -45
[5 empty] | 2019-04-21 | 8 | 2643 | 1461 | -46 | 0 | 0 | 1507 | 240.1484 | 240.1484 | 240.1484 | 1812.7782 | 780 | 200 | 2792.7782 | 69.82% | 95% | 0% | -52.6316 | 187.5168 | -2750 | -200 | -2762.4832 | 69.06% | 70.61% | 95% | 0% | 1507 | -46
[5 empty] | 2019-04-21 | 9 | 2643.5 | 1450 | -49 | 0 | 0 | 1499 | 227.6175 | 227.6175 | 227.6175 | 1812.7782 | 780 | 200 | 2792.7782 | 69.82% | 95% | 0% | -56.0641 | 171.5534 | -2750 | -200 | -2778.4466 | 69.46% | 70.61% | 95% | 0% | 1499 | -49
[5 empty] | 2019-04-21 | 10 | 2644 | 1440 | -51 | 0 | 0 | 1491 | 215.0866 | 215.0866 | 215.0866 | 1811.2119 | 780 | 200 | 2791.2119 | 69.78% | 95% | 0% | -58.3524 | 156.7342 | -2750 | -200 | -2793.2658 | 69.83% | 70.61% | 95% | 0% | 1491 | -51
[5 empty] | 2019-04-21 | 11 | 2644.5 | 1450 | -51 | 0 | 0 | 1501 | 230.7502 | 230.7502 | 230.7502 | 1811.2119 | 780 | 200 | 2791.2119 | 69.78% | 95% | 0% | -58.3524 | 172.3978 | -2750 | -200 | -2777.6022 | 69.44% | 70.6% | 95% | 0% | 1501 | -51
[5 empty] | 2019-04-21 | 12 | 2645 | 1443 | -52 | 0 | 0 | 1495 | 221.352 | 221.352 | 221.352 | 1811.2119 | 780 | 200 | 2791.2119 | 69.78% | 95% | 0% | -59.4966 | 161.8555 | -2750 | -200 | -2788.1445 | 69.7% | 70.6% | 95% | 0% | 1495 | -52
[5 empty] | 2019-04-21 | 13 | 2645.5 | 1469 | -58 | 0 | 0 | 1527 | 271.4757 | 271.4757 | 271.4757 | 1811.2119 | 780 | 200 | 2791.2119 | 69.78% | 95% | 0% | -66.3616 | 205.1141 | -2750 | -200 | -2744.8859 | 68.62% | 70.6% | 95% | 0% | 1527 | -58
[5 empty] | 2019-04-21 | 14 | 2646 | 1464 | -89 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 1811.2119 | 780 | 200 | 2791.2119 | 69.78% | 95% | 0% | -101.8307 | 210.3705 | -2750 | -200 | -2739.6295 | 68.49% | 70.59% | 95% | 0% | 1553 | -89
[5 empty] | 2019-04-21 | 15 | 2646.5 | 1478 | -133 | 1 | 0 | 1611 | 403.0503 | 403.0503 | 403.0503 | 1811.2119 | 780 | 200 | 2791.2119 | 69.78% | 95% | 0% | -152.1739 | 250.8764 | -3550 | -400 | -3699.1236 | 92.48% | 70.58% | 95% | 0% | 1611 | -133
[5 empty] | 2019-04-21 | 16 | 2647 | 1468 | -186 | 1 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 1809.6455 | 780 | 200 | 2789.6455 | 69.74% | 95% | 0% | -212.8146 | 257.5893 | -3550 | -400 | -3692.4107 | 92.31% | 70.57% | 95% | 0% | 1654 | -186
[5 empty] | 2019-04-21 | 17 | 2647.5 | 1434 | -250 | 1 | 0 | 1684 | 517.3949 | 517.3949 | 517.3949 | 1809.6455 | 780 | 200 | 2789.6455 | 69.74% | 95% | 0% | -286.0412 | 231.3537 | -3550 | -400 | -3718.6463 | 92.97% | 70.57% | 95% | 0% | 1684 | -250
[5 empty] | 2019-04-21 | 18 | 2648 | 1358 | -318 | 1 | 0 | 1676 | 504.864 | 504.864 | 504.864 | 1809.6455 | 780 | 200 | 2789.6455 | 69.74% | 95% | 0% | -363.8444 | 141.0196 | -3550 | -400 | -3808.9804 | 95.22% | 70.57% | 95% | 0% | 1676 | -318
[5 empty] | 2019-04-21 | 19 | 2648.5 | 1300 | -386 | 1 | 0 | 1686 | 520.5276 | 520.5276 | 520.5276 | 1809.6455 | 780 | 200 | 2789.6455 | 69.74% | 95% | 0% | -441.6476 | 78.88 | -3550 | -400 | -3871.12 | 96.78% | 70.56% | 95% | 0% | 1686 | -386
[5 empty] | 2019-04-21 | 20 | 2649 | 1213 | -457 | 1 | 0 | 1670 | 495.4658 | 495.4658 | 495.4658 | 1809.6455 | 780 | 200 | 2789.6455 | 69.74% | 95% | 0% | -522.8833 | -27.4175 | -3550 | -400 | -3977.4175 | 99.44% | 70.56% | 95% | 0% | 1670 | -457
[5 empty] | 2019-04-21 | 21 | 2649.5 | 1140 | -528 | 1 | 0 | 1668 | 492.3331 | 492.3331 | 492.3331 | 1809.6455 | 780 | 200 | 2789.6455 | 69.74% | 95% | 0% | -604.119 | -111.7859 | -3550 | -400 | -4061.7859 | 101.5% | 70.56% | 95% | 0% | 1668 | -528
[5 empty] | 2019-04-21 | 22 | 2650 | 1014 | -640 | 1 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 1809.6455 | 780 | 200 | 2789.6455 | 69.74% | 95% | 0% | -732.2654 | -261.8615 | -3550 | -400 | -4211.8615 | 105.3% | 70.56% | 95% | 0% | 1654 | -640
[5 empty] | 2019-04-21 | 23 | 2650.5 | 926 | -694 | 1 | 0 | 1620 | 417.1476 | 417.1476 | 417.1476 | 1809.6455 | 780 | 200 | 2789.6455 | 69.74% | 95% | 0% | -794.0503 | -376.9028 | -3550 | -400 | -4326.9028 | 108.2% | 70.56% | 95% | 0% | 1620 | -694
[5 empty] | 2019-04-21 | 24 | 2651 | 864 | -737 | 1 | 0 | 1601 | 387.3866 | 387.3866 | 387.3866 | 1809.6455 | 780 | 200 | 2789.6455 | 69.74% | 95% | 0% | -843.2494 | -455.8628 | -3550 | -400 | -4405.8628 | 110.1% | 70.55% | 95% | 0% | 1601 | -737
[5 empty] | 2019-04-21 | 25 | 2651.5 | 817 | -768 | 1 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 1808.0791 | 780 | 200 | 2788.0791 | 69.7% | 95% | 0% | -878.7185 | -516.3937 | -3550 | -400 | -4466.3937 | 111.7% | 70.55% | 95% | 0% | 1585 | -768
[5 empty] | 2019-04-21 | 26 | 2652 | 763 | -788 | 1 | 0 | 1551 | 309.0684 | 309.0684 | 309.0684 | 1808.0791 | 780 | 200 | 2788.0791 | 69.7% | 95% | 0% | -901.6018 | -592.5334 | -3550 | -400 | -4542.5334 | 113.6% | 70.54% | 95% | 0% | 1551 | -788
[5 empty] | 2019-04-21 | 27 | 2652.5 | 700 | -795 | 1 | 0 | 1495 | 221.352 | 221.352 | 221.352 | 1808.0791 | 780 | 200 | 2788.0791 | 69.7% | 95% | 0% | -909.611 | -688.259 | -3550 | -400 | -4638.259 | 116% | 70.54% | 95% | 0% | 1495 | -795
[5 empty] | 2019-04-21 | 28 | 2653 | 669 | -786 | 1 | 0 | 1455 | 158.6974 | 158.6974 | 158.6974 | 1808.0791 | 780 | 200 | 2788.0791 | 69.7% | 95% | 0% | -899.3135 | -740.6161 | -3550 | -400 | -4690.6161 | 117.3% | 70.53% | 95% | 0% | 1455 | -786
[5 empty] | 2019-04-21 | 29 | 2653.5 | 660 | -767 | 1 | 0 | 1427 | 114.8392 | 114.8392 | 114.8392 | 1808.0791 | 780 | 200 | 2788.0791 | 69.7% | 95% | 0% | -877.5744 | -762.7351 | -3550 | -400 | -4712.7351 | 117.8% | 70.53% | 95% | 0% | 1427 | -767
[5 empty] | 2019-04-21 | 30 | 2654 | 679 | -736 | 1 | 0 | 1415 | 96.0429 | 96.0429 | 96.0429 | 1808.0791 | 780 | 200 | 2788.0791 | 69.7% | 95% | 0% | -842.1053 | -746.0624 | -3550 | -400 | -4696.0624 | 117.4% | 70.53% | 95% | 0% | 1415 | -736
[5 empty] | 2019-04-21 | 31 | 2654.5 | 734 | -691 | 1 | 0 | 1425 | 111.7065 | 111.7065 | 111.7065 | 1808.0791 | 780 | 200 | 2788.0791 | 69.7% | 95% | 0% | -790.6178 | -678.9113 | -3550 | -400 | -4628.9113 | 115.7% | 70.53% | 95% | 0% | 1425 | -691
[5 empty] | 2019-04-21 | 32 | 2655 | 833 | -634 | 1 | 0 | 1467 | 177.4938 | 177.4938 | 177.4938 | 1808.0791 | 780 | 200 | 2788.0791 | 69.7% | 95% | 0% | -725.4005 | -547.9066 | -3550 | -400 | -4497.9066 | 112.4% | 70.52% | 95% | 0% | 1467 | -634
[5 empty] | 2019-04-21 | 33 | 2655.5 | 965 | -564 | 1 | 0 | 1529 | 274.6084 | 274.6084 | 274.6084 | 1808.0791 | 780 | 200 | 2788.0791 | 69.7% | 95% | 0% | -645.3089 | -370.7005 | -3550 | -400 | -4320.7005 | 108% | 70.52% | 95% | 0% | 1529 | -564
[5 empty] | 2019-04-21 | 34 | 2656 | 1129 | -491 | 1 | 0 | 1620 | 417.1476 | 417.1476 | 417.1476 | 1808.0791 | 780 | 200 | 2788.0791 | 69.7% | 95% | 0% | -561.7849 | -144.6373 | -3550 | -400 | -4094.6373 | 102.4% | 70.51% | 95% | 0% | 1620 | -491
[5 empty] | 2019-04-21 | 35 | 2656.5 | 1302 | -412 | 1 | 0 | 1714 | 564.3858 | 564.3858 | 564.3858 | 1808.0791 | 780 | 200 | 2788.0791 | 69.7% | 95% | 0% | -471.3959 | 92.9899 | -3550 | -400 | -3857.0101 | 96.43% | 70.51% | 95% | 0% | 1714 | -412
[5 empty] | 2019-04-21 | 36 | 2657 | 1435 | -334 | 1 | 0 | 1769 | 650.5359 | 650.5359 | 650.5359 | 1806.5128 | 780 | 200 | 2786.5128 | 69.66% | 95% | 0% | -382.151 | 268.3848 | -3550 | -400 | -3681.6152 | 92.04% | 70.5% | 95% | 0% | 1769 | -334
[5 empty] | 2019-04-21 | 37 | 2657.5 | 1591 | -262 | 1 | 0 | 1853 | 782.1105 | 782.1105 | 782.1105 | 1806.5128 | 780 | 200 | 2786.5128 | 69.66% | 95% | 0% | -299.7712 | 482.3393 | -3550 | -400 | -3467.6607 | 86.69% | 70.5% | 95% | 0% | 1853 | -262
[5 empty] | 2019-04-21 | 38 | 2658 | 1727 | -197 | 1 | 0 | 1924 | 893.3223 | 893.3223 | 893.3223 | 1806.5128 | 780 | 200 | 2786.5128 | 69.66% | 95% | 0% | -225.4005 | 667.9219 | -3550 | -400 | -3282.0781 | 82.05% | 70.5% | 95% | 0% | 1924 | -197
[5 empty] | 2019-04-21 | 39 | 2658.5 | 1833 | -142 | 1 | 0 | 1975 | 973.2069 | 973.2069 | 973.2069 | 1806.5128 | 780 | 200 | 2786.5128 | 69.66% | 95% | 0% | -162.4714 | 810.7355 | -3550 | -400 | -3139.2645 | 78.48% | 70.49% | 95% | 0% | 1975 | -142
[5 empty] | 2019-04-21 | 40 | 2659 | 1885 | -104 | 1 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 1806.5128 | 780 | 200 | 2786.5128 | 69.66% | 95% | 0% | -118.9931 | 876.1429 | -3550 | -400 | -3073.8571 | 76.85% | 70.49% | 95% | 0% | 1989 | -104
[5 empty] | 2019-04-21 | 41 | 2659.5 | 1940 | -92 | 1 | 0 | 2032 | 1062.4897 | 1062.4897 | 1062.4897 | 1806.5128 | 780 | 200 | 2786.5128 | 69.66% | 95% | 0% | -105.2632 | 957.2265 | -3550 | -400 | -2992.7735 | 74.82% | 70.49% | 95% | 0% | 2032 | -92
[5 empty] | 2019-04-21 | 42 | 2660 | 1982 | -93 | 1 | 0 | 2075 | 1129.8434 | 1129.8434 | 1129.8434 | 1806.5128 | 780 | 200 | 2786.5128 | 69.66% | 95% | 0% | -106.4073 | 1023.436 | -3550 | -400 | -2926.564 | 73.16% | 70.49% | 95% | 0% | 2075 | -93
[5 empty] | 2019-04-21 | 43 | 2660.5 | 1974 | -93 | 0 | 0 | 2067 | 1117.3124 | 1117.3124 | 1117.3124 | 1806.5128 | 780 | 200 | 2786.5128 | 69.66% | 95% | 0% | -106.4073 | 1010.9051 | -2750 | -200 | -1939.0949 | 48.48% | 70.48% | 95% | 0% | 2067 | -93
[5 empty] | 2019-04-21 | 44 | 2661 | 1920 | -93 | 0 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 1806.5128 | 780 | 200 | 2786.5128 | 69.66% | 95% | 0% | -106.4073 | 926.3214 | -2750 | -200 | -2023.6786 | 50.59% | 70.48% | 95% | 0% | 2013 | -93
[5 empty] | 2019-04-21 | 45 | 2661.5 | 1862 | -93 | 0 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 1806.5128 | 780 | 200 | 2786.5128 | 69.66% | 95% | 0% | -106.4073 | 835.4723 | -2750 | -200 | -2114.5277 | 52.86% | 70.48% | 95% | 0% | 1955 | -93
[5 empty] | 2019-04-21 | 46 | 2662 | 1761 | -93 | 0 | 0 | 1854 | 783.6768 | 783.6768 | 783.6768 | 1806.5128 | 780 | 200 | 2786.5128 | 69.66% | 95% | 0% | -106.4073 | 677.2695 | -2750 | -200 | -2272.7305 | 56.82% | 70.48% | 95% | 0% | 1854 | -93
[5 empty] | 2019-04-21 | 47 | 2662.5 | 1652 | -94 | 0 | 0 | 1746 | 614.5095 | 614.5095 | 614.5095 | 1806.5128 | 780 | 200 | 2786.5128 | 69.66% | 95% | 0% | -107.5515 | 506.958 | -2750 | -200 | -2443.042 | 61.08% | 70.48% | 95% | 0% | 1746 | -94
[5 empty] | 2019-04-21 | 48 | 2663 | 1555 | -94 | 0 | 0 | 1649 | 462.5721 | 462.5721 | 462.5721 | 1804.9464 | 780 | 200 | 2784.9464 | 69.62% | 95% | 0% | -107.5515 | 355.0206 | -2750 | -200 | -2594.9794 | 64.87% | 70.47% | 95% | 0% | 1649 | -94
[5 empty] | 2019-04-22 | 1 | 2663.5 | 1481 | -92 | 0 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 1804.9464 | 780 | 200 | 2784.9464 | 69.62% | 95% | 0% | -105.2632 | 238.2653 | -2750 | -200 | -2711.7347 | 67.79% | 70.46% | 95% | 0% | 1573 | -92
[5 empty] | 2019-04-22 | 2 | 2664 | 1443 | -90 | 0 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 1804.9464 | 780 | 200 | 2784.9464 | 69.62% | 95% | 0% | -102.9748 | 177.899 | -2750 | -200 | -2772.101 | 69.3% | 70.46% | 95% | 0% | 1533 | -90
[5 empty] | 2019-04-22 | 3 | 2664.5 | 1437 | -89 | 0 | 0 | 1526 | 269.9093 | 269.9093 | 269.9093 | 1804.9464 | 780 | 200 | 2784.9464 | 69.62% | 95% | 0% | -101.8307 | 168.0787 | -2750 | -200 | -2781.9213 | 69.55% | 70.46% | 95% | 0% | 1526 | -89
[5 empty] | 2019-04-22 | 4 | 2665 | 1432 | -89 | 0 | 0 | 1521 | 262.0775 | 262.0775 | 262.0775 | 1804.9464 | 780 | 200 | 2784.9464 | 69.62% | 95% | 0% | -101.8307 | 160.2468 | -2750 | -200 | -2789.7532 | 69.74% | 70.46% | 95% | 0% | 1521 | -89
[5 empty] | 2019-04-22 | 5 | 2665.5 | 1436 | -87 | 0 | 0 | 1523 | 265.2102 | 265.2102 | 265.2102 | 1804.9464 | 780 | 200 | 2784.9464 | 69.62% | 95% | 0% | -99.5423 | 165.6679 | -2750 | -200 | -2784.3321 | 69.61% | 70.45% | 95% | 0% | 1523 | -87
[5 empty] | 2019-04-22 | 6 | 2666 | 1415 | -86 | 0 | 0 | 1501 | 230.7502 | 230.7502 | 230.7502 | 1804.9464 | 780 | 200 | 2784.9464 | 69.62% | 95% | 0% | -98.3982 | 132.352 | -2750 | -200 | -2817.648 | 70.44% | 70.45% | 95% | 0% | 1501 | -86
[5 empty] | 2019-04-22 | 7 | 2666.5 | 1407 | -85 | 0 | 0 | 1492 | 216.6529 | 216.6529 | 216.6529 | 1804.9464 | 780 | 200 | 2784.9464 | 69.62% | 95% | 0% | -97.254 | 119.3989 | -2750 | -200 | -2830.6011 | 70.77% | 70.45% | 95% | 0% | 1492 | -85
[5 empty] | 2019-04-22 | 8 | 2667 | 1401 | -85 | 0 | 0 | 1486 | 207.2547 | 207.2547 | 207.2547 | 1803.38 | 780 | 200 | 2783.38 | 69.58% | 95% | 0% | -97.254 | 110.0007 | -2750 | -200 | -2839.9993 | 71% | 70.45% | 95% | 0% | 1486 | -85
[5 empty] | 2019-04-22 | 9 | 2667.5 | 1399 | -86 | 0 | 0 | 1485 | 205.6884 | 205.6884 | 205.6884 | 1803.38 | 780 | 200 | 2783.38 | 69.58% | 95% | 0% | -98.3982 | 107.2902 | -2750 | -200 | -2842.7098 | 71.07% | 70.45% | 95% | 0% | 1485 | -86
[5 empty] | 2019-04-22 | 10 | 2668 | 1390 | -86 | 0 | 0 | 1476 | 191.5911 | 191.5911 | 191.5911 | 1803.38 | 780 | 200 | 2783.38 | 69.58% | 95% | 0% | -98.3982 | 93.1929 | -2750 | -200 | -2856.8071 | 71.42% | 70.45% | 95% | 0% | 1476 | -86
[5 empty] | 2019-04-22 | 11 | 2668.5 | 1422 | -86 | 0 | 0 | 1508 | 241.7148 | 241.7148 | 241.7148 | 1803.38 | 780 | 200 | 2783.38 | 69.58% | 95% | 0% | -98.3982 | 143.3166 | -2750 | -200 | -2806.6834 | 70.17% | 70.44% | 95% | 0% | 1508 | -86
[5 empty] | 2019-04-22 | 12 | 2669 | 1432 | -87 | 0 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 1803.38 | 780 | 200 | 2783.38 | 69.58% | 95% | 0% | -99.5423 | 159.4024 | -2750 | -200 | -2790.5976 | 69.76% | 70.44% | 95% | 0% | 1519 | -87
[5 empty] | 2019-04-22 | 13 | 2669.5 | 1499 | -93 | 0 | 0 | 1592 | 373.2894 | 373.2894 | 373.2894 | 1803.38 | 780 | 200 | 2783.38 | 69.58% | 95% | 0% | -106.4073 | 266.882 | -2750 | -200 | -2683.118 | 67.08% | 70.44% | 95% | 0% | 1592 | -93
[5 empty] | 2019-04-22 | 14 | 2670 | 1526 | -120 | 0 | 0 | 1646 | 457.873 | 457.873 | 457.873 | 1803.38 | 780 | 200 | 2783.38 | 69.58% | 95% | 0% | -137.2998 | 320.5733 | -2750 | -200 | -2629.4267 | 65.74% | 70.44% | 95% | 0% | 1646 | -120
[5 empty] | 2019-04-22 | 15 | 2670.5 | 1568 | -159 | 1 | 0 | 1727 | 584.7486 | 584.7486 | 584.7486 | 1803.38 | 780 | 200 | 2783.38 | 69.58% | 95% | 0% | -181.9222 | 402.8264 | -3550 | -400 | -3547.1736 | 88.68% | 70.44% | 95% | 0% | 1727 | -159
[5 empty] | 2019-04-22 | 16 | 2671 | 1566 | -208 | 1 | 0 | 1774 | 658.3677 | 658.3677 | 658.3677 | 1803.38 | 780 | 200 | 2783.38 | 69.58% | 95% | 0% | -237.9863 | 420.3814 | -3550 | -400 | -3529.6186 | 88.24% | 70.44% | 95% | 0% | 1774 | -208
[5 empty] | 2019-04-22 | 17 | 2671.5 | 1551 | -268 | 1 | 0 | 1819 | 728.8541 | 728.8541 | 728.8541 | 1803.38 | 780 | 200 | 2783.38 | 69.58% | 95% | 0% | -306.6362 | 422.2179 | -3550 | -400 | -3527.7821 | 88.19% | 70.43% | 95% | 0% | 1819 | -268
[5 empty] | 2019-04-22 | 18 | 2672 | 1499 | -328 | 1 | 0 | 1827 | 741.385 | 741.385 | 741.385 | 1803.38 | 780 | 200 | 2783.38 | 69.58% | 95% | 0% | -375.286 | 366.099 | -3550 | -400 | -3583.901 | 89.6% | 70.43% | 95% | 0% | 1827 | -328
[5 empty] | 2019-04-22 | 19 | 2672.5 | 1469 | -389 | 1 | 0 | 1858 | 789.9423 | 789.9423 | 789.9423 | 1803.38 | 780 | 200 | 2783.38 | 69.58% | 95% | 0% | -445.0801 | 344.8622 | -3550 | -400 | -3605.1378 | 90.13% | 70.42% | 95% | 0% | 1858 | -389
[5 empty] | 2019-04-22 | 20 | 2673 | 1410 | -448 | 1 | 0 | 1858 | 789.9423 | 789.9423 | 789.9423 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -512.5858 | 277.3565 | -3550 | -400 | -3672.6435 | 91.82% | 70.42% | 95% | 0% | 1858 | -448
[5 empty] | 2019-04-22 | 21 | 2673.5 | 1329 | -509 | 1 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -582.3799 | 176.2351 | -3550 | -400 | -3773.7649 | 94.34% | 70.41% | 95% | 0% | 1838 | -509
[5 empty] | 2019-04-22 | 22 | 2674 | 1167 | -613 | 1 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -701.373 | -33.6071 | -3550 | -400 | -3983.6071 | 99.59% | 70.4% | 95% | 0% | 1780 | -613
[5 empty] | 2019-04-22 | 23 | 2674.5 | 1074 | -669 | 1 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -765.4462 | -155.6358 | -3550 | -400 | -4105.6358 | 102.6% | 70.4% | 95% | 0% | 1743 | -669
[5 empty] | 2019-04-22 | 24 | 2675 | 1000 | -713 | 1 | 0 | 1713 | 562.8195 | 562.8195 | 562.8195 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -815.7895 | -252.97 | -3550 | -400 | -4202.97 | 105.1% | 70.4% | 95% | 0% | 1713 | -713
[5 empty] | 2019-04-22 | 25 | 2675.5 | 936 | -740 | 1 | 0 | 1676 | 504.864 | 504.864 | 504.864 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -846.6819 | -341.8179 | -3550 | -400 | -4291.8179 | 107.3% | 70.39% | 95% | 0% | 1676 | -740
[5 empty] | 2019-04-22 | 26 | 2676 | 858 | -774 | 1 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -885.5835 | -449.6396 | -3550 | -400 | -4399.6396 | 110% | 70.38% | 95% | 0% | 1632 | -774
[5 empty] | 2019-04-22 | 27 | 2676.5 | 812 | -774 | 1 | 0 | 1586 | 363.8912 | 363.8912 | 363.8912 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -885.5835 | -521.6923 | -3550 | -400 | -4471.6923 | 111.8% | 70.38% | 95% | 0% | 1586 | -774
[5 empty] | 2019-04-22 | 28 | 2677 | 785 | -772 | 1 | 0 | 1557 | 318.4666 | 318.4666 | 318.4666 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -883.2952 | -564.8286 | -3550 | -400 | -4514.8286 | 112.9% | 70.38% | 95% | 0% | 1557 | -772
[5 empty] | 2019-04-22 | 29 | 2677.5 | 806 | -748 | 1 | 0 | 1554 | 313.7675 | 313.7675 | 313.7675 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -855.8352 | -542.0677 | -3550 | -400 | -4492.0677 | 112.3% | 70.38% | 95% | 0% | 1554 | -748
[5 empty] | 2019-04-22 | 30 | 2678 | 874 | -695 | 1 | 0 | 1569 | 337.263 | 337.263 | 337.263 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -795.1945 | -457.9315 | -3550 | -400 | -4407.9315 | 110.2% | 70.37% | 95% | 0% | 1569 | -695
[5 empty] | 2019-04-22 | 31 | 2678.5 | 969 | -637 | 1 | 0 | 1606 | 395.2185 | 395.2185 | 395.2185 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -728.833 | -333.6145 | -3550 | -400 | -4283.6145 | 107.1% | 70.37% | 95% | 0% | 1606 | -637
[5 empty] | 2019-04-22 | 32 | 2679 | 1073 | -591 | 1 | 0 | 1664 | 486.0676 | 486.0676 | 486.0676 | 1801.8137 | 780 | 200 | 2781.8137 | 69.55% | 95% | 0% | -676.2014 | -190.1338 | -3550 | -400 | -4140.1338 | 103.5% | 70.37% | 95% | 0% | 1664 | -591
[5 empty] | 2019-04-22 | 33 | 2679.5 | 1215 | -520 | 1 | 0 | 1735 | 597.2795 | 597.2795 | 597.2795 | 1800.2473 | 780 | 200 | 2780.2473 | 69.51% | 95% | 0% | -594.9657 | 2.3138 | -3550 | -400 | -3947.6862 | 98.69% | 70.36% | 95% | 0% | 1735 | -520
[5 empty] | 2019-04-22 | 34 | 2680 | 1381 | -438 | 1 | 0 | 1819 | 728.8541 | 728.8541 | 728.8541 | 1800.2473 | 780 | 200 | 2780.2473 | 69.51% | 95% | 0% | -501.1442 | 227.7099 | -3550 | -400 | -3722.2901 | 93.06% | 70.36% | 95% | 0% | 1819 | -438
[5 empty] | 2019-04-22 | 35 | 2680.5 | 1634 | -357 | 1 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1800.2473 | 780 | 200 | 2780.2473 | 69.51% | 95% | 0% | -408.4668 | 589.8019 | -3550 | -400 | -3360.1981 | 84% | 70.35% | 95% | 0% | 1991 | -357
[5 empty] | 2019-04-22 | 36 | 2681 | 1810 | -278 | 1 | 0 | 2088 | 1150.2061 | 1150.2061 | 1150.2061 | 1800.2473 | 780 | 200 | 2780.2473 | 69.51% | 95% | 0% | -318.0778 | 832.1283 | -3550 | -400 | -3117.8717 | 77.95% | 70.35% | 95% | 0% | 2088 | -278
[5 empty] | 2019-04-22 | 37 | 2681.5 | 1943 | -225 | 1 | 0 | 2168 | 1275.5153 | 1275.5153 | 1275.5153 | 1800.2473 | 780 | 200 | 2780.2473 | 69.51% | 95% | 0% | -257.4371 | 1018.0782 | -3550 | -400 | -2931.9218 | 73.3% | 70.35% | 95% | 0% | 2168 | -225
[5 empty] | 2019-04-22 | 38 | 2682 | 2048 | -173 | 1 | 0 | 2221 | 1358.5326 | 1358.5326 | 1358.5326 | 1800.2473 | 780 | 200 | 2780.2473 | 69.51% | 95% | 0% | -197.9405 | 1160.5921 | -3550 | -400 | -2789.4079 | 69.74% | 70.34% | 95% | 0% | 2221 | -173
[5 empty] | 2019-04-22 | 39 | 2682.5 | 2114 | -132 | 1 | 0 | 2246 | 1397.6917 | 1397.6917 | 1397.6917 | 1800.2473 | 780 | 200 | 2780.2473 | 69.51% | 95% | 0% | -151.0297 | 1246.6619 | -3550 | -400 | -2703.3381 | 67.58% | 70.33% | 95% | 0% | 2246 | -132
[5 empty] | 2019-04-22 | 40 | 2683 | 2144 | -112 | 1 | 0 | 2256 | 1413.3553 | 1413.3553 | 1413.3553 | 1800.2473 | 780 | 200 | 2780.2473 | 69.51% | 95% | 0% | -128.1465 | 1285.2089 | -3550 | -400 | -2664.7911 | 66.62% | 70.33% | 95% | 0% | 2256 | -112
[5 empty] | 2019-04-22 | 41 | 2683.5 | 2149 | -107 | 1 | 0 | 2256 | 1413.3553 | 1413.3553 | 1413.3553 | 1800.2473 | 780 | 200 | 2780.2473 | 69.51% | 95% | 0% | -122.4256 | 1290.9297 | -3550 | -400 | -2659.0703 | 66.48% | 70.33% | 95% | 0% | 2256 | -107
[5 empty] | 2019-04-22 | 42 | 2684 | 2148 | -109 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 1800.2473 | 780 | 200 | 2780.2473 | 69.51% | 95% | 0% | -124.714 | 1290.2077 | -3550 | -400 | -2659.7923 | 66.49% | 70.33% | 95% | 0% | 2257 | -109
[5 empty] | 2019-04-22 | 43 | 2684.5 | 2113 | -109 | 0 | 0 | 2222 | 1360.0989 | 1360.0989 | 1360.0989 | 1798.681 | 780 | 200 | 2778.681 | 69.47% | 95% | 0% | -124.714 | 1235.385 | -2750 | -200 | -1714.615 | 42.87% | 70.33% | 95% | 0% | 2222 | -109
[5 empty] | 2019-04-22 | 44 | 2685 | 2025 | -110 | 0 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 1798.681 | 780 | 200 | 2778.681 | 69.47% | 95% | 0% | -125.8581 | 1097.9671 | -2750 | -200 | -1852.0329 | 46.3% | 70.33% | 95% | 0% | 2135 | -110
[5 empty] | 2019-04-22 | 45 | 2685.5 | 1929 | -109 | 0 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 1798.681 | 780 | 200 | 2778.681 | 69.47% | 95% | 0% | -124.714 | 947.1739 | -2750 | -200 | -2002.8261 | 50.07% | 70.31% | 95% | 0% | 2038 | -109
[5 empty] | 2019-04-22 | 46 | 2686 | 1802 | -107 | 0 | 0 | 1909 | 869.8269 | 869.8269 | 869.8269 | 1798.681 | 780 | 200 | 2778.681 | 69.47% | 95% | 0% | -122.4256 | 747.4012 | -2750 | -200 | -2202.5988 | 55.06% | 70.31% | 95% | 0% | 1909 | -107
[5 empty] | 2019-04-22 | 47 | 2686.5 | 1668 | -106 | 0 | 0 | 1774 | 658.3677 | 658.3677 | 658.3677 | 1798.681 | 780 | 200 | 2778.681 | 69.47% | 95% | 0% | -121.2815 | 537.0862 | -2750 | -200 | -2412.9138 | 60.32% | 70.31% | 95% | 0% | 1774 | -106
[5 empty] | 2019-04-22 | 48 | 2687 | 1575 | -104 | 0 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 1798.681 | 780 | 200 | 2778.681 | 69.47% | 95% | 0% | -118.9931 | 390.5699 | -2750 | -200 | -2559.4301 | 63.99% | 70.31% | 95% | 0% | 1679 | -104
[5 empty] | 2019-04-23 | 1 | 2687.5 | 1510 | -103 | 0 | 0 | 1613 | 406.183 | 406.183 | 406.183 | 1798.681 | 780 | 200 | 2778.681 | 69.47% | 95% | 0% | -117.849 | 288.334 | -2750 | -200 | -2661.666 | 66.54% | 70.31% | 95% | 0% | 1613 | -103
[5 empty] | 2019-04-23 | 2 | 2688 | 1474 | -103 | 1 | 0 | 1577 | 349.7939 | 349.7939 | 349.7939 | 1798.681 | 780 | 200 | 2778.681 | 69.47% | 95% | 0% | -117.849 | 231.9449 | -3550 | -400 | -3718.0551 | 92.95% | 70.3% | 95% | 0% | 1577 | -103
[5 empty] | 2019-04-23 | 3 | 2688.5 | 1454 | -101 | 1 | 0 | 1555 | 315.3339 | 315.3339 | 315.3339 | 1797.1146 | 780 | 200 | 2777.1146 | 69.43% | 95% | 0% | -115.5606 | 199.7732 | -3550 | -400 | -3750.2268 | 93.76% | 70.29% | 95% | 0% | 1555 | -101
[5 empty] | 2019-04-23 | 4 | 2689 | 1462 | -100 | 1 | 0 | 1562 | 326.2984 | 326.2984 | 326.2984 | 1797.1146 | 780 | 200 | 2777.1146 | 69.43% | 95% | 0% | -114.4165 | 211.882 | -3550 | -400 | -3738.118 | 93.45% | 70.29% | 95% | 0% | 1562 | -100
[5 empty] | 2019-04-23 | 5 | 2689.5 | 1455 | -100 | 1 | 0 | 1555 | 315.3339 | 315.3339 | 315.3339 | 1797.1146 | 780 | 200 | 2777.1146 | 69.43% | 95% | 0% | -114.4165 | 200.9174 | -3550 | -400 | -3749.0826 | 93.73% | 70.29% | 95% | 0% | 1555 | -100
[5 empty] | 2019-04-23 | 6 | 2690 | 1434 | -99 | 1 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 1797.1146 | 780 | 200 | 2777.1146 | 69.43% | 95% | 0% | -113.2723 | 167.6016 | -3550 | -400 | -3782.3984 | 94.56% | 70.29% | 95% | 0% | 1533 | -99
[5 empty] | 2019-04-23 | 7 | 2690.5 | 1414 | -97 | 1 | 0 | 1511 | 246.4138 | 246.4138 | 246.4138 | 1797.1146 | 780 | 200 | 2777.1146 | 69.43% | 95% | 0% | -110.984 | 135.4299 | -3550 | -400 | -3814.5701 | 95.36% | 70.29% | 95% | 0% | 1511 | -97
[5 empty] | 2019-04-23 | 8 | 2691 | 1399 | -95 | 1 | 0 | 1494 | 219.7857 | 219.7857 | 219.7857 | 1797.1146 | 780 | 200 | 2777.1146 | 69.43% | 95% | 0% | -108.6957 | 111.09 | -3550 | -400 | -3838.91 | 95.97% | 70.27% | 95% | 0% | 1494 | -95
[5 empty] | 2019-04-23 | 9 | 2691.5 | 1404 | -94 | 1 | 0 | 1498 | 226.0511 | 226.0511 | 226.0511 | 1797.1146 | 780 | 200 | 2777.1146 | 69.43% | 95% | 0% | -107.5515 | 118.4996 | -3550 | -400 | -3831.5004 | 95.79% | 70.27% | 95% | 0% | 1498 | -94
[5 empty] | 2019-04-23 | 10 | 2692 | 1413 | -92 | 1 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 1797.1146 | 780 | 200 | 2777.1146 | 69.43% | 95% | 0% | -105.2632 | 131.7525 | -3550 | -400 | -3818.2475 | 95.46% | 70.27% | 95% | 0% | 1505 | -92
[5 empty] | 2019-04-23 | 11 | 2692.5 | 1471 | -95 | 1 | 0 | 1566 | 332.5639 | 332.5639 | 332.5639 | 1797.1146 | 780 | 200 | 2777.1146 | 69.43% | 95% | 0% | -108.6957 | 223.8682 | -3550 | -400 | -3726.1318 | 93.15% | 70.26% | 95% | 0% | 1566 | -95
[5 empty] | 2019-04-23 | 12 | 2693 | 1542 | -98 | 1 | 0 | 1640 | 448.4749 | 448.4749 | 448.4749 | 1797.1146 | 780 | 200 | 2777.1146 | 69.43% | 95% | 0% | -112.1281 | 336.3467 | -3550 | -400 | -3613.6533 | 90.34% | 70.26% | 95% | 0% | 1640 | -98
[5 empty] | 2019-04-23 | 13 | 2693.5 | 1715 | -105 | 1 | 0 | 1820 | 730.4204 | 730.4204 | 730.4204 | 1797.1146 | 780 | 200 | 2777.1146 | 69.43% | 95% | 0% | -120.1373 | 610.2831 | -3550 | -400 | -3339.7169 | 83.49% | 70.25% | 95% | 0% | 1820 | -105
[5 empty] | 2019-04-23 | 14 | 2694 | 1869 | -122 | 1 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1797.1146 | 780 | 200 | 2777.1146 | 69.43% | 95% | 0% | -139.5881 | 858.6807 | -3550 | -400 | -3091.3193 | 77.28% | 70.24% | 95% | 0% | 1991 | -122
[5 empty] | 2019-04-23 | 15 | 2694.5 | 2060 | -146 | 1 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 1795.5482 | 780 | 200 | 2775.5482 | 69.39% | 95% | 0% | -167.0481 | 1167.989 | -3550 | -400 | -2782.011 | 69.55% | 70.24% | 95% | 0% | 2206 | -146
[5 empty] | 2019-04-23 | 16 | 2695 | 2119 | -181 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 1795.5482 | 780 | 200 | 2775.5482 | 69.39% | 95% | 0% | -207.0938 | 1275.1815 | -3550 | -400 | -2674.8185 | 66.87% | 70.24% | 95% | 0% | 2300 | -181
[5 empty] | 2019-04-23 | 17 | 2695.5 | 2098 | -228 | 1 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 1795.5482 | 780 | 200 | 2775.5482 | 69.39% | 95% | 0% | -260.8696 | 1262.1313 | -3550 | -400 | -2687.8687 | 67.2% | 70.23% | 95% | 0% | 2326 | -228
[5 empty] | 2019-04-23 | 18 | 2696 | 2025 | -276 | 1 | 0 | 2301 | 1483.8417 | 1483.8417 | 1483.8417 | 1795.5482 | 780 | 200 | 2775.5482 | 69.39% | 95% | 0% | -315.7895 | 1168.0522 | -3550 | -400 | -2781.9478 | 69.55% | 70.22% | 95% | 0% | 2301 | -276
[5 empty] | 2019-04-23 | 19 | 2696.5 | 1972 | -329 | 1 | 0 | 2301 | 1483.8417 | 1483.8417 | 1483.8417 | 1795.5482 | 780 | 200 | 2775.5482 | 69.39% | 95% | 0% | -376.4302 | 1107.4115 | -3550 | -400 | -2842.5885 | 71.06% | 70.22% | 95% | 0% | 2301 | -329
[5 empty] | 2019-04-23 | 20 | 2697 | 1871 | -386 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 1795.5482 | 780 | 200 | 2775.5482 | 69.39% | 95% | 0% | -441.6476 | 973.2741 | -3550 | -400 | -2976.7259 | 74.42% | 70.22% | 95% | 0% | 2257 | -386
[5 empty] | 2019-04-23 | 21 | 2697.5 | 1781 | -443 | 1 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 1795.5482 | 780 | 200 | 2775.5482 | 69.39% | 95% | 0% | -506.865 | 856.3667 | -3550 | -400 | -3093.6333 | 77.34% | 70.21% | 95% | 0% | 2224 | -443
[5 empty] | 2019-04-23 | 22 | 2698 | 1708 | -511 | 1 | 0 | 2219 | 1355.3998 | 1355.3998 | 1355.3998 | 1795.5482 | 780 | 200 | 2775.5482 | 69.39% | 95% | 0% | -584.6682 | 770.7316 | -3550 | -400 | -3179.2684 | 79.48% | 70.21% | 95% | 0% | 2219 | -511
[5 empty] | 2019-04-23 | 23 | 2698.5 | 1639 | -563 | 1 | 0 | 2202 | 1328.7716 | 1328.7716 | 1328.7716 | 1795.5482 | 780 | 200 | 2775.5482 | 69.39% | 95% | 0% | -644.1648 | 684.6069 | -3550 | -400 | -3265.3931 | 81.63% | 70.21% | 95% | 0% | 2202 | -563
[5 empty] | 2019-04-23 | 24 | 2699 | 1583 | -599 | 1 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 1795.5482 | 780 | 200 | 2775.5482 | 69.39% | 95% | 0% | -685.3547 | 612.0897 | -3550 | -400 | -3337.9103 | 83.45% | 70.21% | 95% | 0% | 2182 | -599
[5 empty] | 2019-04-23 | 25 | 2699.5 | 1565 | -620 | 1 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -709.3822 | 592.7613 | -3550 | -400 | -3357.2387 | 83.93% | 70.2% | 95% | 0% | 2185 | -620
[5 empty] | 2019-04-23 | 26 | 2700 | 1542 | -627 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -717.3913 | 559.6903 | -3550 | -400 | -3390.3097 | 84.76% | 70.19% | 95% | 0% | 2169 | -627
[5 empty] | 2019-04-23 | 27 | 2700.5 | 1523 | -633 | 1 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -724.2563 | 532.4626 | -3550 | -400 | -3417.5374 | 85.44% | 70.19% | 95% | 0% | 2156 | -633
[5 empty] | 2019-04-23 | 28 | 2701 | 1544 | -592 | 1 | 0 | 2136 | 1225.3916 | 1225.3916 | 1225.3916 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -677.3455 | 548.0461 | -3550 | -400 | -3401.9539 | 85.05% | 70.19% | 95% | 0% | 2136 | -592
[5 empty] | 2019-04-23 | 29 | 2701.5 | 1593 | -556 | 1 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -636.1556 | 609.5987 | -3550 | -400 | -3340.4013 | 83.51% | 70.19% | 95% | 0% | 2149 | -556
[5 empty] | 2019-04-23 | 30 | 2702 | 1621 | -541 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -618.9931 | 647.1239 | -3550 | -400 | -3302.8761 | 82.57% | 70.19% | 95% | 0% | 2162 | -541
[5 empty] | 2019-04-23 | 31 | 2702.5 | 1699 | -491 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -561.7849 | 748.1904 | -3550 | -400 | -3201.8096 | 80.05% | 70.18% | 95% | 0% | 2190 | -491
[5 empty] | 2019-04-23 | 32 | 2703 | 1818 | -442 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -505.7208 | 913.9 | -3550 | -400 | -3036.1 | 75.9% | 70.18% | 95% | 0% | 2260 | -442
[5 empty] | 2019-04-23 | 33 | 2703.5 | 1929 | -396 | 1 | 0 | 2325 | 1521.4345 | 1521.4345 | 1521.4345 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -453.0892 | 1068.3452 | -3550 | -400 | -2881.6548 | 72.04% | 70.17% | 95% | 0% | 2325 | -396
[5 empty] | 2019-04-23 | 34 | 2704 | 2054 | -350 | 1 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -400.4577 | 1244.7196 | -3550 | -400 | -2705.2804 | 67.63% | 70.17% | 95% | 0% | 2404 | -350
[5 empty] | 2019-04-23 | 35 | 2704.5 | 2136 | -308 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -352.4027 | 1355.4291 | -3550 | -400 | -2594.5709 | 64.86% | 70.17% | 95% | 0% | 2444 | -308
[5 empty] | 2019-04-23 | 36 | 2705 | 2223 | -262 | 1 | 0 | 2485 | 1772.0528 | 1772.0528 | 1772.0528 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -299.7712 | 1472.2816 | -3550 | -400 | -2477.7184 | 61.94% | 70.17% | 95% | 0% | 2485 | -262
[5 empty] | 2019-04-23 | 37 | 2705.5 | 2266 | -226 | 1 | 0 | 2492 | 1783.0173 | 1783.0173 | 1783.0173 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -258.5812 | 1524.4361 | -3550 | -400 | -2425.5639 | 60.64% | 70.17% | 95% | 0% | 2492 | -226
[5 empty] | 2019-04-23 | 38 | 2706 | 2325 | -189 | 1 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 1793.9819 | 780 | 200 | 2773.9819 | 69.35% | 95% | 0% | -216.2471 | 1601.2302 | -3550 | -400 | -2348.7698 | 58.72% | 70.16% | 95% | 0% | 2514 | -189
[5 empty] | 2019-04-23 | 39 | 2706.5 | 2354 | -154 | 1 | 0 | 2508 | 1808.0791 | 1808.0791 | 1808.0791 | 1792.4155 | 780 | 200 | 2772.4155 | 69.31% | 95% | 0% | -176.2014 | 1631.8778 | -3550 | -400 | -2318.1222 | 57.95% | 70.16% | 95% | 0% | 2508 | -154
[5 empty] | 2019-04-23 | 40 | 2707 | 2376 | -131 | 1 | 0 | 2507 | 1806.5128 | 1806.5128 | 1806.5128 | 1792.4155 | 780 | 200 | 2772.4155 | 69.31% | 95% | 0% | -149.8856 | 1656.6272 | -3550 | -400 | -2293.3728 | 57.33% | 70.15% | 95% | 0% | 2507 | -131
[5 empty] | 2019-04-23 | 41 | 2707.5 | 2381 | -124 | 1 | 0 | 2505 | 1803.38 | 1803.38 | 1803.38 | 1792.4155 | 780 | 200 | 2772.4155 | 69.31% | 95% | 0% | -141.8764 | 1661.5036 | -3550 | -400 | -2288.4964 | 57.21% | 70.15% | 95% | 0% | 2505 | -124
[5 empty] | 2019-04-23 | 42 | 2708 | 2389 | -122 | 1 | 0 | 2511 | 1812.7782 | 1812.7782 | 1812.7782 | 1792.4155 | 780 | 200 | 2772.4155 | 69.31% | 95% | 0% | -139.5881 | 1673.1901 | -3550 | -400 | -2276.8099 | 56.92% | 70.15% | 95% | 0% | 2511 | -122
[5 empty] | 2019-04-23 | 43 | 2708.5 | 2327 | -119 | 0 | 0 | 2446 | 1710.9646 | 1710.9646 | 1710.9646 | 1792.4155 | 780 | 200 | 2772.4155 | 69.31% | 95% | 0% | -136.1556 | 1574.8089 | -2750 | -200 | -1375.1911 | 34.38% | 70.15% | 95% | 0% | 2446 | -119
[5 empty] | 2019-04-23 | 44 | 2709 | 2208 | -117 | 0 | 0 | 2325 | 1521.4345 | 1521.4345 | 1521.4345 | 1792.4155 | 780 | 200 | 2772.4155 | 69.31% | 95% | 0% | -133.8673 | 1387.5672 | -2750 | -200 | -1562.4328 | 39.06% | 70.15% | 95% | 0% | 2325 | -117
[5 empty] | 2019-04-23 | 45 | 2709.5 | 2071 | -116 | 0 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 1792.4155 | 780 | 200 | 2772.4155 | 69.31% | 95% | 0% | -132.7231 | 1172.5531 | -2750 | -200 | -1777.4469 | 44.44% | 70.14% | 95% | 0% | 2187 | -116
[5 empty] | 2019-04-23 | 46 | 2710 | 1926 | -115 | 0 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 1792.4155 | 780 | 200 | 2772.4155 | 69.31% | 95% | 0% | -131.5789 | 945.008 | -2750 | -200 | -2004.992 | 50.12% | 70.13% | 95% | 0% | 2041 | -115
[5 empty] | 2019-04-23 | 47 | 2710.5 | 1780 | -113 | 0 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 1790.8491 | 780 | 200 | 2770.8491 | 69.27% | 95% | 0% | -129.2906 | 715.4744 | -2750 | -200 | -2234.5256 | 55.86% | 70.13% | 95% | 0% | 1893 | -113
[5 empty] | 2019-04-23 | 48 | 2711 | 1662 | -112 | 0 | 0 | 1774 | 658.3677 | 658.3677 | 658.3677 | 1790.8491 | 780 | 200 | 2770.8491 | 69.27% | 95% | 0% | -128.1465 | 530.2212 | -2750 | -200 | -2419.7788 | 60.49% | 70.13% | 95% | 0% | 1774 | -112
[5 empty] | 2019-04-24 | 1 | 2711.5 | 1579 | -107 | 0 | 0 | 1686 | 520.5276 | 520.5276 | 520.5276 | 1790.8491 | 780 | 200 | 2770.8491 | 69.27% | 95% | 0% | -122.4256 | 398.102 | -2750 | -200 | -2551.898 | 63.8% | 70.12% | 95% | 0% | 1686 | -107
[5 empty] | 2019-04-24 | 2 | 2712 | 1535 | -102 | 0 | 0 | 1637 | 443.7758 | 443.7758 | 443.7758 | 1790.8491 | 780 | 200 | 2770.8491 | 69.27% | 95% | 0% | -116.7048 | 327.071 | -2750 | -200 | -2622.929 | 65.57% | 70.12% | 95% | 0% | 1637 | -102
[5 empty] | 2019-04-24 | 3 | 2712.5 | 1533 | -102 | 0 | 0 | 1635 | 440.643 | 440.643 | 440.643 | 1790.8491 | 780 | 200 | 2770.8491 | 69.27% | 95% | 0% | -116.7048 | 323.9382 | -2750 | -200 | -2626.0618 | 65.65% | 70.11% | 95% | 0% | 1635 | -102
[5 empty] | 2019-04-24 | 4 | 2713 | 1525 | -101 | 0 | 0 | 1626 | 426.5458 | 426.5458 | 426.5458 | 1790.8491 | 780 | 200 | 2770.8491 | 69.27% | 95% | 0% | -115.5606 | 310.9851 | -2750 | -200 | -2639.0149 | 65.98% | 70.1% | 95% | 0% | 1626 | -101
[5 empty] | 2019-04-24 | 5 | 2713.5 | 1508 | -100 | 0 | 0 | 1608 | 398.3512 | 398.3512 | 398.3512 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -114.4165 | 283.9347 | -2750 | -200 | -2666.0653 | 66.65% | 70.1% | 95% | 0% | 1608 | -100
[5 empty] | 2019-04-24 | 6 | 2714 | 1471 | -100 | 0 | 0 | 1571 | 340.3957 | 340.3957 | 340.3957 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -114.4165 | 225.9792 | -2750 | -200 | -2724.0208 | 68.1% | 70.09% | 95% | 0% | 1571 | -100
[5 empty] | 2019-04-24 | 7 | 2714.5 | 1467 | -99 | 0 | 0 | 1566 | 332.5639 | 332.5639 | 332.5639 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -113.2723 | 219.2916 | -2750 | -200 | -2730.7084 | 68.27% | 70.08% | 95% | 0% | 1566 | -99
[5 empty] | 2019-04-24 | 8 | 2715 | 1465 | -99 | 0 | 0 | 1564 | 329.4312 | 329.4312 | 329.4312 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -113.2723 | 216.1589 | -2750 | -200 | -2733.8411 | 68.35% | 70.07% | 95% | 0% | 1564 | -99
[5 empty] | 2019-04-24 | 9 | 2715.5 | 1463 | -97 | 0 | 0 | 1560 | 323.1657 | 323.1657 | 323.1657 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -110.984 | 212.1817 | -2750 | -200 | -2737.8183 | 68.45% | 70.06% | 95% | 0% | 1560 | -97
[5 empty] | 2019-04-24 | 10 | 2716 | 1485 | -96 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -109.8398 | 246.2195 | -2750 | -200 | -2703.7805 | 67.59% | 70.06% | 95% | 0% | 1581 | -96
[5 empty] | 2019-04-24 | 11 | 2716.5 | 1535 | -97 | 0 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -110.984 | 324.96 | -2750 | -200 | -2625.04 | 65.63% | 70.06% | 95% | 0% | 1632 | -97
[5 empty] | 2019-04-24 | 12 | 2717 | 1610 | -98 | 0 | 0 | 1708 | 554.9876 | 554.9876 | 554.9876 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -112.1281 | 442.8595 | -2750 | -200 | -2507.1405 | 62.68% | 70.06% | 95% | 0% | 1708 | -98
[5 empty] | 2019-04-24 | 13 | 2717.5 | 1791 | -103 | 0 | 0 | 1894 | 846.3314 | 846.3314 | 846.3314 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -117.849 | 728.4824 | -2750 | -200 | -2221.5176 | 55.54% | 70.05% | 95% | 0% | 1894 | -103
[5 empty] | 2019-04-24 | 14 | 2718 | 1968 | -120 | 1 | 0 | 2088 | 1150.2061 | 1150.2061 | 1150.2061 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -137.2998 | 1012.9063 | -3550 | -400 | -2937.0937 | 73.43% | 70.05% | 95% | 0% | 2088 | -120
[5 empty] | 2019-04-24 | 15 | 2718.5 | 2153 | -146 | 1 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -167.0481 | 1313.6609 | -3550 | -400 | -2636.3391 | 65.91% | 70.05% | 95% | 0% | 2299 | -146
[5 empty] | 2019-04-24 | 16 | 2719 | 2226 | -175 | 1 | 0 | 2401 | 1640.4782 | 1640.4782 | 1640.4782 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -200.2288 | 1440.2493 | -3550 | -400 | -2509.7507 | 62.74% | 70.05% | 95% | 0% | 2401 | -175
[5 empty] | 2019-04-24 | 17 | 2719.5 | 2228 | -223 | 1 | 0 | 2451 | 1718.7964 | 1718.7964 | 1718.7964 | 1789.2828 | 780 | 200 | 2769.2828 | 69.23% | 95% | 0% | -255.1487 | 1463.6476 | -3550 | -400 | -2486.3524 | 62.16% | 70.04% | 95% | 0% | 2451 | -223
[5 empty] | 2019-04-24 | 18 | 2720 | 2188 | -259 | 1 | 0 | 2447 | 1712.5309 | 1712.5309 | 1712.5309 | 1787.7164 | 780 | 200 | 2767.7164 | 69.19% | 95% | 0% | -296.3387 | 1416.1922 | -3550 | -400 | -2533.8078 | 63.35% | 70.03% | 95% | 0% | 2447 | -259
[5 empty] | 2019-04-24 | 19 | 2720.5 | 2157 | -300 | 1 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 1787.7164 | 780 | 200 | 2767.7164 | 69.19% | 95% | 0% | -343.2494 | 1384.9451 | -3550 | -400 | -2565.0549 | 64.13% | 70.03% | 95% | 0% | 2457 | -300
[5 empty] | 2019-04-24 | 20 | 2721 | 2114 | -332 | 1 | 0 | 2446 | 1710.9646 | 1710.9646 | 1710.9646 | 1787.7164 | 780 | 200 | 2767.7164 | 69.19% | 95% | 0% | -379.8627 | 1331.1019 | -3550 | -400 | -2618.8981 | 65.47% | 70.02% | 95% | 0% | 2446 | -332
[5 empty] | 2019-04-24 | 21 | 2721.5 | 2083 | -359 | 1 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 1787.7164 | 780 | 200 | 2767.7164 | 69.19% | 95% | 0% | -410.7551 | 1293.9439 | -3550 | -400 | -2656.0561 | 66.4% | 70.01% | 95% | 0% | 2442 | -359
[5 empty] | 2019-04-24 | 22 | 2722 | 2042 | -421 | 1 | 0 | 2463 | 1737.5927 | 1737.5927 | 1737.5927 | 1787.7164 | 780 | 200 | 2767.7164 | 69.19% | 95% | 0% | -481.6934 | 1255.8994 | -3550 | -400 | -2694.1006 | 67.35% | 70.01% | 95% | 0% | 2463 | -421
[5 empty] | 2019-04-24 | 23 | 2722.5 | 2011 | -441 | 1 | 0 | 2452 | 1720.3627 | 1720.3627 | 1720.3627 | 1787.7164 | 780 | 200 | 2767.7164 | 69.19% | 95% | 0% | -504.5767 | 1215.7861 | -3550 | -400 | -2734.2139 | 68.36% | 70% | 95% | 0% | 2452 | -441
[5 empty] | 2019-04-24 | 24 | 2723 | 2022 | -419 | 1 | 0 | 2441 | 1703.1327 | 1703.1327 | 1703.1327 | 1787.7164 | 780 | 200 | 2767.7164 | 69.19% | 95% | 0% | -479.405 | 1223.7277 | -3550 | -400 | -2726.2723 | 68.16% | 69.99% | 95% | 0% | 2441 | -419
[5 empty] | 2019-04-24 | 25 | 2723.5 | 2020 | -410 | 1 | 0 | 2430 | 1685.9027 | 1685.9027 | 1685.9027 | 1787.7164 | 780 | 200 | 2767.7164 | 69.19% | 95% | 0% | -469.1076 | 1216.7952 | -3550 | -400 | -2733.2048 | 68.33% | 69.99% | 95% | 0% | 2430 | -410
[5 empty] | 2019-04-24 | 26 | 2724 | 2025 | -383 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 1787.7164 | 780 | 200 | 2767.7164 | 69.19% | 95% | 0% | -438.2151 | 1213.2276 | -3550 | -400 | -2736.7724 | 68.42% | 69.99% | 95% | 0% | 2408 | -383
[5 empty] | 2019-04-24 | 27 | 2724.5 | 1961 | -419 | 1 | 0 | 2380 | 1607.5845 | 1607.5845 | 1607.5845 | 1787.7164 | 780 | 200 | 2767.7164 | 69.19% | 95% | 0% | -479.405 | 1128.1795 | -3550 | -400 | -2821.8205 | 70.55% | 69.98% | 95% | 0% | 2380 | -419
[5 empty] | 2019-04-24 | 28 | 2725 | 1905 | -450 | 1 | 0 | 2355 | 1568.4254 | 1568.4254 | 1568.4254 | 1787.7164 | 780 | 200 | 2767.7164 | 69.19% | 95% | 0% | -514.8741 | 1053.5512 | -3550 | -400 | -2896.4488 | 72.41% | 69.98% | 95% | 0% | 2355 | -450
[5 empty] | 2019-04-24 | 29 | 2725.5 | 1913 | -436 | 1 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 1787.7164 | 780 | 200 | 2767.7164 | 69.19% | 95% | 0% | -498.8558 | 1060.1714 | -3550 | -400 | -2889.8286 | 72.25% | 69.97% | 95% | 0% | 2349 | -436
[5 empty] | 2019-04-24 | 30 | 2726 | 1866 | -450 | 1 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 1786.15 | 780 | 200 | 2766.15 | 69.15% | 95% | 0% | -514.8741 | 992.463 | -3550 | -400 | -2957.537 | 73.94% | 69.97% | 95% | 0% | 2316 | -450
[5 empty] | 2019-04-24 | 31 | 2726.5 | 1882 | -428 | 1 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 1786.15 | 780 | 200 | 2766.15 | 69.15% | 95% | 0% | -489.7025 | 1008.2365 | -3550 | -400 | -2941.7635 | 73.54% | 69.97% | 95% | 0% | 2310 | -428
[5 empty] | 2019-04-24 | 32 | 2727 | 1911 | -416 | 1 | 0 | 2327 | 1524.5672 | 1524.5672 | 1524.5672 | 1786.15 | 780 | 200 | 2766.15 | 69.15% | 95% | 0% | -475.9725 | 1048.5946 | -3550 | -400 | -2901.4054 | 72.54% | 69.97% | 95% | 0% | 2327 | -416
[5 empty] | 2019-04-24 | 33 | 2727.5 | 1983 | -400 | 1 | 0 | 2383 | 1612.2836 | 1612.2836 | 1612.2836 | 1786.15 | 780 | 200 | 2766.15 | 69.15% | 95% | 0% | -457.6659 | 1154.6177 | -3550 | -400 | -2795.3823 | 69.88% | 69.97% | 95% | 0% | 2383 | -400
[5 empty] | 2019-04-24 | 34 | 2728 | 2065 | -364 | 1 | 0 | 2429 | 1684.3364 | 1684.3364 | 1684.3364 | 1786.15 | 780 | 200 | 2766.15 | 69.15% | 95% | 0% | -416.476 | 1267.8604 | -3550 | -400 | -2682.1396 | 67.05% | 69.97% | 95% | 0% | 2429 | -364
[5 empty] | 2019-04-24 | 35 | 2728.5 | 2177 | -315 | 1 | 0 | 2492 | 1783.0173 | 1783.0173 | 1783.0173 | 1786.15 | 780 | 200 | 2766.15 | 69.15% | 95% | 0% | -360.4119 | 1422.6054 | -3550 | -400 | -2527.3946 | 63.18% | 69.96% | 95% | 0% | 2492 | -315
[5 empty] | 2019-04-24 | 36 | 2729 | 2271 | -256 | 1 | 0 | 2527 | 1837.8401 | 1837.8401 | 1837.8401 | 1786.15 | 780 | 200 | 2766.15 | 69.15% | 95% | 0% | -292.9062 | 1544.9339 | -3550 | -400 | -2405.0661 | 60.13% | 69.96% | 95% | 0% | 2527 | -256
[5 empty] | 2019-04-24 | 37 | 2729.5 | 2310 | -226 | 1 | 0 | 2536 | 1851.9373 | 1851.9373 | 1851.9373 | 1786.15 | 780 | 200 | 2766.15 | 69.15% | 95% | 0% | -258.5812 | 1593.3561 | -3550 | -400 | -2356.6439 | 58.92% | 69.96% | 95% | 0% | 2536 | -226
[5 empty] | 2019-04-24 | 38 | 2730 | 2326 | -196 | 1 | 0 | 2522 | 1830.0082 | 1830.0082 | 1830.0082 | 1786.15 | 780 | 200 | 2766.15 | 69.15% | 95% | 0% | -224.2563 | 1605.752 | -3550 | -400 | -2344.248 | 58.61% | 69.96% | 95% | 0% | 2522 | -196
[5 empty] | 2019-04-24 | 39 | 2730.5 | 2373 | -162 | 1 | 0 | 2535 | 1850.371 | 1850.371 | 1850.371 | 1786.15 | 780 | 200 | 2766.15 | 69.15% | 95% | 0% | -185.3547 | 1665.0163 | -3550 | -400 | -2284.9837 | 57.12% | 69.96% | 95% | 0% | 2535 | -162
[5 empty] | 2019-04-24 | 40 | 2731 | 2393 | -138 | 1 | 0 | 2531 | 1844.1055 | 1844.1055 | 1844.1055 | 1786.15 | 780 | 200 | 2766.15 | 69.15% | 95% | 0% | -157.8947 | 1686.2108 | -3550 | -400 | -2263.7892 | 56.59% | 69.96% | 95% | 0% | 2531 | -138
[5 empty] | 2019-04-24 | 41 | 2731.5 | 2397 | -123 | 1 | 0 | 2520 | 1826.8755 | 1826.8755 | 1826.8755 | 1786.15 | 780 | 200 | 2766.15 | 69.15% | 95% | 0% | -140.7323 | 1686.1432 | -3550 | -400 | -2263.8568 | 56.6% | 69.93% | 95% | 0% | 2520 | -123
[5 empty] | 2019-04-24 | 42 | 2732 | 2403 | -117 | 1 | 0 | 2520 | 1826.8755 | 1826.8755 | 1826.8755 | 1784.5837 | 780 | 200 | 2764.5837 | 69.11% | 95% | 0% | -133.8673 | 1693.0082 | -3550 | -400 | -2256.9918 | 56.42% | 69.93% | 95% | 0% | 2520 | -117
[5 empty] | 2019-04-24 | 43 | 2732.5 | 2358 | -116 | 1 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 1784.5837 | 780 | 200 | 2764.5837 | 69.11% | 95% | 0% | -132.7231 | 1622.0996 | -3550 | -400 | -2327.9004 | 58.2% | 69.93% | 95% | 0% | 2474 | -116
[5 empty] | 2019-04-24 | 44 | 2733 | 2242 | -114 | 0 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 1784.5837 | 780 | 200 | 2764.5837 | 69.11% | 95% | 0% | -130.4348 | 1439.557 | -2750 | -200 | -1510.443 | 37.76% | 69.93% | 95% | 0% | 2356 | -114
[5 empty] | 2019-04-24 | 45 | 2733.5 | 2138 | -114 | 0 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 1784.5837 | 780 | 200 | 2764.5837 | 69.11% | 95% | 0% | -130.4348 | 1276.6551 | -2750 | -200 | -1673.3449 | 41.83% | 69.92% | 95% | 0% | 2252 | -114
[5 empty] | 2019-04-24 | 46 | 2734 | 2009 | -115 | 0 | 0 | 2124 | 1206.5952 | 1206.5952 | 1206.5952 | 1784.5837 | 780 | 200 | 2764.5837 | 69.11% | 95% | 0% | -131.5789 | 1075.0163 | -2750 | -200 | -1874.9837 | 46.87% | 69.92% | 95% | 0% | 2124 | -115
[5 empty] | 2019-04-24 | 47 | 2734.5 | 1851 | -116 | 0 | 0 | 1967 | 960.676 | 960.676 | 960.676 | 1783.0173 | 780 | 200 | 2763.0173 | 69.08% | 95% | 0% | -132.7231 | 827.9529 | -2750 | -200 | -2122.0471 | 53.05% | 69.92% | 95% | 0% | 1967 | -116
[5 empty] | 2019-04-24 | 48 | 2735 | 1730 | -117 | 0 | 0 | 1847 | 772.7123 | 772.7123 | 772.7123 | 1783.0173 | 780 | 200 | 2763.0173 | 69.08% | 95% | 0% | -133.8673 | 638.845 | -2750 | -200 | -2311.155 | 57.78% | 69.92% | 95% | 0% | 1847 | -117
[5 empty] | 2019-04-25 | 1 | 2735.5 | 1652 | -111 | 0 | 0 | 1763 | 641.1377 | 641.1377 | 641.1377 | 1783.0173 | 780 | 200 | 2763.0173 | 69.08% | 95% | 0% | -127.0023 | 514.1354 | -2750 | -200 | -2435.8646 | 60.9% | 69.92% | 95% | 0% | 1763 | -111
[5 empty] | 2019-04-25 | 2 | 2736 | 1605 | -106 | 0 | 0 | 1711 | 559.6867 | 559.6867 | 559.6867 | 1783.0173 | 780 | 200 | 2763.0173 | 69.08% | 95% | 0% | -121.2815 | 438.4053 | -2750 | -200 | -2511.5947 | 62.79% | 69.92% | 95% | 0% | 1711 | -106
[5 empty] | 2019-04-25 | 3 | 2736.5 | 1585 | -106 | 0 | 0 | 1691 | 528.3594 | 528.3594 | 528.3594 | 1783.0173 | 780 | 200 | 2763.0173 | 69.08% | 95% | 0% | -121.2815 | 407.078 | -2750 | -200 | -2542.922 | 63.57% | 69.91% | 95% | 0% | 1691 | -106
[5 empty] | 2019-04-25 | 4 | 2737 | 1593 | -105 | 0 | 0 | 1698 | 539.324 | 539.324 | 539.324 | 1783.0173 | 780 | 200 | 2763.0173 | 69.08% | 95% | 0% | -120.1373 | 419.1867 | -2750 | -200 | -2530.8133 | 63.27% | 69.91% | 95% | 0% | 1698 | -105
[5 empty] | 2019-04-25 | 5 | 2737.5 | 1572 | -105 | 0 | 0 | 1677 | 506.4303 | 506.4303 | 506.4303 | 1783.0173 | 780 | 200 | 2763.0173 | 69.08% | 95% | 0% | -120.1373 | 386.293 | -2750 | -200 | -2563.707 | 64.09% | 69.91% | 95% | 0% | 1677 | -105
[5 empty] | 2019-04-25 | 6 | 2738 | 1540 | -105 | 0 | 0 | 1645 | 456.3067 | 456.3067 | 456.3067 | 1783.0173 | 780 | 200 | 2763.0173 | 69.08% | 95% | 0% | -120.1373 | 336.1694 | -2750 | -200 | -2613.8306 | 65.35% | 69.9% | 95% | 0% | 1645 | -105
[5 empty] | 2019-04-25 | 7 | 2738.5 | 1523 | -105 | 0 | 0 | 1628 | 429.6785 | 429.6785 | 429.6785 | 1783.0173 | 780 | 200 | 2763.0173 | 69.08% | 95% | 0% | -120.1373 | 309.5412 | -2750 | -200 | -2640.4588 | 66.01% | 69.89% | 95% | 0% | 1628 | -105
[5 empty] | 2019-04-25 | 8 | 2739 | 1517 | -104 | 0 | 0 | 1621 | 418.7139 | 418.7139 | 418.7139 | 1783.0173 | 780 | 200 | 2763.0173 | 69.08% | 95% | 0% | -118.9931 | 299.7208 | -2750 | -200 | -2650.2792 | 66.26% | 69.89% | 95% | 0% | 1621 | -104
[5 empty] | 2019-04-25 | 9 | 2739.5 | 1517 | -103 | 0 | 0 | 1620 | 417.1476 | 417.1476 | 417.1476 | 1783.0173 | 780 | 200 | 2763.0173 | 69.08% | 95% | 0% | -117.849 | 299.2986 | -2750 | -200 | -2650.7014 | 66.27% | 69.89% | 95% | 0% | 1620 | -103
[5 empty] | 2019-04-25 | 10 | 2740 | 1533 | -101 | 0 | 0 | 1634 | 439.0767 | 439.0767 | 439.0767 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -115.5606 | 323.516 | -2750 | -200 | -2626.484 | 65.66% | 69.89% | 95% | 0% | 1634 | -101
[5 empty] | 2019-04-25 | 11 | 2740.5 | 1590 | -103 | 0 | 0 | 1693 | 531.4922 | 531.4922 | 531.4922 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -117.849 | 413.6432 | -2750 | -200 | -2536.3568 | 63.41% | 69.88% | 95% | 0% | 1693 | -103
[5 empty] | 2019-04-25 | 12 | 2741 | 1657 | -104 | 1 | 0 | 1761 | 638.0049 | 638.0049 | 638.0049 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -118.9931 | 519.0118 | -3550 | -400 | -3430.9882 | 85.77% | 69.88% | 95% | 0% | 1761 | -104
[5 empty] | 2019-04-25 | 13 | 2741.5 | 1826 | -109 | 1 | 0 | 1935 | 910.5523 | 910.5523 | 910.5523 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -124.714 | 785.8384 | -3550 | -400 | -3164.1616 | 79.1% | 69.88% | 95% | 0% | 1935 | -109
[5 empty] | 2019-04-25 | 14 | 2742 | 1983 | -125 | 1 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -143.0206 | 1038.5128 | -3550 | -400 | -2911.4872 | 72.79% | 69.87% | 95% | 0% | 2108 | -125
[5 empty] | 2019-04-25 | 15 | 2742.5 | 2171 | -156 | 1 | 0 | 2327 | 1524.5672 | 1524.5672 | 1524.5672 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -178.4897 | 1346.0775 | -3550 | -400 | -2603.9225 | 65.1% | 69.87% | 95% | 0% | 2327 | -156
[5 empty] | 2019-04-25 | 16 | 2743 | 2223 | -190 | 1 | 0 | 2413 | 1659.2745 | 1659.2745 | 1659.2745 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -217.3913 | 1441.8832 | -3550 | -400 | -2508.1168 | 62.7% | 69.86% | 95% | 0% | 2413 | -190
[5 empty] | 2019-04-25 | 17 | 2743.5 | 2249 | -230 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -263.1579 | 1499.4967 | -3550 | -400 | -2450.5033 | 61.26% | 69.86% | 95% | 0% | 2479 | -230
[5 empty] | 2019-04-25 | 18 | 2744 | 2204 | -269 | 1 | 0 | 2473 | 1753.2564 | 1753.2564 | 1753.2564 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -307.7803 | 1445.4761 | -3550 | -400 | -2504.5239 | 62.61% | 69.86% | 95% | 0% | 2473 | -269
[5 empty] | 2019-04-25 | 19 | 2744.5 | 2191 | -305 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -348.9703 | 1440.3125 | -3550 | -400 | -2509.6875 | 62.74% | 69.86% | 95% | 0% | 2496 | -305
[5 empty] | 2019-04-25 | 20 | 2745 | 2108 | -358 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -409.611 | 1332.6809 | -3550 | -400 | -2617.3191 | 65.43% | 69.86% | 95% | 0% | 2466 | -358
[5 empty] | 2019-04-25 | 21 | 2745.5 | 2021 | -418 | 1 | 0 | 2439 | 1700 | 1700 | 1700 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -478.2609 | 1221.7391 | -3550 | -400 | -2728.2609 | 68.21% | 69.85% | 95% | 0% | 2439 | -418
[5 empty] | 2019-04-25 | 22 | 2746 | 1949 | -461 | 1 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -527.46 | 1127.1155 | -3550 | -400 | -2822.8845 | 70.57% | 69.84% | 95% | 0% | 2410 | -461
[5 empty] | 2019-04-25 | 23 | 2746.5 | 1907 | -476 | 1 | 0 | 2383 | 1612.2836 | 1612.2836 | 1612.2836 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -544.6224 | 1067.6612 | -3550 | -400 | -2882.3388 | 72.06% | 69.84% | 95% | 0% | 2383 | -476
[5 empty] | 2019-04-25 | 24 | 2747 | 1817 | -521 | 1 | 0 | 2338 | 1541.7972 | 1541.7972 | 1541.7972 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -596.1098 | 945.6874 | -3550 | -400 | -3004.3126 | 75.11% | 69.84% | 95% | 0% | 2338 | -521
[5 empty] | 2019-04-25 | 25 | 2747.5 | 1845 | -496 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 1781.4509 | 780 | 200 | 2761.4509 | 69.04% | 95% | 0% | -567.5057 | 978.9906 | -3550 | -400 | -2971.0094 | 74.28% | 69.83% | 95% | 0% | 2341 | -496
[5 empty] | 2019-04-25 | 26 | 2748 | 1768 | -558 | 1 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 1779.8846 | 780 | 200 | 2759.8846 | 69% | 95% | 0% | -638.4439 | 884.5569 | -3550 | -400 | -3065.4431 | 76.64% | 69.82% | 95% | 0% | 2326 | -558
[5 empty] | 2019-04-25 | 27 | 2748.5 | 1690 | -580 | 1 | 0 | 2270 | 1435.2844 | 1435.2844 | 1435.2844 | 1779.8846 | 780 | 200 | 2759.8846 | 69% | 95% | 0% | -663.6156 | 771.6689 | -3550 | -400 | -3178.3311 | 79.46% | 69.82% | 95% | 0% | 2270 | -580
[5 empty] | 2019-04-25 | 28 | 2749 | 1637 | -598 | 1 | 0 | 2235 | 1380.4617 | 1380.4617 | 1380.4617 | 1779.8846 | 780 | 200 | 2759.8846 | 69% | 95% | 0% | -684.2105 | 696.2511 | -3550 | -400 | -3253.7489 | 81.34% | 69.82% | 95% | 0% | 2235 | -598
[5 empty] | 2019-04-25 | 29 | 2749.5 | 1637 | -591 | 1 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 1779.8846 | 780 | 200 | 2759.8846 | 69% | 95% | 0% | -676.2014 | 693.2957 | -3550 | -400 | -3256.7043 | 81.42% | 69.81% | 95% | 0% | 2228 | -591
[5 empty] | 2019-04-25 | 30 | 2750 | 1662 | -549 | 1 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 1779.8846 | 780 | 200 | 2759.8846 | 69% | 95% | 0% | -628.1465 | 714.7225 | -3550 | -400 | -3235.2775 | 80.88% | 69.8% | 95% | 0% | 2211 | -549
[5 empty] | 2019-04-25 | 31 | 2750.5 | 1712 | -504 | 1 | 0 | 2216 | 1350.7007 | 1350.7007 | 1350.7007 | 1779.8846 | 780 | 200 | 2759.8846 | 69% | 95% | 0% | -576.659 | 774.0417 | -3550 | -400 | -3175.9583 | 79.4% | 69.78% | 95% | 0% | 2216 | -504
[5 empty] | 2019-04-25 | 32 | 2751 | 1812 | -455 | 1 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 1779.8846 | 780 | 200 | 2759.8846 | 69% | 95% | 0% | -520.595 | 909.9904 | -3550 | -400 | -3040.0096 | 76% | 69.78% | 95% | 0% | 2267 | -455
[5 empty] | 2019-04-25 | 33 | 2751.5 | 1920 | -427 | 1 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 1779.8846 | 780 | 200 | 2759.8846 | 69% | 95% | 0% | -488.5584 | 1067.3361 | -3550 | -400 | -2882.6639 | 72.07% | 69.78% | 95% | 0% | 2347 | -427
[5 empty] | 2019-04-25 | 34 | 2752 | 2038 | -394 | 1 | 0 | 2432 | 1689.0354 | 1689.0354 | 1689.0354 | 1779.8846 | 780 | 200 | 2759.8846 | 69% | 95% | 0% | -450.8009 | 1238.2345 | -3550 | -400 | -2711.7655 | 67.79% | 69.77% | 95% | 0% | 2432 | -394
[5 empty] | 2019-04-25 | 35 | 2752.5 | 2135 | -355 | 1 | 0 | 2490 | 1779.8846 | 1779.8846 | 1779.8846 | 1779.8846 | 780 | 200 | 2759.8846 | 69% | 95% | 0% | -406.1785 | 1373.7061 | -3550 | -400 | -2576.2939 | 64.41% | 69.77% | 95% | 0% | 2490 | -355
[5 empty] | 2019-04-25 | 36 | 2753 | 2193 | -320 | 1 | 0 | 2513 | 1815.911 | 1815.911 | 1815.911 | 1779.8846 | 780 | 200 | 2759.8846 | 69% | 95% | 0% | -366.1327 | 1449.7782 | -3550 | -400 | -2500.2218 | 62.51% | 69.77% | 95% | 0% | 2513 | -320
[5 empty] | 2019-04-25 | 37 | 2753.5 | 2251 | -270 | 1 | 0 | 2521 | 1828.4419 | 1828.4419 | 1828.4419 | 1779.8846 | 780 | 200 | 2759.8846 | 69% | 95% | 0% | -308.9245 | 1519.5174 | -3550 | -400 | -2430.4826 | 60.76% | 69.77% | 95% | 0% | 2521 | -270
[5 empty] | 2019-04-25 | 38 | 2754 | 2328 | -213 | 1 | 0 | 2541 | 1859.7692 | 1859.7692 | 1859.7692 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -243.7071 | 1616.0621 | -3550 | -400 | -2333.9379 | 58.35% | 69.77% | 95% | 0% | 2541 | -213
[5 empty] | 2019-04-25 | 39 | 2754.5 | 2394 | -161 | 1 | 0 | 2555 | 1881.6983 | 1881.6983 | 1881.6983 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -184.2105 | 1697.4877 | -3550 | -400 | -2252.5123 | 56.31% | 69.76% | 95% | 0% | 2555 | -161
[5 empty] | 2019-04-25 | 40 | 2755 | 2451 | -121 | 1 | 0 | 2572 | 1908.3265 | 1908.3265 | 1908.3265 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -138.4439 | 1769.8825 | -3550 | -400 | -2180.1175 | 54.5% | 69.76% | 95% | 0% | 2572 | -121
[5 empty] | 2019-04-25 | 41 | 2755.5 | 2470 | -107 | 1 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -122.4256 | 1793.7327 | -3550 | -400 | -2156.2673 | 53.91% | 69.76% | 95% | 0% | 2577 | -107
[5 empty] | 2019-04-25 | 42 | 2756 | 2484 | -106 | 1 | 0 | 2590 | 1936.521 | 1936.521 | 1936.521 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -121.2815 | 1815.2396 | -3550 | -400 | -2134.7604 | 53.37% | 69.76% | 95% | 0% | 2590 | -106
[5 empty] | 2019-04-25 | 43 | 2756.5 | 2431 | -106 | 1 | 0 | 2537 | 1853.5037 | 1853.5037 | 1853.5037 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -121.2815 | 1732.2222 | -3550 | -400 | -2217.7778 | 55.44% | 69.75% | 95% | 0% | 2537 | -106
[5 empty] | 2019-04-25 | 44 | 2757 | 2313 | -106 | 0 | 0 | 2419 | 1668.6727 | 1668.6727 | 1668.6727 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -121.2815 | 1547.3912 | -2750 | -200 | -1402.6088 | 35.07% | 69.75% | 95% | 0% | 2419 | -106
[5 empty] | 2019-04-25 | 45 | 2757.5 | 2175 | -107 | 0 | 0 | 2282 | 1454.0808 | 1454.0808 | 1454.0808 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -122.4256 | 1331.6552 | -2750 | -200 | -1618.3448 | 40.46% | 69.75% | 95% | 0% | 2282 | -107
[5 empty] | 2019-04-25 | 46 | 2758 | 2034 | -107 | 0 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -122.4256 | 1110.7978 | -2750 | -200 | -1839.2022 | 45.98% | 69.74% | 95% | 0% | 2141 | -107
[5 empty] | 2019-04-25 | 47 | 2758.5 | 1881 | -107 | 0 | 0 | 1988 | 993.5697 | 993.5697 | 993.5697 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -122.4256 | 871.144 | -2750 | -200 | -2078.856 | 51.97% | 69.74% | 95% | 0% | 1988 | -107
[5 empty] | 2019-04-25 | 48 | 2759 | 1765 | -106 | 0 | 0 | 1871 | 810.305 | 810.305 | 810.305 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -121.2815 | 689.0236 | -2750 | -200 | -2260.9764 | 56.52% | 69.74% | 95% | 0% | 1871 | -106
[5 empty] | 2019-04-26 | 1 | 2759.5 | 1673 | -104 | 0 | 0 | 1777 | 663.0668 | 663.0668 | 663.0668 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -118.9931 | 544.0736 | -2750 | -200 | -2405.9264 | 60.15% | 69.74% | 95% | 0% | 1777 | -104
[5 empty] | 2019-04-26 | 2 | 2760 | 1614 | -101 | 0 | 0 | 1715 | 565.9522 | 565.9522 | 565.9522 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -115.5606 | 450.3915 | -2750 | -200 | -2499.6085 | 62.49% | 69.73% | 95% | 0% | 1715 | -101
[5 empty] | 2019-04-26 | 3 | 2760.5 | 1593 | -101 | 0 | 0 | 1694 | 533.0585 | 533.0585 | 533.0585 | 1778.3182 | 780 | 200 | 2758.3182 | 68.96% | 95% | 0% | -115.5606 | 417.4979 | -2750 | -200 | -2532.5021 | 63.31% | 69.72% | 95% | 0% | 1694 | -101
[5 empty] | 2019-04-26 | 4 | 2761 | 1599 | -102 | 0 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 1776.7519 | 780 | 200 | 2756.7519 | 68.92% | 95% | 0% | -116.7048 | 427.3183 | -2750 | -200 | -2522.6817 | 63.07% | 69.72% | 95% | 0% | 1701 | -102
[5 empty] | 2019-04-26 | 5 | 2761.5 | 1591 | -102 | 0 | 0 | 1693 | 531.4922 | 531.4922 | 531.4922 | 1776.7519 | 780 | 200 | 2756.7519 | 68.92% | 95% | 0% | -116.7048 | 414.7874 | -2750 | -200 | -2535.2126 | 63.38% | 69.72% | 95% | 0% | 1693 | -102
[5 empty] | 2019-04-26 | 6 | 2762 | 1560 | -102 | 0 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 1776.7519 | 780 | 200 | 2756.7519 | 68.92% | 95% | 0% | -116.7048 | 366.2301 | -2750 | -200 | -2583.7699 | 64.59% | 69.72% | 95% | 0% | 1662 | -102
[5 empty] | 2019-04-26 | 7 | 2762.5 | 1540 | -103 | 0 | 0 | 1643 | 453.1739 | 453.1739 | 453.1739 | 1776.7519 | 780 | 200 | 2756.7519 | 68.92% | 95% | 0% | -117.849 | 335.325 | -2750 | -200 | -2614.675 | 65.37% | 69.71% | 95% | 0% | 1643 | -103
[5 empty] | 2019-04-26 | 8 | 2763 | 1530 | -103 | 0 | 0 | 1633 | 437.5103 | 437.5103 | 437.5103 | 1776.7519 | 780 | 200 | 2756.7519 | 68.92% | 95% | 0% | -117.849 | 319.6613 | -2750 | -200 | -2630.3387 | 65.76% | 69.71% | 95% | 0% | 1633 | -103
[5 empty] | 2019-04-26 | 9 | 2763.5 | 1530 | -104 | 0 | 0 | 1634 | 439.0767 | 439.0767 | 439.0767 | 1776.7519 | 780 | 200 | 2756.7519 | 68.92% | 95% | 0% | -118.9931 | 320.0835 | -2750 | -200 | -2629.9165 | 65.75% | 69.71% | 95% | 0% | 1634 | -104
[5 empty] | 2019-04-26 | 10 | 2764 | 1540 | -104 | 0 | 0 | 1644 | 454.7403 | 454.7403 | 454.7403 | 1776.7519 | 780 | 200 | 2756.7519 | 68.92% | 95% | 0% | -118.9931 | 335.7472 | -2750 | -200 | -2614.2528 | 65.36% | 69.7% | 95% | 0% | 1644 | -104
[5 empty] | 2019-04-26 | 11 | 2764.5 | 1604 | -105 | 0 | 0 | 1709 | 556.554 | 556.554 | 556.554 | 1776.7519 | 780 | 200 | 2756.7519 | 68.92% | 95% | 0% | -120.1373 | 436.4167 | -2750 | -200 | -2513.5833 | 62.84% | 69.7% | 95% | 0% | 1709 | -105
[5 empty] | 2019-04-26 | 12 | 2765 | 1649 | -107 | 0 | 0 | 1756 | 630.1731 | 630.1731 | 630.1731 | 1776.7519 | 780 | 200 | 2756.7519 | 68.92% | 95% | 0% | -122.4256 | 507.7475 | -2750 | -200 | -2442.2525 | 61.06% | 69.69% | 95% | 0% | 1756 | -107
[5 empty] | 2019-04-26 | 13 | 2765.5 | 1812 | -123 | 1 | 0 | 1935 | 910.5523 | 910.5523 | 910.5523 | 1776.7519 | 780 | 200 | 2756.7519 | 68.92% | 95% | 0% | -140.7323 | 769.8201 | -3550 | -400 | -3180.1799 | 79.5% | 69.69% | 95% | 0% | 1935 | -123
[5 empty] | 2019-04-26 | 14 | 2766 | 1949 | -164 | 1 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 1776.7519 | 780 | 200 | 2756.7519 | 68.92% | 95% | 0% | -187.643 | 1001.7222 | -3550 | -400 | -2948.2778 | 73.71% | 69.68% | 95% | 0% | 2113 | -164
[5 empty] | 2019-04-26 | 15 | 2766.5 | 2097 | -214 | 1 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 1775.1855 | 780 | 200 | 2755.1855 | 68.88% | 95% | 0% | -244.8513 | 1254.6541 | -3550 | -400 | -2695.3459 | 67.38% | 69.68% | 95% | 0% | 2311 | -214
[5 empty] | 2019-04-26 | 16 | 2767 | 2130 | -274 | 1 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 1775.1855 | 780 | 200 | 2755.1855 | 68.88% | 95% | 0% | -313.5011 | 1331.6761 | -3550 | -400 | -2618.3239 | 65.46% | 69.68% | 95% | 0% | 2404 | -274
[5 empty] | 2019-04-26 | 17 | 2767.5 | 2125 | -328 | 1 | 0 | 2453 | 1721.9291 | 1721.9291 | 1721.9291 | 1775.1855 | 780 | 200 | 2755.1855 | 68.88% | 95% | 0% | -375.286 | 1346.6431 | -3550 | -400 | -2603.3569 | 65.08% | 69.67% | 95% | 0% | 2453 | -328
[5 empty] | 2019-04-26 | 18 | 2768 | 2027 | -391 | 1 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 1775.1855 | 780 | 200 | 2755.1855 | 68.88% | 95% | 0% | -447.3684 | 1219.7379 | -3550 | -400 | -2730.2621 | 68.26% | 69.67% | 95% | 0% | 2418 | -391
[5 empty] | 2019-04-26 | 19 | 2768.5 | 1939 | -457 | 1 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 1775.1855 | 780 | 200 | 2755.1855 | 68.88% | 95% | 0% | -522.8833 | 1109.763 | -3550 | -400 | -2840.237 | 71.01% | 69.66% | 95% | 0% | 2396 | -457
[5 empty] | 2019-04-26 | 20 | 2769 | 1857 | -506 | 1 | 0 | 2363 | 1580.9563 | 1580.9563 | 1580.9563 | 1775.1855 | 780 | 200 | 2755.1855 | 68.88% | 95% | 0% | -578.9474 | 1002.0089 | -3550 | -400 | -2947.9911 | 73.7% | 69.66% | 95% | 0% | 2363 | -506
[5 empty] | 2019-04-26 | 21 | 2769.5 | 1790 | -528 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 1775.1855 | 780 | 200 | 2755.1855 | 68.88% | 95% | 0% | -604.119 | 906.3509 | -3550 | -400 | -3043.6491 | 76.09% | 69.66% | 95% | 0% | 2318 | -528
[5 empty] | 2019-04-26 | 22 | 2770 | 1753 | -533 | 1 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 1775.1855 | 780 | 200 | 2755.1855 | 68.88% | 95% | 0% | -609.8398 | 850.5064 | -3550 | -400 | -3099.4936 | 77.49% | 69.65% | 95% | 0% | 2286 | -533
[5 empty] | 2019-04-26 | 23 | 2770.5 | 1704 | -576 | 1 | 0 | 2280 | 1450.9481 | 1450.9481 | 1450.9481 | 1775.1855 | 780 | 200 | 2755.1855 | 68.88% | 95% | 0% | -659.0389 | 791.9092 | -3550 | -400 | -3158.0908 | 78.95% | 69.63% | 95% | 0% | 2280 | -576
[5 empty] | 2019-04-26 | 24 | 2771 | 1664 | -601 | 1 | 0 | 2265 | 1427.4526 | 1427.4526 | 1427.4526 | 1775.1855 | 780 | 200 | 2755.1855 | 68.88% | 95% | 0% | -687.643 | 739.8096 | -3550 | -400 | -3210.1904 | 80.25% | 69.63% | 95% | 0% | 2265 | -601
[5 empty] | 2019-04-26 | 25 | 2771.5 | 1675 | -584 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 1775.1855 | 780 | 200 | 2755.1855 | 68.88% | 95% | 0% | -668.1922 | 749.8622 | -3550 | -400 | -3200.1378 | 80% | 69.63% | 95% | 0% | 2259 | -584
[5 empty] | 2019-04-26 | 26 | 2772 | 1695 | -551 | 1 | 0 | 2246 | 1397.6917 | 1397.6917 | 1397.6917 | 1775.1855 | 780 | 200 | 2755.1855 | 68.88% | 95% | 0% | -630.4348 | 767.2569 | -3550 | -400 | -3182.7431 | 79.57% | 69.63% | 95% | 0% | 2246 | -551
[5 empty] | 2019-04-26 | 27 | 2772.5 | 1698 | -536 | 1 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 1773.6191 | 780 | 200 | 2753.6191 | 68.84% | 95% | 0% | -613.2723 | 765.623 | -3550 | -400 | -3184.377 | 79.61% | 69.63% | 95% | 0% | 2234 | -536
[5 empty] | 2019-04-26 | 28 | 2773 | 1679 | -528 | 1 | 0 | 2207 | 1336.6035 | 1336.6035 | 1336.6035 | 1773.6191 | 780 | 200 | 2753.6191 | 68.84% | 95% | 0% | -604.119 | 732.4845 | -3550 | -400 | -3217.5155 | 80.44% | 69.63% | 95% | 0% | 2207 | -528
[5 empty] | 2019-04-26 | 29 | 2773.5 | 1662 | -532 | 1 | 0 | 2194 | 1316.2407 | 1316.2407 | 1316.2407 | 1773.6191 | 780 | 200 | 2753.6191 | 68.84% | 95% | 0% | -608.6957 | 707.5451 | -3550 | -400 | -3242.4549 | 81.06% | 69.62% | 95% | 0% | 2194 | -532
[5 empty] | 2019-04-26 | 30 | 2774 | 1672 | -498 | 1 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 1773.6191 | 780 | 200 | 2753.6191 | 68.84% | 95% | 0% | -569.7941 | 708.8539 | -3550 | -400 | -3241.1461 | 81.03% | 69.61% | 95% | 0% | 2170 | -498
[5 empty] | 2019-04-26 | 31 | 2774.5 | 1675 | -480 | 1 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 1773.6191 | 780 | 200 | 2753.6191 | 68.84% | 95% | 0% | -549.1991 | 705.9534 | -3550 | -400 | -3244.0466 | 81.1% | 69.61% | 95% | 0% | 2155 | -480
[5 empty] | 2019-04-26 | 32 | 2775 | 1740 | -445 | 1 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 1773.6191 | 780 | 200 | 2753.6191 | 68.84% | 95% | 0% | -509.1533 | 792.9901 | -3550 | -400 | -3157.0099 | 78.93% | 69.61% | 95% | 0% | 2185 | -445
[5 empty] | 2019-04-26 | 33 | 2775.5 | 1875 | -387 | 1 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 1773.6191 | 780 | 200 | 2753.6191 | 68.84% | 95% | 0% | -442.7918 | 979.9617 | -3550 | -400 | -2970.0383 | 74.25% | 69.61% | 95% | 0% | 2262 | -387
[5 empty] | 2019-04-26 | 34 | 2776 | 1980 | -357 | 1 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 1773.6191 | 780 | 200 | 2753.6191 | 68.84% | 95% | 0% | -408.4668 | 1131.764 | -3550 | -400 | -2818.236 | 70.46% | 69.59% | 95% | 0% | 2337 | -357
[5 empty] | 2019-04-26 | 35 | 2776.5 | 2109 | -298 | 1 | 0 | 2407 | 1649.8763 | 1649.8763 | 1649.8763 | 1773.6191 | 780 | 200 | 2753.6191 | 68.84% | 95% | 0% | -340.9611 | 1308.9152 | -3550 | -400 | -2641.0848 | 66.03% | 69.59% | 95% | 0% | 2407 | -298
[5 empty] | 2019-04-26 | 36 | 2777 | 2164 | -280 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 1772.0528 | 780 | 200 | 2752.0528 | 68.8% | 95% | 0% | -320.3661 | 1387.4657 | -3550 | -400 | -2562.5343 | 64.06% | 69.58% | 95% | 0% | 2444 | -280
[5 empty] | 2019-04-26 | 37 | 2777.5 | 2238 | -234 | 1 | 0 | 2472 | 1751.69 | 1751.69 | 1751.69 | 1772.0528 | 780 | 200 | 2752.0528 | 68.8% | 95% | 0% | -267.7346 | 1483.9555 | -3550 | -400 | -2466.0445 | 61.65% | 69.57% | 95% | 0% | 2472 | -234
[5 empty] | 2019-04-26 | 38 | 2778 | 2268 | -203 | 1 | 0 | 2471 | 1750.1237 | 1750.1237 | 1750.1237 | 1772.0528 | 780 | 200 | 2752.0528 | 68.8% | 95% | 0% | -232.2654 | 1517.8582 | -3550 | -400 | -2432.1418 | 60.8% | 69.57% | 95% | 0% | 2471 | -203
[5 empty] | 2019-04-26 | 39 | 2778.5 | 2266 | -184 | 1 | 0 | 2450 | 1717.23 | 1717.23 | 1717.23 | 1772.0528 | 780 | 200 | 2752.0528 | 68.8% | 95% | 0% | -210.5263 | 1506.7037 | -3550 | -400 | -2443.2963 | 61.08% | 69.57% | 95% | 0% | 2450 | -184
[5 empty] | 2019-04-26 | 40 | 2779 | 2277 | -165 | 1 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 1772.0528 | 780 | 200 | 2752.0528 | 68.8% | 95% | 0% | -188.7872 | 1515.9119 | -3550 | -400 | -2434.0881 | 60.85% | 69.57% | 95% | 0% | 2442 | -165
[5 empty] | 2019-04-26 | 41 | 2779.5 | 2264 | -161 | 1 | 0 | 2425 | 1678.0709 | 1678.0709 | 1678.0709 | 1772.0528 | 780 | 200 | 2752.0528 | 68.8% | 95% | 0% | -184.2105 | 1493.8604 | -3550 | -400 | -2456.1396 | 61.4% | 69.57% | 95% | 0% | 2425 | -161
[5 empty] | 2019-04-26 | 42 | 2780 | 2258 | -162 | 1 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 1772.0528 | 780 | 200 | 2752.0528 | 68.8% | 95% | 0% | -185.3547 | 1484.8844 | -3550 | -400 | -2465.1156 | 61.63% | 69.56% | 95% | 0% | 2420 | -162
[5 empty] | 2019-04-26 | 43 | 2780.5 | 2189 | -163 | 1 | 0 | 2352 | 1563.7263 | 1563.7263 | 1563.7263 | 1772.0528 | 780 | 200 | 2752.0528 | 68.8% | 95% | 0% | -186.4989 | 1377.2274 | -3550 | -400 | -2572.7726 | 64.32% | 69.56% | 95% | 0% | 2352 | -163
[5 empty] | 2019-04-26 | 44 | 2781 | 2062 | -164 | 0 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 1772.0528 | 780 | 200 | 2752.0528 | 68.8% | 95% | 0% | -187.643 | 1178.7214 | -2750 | -200 | -1771.2786 | 44.28% | 69.56% | 95% | 0% | 2226 | -164
[5 empty] | 2019-04-26 | 45 | 2781.5 | 1929 | -161 | 0 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 1770.4864 | 780 | 200 | 2750.4864 | 68.76% | 95% | 0% | -184.2105 | 969.1283 | -2750 | -200 | -1980.8717 | 49.52% | 69.56% | 95% | 0% | 2090 | -161
[5 empty] | 2019-04-26 | 46 | 2782 | 1801 | -159 | 0 | 0 | 1960 | 949.7115 | 949.7115 | 949.7115 | 1770.4864 | 780 | 200 | 2750.4864 | 68.76% | 95% | 0% | -181.9222 | 767.7893 | -2750 | -200 | -2182.2107 | 54.56% | 69.56% | 95% | 0% | 1960 | -159
[5 empty] | 2019-04-26 | 47 | 2782.5 | 1670 | -160 | 0 | 0 | 1830 | 746.0841 | 746.0841 | 746.0841 | 1770.4864 | 780 | 200 | 2750.4864 | 68.76% | 95% | 0% | -183.0664 | 563.0177 | -2750 | -200 | -2386.9823 | 59.67% | 69.56% | 95% | 0% | 1830 | -160
[5 empty] | 2019-04-26 | 48 | 2783 | 1550 | -162 | 0 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 1770.4864 | 780 | 200 | 2750.4864 | 68.76% | 95% | 0% | -185.3547 | 375.8984 | -2750 | -200 | -2574.1016 | 64.35% | 69.55% | 95% | 0% | 1712 | -162
[5 empty] | 2019-04-27 | 1 | 2783.5 | 1469 | -166 | 0 | 0 | 1635 | 440.643 | 440.643 | 440.643 | 1770.4864 | 780 | 200 | 2750.4864 | 68.76% | 95% | 0% | -189.9314 | 250.7117 | -2750 | -200 | -2699.2883 | 67.48% | 69.55% | 95% | 0% | 1635 | -166
[5 empty] | 2019-04-27 | 2 | 2784 | 1399 | -171 | 0 | 0 | 1570 | 338.8293 | 338.8293 | 338.8293 | 1770.4864 | 780 | 200 | 2750.4864 | 68.76% | 95% | 0% | -195.6522 | 143.1772 | -2750 | -200 | -2806.8228 | 70.17% | 69.55% | 95% | 0% | 1570 | -171
[5 empty] | 2019-04-27 | 3 | 2784.5 | 1394 | -164 | 0 | 0 | 1558 | 320.033 | 320.033 | 320.033 | 1770.4864 | 780 | 200 | 2750.4864 | 68.76% | 95% | 0% | -187.643 | 132.39 | -2750 | -200 | -2817.61 | 70.44% | 69.55% | 95% | 0% | 1558 | -164
[5 empty] | 2019-04-27 | 4 | 2785 | 1415 | -158 | 0 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 1770.4864 | 780 | 200 | 2750.4864 | 68.76% | 95% | 0% | -180.778 | 162.7504 | -2750 | -200 | -2787.2496 | 69.68% | 69.54% | 95% | 0% | 1573 | -158
[5 empty] | 2019-04-27 | 5 | 2785.5 | 1398 | -155 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 1770.4864 | 780 | 200 | 2750.4864 | 68.76% | 95% | 0% | -177.3455 | 134.8556 | -2750 | -200 | -2815.1444 | 70.38% | 69.54% | 95% | 0% | 1553 | -155
[5 empty] | 2019-04-27 | 6 | 2786 | 1381 | -151 | 0 | 0 | 1532 | 279.3075 | 279.3075 | 279.3075 | 1768.92 | 780 | 200 | 2748.92 | 68.72% | 95% | 0% | -172.7689 | 106.5386 | -2750 | -200 | -2843.4614 | 71.09% | 69.54% | 95% | 0% | 1532 | -151
[5 empty] | 2019-04-27 | 7 | 2786.5 | 1356 | -149 | 0 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 1768.92 | 780 | 200 | 2748.92 | 68.72% | 95% | 0% | -170.4805 | 66.5351 | -2750 | -200 | -2883.4649 | 72.09% | 69.54% | 95% | 0% | 1505 | -149
[5 empty] | 2019-04-27 | 8 | 2787 | 1341 | -147 | 0 | 0 | 1488 | 210.3875 | 210.3875 | 210.3875 | 1768.92 | 780 | 200 | 2748.92 | 68.72% | 95% | 0% | -168.1922 | 42.1952 | -2750 | -200 | -2907.8048 | 72.7% | 69.54% | 95% | 0% | 1488 | -147
[5 empty] | 2019-04-27 | 9 | 2787.5 | 1331 | -147 | 0 | 0 | 1478 | 194.7238 | 194.7238 | 194.7238 | 1768.92 | 780 | 200 | 2748.92 | 68.72% | 95% | 0% | -168.1922 | 26.5316 | -2750 | -200 | -2923.4684 | 73.09% | 69.53% | 95% | 0% | 1478 | -147
[5 empty] | 2019-04-27 | 10 | 2788 | 1330 | -146 | 0 | 0 | 1476 | 191.5911 | 191.5911 | 191.5911 | 1768.92 | 780 | 200 | 2748.92 | 68.72% | 95% | 0% | -167.0481 | 24.543 | -2750 | -200 | -2925.457 | 73.14% | 69.53% | 95% | 0% | 1476 | -146
[5 empty] | 2019-04-27 | 11 | 2788.5 | 1360 | -143 | 0 | 0 | 1503 | 233.8829 | 233.8829 | 233.8829 | 1768.92 | 780 | 200 | 2748.92 | 68.72% | 95% | 0% | -163.6156 | 70.2674 | -2750 | -200 | -2879.7326 | 71.99% | 69.52% | 95% | 0% | 1503 | -143
[5 empty] | 2019-04-27 | 12 | 2789 | 1368 | -141 | 0 | 0 | 1509 | 243.2811 | 243.2811 | 243.2811 | 1768.92 | 780 | 200 | 2748.92 | 68.72% | 95% | 0% | -161.3272 | 81.9539 | -2750 | -200 | -2868.0461 | 71.7% | 69.52% | 95% | 0% | 1509 | -141
[5 empty] | 2019-04-27 | 13 | 2789.5 | 1447 | -146 | 0 | 0 | 1593 | 374.8557 | 374.8557 | 374.8557 | 1768.92 | 780 | 200 | 2748.92 | 68.72% | 95% | 0% | -167.0481 | 207.8077 | -2750 | -200 | -2742.1923 | 68.55% | 69.51% | 95% | 0% | 1593 | -146
[5 empty] | 2019-04-27 | 14 | 2790 | 1512 | -161 | 0 | 0 | 1673 | 500.1649 | 500.1649 | 500.1649 | 1768.92 | 780 | 200 | 2748.92 | 68.72% | 95% | 0% | -184.2105 | 315.9544 | -2750 | -200 | -2634.0456 | 65.85% | 69.51% | 95% | 0% | 1673 | -161
[5 empty] | 2019-04-27 | 15 | 2790.5 | 1622 | -180 | 1 | 0 | 1802 | 702.2259 | 702.2259 | 702.2259 | 1768.92 | 780 | 200 | 2748.92 | 68.72% | 95% | 0% | -205.9497 | 496.2762 | -3550 | -400 | -3453.7238 | 86.34% | 69.5% | 95% | 0% | 1802 | -180
[5 empty] | 2019-04-27 | 16 | 2791 | 1705 | -206 | 1 | 0 | 1911 | 872.9596 | 872.9596 | 872.9596 | 1768.92 | 780 | 200 | 2748.92 | 68.72% | 95% | 0% | -235.6979 | 637.2617 | -3550 | -400 | -3312.7383 | 82.82% | 69.49% | 95% | 0% | 1911 | -206
[5 empty] | 2019-04-27 | 17 | 2791.5 | 1787 | -243 | 1 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 1768.92 | 780 | 200 | 2748.92 | 68.72% | 95% | 0% | -278.032 | 781.3249 | -3550 | -400 | -3168.6751 | 79.22% | 69.49% | 95% | 0% | 2030 | -243
[5 empty] | 2019-04-27 | 18 | 2792 | 1816 | -271 | 1 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 1767.3537 | 780 | 200 | 2747.3537 | 68.68% | 95% | 0% | -310.0686 | 838.5711 | -3550 | -400 | -3111.4289 | 77.79% | 69.49% | 95% | 0% | 2087 | -271
[5 empty] | 2019-04-27 | 19 | 2792.5 | 1803 | -335 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1767.3537 | 780 | 200 | 2747.3537 | 68.68% | 95% | 0% | -383.2952 | 845.2291 | -3550 | -400 | -3104.7709 | 77.62% | 69.48% | 95% | 0% | 2138 | -335
[5 empty] | 2019-04-27 | 20 | 2793 | 1767 | -364 | 1 | 0 | 2131 | 1217.5598 | 1217.5598 | 1217.5598 | 1767.3537 | 780 | 200 | 2747.3537 | 68.68% | 95% | 0% | -416.476 | 801.0838 | -3550 | -400 | -3148.9162 | 78.72% | 69.47% | 95% | 0% | 2131 | -364
[5 empty] | 2019-04-27 | 21 | 2793.5 | 1710 | -406 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1767.3537 | 780 | 200 | 2747.3537 | 68.68% | 95% | 0% | -464.5309 | 729.5334 | -3550 | -400 | -3220.4666 | 80.51% | 69.47% | 95% | 0% | 2116 | -406
[5 empty] | 2019-04-27 | 22 | 2794 | 1669 | -431 | 1 | 0 | 2100 | 1169.0025 | 1169.0025 | 1169.0025 | 1767.3537 | 780 | 200 | 2747.3537 | 68.68% | 95% | 0% | -493.135 | 675.8675 | -3550 | -400 | -3274.1325 | 81.85% | 69.47% | 95% | 0% | 2100 | -431
[5 empty] | 2019-04-27 | 23 | 2794.5 | 1622 | -477 | 1 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 1767.3537 | 780 | 200 | 2747.3537 | 68.68% | 95% | 0% | -545.7666 | 621.6695 | -3550 | -400 | -3328.3305 | 83.21% | 69.47% | 95% | 0% | 2099 | -477
[5 empty] | 2019-04-27 | 24 | 2795 | 1583 | -512 | 1 | 0 | 2095 | 1161.1707 | 1161.1707 | 1161.1707 | 1767.3537 | 780 | 200 | 2747.3537 | 68.68% | 95% | 0% | -585.8124 | 575.3583 | -3550 | -400 | -3374.6417 | 84.37% | 69.47% | 95% | 0% | 2095 | -512
[5 empty] | 2019-04-27 | 25 | 2795.5 | 1549 | -524 | 1 | 0 | 2073 | 1126.7106 | 1126.7106 | 1126.7106 | 1767.3537 | 780 | 200 | 2747.3537 | 68.68% | 95% | 0% | -599.5423 | 527.1683 | -3550 | -400 | -3422.8317 | 85.57% | 69.47% | 95% | 0% | 2073 | -524
[5 empty] | 2019-04-27 | 26 | 2796 | 1476 | -561 | 1 | 0 | 2037 | 1070.3215 | 1070.3215 | 1070.3215 | 1767.3537 | 780 | 200 | 2747.3537 | 68.68% | 95% | 0% | -641.8764 | 428.4451 | -3550 | -400 | -3521.5549 | 88.04% | 69.46% | 95% | 0% | 2037 | -561
[5 empty] | 2019-04-27 | 27 | 2796.5 | 1448 | -552 | 1 | 0 | 2000 | 1012.366 | 1012.366 | 1012.366 | 1767.3537 | 780 | 200 | 2747.3537 | 68.68% | 95% | 0% | -631.5789 | 380.7871 | -3550 | -400 | -3569.2129 | 89.23% | 69.46% | 95% | 0% | 2000 | -552
[5 empty] | 2019-04-27 | 28 | 2797 | 1395 | -546 | 1 | 0 | 1941 | 919.9505 | 919.9505 | 919.9505 | 1765.7873 | 780 | 200 | 2745.7873 | 68.64% | 95% | 0% | -624.714 | 295.2366 | -3550 | -400 | -3654.7634 | 91.37% | 69.46% | 95% | 0% | 1941 | -546
[5 empty] | 2019-04-27 | 29 | 2797.5 | 1367 | -550 | 1 | 0 | 1917 | 882.3578 | 882.3578 | 882.3578 | 1765.7873 | 780 | 200 | 2745.7873 | 68.64% | 95% | 0% | -629.2906 | 253.0672 | -3550 | -400 | -3696.9328 | 92.42% | 69.46% | 95% | 0% | 1917 | -550
[5 empty] | 2019-04-27 | 30 | 2798 | 1366 | -554 | 1 | 0 | 1920 | 887.0569 | 887.0569 | 887.0569 | 1765.7873 | 780 | 200 | 2745.7873 | 68.64% | 95% | 0% | -633.8673 | 253.1896 | -3550 | -400 | -3696.8104 | 92.42% | 69.46% | 95% | 0% | 1920 | -554
[5 empty] | 2019-04-27 | 31 | 2798.5 | 1409 | -520 | 1 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 1765.7873 | 780 | 200 | 2745.7873 | 68.64% | 95% | 0% | -594.9657 | 306.1885 | -3550 | -400 | -3643.8115 | 91.1% | 69.45% | 95% | 0% | 1929 | -520
[5 empty] | 2019-04-27 | 32 | 2799 | 1482 | -475 | 1 | 0 | 1957 | 945.0124 | 945.0124 | 945.0124 | 1765.7873 | 780 | 200 | 2745.7873 | 68.64% | 95% | 0% | -543.4783 | 401.5341 | -3550 | -400 | -3548.4659 | 88.71% | 69.45% | 95% | 0% | 1957 | -475
[5 empty] | 2019-04-27 | 33 | 2799.5 | 1573 | -438 | 1 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 1765.7873 | 780 | 200 | 2745.7873 | 68.64% | 95% | 0% | -501.1442 | 528.4519 | -3550 | -400 | -3421.5481 | 85.54% | 69.44% | 95% | 0% | 2011 | -438
[5 empty] | 2019-04-27 | 34 | 2800 | 1666 | -407 | 1 | 0 | 2073 | 1126.7106 | 1126.7106 | 1126.7106 | 1765.7873 | 780 | 200 | 2745.7873 | 68.64% | 95% | 0% | -465.6751 | 661.0356 | -3550 | -400 | -3288.9644 | 82.22% | 69.44% | 95% | 0% | 2073 | -407
[5 empty] | 2019-04-27 | 35 | 2800.5 | 1786 | -361 | 1 | 0 | 2147 | 1242.6216 | 1242.6216 | 1242.6216 | 1765.7873 | 780 | 200 | 2745.7873 | 68.64% | 95% | 0% | -413.0435 | 829.5781 | -3550 | -400 | -3120.4219 | 78.01% | 69.44% | 95% | 0% | 2147 | -361
[5 empty] | 2019-04-27 | 36 | 2801 | 1890 | -317 | 1 | 0 | 2207 | 1336.6035 | 1336.6035 | 1336.6035 | 1765.7873 | 780 | 200 | 2745.7873 | 68.64% | 95% | 0% | -362.7002 | 973.9032 | -3550 | -400 | -2976.0968 | 74.4% | 69.43% | 95% | 0% | 2207 | -317
[5 empty] | 2019-04-27 | 37 | 2801.5 | 2004 | -266 | 1 | 0 | 2270 | 1435.2844 | 1435.2844 | 1435.2844 | 1765.7873 | 780 | 200 | 2745.7873 | 68.64% | 95% | 0% | -304.3478 | 1130.9366 | -3550 | -400 | -2819.0634 | 70.48% | 69.43% | 95% | 0% | 2270 | -266
[5 empty] | 2019-04-27 | 38 | 2802 | 2073 | -226 | 1 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 1765.7873 | 780 | 200 | 2745.7873 | 68.64% | 95% | 0% | -258.5812 | 1222.1278 | -3550 | -400 | -2727.8722 | 68.2% | 69.42% | 95% | 0% | 2299 | -226
[5 empty] | 2019-04-27 | 39 | 2802.5 | 2115 | -190 | 1 | 0 | 2305 | 1490.1072 | 1490.1072 | 1490.1072 | 1764.2209 | 780 | 200 | 2744.2209 | 68.61% | 95% | 0% | -217.3913 | 1272.7159 | -3550 | -400 | -2677.2841 | 66.93% | 69.42% | 95% | 0% | 2305 | -190
[5 empty] | 2019-04-27 | 40 | 2803 | 2139 | -165 | 1 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 1764.2209 | 780 | 200 | 2744.2209 | 68.61% | 95% | 0% | -188.7872 | 1299.7536 | -3550 | -400 | -2650.2464 | 66.26% | 69.42% | 95% | 0% | 2304 | -165
[5 empty] | 2019-04-27 | 41 | 2803.5 | 2154 | -153 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1764.2209 | 780 | 200 | 2744.2209 | 68.61% | 95% | 0% | -175.0572 | 1318.1827 | -3550 | -400 | -2631.8173 | 65.8% | 69.41% | 95% | 0% | 2307 | -153
[5 empty] | 2019-04-27 | 42 | 2804 | 2162 | -149 | 1 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 1764.2209 | 780 | 200 | 2744.2209 | 68.61% | 95% | 0% | -170.4805 | 1329.0248 | -3550 | -400 | -2620.9752 | 65.52% | 69.41% | 95% | 0% | 2311 | -149
[5 empty] | 2019-04-27 | 43 | 2804.5 | 2119 | -147 | 1 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 1764.2209 | 780 | 200 | 2744.2209 | 68.61% | 95% | 0% | -168.1922 | 1260.8267 | -3550 | -400 | -2689.1733 | 67.23% | 69.41% | 95% | 0% | 2266 | -147
[5 empty] | 2019-04-27 | 44 | 2805 | 2048 | -146 | 0 | 0 | 2194 | 1316.2407 | 1316.2407 | 1316.2407 | 1764.2209 | 780 | 200 | 2744.2209 | 68.61% | 95% | 0% | -167.0481 | 1149.1927 | -2750 | -200 | -1800.8073 | 45.02% | 69.41% | 95% | 0% | 2194 | -146
[5 empty] | 2019-04-27 | 45 | 2805.5 | 1955 | -144 | 0 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 1764.2209 | 780 | 200 | 2744.2209 | 68.61% | 95% | 0% | -164.7597 | 1002.6764 | -2750 | -200 | -1947.3236 | 48.68% | 69.4% | 95% | 0% | 2099 | -144
[5 empty] | 2019-04-27 | 46 | 2806 | 1861 | -141 | 0 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 1764.2209 | 780 | 200 | 2744.2209 | 68.61% | 95% | 0% | -161.3272 | 854.1715 | -2750 | -200 | -2095.8285 | 52.4% | 69.4% | 95% | 0% | 2002 | -141
[5 empty] | 2019-04-27 | 47 | 2806.5 | 1742 | -140 | 0 | 0 | 1882 | 827.535 | 827.535 | 827.535 | 1764.2209 | 780 | 200 | 2744.2209 | 68.61% | 95% | 0% | -160.1831 | 667.352 | -2750 | -200 | -2282.648 | 57.07% | 69.4% | 95% | 0% | 1882 | -140
[5 empty] | 2019-04-27 | 48 | 2807 | 1647 | -138 | 0 | 0 | 1785 | 675.5977 | 675.5977 | 675.5977 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -157.8947 | 517.703 | -2750 | -200 | -2432.297 | 60.81% | 69.4% | 95% | 0% | 1785 | -138
[5 empty] | 2019-04-28 | 1 | 2807.5 | 1568 | -135 | 0 | 0 | 1703 | 547.1558 | 547.1558 | 547.1558 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -154.4622 | 392.6936 | -2750 | -200 | -2557.3064 | 63.93% | 69.4% | 95% | 0% | 1703 | -135
[5 empty] | 2019-04-28 | 2 | 2808 | 1515 | -132 | 0 | 0 | 1647 | 459.4394 | 459.4394 | 459.4394 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -151.0297 | 308.4097 | -2750 | -200 | -2641.5903 | 66.04% | 69.39% | 95% | 0% | 1647 | -132
[5 empty] | 2019-04-28 | 3 | 2808.5 | 1497 | -128 | 0 | 0 | 1625 | 424.9794 | 424.9794 | 424.9794 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -146.4531 | 278.5263 | -2750 | -200 | -2671.4737 | 66.79% | 69.39% | 95% | 0% | 1625 | -128
[5 empty] | 2019-04-28 | 4 | 2809 | 1511 | -124 | 0 | 0 | 1635 | 440.643 | 440.643 | 440.643 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -141.8764 | 298.7666 | -2750 | -200 | -2651.2334 | 66.28% | 69.39% | 95% | 0% | 1635 | -124
[5 empty] | 2019-04-28 | 5 | 2809.5 | 1500 | -120 | 0 | 0 | 1620 | 417.1476 | 417.1476 | 417.1476 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -137.2998 | 279.8478 | -2750 | -200 | -2670.1522 | 66.75% | 69.39% | 95% | 0% | 1620 | -120
[5 empty] | 2019-04-28 | 6 | 2810 | 1482 | -116 | 0 | 0 | 1598 | 382.6876 | 382.6876 | 382.6876 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -132.7231 | 249.9644 | -2750 | -200 | -2700.0356 | 67.5% | 69.39% | 95% | 0% | 1598 | -116
[5 empty] | 2019-04-28 | 7 | 2810.5 | 1460 | -113 | 0 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -129.2906 | 214.2378 | -2750 | -200 | -2735.7622 | 68.39% | 69.39% | 95% | 0% | 1573 | -113
[5 empty] | 2019-04-28 | 8 | 2811 | 1455 | -109 | 0 | 0 | 1564 | 329.4312 | 329.4312 | 329.4312 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -124.714 | 204.7172 | -2750 | -200 | -2745.2828 | 68.63% | 69.39% | 95% | 0% | 1564 | -109
[5 empty] | 2019-04-28 | 9 | 2811.5 | 1458 | -103 | 0 | 0 | 1561 | 324.7321 | 324.7321 | 324.7321 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -117.849 | 206.8831 | -2750 | -200 | -2743.1169 | 68.58% | 69.39% | 95% | 0% | 1561 | -103
[5 empty] | 2019-04-28 | 10 | 2812 | 1457 | -98 | 0 | 0 | 1555 | 315.3339 | 315.3339 | 315.3339 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -112.1281 | 203.2057 | -2750 | -200 | -2746.7943 | 68.67% | 69.39% | 95% | 0% | 1555 | -98
[5 empty] | 2019-04-28 | 11 | 2812.5 | 1473 | -94 | 0 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -107.5515 | 226.5788 | -2750 | -200 | -2723.4212 | 68.09% | 69.38% | 95% | 0% | 1567 | -94
[5 empty] | 2019-04-28 | 12 | 2813 | 1460 | -92 | 0 | 0 | 1552 | 310.6348 | 310.6348 | 310.6348 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -105.2632 | 205.3716 | -2750 | -200 | -2744.6284 | 68.62% | 69.38% | 95% | 0% | 1552 | -92
[5 empty] | 2019-04-28 | 13 | 2813.5 | 1500 | -99 | 0 | 0 | 1599 | 384.2539 | 384.2539 | 384.2539 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -113.2723 | 270.9816 | -2750 | -200 | -2679.0184 | 66.98% | 69.37% | 95% | 0% | 1599 | -99
[5 empty] | 2019-04-28 | 14 | 2814 | 1541 | -119 | 0 | 0 | 1660 | 479.8021 | 479.8021 | 479.8021 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -136.1556 | 343.6465 | -2750 | -200 | -2606.3535 | 65.16% | 69.37% | 95% | 0% | 1660 | -119
[5 empty] | 2019-04-28 | 15 | 2814.5 | 1602 | -141 | 1 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 1762.6546 | 780 | 200 | 2742.6546 | 68.57% | 95% | 0% | -161.3272 | 448.4832 | -3550 | -400 | -3501.5168 | 87.54% | 69.37% | 95% | 0% | 1743 | -141
[5 empty] | 2019-04-28 | 16 | 2815 | 1624 | -186 | 1 | 0 | 1810 | 714.7568 | 714.7568 | 714.7568 | 1761.0882 | 780 | 200 | 2741.0882 | 68.53% | 95% | 0% | -212.8146 | 501.9422 | -3550 | -400 | -3448.0578 | 86.2% | 69.37% | 95% | 0% | 1810 | -186
[5 empty] | 2019-04-28 | 17 | 2815.5 | 1714 | -212 | 1 | 0 | 1926 | 896.4551 | 896.4551 | 896.4551 | 1761.0882 | 780 | 200 | 2741.0882 | 68.53% | 95% | 0% | -242.5629 | 653.8921 | -3550 | -400 | -3296.1079 | 82.4% | 69.36% | 95% | 0% | 1926 | -212
[5 empty] | 2019-04-28 | 18 | 2816 | 1737 | -242 | 1 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 1761.0882 | 780 | 200 | 2741.0882 | 68.53% | 95% | 0% | -276.8879 | 702.5845 | -3550 | -400 | -3247.4155 | 81.19% | 69.36% | 95% | 0% | 1979 | -242
[5 empty] | 2019-04-28 | 19 | 2816.5 | 1766 | -270 | 1 | 0 | 2036 | 1068.7552 | 1068.7552 | 1068.7552 | 1761.0882 | 780 | 200 | 2741.0882 | 68.53% | 95% | 0% | -308.9245 | 759.8307 | -3550 | -400 | -3190.1693 | 79.75% | 69.36% | 95% | 0% | 2036 | -270
[5 empty] | 2019-04-28 | 20 | 2817 | 1764 | -306 | 1 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 1761.0882 | 780 | 200 | 2741.0882 | 68.53% | 95% | 0% | -350.1144 | 771.8971 | -3550 | -400 | -3178.1029 | 79.45% | 69.35% | 95% | 0% | 2070 | -306
[5 empty] | 2019-04-28 | 21 | 2817.5 | 1767 | -334 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 1761.0882 | 780 | 200 | 2741.0882 | 68.53% | 95% | 0% | -382.151 | 788.4178 | -3550 | -400 | -3161.5822 | 79.04% | 69.35% | 95% | 0% | 2101 | -334
[5 empty] | 2019-04-28 | 22 | 2818 | 1727 | -369 | 1 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 1761.0882 | 780 | 200 | 2741.0882 | 68.53% | 95% | 0% | -422.1968 | 740.5402 | -3550 | -400 | -3209.4598 | 80.24% | 69.35% | 95% | 0% | 2096 | -369
[5 empty] | 2019-04-28 | 23 | 2818.5 | 1721 | -381 | 1 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 1761.0882 | 780 | 200 | 2741.0882 | 68.53% | 95% | 0% | -435.9268 | 736.2084 | -3550 | -400 | -3213.7916 | 80.34% | 69.35% | 95% | 0% | 2102 | -381
[5 empty] | 2019-04-28 | 24 | 2819 | 1744 | -372 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -425.6293 | 768.435 | -3550 | -400 | -3181.565 | 79.54% | 69.34% | 95% | 0% | 2116 | -372
[5 empty] | 2019-04-28 | 25 | 2819.5 | 1754 | -401 | 1 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -458.8101 | 796.3424 | -3550 | -400 | -3153.6576 | 78.84% | 69.34% | 95% | 0% | 2155 | -401
[5 empty] | 2019-04-28 | 26 | 2820 | 1735 | -429 | 1 | 0 | 2164 | 1269.2498 | 1269.2498 | 1269.2498 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -490.8467 | 778.4031 | -3550 | -400 | -3171.5969 | 79.29% | 69.34% | 95% | 0% | 2164 | -429
[5 empty] | 2019-04-28 | 27 | 2820.5 | 1695 | -455 | 1 | 0 | 2150 | 1247.3207 | 1247.3207 | 1247.3207 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -520.595 | 726.7257 | -3550 | -400 | -3223.2743 | 80.58% | 69.33% | 95% | 0% | 2150 | -455
[5 empty] | 2019-04-28 | 28 | 2821 | 1650 | -468 | 1 | 0 | 2118 | 1197.197 | 1197.197 | 1197.197 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -535.4691 | 661.7279 | -3550 | -400 | -3288.2721 | 82.21% | 69.32% | 95% | 0% | 2118 | -468
[5 empty] | 2019-04-28 | 29 | 2821.5 | 1703 | -425 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -486.27 | 726.5907 | -3550 | -400 | -3223.4093 | 80.59% | 69.32% | 95% | 0% | 2128 | -425
[5 empty] | 2019-04-28 | 30 | 2822 | 1720 | -398 | 1 | 0 | 2118 | 1197.197 | 1197.197 | 1197.197 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -455.3776 | 741.8195 | -3550 | -400 | -3208.1805 | 80.2% | 69.32% | 95% | 0% | 2118 | -398
[5 empty] | 2019-04-28 | 31 | 2822.5 | 1738 | -378 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -432.4943 | 761.57 | -3550 | -400 | -3188.43 | 79.71% | 69.32% | 95% | 0% | 2116 | -378
[5 empty] | 2019-04-28 | 32 | 2823 | 1773 | -353 | 1 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -403.8902 | 805.8378 | -3550 | -400 | -3144.1622 | 78.6% | 69.32% | 95% | 0% | 2126 | -353
[5 empty] | 2019-04-28 | 33 | 2823.5 | 1872 | -319 | 1 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -364.9886 | 946.5531 | -3550 | -400 | -3003.4469 | 75.09% | 69.32% | 95% | 0% | 2191 | -319
[5 empty] | 2019-04-28 | 34 | 2824 | 1984 | -289 | 1 | 0 | 2273 | 1439.9835 | 1439.9835 | 1439.9835 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -330.6636 | 1109.3199 | -3550 | -400 | -2840.6801 | 71.02% | 69.31% | 95% | 0% | 2273 | -289
[5 empty] | 2019-04-28 | 35 | 2824.5 | 2066 | -250 | 1 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -286.0412 | 1221.296 | -3550 | -400 | -2728.704 | 68.22% | 69.31% | 95% | 0% | 2316 | -250
[5 empty] | 2019-04-28 | 36 | 2825 | 2149 | -211 | 1 | 0 | 2360 | 1576.2572 | 1576.2572 | 1576.2572 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -241.4188 | 1334.8384 | -3550 | -400 | -2615.1616 | 65.38% | 69.31% | 95% | 0% | 2360 | -211
[5 empty] | 2019-04-28 | 37 | 2825.5 | 2220 | -164 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1759.5218 | 780 | 200 | 2739.5218 | 68.49% | 95% | 0% | -187.643 | 1426.2069 | -3550 | -400 | -2523.7931 | 63.09% | 69.31% | 95% | 0% | 2384 | -164
[5 empty] | 2019-04-28 | 38 | 2826 | 2286 | -114 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 1757.9555 | 780 | 200 | 2737.9555 | 68.45% | 95% | 0% | -130.4348 | 1508.477 | -3550 | -400 | -2441.523 | 61.04% | 69.3% | 95% | 0% | 2400 | -114
[5 empty] | 2019-04-28 | 39 | 2826.5 | 2323 | -80 | 1 | 0 | 2403 | 1643.6109 | 1643.6109 | 1643.6109 | 1757.9555 | 780 | 200 | 2737.9555 | 68.45% | 95% | 0% | -91.5332 | 1552.0777 | -3550 | -400 | -2397.9223 | 59.95% | 69.3% | 95% | 0% | 2403 | -80
[5 empty] | 2019-04-28 | 40 | 2827 | 2331 | -53 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1757.9555 | 780 | 200 | 2737.9555 | 68.45% | 95% | 0% | -60.6407 | 1553.2092 | -3550 | -400 | -2396.7908 | 59.92% | 69.3% | 95% | 0% | 2384 | -53
[5 empty] | 2019-04-28 | 41 | 2827.5 | 2358 | -41 | 1 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 1757.9555 | 780 | 200 | 2737.9555 | 68.45% | 95% | 0% | -46.9108 | 1590.4347 | -3550 | -400 | -2359.5653 | 58.99% | 69.3% | 95% | 0% | 2399 | -41
[5 empty] | 2019-04-28 | 42 | 2828 | 2390 | -38 | 1 | 0 | 2428 | 1682.77 | 1682.77 | 1682.77 | 1757.9555 | 780 | 200 | 2737.9555 | 68.45% | 95% | 0% | -43.4783 | 1639.2917 | -3550 | -400 | -2310.7083 | 57.77% | 69.29% | 95% | 0% | 2428 | -38
[5 empty] | 2019-04-28 | 43 | 2828.5 | 2369 | -36 | 0 | 0 | 2405 | 1646.7436 | 1646.7436 | 1646.7436 | 1757.9555 | 780 | 200 | 2737.9555 | 68.45% | 95% | 0% | -41.1899 | 1605.5537 | -2750 | -200 | -1344.4463 | 33.61% | 69.29% | 95% | 0% | 2405 | -36
[5 empty] | 2019-04-28 | 44 | 2829 | 2269 | -35 | 0 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 1757.9555 | 780 | 200 | 2737.9555 | 68.45% | 95% | 0% | -40.0458 | 1448.495 | -2750 | -200 | -1501.505 | 37.54% | 69.28% | 95% | 0% | 2304 | -35
[5 empty] | 2019-04-28 | 45 | 2829.5 | 2208 | -33 | 0 | 0 | 2241 | 1389.8599 | 1389.8599 | 1389.8599 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -37.7574 | 1352.1024 | -2750 | -200 | -1597.8976 | 39.95% | 69.27% | 95% | 0% | 2241 | -33
[5 empty] | 2019-04-28 | 46 | 2830 | 2095 | -32 | 0 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -36.6133 | 1174.681 | -2750 | -200 | -1775.319 | 44.38% | 69.27% | 95% | 0% | 2127 | -32
[5 empty] | 2019-04-28 | 47 | 2830.5 | 1948 | -31 | 0 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -35.4691 | 944.0033 | -2750 | -200 | -2005.9967 | 50.15% | 69.27% | 95% | 0% | 1979 | -31
[5 empty] | 2019-04-28 | 48 | 2831 | 1838 | -30 | 0 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -34.3249 | 771.281 | -2750 | -200 | -2178.719 | 54.47% | 69.26% | 95% | 0% | 1868 | -30
[5 empty] | 2019-04-29 | 1 | 2831.5 | 1758 | -28 | 0 | 0 | 1786 | 677.1641 | 677.1641 | 677.1641 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -32.0366 | 645.1274 | -2750 | -200 | -2304.8726 | 57.62% | 69.26% | 95% | 0% | 1786 | -28
[5 empty] | 2019-04-29 | 2 | 2832 | 1720 | -27 | 0 | 0 | 1747 | 616.0758 | 616.0758 | 616.0758 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -30.8924 | 585.1834 | -2750 | -200 | -2364.8166 | 59.12% | 69.25% | 95% | 0% | 1747 | -27
[5 empty] | 2019-04-29 | 3 | 2832.5 | 1715 | -27 | 0 | 0 | 1742 | 608.244 | 608.244 | 608.244 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -30.8924 | 577.3516 | -2750 | -200 | -2372.6484 | 59.32% | 69.25% | 95% | 0% | 1742 | -27
[5 empty] | 2019-04-29 | 4 | 2833 | 1739 | -26 | 0 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -29.7483 | 614.5221 | -2750 | -200 | -2335.4779 | 58.39% | 69.24% | 95% | 0% | 1765 | -26
[5 empty] | 2019-04-29 | 5 | 2833.5 | 1733 | -26 | 0 | 0 | 1759 | 634.8722 | 634.8722 | 634.8722 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -29.7483 | 605.1239 | -2750 | -200 | -2344.8761 | 58.62% | 69.24% | 95% | 0% | 1759 | -26
[5 empty] | 2019-04-29 | 6 | 2834 | 1712 | -25 | 0 | 0 | 1737 | 600.4122 | 600.4122 | 600.4122 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -28.6041 | 571.8081 | -2750 | -200 | -2378.1919 | 59.45% | 69.24% | 95% | 0% | 1737 | -25
[5 empty] | 2019-04-29 | 7 | 2834.5 | 1705 | -24 | 0 | 0 | 1729 | 587.8813 | 587.8813 | 587.8813 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -27.46 | 560.4213 | -2750 | -200 | -2389.5787 | 59.74% | 69.23% | 95% | 0% | 1729 | -24
[5 empty] | 2019-04-29 | 8 | 2835 | 1691 | -24 | 0 | 0 | 1715 | 565.9522 | 565.9522 | 565.9522 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -27.46 | 538.4922 | -2750 | -200 | -2411.5078 | 60.29% | 69.23% | 95% | 0% | 1715 | -24
[5 empty] | 2019-04-29 | 9 | 2835.5 | 1688 | -25 | 0 | 0 | 1713 | 562.8195 | 562.8195 | 562.8195 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -28.6041 | 534.2153 | -2750 | -200 | -2415.7847 | 60.39% | 69.23% | 95% | 0% | 1713 | -25
[5 empty] | 2019-04-29 | 10 | 2836 | 1712 | -25 | 0 | 0 | 1737 | 600.4122 | 600.4122 | 600.4122 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -28.6041 | 571.8081 | -2750 | -200 | -2378.1919 | 59.45% | 69.23% | 95% | 0% | 1737 | -25
[5 empty] | 2019-04-29 | 11 | 2836.5 | 1763 | -26 | 0 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -29.7483 | 652.1149 | -2750 | -200 | -2297.8851 | 57.45% | 69.23% | 95% | 0% | 1789 | -26
[5 empty] | 2019-04-29 | 12 | 2837 | 1834 | -27 | 0 | 0 | 1861 | 794.6414 | 794.6414 | 794.6414 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -30.8924 | 763.7489 | -2750 | -200 | -2186.2511 | 54.66% | 69.22% | 95% | 0% | 1861 | -27
[5 empty] | 2019-04-29 | 13 | 2837.5 | 2030 | -40 | 0 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -45.7666 | 1076.245 | -2750 | -200 | -1873.755 | 46.84% | 69.22% | 95% | 0% | 2070 | -40
[5 empty] | 2019-04-29 | 14 | 2838 | 2200 | -65 | 0 | 0 | 2265 | 1427.4526 | 1427.4526 | 1427.4526 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -74.3707 | 1353.0819 | -2750 | -200 | -1596.9181 | 39.92% | 69.22% | 95% | 0% | 2265 | -65
[5 empty] | 2019-04-29 | 15 | 2838.5 | 2390 | -101 | 1 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -115.5606 | 1665.8903 | -3550 | -400 | -2284.1097 | 57.1% | 69.21% | 95% | 0% | 2491 | -101
[5 empty] | 2019-04-29 | 16 | 2839 | 2448 | -141 | 1 | 0 | 2589 | 1934.9547 | 1934.9547 | 1934.9547 | 1756.3891 | 780 | 200 | 2736.3891 | 68.41% | 95% | 0% | -161.3272 | 1773.6274 | -3550 | -400 | -2176.3726 | 54.41% | 69.21% | 95% | 0% | 2589 | -141
[5 empty] | 2019-04-29 | 17 | 2839.5 | 2443 | -182 | 1 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -208.238 | 1783.1058 | -3550 | -400 | -2166.8942 | 54.17% | 69.21% | 95% | 0% | 2625 | -182
[5 empty] | 2019-04-29 | 18 | 2840 | 2380 | -230 | 1 | 0 | 2610 | 1967.8483 | 1967.8483 | 1967.8483 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -263.1579 | 1704.6904 | -3550 | -400 | -2245.3096 | 56.13% | 69.21% | 95% | 0% | 2610 | -230
[5 empty] | 2019-04-29 | 19 | 2840.5 | 2350 | -279 | 1 | 0 | 2629 | 1997.6092 | 1997.6092 | 1997.6092 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -319.222 | 1678.3873 | -3550 | -400 | -2271.6127 | 56.79% | 69.21% | 95% | 0% | 2629 | -279
[5 empty] | 2019-04-29 | 20 | 2841 | 2277 | -321 | 1 | 0 | 2598 | 1949.0519 | 1949.0519 | 1949.0519 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -367.2769 | 1581.775 | -3550 | -400 | -2368.225 | 59.21% | 69.2% | 95% | 0% | 2598 | -321
[5 empty] | 2019-04-29 | 21 | 2841.5 | 2192 | -367 | 1 | 0 | 2559 | 1887.9637 | 1887.9637 | 1887.9637 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -419.9085 | 1468.0553 | -3550 | -400 | -2481.9447 | 62.05% | 69.2% | 95% | 0% | 2559 | -367
[5 empty] | 2019-04-29 | 22 | 2842 | 2132 | -413 | 1 | 0 | 2545 | 1866.0346 | 1866.0346 | 1866.0346 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -472.54 | 1393.4946 | -3550 | -400 | -2556.5054 | 63.91% | 69.2% | 95% | 0% | 2545 | -413
[5 empty] | 2019-04-29 | 23 | 2842.5 | 2103 | -422 | 1 | 0 | 2525 | 1834.7073 | 1834.7073 | 1834.7073 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -482.8375 | 1351.8698 | -3550 | -400 | -2598.1302 | 64.95% | 69.19% | 95% | 0% | 2525 | -422
[5 empty] | 2019-04-29 | 24 | 2843 | 2056 | -450 | 1 | 0 | 2506 | 1804.9464 | 1804.9464 | 1804.9464 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -514.8741 | 1290.0723 | -3550 | -400 | -2659.9277 | 66.5% | 69.18% | 95% | 0% | 2506 | -450
[5 empty] | 2019-04-29 | 25 | 2843.5 | 2074 | -435 | 1 | 0 | 2509 | 1809.6455 | 1809.6455 | 1809.6455 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -497.7117 | 1311.9338 | -3550 | -400 | -2638.0662 | 65.95% | 69.18% | 95% | 0% | 2509 | -435
[5 empty] | 2019-04-29 | 26 | 2844 | 2067 | -414 | 1 | 0 | 2481 | 1765.7873 | 1765.7873 | 1765.7873 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -473.6842 | 1292.1031 | -3550 | -400 | -2657.8969 | 66.45% | 69.18% | 95% | 0% | 2481 | -414
[5 empty] | 2019-04-29 | 27 | 2844.5 | 1996 | -442 | 1 | 0 | 2438 | 1698.4336 | 1698.4336 | 1698.4336 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -505.7208 | 1192.7128 | -3550 | -400 | -2757.2872 | 68.93% | 69.16% | 95% | 0% | 2438 | -442
[5 empty] | 2019-04-29 | 28 | 2845 | 1972 | -439 | 1 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -502.2883 | 1153.8535 | -3550 | -400 | -2796.1465 | 69.9% | 69.16% | 95% | 0% | 2411 | -439
[5 empty] | 2019-04-29 | 29 | 2845.5 | 1983 | -415 | 1 | 0 | 2398 | 1635.7791 | 1635.7791 | 1635.7791 | 1754.8228 | 780 | 200 | 2734.8228 | 68.37% | 95% | 0% | -474.8284 | 1160.9507 | -3550 | -400 | -2789.0493 | 69.73% | 69.16% | 95% | 0% | 2398 | -415
[5 empty] | 2019-04-29 | 30 | 2846 | 1977 | -407 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1753.2564 | 780 | 200 | 2733.2564 | 68.33% | 95% | 0% | -465.6751 | 1148.1749 | -3550 | -400 | -2801.8251 | 70.05% | 69.15% | 95% | 0% | 2384 | -407
[5 empty] | 2019-04-29 | 31 | 2846.5 | 1984 | -388 | 1 | 0 | 2372 | 1595.0536 | 1595.0536 | 1595.0536 | 1753.2564 | 780 | 200 | 2733.2564 | 68.33% | 95% | 0% | -443.9359 | 1151.1177 | -3550 | -400 | -2798.8823 | 69.97% | 69.14% | 95% | 0% | 2372 | -388
[5 empty] | 2019-04-29 | 32 | 2847 | 2036 | -374 | 1 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 1753.2564 | 780 | 200 | 2733.2564 | 68.33% | 95% | 0% | -427.9176 | 1226.6578 | -3550 | -400 | -2723.3422 | 68.08% | 69.14% | 95% | 0% | 2410 | -374
[5 empty] | 2019-04-29 | 33 | 2847.5 | 2112 | -353 | 1 | 0 | 2465 | 1740.7255 | 1740.7255 | 1740.7255 | 1753.2564 | 780 | 200 | 2733.2564 | 68.33% | 95% | 0% | -403.8902 | 1336.8353 | -3550 | -400 | -2613.1647 | 65.33% | 69.13% | 95% | 0% | 2465 | -353
[5 empty] | 2019-04-29 | 34 | 2848 | 2212 | -327 | 1 | 0 | 2539 | 1856.6364 | 1856.6364 | 1856.6364 | 1753.2564 | 780 | 200 | 2733.2564 | 68.33% | 95% | 0% | -374.1419 | 1482.4946 | -3550 | -400 | -2467.5054 | 61.69% | 69.13% | 95% | 0% | 2539 | -327
[5 empty] | 2019-04-29 | 35 | 2848.5 | 2324 | -277 | 1 | 0 | 2601 | 1953.751 | 1953.751 | 1953.751 | 1753.2564 | 780 | 200 | 2733.2564 | 68.33% | 95% | 0% | -316.9336 | 1636.8174 | -3550 | -400 | -2313.1826 | 57.83% | 69.13% | 95% | 0% | 2601 | -277
[5 empty] | 2019-04-29 | 36 | 2849 | 2420 | -223 | 1 | 0 | 2643 | 2019.5383 | 2019.5383 | 2019.5383 | 1753.2564 | 780 | 200 | 2733.2564 | 68.33% | 95% | 0% | -255.1487 | 1764.3896 | -3550 | -400 | -2185.6104 | 54.64% | 69.12% | 95% | 0% | 2643 | -223
[5 empty] | 2019-04-29 | 37 | 2849.5 | 2478 | -179 | 1 | 0 | 2657 | 2041.4674 | 2041.4674 | 2041.4674 | 1753.2564 | 780 | 200 | 2733.2564 | 68.33% | 95% | 0% | -204.8055 | 1836.6619 | -3550 | -400 | -2113.3381 | 52.83% | 69.12% | 95% | 0% | 2657 | -179
[5 empty] | 2019-04-29 | 38 | 2850 | 2536 | -139 | 1 | 0 | 2675 | 2069.662 | 2069.662 | 2069.662 | 1753.2564 | 780 | 200 | 2733.2564 | 68.33% | 95% | 0% | -159.0389 | 1910.6231 | -3550 | -400 | -2039.3769 | 50.98% | 69.12% | 95% | 0% | 2675 | -139
[5 empty] | 2019-04-29 | 39 | 2850.5 | 2586 | -103 | 1 | 0 | 2689 | 2091.5911 | 2091.5911 | 2091.5911 | 1753.2564 | 780 | 200 | 2733.2564 | 68.33% | 95% | 0% | -117.849 | 1973.7421 | -3550 | -400 | -1976.2579 | 49.41% | 69.11% | 95% | 0% | 2689 | -103
[5 empty] | 2019-04-29 | 40 | 2851 | 2616 | -64 | 1 | 0 | 2680 | 2077.4938 | 2077.4938 | 2077.4938 | 1751.69 | 780 | 200 | 2731.69 | 68.29% | 95% | 0% | -73.2265 | 2004.2673 | -3550 | -400 | -1945.7327 | 48.64% | 69.11% | 95% | 0% | 2680 | -64
[5 empty] | 2019-04-29 | 41 | 2851.5 | 2617 | -47 | 1 | 0 | 2664 | 2052.432 | 2052.432 | 2052.432 | 1751.69 | 780 | 200 | 2731.69 | 68.29% | 95% | 0% | -53.7757 | 1998.6562 | -3550 | -400 | -1951.3438 | 48.78% | 69.11% | 95% | 0% | 2664 | -47
[5 empty] | 2019-04-29 | 42 | 2852 | 2605 | -45 | 1 | 0 | 2650 | 2030.5029 | 2030.5029 | 2030.5029 | 1751.69 | 780 | 200 | 2731.69 | 68.29% | 95% | 0% | -51.4874 | 1979.0155 | -3550 | -400 | -1970.9845 | 49.27% | 69.11% | 95% | 0% | 2650 | -45
[5 empty] | 2019-04-29 | 43 | 2852.5 | 2587 | -46 | 1 | 0 | 2633 | 2003.8747 | 2003.8747 | 2003.8747 | 1751.69 | 780 | 200 | 2731.69 | 68.29% | 95% | 0% | -52.6316 | 1951.2431 | -3550 | -400 | -1998.7569 | 49.97% | 69.1% | 95% | 0% | 2633 | -46
[5 empty] | 2019-04-29 | 44 | 2853 | 2481 | -47 | 0 | 0 | 2528 | 1839.4064 | 1839.4064 | 1839.4064 | 1751.69 | 780 | 200 | 2731.69 | 68.29% | 95% | 0% | -53.7757 | 1785.6307 | -2750 | -200 | -1164.3693 | 29.11% | 69.1% | 95% | 0% | 2528 | -47
[5 empty] | 2019-04-29 | 45 | 2853.5 | 2322 | -48 | 0 | 0 | 2370 | 1591.9209 | 1591.9209 | 1591.9209 | 1751.69 | 780 | 200 | 2731.69 | 68.29% | 95% | 0% | -54.9199 | 1537.0009 | -2750 | -200 | -1412.9991 | 35.32% | 69.09% | 95% | 0% | 2370 | -48
[5 empty] | 2019-04-29 | 46 | 2854 | 2163 | -48 | 0 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 1751.69 | 780 | 200 | 2731.69 | 68.29% | 95% | 0% | -54.9199 | 1287.949 | -2750 | -200 | -1662.051 | 41.55% | 69.09% | 95% | 0% | 2211 | -48
[5 empty] | 2019-04-29 | 47 | 2854.5 | 2008 | -50 | 0 | 0 | 2058 | 1103.2152 | 1103.2152 | 1103.2152 | 1751.69 | 780 | 200 | 2731.69 | 68.29% | 95% | 0% | -57.2082 | 1046.0069 | -2750 | -200 | -1903.9931 | 47.6% | 69.09% | 95% | 0% | 2058 | -50
[5 empty] | 2019-04-29 | 48 | 2855 | 1895 | -51 | 0 | 0 | 1946 | 927.7824 | 927.7824 | 927.7824 | 1751.69 | 780 | 200 | 2731.69 | 68.29% | 95% | 0% | -58.3524 | 869.43 | -2750 | -200 | -2080.57 | 52.01% | 69.09% | 95% | 0% | 1946 | -51
[5 empty] | 2019-04-30 | 1 | 2855.5 | 1803 | -53 | 0 | 0 | 1856 | 786.8096 | 786.8096 | 786.8096 | 1751.69 | 780 | 200 | 2731.69 | 68.29% | 95% | 0% | -60.6407 | 726.1688 | -2750 | -200 | -2223.8312 | 55.6% | 69.08% | 95% | 0% | 1856 | -53
[5 empty] | 2019-04-30 | 2 | 2856 | 1760 | -56 | 0 | 0 | 1816 | 724.155 | 724.155 | 724.155 | 1751.69 | 780 | 200 | 2731.69 | 68.29% | 95% | 0% | -64.0732 | 660.0818 | -2750 | -200 | -2289.9182 | 57.25% | 69.08% | 95% | 0% | 1816 | -56
[5 empty] | 2019-04-30 | 3 | 2856.5 | 1742 | -56 | 0 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 1750.1237 | 780 | 200 | 2730.1237 | 68.25% | 95% | 0% | -64.0732 | 631.8872 | -2750 | -200 | -2318.1128 | 57.95% | 69.08% | 95% | 0% | 1798 | -56
[5 empty] | 2019-04-30 | 4 | 2857 | 1760 | -55 | 0 | 0 | 1815 | 722.5886 | 722.5886 | 722.5886 | 1750.1237 | 780 | 200 | 2730.1237 | 68.25% | 95% | 0% | -62.9291 | 659.6596 | -2750 | -200 | -2290.3404 | 57.26% | 69.08% | 95% | 0% | 1815 | -55
[5 empty] | 2019-04-30 | 5 | 2857.5 | 1746 | -55 | 0 | 0 | 1801 | 700.6595 | 700.6595 | 700.6595 | 1750.1237 | 780 | 200 | 2730.1237 | 68.25% | 95% | 0% | -62.9291 | 637.7305 | -2750 | -200 | -2312.2695 | 57.81% | 69.08% | 95% | 0% | 1801 | -55
[5 empty] | 2019-04-30 | 6 | 2858 | 1720 | -55 | 0 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 1750.1237 | 780 | 200 | 2730.1237 | 68.25% | 95% | 0% | -62.9291 | 597.005 | -2750 | -200 | -2352.995 | 58.82% | 69.08% | 95% | 0% | 1775 | -55
[5 empty] | 2019-04-30 | 7 | 2858.5 | 1704 | -54 | 0 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 1750.1237 | 780 | 200 | 2730.1237 | 68.25% | 95% | 0% | -61.7849 | 571.521 | -2750 | -200 | -2378.479 | 59.46% | 69.07% | 95% | 0% | 1758 | -54
[5 empty] | 2019-04-30 | 8 | 2859 | 1702 | -54 | 0 | 0 | 1756 | 630.1731 | 630.1731 | 630.1731 | 1750.1237 | 780 | 200 | 2730.1237 | 68.25% | 95% | 0% | -61.7849 | 568.3882 | -2750 | -200 | -2381.6118 | 59.54% | 69.07% | 95% | 0% | 1756 | -54
[5 empty] | 2019-04-30 | 9 | 2859.5 | 1709 | -54 | 0 | 0 | 1763 | 641.1377 | 641.1377 | 641.1377 | 1750.1237 | 780 | 200 | 2730.1237 | 68.25% | 95% | 0% | -61.7849 | 579.3528 | -2750 | -200 | -2370.6472 | 59.27% | 69.06% | 95% | 0% | 1763 | -54
[5 empty] | 2019-04-30 | 10 | 2860 | 1725 | -54 | 0 | 0 | 1779 | 666.1995 | 666.1995 | 666.1995 | 1750.1237 | 780 | 200 | 2730.1237 | 68.25% | 95% | 0% | -61.7849 | 604.4146 | -2750 | -200 | -2345.5854 | 58.64% | 69.06% | 95% | 0% | 1779 | -54
[5 empty] | 2019-04-30 | 11 | 2860.5 | 1773 | -53 | 0 | 0 | 1826 | 739.8186 | 739.8186 | 739.8186 | 1750.1237 | 780 | 200 | 2730.1237 | 68.25% | 95% | 0% | -60.6407 | 679.1779 | -2750 | -200 | -2270.8221 | 56.77% | 69.06% | 95% | 0% | 1826 | -53
[5 empty] | 2019-04-30 | 12 | 2861 | 1827 | -54 | 0 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -61.7849 | 764.1838 | -2750 | -200 | -2185.8162 | 54.65% | 69.06% | 95% | 0% | 1881 | -54
[5 empty] | 2019-04-30 | 13 | 2861.5 | 2006 | -69 | 0 | 0 | 2075 | 1129.8434 | 1129.8434 | 1129.8434 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -78.9474 | 1050.896 | -2750 | -200 | -1899.104 | 47.48% | 69.05% | 95% | 0% | 2075 | -69
[5 empty] | 2019-04-30 | 14 | 2862 | 2175 | -99 | 0 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -113.2723 | 1328.2776 | -2750 | -200 | -1621.7224 | 40.54% | 69.05% | 95% | 0% | 2274 | -99
[5 empty] | 2019-04-30 | 15 | 2862.5 | 2346 | -135 | 1 | 0 | 2481 | 1765.7873 | 1765.7873 | 1765.7873 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -154.4622 | 1611.3251 | -3550 | -400 | -2338.6749 | 58.47% | 69.05% | 95% | 0% | 2481 | -135
[5 empty] | 2019-04-30 | 16 | 2863 | 2363 | -177 | 1 | 0 | 2540 | 1858.2028 | 1858.2028 | 1858.2028 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -202.5172 | 1655.6856 | -3550 | -400 | -2294.3144 | 57.36% | 69.05% | 95% | 0% | 2540 | -177
[5 empty] | 2019-04-30 | 17 | 2863.5 | 2341 | -229 | 1 | 0 | 2570 | 1905.1937 | 1905.1937 | 1905.1937 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -262.0137 | 1643.18 | -3550 | -400 | -2306.82 | 57.67% | 69.04% | 95% | 0% | 2570 | -229
[5 empty] | 2019-04-30 | 18 | 2864 | 2261 | -283 | 1 | 0 | 2544 | 1864.4683 | 1864.4683 | 1864.4683 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -323.7986 | 1540.6696 | -3550 | -400 | -2409.3304 | 60.23% | 69.04% | 95% | 0% | 2544 | -283
[5 empty] | 2019-04-30 | 19 | 2864.5 | 2194 | -344 | 1 | 0 | 2538 | 1855.0701 | 1855.0701 | 1855.0701 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -393.5927 | 1461.4774 | -3550 | -400 | -2488.5226 | 62.21% | 69.04% | 95% | 0% | 2538 | -344
[5 empty] | 2019-04-30 | 20 | 2865 | 2128 | -398 | 1 | 0 | 2526 | 1836.2737 | 1836.2737 | 1836.2737 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -455.3776 | 1380.8961 | -3550 | -400 | -2569.1039 | 64.23% | 69.03% | 95% | 0% | 2526 | -398
[5 empty] | 2019-04-30 | 21 | 2865.5 | 2025 | -450 | 1 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -514.8741 | 1241.515 | -3550 | -400 | -2708.485 | 67.71% | 69.03% | 95% | 0% | 2475 | -450
[5 empty] | 2019-04-30 | 22 | 2866 | 1912 | -515 | 1 | 0 | 2427 | 1681.2036 | 1681.2036 | 1681.2036 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -589.2449 | 1091.9588 | -3550 | -400 | -2858.0412 | 71.45% | 69.03% | 95% | 0% | 2427 | -515
[5 empty] | 2019-04-30 | 23 | 2866.5 | 1823 | -564 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -645.3089 | 973.2401 | -3550 | -400 | -2976.7599 | 74.42% | 69.03% | 95% | 0% | 2387 | -564
[5 empty] | 2019-04-30 | 24 | 2867 | 1823 | -560 | 1 | 0 | 2383 | 1612.2836 | 1612.2836 | 1612.2836 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -640.7323 | 971.5513 | -3550 | -400 | -2978.4487 | 74.46% | 69.02% | 95% | 0% | 2383 | -560
[5 empty] | 2019-04-30 | 25 | 2867.5 | 1800 | -563 | 1 | 0 | 2363 | 1580.9563 | 1580.9563 | 1580.9563 | 1748.5573 | 780 | 200 | 2728.5573 | 68.21% | 95% | 0% | -644.1648 | 936.7915 | -3550 | -400 | -3013.2085 | 75.33% | 69.02% | 95% | 0% | 2363 | -563
[5 empty] | 2019-04-30 | 26 | 2868 | 1765 | -577 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 1746.9909 | 780 | 200 | 2726.9909 | 68.17% | 95% | 0% | -660.1831 | 887.8796 | -3550 | -400 | -3062.1204 | 76.55% | 69.02% | 95% | 0% | 2342 | -577
[5 empty] | 2019-04-30 | 27 | 2868.5 | 1720 | -599 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 1746.9909 | 780 | 200 | 2726.9909 | 68.17% | 95% | 0% | -685.3547 | 826.6816 | -3550 | -400 | -3123.3184 | 78.08% | 69.02% | 95% | 0% | 2319 | -599
[5 empty] | 2019-04-30 | 28 | 2869 | 1740 | -561 | 1 | 0 | 2301 | 1483.8417 | 1483.8417 | 1483.8417 | 1746.9909 | 780 | 200 | 2726.9909 | 68.17% | 95% | 0% | -641.8764 | 841.9653 | -3550 | -400 | -3108.0347 | 77.7% | 69.02% | 95% | 0% | 2301 | -561
[5 empty] | 2019-04-30 | 29 | 2869.5 | 1748 | -548 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1746.9909 | 780 | 200 | 2726.9909 | 68.17% | 95% | 0% | -627.0023 | 849.0076 | -3550 | -400 | -3100.9924 | 77.52% | 69.01% | 95% | 0% | 2296 | -548
[5 empty] | 2019-04-30 | 30 | 2870 | 1769 | -518 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1746.9909 | 780 | 200 | 2726.9909 | 68.17% | 95% | 0% | -592.6773 | 869.2353 | -3550 | -400 | -3080.7647 | 77.02% | 69% | 95% | 0% | 2287 | -518
[5 empty] | 2019-04-30 | 31 | 2870.5 | 1808 | -487 | 1 | 0 | 2295 | 1474.4435 | 1474.4435 | 1474.4435 | 1746.9909 | 780 | 200 | 2726.9909 | 68.17% | 95% | 0% | -557.2082 | 917.2353 | -3550 | -400 | -3032.7647 | 75.82% | 69% | 95% | 0% | 2295 | -487
[5 empty] | 2019-04-30 | 32 | 2871 | 1887 | -457 | 1 | 0 | 2344 | 1551.1954 | 1551.1954 | 1551.1954 | 1746.9909 | 780 | 200 | 2726.9909 | 68.17% | 95% | 0% | -522.8833 | 1028.3121 | -3550 | -400 | -2921.6879 | 73.04% | 69% | 95% | 0% | 2344 | -457
[5 empty] | 2019-04-30 | 33 | 2871.5 | 2011 | -404 | 1 | 0 | 2415 | 1662.4073 | 1662.4073 | 1662.4073 | 1746.9909 | 780 | 200 | 2726.9909 | 68.17% | 95% | 0% | -462.2426 | 1200.1647 | -3550 | -400 | -2749.8353 | 68.75% | 68.99% | 95% | 0% | 2415 | -404
[5 empty] | 2019-04-30 | 34 | 2872 | 2168 | -323 | 1 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 1746.9909 | 780 | 200 | 2726.9909 | 68.17% | 95% | 0% | -369.5652 | 1411.8857 | -3550 | -400 | -2538.1143 | 63.45% | 68.99% | 95% | 0% | 2491 | -323
[5 empty] | 2019-04-30 | 35 | 2872.5 | 2275 | -276 | 1 | 0 | 2551 | 1875.4328 | 1875.4328 | 1875.4328 | 1746.9909 | 780 | 200 | 2726.9909 | 68.17% | 95% | 0% | -315.7895 | 1559.6433 | -3550 | -400 | -2390.3567 | 59.76% | 68.98% | 95% | 0% | 2551 | -276
[5 empty] | 2019-04-30 | 36 | 2873 | 2352 | -227 | 1 | 0 | 2579 | 1919.291 | 1919.291 | 1919.291 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -259.7254 | 1659.5656 | -3550 | -400 | -2290.4344 | 57.26% | 68.98% | 95% | 0% | 2579 | -227
[5 empty] | 2019-04-30 | 37 | 2873.5 | 2432 | -175 | 1 | 0 | 2607 | 1963.1492 | 1963.1492 | 1963.1492 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -200.2288 | 1762.9204 | -3550 | -400 | -2187.0796 | 54.68% | 68.97% | 95% | 0% | 2607 | -175
[5 empty] | 2019-04-30 | 38 | 2874 | 2508 | -120 | 1 | 0 | 2628 | 1996.0429 | 1996.0429 | 1996.0429 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -137.2998 | 1858.7431 | -3550 | -400 | -2091.2569 | 52.28% | 68.97% | 95% | 0% | 2628 | -120
[5 empty] | 2019-04-30 | 39 | 2874.5 | 2568 | -79 | 1 | 0 | 2647 | 2025.8038 | 2025.8038 | 2025.8038 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -90.389 | 1935.4148 | -3550 | -400 | -2014.5852 | 50.36% | 68.97% | 95% | 0% | 2647 | -79
[5 empty] | 2019-04-30 | 40 | 2875 | 2602 | -48 | 1 | 0 | 2650 | 2030.5029 | 2030.5029 | 2030.5029 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -54.9199 | 1975.583 | -3550 | -400 | -1974.417 | 49.36% | 68.97% | 95% | 0% | 2650 | -48
[5 empty] | 2019-04-30 | 41 | 2875.5 | 2591 | -33 | 1 | 0 | 2624 | 1989.7774 | 1989.7774 | 1989.7774 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -37.7574 | 1952.02 | -3550 | -400 | -1997.98 | 49.95% | 68.97% | 95% | 0% | 2624 | -33
[5 empty] | 2019-04-30 | 42 | 2876 | 2604 | -31 | 1 | 0 | 2635 | 2007.0074 | 2007.0074 | 2007.0074 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -35.4691 | 1971.5383 | -3550 | -400 | -1978.4617 | 49.46% | 68.96% | 95% | 0% | 2635 | -31
[5 empty] | 2019-04-30 | 43 | 2876.5 | 2566 | -30 | 1 | 0 | 2596 | 1945.9192 | 1945.9192 | 1945.9192 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -34.3249 | 1911.5943 | -3550 | -400 | -2038.4057 | 50.96% | 68.96% | 95% | 0% | 2596 | -30
[5 empty] | 2019-04-30 | 44 | 2877 | 2463 | -30 | 0 | 0 | 2493 | 1784.5837 | 1784.5837 | 1784.5837 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -34.3249 | 1750.2587 | -2750 | -200 | -1199.7413 | 29.99% | 68.95% | 95% | 0% | 2493 | -30
[5 empty] | 2019-04-30 | 45 | 2877.5 | 2351 | -29 | 0 | 0 | 2380 | 1607.5845 | 1607.5845 | 1607.5845 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -33.1808 | 1574.4037 | -2750 | -200 | -1375.5963 | 34.39% | 68.95% | 95% | 0% | 2380 | -29
[5 empty] | 2019-04-30 | 46 | 2878 | 2206 | -28 | 0 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -32.0366 | 1346.8587 | -2750 | -200 | -1603.1413 | 40.08% | 68.95% | 95% | 0% | 2234 | -28
[5 empty] | 2019-04-30 | 47 | 2878.5 | 2050 | -28 | 0 | 0 | 2078 | 1134.5425 | 1134.5425 | 1134.5425 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -32.0366 | 1102.5058 | -2750 | -200 | -1847.4942 | 46.19% | 68.94% | 95% | 0% | 2078 | -28
[5 empty] | 2019-04-30 | 48 | 2879 | 1936 | -27 | 0 | 0 | 1963 | 954.4106 | 954.4106 | 954.4106 | 1745.4246 | 780 | 200 | 2725.4246 | 68.14% | 95% | 0% | -30.8924 | 923.5181 | -2750 | -200 | -2026.4819 | 50.66% | 68.94% | 95% | 0% | 1963 | -27
[5 empty] | 2019-05-01 | 1 | 2879.5 | 1844 | -26 | 0 | 0 | 1870 | 808.7387 | 808.7387 | 808.7387 | 1743.8582 | 780 | 200 | 2723.8582 | 68.1% | 95% | 0% | -29.7483 | 778.9904 | -2750 | -200 | -2171.0096 | 54.28% | 68.94% | 95% | 0% | 1870 | -26
[5 empty] | 2019-05-01 | 2 | 2880 | 1795 | -26 | 0 | 0 | 1821 | 731.9868 | 731.9868 | 731.9868 | 1743.8582 | 780 | 200 | 2723.8582 | 68.1% | 95% | 0% | -29.7483 | 702.2385 | -2750 | -200 | -2247.7615 | 56.19% | 68.93% | 95% | 0% | 1821 | -26
[5 empty] | 2019-05-01 | 3 | 2880.5 | 1781 | -25 | 0 | 0 | 1806 | 708.4913 | 708.4913 | 708.4913 | 1743.8582 | 780 | 200 | 2723.8582 | 68.1% | 95% | 0% | -28.6041 | 679.8872 | -2750 | -200 | -2270.1128 | 56.75% | 68.93% | 95% | 0% | 1806 | -25
[5 empty] | 2019-05-01 | 4 | 2881 | 1805 | -25 | 0 | 0 | 1830 | 746.0841 | 746.0841 | 746.0841 | 1743.8582 | 780 | 200 | 2723.8582 | 68.1% | 95% | 0% | -28.6041 | 717.48 | -2750 | -200 | -2232.52 | 55.81% | 68.93% | 95% | 0% | 1830 | -25
[5 empty] | 2019-05-01 | 5 | 2881.5 | 1779 | -24 | 0 | 0 | 1803 | 703.7923 | 703.7923 | 703.7923 | 1743.8582 | 780 | 200 | 2723.8582 | 68.1% | 95% | 0% | -27.46 | 676.3323 | -2750 | -200 | -2273.6677 | 56.84% | 68.93% | 95% | 0% | 1803 | -24
[5 empty] | 2019-05-01 | 6 | 2882 | 1757 | -24 | 0 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 1743.8582 | 780 | 200 | 2723.8582 | 68.1% | 95% | 0% | -27.46 | 641.8723 | -2750 | -200 | -2308.1277 | 57.7% | 68.93% | 95% | 0% | 1781 | -24
[5 empty] | 2019-05-01 | 7 | 2882.5 | 1742 | -23 | 0 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 1743.8582 | 780 | 200 | 2723.8582 | 68.1% | 95% | 0% | -26.3158 | 617.9546 | -2750 | -200 | -2332.0454 | 58.3% | 68.93% | 95% | 0% | 1765 | -23
[5 empty] | 2019-05-01 | 8 | 2883 | 1738 | -22 | 0 | 0 | 1760 | 636.4386 | 636.4386 | 636.4386 | 1743.8582 | 780 | 200 | 2723.8582 | 68.1% | 95% | 0% | -25.1716 | 611.267 | -2750 | -200 | -2338.733 | 58.47% | 68.93% | 95% | 0% | 1760 | -22
[5 empty] | 2019-05-01 | 9 | 2883.5 | 1740 | -22 | 0 | 0 | 1762 | 639.5713 | 639.5713 | 639.5713 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -25.1716 | 614.3997 | -2750 | -200 | -2335.6003 | 58.39% | 68.93% | 95% | 0% | 1762 | -22
[5 empty] | 2019-05-01 | 10 | 2884 | 1753 | -22 | 0 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -25.1716 | 634.7624 | -2750 | -200 | -2315.2376 | 57.88% | 68.92% | 95% | 0% | 1775 | -22
[5 empty] | 2019-05-01 | 11 | 2884.5 | 1806 | -21 | 0 | 0 | 1827 | 741.385 | 741.385 | 741.385 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -24.0275 | 717.3575 | -2750 | -200 | -2232.6425 | 55.82% | 68.92% | 95% | 0% | 1827 | -21
[5 empty] | 2019-05-01 | 12 | 2885 | 1864 | -22 | 0 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -25.1716 | 808.6289 | -2750 | -200 | -2141.3711 | 53.53% | 68.92% | 95% | 0% | 1886 | -22
[5 empty] | 2019-05-01 | 13 | 2885.5 | 2049 | -33 | 0 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -37.7574 | 1103.0505 | -2750 | -200 | -1846.9495 | 46.17% | 68.91% | 95% | 0% | 2082 | -33
[5 empty] | 2019-05-01 | 14 | 2886 | 2232 | -55 | 0 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -62.9291 | 1398.9836 | -2750 | -200 | -1551.0164 | 38.78% | 68.91% | 95% | 0% | 2287 | -55
[5 empty] | 2019-05-01 | 15 | 2886.5 | 2405 | -85 | 1 | 0 | 2490 | 1779.8846 | 1779.8846 | 1779.8846 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -97.254 | 1682.6306 | -3550 | -400 | -2267.3694 | 56.68% | 68.91% | 95% | 0% | 2490 | -85
[5 empty] | 2019-05-01 | 16 | 2887 | 2463 | -121 | 1 | 0 | 2584 | 1927.1228 | 1927.1228 | 1927.1228 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -138.4439 | 1788.6789 | -3550 | -400 | -2161.3211 | 54.03% | 68.91% | 95% | 0% | 2584 | -121
[5 empty] | 2019-05-01 | 17 | 2887.5 | 2466 | -161 | 1 | 0 | 2627 | 1994.4765 | 1994.4765 | 1994.4765 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -184.2105 | 1810.266 | -3550 | -400 | -2139.734 | 53.49% | 68.9% | 95% | 0% | 2627 | -161
[5 empty] | 2019-05-01 | 18 | 2888 | 2388 | -206 | 1 | 0 | 2594 | 1942.7865 | 1942.7865 | 1942.7865 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -235.6979 | 1707.0885 | -3550 | -400 | -2242.9115 | 56.07% | 68.9% | 95% | 0% | 2594 | -206
[5 empty] | 2019-05-01 | 19 | 2888.5 | 2342 | -249 | 1 | 0 | 2591 | 1938.0874 | 1938.0874 | 1938.0874 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -284.897 | 1653.1904 | -3550 | -400 | -2296.8096 | 57.42% | 68.9% | 95% | 0% | 2591 | -249
[5 empty] | 2019-05-01 | 20 | 2889 | 2267 | -293 | 1 | 0 | 2560 | 1889.5301 | 1889.5301 | 1889.5301 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -335.2403 | 1554.2898 | -3550 | -400 | -2395.7102 | 59.89% | 68.9% | 95% | 0% | 2560 | -293
[5 empty] | 2019-05-01 | 21 | 2889.5 | 2182 | -329 | 1 | 0 | 2511 | 1812.7782 | 1812.7782 | 1812.7782 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -376.4302 | 1436.348 | -3550 | -400 | -2513.652 | 62.84% | 68.9% | 95% | 0% | 2511 | -329
[5 empty] | 2019-05-01 | 22 | 2890 | 2129 | -350 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -400.4577 | 1362.1969 | -3550 | -400 | -2587.8031 | 64.7% | 68.9% | 95% | 0% | 2479 | -350
[5 empty] | 2019-05-01 | 23 | 2890.5 | 2121 | -361 | 1 | 0 | 2482 | 1767.3537 | 1767.3537 | 1767.3537 | 1742.2918 | 780 | 200 | 2722.2918 | 68.06% | 95% | 0% | -413.0435 | 1354.3102 | -3550 | -400 | -2595.6898 | 64.89% | 68.89% | 95% | 0% | 2482 | -361
[5 empty] | 2019-05-01 | 24 | 2891 | 2124 | -357 | 1 | 0 | 2481 | 1765.7873 | 1765.7873 | 1765.7873 | 1740.7255 | 780 | 200 | 2720.7255 | 68.02% | 95% | 0% | -408.4668 | 1357.3205 | -3550 | -400 | -2592.6795 | 64.82% | 68.89% | 95% | 0% | 2481 | -357
[5 empty] | 2019-05-01 | 25 | 2891.5 | 2151 | -351 | 1 | 0 | 2502 | 1798.681 | 1798.681 | 1798.681 | 1740.7255 | 780 | 200 | 2720.7255 | 68.02% | 95% | 0% | -401.6018 | 1397.0791 | -3550 | -400 | -2552.9209 | 63.82% | 68.88% | 95% | 0% | 2502 | -351
[5 empty] | 2019-05-01 | 26 | 2892 | 2146 | -352 | 1 | 0 | 2498 | 1792.4155 | 1792.4155 | 1792.4155 | 1740.7255 | 780 | 200 | 2720.7255 | 68.02% | 95% | 0% | -402.746 | 1389.6695 | -3550 | -400 | -2560.3305 | 64.01% | 68.88% | 95% | 0% | 2498 | -352
[5 empty] | 2019-05-01 | 27 | 2892.5 | 2140 | -341 | 1 | 0 | 2481 | 1765.7873 | 1765.7873 | 1765.7873 | 1740.7255 | 780 | 200 | 2720.7255 | 68.02% | 95% | 0% | -390.1602 | 1375.6271 | -3550 | -400 | -2574.3729 | 64.36% | 68.88% | 95% | 0% | 2481 | -341
[5 empty] | 2019-05-01 | 28 | 2893 | 2133 | -330 | 1 | 0 | 2463 | 1737.5927 | 1737.5927 | 1737.5927 | 1740.7255 | 780 | 200 | 2720.7255 | 68.02% | 95% | 0% | -377.5744 | 1360.0184 | -3550 | -400 | -2589.9816 | 64.75% | 68.88% | 95% | 0% | 2463 | -330
[5 empty] | 2019-05-01 | 29 | 2893.5 | 2146 | -313 | 1 | 0 | 2459 | 1731.3273 | 1731.3273 | 1731.3273 | 1740.7255 | 780 | 200 | 2720.7255 | 68.02% | 95% | 0% | -358.1236 | 1373.2037 | -3550 | -400 | -2576.7963 | 64.42% | 68.88% | 95% | 0% | 2459 | -313
[5 empty] | 2019-05-01 | 30 | 2894 | 2154 | -300 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 1740.7255 | 780 | 200 | 2720.7255 | 68.02% | 95% | 0% | -343.2494 | 1380.246 | -3550 | -400 | -2569.754 | 64.24% | 68.86% | 95% | 0% | 2454 | -300
[5 empty] | 2019-05-01 | 31 | 2894.5 | 2196 | -274 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 1740.7255 | 780 | 200 | 2720.7255 | 68.02% | 95% | 0% | -313.5011 | 1435.0562 | -3550 | -400 | -2514.9438 | 62.87% | 68.86% | 95% | 0% | 2470 | -274
[5 empty] | 2019-05-01 | 32 | 2895 | 2256 | -258 | 1 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 1740.7255 | 780 | 200 | 2720.7255 | 68.02% | 95% | 0% | -295.1945 | 1522.2828 | -3550 | -400 | -2427.7172 | 60.69% | 68.86% | 95% | 0% | 2514 | -258
[5 empty] | 2019-05-01 | 33 | 2895.5 | 2327 | -239 | 1 | 0 | 2566 | 1898.9283 | 1898.9283 | 1898.9283 | 1740.7255 | 780 | 200 | 2720.7255 | 68.02% | 95% | 0% | -273.4554 | 1625.4729 | -3550 | -400 | -2324.5271 | 58.11% | 68.86% | 95% | 0% | 2566 | -239
[5 empty] | 2019-05-01 | 34 | 2896 | 2382 | -219 | 1 | 0 | 2601 | 1953.751 | 1953.751 | 1953.751 | 1740.7255 | 780 | 200 | 2720.7255 | 68.02% | 95% | 0% | -250.5721 | 1703.1789 | -3550 | -400 | -2246.8211 | 56.17% | 68.86% | 95% | 0% | 2601 | -219
[5 empty] | 2019-05-01 | 35 | 2896.5 | 2460 | -183 | 1 | 0 | 2643 | 2019.5383 | 2019.5383 | 2019.5383 | 1740.7255 | 780 | 200 | 2720.7255 | 68.02% | 95% | 0% | -209.3822 | 1810.1562 | -3550 | -400 | -2139.8438 | 53.5% | 68.86% | 95% | 0% | 2643 | -183
[5 empty] | 2019-05-01 | 36 | 2897 | 2497 | -161 | 1 | 0 | 2658 | 2043.0338 | 2043.0338 | 2043.0338 | 1739.1591 | 780 | 200 | 2719.1591 | 67.98% | 95% | 0% | -184.2105 | 1858.8233 | -3550 | -400 | -2091.1767 | 52.28% | 68.86% | 95% | 0% | 2658 | -161
[5 empty] | 2019-05-01 | 37 | 2897.5 | 2541 | -137 | 1 | 0 | 2678 | 2074.3611 | 2074.3611 | 2074.3611 | 1739.1591 | 780 | 200 | 2719.1591 | 67.98% | 95% | 0% | -156.7506 | 1917.6105 | -3550 | -400 | -2032.3895 | 50.81% | 68.86% | 95% | 0% | 2678 | -137
[5 empty] | 2019-05-01 | 38 | 2898 | 2581 | -112 | 1 | 0 | 2693 | 2097.8566 | 2097.8566 | 2097.8566 | 1739.1591 | 780 | 200 | 2719.1591 | 67.98% | 95% | 0% | -128.1465 | 1969.7101 | -3550 | -400 | -1980.2899 | 49.51% | 68.85% | 95% | 0% | 2693 | -112
[5 empty] | 2019-05-01 | 39 | 2898.5 | 2598 | -87 | 1 | 0 | 2685 | 2085.3256 | 2085.3256 | 2085.3256 | 1739.1591 | 780 | 200 | 2719.1591 | 67.98% | 95% | 0% | -99.5423 | 1985.7833 | -3550 | -400 | -1964.2167 | 49.11% | 68.85% | 95% | 0% | 2685 | -87
[5 empty] | 2019-05-01 | 40 | 2899 | 2610 | -62 | 1 | 0 | 2672 | 2064.9629 | 2064.9629 | 2064.9629 | 1739.1591 | 780 | 200 | 2719.1591 | 67.98% | 95% | 0% | -70.9382 | 1994.0247 | -3550 | -400 | -1955.9753 | 48.9% | 68.85% | 95% | 0% | 2672 | -62
[5 empty] | 2019-05-01 | 41 | 2899.5 | 2611 | -44 | 1 | 0 | 2655 | 2038.3347 | 2038.3347 | 2038.3347 | 1739.1591 | 780 | 200 | 2719.1591 | 67.98% | 95% | 0% | -50.3432 | 1987.9915 | -3550 | -400 | -1962.0085 | 49.05% | 68.85% | 95% | 0% | 2655 | -44
[5 empty] | 2019-05-01 | 42 | 2900 | 2617 | -41 | 1 | 0 | 2658 | 2043.0338 | 2043.0338 | 2043.0338 | 1739.1591 | 780 | 200 | 2719.1591 | 67.98% | 95% | 0% | -46.9108 | 1996.123 | -3550 | -400 | -1953.877 | 48.85% | 68.85% | 95% | 0% | 2658 | -41
[5 empty] | 2019-05-01 | 43 | 2900.5 | 2582 | -43 | 1 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 1739.1591 | 780 | 200 | 2719.1591 | 67.98% | 95% | 0% | -49.1991 | 1942.1447 | -3550 | -400 | -2007.8553 | 50.2% | 68.84% | 95% | 0% | 2625 | -43
[5 empty] | 2019-05-01 | 44 | 2901 | 2460 | -45 | 0 | 0 | 2505 | 1803.38 | 1803.38 | 1803.38 | 1739.1591 | 780 | 200 | 2719.1591 | 67.98% | 95% | 0% | -51.4874 | 1751.8926 | -2750 | -200 | -1198.1074 | 29.95% | 68.83% | 95% | 0% | 2505 | -45
[5 empty] | 2019-05-01 | 45 | 2901.5 | 2313 | -47 | 0 | 0 | 2360 | 1576.2572 | 1576.2572 | 1576.2572 | 1739.1591 | 780 | 200 | 2719.1591 | 67.98% | 95% | 0% | -53.7757 | 1522.4815 | -2750 | -200 | -1427.5185 | 35.69% | 68.83% | 95% | 0% | 2360 | -47
[5 empty] | 2019-05-01 | 46 | 2902 | 2156 | -50 | 0 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 1739.1591 | 780 | 200 | 2719.1591 | 67.98% | 95% | 0% | -57.2082 | 1277.8289 | -2750 | -200 | -1672.1711 | 41.8% | 68.82% | 95% | 0% | 2206 | -50
[5 empty] | 2019-05-01 | 47 | 2902.5 | 1995 | -51 | 0 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1737.5927 | 780 | 200 | 2717.5927 | 67.94% | 95% | 0% | -58.3524 | 1026.0664 | -2750 | -200 | -1923.9336 | 48.1% | 68.82% | 95% | 0% | 2046 | -51
[5 empty] | 2019-05-01 | 48 | 2903 | 1865 | -52 | 0 | 0 | 1917 | 882.3578 | 882.3578 | 882.3578 | 1737.5927 | 780 | 200 | 2717.5927 | 67.94% | 95% | 0% | -59.4966 | 822.8612 | -2750 | -200 | -2127.1388 | 53.18% | 68.82% | 95% | 0% | 1917 | -52
[5 empty] | 2019-05-02 | 1 | 2903.5 | 1782 | -52 | 0 | 0 | 1834 | 752.3495 | 752.3495 | 752.3495 | 1737.5927 | 780 | 200 | 2717.5927 | 67.94% | 95% | 0% | -59.4966 | 692.853 | -2750 | -200 | -2257.147 | 56.43% | 68.81% | 95% | 0% | 1834 | -52
[5 empty] | 2019-05-02 | 2 | 2904 | 1730 | -51 | 0 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 1737.5927 | 780 | 200 | 2717.5927 | 67.94% | 95% | 0% | -58.3524 | 610.9798 | -2750 | -200 | -2339.0202 | 58.48% | 68.81% | 95% | 0% | 1781 | -51
[5 empty] | 2019-05-02 | 3 | 2904.5 | 1713 | -53 | 0 | 0 | 1766 | 645.8368 | 645.8368 | 645.8368 | 1737.5927 | 780 | 200 | 2717.5927 | 67.94% | 95% | 0% | -60.6407 | 585.196 | -2750 | -200 | -2364.804 | 59.12% | 68.81% | 95% | 0% | 1766 | -53
[5 empty] | 2019-05-02 | 4 | 2905 | 1723 | -54 | 0 | 0 | 1777 | 663.0668 | 663.0668 | 663.0668 | 1737.5927 | 780 | 200 | 2717.5927 | 67.94% | 95% | 0% | -61.7849 | 601.2819 | -2750 | -200 | -2348.7181 | 58.72% | 68.81% | 95% | 0% | 1777 | -54
[5 empty] | 2019-05-02 | 5 | 2905.5 | 1703 | -55 | 0 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 1737.5927 | 780 | 200 | 2717.5927 | 67.94% | 95% | 0% | -62.9291 | 570.3768 | -2750 | -200 | -2379.6232 | 59.49% | 68.81% | 95% | 0% | 1758 | -55
[5 empty] | 2019-05-02 | 6 | 2906 | 1680 | -56 | 0 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 1737.5927 | 780 | 200 | 2717.5927 | 67.94% | 95% | 0% | -64.0732 | 534.7726 | -2750 | -200 | -2415.2274 | 60.38% | 68.81% | 95% | 0% | 1736 | -56
[5 empty] | 2019-05-02 | 7 | 2906.5 | 1660 | -57 | 0 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 1737.5927 | 780 | 200 | 2717.5927 | 67.94% | 95% | 0% | -65.2174 | 503.8675 | -2750 | -200 | -2446.1325 | 61.15% | 68.81% | 95% | 0% | 1717 | -57
[5 empty] | 2019-05-02 | 8 | 2907 | 1640 | -59 | 0 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 1737.5927 | 780 | 200 | 2717.5927 | 67.94% | 95% | 0% | -67.5057 | 473.3846 | -2750 | -200 | -2476.6154 | 61.92% | 68.8% | 95% | 0% | 1699 | -59
[5 empty] | 2019-05-02 | 9 | 2907.5 | 1644 | -59 | 0 | 0 | 1703 | 547.1558 | 547.1558 | 547.1558 | 1736.0264 | 780 | 200 | 2716.0264 | 67.9% | 95% | 0% | -67.5057 | 479.6501 | -2750 | -200 | -2470.3499 | 61.76% | 68.79% | 95% | 0% | 1703 | -59
[5 empty] | 2019-05-02 | 10 | 2908 | 1646 | -59 | 0 | 0 | 1705 | 550.2885 | 550.2885 | 550.2885 | 1736.0264 | 780 | 200 | 2716.0264 | 67.9% | 95% | 0% | -67.5057 | 482.7828 | -2750 | -200 | -2467.2172 | 61.68% | 68.79% | 95% | 0% | 1705 | -59
[5 empty] | 2019-05-02 | 11 | 2908.5 | 1702 | -61 | 0 | 0 | 1763 | 641.1377 | 641.1377 | 641.1377 | 1736.0264 | 780 | 200 | 2716.0264 | 67.9% | 95% | 0% | -69.7941 | 571.3436 | -2750 | -200 | -2378.6564 | 59.47% | 68.79% | 95% | 0% | 1763 | -61
[5 empty] | 2019-05-02 | 12 | 2909 | 1765 | -65 | 0 | 0 | 1830 | 746.0841 | 746.0841 | 746.0841 | 1736.0264 | 780 | 200 | 2716.0264 | 67.9% | 95% | 0% | -74.3707 | 671.7134 | -2750 | -200 | -2278.2866 | 56.96% | 68.79% | 95% | 0% | 1830 | -65
[5 empty] | 2019-05-02 | 13 | 2909.5 | 1946 | -80 | 1 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 1736.0264 | 780 | 200 | 2716.0264 | 67.9% | 95% | 0% | -91.5332 | 961.5583 | -3550 | -400 | -2988.4417 | 74.71% | 68.78% | 95% | 0% | 2026 | -80
[5 empty] | 2019-05-02 | 14 | 2910 | 2116 | -113 | 1 | 0 | 2229 | 1371.0635 | 1371.0635 | 1371.0635 | 1736.0264 | 780 | 200 | 2716.0264 | 67.9% | 95% | 0% | -129.2906 | 1241.7729 | -3550 | -400 | -2708.2271 | 67.71% | 68.78% | 95% | 0% | 2229 | -113
[5 empty] | 2019-05-02 | 15 | 2910.5 | 2263 | -165 | 1 | 0 | 2428 | 1682.77 | 1682.77 | 1682.77 | 1736.0264 | 780 | 200 | 2716.0264 | 67.9% | 95% | 0% | -188.7872 | 1493.9828 | -3550 | -400 | -2456.0172 | 61.4% | 68.78% | 95% | 0% | 2428 | -165
[5 empty] | 2019-05-02 | 16 | 2911 | 2322 | -211 | 1 | 0 | 2533 | 1847.2383 | 1847.2383 | 1847.2383 | 1736.0264 | 780 | 200 | 2716.0264 | 67.9% | 95% | 0% | -241.4188 | 1605.8195 | -3550 | -400 | -2344.1805 | 58.6% | 68.77% | 95% | 0% | 2533 | -211
[5 empty] | 2019-05-02 | 17 | 2911.5 | 2308 | -256 | 1 | 0 | 2564 | 1895.7955 | 1895.7955 | 1895.7955 | 1736.0264 | 780 | 200 | 2716.0264 | 67.9% | 95% | 0% | -292.9062 | 1602.8894 | -3550 | -400 | -2347.1106 | 58.68% | 68.77% | 95% | 0% | 2564 | -256
[5 empty] | 2019-05-02 | 18 | 2912 | 2208 | -318 | 1 | 0 | 2526 | 1836.2737 | 1836.2737 | 1836.2737 | 1736.0264 | 780 | 200 | 2716.0264 | 67.9% | 95% | 0% | -363.8444 | 1472.4293 | -3550 | -400 | -2477.5707 | 61.94% | 68.76% | 95% | 0% | 2526 | -318
[5 empty] | 2019-05-02 | 19 | 2912.5 | 2113 | -375 | 1 | 0 | 2488 | 1776.7519 | 1776.7519 | 1776.7519 | 1736.0264 | 780 | 200 | 2716.0264 | 67.9% | 95% | 0% | -429.0618 | 1347.6901 | -3550 | -400 | -2602.3099 | 65.06% | 68.75% | 95% | 0% | 2488 | -375
[5 empty] | 2019-05-02 | 20 | 2913 | 2043 | -424 | 1 | 0 | 2467 | 1743.8582 | 1743.8582 | 1743.8582 | 1734.46 | 780 | 200 | 2714.46 | 67.86% | 95% | 0% | -485.1259 | 1258.7323 | -3550 | -400 | -2691.2677 | 67.28% | 68.75% | 95% | 0% | 2467 | -424
[5 empty] | 2019-05-02 | 21 | 2913.5 | 1994 | -456 | 1 | 0 | 2450 | 1717.23 | 1717.23 | 1717.23 | 1734.46 | 780 | 200 | 2714.46 | 67.86% | 95% | 0% | -521.7391 | 1195.4909 | -3550 | -400 | -2754.5091 | 68.86% | 68.75% | 95% | 0% | 2450 | -456
[5 empty] | 2019-05-02 | 22 | 2914 | 1936 | -482 | 1 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 1734.46 | 780 | 200 | 2714.46 | 67.86% | 95% | 0% | -551.4874 | 1115.6189 | -3550 | -400 | -2834.3811 | 70.86% | 68.75% | 95% | 0% | 2418 | -482
[5 empty] | 2019-05-02 | 23 | 2914.5 | 1886 | -514 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 1734.46 | 780 | 200 | 2714.46 | 67.86% | 95% | 0% | -588.1007 | 1050.8111 | -3550 | -400 | -2899.1889 | 72.48% | 68.75% | 95% | 0% | 2400 | -514
[5 empty] | 2019-05-02 | 24 | 2915 | 1907 | -477 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1732.8937 | 780 | 200 | 2712.8937 | 67.82% | 95% | 0% | -545.7666 | 1068.0834 | -3550 | -400 | -2881.9166 | 72.05% | 68.74% | 95% | 0% | 2384 | -477
[5 empty] | 2019-05-02 | 25 | 2915.5 | 1936 | -462 | 1 | 0 | 2398 | 1635.7791 | 1635.7791 | 1635.7791 | 1732.8937 | 780 | 200 | 2712.8937 | 67.82% | 95% | 0% | -528.6041 | 1107.1749 | -3550 | -400 | -2842.8251 | 71.07% | 68.74% | 95% | 0% | 2398 | -462
[5 empty] | 2019-05-02 | 26 | 2916 | 1931 | -438 | 1 | 0 | 2369 | 1590.3545 | 1590.3545 | 1590.3545 | 1732.8937 | 780 | 200 | 2712.8937 | 67.82% | 95% | 0% | -501.1442 | 1089.2103 | -3550 | -400 | -2860.7897 | 71.52% | 68.73% | 95% | 0% | 2369 | -438
[5 empty] | 2019-05-02 | 27 | 2916.5 | 1967 | -428 | 1 | 0 | 2395 | 1631.08 | 1631.08 | 1631.08 | 1732.8937 | 780 | 200 | 2712.8937 | 67.82% | 95% | 0% | -489.7025 | 1141.3774 | -3550 | -400 | -2808.6226 | 70.22% | 68.73% | 95% | 0% | 2395 | -428
[5 empty] | 2019-05-02 | 28 | 2917 | 1918 | -478 | 1 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 1732.8937 | 780 | 200 | 2712.8937 | 67.82% | 95% | 0% | -546.9108 | 1085.7356 | -3550 | -400 | -2864.2644 | 71.61% | 68.73% | 95% | 0% | 2396 | -478
[5 empty] | 2019-05-02 | 29 | 2917.5 | 1924 | -470 | 1 | 0 | 2394 | 1629.5136 | 1629.5136 | 1629.5136 | 1732.8937 | 780 | 200 | 2712.8937 | 67.82% | 95% | 0% | -537.7574 | 1091.7562 | -3550 | -400 | -2858.2438 | 71.46% | 68.72% | 95% | 0% | 2394 | -470
[5 empty] | 2019-05-02 | 30 | 2918 | 1944 | -441 | 1 | 0 | 2385 | 1615.4163 | 1615.4163 | 1615.4163 | 1732.8937 | 780 | 200 | 2712.8937 | 67.82% | 95% | 0% | -504.5767 | 1110.8397 | -3550 | -400 | -2839.1603 | 70.98% | 68.71% | 95% | 0% | 2385 | -441
[5 empty] | 2019-05-02 | 31 | 2918.5 | 2001 | -388 | 1 | 0 | 2389 | 1621.6818 | 1621.6818 | 1621.6818 | 1732.8937 | 780 | 200 | 2712.8937 | 67.82% | 95% | 0% | -443.9359 | 1177.7459 | -3550 | -400 | -2772.2541 | 69.31% | 68.71% | 95% | 0% | 2389 | -388
[5 empty] | 2019-05-02 | 32 | 2919 | 2045 | -378 | 1 | 0 | 2423 | 1674.9382 | 1674.9382 | 1674.9382 | 1731.3273 | 780 | 200 | 2711.3273 | 67.78% | 95% | 0% | -432.4943 | 1242.4439 | -3550 | -400 | -2707.5561 | 67.69% | 68.71% | 95% | 0% | 2423 | -378
[5 empty] | 2019-05-02 | 33 | 2919.5 | 2154 | -326 | 1 | 0 | 2480 | 1764.2209 | 1764.2209 | 1764.2209 | 1731.3273 | 780 | 200 | 2711.3273 | 67.78% | 95% | 0% | -372.9977 | 1391.2232 | -3550 | -400 | -2558.7768 | 63.97% | 68.71% | 95% | 0% | 2480 | -326
[5 empty] | 2019-05-02 | 34 | 2920 | 2286 | -277 | 1 | 0 | 2563 | 1894.2292 | 1894.2292 | 1894.2292 | 1731.3273 | 780 | 200 | 2711.3273 | 67.78% | 95% | 0% | -316.9336 | 1577.2955 | -3550 | -400 | -2372.7045 | 59.32% | 68.71% | 95% | 0% | 2563 | -277
[5 empty] | 2019-05-02 | 35 | 2920.5 | 2330 | -282 | 1 | 0 | 2612 | 1970.981 | 1970.981 | 1970.981 | 1731.3273 | 780 | 200 | 2711.3273 | 67.78% | 95% | 0% | -322.6545 | 1648.3266 | -3550 | -400 | -2301.6734 | 57.54% | 68.71% | 95% | 0% | 2612 | -282
[5 empty] | 2019-05-02 | 36 | 2921 | 2401 | -226 | 1 | 0 | 2627 | 1994.4765 | 1994.4765 | 1994.4765 | 1731.3273 | 780 | 200 | 2711.3273 | 67.78% | 95% | 0% | -258.5812 | 1735.8953 | -3550 | -400 | -2214.1047 | 55.35% | 68.71% | 95% | 0% | 2627 | -226
[5 empty] | 2019-05-02 | 37 | 2921.5 | 2472 | -174 | 1 | 0 | 2646 | 2024.2374 | 2024.2374 | 2024.2374 | 1731.3273 | 780 | 200 | 2711.3273 | 67.78% | 95% | 0% | -199.0847 | 1825.1528 | -3550 | -400 | -2124.8472 | 53.12% | 68.7% | 95% | 0% | 2646 | -174
[5 empty] | 2019-05-02 | 38 | 2922 | 2522 | -154 | 1 | 0 | 2676 | 2071.2284 | 2071.2284 | 2071.2284 | 1731.3273 | 780 | 200 | 2711.3273 | 67.78% | 95% | 0% | -176.2014 | 1895.027 | -3550 | -400 | -2054.973 | 51.37% | 68.7% | 95% | 0% | 2676 | -154
[5 empty] | 2019-05-02 | 39 | 2922.5 | 2565 | -118 | 1 | 0 | 2683 | 2082.1929 | 2082.1929 | 2082.1929 | 1731.3273 | 780 | 200 | 2711.3273 | 67.78% | 95% | 0% | -135.0114 | 1947.1815 | -3550 | -400 | -2002.8185 | 50.07% | 68.7% | 95% | 0% | 2683 | -118
[5 empty] | 2019-05-02 | 40 | 2923 | 2581 | -93 | 1 | 0 | 2674 | 2068.0956 | 2068.0956 | 2068.0956 | 1731.3273 | 780 | 200 | 2711.3273 | 67.78% | 95% | 0% | -106.4073 | 1961.6883 | -3550 | -400 | -1988.3117 | 49.71% | 68.69% | 95% | 0% | 2674 | -93
[5 empty] | 2019-05-02 | 41 | 2923.5 | 2568 | -76 | 1 | 0 | 2644 | 2021.1047 | 2021.1047 | 2021.1047 | 1731.3273 | 780 | 200 | 2711.3273 | 67.78% | 95% | 0% | -86.9565 | 1934.1482 | -3550 | -400 | -2015.8518 | 50.4% | 68.69% | 95% | 0% | 2644 | -76
[5 empty] | 2019-05-02 | 42 | 2924 | 2589 | -69 | 1 | 0 | 2658 | 2043.0338 | 2043.0338 | 2043.0338 | 1731.3273 | 780 | 200 | 2711.3273 | 67.78% | 95% | 0% | -78.9474 | 1964.0864 | -3550 | -400 | -1985.9136 | 49.65% | 68.68% | 95% | 0% | 2658 | -69
[5 empty] | 2019-05-02 | 43 | 2924.5 | 2554 | -67 | 1 | 0 | 2621 | 1985.0783 | 1985.0783 | 1985.0783 | 1731.3273 | 780 | 200 | 2711.3273 | 67.78% | 95% | 0% | -76.659 | 1908.4193 | -3550 | -400 | -2041.5807 | 51.04% | 68.67% | 95% | 0% | 2621 | -67
[5 empty] | 2019-05-02 | 44 | 2925 | 2457 | -64 | 0 | 0 | 2521 | 1828.4419 | 1828.4419 | 1828.4419 | 1729.7609 | 780 | 200 | 2709.7609 | 67.74% | 95% | 0% | -73.2265 | 1755.2153 | -2750 | -200 | -1194.7847 | 29.87% | 68.67% | 95% | 0% | 2521 | -64
[5 empty] | 2019-05-02 | 45 | 2925.5 | 2325 | -62 | 0 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 1729.7609 | 780 | 200 | 2709.7609 | 67.74% | 95% | 0% | -70.9382 | 1547.6108 | -2750 | -200 | -1402.3892 | 35.06% | 68.67% | 95% | 0% | 2387 | -62
[5 empty] | 2019-05-02 | 46 | 2926 | 2175 | -60 | 0 | 0 | 2235 | 1380.4617 | 1380.4617 | 1380.4617 | 1729.7609 | 780 | 200 | 2709.7609 | 67.74% | 95% | 0% | -68.6499 | 1311.8118 | -2750 | -200 | -1638.1882 | 40.95% | 68.67% | 95% | 0% | 2235 | -60
[5 empty] | 2019-05-02 | 47 | 2926.5 | 2016 | -58 | 0 | 0 | 2074 | 1128.277 | 1128.277 | 1128.277 | 1729.7609 | 780 | 200 | 2709.7609 | 67.74% | 95% | 0% | -66.3616 | 1061.9154 | -2750 | -200 | -1888.0846 | 47.2% | 68.67% | 95% | 0% | 2074 | -58
[5 empty] | 2019-05-02 | 48 | 2927 | 1897 | -57 | 0 | 0 | 1954 | 940.3133 | 940.3133 | 940.3133 | 1729.7609 | 780 | 200 | 2709.7609 | 67.74% | 95% | 0% | -65.2174 | 875.0959 | -2750 | -200 | -2074.9041 | 51.87% | 68.67% | 95% | 0% | 1954 | -57
[5 empty] | 2019-05-03 | 1 | 2927.5 | 1800 | -54 | 0 | 0 | 1854 | 783.6768 | 783.6768 | 783.6768 | 1729.7609 | 780 | 200 | 2709.7609 | 67.74% | 95% | 0% | -61.7849 | 721.8919 | -2750 | -200 | -2228.1081 | 55.7% | 68.67% | 95% | 0% | 1854 | -54
[5 empty] | 2019-05-03 | 2 | 2928 | 1761 | -51 | 0 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 1729.7609 | 780 | 200 | 2709.7609 | 67.74% | 95% | 0% | -58.3524 | 659.5371 | -2750 | -200 | -2290.4629 | 57.26% | 68.66% | 95% | 0% | 1812 | -51
[5 empty] | 2019-05-03 | 3 | 2928.5 | 1744 | -50 | 0 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 1729.7609 | 780 | 200 | 2709.7609 | 67.74% | 95% | 0% | -57.2082 | 632.4867 | -2750 | -200 | -2317.5133 | 57.94% | 68.66% | 95% | 0% | 1794 | -50
[5 empty] | 2019-05-03 | 4 | 2929 | 1760 | -50 | 1 | 0 | 1810 | 714.7568 | 714.7568 | 714.7568 | 1729.7609 | 780 | 200 | 2709.7609 | 67.74% | 95% | 0% | -57.2082 | 657.5486 | -3550 | -400 | -3292.4514 | 82.31% | 68.66% | 95% | 0% | 1810 | -50
[5 empty] | 2019-05-03 | 5 | 2929.5 | 1742 | -49 | 1 | 0 | 1791 | 684.9959 | 684.9959 | 684.9959 | 1729.7609 | 780 | 200 | 2709.7609 | 67.74% | 95% | 0% | -56.0641 | 628.9318 | -3550 | -400 | -3321.0682 | 83.03% | 68.65% | 95% | 0% | 1791 | -49
[5 empty] | 2019-05-03 | 6 | 2930 | 1724 | -48 | 1 | 0 | 1772 | 655.235 | 655.235 | 655.235 | 1729.7609 | 780 | 200 | 2709.7609 | 67.74% | 95% | 0% | -54.9199 | 600.315 | -3550 | -400 | -3349.685 | 83.74% | 68.65% | 95% | 0% | 1772 | -48
[5 empty] | 2019-05-03 | 7 | 2930.5 | 1701 | -47 | 1 | 0 | 1748 | 617.6422 | 617.6422 | 617.6422 | 1729.7609 | 780 | 200 | 2709.7609 | 67.74% | 95% | 0% | -53.7757 | 563.8665 | -3550 | -400 | -3386.1335 | 84.65% | 68.65% | 95% | 0% | 1748 | -47
[5 empty] | 2019-05-03 | 8 | 2931 | 1691 | -46 | 1 | 0 | 1737 | 600.4122 | 600.4122 | 600.4122 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -52.6316 | 547.7806 | -3550 | -400 | -3402.2194 | 85.06% | 68.64% | 95% | 0% | 1737 | -46
[5 empty] | 2019-05-03 | 9 | 2931.5 | 1693 | -46 | 1 | 0 | 1739 | 603.5449 | 603.5449 | 603.5449 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -52.6316 | 550.9134 | -3550 | -400 | -3399.0866 | 84.98% | 68.64% | 95% | 0% | 1739 | -46
[5 empty] | 2019-05-03 | 10 | 2932 | 1720 | -47 | 1 | 0 | 1767 | 647.4031 | 647.4031 | 647.4031 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -53.7757 | 593.6274 | -3550 | -400 | -3356.3726 | 83.91% | 68.63% | 95% | 0% | 1767 | -47
[5 empty] | 2019-05-03 | 11 | 2932.5 | 1767 | -48 | 1 | 0 | 1815 | 722.5886 | 722.5886 | 722.5886 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -54.9199 | 667.6687 | -3550 | -400 | -3282.3313 | 82.06% | 68.63% | 95% | 0% | 1815 | -48
[5 empty] | 2019-05-03 | 12 | 2933 | 1817 | -50 | 1 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -57.2082 | 746.8313 | -3550 | -400 | -3203.1687 | 80.08% | 68.63% | 95% | 0% | 1867 | -50
[5 empty] | 2019-05-03 | 13 | 2933.5 | 2010 | -58 | 1 | 0 | 2068 | 1118.8788 | 1118.8788 | 1118.8788 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -66.3616 | 1052.5173 | -3550 | -400 | -2897.4827 | 72.44% | 68.63% | 95% | 0% | 2068 | -58
[5 empty] | 2019-05-03 | 14 | 2934 | 2198 | -78 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -89.2449 | 1355.4378 | -3550 | -400 | -2594.5622 | 64.86% | 68.63% | 95% | 0% | 2276 | -78
[5 empty] | 2019-05-03 | 15 | 2934.5 | 2369 | -102 | 1 | 0 | 2471 | 1750.1237 | 1750.1237 | 1750.1237 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -116.7048 | 1633.4189 | -3550 | -400 | -2316.5811 | 57.91% | 68.62% | 95% | 0% | 2471 | -102
[5 empty] | 2019-05-03 | 16 | 2935 | 2431 | -124 | 1 | 0 | 2555 | 1881.6983 | 1881.6983 | 1881.6983 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -141.8764 | 1739.8218 | -3550 | -400 | -2210.1782 | 55.25% | 68.62% | 95% | 0% | 2555 | -124
[5 empty] | 2019-05-03 | 17 | 2935.5 | 2460 | -156 | 1 | 0 | 2616 | 1977.2465 | 1977.2465 | 1977.2465 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -178.4897 | 1798.7568 | -3550 | -400 | -2151.2432 | 53.78% | 68.62% | 95% | 0% | 2616 | -156
[5 empty] | 2019-05-03 | 18 | 2936 | 2426 | -190 | 1 | 0 | 2616 | 1977.2465 | 1977.2465 | 1977.2465 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -217.3913 | 1759.8552 | -3550 | -400 | -2190.1448 | 54.75% | 68.62% | 95% | 0% | 2616 | -190
[5 empty] | 2019-05-03 | 19 | 2936.5 | 2404 | -228 | 1 | 0 | 2632 | 2002.3083 | 2002.3083 | 2002.3083 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -260.8696 | 1741.4388 | -3550 | -400 | -2208.5612 | 55.21% | 68.61% | 95% | 0% | 2632 | -228
[5 empty] | 2019-05-03 | 20 | 2937 | 2383 | -242 | 1 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -276.8879 | 1714.4559 | -3550 | -400 | -2235.5441 | 55.89% | 68.61% | 95% | 0% | 2625 | -242
[5 empty] | 2019-05-03 | 21 | 2937.5 | 2332 | -272 | 1 | 0 | 2604 | 1958.4501 | 1958.4501 | 1958.4501 | 1728.1946 | 780 | 200 | 2708.1946 | 67.7% | 95% | 0% | -311.2128 | 1647.2373 | -3550 | -400 | -2302.7627 | 57.57% | 68.61% | 95% | 0% | 2604 | -272
[5 empty] | 2019-05-03 | 22 | 2938 | 2284 | -296 | 1 | 0 | 2580 | 1920.8574 | 1920.8574 | 1920.8574 | 1726.6282 | 780 | 200 | 2706.6282 | 67.67% | 95% | 0% | -338.6728 | 1582.1846 | -3550 | -400 | -2367.8154 | 59.2% | 68.61% | 95% | 0% | 2580 | -296
[5 empty] | 2019-05-03 | 23 | 2938.5 | 2203 | -343 | 1 | 0 | 2546 | 1867.601 | 1867.601 | 1867.601 | 1726.6282 | 780 | 200 | 2706.6282 | 67.67% | 95% | 0% | -392.4485 | 1475.1525 | -3550 | -400 | -2474.8475 | 61.87% | 68.61% | 95% | 0% | 2546 | -343
[5 empty] | 2019-05-03 | 24 | 2939 | 2186 | -359 | 1 | 0 | 2545 | 1866.0346 | 1866.0346 | 1866.0346 | 1726.6282 | 780 | 200 | 2706.6282 | 67.67% | 95% | 0% | -410.7551 | 1455.2795 | -3550 | -400 | -2494.7205 | 62.37% | 68.61% | 95% | 0% | 2545 | -359
[5 empty] | 2019-05-03 | 25 | 2939.5 | 2185 | -378 | 1 | 0 | 2563 | 1894.2292 | 1894.2292 | 1894.2292 | 1726.6282 | 780 | 200 | 2706.6282 | 67.67% | 95% | 0% | -432.4943 | 1461.7349 | -3550 | -400 | -2488.2651 | 62.21% | 68.6% | 95% | 0% | 2563 | -378
[5 empty] | 2019-05-03 | 26 | 2940 | 2138 | -401 | 1 | 0 | 2539 | 1856.6364 | 1856.6364 | 1856.6364 | 1726.6282 | 780 | 200 | 2706.6282 | 67.67% | 95% | 0% | -458.8101 | 1397.8264 | -3550 | -400 | -2552.1736 | 63.8% | 68.59% | 95% | 0% | 2539 | -401
[5 empty] | 2019-05-03 | 27 | 2940.5 | 2120 | -405 | 1 | 0 | 2525 | 1834.7073 | 1834.7073 | 1834.7073 | 1726.6282 | 780 | 200 | 2706.6282 | 67.67% | 95% | 0% | -463.3867 | 1371.3206 | -3550 | -400 | -2578.6794 | 64.47% | 68.59% | 95% | 0% | 2525 | -405
[5 empty] | 2019-05-03 | 28 | 2941 | 2105 | -393 | 1 | 0 | 2498 | 1792.4155 | 1792.4155 | 1792.4155 | 1726.6282 | 780 | 200 | 2706.6282 | 67.67% | 95% | 0% | -449.6568 | 1342.7587 | -3550 | -400 | -2607.2413 | 65.18% | 68.59% | 95% | 0% | 2498 | -393
[5 empty] | 2019-05-03 | 29 | 2941.5 | 2133 | -351 | 1 | 0 | 2484 | 1770.4864 | 1770.4864 | 1770.4864 | 1726.6282 | 780 | 200 | 2706.6282 | 67.67% | 95% | 0% | -401.6018 | 1368.8846 | -3550 | -400 | -2581.1154 | 64.53% | 68.59% | 95% | 0% | 2484 | -351
[5 empty] | 2019-05-03 | 30 | 2942 | 2108 | -352 | 1 | 0 | 2460 | 1732.8937 | 1732.8937 | 1732.8937 | 1725.0618 | 780 | 200 | 2705.0618 | 67.63% | 95% | 0% | -402.746 | 1330.1477 | -3550 | -400 | -2619.8523 | 65.5% | 68.59% | 95% | 0% | 2460 | -352
[5 empty] | 2019-05-03 | 31 | 2942.5 | 2117 | -327 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 1725.0618 | 780 | 200 | 2705.0618 | 67.63% | 95% | 0% | -374.1419 | 1333.6899 | -3550 | -400 | -2616.3101 | 65.41% | 68.58% | 95% | 0% | 2444 | -327
[5 empty] | 2019-05-03 | 32 | 2943 | 2169 | -308 | 1 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 1725.0618 | 780 | 200 | 2705.0618 | 67.63% | 95% | 0% | -352.4027 | 1407.1191 | -3550 | -400 | -2542.8809 | 63.57% | 68.58% | 95% | 0% | 2477 | -308
[5 empty] | 2019-05-03 | 33 | 2943.5 | 2265 | -267 | 1 | 0 | 2532 | 1845.6719 | 1845.6719 | 1845.6719 | 1725.0618 | 780 | 200 | 2705.0618 | 67.63% | 95% | 0% | -305.492 | 1540.1799 | -3550 | -400 | -2409.8201 | 60.25% | 68.58% | 95% | 0% | 2532 | -267
[5 empty] | 2019-05-03 | 34 | 2944 | 2338 | -244 | 1 | 0 | 2582 | 1923.9901 | 1923.9901 | 1923.9901 | 1725.0618 | 780 | 200 | 2705.0618 | 67.63% | 95% | 0% | -279.1762 | 1644.8139 | -3550 | -400 | -2305.1861 | 57.63% | 68.58% | 95% | 0% | 2582 | -244
[5 empty] | 2019-05-03 | 35 | 2944.5 | 2431 | -210 | 1 | 0 | 2641 | 2016.4056 | 2016.4056 | 2016.4056 | 1725.0618 | 780 | 200 | 2705.0618 | 67.63% | 95% | 0% | -240.2746 | 1776.131 | -3550 | -400 | -2173.869 | 54.35% | 68.57% | 95% | 0% | 2641 | -210
[5 empty] | 2019-05-03 | 36 | 2945 | 2478 | -204 | 1 | 0 | 2682 | 2080.6265 | 2080.6265 | 2080.6265 | 1725.0618 | 780 | 200 | 2705.0618 | 67.63% | 95% | 0% | -233.4096 | 1847.2169 | -3550 | -400 | -2102.7831 | 52.57% | 68.56% | 95% | 0% | 2682 | -204
[5 empty] | 2019-05-03 | 37 | 2945.5 | 2505 | -195 | 1 | 0 | 2700 | 2108.8211 | 2108.8211 | 2108.8211 | 1725.0618 | 780 | 200 | 2705.0618 | 67.63% | 95% | 0% | -223.1121 | 1885.709 | -3550 | -400 | -2064.291 | 51.61% | 68.55% | 95% | 0% | 2700 | -195
[5 empty] | 2019-05-03 | 38 | 2946 | 2522 | -168 | 1 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 1725.0618 | 780 | 200 | 2705.0618 | 67.63% | 95% | 0% | -192.2197 | 1900.9378 | -3550 | -400 | -2049.0622 | 51.23% | 68.55% | 95% | 0% | 2690 | -168
[5 empty] | 2019-05-03 | 39 | 2946.5 | 2533 | -140 | 1 | 0 | 2673 | 2066.5293 | 2066.5293 | 2066.5293 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -160.1831 | 1906.3462 | -3550 | -400 | -2043.6538 | 51.09% | 68.55% | 95% | 0% | 2673 | -140
[5 empty] | 2019-05-03 | 40 | 2947 | 2514 | -121 | 1 | 0 | 2635 | 2007.0074 | 2007.0074 | 2007.0074 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -138.4439 | 1868.5635 | -3550 | -400 | -2081.4365 | 52.04% | 68.55% | 95% | 0% | 2635 | -121
[5 empty] | 2019-05-03 | 41 | 2947.5 | 2464 | -113 | 1 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -129.2906 | 1786.8677 | -3550 | -400 | -2163.1323 | 54.08% | 68.54% | 95% | 0% | 2577 | -113
[5 empty] | 2019-05-03 | 42 | 2948 | 2458 | -110 | 1 | 0 | 2568 | 1902.061 | 1902.061 | 1902.061 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -125.8581 | 1776.2029 | -3550 | -400 | -2173.7971 | 54.34% | 68.54% | 95% | 0% | 2568 | -110
[5 empty] | 2019-05-03 | 43 | 2948.5 | 2429 | -110 | 1 | 0 | 2539 | 1856.6364 | 1856.6364 | 1856.6364 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -125.8581 | 1730.7783 | -3550 | -400 | -2219.2217 | 55.48% | 68.54% | 95% | 0% | 2539 | -110
[5 empty] | 2019-05-03 | 44 | 2949 | 2314 | -110 | 0 | 0 | 2424 | 1676.5045 | 1676.5045 | 1676.5045 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -125.8581 | 1550.6464 | -2750 | -200 | -1399.3536 | 34.98% | 68.54% | 95% | 0% | 2424 | -110
[5 empty] | 2019-05-03 | 45 | 2949.5 | 2183 | -109 | 0 | 0 | 2292 | 1469.7444 | 1469.7444 | 1469.7444 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -124.714 | 1345.0305 | -2750 | -200 | -1604.9695 | 40.12% | 68.53% | 95% | 0% | 2292 | -109
[5 empty] | 2019-05-03 | 46 | 2950 | 2050 | -108 | 0 | 0 | 2158 | 1259.8516 | 1259.8516 | 1259.8516 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -123.5698 | 1136.2818 | -2750 | -200 | -1813.7182 | 45.34% | 68.53% | 95% | 0% | 2158 | -108
[5 empty] | 2019-05-03 | 47 | 2950.5 | 1902 | -108 | 0 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -123.5698 | 904.4599 | -2750 | -200 | -2045.5401 | 51.14% | 68.52% | 95% | 0% | 2010 | -108
[5 empty] | 2019-05-03 | 48 | 2951 | 1781 | -107 | 0 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -122.4256 | 714.5076 | -2750 | -200 | -2235.4924 | 55.89% | 68.52% | 95% | 0% | 1888 | -107
[5 empty] | 2019-05-04 | 1 | 2951.5 | 1692 | -104 | 0 | 0 | 1796 | 692.8277 | 692.8277 | 692.8277 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -118.9931 | 573.8346 | -2750 | -200 | -2376.1654 | 59.4% | 68.51% | 95% | 0% | 1796 | -104
[5 empty] | 2019-05-04 | 2 | 2952 | 1636 | -100 | 0 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -114.4165 | 484.4294 | -2750 | -200 | -2465.5706 | 61.64% | 68.51% | 95% | 0% | 1736 | -100
[5 empty] | 2019-05-04 | 3 | 2952.5 | 1623 | -103 | 0 | 0 | 1726 | 583.1822 | 583.1822 | 583.1822 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -117.849 | 465.3332 | -2750 | -200 | -2484.6668 | 62.12% | 68.51% | 95% | 0% | 1726 | -103
[5 empty] | 2019-05-04 | 4 | 2953 | 1628 | -107 | 0 | 0 | 1735 | 597.2795 | 597.2795 | 597.2795 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -122.4256 | 474.8538 | -2750 | -200 | -2475.1462 | 61.88% | 68.51% | 95% | 0% | 1735 | -107
[5 empty] | 2019-05-04 | 5 | 2953.5 | 1598 | -111 | 0 | 0 | 1709 | 556.554 | 556.554 | 556.554 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -127.0023 | 429.5517 | -2750 | -200 | -2520.4483 | 63.01% | 68.51% | 95% | 0% | 1709 | -111
[5 empty] | 2019-05-04 | 6 | 2954 | 1558 | -115 | 0 | 0 | 1673 | 500.1649 | 500.1649 | 500.1649 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -131.5789 | 368.5859 | -2750 | -200 | -2581.4141 | 64.54% | 68.51% | 95% | 0% | 1673 | -115
[5 empty] | 2019-05-04 | 7 | 2954.5 | 1531 | -118 | 0 | 0 | 1649 | 462.5721 | 462.5721 | 462.5721 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -135.0114 | 327.5607 | -2750 | -200 | -2622.4393 | 65.56% | 68.51% | 95% | 0% | 1649 | -118
[5 empty] | 2019-05-04 | 8 | 2955 | 1501 | -122 | 0 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -139.5881 | 282.2586 | -2750 | -200 | -2667.7414 | 66.69% | 68.5% | 95% | 0% | 1623 | -122
[5 empty] | 2019-05-04 | 9 | 2955.5 | 1494 | -122 | 0 | 0 | 1616 | 410.8821 | 410.8821 | 410.8821 | 1723.4955 | 780 | 200 | 2703.4955 | 67.59% | 95% | 0% | -139.5881 | 271.294 | -2750 | -200 | -2678.706 | 66.97% | 68.49% | 95% | 0% | 1616 | -122
[5 empty] | 2019-05-04 | 10 | 2956 | 1479 | -121 | 0 | 0 | 1600 | 385.8203 | 385.8203 | 385.8203 | 1721.9291 | 780 | 200 | 2701.9291 | 67.55% | 95% | 0% | -138.4439 | 247.3763 | -2750 | -200 | -2702.6237 | 67.57% | 68.49% | 95% | 0% | 1600 | -121
[5 empty] | 2019-05-04 | 11 | 2956.5 | 1472 | -124 | 0 | 0 | 1596 | 379.5548 | 379.5548 | 379.5548 | 1721.9291 | 780 | 200 | 2701.9291 | 67.55% | 95% | 0% | -141.8764 | 237.6784 | -2750 | -200 | -2712.3216 | 67.81% | 68.49% | 95% | 0% | 1596 | -124
[5 empty] | 2019-05-04 | 12 | 2957 | 1464 | -131 | 0 | 0 | 1595 | 377.9885 | 377.9885 | 377.9885 | 1721.9291 | 780 | 200 | 2701.9291 | 67.55% | 95% | 0% | -149.8856 | 228.1029 | -2750 | -200 | -2721.8971 | 68.05% | 68.49% | 95% | 0% | 1595 | -131
[5 empty] | 2019-05-04 | 13 | 2957.5 | 1523 | -155 | 0 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 1721.9291 | 780 | 200 | 2701.9291 | 67.55% | 95% | 0% | -177.3455 | 330.6512 | -2750 | -200 | -2619.3488 | 65.48% | 68.48% | 95% | 0% | 1678 | -155
[5 empty] | 2019-05-04 | 14 | 2958 | 1530 | -203 | 0 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 1721.9291 | 780 | 200 | 2701.9291 | 67.55% | 95% | 0% | -232.2654 | 361.8813 | -2750 | -200 | -2588.1187 | 64.7% | 68.48% | 95% | 0% | 1733 | -203
[5 empty] | 2019-05-04 | 15 | 2958.5 | 1568 | -265 | 1 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 1721.9291 | 780 | 200 | 2701.9291 | 67.55% | 95% | 0% | -303.2037 | 447.5795 | -3550 | -400 | -3502.4205 | 87.56% | 68.48% | 95% | 0% | 1833 | -265
[5 empty] | 2019-05-04 | 16 | 2959 | 1546 | -340 | 1 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 1721.9291 | 780 | 200 | 2701.9291 | 67.55% | 95% | 0% | -389.016 | 444.7845 | -3550 | -400 | -3505.2155 | 87.63% | 68.48% | 95% | 0% | 1886 | -340
[5 empty] | 2019-05-04 | 17 | 2959.5 | 1499 | -424 | 1 | 0 | 1923 | 891.756 | 891.756 | 891.756 | 1721.9291 | 780 | 200 | 2701.9291 | 67.55% | 95% | 0% | -485.1259 | 406.6301 | -3550 | -400 | -3543.3699 | 88.58% | 68.48% | 95% | 0% | 1923 | -424
[5 empty] | 2019-05-04 | 18 | 2960 | 1401 | -500 | 1 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 1721.9291 | 780 | 200 | 2701.9291 | 67.55% | 95% | 0% | -572.0824 | 285.2136 | -3550 | -400 | -3664.7864 | 91.62% | 68.48% | 95% | 0% | 1901 | -500
[5 empty] | 2019-05-04 | 19 | 2960.5 | 1339 | -559 | 1 | 0 | 1898 | 852.5969 | 852.5969 | 852.5969 | 1721.9291 | 780 | 200 | 2701.9291 | 67.55% | 95% | 0% | -639.5881 | 213.0088 | -3550 | -400 | -3736.9912 | 93.42% | 68.47% | 95% | 0% | 1898 | -559
[5 empty] | 2019-05-04 | 20 | 2961 | 1285 | -606 | 1 | 0 | 1891 | 841.6323 | 841.6323 | 841.6323 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -693.3638 | 148.2685 | -3550 | -400 | -3801.7315 | 95.04% | 68.47% | 95% | 0% | 1891 | -606
[5 empty] | 2019-05-04 | 21 | 2961.5 | 1188 | -666 | 1 | 0 | 1854 | 783.6768 | 783.6768 | 783.6768 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -762.0137 | 21.6631 | -3550 | -400 | -3928.3369 | 98.21% | 68.46% | 95% | 0% | 1854 | -666
[5 empty] | 2019-05-04 | 22 | 2962 | 1140 | -693 | 1 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -792.9062 | -42.123 | -3550 | -400 | -3992.123 | 99.8% | 68.46% | 95% | 0% | 1833 | -693
[5 empty] | 2019-05-04 | 23 | 2962.5 | 1076 | -719 | 1 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -822.6545 | -131.3931 | -3550 | -400 | -4081.3931 | 102% | 68.46% | 95% | 0% | 1795 | -719
[5 empty] | 2019-05-04 | 24 | 2963 | 1083 | -724 | 1 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -828.3753 | -118.3176 | -3550 | -400 | -4068.3176 | 101.7% | 68.46% | 95% | 0% | 1807 | -724
[5 empty] | 2019-05-04 | 25 | 2963.5 | 1018 | -793 | 1 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -907.3227 | -190.9995 | -3550 | -400 | -4140.9995 | 103.5% | 68.45% | 95% | 0% | 1811 | -793
[5 empty] | 2019-05-04 | 26 | 2964 | 1051 | -728 | 1 | 0 | 1779 | 666.1995 | 666.1995 | 666.1995 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -832.9519 | -166.7524 | -3550 | -400 | -4116.7524 | 102.9% | 68.45% | 95% | 0% | 1779 | -728
[5 empty] | 2019-05-04 | 27 | 2964.5 | 935 | -799 | 1 | 0 | 1734 | 595.7131 | 595.7131 | 595.7131 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -914.1876 | -318.4745 | -3550 | -400 | -4268.4745 | 106.7% | 68.44% | 95% | 0% | 1734 | -799
[5 empty] | 2019-05-04 | 28 | 2965 | 939 | -778 | 1 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -890.1602 | -321.0753 | -3550 | -400 | -4271.0753 | 106.8% | 68.44% | 95% | 0% | 1717 | -778
[5 empty] | 2019-05-04 | 29 | 2965.5 | 978 | -712 | 1 | 0 | 1690 | 526.7931 | 526.7931 | 526.7931 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -814.6453 | -287.8522 | -3550 | -400 | -4237.8522 | 105.9% | 68.44% | 95% | 0% | 1690 | -712
[5 empty] | 2019-05-04 | 30 | 2966 | 955 | -724 | 1 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -828.3753 | -318.8122 | -3550 | -400 | -4268.8122 | 106.7% | 68.44% | 95% | 0% | 1679 | -724
[5 empty] | 2019-05-04 | 31 | 2966.5 | 1015 | -673 | 1 | 0 | 1688 | 523.6603 | 523.6603 | 523.6603 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -770.0229 | -246.3625 | -3550 | -400 | -4196.3625 | 104.9% | 68.44% | 95% | 0% | 1688 | -673
[5 empty] | 2019-05-04 | 32 | 2967 | 1124 | -605 | 1 | 0 | 1729 | 587.8813 | 587.8813 | 587.8813 | 1720.3627 | 780 | 200 | 2700.3627 | 67.51% | 95% | 0% | -692.2197 | -104.3384 | -3550 | -400 | -4054.3384 | 101.4% | 68.43% | 95% | 0% | 1729 | -605
[5 empty] | 2019-05-04 | 33 | 2967.5 | 1235 | -552 | 1 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 1718.7964 | 780 | 200 | 2698.7964 | 67.47% | 95% | 0% | -631.5789 | 47.1515 | -3550 | -400 | -3902.8485 | 97.57% | 68.43% | 95% | 0% | 1787 | -552
[5 empty] | 2019-05-04 | 34 | 2968 | 1416 | -481 | 1 | 0 | 1897 | 851.0305 | 851.0305 | 851.0305 | 1718.7964 | 780 | 200 | 2698.7964 | 67.47% | 95% | 0% | -550.3432 | 300.6873 | -3550 | -400 | -3649.3127 | 91.23% | 68.43% | 95% | 0% | 1897 | -481
[5 empty] | 2019-05-04 | 35 | 2968.5 | 1585 | -426 | 1 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 1718.7964 | 780 | 200 | 2698.7964 | 67.47% | 95% | 0% | -487.4142 | 542.1819 | -3550 | -400 | -3407.8181 | 85.2% | 68.43% | 95% | 0% | 2011 | -426
[5 empty] | 2019-05-04 | 36 | 2969 | 1737 | -363 | 1 | 0 | 2100 | 1169.0025 | 1169.0025 | 1169.0025 | 1718.7964 | 780 | 200 | 2698.7964 | 67.47% | 95% | 0% | -415.3318 | 753.6707 | -3550 | -400 | -3196.3293 | 79.91% | 68.42% | 95% | 0% | 2100 | -363
[5 empty] | 2019-05-04 | 37 | 2969.5 | 1859 | -307 | 1 | 0 | 2166 | 1272.3825 | 1272.3825 | 1272.3825 | 1718.7964 | 780 | 200 | 2698.7964 | 67.47% | 95% | 0% | -351.2586 | 921.1239 | -3550 | -400 | -3028.8761 | 75.72% | 68.42% | 95% | 0% | 2166 | -307
[5 empty] | 2019-05-04 | 38 | 2970 | 1967 | -249 | 1 | 0 | 2216 | 1350.7007 | 1350.7007 | 1350.7007 | 1718.7964 | 780 | 200 | 2698.7964 | 67.47% | 95% | 0% | -284.897 | 1065.8037 | -3550 | -400 | -2884.1963 | 72.1% | 68.42% | 95% | 0% | 2216 | -249
[5 empty] | 2019-05-04 | 39 | 2970.5 | 2065 | -189 | 1 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 1718.7964 | 780 | 200 | 2698.7964 | 67.47% | 95% | 0% | -216.2471 | 1193.9754 | -3550 | -400 | -2756.0246 | 68.9% | 68.42% | 95% | 0% | 2254 | -189
[5 empty] | 2019-05-04 | 40 | 2971 | 2135 | -141 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1718.7964 | 780 | 200 | 2698.7964 | 67.47% | 95% | 0% | -161.3272 | 1283.3554 | -3550 | -400 | -2666.6446 | 66.67% | 68.42% | 95% | 0% | 2276 | -141
[5 empty] | 2019-05-04 | 41 | 2971.5 | 2157 | -115 | 1 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 1718.7964 | 780 | 200 | 2698.7964 | 67.47% | 95% | 0% | -131.5789 | 1306.8382 | -3550 | -400 | -2643.1618 | 66.08% | 68.41% | 95% | 0% | 2272 | -115
[5 empty] | 2019-05-04 | 42 | 2972 | 2178 | -104 | 1 | 0 | 2282 | 1454.0808 | 1454.0808 | 1454.0808 | 1717.23 | 780 | 200 | 2697.23 | 67.43% | 95% | 0% | -118.9931 | 1335.0877 | -3550 | -400 | -2614.9123 | 65.37% | 68.41% | 95% | 0% | 2282 | -104
[5 empty] | 2019-05-04 | 43 | 2972.5 | 2175 | -101 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1717.23 | 780 | 200 | 2697.23 | 67.43% | 95% | 0% | -115.5606 | 1329.122 | -3550 | -400 | -2620.878 | 65.52% | 68.41% | 95% | 0% | 2276 | -101
[5 empty] | 2019-05-04 | 44 | 2973 | 2127 | -99 | 0 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 1717.23 | 780 | 200 | 2697.23 | 67.43% | 95% | 0% | -113.2723 | 1253.0921 | -2750 | -200 | -1696.9079 | 42.42% | 68.4% | 95% | 0% | 2226 | -99
[5 empty] | 2019-05-04 | 45 | 2973.5 | 2066 | -96 | 0 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 1717.23 | 780 | 200 | 2697.23 | 67.43% | 95% | 0% | -109.8398 | 1156.2772 | -2750 | -200 | -1793.7228 | 44.84% | 68.4% | 95% | 0% | 2162 | -96
[5 empty] | 2019-05-04 | 46 | 2974 | 1992 | -94 | 0 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 1717.23 | 780 | 200 | 2697.23 | 67.43% | 95% | 0% | -107.5515 | 1039.5219 | -2750 | -200 | -1910.4781 | 47.76% | 68.4% | 95% | 0% | 2086 | -94
[5 empty] | 2019-05-04 | 47 | 2974.5 | 1877 | -92 | 0 | 0 | 1969 | 963.8087 | 963.8087 | 963.8087 | 1717.23 | 780 | 200 | 2697.23 | 67.43% | 95% | 0% | -105.2632 | 858.5456 | -2750 | -200 | -2091.4544 | 52.29% | 68.39% | 95% | 0% | 1969 | -92
[5 empty] | 2019-05-04 | 48 | 2975 | 1781 | -89 | 0 | 0 | 1870 | 808.7387 | 808.7387 | 808.7387 | 1717.23 | 780 | 200 | 2697.23 | 67.43% | 95% | 0% | -101.8307 | 706.908 | -2750 | -200 | -2243.092 | 56.08% | 68.39% | 95% | 0% | 1870 | -89
[5 empty] | 2019-05-05 | 1 | 2975.5 | 1702 | -84 | 0 | 0 | 1786 | 677.1641 | 677.1641 | 677.1641 | 1717.23 | 780 | 200 | 2697.23 | 67.43% | 95% | 0% | -96.1098 | 581.0542 | -2750 | -200 | -2368.9458 | 59.22% | 68.39% | 95% | 0% | 1786 | -84
[5 empty] | 2019-05-05 | 2 | 2976 | 1658 | -79 | 0 | 0 | 1737 | 600.4122 | 600.4122 | 600.4122 | 1717.23 | 780 | 200 | 2697.23 | 67.43% | 95% | 0% | -90.389 | 510.0232 | -2750 | -200 | -2439.9768 | 61% | 68.39% | 95% | 0% | 1737 | -79
[5 empty] | 2019-05-05 | 3 | 2976.5 | 1649 | -77 | 0 | 0 | 1726 | 583.1822 | 583.1822 | 583.1822 | 1717.23 | 780 | 200 | 2697.23 | 67.43% | 95% | 0% | -88.1007 | 495.0815 | -2750 | -200 | -2454.9185 | 61.37% | 68.38% | 95% | 0% | 1726 | -77
[5 empty] | 2019-05-05 | 4 | 2977 | 1668 | -75 | 0 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 1717.23 | 780 | 200 | 2697.23 | 67.43% | 95% | 0% | -85.8124 | 523.998 | -2750 | -200 | -2426.002 | 60.65% | 68.38% | 95% | 0% | 1743 | -75
[5 empty] | 2019-05-05 | 5 | 2977.5 | 1652 | -74 | 0 | 0 | 1726 | 583.1822 | 583.1822 | 583.1822 | 1715.6636 | 780 | 200 | 2695.6636 | 67.39% | 95% | 0% | -84.6682 | 498.514 | -2750 | -200 | -2451.486 | 61.29% | 68.38% | 95% | 0% | 1726 | -74
[5 empty] | 2019-05-05 | 6 | 2978 | 1632 | -72 | 0 | 0 | 1704 | 548.7222 | 548.7222 | 548.7222 | 1715.6636 | 780 | 200 | 2695.6636 | 67.39% | 95% | 0% | -82.3799 | 466.3423 | -2750 | -200 | -2483.6577 | 62.09% | 68.38% | 95% | 0% | 1704 | -72
[5 empty] | 2019-05-05 | 7 | 2978.5 | 1608 | -71 | 0 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 1715.6636 | 780 | 200 | 2695.6636 | 67.39% | 95% | 0% | -81.2357 | 428.3274 | -2750 | -200 | -2521.6726 | 63.04% | 68.37% | 95% | 0% | 1679 | -71
[5 empty] | 2019-05-05 | 8 | 2979 | 1593 | -69 | 0 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 1715.6636 | 780 | 200 | 2695.6636 | 67.39% | 95% | 0% | -78.9474 | 403.9875 | -2750 | -200 | -2546.0125 | 63.65% | 68.37% | 95% | 0% | 1662 | -69
[5 empty] | 2019-05-05 | 9 | 2979.5 | 1580 | -68 | 1 | 0 | 1648 | 461.0058 | 461.0058 | 461.0058 | 1715.6636 | 780 | 200 | 2695.6636 | 67.39% | 95% | 0% | -77.8032 | 383.2026 | -3550 | -400 | -3566.7974 | 89.17% | 68.36% | 95% | 0% | 1648 | -68
[5 empty] | 2019-05-05 | 10 | 2980 | 1572 | -67 | 1 | 0 | 1639 | 446.9085 | 446.9085 | 446.9085 | 1715.6636 | 780 | 200 | 2695.6636 | 67.39% | 95% | 0% | -76.659 | 370.2495 | -3550 | -400 | -3579.7505 | 89.49% | 68.36% | 95% | 0% | 1639 | -67
[5 empty] | 2019-05-05 | 11 | 2980.5 | 1564 | -67 | 1 | 0 | 1631 | 434.3776 | 434.3776 | 434.3776 | 1715.6636 | 780 | 200 | 2695.6636 | 67.39% | 95% | 0% | -76.659 | 357.7185 | -3550 | -400 | -3592.2815 | 89.81% | 68.36% | 95% | 0% | 1631 | -67
[5 empty] | 2019-05-05 | 12 | 2981 | 1541 | -70 | 1 | 0 | 1611 | 403.0503 | 403.0503 | 403.0503 | 1714.0973 | 780 | 200 | 2694.0973 | 67.35% | 95% | 0% | -80.0915 | 322.9588 | -3550 | -400 | -3627.0412 | 90.68% | 68.36% | 95% | 0% | 1611 | -70
[5 empty] | 2019-05-05 | 13 | 2981.5 | 1571 | -91 | 1 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 1714.0973 | 780 | 200 | 2694.0973 | 67.35% | 95% | 0% | -104.119 | 378.8159 | -3550 | -400 | -3571.1841 | 89.28% | 68.36% | 95% | 0% | 1662 | -91
[5 empty] | 2019-05-05 | 14 | 2982 | 1581 | -131 | 1 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 1714.0973 | 780 | 200 | 2694.0973 | 67.35% | 95% | 0% | -149.8856 | 411.3675 | -3550 | -400 | -3538.6325 | 88.47% | 68.35% | 95% | 0% | 1712 | -131
[5 empty] | 2019-05-05 | 15 | 2982.5 | 1593 | -183 | 1 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 1714.0973 | 780 | 200 | 2694.0973 | 67.35% | 95% | 0% | -209.3822 | 452.1183 | -3550 | -400 | -3497.8817 | 87.45% | 68.35% | 95% | 0% | 1776 | -183
[5 empty] | 2019-05-05 | 16 | 2983 | 1583 | -228 | 1 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1714.0973 | 780 | 200 | 2694.0973 | 67.35% | 95% | 0% | -260.8696 | 455.4536 | -3550 | -400 | -3494.5464 | 87.36% | 68.35% | 95% | 0% | 1811 | -228
[5 empty] | 2019-05-05 | 17 | 2983.5 | 1583 | -280 | 1 | 0 | 1863 | 797.7741 | 797.7741 | 797.7741 | 1714.0973 | 780 | 200 | 2694.0973 | 67.35% | 95% | 0% | -320.3661 | 477.408 | -3550 | -400 | -3472.592 | 86.81% | 68.34% | 95% | 0% | 1863 | -280
[5 empty] | 2019-05-05 | 18 | 2984 | 1554 | -341 | 1 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 1714.0973 | 780 | 200 | 2694.0973 | 67.35% | 95% | 0% | -390.1602 | 457.7376 | -3550 | -400 | -3492.2624 | 87.31% | 68.34% | 95% | 0% | 1895 | -341
[5 empty] | 2019-05-05 | 19 | 2984.5 | 1515 | -420 | 1 | 0 | 1935 | 910.5523 | 910.5523 | 910.5523 | 1712.5309 | 780 | 200 | 2692.5309 | 67.31% | 95% | 0% | -480.5492 | 430.0032 | -3550 | -400 | -3519.9968 | 88% | 68.34% | 95% | 0% | 1935 | -420
[5 empty] | 2019-05-05 | 20 | 2985 | 1477 | -475 | 1 | 0 | 1952 | 937.1805 | 937.1805 | 937.1805 | 1712.5309 | 780 | 200 | 2692.5309 | 67.31% | 95% | 0% | -543.4783 | 393.7023 | -3550 | -400 | -3556.2977 | 88.91% | 68.33% | 95% | 0% | 1952 | -475
[5 empty] | 2019-05-05 | 21 | 2985.5 | 1460 | -504 | 1 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 1712.5309 | 780 | 200 | 2692.5309 | 67.31% | 95% | 0% | -576.659 | 379.3179 | -3550 | -400 | -3570.6821 | 89.27% | 68.32% | 95% | 0% | 1964 | -504
[5 empty] | 2019-05-05 | 22 | 2986 | 1486 | -516 | 1 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 1712.5309 | 780 | 200 | 2692.5309 | 67.31% | 95% | 0% | -590.389 | 425.1097 | -3550 | -400 | -3524.8903 | 88.12% | 68.32% | 95% | 0% | 2002 | -516
[5 empty] | 2019-05-05 | 23 | 2986.5 | 1563 | -475 | 1 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 1712.5309 | 780 | 200 | 2692.5309 | 67.31% | 95% | 0% | -543.4783 | 528.4096 | -3550 | -400 | -3421.5904 | 85.54% | 68.32% | 95% | 0% | 2038 | -475
[5 empty] | 2019-05-05 | 24 | 2987 | 1601 | -450 | 1 | 0 | 2051 | 1092.2506 | 1092.2506 | 1092.2506 | 1712.5309 | 780 | 200 | 2692.5309 | 67.31% | 95% | 0% | -514.8741 | 577.3765 | -3550 | -400 | -3372.6235 | 84.32% | 68.32% | 95% | 0% | 2051 | -450
[5 empty] | 2019-05-05 | 25 | 2987.5 | 1634 | -420 | 1 | 0 | 2054 | 1096.9497 | 1096.9497 | 1096.9497 | 1712.5309 | 780 | 200 | 2692.5309 | 67.31% | 95% | 0% | -480.5492 | 616.4005 | -3550 | -400 | -3333.5995 | 83.34% | 68.31% | 95% | 0% | 2054 | -420
[5 empty] | 2019-05-05 | 26 | 2988 | 1644 | -413 | 1 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 1712.5309 | 780 | 200 | 2692.5309 | 67.31% | 95% | 0% | -472.54 | 629.1088 | -3550 | -400 | -3320.8912 | 83.02% | 68.31% | 95% | 0% | 2057 | -413
[5 empty] | 2019-05-05 | 27 | 2988.5 | 1579 | -467 | 1 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1712.5309 | 780 | 200 | 2692.5309 | 67.31% | 95% | 0% | -534.3249 | 550.0939 | -3550 | -400 | -3399.9061 | 85% | 68.3% | 95% | 0% | 2046 | -467
[5 empty] | 2019-05-05 | 28 | 2989 | 1577 | -455 | 1 | 0 | 2032 | 1062.4897 | 1062.4897 | 1062.4897 | 1712.5309 | 780 | 200 | 2692.5309 | 67.31% | 95% | 0% | -520.595 | 541.8947 | -3550 | -400 | -3408.1053 | 85.2% | 68.29% | 95% | 0% | 2032 | -455
[5 empty] | 2019-05-05 | 29 | 2989.5 | 1572 | -446 | 1 | 0 | 2018 | 1040.5606 | 1040.5606 | 1040.5606 | 1712.5309 | 780 | 200 | 2692.5309 | 67.31% | 95% | 0% | -510.2975 | 530.2631 | -3550 | -400 | -3419.7369 | 85.49% | 68.29% | 95% | 0% | 2018 | -446
[5 empty] | 2019-05-05 | 30 | 2990 | 1557 | -456 | 1 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 1710.9646 | 780 | 200 | 2690.9646 | 67.27% | 95% | 0% | -521.7391 | 510.9896 | -3550 | -400 | -3439.0104 | 85.98% | 68.29% | 95% | 0% | 2013 | -456
[5 empty] | 2019-05-05 | 31 | 2990.5 | 1566 | -451 | 1 | 0 | 2017 | 1038.9942 | 1038.9942 | 1038.9942 | 1710.9646 | 780 | 200 | 2690.9646 | 67.27% | 95% | 0% | -516.0183 | 522.9759 | -3550 | -400 | -3427.0241 | 85.68% | 68.28% | 95% | 0% | 2017 | -451
[5 empty] | 2019-05-05 | 32 | 2991 | 1619 | -411 | 1 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 1710.9646 | 780 | 200 | 2690.9646 | 67.27% | 95% | 0% | -470.2517 | 589.1052 | -3550 | -400 | -3360.8948 | 84.02% | 68.28% | 95% | 0% | 2030 | -411
[5 empty] | 2019-05-05 | 33 | 2991.5 | 1692 | -387 | 1 | 0 | 2079 | 1136.1088 | 1136.1088 | 1136.1088 | 1710.9646 | 780 | 200 | 2690.9646 | 67.27% | 95% | 0% | -442.7918 | 693.3171 | -3550 | -400 | -3256.6829 | 81.42% | 68.28% | 95% | 0% | 2079 | -387
[5 empty] | 2019-05-05 | 34 | 2992 | 1817 | -333 | 1 | 0 | 2150 | 1247.3207 | 1247.3207 | 1247.3207 | 1710.9646 | 780 | 200 | 2690.9646 | 67.27% | 95% | 0% | -381.0069 | 866.3138 | -3550 | -400 | -3083.6862 | 77.09% | 68.28% | 95% | 0% | 2150 | -333
[5 empty] | 2019-05-05 | 35 | 2992.5 | 1915 | -290 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 1710.9646 | 780 | 200 | 2690.9646 | 67.27% | 95% | 0% | -331.8078 | 1001.663 | -3550 | -400 | -2948.337 | 73.71% | 68.27% | 95% | 0% | 2205 | -290
[5 empty] | 2019-05-05 | 36 | 2993 | 1987 | -249 | 1 | 0 | 2236 | 1382.028 | 1382.028 | 1382.028 | 1710.9646 | 780 | 200 | 2690.9646 | 67.27% | 95% | 0% | -284.897 | 1097.131 | -3550 | -400 | -2852.869 | 71.32% | 68.27% | 95% | 0% | 2236 | -249
[5 empty] | 2019-05-05 | 37 | 2993.5 | 2054 | -209 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 1710.9646 | 780 | 200 | 2690.9646 | 67.27% | 95% | 0% | -239.1304 | 1185.1894 | -3550 | -400 | -2764.8106 | 69.12% | 68.27% | 95% | 0% | 2263 | -209
[5 empty] | 2019-05-05 | 38 | 2994 | 2116 | -172 | 1 | 0 | 2288 | 1463.479 | 1463.479 | 1463.479 | 1709.3982 | 780 | 200 | 2689.3982 | 67.23% | 95% | 0% | -196.7963 | 1266.6826 | -3550 | -400 | -2683.3174 | 67.08% | 68.26% | 95% | 0% | 2288 | -172
[5 empty] | 2019-05-05 | 39 | 2994.5 | 2174 | -131 | 1 | 0 | 2305 | 1490.1072 | 1490.1072 | 1490.1072 | 1709.3982 | 780 | 200 | 2689.3982 | 67.23% | 95% | 0% | -149.8856 | 1340.2216 | -3550 | -400 | -2609.7784 | 65.24% | 68.26% | 95% | 0% | 2305 | -131
[5 empty] | 2019-05-05 | 40 | 2995 | 2209 | -100 | 1 | 0 | 2309 | 1496.3726 | 1496.3726 | 1496.3726 | 1709.3982 | 780 | 200 | 2689.3982 | 67.23% | 95% | 0% | -114.4165 | 1381.9562 | -3550 | -400 | -2568.0438 | 64.2% | 68.26% | 95% | 0% | 2309 | -100
[5 empty] | 2019-05-05 | 41 | 2995.5 | 2234 | -84 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 1709.3982 | 780 | 200 | 2689.3982 | 67.23% | 95% | 0% | -96.1098 | 1414.3601 | -3550 | -400 | -2535.6399 | 63.39% | 68.26% | 95% | 0% | 2318 | -84
[5 empty] | 2019-05-05 | 42 | 2996 | 2225 | -79 | 1 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 1709.3982 | 780 | 200 | 2689.3982 | 67.23% | 95% | 0% | -90.389 | 1398.1518 | -3550 | -400 | -2551.8482 | 63.8% | 68.24% | 95% | 0% | 2304 | -79
[5 empty] | 2019-05-05 | 43 | 2996.5 | 2239 | -79 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 1709.3982 | 780 | 200 | 2689.3982 | 67.23% | 95% | 0% | -90.389 | 1420.0809 | -3550 | -400 | -2529.9191 | 63.25% | 68.24% | 95% | 0% | 2318 | -79
[5 empty] | 2019-05-05 | 44 | 2997 | 2176 | -79 | 0 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 1709.3982 | 780 | 200 | 2689.3982 | 67.23% | 95% | 0% | -90.389 | 1321.3999 | -2750 | -200 | -1628.6001 | 40.72% | 68.23% | 95% | 0% | 2255 | -79
[5 empty] | 2019-05-05 | 45 | 2997.5 | 2081 | -79 | 0 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1709.3982 | 780 | 200 | 2689.3982 | 67.23% | 95% | 0% | -90.389 | 1172.5953 | -2750 | -200 | -1777.4047 | 44.44% | 68.23% | 95% | 0% | 2160 | -79
[5 empty] | 2019-05-05 | 46 | 2998 | 1996 | -78 | 0 | 0 | 2074 | 1128.277 | 1128.277 | 1128.277 | 1709.3982 | 780 | 200 | 2689.3982 | 67.23% | 95% | 0% | -89.2449 | 1039.0321 | -2750 | -200 | -1910.9679 | 47.77% | 68.22% | 95% | 0% | 2074 | -78
[5 empty] | 2019-05-05 | 47 | 2998.5 | 1874 | -79 | 0 | 0 | 1953 | 938.7469 | 938.7469 | 938.7469 | 1709.3982 | 780 | 200 | 2689.3982 | 67.23% | 95% | 0% | -90.389 | 848.3579 | -2750 | -200 | -2101.6421 | 52.54% | 68.22% | 95% | 0% | 1953 | -79
[5 empty] | 2019-05-05 | 48 | 2999 | 1757 | -79 | 0 | 0 | 1836 | 755.4823 | 755.4823 | 755.4823 | 1709.3982 | 780 | 200 | 2689.3982 | 67.23% | 95% | 0% | -90.389 | 665.0933 | -2750 | -200 | -2284.9067 | 57.12% | 68.22% | 95% | 0% | 1836 | -79
[5 empty] | 2019-05-06 | 1 | 2999.5 | 1679 | -75 | 0 | 0 | 1754 | 627.0404 | 627.0404 | 627.0404 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -85.8124 | 541.228 | -2750 | -200 | -2408.772 | 60.22% | 68.21% | 95% | 0% | 1754 | -75
[5 empty] | 2019-05-06 | 2 | 3000 | 1632 | -71 | 0 | 0 | 1703 | 547.1558 | 547.1558 | 547.1558 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -81.2357 | 465.9201 | -2750 | -200 | -2484.0799 | 62.1% | 68.21% | 95% | 0% | 1703 | -71
[5 empty] | 2019-05-06 | 3 | 3000.5 | 1633 | -72 | 0 | 0 | 1705 | 550.2885 | 550.2885 | 550.2885 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -82.3799 | 467.9087 | -2750 | -200 | -2482.0913 | 62.05% | 68.21% | 95% | 0% | 1705 | -72
[5 empty] | 2019-05-06 | 4 | 3001 | 1657 | -72 | 0 | 0 | 1729 | 587.8813 | 587.8813 | 587.8813 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -82.3799 | 505.5014 | -2750 | -200 | -2444.4986 | 61.11% | 68.2% | 95% | 0% | 1729 | -72
[5 empty] | 2019-05-06 | 5 | 3001.5 | 1656 | -72 | 1 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -82.3799 | 503.9351 | -3550 | -400 | -3446.0649 | 86.15% | 68.2% | 95% | 0% | 1728 | -72
[5 empty] | 2019-05-06 | 6 | 3002 | 1634 | -71 | 1 | 0 | 1705 | 550.2885 | 550.2885 | 550.2885 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -81.2357 | 469.0528 | -3550 | -400 | -3480.9472 | 87.02% | 68.19% | 95% | 0% | 1705 | -71
[5 empty] | 2019-05-06 | 7 | 3002.5 | 1622 | -71 | 1 | 0 | 1693 | 531.4922 | 531.4922 | 531.4922 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -81.2357 | 450.2565 | -3550 | -400 | -3499.7435 | 87.49% | 68.18% | 95% | 0% | 1693 | -71
[5 empty] | 2019-05-06 | 8 | 3003 | 1606 | -70 | 1 | 0 | 1676 | 504.864 | 504.864 | 504.864 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -80.0915 | 424.7724 | -3550 | -400 | -3525.2276 | 88.13% | 68.18% | 95% | 0% | 1676 | -70
[5 empty] | 2019-05-06 | 9 | 3003.5 | 1589 | -68 | 1 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -77.8032 | 397.2998 | -3550 | -400 | -3552.7002 | 88.82% | 68.18% | 95% | 0% | 1657 | -68
[5 empty] | 2019-05-06 | 10 | 3004 | 1579 | -66 | 1 | 0 | 1645 | 456.3067 | 456.3067 | 456.3067 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -75.5149 | 380.7918 | -3550 | -400 | -3569.2082 | 89.23% | 68.17% | 95% | 0% | 1645 | -66
[5 empty] | 2019-05-06 | 11 | 3004.5 | 1582 | -65 | 1 | 0 | 1647 | 459.4394 | 459.4394 | 459.4394 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -74.3707 | 385.0687 | -3550 | -400 | -3564.9313 | 89.12% | 68.17% | 95% | 0% | 1647 | -65
[5 empty] | 2019-05-06 | 12 | 3005 | 1596 | -66 | 1 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -75.5149 | 407.42 | -3550 | -400 | -3542.58 | 88.56% | 68.17% | 95% | 0% | 1662 | -66
[5 empty] | 2019-05-06 | 13 | 3005.5 | 1659 | -83 | 1 | 0 | 1742 | 608.244 | 608.244 | 608.244 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -94.9657 | 513.2783 | -3550 | -400 | -3436.7217 | 85.92% | 68.16% | 95% | 0% | 1742 | -83
[5 empty] | 2019-05-06 | 14 | 3006 | 1700 | -112 | 1 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -128.1465 | 589.7431 | -3550 | -400 | -3360.2569 | 84.01% | 68.16% | 95% | 0% | 1812 | -112
[5 empty] | 2019-05-06 | 15 | 3006.5 | 1729 | -147 | 1 | 0 | 1876 | 818.1369 | 818.1369 | 818.1369 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -168.1922 | 649.9446 | -3550 | -400 | -3300.0554 | 82.5% | 68.16% | 95% | 0% | 1876 | -147
[5 empty] | 2019-05-06 | 16 | 3007 | 1731 | -188 | 1 | 0 | 1919 | 885.4905 | 885.4905 | 885.4905 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -215.103 | 670.3875 | -3550 | -400 | -3279.6125 | 81.99% | 68.16% | 95% | 0% | 1919 | -188
[5 empty] | 2019-05-06 | 17 | 3007.5 | 1768 | -238 | 1 | 0 | 2006 | 1021.7642 | 1021.7642 | 1021.7642 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -272.3112 | 749.453 | -3550 | -400 | -3200.547 | 80.01% | 68.15% | 95% | 0% | 2006 | -238
[5 empty] | 2019-05-06 | 18 | 3008 | 1738 | -297 | 1 | 0 | 2035 | 1067.1888 | 1067.1888 | 1067.1888 | 1707.8318 | 780 | 200 | 2687.8318 | 67.2% | 95% | 0% | -339.8169 | 727.3719 | -3550 | -400 | -3222.6281 | 80.57% | 68.14% | 95% | 0% | 2035 | -297
[5 empty] | 2019-05-06 | 19 | 3008.5 | 1715 | -354 | 1 | 0 | 2069 | 1120.4452 | 1120.4452 | 1120.4452 | 1706.2655 | 780 | 200 | 2686.2655 | 67.16% | 95% | 0% | -405.0343 | 715.4109 | -3550 | -400 | -3234.5891 | 80.86% | 68.14% | 95% | 0% | 2069 | -354
[5 empty] | 2019-05-06 | 20 | 3009 | 1704 | -387 | 1 | 0 | 2091 | 1154.9052 | 1154.9052 | 1154.9052 | 1706.2655 | 780 | 200 | 2686.2655 | 67.16% | 95% | 0% | -442.7918 | 712.1134 | -3550 | -400 | -3237.8866 | 80.95% | 68.13% | 95% | 0% | 2091 | -387
[5 empty] | 2019-05-06 | 21 | 3009.5 | 1727 | -407 | 1 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 1706.2655 | 780 | 200 | 2686.2655 | 67.16% | 95% | 0% | -465.6751 | 756.5838 | -3550 | -400 | -3193.4162 | 79.84% | 68.13% | 95% | 0% | 2134 | -407
[5 empty] | 2019-05-06 | 22 | 3010 | 1729 | -421 | 1 | 0 | 2150 | 1247.3207 | 1247.3207 | 1247.3207 | 1706.2655 | 780 | 200 | 2686.2655 | 67.16% | 95% | 0% | -481.6934 | 765.6273 | -3550 | -400 | -3184.3727 | 79.61% | 68.13% | 95% | 0% | 2150 | -421
[5 empty] | 2019-05-06 | 23 | 3010.5 | 1763 | -416 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 1706.2655 | 780 | 200 | 2686.2655 | 67.16% | 95% | 0% | -475.9725 | 816.7727 | -3550 | -400 | -3133.2273 | 78.33% | 68.12% | 95% | 0% | 2179 | -416
[5 empty] | 2019-05-06 | 24 | 3011 | 1791 | -404 | 1 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 1706.2655 | 780 | 200 | 2686.2655 | 67.16% | 95% | 0% | -462.2426 | 855.5645 | -3550 | -400 | -3094.4355 | 77.36% | 68.12% | 95% | 0% | 2195 | -404
[5 empty] | 2019-05-06 | 25 | 3011.5 | 1860 | -366 | 1 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 1706.2655 | 780 | 200 | 2686.2655 | 67.16% | 95% | 0% | -418.7643 | 947.6001 | -3550 | -400 | -3002.3999 | 75.06% | 68.12% | 95% | 0% | 2226 | -366
[5 empty] | 2019-05-06 | 26 | 3012 | 1869 | -358 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1706.2655 | 780 | 200 | 2686.2655 | 67.16% | 95% | 0% | -409.611 | 958.3198 | -3550 | -400 | -2991.6802 | 74.79% | 68.11% | 95% | 0% | 2227 | -358
[5 empty] | 2019-05-06 | 27 | 3012.5 | 1843 | -375 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 1706.2655 | 780 | 200 | 2686.2655 | 67.16% | 95% | 0% | -429.0618 | 924.7717 | -3550 | -400 | -3025.2283 | 75.63% | 68.11% | 95% | 0% | 2218 | -375
[5 empty] | 2019-05-06 | 28 | 3013 | 1803 | -385 | 1 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 1706.2655 | 780 | 200 | 2686.2655 | 67.16% | 95% | 0% | -440.5034 | 866.3391 | -3550 | -400 | -3083.6609 | 77.09% | 68.11% | 95% | 0% | 2188 | -385
[5 empty] | 2019-05-06 | 29 | 3013.5 | 1807 | -375 | 1 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 1706.2655 | 780 | 200 | 2686.2655 | 67.16% | 95% | 0% | -429.0618 | 868.3826 | -3550 | -400 | -3081.6174 | 77.04% | 68.11% | 95% | 0% | 2182 | -375
[5 empty] | 2019-05-06 | 30 | 3014 | 1829 | -341 | 1 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -390.1602 | 888.4878 | -3550 | -400 | -3061.5122 | 76.54% | 68.1% | 95% | 0% | 2170 | -341
[5 empty] | 2019-05-06 | 31 | 3014.5 | 1840 | -342 | 1 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -391.3043 | 906.14 | -3550 | -400 | -3043.86 | 76.1% | 68.1% | 95% | 0% | 2182 | -342
[5 empty] | 2019-05-06 | 32 | 3015 | 1857 | -337 | 1 | 0 | 2194 | 1316.2407 | 1316.2407 | 1316.2407 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -385.5835 | 930.6572 | -3550 | -400 | -3019.3428 | 75.48% | 68.1% | 95% | 0% | 2194 | -337
[5 empty] | 2019-05-06 | 33 | 3015.5 | 1949 | -304 | 1 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -347.8261 | 1060.8301 | -3550 | -400 | -2889.1699 | 72.23% | 68.09% | 95% | 0% | 2253 | -304
[5 empty] | 2019-05-06 | 34 | 3016 | 2073 | -276 | 1 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -315.7895 | 1243.2377 | -3550 | -400 | -2706.7623 | 67.67% | 68.09% | 95% | 0% | 2349 | -276
[5 empty] | 2019-05-06 | 35 | 3016.5 | 2192 | -252 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -288.3295 | 1419.5023 | -3550 | -400 | -2530.4977 | 63.26% | 68.09% | 95% | 0% | 2444 | -252
[5 empty] | 2019-05-06 | 36 | 3017 | 2273 | -202 | 1 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -231.1213 | 1525.2678 | -3550 | -400 | -2424.7322 | 60.62% | 68.09% | 95% | 0% | 2475 | -202
[5 empty] | 2019-05-06 | 37 | 3017.5 | 2351 | -156 | 1 | 0 | 2507 | 1806.5128 | 1806.5128 | 1806.5128 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -178.4897 | 1628.0231 | -3550 | -400 | -2321.9769 | 58.05% | 68.09% | 95% | 0% | 2507 | -156
[5 empty] | 2019-05-06 | 38 | 3018 | 2418 | -111 | 1 | 0 | 2529 | 1840.9728 | 1840.9728 | 1840.9728 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -127.0023 | 1713.9705 | -3550 | -400 | -2236.0295 | 55.9% | 68.09% | 95% | 0% | 2529 | -111
[5 empty] | 2019-05-06 | 39 | 3018.5 | 2465 | -76 | 1 | 0 | 2541 | 1859.7692 | 1859.7692 | 1859.7692 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -86.9565 | 1772.8126 | -3550 | -400 | -2177.1874 | 54.43% | 68.09% | 95% | 0% | 2541 | -76
[5 empty] | 2019-05-06 | 40 | 3019 | 2477 | -50 | 1 | 0 | 2527 | 1837.8401 | 1837.8401 | 1837.8401 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -57.2082 | 1780.6318 | -3550 | -400 | -2169.3682 | 54.23% | 68.08% | 95% | 0% | 2527 | -50
[5 empty] | 2019-05-06 | 41 | 3019.5 | 2472 | -32 | 1 | 0 | 2504 | 1801.8137 | 1801.8137 | 1801.8137 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -36.6133 | 1765.2004 | -3550 | -400 | -2184.7996 | 54.62% | 68.08% | 95% | 0% | 2504 | -32
[5 empty] | 2019-05-06 | 42 | 3020 | 2473 | -26 | 1 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -29.7483 | 1764.2336 | -3550 | -400 | -2185.7664 | 54.64% | 68.07% | 95% | 0% | 2499 | -26
[5 empty] | 2019-05-06 | 43 | 3020.5 | 2472 | -25 | 1 | 0 | 2497 | 1790.8491 | 1790.8491 | 1790.8491 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -28.6041 | 1762.245 | -3550 | -400 | -2187.755 | 54.69% | 68.07% | 95% | 0% | 2497 | -25
[5 empty] | 2019-05-06 | 44 | 3021 | 2401 | -24 | 0 | 0 | 2425 | 1678.0709 | 1678.0709 | 1678.0709 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -27.46 | 1650.6109 | -2750 | -200 | -1299.3891 | 32.48% | 68.07% | 95% | 0% | 2425 | -24
[5 empty] | 2019-05-06 | 45 | 3021.5 | 2271 | -23 | 0 | 0 | 2294 | 1472.8772 | 1472.8772 | 1472.8772 | 1704.6991 | 780 | 200 | 2684.6991 | 67.12% | 95% | 0% | -26.3158 | 1446.5614 | -2750 | -200 | -1503.4386 | 37.59% | 68.07% | 95% | 0% | 2294 | -23
[5 empty] | 2019-05-06 | 46 | 3022 | 2132 | -22 | 0 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 1703.1327 | 780 | 200 | 2683.1327 | 67.08% | 95% | 0% | -25.1716 | 1228.4145 | -2750 | -200 | -1721.5855 | 43.04% | 68.06% | 95% | 0% | 2154 | -22
[5 empty] | 2019-05-06 | 47 | 3022.5 | 1996 | -22 | 0 | 0 | 2018 | 1040.5606 | 1040.5606 | 1040.5606 | 1703.1327 | 780 | 200 | 2683.1327 | 67.08% | 95% | 0% | -25.1716 | 1015.389 | -2750 | -200 | -1934.611 | 48.37% | 68.06% | 95% | 0% | 2018 | -22
[5 empty] | 2019-05-06 | 48 | 3023 | 1873 | -22 | 0 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 1703.1327 | 780 | 200 | 2683.1327 | 67.08% | 95% | 0% | -25.1716 | 822.7261 | -2750 | -200 | -2127.2739 | 53.18% | 68.05% | 95% | 0% | 1895 | -22
[5 empty] | 2019-05-07 | 1 | 3023.5 | 1795 | -22 | 1 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 1703.1327 | 780 | 200 | 2683.1327 | 67.08% | 95% | 0% | -25.1716 | 700.5497 | -3550 | -400 | -3249.4503 | 81.24% | 68.05% | 95% | 0% | 1817 | -22
[5 empty] | 2019-05-07 | 2 | 3024 | 1747 | -22 | 1 | 0 | 1769 | 650.5359 | 650.5359 | 650.5359 | 1703.1327 | 780 | 200 | 2683.1327 | 67.08% | 95% | 0% | -25.1716 | 625.3642 | -3550 | -400 | -3324.6358 | 83.12% | 68.05% | 95% | 0% | 1769 | -22
[5 empty] | 2019-05-07 | 3 | 3024.5 | 1751 | -21 | 1 | 0 | 1772 | 655.235 | 655.235 | 655.235 | 1703.1327 | 780 | 200 | 2683.1327 | 67.08% | 95% | 0% | -24.0275 | 631.2075 | -3550 | -400 | -3318.7925 | 82.97% | 68.05% | 95% | 0% | 1772 | -21
[5 empty] | 2019-05-07 | 4 | 3025 | 1781 | -21 | 1 | 0 | 1802 | 702.2259 | 702.2259 | 702.2259 | 1703.1327 | 780 | 200 | 2683.1327 | 67.08% | 95% | 0% | -24.0275 | 678.1984 | -3550 | -400 | -3271.8016 | 81.8% | 68.05% | 95% | 0% | 1802 | -21
[5 empty] | 2019-05-07 | 5 | 3025.5 | 1773 | -21 | 1 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 1703.1327 | 780 | 200 | 2683.1327 | 67.08% | 95% | 0% | -24.0275 | 665.6675 | -3550 | -400 | -3284.3325 | 82.11% | 68.05% | 95% | 0% | 1794 | -21
[5 empty] | 2019-05-07 | 6 | 3026 | 1760 | -20 | 1 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 1703.1327 | 780 | 200 | 2683.1327 | 67.08% | 95% | 0% | -22.8833 | 644.8826 | -3550 | -400 | -3305.1174 | 82.63% | 68.04% | 95% | 0% | 1780 | -20
[5 empty] | 2019-05-07 | 7 | 3026.5 | 1745 | -20 | 1 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 1703.1327 | 780 | 200 | 2683.1327 | 67.08% | 95% | 0% | -22.8833 | 621.3871 | -3550 | -400 | -3328.6129 | 83.22% | 68.04% | 95% | 0% | 1765 | -20
[5 empty] | 2019-05-07 | 8 | 3027 | 1727 | -20 | 1 | 0 | 1747 | 616.0758 | 616.0758 | 616.0758 | 1703.1327 | 780 | 200 | 2683.1327 | 67.08% | 95% | 0% | -22.8833 | 593.1925 | -3550 | -400 | -3356.8075 | 83.92% | 68.04% | 95% | 0% | 1747 | -20
[5 empty] | 2019-05-07 | 9 | 3027.5 | 1713 | -20 | 1 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 1703.1327 | 780 | 200 | 2683.1327 | 67.08% | 95% | 0% | -22.8833 | 571.2634 | -3550 | -400 | -3378.7366 | 84.47% | 68.04% | 95% | 0% | 1733 | -20
[5 empty] | 2019-05-07 | 10 | 3028 | 1728 | -21 | 1 | 0 | 1749 | 619.2086 | 619.2086 | 619.2086 | 1701.5664 | 780 | 200 | 2681.5664 | 67.04% | 95% | 0% | -24.0275 | 595.1811 | -3550 | -400 | -3354.8189 | 83.87% | 68.03% | 95% | 0% | 1749 | -21
[5 empty] | 2019-05-07 | 11 | 3028.5 | 1759 | -21 | 1 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 1701.5664 | 780 | 200 | 2681.5664 | 67.04% | 95% | 0% | -24.0275 | 643.7384 | -3550 | -400 | -3306.2616 | 82.66% | 68.03% | 95% | 0% | 1780 | -21
[5 empty] | 2019-05-07 | 12 | 3029 | 1821 | -23 | 1 | 0 | 1844 | 768.0132 | 768.0132 | 768.0132 | 1701.5664 | 780 | 200 | 2681.5664 | 67.04% | 95% | 0% | -26.3158 | 741.6974 | -3550 | -400 | -3208.3026 | 80.21% | 68.03% | 95% | 0% | 1844 | -23
[5 empty] | 2019-05-07 | 13 | 3029.5 | 2033 | -41 | 1 | 0 | 2074 | 1128.277 | 1128.277 | 1128.277 | 1701.5664 | 780 | 200 | 2681.5664 | 67.04% | 95% | 0% | -46.9108 | 1081.3662 | -3550 | -400 | -2868.6338 | 71.72% | 68.03% | 95% | 0% | 2074 | -41
[5 empty] | 2019-05-07 | 14 | 3030 | 2199 | -72 | 1 | 0 | 2271 | 1436.8508 | 1436.8508 | 1436.8508 | 1701.5664 | 780 | 200 | 2681.5664 | 67.04% | 95% | 0% | -82.3799 | 1354.4709 | -3550 | -400 | -2595.5291 | 64.89% | 68.02% | 95% | 0% | 2271 | -72
[5 empty] | 2019-05-07 | 15 | 3030.5 | 2355 | -117 | 1 | 0 | 2472 | 1751.69 | 1751.69 | 1751.69 | 1701.5664 | 780 | 200 | 2681.5664 | 67.04% | 95% | 0% | -133.8673 | 1617.8227 | -3550 | -400 | -2332.1773 | 58.3% | 68.02% | 95% | 0% | 2472 | -117
[5 empty] | 2019-05-07 | 16 | 3031 | 2379 | -174 | 1 | 0 | 2553 | 1878.5655 | 1878.5655 | 1878.5655 | 1701.5664 | 780 | 200 | 2681.5664 | 67.04% | 95% | 0% | -199.0847 | 1679.4809 | -3550 | -400 | -2270.5191 | 56.76% | 68.01% | 95% | 0% | 2553 | -174
[5 empty] | 2019-05-07 | 17 | 3031.5 | 2355 | -237 | 1 | 0 | 2592 | 1939.6538 | 1939.6538 | 1939.6538 | 1701.5664 | 780 | 200 | 2681.5664 | 67.04% | 95% | 0% | -271.167 | 1668.4867 | -3550 | -400 | -2281.5133 | 57.04% | 68.01% | 95% | 0% | 2592 | -237
[5 empty] | 2019-05-07 | 18 | 3032 | 2286 | -286 | 1 | 0 | 2572 | 1908.3265 | 1908.3265 | 1908.3265 | 1701.5664 | 780 | 200 | 2681.5664 | 67.04% | 95% | 0% | -327.2311 | 1581.0953 | -3550 | -400 | -2368.9047 | 59.22% | 68.01% | 95% | 0% | 2572 | -286
[5 empty] | 2019-05-07 | 19 | 3032.5 | 2253 | -329 | 1 | 0 | 2582 | 1923.9901 | 1923.9901 | 1923.9901 | 1700 | 780 | 200 | 2680 | 67% | 95% | 0% | -376.4302 | 1547.5599 | -3550 | -400 | -2402.4401 | 60.06% | 68.01% | 95% | 0% | 2582 | -329
[5 empty] | 2019-05-07 | 20 | 3033 | 2171 | -372 | 1 | 0 | 2543 | 1862.9019 | 1862.9019 | 1862.9019 | 1700 | 780 | 200 | 2680 | 67% | 95% | 0% | -425.6293 | 1437.2726 | -3550 | -400 | -2512.7274 | 62.82% | 68% | 95% | 0% | 2543 | -372
[5 empty] | 2019-05-07 | 21 | 3033.5 | 2073 | -413 | 1 | 0 | 2486 | 1773.6191 | 1773.6191 | 1773.6191 | 1700 | 780 | 200 | 2680 | 67% | 95% | 0% | -472.54 | 1301.0791 | -3550 | -400 | -2648.9209 | 66.22% | 68% | 95% | 0% | 2486 | -413
[5 empty] | 2019-05-07 | 22 | 3034 | 2027 | -448 | 1 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 1700 | 780 | 200 | 2680 | 67% | 95% | 0% | -512.5858 | 1243.8033 | -3550 | -400 | -2706.1967 | 67.65% | 67.99% | 95% | 0% | 2475 | -448
[5 empty] | 2019-05-07 | 23 | 3034.5 | 2004 | -471 | 1 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 1700 | 780 | 200 | 2680 | 67% | 95% | 0% | -538.9016 | 1217.4875 | -3550 | -400 | -2732.5125 | 68.31% | 67.99% | 95% | 0% | 2475 | -471
[5 empty] | 2019-05-07 | 24 | 3035 | 2016 | -459 | 1 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 1700 | 780 | 200 | 2680 | 67% | 95% | 0% | -525.1716 | 1231.2175 | -3550 | -400 | -2718.7825 | 67.97% | 67.99% | 95% | 0% | 2475 | -459
[5 empty] | 2019-05-07 | 25 | 3035.5 | 2014 | -467 | 1 | 0 | 2481 | 1765.7873 | 1765.7873 | 1765.7873 | 1700 | 780 | 200 | 2680 | 67% | 95% | 0% | -534.3249 | 1231.4624 | -3550 | -400 | -2718.5376 | 67.96% | 67.99% | 95% | 0% | 2481 | -467
[5 empty] | 2019-05-07 | 26 | 3036 | 1980 | -492 | 1 | 0 | 2472 | 1751.69 | 1751.69 | 1751.69 | 1700 | 780 | 200 | 2680 | 67% | 95% | 0% | -562.9291 | 1188.761 | -3550 | -400 | -2761.239 | 69.03% | 67.98% | 95% | 0% | 2472 | -492
[5 empty] | 2019-05-07 | 27 | 3036.5 | 1975 | -477 | 1 | 0 | 2452 | 1720.3627 | 1720.3627 | 1720.3627 | 1700 | 780 | 200 | 2680 | 67% | 95% | 0% | -545.7666 | 1174.5961 | -3550 | -400 | -2775.4039 | 69.39% | 67.98% | 95% | 0% | 2452 | -477
[5 empty] | 2019-05-07 | 28 | 3037 | 1956 | -473 | 1 | 0 | 2429 | 1684.3364 | 1684.3364 | 1684.3364 | 1698.4336 | 780 | 200 | 2678.4336 | 66.96% | 95% | 0% | -541.1899 | 1143.1464 | -3550 | -400 | -2806.8536 | 70.17% | 67.97% | 95% | 0% | 2429 | -473
[5 empty] | 2019-05-07 | 29 | 3037.5 | 2001 | -424 | 1 | 0 | 2425 | 1678.0709 | 1678.0709 | 1678.0709 | 1698.4336 | 780 | 200 | 2678.4336 | 66.96% | 95% | 0% | -485.1259 | 1192.945 | -3550 | -400 | -2757.055 | 68.93% | 67.97% | 95% | 0% | 2425 | -424
[5 empty] | 2019-05-07 | 30 | 3038 | 2044 | -376 | 1 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 1698.4336 | 780 | 200 | 2678.4336 | 66.96% | 95% | 0% | -430.2059 | 1240.0331 | -3550 | -400 | -2709.9669 | 67.75% | 67.97% | 95% | 0% | 2420 | -376
[5 empty] | 2019-05-07 | 31 | 3038.5 | 2074 | -352 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1698.4336 | 780 | 200 | 2678.4336 | 66.96% | 95% | 0% | -402.746 | 1276.8913 | -3550 | -400 | -2673.1087 | 66.83% | 67.96% | 95% | 0% | 2426 | -352
[5 empty] | 2019-05-07 | 32 | 3039 | 2124 | -342 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 1698.4336 | 780 | 200 | 2678.4336 | 66.96% | 95% | 0% | -391.3043 | 1350.9875 | -3550 | -400 | -2599.0125 | 64.98% | 67.96% | 95% | 0% | 2466 | -342
[5 empty] | 2019-05-07 | 33 | 3039.5 | 2238 | -311 | 1 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 1698.4336 | 780 | 200 | 2678.4336 | 66.96% | 95% | 0% | -355.8352 | 1516.4648 | -3550 | -400 | -2433.5352 | 60.84% | 67.96% | 95% | 0% | 2549 | -311
[5 empty] | 2019-05-07 | 34 | 3040 | 2339 | -277 | 1 | 0 | 2616 | 1977.2465 | 1977.2465 | 1977.2465 | 1698.4336 | 780 | 200 | 2678.4336 | 66.96% | 95% | 0% | -316.9336 | 1660.3129 | -3550 | -400 | -2289.6871 | 57.24% | 67.96% | 95% | 0% | 2616 | -277
[5 empty] | 2019-05-07 | 35 | 3040.5 | 2429 | -230 | 1 | 0 | 2659 | 2044.6002 | 2044.6002 | 2044.6002 | 1698.4336 | 780 | 200 | 2678.4336 | 66.96% | 95% | 0% | -263.1579 | 1781.4423 | -3550 | -400 | -2168.5577 | 54.21% | 67.95% | 95% | 0% | 2659 | -230
[5 empty] | 2019-05-07 | 36 | 3041 | 2507 | -190 | 1 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 1698.4336 | 780 | 200 | 2678.4336 | 66.96% | 95% | 0% | -217.3913 | 1886.7307 | -3550 | -400 | -2063.2693 | 51.58% | 67.94% | 95% | 0% | 2697 | -190
[5 empty] | 2019-05-07 | 37 | 3041.5 | 2545 | -149 | 1 | 0 | 2694 | 2099.4229 | 2099.4229 | 2099.4229 | 1698.4336 | 780 | 200 | 2678.4336 | 66.96% | 95% | 0% | -170.4805 | 1928.9424 | -3550 | -400 | -2021.0576 | 50.53% | 67.94% | 95% | 0% | 2694 | -149
[5 empty] | 2019-05-07 | 38 | 3042 | 2602 | -114 | 1 | 0 | 2716 | 2133.8829 | 2133.8829 | 2133.8829 | 1698.4336 | 780 | 200 | 2678.4336 | 66.96% | 95% | 0% | -130.4348 | 2003.4482 | -3550 | -400 | -1946.5518 | 48.66% | 67.94% | 95% | 0% | 2716 | -114
[5 empty] | 2019-05-07 | 39 | 3042.5 | 2585 | -93 | 1 | 0 | 2678 | 2074.3611 | 2074.3611 | 2074.3611 | 1698.4336 | 780 | 200 | 2678.4336 | 66.96% | 95% | 0% | -106.4073 | 1967.9538 | -3550 | -400 | -1982.0462 | 49.55% | 67.94% | 95% | 0% | 2678 | -93
[5 empty] | 2019-05-07 | 40 | 3043 | 2571 | -76 | 1 | 0 | 2647 | 2025.8038 | 2025.8038 | 2025.8038 | 1696.8673 | 780 | 200 | 2676.8673 | 66.92% | 95% | 0% | -86.9565 | 1938.8473 | -3550 | -400 | -2011.1527 | 50.28% | 67.93% | 95% | 0% | 2647 | -76
[5 empty] | 2019-05-07 | 41 | 3043.5 | 2574 | -65 | 1 | 0 | 2639 | 2013.2729 | 2013.2729 | 2013.2729 | 1696.8673 | 780 | 200 | 2676.8673 | 66.92% | 95% | 0% | -74.3707 | 1938.9022 | -3550 | -400 | -2011.0978 | 50.28% | 67.91% | 95% | 0% | 2639 | -65
[5 empty] | 2019-05-07 | 42 | 3044 | 2564 | -66 | 1 | 0 | 2630 | 1999.1756 | 1999.1756 | 1999.1756 | 1696.8673 | 780 | 200 | 2676.8673 | 66.92% | 95% | 0% | -75.5149 | 1923.6607 | -3550 | -400 | -2026.3393 | 50.66% | 67.91% | 95% | 0% | 2630 | -66
[5 empty] | 2019-05-07 | 43 | 3044.5 | 2516 | -69 | 1 | 0 | 2585 | 1928.6892 | 1928.6892 | 1928.6892 | 1696.8673 | 780 | 200 | 2676.8673 | 66.92% | 95% | 0% | -78.9474 | 1849.7418 | -3550 | -400 | -2100.2582 | 52.51% | 67.91% | 95% | 0% | 2585 | -69
[5 empty] | 2019-05-07 | 44 | 3045 | 2412 | -73 | 0 | 0 | 2485 | 1772.0528 | 1772.0528 | 1772.0528 | 1696.8673 | 780 | 200 | 2676.8673 | 66.92% | 95% | 0% | -83.524 | 1688.5287 | -2750 | -200 | -1261.4713 | 31.54% | 67.91% | 95% | 0% | 2485 | -73
[5 empty] | 2019-05-07 | 45 | 3045.5 | 2268 | -75 | 0 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 1696.8673 | 780 | 200 | 2676.8673 | 66.92% | 95% | 0% | -85.8124 | 1463.8167 | -2750 | -200 | -1486.1833 | 37.15% | 67.9% | 95% | 0% | 2343 | -75
[5 empty] | 2019-05-07 | 46 | 3046 | 2110 | -77 | 0 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 1696.8673 | 780 | 200 | 2676.8673 | 66.92% | 95% | 0% | -88.1007 | 1217.1755 | -2750 | -200 | -1732.8245 | 43.32% | 67.9% | 95% | 0% | 2187 | -77
[5 empty] | 2019-05-07 | 47 | 3046.5 | 1931 | -80 | 0 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 1696.8673 | 780 | 200 | 2676.8673 | 66.92% | 95% | 0% | -91.5332 | 938.0629 | -2750 | -200 | -2011.9371 | 50.3% | 67.9% | 95% | 0% | 2011 | -80
[5 empty] | 2019-05-07 | 48 | 3047 | 1795 | -83 | 0 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 1696.8673 | 780 | 200 | 2676.8673 | 66.92% | 95% | 0% | -94.9657 | 726.3039 | -2750 | -200 | -2223.6961 | 55.59% | 67.9% | 95% | 0% | 1878 | -83
[5 empty] | 2019-05-08 | 1 | 3047.5 | 1701 | -85 | 0 | 0 | 1786 | 677.1641 | 677.1641 | 677.1641 | 1695.3009 | 780 | 200 | 2675.3009 | 66.88% | 95% | 0% | -97.254 | 579.9101 | -2750 | -200 | -2370.0899 | 59.25% | 67.9% | 95% | 0% | 1786 | -85
[5 empty] | 2019-05-08 | 2 | 3048 | 1653 | -87 | 0 | 0 | 1740 | 605.1113 | 605.1113 | 605.1113 | 1695.3009 | 780 | 200 | 2675.3009 | 66.88% | 95% | 0% | -99.5423 | 505.569 | -2750 | -200 | -2444.431 | 61.11% | 67.89% | 95% | 0% | 1740 | -87
[5 empty] | 2019-05-08 | 3 | 3048.5 | 1640 | -90 | 1 | 0 | 1730 | 589.4477 | 589.4477 | 589.4477 | 1695.3009 | 780 | 200 | 2675.3009 | 66.88% | 95% | 0% | -102.9748 | 486.4728 | -3550 | -400 | -3463.5272 | 86.59% | 67.89% | 95% | 0% | 1730 | -90
[5 empty] | 2019-05-08 | 4 | 3049 | 1647 | -93 | 1 | 0 | 1740 | 605.1113 | 605.1113 | 605.1113 | 1695.3009 | 780 | 200 | 2675.3009 | 66.88% | 95% | 0% | -106.4073 | 498.704 | -3550 | -400 | -3451.296 | 86.28% | 67.88% | 95% | 0% | 1740 | -93
[5 empty] | 2019-05-08 | 5 | 3049.5 | 1635 | -96 | 1 | 0 | 1731 | 591.014 | 591.014 | 591.014 | 1695.3009 | 780 | 200 | 2675.3009 | 66.88% | 95% | 0% | -109.8398 | 481.1742 | -3550 | -400 | -3468.8258 | 86.72% | 67.88% | 95% | 0% | 1731 | -96
[5 empty] | 2019-05-08 | 6 | 3050 | 1598 | -100 | 1 | 0 | 1698 | 539.324 | 539.324 | 539.324 | 1695.3009 | 780 | 200 | 2675.3009 | 66.88% | 95% | 0% | -114.4165 | 424.9075 | -3550 | -400 | -3525.0925 | 88.13% | 67.87% | 95% | 0% | 1698 | -100
[5 empty] | 2019-05-08 | 7 | 3050.5 | 1575 | -103 | 1 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 1695.3009 | 780 | 200 | 2675.3009 | 66.88% | 95% | 0% | -117.849 | 390.1477 | -3550 | -400 | -3559.8523 | 89% | 67.87% | 95% | 0% | 1678 | -103
[5 empty] | 2019-05-08 | 8 | 3051 | 1550 | -106 | 1 | 0 | 1656 | 473.5367 | 473.5367 | 473.5367 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -121.2815 | 352.2552 | -3550 | -400 | -3597.7448 | 89.94% | 67.87% | 95% | 0% | 1656 | -106
[5 empty] | 2019-05-08 | 9 | 3051.5 | 1535 | -108 | 1 | 0 | 1643 | 453.1739 | 453.1739 | 453.1739 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -123.5698 | 329.6042 | -3550 | -400 | -3620.3958 | 90.51% | 67.87% | 95% | 0% | 1643 | -108
[5 empty] | 2019-05-08 | 10 | 3052 | 1548 | -110 | 1 | 0 | 1658 | 476.6694 | 476.6694 | 476.6694 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -125.8581 | 350.8113 | -3550 | -400 | -3599.1887 | 89.98% | 67.86% | 95% | 0% | 1658 | -110
[5 empty] | 2019-05-08 | 11 | 3052.5 | 1572 | -115 | 1 | 0 | 1687 | 522.094 | 522.094 | 522.094 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -131.5789 | 390.515 | -3550 | -400 | -3559.485 | 88.99% | 67.86% | 95% | 0% | 1687 | -115
[5 empty] | 2019-05-08 | 12 | 3053 | 1624 | -119 | 1 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -136.1556 | 473.6548 | -3550 | -400 | -3476.3452 | 86.91% | 67.86% | 95% | 0% | 1743 | -119
[5 empty] | 2019-05-08 | 13 | 3053.5 | 1818 | -124 | 1 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -141.8764 | 779.6405 | -3550 | -400 | -3170.3595 | 79.26% | 67.85% | 95% | 0% | 1942 | -124
[5 empty] | 2019-05-08 | 14 | 3054 | 2026 | -133 | 1 | 0 | 2159 | 1261.418 | 1261.418 | 1261.418 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -152.1739 | 1109.2441 | -3550 | -400 | -2840.7559 | 71.02% | 67.85% | 95% | 0% | 2159 | -133
[5 empty] | 2019-05-08 | 15 | 3054.5 | 2255 | -144 | 1 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -164.7597 | 1472.5857 | -3550 | -400 | -2477.4143 | 61.94% | 67.85% | 95% | 0% | 2399 | -144
[5 empty] | 2019-05-08 | 16 | 3055 | 2382 | -159 | 1 | 0 | 2541 | 1859.7692 | 1859.7692 | 1859.7692 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -181.9222 | 1677.847 | -3550 | -400 | -2272.153 | 56.8% | 67.84% | 95% | 0% | 2541 | -159
[5 empty] | 2019-05-08 | 17 | 3055.5 | 2471 | -175 | 1 | 0 | 2646 | 2024.2374 | 2024.2374 | 2024.2374 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -200.2288 | 1824.0086 | -3550 | -400 | -2125.9914 | 53.15% | 67.84% | 95% | 0% | 2646 | -175
[5 empty] | 2019-05-08 | 18 | 3056 | 2449 | -194 | 1 | 0 | 2643 | 2019.5383 | 2019.5383 | 2019.5383 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -221.968 | 1797.5704 | -3550 | -400 | -2152.4296 | 53.81% | 67.84% | 95% | 0% | 2643 | -194
[5 empty] | 2019-05-08 | 19 | 3056.5 | 2446 | -216 | 1 | 0 | 2662 | 2049.2993 | 2049.2993 | 2049.2993 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -247.1396 | 1802.1597 | -3550 | -400 | -2147.8403 | 53.7% | 67.84% | 95% | 0% | 2662 | -216
[5 empty] | 2019-05-08 | 20 | 3057 | 2408 | -241 | 1 | 0 | 2649 | 2028.9365 | 2028.9365 | 2028.9365 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -275.7437 | 1753.1928 | -3550 | -400 | -2196.8072 | 54.92% | 67.84% | 95% | 0% | 2649 | -241
[5 empty] | 2019-05-08 | 21 | 3057.5 | 2361 | -283 | 1 | 0 | 2644 | 2021.1047 | 2021.1047 | 2021.1047 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -323.7986 | 1697.3061 | -3550 | -400 | -2252.6939 | 56.32% | 67.83% | 95% | 0% | 2644 | -283
[5 empty] | 2019-05-08 | 22 | 3058 | 2302 | -324 | 1 | 0 | 2626 | 1992.9101 | 1992.9101 | 1992.9101 | 1693.7345 | 780 | 200 | 2673.7345 | 66.84% | 95% | 0% | -370.7094 | 1622.2008 | -3550 | -400 | -2327.7992 | 58.19% | 67.83% | 95% | 0% | 2626 | -324
[5 empty] | 2019-05-08 | 23 | 3058.5 | 2265 | -350 | 1 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 1692.1682 | 780 | 200 | 2672.1682 | 66.8% | 95% | 0% | -400.4577 | 1575.2225 | -3550 | -400 | -2374.7775 | 59.37% | 67.82% | 95% | 0% | 2615 | -350
[5 empty] | 2019-05-08 | 24 | 3059 | 2213 | -383 | 1 | 0 | 2596 | 1945.9192 | 1945.9192 | 1945.9192 | 1692.1682 | 780 | 200 | 2672.1682 | 66.8% | 95% | 0% | -438.2151 | 1507.7041 | -3550 | -400 | -2442.2959 | 61.06% | 67.82% | 95% | 0% | 2596 | -383
[5 empty] | 2019-05-08 | 25 | 3059.5 | 2171 | -407 | 1 | 0 | 2578 | 1917.7246 | 1917.7246 | 1917.7246 | 1692.1682 | 780 | 200 | 2672.1682 | 66.8% | 95% | 0% | -465.6751 | 1452.0496 | -3550 | -400 | -2497.9504 | 62.45% | 67.82% | 95% | 0% | 2578 | -407
[5 empty] | 2019-05-08 | 26 | 3060 | 2134 | -428 | 1 | 0 | 2562 | 1892.6628 | 1892.6628 | 1892.6628 | 1692.1682 | 780 | 200 | 2672.1682 | 66.8% | 95% | 0% | -489.7025 | 1402.9603 | -3550 | -400 | -2547.0397 | 63.68% | 67.82% | 95% | 0% | 2562 | -428
[5 empty] | 2019-05-08 | 27 | 3060.5 | 2111 | -417 | 1 | 0 | 2528 | 1839.4064 | 1839.4064 | 1839.4064 | 1692.1682 | 780 | 200 | 2672.1682 | 66.8% | 95% | 0% | -477.1167 | 1362.2897 | -3550 | -400 | -2587.7103 | 64.69% | 67.81% | 95% | 0% | 2528 | -417
[5 empty] | 2019-05-08 | 28 | 3061 | 2062 | -442 | 1 | 0 | 2504 | 1801.8137 | 1801.8137 | 1801.8137 | 1692.1682 | 780 | 200 | 2672.1682 | 66.8% | 95% | 0% | -505.7208 | 1296.0929 | -3550 | -400 | -2653.9071 | 66.35% | 67.81% | 95% | 0% | 2504 | -442
[5 empty] | 2019-05-08 | 29 | 3061.5 | 2063 | -447 | 1 | 0 | 2510 | 1811.2119 | 1811.2119 | 1811.2119 | 1692.1682 | 780 | 200 | 2672.1682 | 66.8% | 95% | 0% | -511.4416 | 1299.7702 | -3550 | -400 | -2650.2298 | 66.26% | 67.81% | 95% | 0% | 2510 | -447
[5 empty] | 2019-05-08 | 30 | 3062 | 2103 | -412 | 1 | 0 | 2515 | 1819.0437 | 1819.0437 | 1819.0437 | 1692.1682 | 780 | 200 | 2672.1682 | 66.8% | 95% | 0% | -471.3959 | 1347.6478 | -3550 | -400 | -2602.3522 | 65.06% | 67.81% | 95% | 0% | 2515 | -412
[5 empty] | 2019-05-08 | 31 | 3062.5 | 2074 | -415 | 1 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 1692.1682 | 780 | 200 | 2672.1682 | 66.8% | 95% | 0% | -474.8284 | 1303.4898 | -3550 | -400 | -2646.5102 | 66.16% | 67.8% | 95% | 0% | 2489 | -415
[5 empty] | 2019-05-08 | 32 | 3063 | 2119 | -409 | 1 | 0 | 2528 | 1839.4064 | 1839.4064 | 1839.4064 | 1692.1682 | 780 | 200 | 2672.1682 | 66.8% | 95% | 0% | -467.9634 | 1371.443 | -3550 | -400 | -2578.557 | 64.46% | 67.8% | 95% | 0% | 2528 | -409
[5 empty] | 2019-05-08 | 33 | 3063.5 | 2180 | -397 | 1 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 1690.6018 | 780 | 200 | 2670.6018 | 66.77% | 95% | 0% | -454.2334 | 1461.9249 | -3550 | -400 | -2488.0751 | 62.2% | 67.8% | 95% | 0% | 2577 | -397
[5 empty] | 2019-05-08 | 34 | 3064 | 2324 | -337 | 1 | 0 | 2661 | 2047.7329 | 2047.7329 | 2047.7329 | 1690.6018 | 780 | 200 | 2670.6018 | 66.77% | 95% | 0% | -385.5835 | 1662.1494 | -3550 | -400 | -2287.8506 | 57.2% | 67.8% | 95% | 0% | 2661 | -337
[5 empty] | 2019-05-08 | 35 | 3064.5 | 2431 | -297 | 1 | 0 | 2728 | 2152.6793 | 2152.6793 | 2152.6793 | 1690.6018 | 780 | 200 | 2670.6018 | 66.77% | 95% | 0% | -339.8169 | 1812.8624 | -3550 | -400 | -2137.1376 | 53.43% | 67.79% | 95% | 0% | 2728 | -297
[5 empty] | 2019-05-08 | 36 | 3065 | 2480 | -266 | 1 | 0 | 2746 | 2180.8739 | 2180.8739 | 2180.8739 | 1690.6018 | 780 | 200 | 2670.6018 | 66.77% | 95% | 0% | -304.3478 | 1876.526 | -3550 | -400 | -2073.474 | 51.84% | 67.79% | 95% | 0% | 2746 | -266
[5 empty] | 2019-05-08 | 37 | 3065.5 | 2512 | -234 | 1 | 0 | 2746 | 2180.8739 | 2180.8739 | 2180.8739 | 1690.6018 | 780 | 200 | 2670.6018 | 66.77% | 95% | 0% | -267.7346 | 1913.1393 | -3550 | -400 | -2036.8607 | 50.92% | 67.79% | 95% | 0% | 2746 | -234
[5 empty] | 2019-05-08 | 38 | 3066 | 2537 | -208 | 1 | 0 | 2745 | 2179.3075 | 2179.3075 | 2179.3075 | 1690.6018 | 780 | 200 | 2670.6018 | 66.77% | 95% | 0% | -237.9863 | 1941.3212 | -3550 | -400 | -2008.6788 | 50.22% | 67.79% | 95% | 0% | 2745 | -208
[5 empty] | 2019-05-08 | 39 | 3066.5 | 2528 | -181 | 1 | 0 | 2709 | 2122.9184 | 2122.9184 | 2122.9184 | 1690.6018 | 780 | 200 | 2670.6018 | 66.77% | 95% | 0% | -207.0938 | 1915.8246 | -3550 | -400 | -2034.1754 | 50.85% | 67.78% | 95% | 0% | 2709 | -181
[5 empty] | 2019-05-08 | 40 | 3067 | 2569 | -148 | 1 | 0 | 2717 | 2135.4493 | 2135.4493 | 2135.4493 | 1690.6018 | 780 | 200 | 2670.6018 | 66.77% | 95% | 0% | -169.3364 | 1966.1129 | -3550 | -400 | -1983.8871 | 49.6% | 67.77% | 95% | 0% | 2717 | -148
[5 empty] | 2019-05-08 | 41 | 3067.5 | 2555 | -133 | 1 | 0 | 2688 | 2090.0247 | 2090.0247 | 2090.0247 | 1690.6018 | 780 | 200 | 2670.6018 | 66.77% | 95% | 0% | -152.1739 | 1937.8508 | -3550 | -400 | -2012.1492 | 50.3% | 67.77% | 95% | 0% | 2688 | -133
[5 empty] | 2019-05-08 | 42 | 3068 | 2513 | -127 | 1 | 0 | 2640 | 2014.8392 | 2014.8392 | 2014.8392 | 1690.6018 | 780 | 200 | 2670.6018 | 66.77% | 95% | 0% | -145.3089 | 1869.5303 | -3550 | -400 | -2080.4697 | 52.01% | 67.76% | 95% | 0% | 2640 | -127
[5 empty] | 2019-05-08 | 43 | 3068.5 | 2483 | -125 | 1 | 0 | 2608 | 1964.7156 | 1964.7156 | 1964.7156 | 1689.0354 | 780 | 200 | 2669.0354 | 66.73% | 95% | 0% | -143.0206 | 1821.695 | -3550 | -400 | -2128.305 | 53.21% | 67.76% | 95% | 0% | 2608 | -125
[5 empty] | 2019-05-08 | 44 | 3069 | 2376 | -123 | 1 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 1689.0354 | 780 | 200 | 2669.0354 | 66.73% | 95% | 0% | -140.7323 | 1653.2496 | -3550 | -400 | -2296.7504 | 57.42% | 67.76% | 95% | 0% | 2499 | -123
[5 empty] | 2019-05-08 | 45 | 3069.5 | 2238 | -122 | 0 | 0 | 2360 | 1576.2572 | 1576.2572 | 1576.2572 | 1689.0354 | 780 | 200 | 2669.0354 | 66.73% | 95% | 0% | -139.5881 | 1436.6691 | -2750 | -200 | -1513.3309 | 37.83% | 67.76% | 95% | 0% | 2360 | -122
[5 empty] | 2019-05-08 | 46 | 3070 | 2086 | -120 | 0 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 1689.0354 | 780 | 200 | 2669.0354 | 66.73% | 95% | 0% | -137.2998 | 1197.7373 | -2750 | -200 | -1752.2627 | 43.81% | 67.75% | 95% | 0% | 2206 | -120
[5 empty] | 2019-05-08 | 47 | 3070.5 | 1928 | -118 | 0 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1689.0354 | 780 | 200 | 2669.0354 | 66.73% | 95% | 0% | -135.0114 | 949.4074 | -2750 | -200 | -2000.5926 | 50.01% | 67.74% | 95% | 0% | 2046 | -118
[5 empty] | 2019-05-08 | 48 | 3071 | 1812 | -116 | 0 | 0 | 1928 | 899.5878 | 899.5878 | 899.5878 | 1689.0354 | 780 | 200 | 2669.0354 | 66.73% | 95% | 0% | -132.7231 | 766.8647 | -2750 | -200 | -2183.1353 | 54.58% | 67.74% | 95% | 0% | 1928 | -116
[5 empty] | 2019-05-09 | 1 | 3071.5 | 1712 | -113 | 0 | 0 | 1825 | 738.2523 | 738.2523 | 738.2523 | 1689.0354 | 780 | 200 | 2669.0354 | 66.73% | 95% | 0% | -129.2906 | 608.9616 | -2750 | -200 | -2341.0384 | 58.53% | 67.74% | 95% | 0% | 1825 | -113
[5 empty] | 2019-05-09 | 2 | 3072 | 1665 | -110 | 0 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 1689.0354 | 780 | 200 | 2669.0354 | 66.73% | 95% | 0% | -125.8581 | 534.0759 | -2750 | -200 | -2415.9241 | 60.4% | 67.74% | 95% | 0% | 1775 | -110
[5 empty] | 2019-05-09 | 3 | 3072.5 | 1666 | -109 | 1 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 1689.0354 | 780 | 200 | 2669.0354 | 66.73% | 95% | 0% | -124.714 | 535.2201 | -3550 | -400 | -3414.7799 | 85.37% | 67.73% | 95% | 0% | 1775 | -109
[5 empty] | 2019-05-09 | 4 | 3073 | 1692 | -109 | 1 | 0 | 1801 | 700.6595 | 700.6595 | 700.6595 | 1689.0354 | 780 | 200 | 2669.0354 | 66.73% | 95% | 0% | -124.714 | 575.9456 | -3550 | -400 | -3374.0544 | 84.35% | 67.73% | 95% | 0% | 1801 | -109
[5 empty] | 2019-05-09 | 5 | 3073.5 | 1687 | -108 | 1 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 1687.4691 | 780 | 200 | 2667.4691 | 66.69% | 95% | 0% | -123.5698 | 567.6915 | -3550 | -400 | -3382.3085 | 84.56% | 67.73% | 95% | 0% | 1795 | -108
[5 empty] | 2019-05-09 | 6 | 3074 | 1669 | -107 | 1 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 1687.4691 | 780 | 200 | 2667.4691 | 66.69% | 95% | 0% | -122.4256 | 539.0748 | -3550 | -400 | -3410.9252 | 85.27% | 67.73% | 95% | 0% | 1776 | -107
[5 empty] | 2019-05-09 | 7 | 3074.5 | 1650 | -107 | 1 | 0 | 1757 | 631.7395 | 631.7395 | 631.7395 | 1687.4691 | 780 | 200 | 2667.4691 | 66.69% | 95% | 0% | -122.4256 | 509.3139 | -3550 | -400 | -3440.6861 | 86.02% | 67.73% | 95% | 0% | 1757 | -107
[5 empty] | 2019-05-09 | 8 | 3075 | 1628 | -106 | 1 | 0 | 1734 | 595.7131 | 595.7131 | 595.7131 | 1687.4691 | 780 | 200 | 2667.4691 | 66.69% | 95% | 0% | -121.2815 | 474.4316 | -3550 | -400 | -3475.5684 | 86.89% | 67.72% | 95% | 0% | 1734 | -106
[5 empty] | 2019-05-09 | 9 | 3075.5 | 1624 | -104 | 1 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 1687.4691 | 780 | 200 | 2667.4691 | 66.69% | 95% | 0% | -118.9931 | 467.3218 | -3550 | -400 | -3482.6782 | 87.07% | 67.72% | 95% | 0% | 1728 | -104
[5 empty] | 2019-05-09 | 10 | 3076 | 1637 | -101 | 1 | 0 | 1738 | 601.9786 | 601.9786 | 601.9786 | 1687.4691 | 780 | 200 | 2667.4691 | 66.69% | 95% | 0% | -115.5606 | 486.4179 | -3550 | -400 | -3463.5821 | 86.59% | 67.72% | 95% | 0% | 1738 | -101
[5 empty] | 2019-05-09 | 11 | 3076.5 | 1664 | -101 | 1 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 1687.4691 | 780 | 200 | 2667.4691 | 66.69% | 95% | 0% | -115.5606 | 528.7098 | -3550 | -400 | -3421.2902 | 85.53% | 67.71% | 95% | 0% | 1765 | -101
[5 empty] | 2019-05-09 | 12 | 3077 | 1732 | -102 | 1 | 0 | 1834 | 752.3495 | 752.3495 | 752.3495 | 1687.4691 | 780 | 200 | 2667.4691 | 66.69% | 95% | 0% | -116.7048 | 635.6447 | -3550 | -400 | -3314.3553 | 82.86% | 67.71% | 95% | 0% | 1834 | -102
[5 empty] | 2019-05-09 | 13 | 3077.5 | 1938 | -111 | 1 | 0 | 2049 | 1089.1179 | 1089.1179 | 1089.1179 | 1687.4691 | 780 | 200 | 2667.4691 | 66.69% | 95% | 0% | -127.0023 | 962.1156 | -3550 | -400 | -2987.8844 | 74.7% | 67.71% | 95% | 0% | 2049 | -111
[5 empty] | 2019-05-09 | 14 | 3078 | 2117 | -130 | 1 | 0 | 2247 | 1399.258 | 1399.258 | 1399.258 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -148.7414 | 1250.5166 | -3550 | -400 | -2699.4834 | 67.49% | 67.7% | 95% | 0% | 2247 | -130
[5 empty] | 2019-05-09 | 15 | 3078.5 | 2319 | -150 | 1 | 0 | 2469 | 1746.9909 | 1746.9909 | 1746.9909 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -171.6247 | 1575.3662 | -3550 | -400 | -2374.6338 | 59.37% | 67.7% | 95% | 0% | 2469 | -150
[5 empty] | 2019-05-09 | 16 | 3079 | 2392 | -177 | 1 | 0 | 2569 | 1903.6274 | 1903.6274 | 1903.6274 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -202.5172 | 1701.1102 | -3550 | -400 | -2248.8898 | 56.22% | 67.7% | 95% | 0% | 2569 | -177
[5 empty] | 2019-05-09 | 17 | 3079.5 | 2415 | -211 | 1 | 0 | 2626 | 1992.9101 | 1992.9101 | 1992.9101 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -241.4188 | 1751.4914 | -3550 | -400 | -2198.5086 | 54.96% | 67.7% | 95% | 0% | 2626 | -211
[5 empty] | 2019-05-09 | 18 | 3080 | 2379 | -235 | 1 | 0 | 2614 | 1974.1138 | 1974.1138 | 1974.1138 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -268.8787 | 1705.235 | -3550 | -400 | -2244.765 | 56.12% | 67.69% | 95% | 0% | 2614 | -235
[5 empty] | 2019-05-09 | 19 | 3080.5 | 2372 | -258 | 1 | 0 | 2630 | 1999.1756 | 1999.1756 | 1999.1756 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -295.1945 | 1703.9811 | -3550 | -400 | -2246.0189 | 56.15% | 67.68% | 95% | 0% | 2630 | -258
[5 empty] | 2019-05-09 | 20 | 3081 | 2326 | -298 | 1 | 0 | 2624 | 1989.7774 | 1989.7774 | 1989.7774 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -340.9611 | 1648.8163 | -3550 | -400 | -2301.1837 | 57.53% | 67.67% | 95% | 0% | 2624 | -298
[5 empty] | 2019-05-09 | 21 | 3081.5 | 2253 | -313 | 1 | 0 | 2566 | 1898.9283 | 1898.9283 | 1898.9283 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -358.1236 | 1540.8047 | -3550 | -400 | -2409.1953 | 60.23% | 67.67% | 95% | 0% | 2566 | -313
[5 empty] | 2019-05-09 | 22 | 3082 | 2241 | -323 | 1 | 0 | 2564 | 1895.7955 | 1895.7955 | 1895.7955 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -369.5652 | 1526.2303 | -3550 | -400 | -2423.7697 | 60.59% | 67.67% | 95% | 0% | 2564 | -323
[5 empty] | 2019-05-09 | 23 | 3082.5 | 2204 | -360 | 1 | 0 | 2564 | 1895.7955 | 1895.7955 | 1895.7955 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -411.8993 | 1483.8962 | -3550 | -400 | -2466.1038 | 61.65% | 67.66% | 95% | 0% | 2564 | -360
[5 empty] | 2019-05-09 | 24 | 3083 | 2172 | -382 | 1 | 0 | 2554 | 1880.1319 | 1880.1319 | 1880.1319 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -437.0709 | 1443.061 | -3550 | -400 | -2506.939 | 62.67% | 67.66% | 95% | 0% | 2554 | -382
[5 empty] | 2019-05-09 | 25 | 3083.5 | 2182 | -383 | 1 | 0 | 2565 | 1897.3619 | 1897.3619 | 1897.3619 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -438.2151 | 1459.1468 | -3550 | -400 | -2490.8532 | 62.27% | 67.66% | 95% | 0% | 2565 | -383
[5 empty] | 2019-05-09 | 26 | 3084 | 2161 | -367 | 1 | 0 | 2528 | 1839.4064 | 1839.4064 | 1839.4064 | 1685.9027 | 780 | 200 | 2665.9027 | 66.65% | 95% | 0% | -419.9085 | 1419.498 | -3550 | -400 | -2530.502 | 63.26% | 67.66% | 95% | 0% | 2528 | -367
[5 empty] | 2019-05-09 | 27 | 3084.5 | 2136 | -372 | 1 | 0 | 2508 | 1808.0791 | 1808.0791 | 1808.0791 | 1684.3364 | 780 | 200 | 2664.3364 | 66.61% | 95% | 0% | -425.6293 | 1382.4499 | -3550 | -400 | -2567.5501 | 64.19% | 67.66% | 95% | 0% | 2508 | -372
[5 empty] | 2019-05-09 | 28 | 3085 | 2136 | -368 | 1 | 0 | 2504 | 1801.8137 | 1801.8137 | 1801.8137 | 1684.3364 | 780 | 200 | 2664.3364 | 66.61% | 95% | 0% | -421.0526 | 1380.7611 | -3550 | -400 | -2569.2389 | 64.23% | 67.66% | 95% | 0% | 2504 | -368
[5 empty] | 2019-05-09 | 29 | 3085.5 | 2166 | -348 | 1 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 1684.3364 | 780 | 200 | 2664.3364 | 66.61% | 95% | 0% | -398.1693 | 1419.308 | -3550 | -400 | -2530.692 | 63.27% | 67.65% | 95% | 0% | 2514 | -348
[5 empty] | 2019-05-09 | 30 | 3086 | 2153 | -344 | 1 | 0 | 2497 | 1790.8491 | 1790.8491 | 1790.8491 | 1684.3364 | 780 | 200 | 2664.3364 | 66.61% | 95% | 0% | -393.5927 | 1397.2565 | -3550 | -400 | -2552.7435 | 63.82% | 67.65% | 95% | 0% | 2497 | -344
[5 empty] | 2019-05-09 | 31 | 3086.5 | 2175 | -323 | 1 | 0 | 2498 | 1792.4155 | 1792.4155 | 1792.4155 | 1684.3364 | 780 | 200 | 2664.3364 | 66.61% | 95% | 0% | -369.5652 | 1422.8503 | -3550 | -400 | -2527.1497 | 63.18% | 67.65% | 95% | 0% | 2498 | -323
[5 empty] | 2019-05-09 | 32 | 3087 | 2249 | -307 | 1 | 0 | 2556 | 1883.2646 | 1883.2646 | 1883.2646 | 1684.3364 | 780 | 200 | 2664.3364 | 66.61% | 95% | 0% | -351.2586 | 1532.0061 | -3550 | -400 | -2417.9939 | 60.45% | 67.65% | 95% | 0% | 2556 | -307
[5 empty] | 2019-05-09 | 33 | 3087.5 | 2326 | -289 | 1 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 1684.3364 | 780 | 200 | 2664.3364 | 66.61% | 95% | 0% | -330.6636 | 1645.0165 | -3550 | -400 | -2304.9835 | 57.62% | 67.65% | 95% | 0% | 2615 | -289
[5 empty] | 2019-05-09 | 34 | 3088 | 2390 | -274 | 1 | 0 | 2664 | 2052.432 | 2052.432 | 2052.432 | 1684.3364 | 780 | 200 | 2664.3364 | 66.61% | 95% | 0% | -313.5011 | 1738.9308 | -3550 | -400 | -2211.0692 | 55.28% | 67.64% | 95% | 0% | 2664 | -274
[5 empty] | 2019-05-09 | 35 | 3088.5 | 2454 | -242 | 1 | 0 | 2696 | 2102.5556 | 2102.5556 | 2102.5556 | 1684.3364 | 780 | 200 | 2664.3364 | 66.61% | 95% | 0% | -276.8879 | 1825.6678 | -3550 | -400 | -2124.3322 | 53.11% | 67.64% | 95% | 0% | 2696 | -242
[5 empty] | 2019-05-09 | 36 | 3089 | 2510 | -206 | 1 | 0 | 2716 | 2133.8829 | 2133.8829 | 2133.8829 | 1684.3364 | 780 | 200 | 2664.3364 | 66.61% | 95% | 0% | -235.6979 | 1898.185 | -3550 | -400 | -2051.815 | 51.3% | 67.64% | 95% | 0% | 2716 | -206
[5 empty] | 2019-05-09 | 37 | 3089.5 | 2546 | -175 | 1 | 0 | 2721 | 2141.7148 | 2141.7148 | 2141.7148 | 1684.3364 | 780 | 200 | 2664.3364 | 66.61% | 95% | 0% | -200.2288 | 1941.4859 | -3550 | -400 | -2008.5141 | 50.21% | 67.64% | 95% | 0% | 2721 | -175
[5 empty] | 2019-05-09 | 38 | 3090 | 2579 | -146 | 1 | 0 | 2725 | 2147.9802 | 2147.9802 | 2147.9802 | 1684.3364 | 780 | 200 | 2664.3364 | 66.61% | 95% | 0% | -167.0481 | 1980.9322 | -3550 | -400 | -1969.0678 | 49.23% | 67.63% | 95% | 0% | 2725 | -146
[5 empty] | 2019-05-09 | 39 | 3090.5 | 2601 | -115 | 1 | 0 | 2716 | 2133.8829 | 2133.8829 | 2133.8829 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -131.5789 | 2002.304 | -3550 | -400 | -1947.696 | 48.69% | 67.63% | 95% | 0% | 2716 | -115
[5 empty] | 2019-05-09 | 40 | 3091 | 2616 | -86 | 1 | 0 | 2702 | 2111.9538 | 2111.9538 | 2111.9538 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -98.3982 | 2013.5557 | -3550 | -400 | -1936.4443 | 48.41% | 67.63% | 95% | 0% | 2702 | -86
[5 empty] | 2019-05-09 | 41 | 3091.5 | 2623 | -65 | 1 | 0 | 2688 | 2090.0247 | 2090.0247 | 2090.0247 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -74.3707 | 2015.654 | -3550 | -400 | -1934.346 | 48.36% | 67.62% | 95% | 0% | 2688 | -65
[5 empty] | 2019-05-09 | 42 | 3092 | 2645 | -55 | 1 | 0 | 2700 | 2108.8211 | 2108.8211 | 2108.8211 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -62.9291 | 2045.892 | -3550 | -400 | -1904.108 | 47.6% | 67.62% | 95% | 0% | 2700 | -55
[5 empty] | 2019-05-09 | 43 | 3092.5 | 2626 | -52 | 1 | 0 | 2678 | 2074.3611 | 2074.3611 | 2074.3611 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -59.4966 | 2014.8645 | -3550 | -400 | -1935.1355 | 48.38% | 67.62% | 95% | 0% | 2678 | -52
[5 empty] | 2019-05-09 | 44 | 3093 | 2552 | -49 | 0 | 0 | 2601 | 1953.751 | 1953.751 | 1953.751 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -56.0641 | 1897.687 | -2750 | -200 | -1052.313 | 26.31% | 67.62% | 95% | 0% | 2601 | -49
[5 empty] | 2019-05-09 | 45 | 3093.5 | 2418 | -46 | 0 | 0 | 2464 | 1739.1591 | 1739.1591 | 1739.1591 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -52.6316 | 1686.5275 | -2750 | -200 | -1263.4725 | 31.59% | 67.61% | 95% | 0% | 2464 | -46
[5 empty] | 2019-05-09 | 46 | 3094 | 2285 | -44 | 0 | 0 | 2329 | 1527.6999 | 1527.6999 | 1527.6999 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -50.3432 | 1477.3567 | -2750 | -200 | -1472.6433 | 36.82% | 67.61% | 95% | 0% | 2329 | -44
[5 empty] | 2019-05-09 | 47 | 3094.5 | 2116 | -41 | 0 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -46.9108 | 1211.3745 | -2750 | -200 | -1738.6255 | 43.47% | 67.61% | 95% | 0% | 2157 | -41
[5 empty] | 2019-05-09 | 48 | 3095 | 1991 | -39 | 0 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -44.6224 | 1014.7345 | -2750 | -200 | -1935.2655 | 48.38% | 67.6% | 95% | 0% | 2030 | -39
[5 empty] | 2019-05-10 | 1 | 3095.5 | 1896 | -34 | 0 | 0 | 1930 | 902.7205 | 902.7205 | 902.7205 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -38.9016 | 863.8189 | -2750 | -200 | -2086.1811 | 52.15% | 67.6% | 95% | 0% | 1930 | -34
[5 empty] | 2019-05-10 | 2 | 3096 | 1848 | -30 | 0 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -34.3249 | 786.9446 | -2750 | -200 | -2163.0554 | 54.08% | 67.6% | 95% | 0% | 1878 | -30
[5 empty] | 2019-05-10 | 3 | 3096.5 | 1846 | -28 | 0 | 0 | 1874 | 815.0041 | 815.0041 | 815.0041 | 1682.77 | 780 | 200 | 2662.77 | 66.57% | 95% | 0% | -32.0366 | 782.9675 | -2750 | -200 | -2167.0325 | 54.18% | 67.59% | 95% | 0% | 1874 | -28
[5 empty] | 2019-05-10 | 4 | 3097 | 1872 | -27 | 0 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 1681.2036 | 780 | 200 | 2661.2036 | 66.53% | 95% | 0% | -30.8924 | 823.2708 | -2750 | -200 | -2126.7292 | 53.17% | 67.59% | 95% | 0% | 1899 | -27
[5 empty] | 2019-05-10 | 5 | 3097.5 | 1873 | -26 | 0 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 1681.2036 | 780 | 200 | 2661.2036 | 66.53% | 95% | 0% | -29.7483 | 824.4149 | -2750 | -200 | -2125.5851 | 53.14% | 67.59% | 95% | 0% | 1899 | -26
[5 empty] | 2019-05-10 | 6 | 3098 | 1849 | -26 | 0 | 0 | 1875 | 816.5705 | 816.5705 | 816.5705 | 1681.2036 | 780 | 200 | 2661.2036 | 66.53% | 95% | 0% | -29.7483 | 786.8222 | -2750 | -200 | -2163.1778 | 54.08% | 67.59% | 95% | 0% | 1875 | -26
[5 empty] | 2019-05-10 | 7 | 3098.5 | 1834 | -25 | 0 | 0 | 1859 | 791.5087 | 791.5087 | 791.5087 | 1681.2036 | 780 | 200 | 2661.2036 | 66.53% | 95% | 0% | -28.6041 | 762.9045 | -2750 | -200 | -2187.0955 | 54.68% | 67.59% | 95% | 0% | 1859 | -25
[5 empty] | 2019-05-10 | 8 | 3099 | 1816 | -25 | 1 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 1681.2036 | 780 | 200 | 2661.2036 | 66.53% | 95% | 0% | -28.6041 | 734.71 | -3550 | -400 | -3215.29 | 80.38% | 67.58% | 95% | 0% | 1841 | -25
[5 empty] | 2019-05-10 | 9 | 3099.5 | 1814 | -25 | 1 | 0 | 1839 | 760.1814 | 760.1814 | 760.1814 | 1681.2036 | 780 | 200 | 2661.2036 | 66.53% | 95% | 0% | -28.6041 | 731.5772 | -3550 | -400 | -3218.4228 | 80.46% | 67.58% | 95% | 0% | 1839 | -25
[5 empty] | 2019-05-10 | 10 | 3100 | 1823 | -25 | 1 | 0 | 1848 | 774.2786 | 774.2786 | 774.2786 | 1681.2036 | 780 | 200 | 2661.2036 | 66.53% | 95% | 0% | -28.6041 | 745.6745 | -3550 | -400 | -3204.3255 | 80.11% | 67.58% | 95% | 0% | 1848 | -25
[5 empty] | 2019-05-10 | 11 | 3100.5 | 1846 | -26 | 1 | 0 | 1872 | 811.8714 | 811.8714 | 811.8714 | 1681.2036 | 780 | 200 | 2661.2036 | 66.53% | 95% | 0% | -29.7483 | 782.1231 | -3550 | -400 | -3167.8769 | 79.2% | 67.58% | 95% | 0% | 1872 | -26
[5 empty] | 2019-05-10 | 12 | 3101 | 1901 | -30 | 1 | 0 | 1931 | 904.2869 | 904.2869 | 904.2869 | 1681.2036 | 780 | 200 | 2661.2036 | 66.53% | 95% | 0% | -34.3249 | 869.9619 | -3550 | -400 | -3080.0381 | 77% | 67.58% | 95% | 0% | 1931 | -30
[5 empty] | 2019-05-10 | 13 | 3101.5 | 2086 | -48 | 1 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 1681.2036 | 780 | 200 | 2661.2036 | 66.53% | 95% | 0% | -54.9199 | 1167.339 | -3550 | -400 | -2782.661 | 69.57% | 67.57% | 95% | 0% | 2134 | -48
[5 empty] | 2019-05-10 | 14 | 3102 | 2250 | -74 | 1 | 0 | 2324 | 1519.8681 | 1519.8681 | 1519.8681 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -84.6682 | 1435.1999 | -3550 | -400 | -2514.8001 | 62.87% | 67.57% | 95% | 0% | 2324 | -74
[5 empty] | 2019-05-10 | 15 | 3102.5 | 2432 | -109 | 1 | 0 | 2541 | 1859.7692 | 1859.7692 | 1859.7692 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -124.714 | 1735.0552 | -3550 | -400 | -2214.9448 | 55.37% | 67.57% | 95% | 0% | 2541 | -109
[5 empty] | 2019-05-10 | 16 | 3103 | 2459 | -146 | 1 | 0 | 2605 | 1960.0165 | 1960.0165 | 1960.0165 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -167.0481 | 1792.9684 | -3550 | -400 | -2157.0316 | 53.93% | 67.57% | 95% | 0% | 2605 | -146
[5 empty] | 2019-05-10 | 17 | 3103.5 | 2450 | -188 | 1 | 0 | 2638 | 2011.7065 | 2011.7065 | 2011.7065 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -215.103 | 1796.6035 | -3550 | -400 | -2153.3965 | 53.83% | 67.57% | 95% | 0% | 2638 | -188
[5 empty] | 2019-05-10 | 18 | 3104 | 2369 | -240 | 1 | 0 | 2609 | 1966.2819 | 1966.2819 | 1966.2819 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -274.5995 | 1691.6824 | -3550 | -400 | -2258.3176 | 56.46% | 67.56% | 95% | 0% | 2609 | -240
[5 empty] | 2019-05-10 | 19 | 3104.5 | 2301 | -289 | 1 | 0 | 2590 | 1936.521 | 1936.521 | 1936.521 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -330.6636 | 1605.8574 | -3550 | -400 | -2344.1426 | 58.6% | 67.56% | 95% | 0% | 2590 | -289
[5 empty] | 2019-05-10 | 20 | 3105 | 2231 | -346 | 1 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -395.881 | 1520.2773 | -3550 | -400 | -2429.7227 | 60.74% | 67.55% | 95% | 0% | 2577 | -346
[5 empty] | 2019-05-10 | 21 | 3105.5 | 2171 | -382 | 1 | 0 | 2553 | 1878.5655 | 1878.5655 | 1878.5655 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -437.0709 | 1441.4946 | -3550 | -400 | -2508.5054 | 62.71% | 67.54% | 95% | 0% | 2553 | -382
[5 empty] | 2019-05-10 | 22 | 3106 | 2096 | -430 | 1 | 0 | 2526 | 1836.2737 | 1836.2737 | 1836.2737 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -491.9908 | 1344.2829 | -3550 | -400 | -2605.7171 | 65.14% | 67.54% | 95% | 0% | 2526 | -430
[5 empty] | 2019-05-10 | 23 | 3106.5 | 2039 | -448 | 1 | 0 | 2487 | 1775.1855 | 1775.1855 | 1775.1855 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -512.5858 | 1262.5997 | -3550 | -400 | -2687.4003 | 67.19% | 67.54% | 95% | 0% | 2487 | -448
[5 empty] | 2019-05-10 | 24 | 3107 | 1998 | -485 | 1 | 0 | 2483 | 1768.92 | 1768.92 | 1768.92 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -554.9199 | 1214.0001 | -3550 | -400 | -2735.9999 | 68.4% | 67.53% | 95% | 0% | 2483 | -485
[5 empty] | 2019-05-10 | 25 | 3107.5 | 1965 | -531 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -607.5515 | 1181.7313 | -3550 | -400 | -2768.2687 | 69.21% | 67.53% | 95% | 0% | 2496 | -531
[5 empty] | 2019-05-10 | 26 | 3108 | 1944 | -520 | 1 | 0 | 2464 | 1739.1591 | 1739.1591 | 1739.1591 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -594.9657 | 1144.1934 | -3550 | -400 | -2805.8066 | 70.15% | 67.52% | 95% | 0% | 2464 | -520
[5 empty] | 2019-05-10 | 27 | 3108.5 | 1945 | -487 | 1 | 0 | 2432 | 1689.0354 | 1689.0354 | 1689.0354 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -557.2082 | 1131.8272 | -3550 | -400 | -2818.1728 | 70.45% | 67.52% | 95% | 0% | 2432 | -487
[5 empty] | 2019-05-10 | 28 | 3109 | 1850 | -540 | 1 | 0 | 2390 | 1623.2481 | 1623.2481 | 1623.2481 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -617.849 | 1005.3992 | -3550 | -400 | -2944.6008 | 73.62% | 67.52% | 95% | 0% | 2390 | -540
[5 empty] | 2019-05-10 | 29 | 3109.5 | 1871 | -503 | 1 | 0 | 2374 | 1598.1863 | 1598.1863 | 1598.1863 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -575.5149 | 1022.6714 | -3550 | -400 | -2927.3286 | 73.18% | 67.52% | 95% | 0% | 2374 | -503
[5 empty] | 2019-05-10 | 30 | 3110 | 1860 | -493 | 1 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -564.0732 | 1001.2194 | -3550 | -400 | -2948.7806 | 73.72% | 67.52% | 95% | 0% | 2353 | -493
[5 empty] | 2019-05-10 | 31 | 3110.5 | 1840 | -498 | 1 | 0 | 2338 | 1541.7972 | 1541.7972 | 1541.7972 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -569.7941 | 972.0031 | -3550 | -400 | -2977.9969 | 74.45% | 67.51% | 95% | 0% | 2338 | -498
[5 empty] | 2019-05-10 | 32 | 3111 | 1943 | -430 | 1 | 0 | 2373 | 1596.62 | 1596.62 | 1596.62 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -491.9908 | 1104.6291 | -3550 | -400 | -2845.3709 | 71.13% | 67.51% | 95% | 0% | 2373 | -430
[5 empty] | 2019-05-10 | 33 | 3111.5 | 2038 | -390 | 1 | 0 | 2428 | 1682.77 | 1682.77 | 1682.77 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -446.2243 | 1236.5457 | -3550 | -400 | -2713.4543 | 67.84% | 67.51% | 95% | 0% | 2428 | -390
[5 empty] | 2019-05-10 | 34 | 3112 | 2173 | -319 | 1 | 0 | 2492 | 1783.0173 | 1783.0173 | 1783.0173 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -364.9886 | 1418.0288 | -3550 | -400 | -2531.9712 | 63.3% | 67.5% | 95% | 0% | 2492 | -319
[5 empty] | 2019-05-10 | 35 | 3112.5 | 2298 | -268 | 1 | 0 | 2566 | 1898.9283 | 1898.9283 | 1898.9283 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -306.6362 | 1592.2921 | -3550 | -400 | -2357.7079 | 58.94% | 67.5% | 95% | 0% | 2566 | -268
[5 empty] | 2019-05-10 | 36 | 3113 | 2389 | -206 | 1 | 0 | 2595 | 1944.3528 | 1944.3528 | 1944.3528 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -235.6979 | 1708.6549 | -3550 | -400 | -2241.3451 | 56.03% | 67.5% | 95% | 0% | 2595 | -206
[5 empty] | 2019-05-10 | 37 | 3113.5 | 2434 | -155 | 1 | 0 | 2589 | 1934.9547 | 1934.9547 | 1934.9547 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -177.3455 | 1757.6091 | -3550 | -400 | -2192.3909 | 54.81% | 67.5% | 95% | 0% | 2589 | -155
[5 empty] | 2019-05-10 | 38 | 3114 | 2494 | -112 | 1 | 0 | 2606 | 1961.5829 | 1961.5829 | 1961.5829 | 1679.6373 | 780 | 200 | 2659.6373 | 66.49% | 95% | 0% | -128.1465 | 1833.4364 | -3550 | -400 | -2116.5636 | 52.91% | 67.49% | 95% | 0% | 2606 | -112
[5 empty] | 2019-05-10 | 39 | 3114.5 | 2494 | -83 | 1 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -94.9657 | 1821.1926 | -3550 | -400 | -2128.8074 | 53.22% | 67.49% | 95% | 0% | 2577 | -83
[5 empty] | 2019-05-10 | 40 | 3115 | 2523 | -55 | 1 | 0 | 2578 | 1917.7246 | 1917.7246 | 1917.7246 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -62.9291 | 1854.7956 | -3550 | -400 | -2095.2044 | 52.38% | 67.49% | 95% | 0% | 2578 | -55
[5 empty] | 2019-05-10 | 41 | 3115.5 | 2553 | -37 | 1 | 0 | 2590 | 1936.521 | 1936.521 | 1936.521 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -42.3341 | 1894.1869 | -3550 | -400 | -2055.8131 | 51.4% | 67.48% | 95% | 0% | 2590 | -37
[5 empty] | 2019-05-10 | 42 | 3116 | 2545 | -29 | 1 | 0 | 2574 | 1911.4592 | 1911.4592 | 1911.4592 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -33.1808 | 1878.2784 | -3550 | -400 | -2071.7216 | 51.79% | 67.48% | 95% | 0% | 2574 | -29
[5 empty] | 2019-05-10 | 43 | 3116.5 | 2526 | -28 | 1 | 0 | 2554 | 1880.1319 | 1880.1319 | 1880.1319 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -32.0366 | 1848.0953 | -3550 | -400 | -2101.9047 | 52.55% | 67.47% | 95% | 0% | 2554 | -28
[5 empty] | 2019-05-10 | 44 | 3117 | 2458 | -27 | 1 | 0 | 2485 | 1772.0528 | 1772.0528 | 1772.0528 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -30.8924 | 1741.1603 | -3550 | -400 | -2208.8397 | 55.22% | 67.47% | 95% | 0% | 2485 | -27
[5 empty] | 2019-05-10 | 45 | 3117.5 | 2350 | -27 | 0 | 0 | 2377 | 1602.8854 | 1602.8854 | 1602.8854 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -30.8924 | 1571.993 | -2750 | -200 | -1378.007 | 34.45% | 67.47% | 95% | 0% | 2377 | -27
[5 empty] | 2019-05-10 | 46 | 3118 | 2222 | -26 | 0 | 0 | 2248 | 1400.8244 | 1400.8244 | 1400.8244 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -29.7483 | 1371.0761 | -2750 | -200 | -1578.9239 | 39.47% | 67.47% | 95% | 0% | 2248 | -26
[5 empty] | 2019-05-10 | 47 | 3118.5 | 2086 | -25 | 0 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -28.6041 | 1157.6284 | -2750 | -200 | -1792.3716 | 44.81% | 67.47% | 95% | 0% | 2111 | -25
[5 empty] | 2019-05-10 | 48 | 3119 | 1980 | -25 | 0 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -28.6041 | 991.5937 | -2750 | -200 | -1958.4063 | 48.96% | 67.46% | 95% | 0% | 2005 | -25
[5 empty] | 2019-05-11 | 1 | 3119.5 | 1890 | -23 | 0 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -26.3158 | 849.7765 | -2750 | -200 | -2100.2235 | 52.51% | 67.46% | 95% | 0% | 1913 | -23
[5 empty] | 2019-05-11 | 2 | 3120 | 1830 | -22 | 0 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -25.1716 | 755.3725 | -2750 | -200 | -2194.6275 | 54.87% | 67.45% | 95% | 0% | 1852 | -22
[5 empty] | 2019-05-11 | 3 | 3120.5 | 1811 | -23 | 0 | 0 | 1834 | 752.3495 | 752.3495 | 752.3495 | 1678.0709 | 780 | 200 | 2658.0709 | 66.45% | 95% | 0% | -26.3158 | 726.0338 | -2750 | -200 | -2223.9662 | 55.6% | 67.44% | 95% | 0% | 1834 | -23
[5 empty] | 2019-05-11 | 4 | 3121 | 1820 | -23 | 1 | 0 | 1843 | 766.4468 | 766.4468 | 766.4468 | 1676.5045 | 780 | 200 | 2656.5045 | 66.41% | 95% | 0% | -26.3158 | 740.131 | -3550 | -400 | -3209.869 | 80.25% | 67.44% | 95% | 0% | 1843 | -23
[5 empty] | 2019-05-11 | 5 | 3121.5 | 1802 | -25 | 1 | 0 | 1827 | 741.385 | 741.385 | 741.385 | 1676.5045 | 780 | 200 | 2656.5045 | 66.41% | 95% | 0% | -28.6041 | 712.7809 | -3550 | -400 | -3237.2191 | 80.93% | 67.43% | 95% | 0% | 1827 | -25
[5 empty] | 2019-05-11 | 6 | 3122 | 1769 | -26 | 1 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 1676.5045 | 780 | 200 | 2656.5045 | 66.41% | 95% | 0% | -29.7483 | 661.5131 | -3550 | -400 | -3288.4869 | 82.21% | 67.43% | 95% | 0% | 1795 | -26
[5 empty] | 2019-05-11 | 7 | 3122.5 | 1741 | -27 | 1 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 1676.5045 | 780 | 200 | 2656.5045 | 66.41% | 95% | 0% | -30.8924 | 618.077 | -3550 | -400 | -3331.923 | 83.3% | 67.42% | 95% | 0% | 1768 | -27
[5 empty] | 2019-05-11 | 8 | 3123 | 1717 | -28 | 1 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 1676.5045 | 780 | 200 | 2656.5045 | 66.41% | 95% | 0% | -32.0366 | 580.9065 | -3550 | -400 | -3369.0935 | 84.23% | 67.4% | 95% | 0% | 1745 | -28
[5 empty] | 2019-05-11 | 9 | 3123.5 | 1702 | -29 | 1 | 0 | 1731 | 591.014 | 591.014 | 591.014 | 1674.9382 | 780 | 200 | 2654.9382 | 66.37% | 95% | 0% | -33.1808 | 557.8332 | -3550 | -400 | -3392.1668 | 84.8% | 67.4% | 95% | 0% | 1731 | -29
[5 empty] | 2019-05-11 | 10 | 3124 | 1690 | -30 | 1 | 0 | 1720 | 573.784 | 573.784 | 573.784 | 1674.9382 | 780 | 200 | 2654.9382 | 66.37% | 95% | 0% | -34.3249 | 539.4591 | -3550 | -400 | -3410.5409 | 85.26% | 67.4% | 95% | 0% | 1720 | -30
[5 empty] | 2019-05-11 | 11 | 3124.5 | 1669 | -33 | 1 | 0 | 1702 | 545.5894 | 545.5894 | 545.5894 | 1674.9382 | 780 | 200 | 2654.9382 | 66.37% | 95% | 0% | -37.7574 | 507.832 | -3550 | -400 | -3442.168 | 86.05% | 67.39% | 95% | 0% | 1702 | -33
[5 empty] | 2019-05-11 | 12 | 3125 | 1673 | -39 | 1 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 1674.9382 | 780 | 200 | 2654.9382 | 66.37% | 95% | 0% | -44.6224 | 516.6307 | -3550 | -400 | -3433.3693 | 85.83% | 67.39% | 95% | 0% | 1712 | -39
[5 empty] | 2019-05-11 | 13 | 3125.5 | 1728 | -63 | 1 | 0 | 1791 | 684.9959 | 684.9959 | 684.9959 | 1674.9382 | 780 | 200 | 2654.9382 | 66.37% | 95% | 0% | -72.0824 | 612.9135 | -3550 | -400 | -3337.0865 | 83.43% | 67.39% | 95% | 0% | 1791 | -63
[5 empty] | 2019-05-11 | 14 | 3126 | 1768 | -96 | 1 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 1674.9382 | 780 | 200 | 2654.9382 | 66.37% | 95% | 0% | -109.8398 | 689.5007 | -3550 | -400 | -3260.4993 | 81.51% | 67.39% | 95% | 0% | 1864 | -96
[5 empty] | 2019-05-11 | 15 | 3126.5 | 1835 | -137 | 1 | 0 | 1972 | 968.5078 | 968.5078 | 968.5078 | 1674.9382 | 780 | 200 | 2654.9382 | 66.37% | 95% | 0% | -156.7506 | 811.7573 | -3550 | -400 | -3138.2427 | 78.46% | 67.39% | 95% | 0% | 1972 | -137
[5 empty] | 2019-05-11 | 16 | 3127 | 1846 | -190 | 1 | 0 | 2036 | 1068.7552 | 1068.7552 | 1068.7552 | 1674.9382 | 780 | 200 | 2654.9382 | 66.37% | 95% | 0% | -217.3913 | 851.3638 | -3550 | -400 | -3098.6362 | 77.47% | 67.38% | 95% | 0% | 2036 | -190
[5 empty] | 2019-05-11 | 17 | 3127.5 | 1876 | -239 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 1674.9382 | 780 | 200 | 2654.9382 | 66.37% | 95% | 0% | -273.4554 | 919.0426 | -3550 | -400 | -3030.9574 | 75.77% | 67.38% | 95% | 0% | 2115 | -239
[5 empty] | 2019-05-11 | 18 | 3128 | 1850 | -301 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1674.9382 | 780 | 200 | 2654.9382 | 66.37% | 95% | 0% | -344.3936 | 904.4935 | -3550 | -400 | -3045.5065 | 76.14% | 67.38% | 95% | 0% | 2151 | -301
[5 empty] | 2019-05-11 | 19 | 3128.5 | 1793 | -368 | 1 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 1673.3718 | 780 | 200 | 2653.3718 | 66.33% | 95% | 0% | -421.0526 | 843.4981 | -3550 | -400 | -3106.5019 | 77.66% | 67.38% | 95% | 0% | 2161 | -368
[5 empty] | 2019-05-11 | 20 | 3129 | 1743 | -395 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1673.3718 | 780 | 200 | 2653.3718 | 66.33% | 95% | 0% | -451.9451 | 776.5792 | -3550 | -400 | -3173.4208 | 79.34% | 67.37% | 95% | 0% | 2138 | -395
[5 empty] | 2019-05-11 | 21 | 3129.5 | 1693 | -440 | 1 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 1673.3718 | 780 | 200 | 2653.3718 | 66.33% | 95% | 0% | -503.4325 | 717.26 | -3550 | -400 | -3232.74 | 80.82% | 67.37% | 95% | 0% | 2133 | -440
[5 empty] | 2019-05-11 | 22 | 3130 | 1638 | -469 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1673.3718 | 780 | 200 | 2653.3718 | 66.33% | 95% | 0% | -536.6133 | 643.3538 | -3550 | -400 | -3306.6462 | 82.67% | 67.36% | 95% | 0% | 2107 | -469
[5 empty] | 2019-05-11 | 23 | 3130.5 | 1577 | -504 | 1 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 1673.3718 | 780 | 200 | 2653.3718 | 66.33% | 95% | 0% | -576.659 | 562.5825 | -3550 | -400 | -3387.4175 | 84.69% | 67.36% | 95% | 0% | 2081 | -504
[5 empty] | 2019-05-11 | 24 | 3131 | 1502 | -566 | 1 | 0 | 2068 | 1118.8788 | 1118.8788 | 1118.8788 | 1673.3718 | 780 | 200 | 2653.3718 | 66.33% | 95% | 0% | -647.5973 | 471.2816 | -3550 | -400 | -3478.7184 | 86.97% | 67.36% | 95% | 0% | 2068 | -566
[5 empty] | 2019-05-11 | 25 | 3131.5 | 1470 | -574 | 1 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 1673.3718 | 780 | 200 | 2653.3718 | 66.33% | 95% | 0% | -656.7506 | 424.5355 | -3550 | -400 | -3525.4645 | 88.14% | 67.36% | 95% | 0% | 2044 | -574
[5 empty] | 2019-05-11 | 26 | 3132 | 1445 | -576 | 1 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 1673.3718 | 780 | 200 | 2653.3718 | 66.33% | 95% | 0% | -659.0389 | 386.2208 | -3550 | -400 | -3563.7792 | 89.09% | 67.36% | 95% | 0% | 2021 | -576
[5 empty] | 2019-05-11 | 27 | 3132.5 | 1398 | -580 | 1 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 1673.3718 | 780 | 200 | 2653.3718 | 66.33% | 95% | 0% | -663.6156 | 314.2905 | -3550 | -400 | -3635.7095 | 90.89% | 67.35% | 95% | 0% | 1978 | -580
[5 empty] | 2019-05-11 | 28 | 3133 | 1307 | -617 | 1 | 0 | 1924 | 893.3223 | 893.3223 | 893.3223 | 1673.3718 | 780 | 200 | 2653.3718 | 66.33% | 95% | 0% | -705.9497 | 187.3727 | -3550 | -400 | -3762.6273 | 94.07% | 67.35% | 95% | 0% | 1924 | -617
[5 empty] | 2019-05-11 | 29 | 3133.5 | 1262 | -623 | 1 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 1671.8054 | 780 | 200 | 2651.8054 | 66.3% | 95% | 0% | -712.8146 | 119.4195 | -3550 | -400 | -3830.5805 | 95.76% | 67.35% | 95% | 0% | 1885 | -623
[5 empty] | 2019-05-11 | 30 | 3134 | 1269 | -583 | 1 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 1671.8054 | 780 | 200 | 2651.8054 | 66.3% | 95% | 0% | -667.0481 | 113.4961 | -3550 | -400 | -3836.5039 | 95.91% | 67.35% | 95% | 0% | 1852 | -583
[5 empty] | 2019-05-11 | 31 | 3134.5 | 1291 | -547 | 1 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 1671.8054 | 780 | 200 | 2651.8054 | 66.3% | 95% | 0% | -625.8581 | 132.7569 | -3550 | -400 | -3817.2431 | 95.43% | 67.34% | 95% | 0% | 1838 | -547
[5 empty] | 2019-05-11 | 32 | 3135 | 1286 | -553 | 1 | 0 | 1839 | 760.1814 | 760.1814 | 760.1814 | 1671.8054 | 780 | 200 | 2651.8054 | 66.3% | 95% | 0% | -632.7231 | 127.4583 | -3550 | -400 | -3822.5417 | 95.56% | 67.34% | 95% | 0% | 1839 | -553
[5 empty] | 2019-05-11 | 33 | 3135.5 | 1389 | -510 | 1 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 1671.8054 | 780 | 200 | 2651.8054 | 66.3% | 95% | 0% | -583.524 | 270.6392 | -3550 | -400 | -3679.3608 | 91.98% | 67.34% | 95% | 0% | 1899 | -510
[5 empty] | 2019-05-11 | 34 | 3136 | 1554 | -442 | 1 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 1671.8054 | 780 | 200 | 2651.8054 | 66.3% | 95% | 0% | -505.7208 | 500.3798 | -3550 | -400 | -3449.6202 | 86.24% | 67.33% | 95% | 0% | 1996 | -442
[5 empty] | 2019-05-11 | 35 | 3136.5 | 1739 | -368 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1671.8054 | 780 | 200 | 2651.8054 | 66.3% | 95% | 0% | -421.0526 | 758.9144 | -3550 | -400 | -3191.0856 | 79.78% | 67.33% | 95% | 0% | 2107 | -368
[5 empty] | 2019-05-11 | 36 | 3137 | 1891 | -296 | 1 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 1671.8054 | 780 | 200 | 2651.8054 | 66.3% | 95% | 0% | -338.6728 | 966.6034 | -3550 | -400 | -2983.3966 | 74.58% | 67.33% | 95% | 0% | 2187 | -296
[5 empty] | 2019-05-11 | 37 | 3137.5 | 2012 | -242 | 1 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 1671.8054 | 780 | 200 | 2651.8054 | 66.3% | 95% | 0% | -276.8879 | 1133.3347 | -3550 | -400 | -2816.6653 | 70.42% | 67.32% | 95% | 0% | 2254 | -242
[5 empty] | 2019-05-11 | 38 | 3138 | 2119 | -177 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1671.8054 | 780 | 200 | 2651.8054 | 66.3% | 95% | 0% | -202.5172 | 1273.4927 | -3550 | -400 | -2676.5073 | 66.91% | 67.32% | 95% | 0% | 2296 | -177
[5 empty] | 2019-05-11 | 39 | 3138.5 | 2195 | -135 | 1 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 1671.8054 | 780 | 200 | 2651.8054 | 66.3% | 95% | 0% | -154.4622 | 1374.804 | -3550 | -400 | -2575.196 | 64.38% | 67.32% | 95% | 0% | 2330 | -135
[5 empty] | 2019-05-11 | 40 | 3139 | 2242 | -95 | 1 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 1671.8054 | 780 | 200 | 2651.8054 | 66.3% | 95% | 0% | -108.6957 | 1431.5352 | -3550 | -400 | -2518.4648 | 62.96% | 67.32% | 95% | 0% | 2337 | -95
[5 empty] | 2019-05-11 | 41 | 3139.5 | 2258 | -63 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -72.0824 | 1443.0866 | -3550 | -400 | -2506.9134 | 62.67% | 67.31% | 95% | 0% | 2321 | -63
[5 empty] | 2019-05-11 | 42 | 3140 | 2247 | -51 | 1 | 0 | 2298 | 1479.1426 | 1479.1426 | 1479.1426 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -58.3524 | 1420.7902 | -3550 | -400 | -2529.2098 | 63.23% | 67.31% | 95% | 0% | 2298 | -51
[5 empty] | 2019-05-11 | 43 | 3140.5 | 2239 | -47 | 1 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -53.7757 | 1406.5705 | -3550 | -400 | -2543.4295 | 63.59% | 67.3% | 95% | 0% | 2286 | -47
[5 empty] | 2019-05-11 | 44 | 3141 | 2225 | -45 | 1 | 0 | 2270 | 1435.2844 | 1435.2844 | 1435.2844 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -51.4874 | 1383.797 | -3550 | -400 | -2566.203 | 64.16% | 67.29% | 95% | 0% | 2270 | -45
[5 empty] | 2019-05-11 | 45 | 3141.5 | 2167 | -43 | 0 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -49.1991 | 1292.1035 | -2750 | -200 | -1657.8965 | 41.45% | 67.29% | 95% | 0% | 2210 | -43
[5 empty] | 2019-05-11 | 46 | 3142 | 2080 | -41 | 0 | 0 | 2121 | 1201.8961 | 1201.8961 | 1201.8961 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -46.9108 | 1154.9854 | -2750 | -200 | -1795.0146 | 44.88% | 67.29% | 95% | 0% | 2121 | -41
[5 empty] | 2019-05-11 | 47 | 3142.5 | 1964 | -39 | 0 | 0 | 2003 | 1017.0651 | 1017.0651 | 1017.0651 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -44.6224 | 972.4427 | -2750 | -200 | -1977.5573 | 49.44% | 67.28% | 95% | 0% | 2003 | -39
[5 empty] | 2019-05-11 | 48 | 3143 | 1864 | -37 | 0 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -42.3341 | 814.9619 | -2750 | -200 | -2135.0381 | 53.38% | 67.28% | 95% | 0% | 1901 | -37
[5 empty] | 2019-05-12 | 1 | 3143.5 | 1793 | -34 | 0 | 0 | 1827 | 741.385 | 741.385 | 741.385 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -38.9016 | 702.4834 | -2750 | -200 | -2247.5166 | 56.19% | 67.27% | 95% | 0% | 1827 | -34
[5 empty] | 2019-05-12 | 2 | 3144 | 1742 | -31 | 0 | 0 | 1773 | 656.8013 | 656.8013 | 656.8013 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -35.4691 | 621.3322 | -2750 | -200 | -2328.6678 | 58.22% | 67.27% | 95% | 0% | 1773 | -31
[5 empty] | 2019-05-12 | 3 | 3144.5 | 1733 | -28 | 0 | 0 | 1761 | 638.0049 | 638.0049 | 638.0049 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -32.0366 | 605.9683 | -2750 | -200 | -2344.0317 | 58.6% | 67.26% | 95% | 0% | 1761 | -28
[5 empty] | 2019-05-12 | 4 | 3145 | 1745 | -26 | 0 | 0 | 1771 | 653.6686 | 653.6686 | 653.6686 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -29.7483 | 623.9203 | -2750 | -200 | -2326.0797 | 58.15% | 67.26% | 95% | 0% | 1771 | -26
[5 empty] | 2019-05-12 | 5 | 3145.5 | 1735 | -24 | 1 | 0 | 1759 | 634.8722 | 634.8722 | 634.8722 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -27.46 | 607.4123 | -3550 | -400 | -3342.5877 | 83.56% | 67.26% | 95% | 0% | 1759 | -24
[5 empty] | 2019-05-12 | 6 | 3146 | 1705 | -22 | 1 | 0 | 1727 | 584.7486 | 584.7486 | 584.7486 | 1670.2391 | 780 | 200 | 2650.2391 | 66.26% | 95% | 0% | -25.1716 | 559.5769 | -3550 | -400 | -3390.4231 | 84.76% | 67.26% | 95% | 0% | 1727 | -22
[5 empty] | 2019-05-12 | 7 | 3146.5 | 1683 | -22 | 1 | 0 | 1705 | 550.2885 | 550.2885 | 550.2885 | 1668.6727 | 780 | 200 | 2648.6727 | 66.22% | 95% | 0% | -25.1716 | 525.1169 | -3550 | -400 | -3424.8831 | 85.62% | 67.25% | 95% | 0% | 1705 | -22
[5 empty] | 2019-05-12 | 8 | 3147 | 1667 | -21 | 1 | 0 | 1688 | 523.6603 | 523.6603 | 523.6603 | 1668.6727 | 780 | 200 | 2648.6727 | 66.22% | 95% | 0% | -24.0275 | 499.6329 | -3550 | -400 | -3450.3671 | 86.26% | 67.25% | 95% | 0% | 1688 | -21
[5 empty] | 2019-05-12 | 9 | 3147.5 | 1647 | -21 | 1 | 0 | 1668 | 492.3331 | 492.3331 | 492.3331 | 1668.6727 | 780 | 200 | 2648.6727 | 66.22% | 95% | 0% | -24.0275 | 468.3056 | -3550 | -400 | -3481.6944 | 87.04% | 67.25% | 95% | 0% | 1668 | -21
[5 empty] | 2019-05-12 | 10 | 3148 | 1635 | -21 | 1 | 0 | 1656 | 473.5367 | 473.5367 | 473.5367 | 1668.6727 | 780 | 200 | 2648.6727 | 66.22% | 95% | 0% | -24.0275 | 449.5092 | -3550 | -400 | -3500.4908 | 87.51% | 67.24% | 95% | 0% | 1656 | -21
[5 empty] | 2019-05-12 | 11 | 3148.5 | 1605 | -20 | 1 | 0 | 1625 | 424.9794 | 424.9794 | 424.9794 | 1668.6727 | 780 | 200 | 2648.6727 | 66.22% | 95% | 0% | -22.8833 | 402.0961 | -3550 | -400 | -3547.9039 | 88.7% | 67.24% | 95% | 0% | 1625 | -20
[5 empty] | 2019-05-12 | 12 | 3149 | 1594 | -31 | 1 | 0 | 1625 | 424.9794 | 424.9794 | 424.9794 | 1668.6727 | 780 | 200 | 2648.6727 | 66.22% | 95% | 0% | -35.4691 | 389.5103 | -3550 | -400 | -3560.4897 | 89.01% | 67.24% | 95% | 0% | 1625 | -31
[5 empty] | 2019-05-12 | 13 | 3149.5 | 1603 | -65 | 1 | 0 | 1668 | 492.3331 | 492.3331 | 492.3331 | 1668.6727 | 780 | 200 | 2648.6727 | 66.22% | 95% | 0% | -74.3707 | 417.9623 | -3550 | -400 | -3532.0377 | 88.3% | 67.24% | 95% | 0% | 1668 | -65
[5 empty] | 2019-05-12 | 14 | 3150 | 1590 | -111 | 1 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 1668.6727 | 780 | 200 | 2648.6727 | 66.22% | 95% | 0% | -127.0023 | 417.0208 | -3550 | -400 | -3532.9792 | 88.32% | 67.24% | 95% | 0% | 1701 | -111
[5 empty] | 2019-05-12 | 15 | 3150.5 | 1574 | -166 | 1 | 0 | 1740 | 605.1113 | 605.1113 | 605.1113 | 1668.6727 | 780 | 200 | 2648.6727 | 66.22% | 95% | 0% | -189.9314 | 415.1799 | -3550 | -400 | -3534.8201 | 88.37% | 67.24% | 95% | 0% | 1740 | -166
[5 empty] | 2019-05-12 | 16 | 3151 | 1517 | -235 | 1 | 0 | 1752 | 623.9077 | 623.9077 | 623.9077 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -268.8787 | 355.0289 | -3550 | -400 | -3594.9711 | 89.87% | 67.23% | 95% | 0% | 1752 | -235
[5 empty] | 2019-05-12 | 17 | 3151.5 | 1486 | -305 | 1 | 0 | 1791 | 684.9959 | 684.9959 | 684.9959 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -348.9703 | 336.0256 | -3550 | -400 | -3613.9744 | 90.35% | 67.23% | 95% | 0% | 1791 | -305
[5 empty] | 2019-05-12 | 18 | 3152 | 1434 | -378 | 1 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -432.4943 | 285.3953 | -3550 | -400 | -3664.6047 | 91.62% | 67.23% | 95% | 0% | 1812 | -378
[5 empty] | 2019-05-12 | 19 | 3152.5 | 1378 | -456 | 1 | 0 | 1834 | 752.3495 | 752.3495 | 752.3495 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -521.7391 | 230.6104 | -3550 | -400 | -3719.3896 | 92.98% | 67.23% | 95% | 0% | 1834 | -456
[5 empty] | 2019-05-12 | 20 | 3153 | 1312 | -529 | 1 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -605.2632 | 158.0509 | -3550 | -400 | -3791.9491 | 94.8% | 67.23% | 95% | 0% | 1841 | -529
[5 empty] | 2019-05-12 | 21 | 3153.5 | 1246 | -587 | 1 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -671.6247 | 79.1585 | -3550 | -400 | -3870.8415 | 96.77% | 67.22% | 95% | 0% | 1833 | -587
[5 empty] | 2019-05-12 | 22 | 3154 | 1183 | -637 | 1 | 0 | 1820 | 730.4204 | 730.4204 | 730.4204 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -728.833 | 1.5875 | -3550 | -400 | -3948.4125 | 98.71% | 67.22% | 95% | 0% | 1820 | -637
[5 empty] | 2019-05-12 | 23 | 3154.5 | 1143 | -668 | 1 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -764.3021 | -47.9789 | -3550 | -400 | -3997.9789 | 99.95% | 67.22% | 95% | 0% | 1811 | -668
[5 empty] | 2019-05-12 | 24 | 3155 | 1121 | -695 | 1 | 0 | 1816 | 724.155 | 724.155 | 724.155 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -795.1945 | -71.0395 | -3550 | -400 | -4021.0395 | 100.5% | 67.22% | 95% | 0% | 1816 | -695
[5 empty] | 2019-05-12 | 25 | 3155.5 | 1127 | -690 | 1 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -789.4737 | -63.7523 | -3550 | -400 | -4013.7523 | 100.3% | 67.21% | 95% | 0% | 1817 | -690
[5 empty] | 2019-05-12 | 26 | 3156 | 1148 | -667 | 1 | 0 | 1815 | 722.5886 | 722.5886 | 722.5886 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -763.1579 | -40.5693 | -3550 | -400 | -3990.5693 | 99.76% | 67.2% | 95% | 0% | 1815 | -667
[5 empty] | 2019-05-12 | 27 | 3156.5 | 1140 | -647 | 1 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -740.2746 | -61.5442 | -3550 | -400 | -4011.5442 | 100.3% | 67.2% | 95% | 0% | 1787 | -647
[5 empty] | 2019-05-12 | 28 | 3157 | 1100 | -652 | 1 | 0 | 1752 | 623.9077 | 623.9077 | 623.9077 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -745.9954 | -122.0878 | -3550 | -400 | -4072.0878 | 101.8% | 67.2% | 95% | 0% | 1752 | -652
[5 empty] | 2019-05-12 | 29 | 3157.5 | 1127 | -612 | 1 | 0 | 1739 | 603.5449 | 603.5449 | 603.5449 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -700.2288 | -96.6839 | -3550 | -400 | -4046.6839 | 101.2% | 67.2% | 95% | 0% | 1739 | -612
[5 empty] | 2019-05-12 | 30 | 3158 | 1107 | -614 | 1 | 0 | 1721 | 575.3504 | 575.3504 | 575.3504 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -702.5172 | -127.1668 | -3550 | -400 | -4077.1668 | 101.9% | 67.19% | 95% | 0% | 1721 | -614
[5 empty] | 2019-05-12 | 31 | 3158.5 | 1128 | -590 | 1 | 0 | 1718 | 570.6513 | 570.6513 | 570.6513 | 1667.1063 | 780 | 200 | 2647.1063 | 66.18% | 95% | 0% | -675.0572 | -104.4059 | -3550 | -400 | -4054.4059 | 101.4% | 67.19% | 95% | 0% | 1718 | -590
[5 empty] | 2019-05-12 | 32 | 3159 | 1184 | -561 | 1 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 1665.54 | 780 | 200 | 2645.54 | 66.14% | 95% | 0% | -641.8764 | -28.9333 | -3550 | -400 | -3978.9333 | 99.47% | 67.19% | 95% | 0% | 1745 | -561
[5 empty] | 2019-05-12 | 33 | 3159.5 | 1322 | -502 | 1 | 0 | 1824 | 736.6859 | 736.6859 | 736.6859 | 1665.54 | 780 | 200 | 2645.54 | 66.14% | 95% | 0% | -574.3707 | 162.3152 | -3550 | -400 | -3787.6848 | 94.69% | 67.18% | 95% | 0% | 1824 | -502
[5 empty] | 2019-05-12 | 34 | 3160 | 1485 | -435 | 1 | 0 | 1920 | 887.0569 | 887.0569 | 887.0569 | 1665.54 | 780 | 200 | 2645.54 | 66.14% | 95% | 0% | -497.7117 | 389.3452 | -3550 | -400 | -3560.6548 | 89.02% | 67.18% | 95% | 0% | 1920 | -435
[5 empty] | 2019-05-12 | 35 | 3160.5 | 1662 | -376 | 1 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 1665.54 | 780 | 200 | 2645.54 | 66.14% | 95% | 0% | -430.2059 | 641.6819 | -3550 | -400 | -3308.3181 | 82.71% | 67.18% | 95% | 0% | 2038 | -376
[5 empty] | 2019-05-12 | 36 | 3161 | 1802 | -318 | 1 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1665.54 | 780 | 200 | 2645.54 | 66.14% | 95% | 0% | -363.8444 | 836.4854 | -3550 | -400 | -3113.5146 | 77.84% | 67.18% | 95% | 0% | 2120 | -318
[5 empty] | 2019-05-12 | 37 | 3161.5 | 1940 | -249 | 1 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 1665.54 | 780 | 200 | 2645.54 | 66.14% | 95% | 0% | -284.897 | 1023.5119 | -3550 | -400 | -2926.4881 | 73.16% | 67.18% | 95% | 0% | 2189 | -249
[5 empty] | 2019-05-12 | 38 | 3162 | 2064 | -189 | 1 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 1665.54 | 780 | 200 | 2645.54 | 66.14% | 95% | 0% | -216.2471 | 1192.4091 | -3550 | -400 | -2757.5909 | 68.94% | 67.18% | 95% | 0% | 2253 | -189
[5 empty] | 2019-05-12 | 39 | 3162.5 | 2139 | -139 | 1 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 1665.54 | 780 | 200 | 2645.54 | 66.14% | 95% | 0% | -159.0389 | 1288.7764 | -3550 | -400 | -2661.2236 | 66.53% | 67.17% | 95% | 0% | 2278 | -139
[5 empty] | 2019-05-12 | 40 | 3163 | 2183 | -97 | 1 | 0 | 2280 | 1450.9481 | 1450.9481 | 1450.9481 | 1665.54 | 780 | 200 | 2645.54 | 66.14% | 95% | 0% | -110.984 | 1339.9641 | -3550 | -400 | -2610.0359 | 65.25% | 67.17% | 95% | 0% | 2280 | -97
[5 empty] | 2019-05-12 | 41 | 3163.5 | 2226 | -61 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1665.54 | 780 | 200 | 2645.54 | 66.14% | 95% | 0% | -69.7941 | 1392.1186 | -3550 | -400 | -2557.8814 | 63.95% | 67.17% | 95% | 0% | 2287 | -61
[5 empty] | 2019-05-12 | 42 | 3164 | 2232 | -48 | 1 | 0 | 2280 | 1450.9481 | 1450.9481 | 1450.9481 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -54.9199 | 1396.0282 | -3550 | -400 | -2553.9718 | 63.85% | 67.16% | 95% | 0% | 2280 | -48
[5 empty] | 2019-05-12 | 43 | 3164.5 | 2237 | -48 | 1 | 0 | 2285 | 1458.7799 | 1458.7799 | 1458.7799 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -54.9199 | 1403.86 | -3550 | -400 | -2546.14 | 63.65% | 67.16% | 95% | 0% | 2285 | -48
[5 empty] | 2019-05-12 | 44 | 3165 | 2214 | -48 | 1 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -54.9199 | 1367.8336 | -3550 | -400 | -2582.1664 | 64.55% | 67.16% | 95% | 0% | 2262 | -48
[5 empty] | 2019-05-12 | 45 | 3165.5 | 2130 | -47 | 0 | 0 | 2177 | 1289.6125 | 1289.6125 | 1289.6125 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -53.7757 | 1235.8368 | -2750 | -200 | -1714.1632 | 42.85% | 67.16% | 95% | 0% | 2177 | -47
[5 empty] | 2019-05-12 | 46 | 3166 | 2004 | -47 | 0 | 0 | 2051 | 1092.2506 | 1092.2506 | 1092.2506 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -53.7757 | 1038.4749 | -2750 | -200 | -1911.5251 | 47.79% | 67.16% | 95% | 0% | 2051 | -47
[5 empty] | 2019-05-12 | 47 | 3166.5 | 1866 | -46 | 0 | 0 | 1912 | 874.526 | 874.526 | 874.526 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -52.6316 | 821.8944 | -2750 | -200 | -2128.1056 | 53.2% | 67.16% | 95% | 0% | 1912 | -46
[5 empty] | 2019-05-12 | 48 | 3167 | 1762 | -46 | 0 | 0 | 1808 | 711.6241 | 711.6241 | 711.6241 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -52.6316 | 658.9925 | -2750 | -200 | -2291.0075 | 57.28% | 67.16% | 95% | 0% | 1808 | -46
[5 empty] | 2019-05-13 | 1 | 3167.5 | 1680 | -47 | 0 | 0 | 1727 | 584.7486 | 584.7486 | 584.7486 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -53.7757 | 530.9728 | -2750 | -200 | -2419.0272 | 60.48% | 67.16% | 95% | 0% | 1727 | -47
[5 empty] | 2019-05-13 | 2 | 3168 | 1640 | -48 | 0 | 0 | 1688 | 523.6603 | 523.6603 | 523.6603 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -54.9199 | 468.7404 | -2750 | -200 | -2481.2596 | 62.03% | 67.15% | 95% | 0% | 1688 | -48
[5 empty] | 2019-05-13 | 3 | 3168.5 | 1632 | -47 | 0 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -53.7757 | 455.7873 | -2750 | -200 | -2494.2127 | 62.36% | 67.15% | 95% | 0% | 1679 | -47
[5 empty] | 2019-05-13 | 4 | 3169 | 1656 | -45 | 0 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -51.4874 | 492.5357 | -2750 | -200 | -2457.4643 | 61.44% | 67.14% | 95% | 0% | 1701 | -45
[5 empty] | 2019-05-13 | 5 | 3169.5 | 1652 | -45 | 0 | 0 | 1697 | 537.7576 | 537.7576 | 537.7576 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -51.4874 | 486.2702 | -2750 | -200 | -2463.7298 | 61.59% | 67.14% | 95% | 0% | 1697 | -45
[5 empty] | 2019-05-13 | 6 | 3170 | 1634 | -44 | 0 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -50.3432 | 457.6535 | -2750 | -200 | -2492.3465 | 62.31% | 67.14% | 95% | 0% | 1678 | -44
[5 empty] | 2019-05-13 | 7 | 3170.5 | 1613 | -44 | 0 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -50.3432 | 424.7598 | -2750 | -200 | -2525.2402 | 63.13% | 67.13% | 95% | 0% | 1657 | -44
[5 empty] | 2019-05-13 | 8 | 3171 | 1607 | -44 | 0 | 0 | 1651 | 465.7049 | 465.7049 | 465.7049 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -50.3432 | 415.3616 | -2750 | -200 | -2534.6384 | 63.37% | 67.13% | 95% | 0% | 1651 | -44
[5 empty] | 2019-05-13 | 9 | 3171.5 | 1609 | -46 | 0 | 0 | 1655 | 471.9703 | 471.9703 | 471.9703 | 1663.9736 | 780 | 200 | 2643.9736 | 66.1% | 95% | 0% | -52.6316 | 419.3387 | -2750 | -200 | -2530.6613 | 63.27% | 67.13% | 95% | 0% | 1655 | -46
[5 empty] | 2019-05-13 | 10 | 3172 | 1613 | -47 | 0 | 0 | 1660 | 479.8021 | 479.8021 | 479.8021 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -53.7757 | 426.0264 | -2750 | -200 | -2523.9736 | 63.1% | 67.12% | 95% | 0% | 1660 | -47
[5 empty] | 2019-05-13 | 11 | 3172.5 | 1640 | -48 | 0 | 0 | 1688 | 523.6603 | 523.6603 | 523.6603 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -54.9199 | 468.7404 | -2750 | -200 | -2481.2596 | 62.03% | 67.12% | 95% | 0% | 1688 | -48
[5 empty] | 2019-05-13 | 12 | 3173 | 1704 | -60 | 0 | 0 | 1764 | 642.704 | 642.704 | 642.704 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -68.6499 | 574.0542 | -2750 | -200 | -2375.9458 | 59.4% | 67.11% | 95% | 0% | 1764 | -60
[5 empty] | 2019-05-13 | 13 | 3173.5 | 1887 | -94 | 0 | 0 | 1981 | 982.6051 | 982.6051 | 982.6051 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -107.5515 | 875.0536 | -2750 | -200 | -2074.9464 | 51.87% | 67.11% | 95% | 0% | 1981 | -94
[5 empty] | 2019-05-13 | 14 | 3174 | 2040 | -142 | 0 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -162.4714 | 1134.973 | -2750 | -200 | -1815.027 | 45.38% | 67.11% | 95% | 0% | 2182 | -142
[5 empty] | 2019-05-13 | 15 | 3174.5 | 2153 | -199 | 1 | 0 | 2352 | 1563.7263 | 1563.7263 | 1563.7263 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -227.6888 | 1336.0375 | -3550 | -400 | -2613.9625 | 65.35% | 67.1% | 95% | 0% | 2352 | -199
[5 empty] | 2019-05-13 | 16 | 3175 | 2106 | -259 | 1 | 0 | 2365 | 1584.089 | 1584.089 | 1584.089 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -296.3387 | 1287.7504 | -3550 | -400 | -2662.2496 | 66.56% | 67.1% | 95% | 0% | 2365 | -259
[5 empty] | 2019-05-13 | 17 | 3175.5 | 2036 | -334 | 1 | 0 | 2370 | 1591.9209 | 1591.9209 | 1591.9209 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -382.151 | 1209.7698 | -3550 | -400 | -2740.2302 | 68.51% | 67.1% | 95% | 0% | 2370 | -334
[5 empty] | 2019-05-13 | 18 | 3176 | 1931 | -408 | 1 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -466.8192 | 1076.5443 | -3550 | -400 | -2873.4557 | 71.84% | 67.1% | 95% | 0% | 2339 | -408
[5 empty] | 2019-05-13 | 19 | 3176.5 | 1844 | -483 | 1 | 0 | 2327 | 1524.5672 | 1524.5672 | 1524.5672 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -552.6316 | 971.9356 | -3550 | -400 | -2978.0644 | 74.45% | 67.1% | 95% | 0% | 2327 | -483
[5 empty] | 2019-05-13 | 20 | 3177 | 1711 | -553 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -632.7231 | 793.1631 | -3550 | -400 | -3156.8369 | 78.92% | 67.1% | 95% | 0% | 2264 | -553
[5 empty] | 2019-05-13 | 21 | 3177.5 | 1570 | -619 | 1 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -708.238 | 600.1709 | -3550 | -400 | -3349.8291 | 83.75% | 67.1% | 95% | 0% | 2189 | -619
[5 empty] | 2019-05-13 | 22 | 3178 | 1464 | -674 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -771.167 | 457.3573 | -3550 | -400 | -3492.6427 | 87.32% | 67.09% | 95% | 0% | 2138 | -674
[5 empty] | 2019-05-13 | 23 | 3178.5 | 1382 | -721 | 1 | 0 | 2103 | 1173.7016 | 1173.7016 | 1173.7016 | 1662.4073 | 780 | 200 | 2642.4073 | 66.06% | 95% | 0% | -824.9428 | 348.7588 | -3550 | -400 | -3601.2412 | 90.03% | 67.09% | 95% | 0% | 2103 | -721
[5 empty] | 2019-05-13 | 24 | 3179 | 1323 | -759 | 1 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 1660.8409 | 780 | 200 | 2640.8409 | 66.02% | 95% | 0% | -868.4211 | 272.3869 | -3550 | -400 | -3677.6131 | 91.94% | 67.09% | 95% | 0% | 2082 | -759
[5 empty] | 2019-05-13 | 25 | 3179.5 | 1289 | -782 | 1 | 0 | 2071 | 1123.5779 | 1123.5779 | 1123.5779 | 1660.8409 | 780 | 200 | 2640.8409 | 66.02% | 95% | 0% | -894.7368 | 228.8411 | -3550 | -400 | -3721.1589 | 93.03% | 67.09% | 95% | 0% | 2071 | -782
[5 empty] | 2019-05-13 | 26 | 3180 | 1249 | -795 | 1 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 1660.8409 | 780 | 200 | 2640.8409 | 66.02% | 95% | 0% | -909.611 | 171.6751 | -3550 | -400 | -3778.3249 | 94.46% | 67.08% | 95% | 0% | 2044 | -795
[5 empty] | 2019-05-13 | 27 | 3180.5 | 1226 | -794 | 1 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 1660.8409 | 780 | 200 | 2640.8409 | 66.02% | 95% | 0% | -908.4668 | 135.2265 | -3550 | -400 | -3814.7735 | 95.37% | 67.08% | 95% | 0% | 2020 | -794
[5 empty] | 2019-05-13 | 28 | 3181 | 1213 | -786 | 1 | 0 | 1999 | 1010.7997 | 1010.7997 | 1010.7997 | 1660.8409 | 780 | 200 | 2640.8409 | 66.02% | 95% | 0% | -899.3135 | 111.4862 | -3550 | -400 | -3838.5138 | 95.96% | 67.08% | 95% | 0% | 1999 | -786
[5 empty] | 2019-05-13 | 29 | 3181.5 | 1229 | -764 | 1 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 1660.8409 | 780 | 200 | 2640.8409 | 66.02% | 95% | 0% | -874.1419 | 127.2596 | -3550 | -400 | -3822.7404 | 95.57% | 67.08% | 95% | 0% | 1993 | -764
[5 empty] | 2019-05-13 | 30 | 3182 | 1252 | -732 | 1 | 0 | 1984 | 987.3042 | 987.3042 | 987.3042 | 1660.8409 | 780 | 200 | 2640.8409 | 66.02% | 95% | 0% | -837.5286 | 149.7756 | -3550 | -400 | -3800.2244 | 95.01% | 67.08% | 95% | 0% | 1984 | -732
[5 empty] | 2019-05-13 | 31 | 3182.5 | 1294 | -689 | 1 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 1660.8409 | 780 | 200 | 2640.8409 | 66.02% | 95% | 0% | -788.3295 | 197.4083 | -3550 | -400 | -3752.5917 | 93.81% | 67.08% | 95% | 0% | 1983 | -689
[5 empty] | 2019-05-13 | 32 | 3183 | 1416 | -629 | 1 | 0 | 2045 | 1082.8524 | 1082.8524 | 1082.8524 | 1660.8409 | 780 | 200 | 2640.8409 | 66.02% | 95% | 0% | -719.6796 | 363.1728 | -3550 | -400 | -3586.8272 | 89.67% | 67.07% | 95% | 0% | 2045 | -629
[5 empty] | 2019-05-13 | 33 | 3183.5 | 1567 | -560 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 1660.8409 | 780 | 200 | 2640.8409 | 66.02% | 95% | 0% | -640.7323 | 570.562 | -3550 | -400 | -3379.438 | 84.49% | 67.07% | 95% | 0% | 2127 | -560
[5 empty] | 2019-05-13 | 34 | 3184 | 1727 | -499 | 1 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 1660.8409 | 780 | 200 | 2640.8409 | 66.02% | 95% | 0% | -570.9382 | 795.4262 | -3550 | -400 | -3154.5738 | 78.86% | 67.06% | 95% | 0% | 2226 | -499
[5 empty] | 2019-05-13 | 35 | 3184.5 | 1877 | -434 | 1 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 1660.8409 | 780 | 200 | 2640.8409 | 66.02% | 95% | 0% | -496.5675 | 1002.9379 | -3550 | -400 | -2947.0621 | 73.68% | 67.06% | 95% | 0% | 2311 | -434
[5 empty] | 2019-05-13 | 36 | 3185 | 2030 | -356 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 1659.2745 | 780 | 200 | 2639.2745 | 65.98% | 95% | 0% | -407.3227 | 1209.66 | -3550 | -400 | -2740.34 | 68.51% | 67.06% | 95% | 0% | 2386 | -356
[5 empty] | 2019-05-13 | 37 | 3185.5 | 2150 | -276 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1659.2745 | 780 | 200 | 2639.2745 | 65.98% | 95% | 0% | -315.7895 | 1363.8478 | -3550 | -400 | -2586.1522 | 64.65% | 67.05% | 95% | 0% | 2426 | -276
[5 empty] | 2019-05-13 | 38 | 3186 | 2237 | -212 | 1 | 0 | 2449 | 1715.6636 | 1715.6636 | 1715.6636 | 1659.2745 | 780 | 200 | 2639.2745 | 65.98% | 95% | 0% | -242.5629 | 1473.1007 | -3550 | -400 | -2476.8993 | 61.92% | 67.04% | 95% | 0% | 2449 | -212
[5 empty] | 2019-05-13 | 39 | 3186.5 | 2298 | -159 | 1 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 1659.2745 | 780 | 200 | 2639.2745 | 65.98% | 95% | 0% | -181.9222 | 1546.2724 | -3550 | -400 | -2403.7276 | 60.09% | 67.04% | 95% | 0% | 2457 | -159
[5 empty] | 2019-05-13 | 40 | 3187 | 2335 | -110 | 1 | 0 | 2445 | 1709.3982 | 1709.3982 | 1709.3982 | 1659.2745 | 780 | 200 | 2639.2745 | 65.98% | 95% | 0% | -125.8581 | 1583.5401 | -3550 | -400 | -2366.4599 | 59.16% | 67.04% | 95% | 0% | 2445 | -110
[5 empty] | 2019-05-13 | 41 | 3187.5 | 2356 | -79 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1659.2745 | 780 | 200 | 2639.2745 | 65.98% | 95% | 0% | -90.389 | 1603.3455 | -3550 | -400 | -2346.6545 | 58.67% | 67.03% | 95% | 0% | 2435 | -79
[5 empty] | 2019-05-13 | 42 | 3188 | 2348 | -65 | 1 | 0 | 2413 | 1659.2745 | 1659.2745 | 1659.2745 | 1659.2745 | 780 | 200 | 2639.2745 | 65.98% | 95% | 0% | -74.3707 | 1584.9038 | -3550 | -400 | -2365.0962 | 59.13% | 67.03% | 95% | 0% | 2413 | -65
[5 empty] | 2019-05-13 | 43 | 3188.5 | 2358 | -64 | 1 | 0 | 2422 | 1673.3718 | 1673.3718 | 1673.3718 | 1659.2745 | 780 | 200 | 2639.2745 | 65.98% | 95% | 0% | -73.2265 | 1600.1453 | -3550 | -400 | -2349.8547 | 58.75% | 67.03% | 95% | 0% | 2422 | -64
[5 empty] | 2019-05-13 | 44 | 3189 | 2339 | -65 | 0 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 1659.2745 | 780 | 200 | 2639.2745 | 65.98% | 95% | 0% | -74.3707 | 1570.8065 | -2750 | -200 | -1379.1935 | 34.48% | 67.03% | 95% | 0% | 2404 | -65
[5 empty] | 2019-05-13 | 45 | 3189.5 | 2232 | -65 | 0 | 0 | 2297 | 1477.5763 | 1477.5763 | 1477.5763 | 1659.2745 | 780 | 200 | 2639.2745 | 65.98% | 95% | 0% | -74.3707 | 1403.2055 | -2750 | -200 | -1546.7945 | 38.67% | 67.03% | 95% | 0% | 2297 | -65
[5 empty] | 2019-05-13 | 46 | 3190 | 2074 | -65 | 0 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 1657.7082 | 780 | 200 | 2637.7082 | 65.94% | 95% | 0% | -74.3707 | 1155.72 | -2750 | -200 | -1794.28 | 44.86% | 67.02% | 95% | 0% | 2139 | -65
[5 empty] | 2019-05-13 | 47 | 3190.5 | 1927 | -64 | 0 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1657.7082 | 780 | 200 | 2637.7082 | 65.94% | 95% | 0% | -73.2265 | 925.0422 | -2750 | -200 | -2024.9578 | 50.62% | 67.02% | 95% | 0% | 1991 | -64
[5 empty] | 2019-05-13 | 48 | 3191 | 1808 | -64 | 0 | 0 | 1872 | 811.8714 | 811.8714 | 811.8714 | 1657.7082 | 780 | 200 | 2637.7082 | 65.94% | 95% | 0% | -73.2265 | 738.6448 | -2750 | -200 | -2211.3552 | 55.28% | 67.02% | 95% | 0% | 1872 | -64
[5 empty] | 2019-05-14 | 1 | 3191.5 | 1724 | -62 | 0 | 0 | 1786 | 677.1641 | 677.1641 | 677.1641 | 1657.7082 | 780 | 200 | 2637.7082 | 65.94% | 95% | 0% | -70.9382 | 606.2258 | -2750 | -200 | -2343.7742 | 58.59% | 67.02% | 95% | 0% | 1786 | -62
[5 empty] | 2019-05-14 | 2 | 3192 | 1668 | -60 | 0 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 1657.7082 | 780 | 200 | 2637.7082 | 65.94% | 95% | 0% | -68.6499 | 517.665 | -2750 | -200 | -2432.335 | 60.81% | 67.01% | 95% | 0% | 1728 | -60
[5 empty] | 2019-05-14 | 3 | 3192.5 | 1660 | -59 | 0 | 0 | 1719 | 572.2176 | 572.2176 | 572.2176 | 1657.7082 | 780 | 200 | 2637.7082 | 65.94% | 95% | 0% | -67.5057 | 504.7119 | -2750 | -200 | -2445.2881 | 61.13% | 67.01% | 95% | 0% | 1719 | -59
[5 empty] | 2019-05-14 | 4 | 3193 | 1668 | -59 | 1 | 0 | 1727 | 584.7486 | 584.7486 | 584.7486 | 1657.7082 | 780 | 200 | 2637.7082 | 65.94% | 95% | 0% | -67.5057 | 517.2428 | -3550 | -400 | -3432.7572 | 85.82% | 67.01% | 95% | 0% | 1727 | -59
[5 empty] | 2019-05-14 | 5 | 3193.5 | 1655 | -58 | 1 | 0 | 1713 | 562.8195 | 562.8195 | 562.8195 | 1657.7082 | 780 | 200 | 2637.7082 | 65.94% | 95% | 0% | -66.3616 | 496.4579 | -3550 | -400 | -3453.5421 | 86.34% | 67.01% | 95% | 0% | 1713 | -58
[5 empty] | 2019-05-14 | 6 | 3194 | 1628 | -58 | 1 | 0 | 1686 | 520.5276 | 520.5276 | 520.5276 | 1657.7082 | 780 | 200 | 2637.7082 | 65.94% | 95% | 0% | -66.3616 | 454.1661 | -3550 | -400 | -3495.8339 | 87.4% | 67.01% | 95% | 0% | 1686 | -58
[5 empty] | 2019-05-14 | 7 | 3194.5 | 1610 | -58 | 1 | 0 | 1668 | 492.3331 | 492.3331 | 492.3331 | 1657.7082 | 780 | 200 | 2637.7082 | 65.94% | 95% | 0% | -66.3616 | 425.9715 | -3550 | -400 | -3524.0285 | 88.1% | 67% | 95% | 0% | 1668 | -58
[5 empty] | 2019-05-14 | 8 | 3195 | 1599 | -57 | 1 | 0 | 1656 | 473.5367 | 473.5367 | 473.5367 | 1657.7082 | 780 | 200 | 2637.7082 | 65.94% | 95% | 0% | -65.2174 | 408.3193 | -3550 | -400 | -3541.6807 | 88.54% | 67% | 95% | 0% | 1656 | -57
[5 empty] | 2019-05-14 | 9 | 3195.5 | 1598 | -57 | 1 | 0 | 1655 | 471.9703 | 471.9703 | 471.9703 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -65.2174 | 406.7529 | -3550 | -400 | -3543.2471 | 88.58% | 67% | 95% | 0% | 1655 | -57
[5 empty] | 2019-05-14 | 10 | 3196 | 1600 | -58 | 1 | 0 | 1658 | 476.6694 | 476.6694 | 476.6694 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -66.3616 | 410.3079 | -3550 | -400 | -3539.6921 | 88.49% | 66.99% | 95% | 0% | 1658 | -58
[5 empty] | 2019-05-14 | 11 | 3196.5 | 1624 | -57 | 1 | 0 | 1681 | 512.6958 | 512.6958 | 512.6958 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -65.2174 | 447.4784 | -3550 | -400 | -3502.5216 | 87.56% | 66.99% | 95% | 0% | 1681 | -57
[5 empty] | 2019-05-14 | 12 | 3197 | 1692 | -68 | 1 | 0 | 1760 | 636.4386 | 636.4386 | 636.4386 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -77.8032 | 558.6354 | -3550 | -400 | -3391.3646 | 84.78% | 66.99% | 95% | 0% | 1760 | -68
[5 empty] | 2019-05-14 | 13 | 3197.5 | 1859 | -100 | 1 | 0 | 1959 | 948.1451 | 948.1451 | 948.1451 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -114.4165 | 833.7286 | -3550 | -400 | -3116.2714 | 77.91% | 66.98% | 95% | 0% | 1959 | -100
[5 empty] | 2019-05-14 | 14 | 3198 | 1994 | -147 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -168.1922 | 1065.0312 | -3550 | -400 | -2884.9688 | 72.12% | 66.98% | 95% | 0% | 2141 | -147
[5 empty] | 2019-05-14 | 15 | 3198.5 | 2117 | -205 | 1 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -234.5538 | 1282.1816 | -3550 | -400 | -2667.8184 | 66.7% | 66.98% | 95% | 0% | 2322 | -205
[5 empty] | 2019-05-14 | 16 | 3199 | 2112 | -267 | 1 | 0 | 2379 | 1606.0181 | 1606.0181 | 1606.0181 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -305.492 | 1300.5261 | -3550 | -400 | -2649.4739 | 66.24% | 66.97% | 95% | 0% | 2379 | -267
[5 empty] | 2019-05-14 | 17 | 3199.5 | 2059 | -337 | 1 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -385.5835 | 1247.0628 | -3550 | -400 | -2702.9372 | 67.57% | 66.97% | 95% | 0% | 2396 | -337
[5 empty] | 2019-05-14 | 18 | 3200 | 1909 | -410 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -469.1076 | 1042.9287 | -3550 | -400 | -2907.0713 | 72.68% | 66.97% | 95% | 0% | 2319 | -410
[5 empty] | 2019-05-14 | 19 | 3200.5 | 1783 | -484 | 1 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -553.7757 | 876.8096 | -3550 | -400 | -3073.1904 | 76.83% | 66.97% | 95% | 0% | 2267 | -484
[5 empty] | 2019-05-14 | 20 | 3201 | 1657 | -552 | 1 | 0 | 2209 | 1339.7362 | 1339.7362 | 1339.7362 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -631.5789 | 708.1572 | -3550 | -400 | -3241.8428 | 81.05% | 66.96% | 95% | 0% | 2209 | -552
[5 empty] | 2019-05-14 | 21 | 3201.5 | 1526 | -617 | 1 | 0 | 2143 | 1236.3561 | 1236.3561 | 1236.3561 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -705.9497 | 530.4065 | -3550 | -400 | -3419.5935 | 85.49% | 66.96% | 95% | 0% | 2143 | -617
[5 empty] | 2019-05-14 | 22 | 3202 | 1422 | -676 | 1 | 0 | 2098 | 1165.8697 | 1165.8697 | 1165.8697 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -773.4554 | 392.4144 | -3550 | -400 | -3557.5856 | 88.94% | 66.96% | 95% | 0% | 2098 | -676
[5 empty] | 2019-05-14 | 23 | 3202.5 | 1329 | -725 | 1 | 0 | 2054 | 1096.9497 | 1096.9497 | 1096.9497 | 1656.1418 | 780 | 200 | 2636.1418 | 65.9% | 95% | 0% | -829.5195 | 267.4303 | -3550 | -400 | -3682.5697 | 92.06% | 66.95% | 95% | 0% | 2054 | -725
[5 empty] | 2019-05-14 | 24 | 3203 | 1275 | -761 | 1 | 0 | 2036 | 1068.7552 | 1068.7552 | 1068.7552 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -870.7094 | 198.0458 | -3550 | -400 | -3751.9542 | 93.8% | 66.95% | 95% | 0% | 2036 | -761
[5 empty] | 2019-05-14 | 25 | 3203.5 | 1229 | -789 | 1 | 0 | 2018 | 1040.5606 | 1040.5606 | 1040.5606 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -902.746 | 137.8146 | -3550 | -400 | -3812.1854 | 95.3% | 66.95% | 95% | 0% | 2018 | -789
[5 empty] | 2019-05-14 | 26 | 3204 | 1183 | -806 | 1 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -922.1968 | 72.9392 | -3550 | -400 | -3877.0608 | 96.93% | 66.95% | 95% | 0% | 1989 | -806
[5 empty] | 2019-05-14 | 27 | 3204.5 | 1154 | -808 | 1 | 0 | 1962 | 952.8442 | 952.8442 | 952.8442 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -924.4851 | 28.3591 | -3550 | -400 | -3921.6409 | 98.04% | 66.95% | 95% | 0% | 1962 | -808
[5 empty] | 2019-05-14 | 28 | 3205 | 1148 | -797 | 1 | 0 | 1945 | 926.216 | 926.216 | 926.216 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -911.8993 | 14.3167 | -3550 | -400 | -3935.6833 | 98.39% | 66.94% | 95% | 0% | 1945 | -797
[5 empty] | 2019-05-14 | 29 | 3205.5 | 1168 | -774 | 1 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -885.5835 | 35.9334 | -3550 | -400 | -3914.0666 | 97.85% | 66.94% | 95% | 0% | 1942 | -774
[5 empty] | 2019-05-14 | 30 | 3206 | 1200 | -738 | 1 | 0 | 1938 | 915.2514 | 915.2514 | 915.2514 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -844.3936 | 70.8579 | -3550 | -400 | -3879.1421 | 96.98% | 66.94% | 95% | 0% | 1938 | -738
[5 empty] | 2019-05-14 | 31 | 3206.5 | 1260 | -691 | 1 | 0 | 1951 | 935.6142 | 935.6142 | 935.6142 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -790.6178 | 144.9963 | -3550 | -400 | -3805.0037 | 95.13% | 66.93% | 95% | 0% | 1951 | -691
[5 empty] | 2019-05-14 | 32 | 3207 | 1387 | -634 | 1 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -725.4005 | 319.8592 | -3550 | -400 | -3630.1408 | 90.75% | 66.93% | 95% | 0% | 2021 | -634
[5 empty] | 2019-05-14 | 33 | 3207.5 | 1535 | -570 | 1 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -652.1739 | 524.6604 | -3550 | -400 | -3425.3396 | 85.63% | 66.93% | 95% | 0% | 2105 | -570
[5 empty] | 2019-05-14 | 34 | 3208 | 1709 | -499 | 1 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -570.9382 | 767.2316 | -3550 | -400 | -3182.7684 | 79.57% | 66.93% | 95% | 0% | 2208 | -499
[5 empty] | 2019-05-14 | 35 | 3208.5 | 1873 | -425 | 1 | 0 | 2298 | 1479.1426 | 1479.1426 | 1479.1426 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -486.27 | 992.8726 | -3550 | -400 | -2957.1274 | 73.93% | 66.93% | 95% | 0% | 2298 | -425
[5 empty] | 2019-05-14 | 36 | 3209 | 2021 | -351 | 1 | 0 | 2372 | 1595.0536 | 1595.0536 | 1595.0536 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -401.6018 | 1193.4518 | -3550 | -400 | -2756.5482 | 68.91% | 66.93% | 95% | 0% | 2372 | -351
[5 empty] | 2019-05-14 | 37 | 3209.5 | 2157 | -278 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -318.0778 | 1375.6567 | -3550 | -400 | -2574.3433 | 64.36% | 66.93% | 95% | 0% | 2435 | -278
[5 empty] | 2019-05-14 | 38 | 3210 | 2271 | -211 | 1 | 0 | 2482 | 1767.3537 | 1767.3537 | 1767.3537 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -241.4188 | 1525.9349 | -3550 | -400 | -2424.0651 | 60.6% | 66.93% | 95% | 0% | 2482 | -211
[5 empty] | 2019-05-14 | 39 | 3210.5 | 2343 | -154 | 1 | 0 | 2497 | 1790.8491 | 1790.8491 | 1790.8491 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -176.2014 | 1614.6478 | -3550 | -400 | -2335.3522 | 58.38% | 66.93% | 95% | 0% | 2497 | -154
[5 empty] | 2019-05-14 | 40 | 3211 | 2391 | -106 | 1 | 0 | 2497 | 1790.8491 | 1790.8491 | 1790.8491 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -121.2815 | 1669.5677 | -3550 | -400 | -2280.4323 | 57.01% | 66.93% | 95% | 0% | 2497 | -106
[5 empty] | 2019-05-14 | 41 | 3211.5 | 2383 | -74 | 1 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 1654.5754 | 780 | 200 | 2634.5754 | 65.86% | 95% | 0% | -84.6682 | 1643.5264 | -3550 | -400 | -2306.4736 | 57.66% | 66.92% | 95% | 0% | 2457 | -74
[5 empty] | 2019-05-14 | 42 | 3212 | 2380 | -63 | 1 | 0 | 2443 | 1706.2655 | 1706.2655 | 1706.2655 | 1653.0091 | 780 | 200 | 2633.0091 | 65.83% | 95% | 0% | -72.0824 | 1634.1831 | -3550 | -400 | -2315.8169 | 57.9% | 66.92% | 95% | 0% | 2443 | -63
[5 empty] | 2019-05-14 | 43 | 3212.5 | 2399 | -63 | 1 | 0 | 2462 | 1736.0264 | 1736.0264 | 1736.0264 | 1653.0091 | 780 | 200 | 2633.0091 | 65.83% | 95% | 0% | -72.0824 | 1663.944 | -3550 | -400 | -2286.056 | 57.15% | 66.91% | 95% | 0% | 2462 | -63
[5 empty] | 2019-05-14 | 44 | 3213 | 2342 | -64 | 1 | 0 | 2406 | 1648.31 | 1648.31 | 1648.31 | 1653.0091 | 780 | 200 | 2633.0091 | 65.83% | 95% | 0% | -73.2265 | 1575.0834 | -3550 | -400 | -2374.9166 | 59.37% | 66.9% | 95% | 0% | 2406 | -64
[5 empty] | 2019-05-14 | 45 | 3213.5 | 2220 | -63 | 0 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 1653.0091 | 780 | 200 | 2633.0091 | 65.83% | 95% | 0% | -72.0824 | 1383.5648 | -2750 | -200 | -1566.4352 | 39.16% | 66.89% | 95% | 0% | 2283 | -63
[5 empty] | 2019-05-14 | 46 | 3214 | 2057 | -62 | 0 | 0 | 2119 | 1198.7634 | 1198.7634 | 1198.7634 | 1653.0091 | 780 | 200 | 2633.0091 | 65.83% | 95% | 0% | -70.9382 | 1127.8252 | -2750 | -200 | -1822.1748 | 45.55% | 66.88% | 95% | 0% | 2119 | -62
[5 empty] | 2019-05-14 | 47 | 3214.5 | 1919 | -61 | 0 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -69.7941 | 911.2447 | -2750 | -200 | -2038.7553 | 50.97% | 66.88% | 95% | 0% | 1980 | -61
[5 empty] | 2019-05-14 | 48 | 3215 | 1814 | -61 | 0 | 0 | 1875 | 816.5705 | 816.5705 | 816.5705 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -69.7941 | 746.7764 | -2750 | -200 | -2203.2236 | 55.08% | 66.87% | 95% | 0% | 1875 | -61
[5 empty] | 2019-05-15 | 1 | 3215.5 | 1728 | -59 | 0 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -67.5057 | 611.2247 | -2750 | -200 | -2338.7753 | 58.47% | 66.87% | 95% | 0% | 1787 | -59
[5 empty] | 2019-05-15 | 2 | 3216 | 1684 | -58 | 0 | 0 | 1742 | 608.244 | 608.244 | 608.244 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -66.3616 | 541.8825 | -2750 | -200 | -2408.1175 | 60.2% | 66.85% | 95% | 0% | 1742 | -58
[5 empty] | 2019-05-15 | 3 | 3216.5 | 1665 | -57 | 0 | 0 | 1722 | 576.9167 | 576.9167 | 576.9167 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -65.2174 | 511.6993 | -2750 | -200 | -2438.3007 | 60.96% | 66.85% | 95% | 0% | 1722 | -57
[5 empty] | 2019-05-15 | 4 | 3217 | 1675 | -55 | 0 | 0 | 1730 | 589.4477 | 589.4477 | 589.4477 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -62.9291 | 526.5186 | -2750 | -200 | -2423.4814 | 60.59% | 66.84% | 95% | 0% | 1730 | -55
[5 empty] | 2019-05-15 | 5 | 3217.5 | 1660 | -55 | 0 | 0 | 1715 | 565.9522 | 565.9522 | 565.9522 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -62.9291 | 503.0231 | -2750 | -200 | -2446.9769 | 61.17% | 66.84% | 95% | 0% | 1715 | -55
[5 empty] | 2019-05-15 | 6 | 3218 | 1636 | -54 | 0 | 0 | 1690 | 526.7931 | 526.7931 | 526.7931 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -61.7849 | 465.0082 | -2750 | -200 | -2484.9918 | 62.12% | 66.84% | 95% | 0% | 1690 | -54
[5 empty] | 2019-05-15 | 7 | 3218.5 | 1618 | -54 | 0 | 0 | 1672 | 498.5985 | 498.5985 | 498.5985 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -61.7849 | 436.8136 | -2750 | -200 | -2513.1864 | 62.83% | 66.84% | 95% | 0% | 1672 | -54
[5 empty] | 2019-05-15 | 8 | 3219 | 1604 | -54 | 0 | 0 | 1658 | 476.6694 | 476.6694 | 476.6694 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -61.7849 | 414.8845 | -2750 | -200 | -2535.1155 | 63.38% | 66.83% | 95% | 0% | 1658 | -54
[5 empty] | 2019-05-15 | 9 | 3219.5 | 1605 | -54 | 0 | 0 | 1659 | 478.2358 | 478.2358 | 478.2358 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -61.7849 | 416.4509 | -2750 | -200 | -2533.5491 | 63.34% | 66.83% | 95% | 0% | 1659 | -54
[5 empty] | 2019-05-15 | 10 | 3220 | 1602 | -55 | 0 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -62.9291 | 412.174 | -2750 | -200 | -2537.826 | 63.45% | 66.83% | 95% | 0% | 1657 | -55
[5 empty] | 2019-05-15 | 11 | 3220.5 | 1630 | -55 | 0 | 0 | 1685 | 518.9613 | 518.9613 | 518.9613 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -62.9291 | 456.0322 | -2750 | -200 | -2493.9678 | 62.35% | 66.83% | 95% | 0% | 1685 | -55
[5 empty] | 2019-05-15 | 12 | 3221 | 1697 | -69 | 0 | 0 | 1766 | 645.8368 | 645.8368 | 645.8368 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -78.9474 | 566.8894 | -2750 | -200 | -2383.1106 | 59.58% | 66.83% | 95% | 0% | 1766 | -69
[5 empty] | 2019-05-15 | 13 | 3221.5 | 1861 | -104 | 0 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 1651.4427 | 780 | 200 | 2631.4427 | 65.79% | 95% | 0% | -118.9931 | 838.5501 | -2750 | -200 | -2111.4499 | 52.79% | 66.82% | 95% | 0% | 1965 | -104
[5 empty] | 2019-05-15 | 14 | 3222 | 1989 | -151 | 1 | 0 | 2140 | 1231.657 | 1231.657 | 1231.657 | 1649.8763 | 780 | 200 | 2629.8763 | 65.75% | 95% | 0% | -172.7689 | 1058.8882 | -3550 | -400 | -2891.1118 | 72.28% | 66.82% | 95% | 0% | 2140 | -151
[5 empty] | 2019-05-15 | 15 | 3222.5 | 2130 | -206 | 1 | 0 | 2336 | 1538.6645 | 1538.6645 | 1538.6645 | 1649.8763 | 780 | 200 | 2629.8763 | 65.75% | 95% | 0% | -235.6979 | 1302.9665 | -3550 | -400 | -2647.0335 | 66.18% | 66.82% | 95% | 0% | 2336 | -206
[5 empty] | 2019-05-15 | 16 | 3223 | 2132 | -267 | 1 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 1649.8763 | 780 | 200 | 2629.8763 | 65.75% | 95% | 0% | -305.492 | 1331.8534 | -3550 | -400 | -2618.1466 | 65.45% | 66.8% | 95% | 0% | 2399 | -267
[5 empty] | 2019-05-15 | 17 | 3223.5 | 2064 | -332 | 1 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 1649.8763 | 780 | 200 | 2629.8763 | 65.75% | 95% | 0% | -379.8627 | 1252.7836 | -3550 | -400 | -2697.2164 | 67.43% | 66.8% | 95% | 0% | 2396 | -332
[5 empty] | 2019-05-15 | 18 | 3224 | 1925 | -404 | 1 | 0 | 2329 | 1527.6999 | 1527.6999 | 1527.6999 | 1649.8763 | 780 | 200 | 2629.8763 | 65.75% | 95% | 0% | -462.2426 | 1065.4574 | -3550 | -400 | -2884.5426 | 72.11% | 66.8% | 95% | 0% | 2329 | -404
[5 empty] | 2019-05-15 | 19 | 3224.5 | 1825 | -475 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 1649.8763 | 780 | 200 | 2629.8763 | 65.75% | 95% | 0% | -543.4783 | 938.7971 | -3550 | -400 | -3011.2029 | 75.28% | 66.8% | 95% | 0% | 2300 | -475
[5 empty] | 2019-05-15 | 20 | 3225 | 1694 | -545 | 1 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 1649.8763 | 780 | 200 | 2629.8763 | 65.75% | 95% | 0% | -623.5698 | 763.1573 | -3550 | -400 | -3186.8427 | 79.67% | 66.8% | 95% | 0% | 2239 | -545
[5 empty] | 2019-05-15 | 21 | 3225.5 | 1566 | -613 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 1649.8763 | 780 | 200 | 2629.8763 | 65.75% | 95% | 0% | -701.373 | 591.3723 | -3550 | -400 | -3358.6277 | 83.97% | 66.79% | 95% | 0% | 2179 | -613
[5 empty] | 2019-05-15 | 22 | 3226 | 1468 | -668 | 1 | 0 | 2136 | 1225.3916 | 1225.3916 | 1225.3916 | 1648.31 | 780 | 200 | 2628.31 | 65.71% | 95% | 0% | -764.3021 | 461.0895 | -3550 | -400 | -3488.9105 | 87.22% | 66.79% | 95% | 0% | 2136 | -668
[5 empty] | 2019-05-15 | 23 | 3226.5 | 1400 | -711 | 1 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 1648.31 | 780 | 200 | 2628.31 | 65.71% | 95% | 0% | -813.5011 | 372.7313 | -3550 | -400 | -3577.2687 | 89.43% | 66.79% | 95% | 0% | 2111 | -711
[5 empty] | 2019-05-15 | 24 | 3227 | 1350 | -738 | 1 | 0 | 2088 | 1150.2061 | 1150.2061 | 1150.2061 | 1648.31 | 780 | 200 | 2628.31 | 65.71% | 95% | 0% | -844.3936 | 305.8125 | -3550 | -400 | -3644.1875 | 91.1% | 66.78% | 95% | 0% | 2088 | -738
[5 empty] | 2019-05-15 | 25 | 3227.5 | 1309 | -762 | 1 | 0 | 2071 | 1123.5779 | 1123.5779 | 1123.5779 | 1648.31 | 780 | 200 | 2628.31 | 65.71% | 95% | 0% | -871.8535 | 251.7244 | -3550 | -400 | -3698.2756 | 92.46% | 66.78% | 95% | 0% | 2071 | -762
[5 empty] | 2019-05-15 | 26 | 3228 | 1273 | -772 | 1 | 0 | 2045 | 1082.8524 | 1082.8524 | 1082.8524 | 1648.31 | 780 | 200 | 2628.31 | 65.71% | 95% | 0% | -883.2952 | 199.5572 | -3550 | -400 | -3750.4428 | 93.76% | 66.78% | 95% | 0% | 2045 | -772
[5 empty] | 2019-05-15 | 27 | 3228.5 | 1248 | -771 | 1 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 1648.31 | 780 | 200 | 2628.31 | 65.71% | 95% | 0% | -882.151 | 159.9759 | -3550 | -400 | -3790.0241 | 94.75% | 66.77% | 95% | 0% | 2019 | -771
[5 empty] | 2019-05-15 | 28 | 3229 | 1251 | -751 | 1 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 1648.31 | 780 | 200 | 2628.31 | 65.71% | 95% | 0% | -859.2677 | 156.231 | -3550 | -400 | -3793.769 | 94.84% | 66.77% | 95% | 0% | 2002 | -751
[5 empty] | 2019-05-15 | 29 | 3229.5 | 1284 | -723 | 1 | 0 | 2007 | 1023.3306 | 1023.3306 | 1023.3306 | 1648.31 | 780 | 200 | 2628.31 | 65.71% | 95% | 0% | -827.2311 | 196.0995 | -3550 | -400 | -3753.9005 | 93.85% | 66.76% | 95% | 0% | 2007 | -723
[5 empty] | 2019-05-15 | 30 | 3230 | 1326 | -686 | 1 | 0 | 2012 | 1031.1624 | 1031.1624 | 1031.1624 | 1648.31 | 780 | 200 | 2628.31 | 65.71% | 95% | 0% | -784.897 | 246.2654 | -3550 | -400 | -3703.7346 | 92.59% | 66.76% | 95% | 0% | 2012 | -686
[5 empty] | 2019-05-15 | 31 | 3230.5 | 1390 | -643 | 1 | 0 | 2033 | 1064.0561 | 1064.0561 | 1064.0561 | 1646.7436 | 780 | 200 | 2626.7436 | 65.67% | 95% | 0% | -735.6979 | 328.3581 | -3550 | -400 | -3621.6419 | 90.54% | 66.76% | 95% | 0% | 2033 | -643
[5 empty] | 2019-05-15 | 32 | 3231 | 1513 | -594 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1646.7436 | 780 | 200 | 2626.7436 | 65.67% | 95% | 0% | -679.6339 | 500.3332 | -3550 | -400 | -3449.6668 | 86.24% | 66.76% | 95% | 0% | 2107 | -594
[5 empty] | 2019-05-15 | 33 | 3231.5 | 1660 | -530 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1646.7436 | 780 | 200 | 2626.7436 | 65.67% | 95% | 0% | -606.4073 | 703.5679 | -3550 | -400 | -3246.4321 | 81.16% | 66.76% | 95% | 0% | 2190 | -530
[5 empty] | 2019-05-15 | 34 | 3232 | 1825 | -456 | 1 | 0 | 2281 | 1452.5144 | 1452.5144 | 1452.5144 | 1646.7436 | 780 | 200 | 2626.7436 | 65.67% | 95% | 0% | -521.7391 | 930.7753 | -3550 | -400 | -3019.2247 | 75.48% | 66.76% | 95% | 0% | 2281 | -456
[5 empty] | 2019-05-15 | 35 | 3232.5 | 1953 | -385 | 1 | 0 | 2338 | 1541.7972 | 1541.7972 | 1541.7972 | 1646.7436 | 780 | 200 | 2626.7436 | 65.67% | 95% | 0% | -440.5034 | 1101.2938 | -3550 | -400 | -2848.7062 | 71.22% | 66.75% | 95% | 0% | 2338 | -385
[5 empty] | 2019-05-15 | 36 | 3233 | 2056 | -317 | 1 | 0 | 2373 | 1596.62 | 1596.62 | 1596.62 | 1646.7436 | 780 | 200 | 2626.7436 | 65.67% | 95% | 0% | -362.7002 | 1233.9197 | -3550 | -400 | -2716.0803 | 67.9% | 66.75% | 95% | 0% | 2373 | -317
[5 empty] | 2019-05-15 | 37 | 3233.5 | 2179 | -256 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1646.7436 | 780 | 200 | 2626.7436 | 65.67% | 95% | 0% | -292.9062 | 1400.8284 | -3550 | -400 | -2549.1716 | 63.73% | 66.75% | 95% | 0% | 2435 | -256
[5 empty] | 2019-05-15 | 38 | 3234 | 2288 | -201 | 1 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 1646.7436 | 780 | 200 | 2626.7436 | 65.67% | 95% | 0% | -229.9771 | 1548.3411 | -3550 | -400 | -2401.6589 | 60.04% | 66.75% | 95% | 0% | 2489 | -201
[5 empty] | 2019-05-15 | 39 | 3234.5 | 2372 | -150 | 1 | 0 | 2522 | 1830.0082 | 1830.0082 | 1830.0082 | 1646.7436 | 780 | 200 | 2626.7436 | 65.67% | 95% | 0% | -171.6247 | 1658.3835 | -3550 | -400 | -2291.6165 | 57.29% | 66.75% | 95% | 0% | 2522 | -150
[5 empty] | 2019-05-15 | 40 | 3235 | 2426 | -104 | 1 | 0 | 2530 | 1842.5392 | 1842.5392 | 1842.5392 | 1646.7436 | 780 | 200 | 2626.7436 | 65.67% | 95% | 0% | -118.9931 | 1723.546 | -3550 | -400 | -2226.454 | 55.66% | 66.75% | 95% | 0% | 2530 | -104
[5 empty] | 2019-05-15 | 41 | 3235.5 | 2432 | -75 | 1 | 0 | 2507 | 1806.5128 | 1806.5128 | 1806.5128 | 1646.7436 | 780 | 200 | 2626.7436 | 65.67% | 95% | 0% | -85.8124 | 1720.7004 | -3550 | -400 | -2229.2996 | 55.73% | 66.75% | 95% | 0% | 2507 | -75
[5 empty] | 2019-05-15 | 42 | 3236 | 2413 | -64 | 1 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 1646.7436 | 780 | 200 | 2626.7436 | 65.67% | 95% | 0% | -73.2265 | 1686.2953 | -3550 | -400 | -2263.7047 | 56.59% | 66.75% | 95% | 0% | 2477 | -64
[5 empty] | 2019-05-15 | 43 | 3236.5 | 2404 | -65 | 1 | 0 | 2469 | 1746.9909 | 1746.9909 | 1746.9909 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -74.3707 | 1672.6202 | -3550 | -400 | -2277.3798 | 56.93% | 66.75% | 95% | 0% | 2469 | -65
[5 empty] | 2019-05-15 | 44 | 3237 | 2339 | -67 | 1 | 0 | 2406 | 1648.31 | 1648.31 | 1648.31 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -76.659 | 1571.6509 | -3550 | -400 | -2378.3491 | 59.46% | 66.75% | 95% | 0% | 2406 | -67
[5 empty] | 2019-05-15 | 45 | 3237.5 | 2213 | -69 | 0 | 0 | 2282 | 1454.0808 | 1454.0808 | 1454.0808 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -78.9474 | 1375.1334 | -2750 | -200 | -1574.8666 | 39.37% | 66.74% | 95% | 0% | 2282 | -69
[5 empty] | 2019-05-15 | 46 | 3238 | 2062 | -72 | 0 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -82.3799 | 1139.879 | -2750 | -200 | -1810.121 | 45.25% | 66.74% | 95% | 0% | 2134 | -72
[5 empty] | 2019-05-15 | 47 | 3238.5 | 1902 | -73 | 0 | 0 | 1975 | 973.2069 | 973.2069 | 973.2069 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -83.524 | 889.6829 | -2750 | -200 | -2060.3171 | 51.51% | 66.74% | 95% | 0% | 1975 | -73
[5 empty] | 2019-05-15 | 48 | 3239 | 1784 | -75 | 0 | 0 | 1859 | 791.5087 | 791.5087 | 791.5087 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -85.8124 | 705.6963 | -2750 | -200 | -2244.3037 | 56.11% | 66.74% | 95% | 0% | 1859 | -75
[5 empty] | 2019-05-16 | 1 | 3239.5 | 1692 | -75 | 0 | 0 | 1767 | 647.4031 | 647.4031 | 647.4031 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -85.8124 | 561.5908 | -2750 | -200 | -2388.4092 | 59.71% | 66.73% | 95% | 0% | 1767 | -75
[5 empty] | 2019-05-16 | 2 | 3240 | 1639 | -76 | 0 | 0 | 1715 | 565.9522 | 565.9522 | 565.9522 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -86.9565 | 478.9957 | -2750 | -200 | -2471.0043 | 61.78% | 66.73% | 95% | 0% | 1715 | -76
[5 empty] | 2019-05-16 | 3 | 3240.5 | 1619 | -75 | 0 | 0 | 1694 | 533.0585 | 533.0585 | 533.0585 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -85.8124 | 447.2462 | -2750 | -200 | -2502.7538 | 62.57% | 66.73% | 95% | 0% | 1694 | -75
[5 empty] | 2019-05-16 | 4 | 3241 | 1618 | -74 | 0 | 0 | 1692 | 529.9258 | 529.9258 | 529.9258 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -84.6682 | 445.2576 | -2750 | -200 | -2504.7424 | 62.62% | 66.73% | 95% | 0% | 1692 | -74
[5 empty] | 2019-05-16 | 5 | 3241.5 | 1609 | -73 | 0 | 0 | 1682 | 514.2622 | 514.2622 | 514.2622 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -83.524 | 430.7381 | -2750 | -200 | -2519.2619 | 62.98% | 66.73% | 95% | 0% | 1682 | -73
[5 empty] | 2019-05-16 | 6 | 3242 | 1579 | -72 | 0 | 0 | 1651 | 465.7049 | 465.7049 | 465.7049 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -82.3799 | 383.325 | -2750 | -200 | -2566.675 | 64.17% | 66.72% | 95% | 0% | 1651 | -72
[5 empty] | 2019-05-16 | 7 | 3242.5 | 1564 | -70 | 0 | 0 | 1634 | 439.0767 | 439.0767 | 439.0767 | 1645.1772 | 780 | 200 | 2625.1772 | 65.63% | 95% | 0% | -80.0915 | 358.9851 | -2750 | -200 | -2591.0149 | 64.78% | 66.72% | 95% | 0% | 1634 | -70
[5 empty] | 2019-05-16 | 8 | 3243 | 1562 | -68 | 0 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 1643.6109 | 780 | 200 | 2623.6109 | 65.59% | 95% | 0% | -77.8032 | 355.008 | -2750 | -200 | -2594.992 | 64.87% | 66.72% | 95% | 0% | 1630 | -68
[5 empty] | 2019-05-16 | 9 | 3243.5 | 1560 | -70 | 0 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 1643.6109 | 780 | 200 | 2623.6109 | 65.59% | 95% | 0% | -80.0915 | 352.7197 | -2750 | -200 | -2597.2803 | 64.93% | 66.72% | 95% | 0% | 1630 | -70
[5 empty] | 2019-05-16 | 10 | 3244 | 1565 | -72 | 0 | 0 | 1637 | 443.7758 | 443.7758 | 443.7758 | 1643.6109 | 780 | 200 | 2623.6109 | 65.59% | 95% | 0% | -82.3799 | 361.3959 | -2750 | -200 | -2588.6041 | 64.72% | 66.71% | 95% | 0% | 1637 | -72
[5 empty] | 2019-05-16 | 11 | 3244.5 | 1585 | -74 | 0 | 0 | 1659 | 478.2358 | 478.2358 | 478.2358 | 1643.6109 | 780 | 200 | 2623.6109 | 65.59% | 95% | 0% | -84.6682 | 393.5676 | -2750 | -200 | -2556.4324 | 63.91% | 66.71% | 95% | 0% | 1659 | -74
[5 empty] | 2019-05-16 | 12 | 3245 | 1640 | -91 | 0 | 0 | 1731 | 591.014 | 591.014 | 591.014 | 1643.6109 | 780 | 200 | 2623.6109 | 65.59% | 95% | 0% | -104.119 | 486.895 | -2750 | -200 | -2463.105 | 61.58% | 66.71% | 95% | 0% | 1731 | -91
[5 empty] | 2019-05-16 | 13 | 3245.5 | 1801 | -127 | 0 | 0 | 1928 | 899.5878 | 899.5878 | 899.5878 | 1643.6109 | 780 | 200 | 2623.6109 | 65.59% | 95% | 0% | -145.3089 | 754.2789 | -2750 | -200 | -2195.7211 | 54.89% | 66.71% | 95% | 0% | 1928 | -127
[5 empty] | 2019-05-16 | 14 | 3246 | 1932 | -172 | 1 | 0 | 2104 | 1175.2679 | 1175.2679 | 1175.2679 | 1643.6109 | 780 | 200 | 2623.6109 | 65.59% | 95% | 0% | -196.7963 | 978.4716 | -3550 | -400 | -2971.5284 | 74.29% | 66.71% | 95% | 0% | 2104 | -172
[5 empty] | 2019-05-16 | 15 | 3246.5 | 2065 | -229 | 1 | 0 | 2294 | 1472.8772 | 1472.8772 | 1472.8772 | 1643.6109 | 780 | 200 | 2623.6109 | 65.59% | 95% | 0% | -262.0137 | 1210.8634 | -3550 | -400 | -2739.1366 | 68.48% | 66.7% | 95% | 0% | 2294 | -229
[5 empty] | 2019-05-16 | 16 | 3247 | 2067 | -295 | 1 | 0 | 2362 | 1579.3899 | 1579.3899 | 1579.3899 | 1643.6109 | 780 | 200 | 2623.6109 | 65.59% | 95% | 0% | -337.5286 | 1241.8613 | -3550 | -400 | -2708.1387 | 67.7% | 66.7% | 95% | 0% | 2362 | -295
[5 empty] | 2019-05-16 | 17 | 3247.5 | 2001 | -366 | 1 | 0 | 2367 | 1587.2218 | 1587.2218 | 1587.2218 | 1643.6109 | 780 | 200 | 2623.6109 | 65.59% | 95% | 0% | -418.7643 | 1168.4575 | -3550 | -400 | -2781.5425 | 69.54% | 66.7% | 95% | 0% | 2367 | -366
[5 empty] | 2019-05-16 | 18 | 3248 | 1865 | -443 | 1 | 0 | 2308 | 1494.8063 | 1494.8063 | 1494.8063 | 1643.6109 | 780 | 200 | 2623.6109 | 65.59% | 95% | 0% | -506.865 | 987.9413 | -3550 | -400 | -2962.0587 | 74.05% | 66.7% | 95% | 0% | 2308 | -443
[5 empty] | 2019-05-16 | 19 | 3248.5 | 1751 | -515 | 1 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 1642.0445 | 780 | 200 | 2622.0445 | 65.55% | 95% | 0% | -589.2449 | 839.7741 | -3550 | -400 | -3110.2259 | 77.76% | 66.7% | 95% | 0% | 2266 | -515
[5 empty] | 2019-05-16 | 20 | 3249 | 1623 | -581 | 1 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 1642.0445 | 780 | 200 | 2622.0445 | 65.55% | 95% | 0% | -664.7597 | 667.1446 | -3550 | -400 | -3282.8554 | 82.07% | 66.69% | 95% | 0% | 2204 | -581
[5 empty] | 2019-05-16 | 21 | 3249.5 | 1488 | -646 | 1 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 1642.0445 | 780 | 200 | 2622.0445 | 65.55% | 95% | 0% | -739.1304 | 483.1284 | -3550 | -400 | -3466.8716 | 86.67% | 66.69% | 95% | 0% | 2134 | -646
[5 empty] | 2019-05-16 | 22 | 3250 | 1386 | -701 | 1 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 1642.0445 | 780 | 200 | 2622.0445 | 65.55% | 95% | 0% | -802.0595 | 346.5802 | -3550 | -400 | -3603.4198 | 90.09% | 66.69% | 95% | 0% | 2087 | -701
[5 empty] | 2019-05-16 | 23 | 3250.5 | 1330 | -732 | 1 | 0 | 2062 | 1109.4806 | 1109.4806 | 1109.4806 | 1642.0445 | 780 | 200 | 2622.0445 | 65.55% | 95% | 0% | -837.5286 | 271.952 | -3550 | -400 | -3678.048 | 91.95% | 66.68% | 95% | 0% | 2062 | -732
[5 empty] | 2019-05-16 | 24 | 3251 | 1303 | -759 | 1 | 0 | 2062 | 1109.4806 | 1109.4806 | 1109.4806 | 1642.0445 | 780 | 200 | 2622.0445 | 65.55% | 95% | 0% | -868.4211 | 241.0596 | -3550 | -400 | -3708.9404 | 92.72% | 66.67% | 95% | 0% | 2062 | -759
[5 empty] | 2019-05-16 | 25 | 3251.5 | 1317 | -758 | 1 | 0 | 2075 | 1129.8434 | 1129.8434 | 1129.8434 | 1642.0445 | 780 | 200 | 2622.0445 | 65.55% | 95% | 0% | -867.2769 | 262.5665 | -3550 | -400 | -3687.4335 | 92.19% | 66.67% | 95% | 0% | 2075 | -758
[5 empty] | 2019-05-16 | 26 | 3252 | 1290 | -765 | 1 | 0 | 2055 | 1098.5161 | 1098.5161 | 1098.5161 | 1642.0445 | 780 | 200 | 2622.0445 | 65.55% | 95% | 0% | -875.286 | 223.23 | -3550 | -400 | -3726.77 | 93.17% | 66.67% | 95% | 0% | 2055 | -765
[5 empty] | 2019-05-16 | 27 | 3252.5 | 1268 | -767 | 1 | 0 | 2035 | 1067.1888 | 1067.1888 | 1067.1888 | 1640.4782 | 780 | 200 | 2620.4782 | 65.51% | 95% | 0% | -877.5744 | 189.6144 | -3550 | -400 | -3760.3856 | 94.01% | 66.67% | 95% | 0% | 2035 | -767
[5 empty] | 2019-05-16 | 28 | 3253 | 1259 | -757 | 1 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 1640.4782 | 780 | 200 | 2620.4782 | 65.51% | 95% | 0% | -866.1327 | 171.2951 | -3550 | -400 | -3778.7049 | 94.47% | 66.66% | 95% | 0% | 2016 | -757
[5 empty] | 2019-05-16 | 29 | 3253.5 | 1272 | -733 | 1 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 1640.4782 | 780 | 200 | 2620.4782 | 65.51% | 95% | 0% | -838.6728 | 181.5251 | -3550 | -400 | -3768.4749 | 94.21% | 66.66% | 95% | 0% | 2005 | -733
[5 empty] | 2019-05-16 | 30 | 3254 | 1322 | -685 | 1 | 0 | 2007 | 1023.3306 | 1023.3306 | 1023.3306 | 1640.4782 | 780 | 200 | 2620.4782 | 65.51% | 95% | 0% | -783.7529 | 239.5777 | -3550 | -400 | -3710.4223 | 92.76% | 66.66% | 95% | 0% | 2007 | -685
[5 empty] | 2019-05-16 | 31 | 3254.5 | 1400 | -610 | 1 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 1640.4782 | 780 | 200 | 2620.4782 | 65.51% | 95% | 0% | -697.9405 | 330.0892 | -3550 | -400 | -3619.9108 | 90.5% | 66.65% | 95% | 0% | 2010 | -610
[5 empty] | 2019-05-16 | 32 | 3255 | 1524 | -548 | 1 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 1640.4782 | 780 | 200 | 2620.4782 | 65.51% | 95% | 0% | -627.0023 | 498.142 | -3550 | -400 | -3451.858 | 86.3% | 66.65% | 95% | 0% | 2072 | -548
[5 empty] | 2019-05-16 | 33 | 3255.5 | 1641 | -504 | 1 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 1640.4782 | 780 | 200 | 2620.4782 | 65.51% | 95% | 0% | -576.659 | 662.8298 | -3550 | -400 | -3287.1702 | 82.18% | 66.65% | 95% | 0% | 2145 | -504
[5 empty] | 2019-05-16 | 34 | 3256 | 1747 | -473 | 1 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 1640.4782 | 780 | 200 | 2620.4782 | 65.51% | 95% | 0% | -541.1899 | 815.7763 | -3550 | -400 | -3134.2237 | 78.36% | 66.64% | 95% | 0% | 2220 | -473
[5 empty] | 2019-05-16 | 35 | 3256.5 | 1870 | -420 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 1640.4782 | 780 | 200 | 2620.4782 | 65.51% | 95% | 0% | -480.5492 | 986.0625 | -3550 | -400 | -2963.9375 | 74.1% | 66.64% | 95% | 0% | 2290 | -420
[5 empty] | 2019-05-16 | 36 | 3257 | 1978 | -365 | 1 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -417.6201 | 1132.0089 | -3550 | -400 | -2817.9911 | 70.45% | 66.64% | 95% | 0% | 2343 | -365
[5 empty] | 2019-05-16 | 37 | 3257.5 | 2081 | -295 | 1 | 0 | 2376 | 1601.319 | 1601.319 | 1601.319 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -337.5286 | 1263.7904 | -3550 | -400 | -2686.2096 | 67.16% | 66.63% | 95% | 0% | 2376 | -295
[5 empty] | 2019-05-16 | 38 | 3258 | 2167 | -241 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -275.7437 | 1375.699 | -3550 | -400 | -2574.301 | 64.36% | 66.63% | 95% | 0% | 2408 | -241
[5 empty] | 2019-05-16 | 39 | 3258.5 | 2243 | -192 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -219.6796 | 1474.0549 | -3550 | -400 | -2475.9451 | 61.9% | 66.63% | 95% | 0% | 2435 | -192
[5 empty] | 2019-05-16 | 40 | 3259 | 2304 | -150 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -171.6247 | 1551.8708 | -3550 | -400 | -2398.1292 | 59.95% | 66.63% | 95% | 0% | 2454 | -150
[5 empty] | 2019-05-16 | 41 | 3259.5 | 2325 | -123 | 1 | 0 | 2448 | 1714.0973 | 1714.0973 | 1714.0973 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -140.7323 | 1573.365 | -3550 | -400 | -2376.635 | 59.42% | 66.62% | 95% | 0% | 2448 | -123
[5 empty] | 2019-05-16 | 42 | 3260 | 2330 | -110 | 1 | 0 | 2440 | 1701.5664 | 1701.5664 | 1701.5664 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -125.8581 | 1575.7082 | -3550 | -400 | -2374.2918 | 59.36% | 66.62% | 95% | 0% | 2440 | -110
[5 empty] | 2019-05-16 | 43 | 3260.5 | 2317 | -108 | 1 | 0 | 2425 | 1678.0709 | 1678.0709 | 1678.0709 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -123.5698 | 1554.5011 | -3550 | -400 | -2395.4989 | 59.89% | 66.62% | 95% | 0% | 2425 | -108
[5 empty] | 2019-05-16 | 44 | 3261 | 2254 | -106 | 1 | 0 | 2360 | 1576.2572 | 1576.2572 | 1576.2572 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -121.2815 | 1454.9757 | -3550 | -400 | -2495.0243 | 62.38% | 66.61% | 95% | 0% | 2360 | -106
[5 empty] | 2019-05-16 | 45 | 3261.5 | 2134 | -103 | 0 | 0 | 2237 | 1383.5944 | 1383.5944 | 1383.5944 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -117.849 | 1265.7454 | -2750 | -200 | -1684.2546 | 42.11% | 66.61% | 95% | 0% | 2237 | -103
[5 empty] | 2019-05-16 | 46 | 3262 | 1985 | -101 | 0 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -115.5606 | 1031.5127 | -2750 | -200 | -1918.4873 | 47.96% | 66.61% | 95% | 0% | 2086 | -101
[5 empty] | 2019-05-16 | 47 | 3262.5 | 1843 | -98 | 0 | 0 | 1941 | 919.9505 | 919.9505 | 919.9505 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -112.1281 | 807.8224 | -2750 | -200 | -2142.1776 | 53.55% | 66.6% | 95% | 0% | 1941 | -98
[5 empty] | 2019-05-16 | 48 | 3263 | 1727 | -96 | 0 | 0 | 1823 | 735.1195 | 735.1195 | 735.1195 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -109.8398 | 625.2797 | -2750 | -200 | -2324.7203 | 58.12% | 66.6% | 95% | 0% | 1823 | -96
[5 empty] | 2019-05-17 | 1 | 3263.5 | 1655 | -93 | 0 | 0 | 1748 | 617.6422 | 617.6422 | 617.6422 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -106.4073 | 511.2349 | -2750 | -200 | -2438.7651 | 60.97% | 66.59% | 95% | 0% | 1748 | -93
[5 empty] | 2019-05-17 | 2 | 3264 | 1609 | -90 | 0 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -102.9748 | 437.9155 | -2750 | -200 | -2512.0845 | 62.8% | 66.59% | 95% | 0% | 1699 | -90
[5 empty] | 2019-05-17 | 3 | 3264.5 | 1578 | -91 | 0 | 0 | 1669 | 493.8994 | 493.8994 | 493.8994 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -104.119 | 389.7804 | -2750 | -200 | -2560.2196 | 64.01% | 66.59% | 95% | 0% | 1669 | -91
[5 empty] | 2019-05-17 | 4 | 3265 | 1575 | -93 | 0 | 0 | 1668 | 492.3331 | 492.3331 | 492.3331 | 1638.9118 | 780 | 200 | 2618.9118 | 65.47% | 95% | 0% | -106.4073 | 385.9257 | -2750 | -200 | -2564.0743 | 64.1% | 66.59% | 95% | 0% | 1668 | -93
[5 empty] | 2019-05-17 | 5 | 3265.5 | 1570 | -94 | 0 | 0 | 1664 | 486.0676 | 486.0676 | 486.0676 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -107.5515 | 378.5161 | -2750 | -200 | -2571.4839 | 64.29% | 66.58% | 95% | 0% | 1664 | -94
[5 empty] | 2019-05-17 | 6 | 3266 | 1541 | -95 | 0 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -108.6957 | 333.5137 | -2750 | -200 | -2616.4863 | 65.41% | 66.58% | 95% | 0% | 1636 | -95
[5 empty] | 2019-05-17 | 7 | 3266.5 | 1511 | -95 | 0 | 0 | 1606 | 395.2185 | 395.2185 | 395.2185 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -108.6957 | 286.5228 | -2750 | -200 | -2663.4772 | 66.59% | 66.58% | 95% | 0% | 1606 | -95
[5 empty] | 2019-05-17 | 8 | 3267 | 1501 | -94 | 1 | 0 | 1595 | 377.9885 | 377.9885 | 377.9885 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -107.5515 | 270.437 | -3550 | -400 | -3679.563 | 91.99% | 66.58% | 95% | 0% | 1595 | -94
[5 empty] | 2019-05-17 | 9 | 3267.5 | 1484 | -96 | 1 | 0 | 1580 | 354.493 | 354.493 | 354.493 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -109.8398 | 244.6532 | -3550 | -400 | -3705.3468 | 92.63% | 66.58% | 95% | 0% | 1580 | -96
[5 empty] | 2019-05-17 | 10 | 3268 | 1482 | -98 | 1 | 0 | 1580 | 354.493 | 354.493 | 354.493 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -112.1281 | 242.3648 | -3550 | -400 | -3707.6352 | 92.69% | 66.58% | 95% | 0% | 1580 | -98
[5 empty] | 2019-05-17 | 11 | 3268.5 | 1516 | -97 | 1 | 0 | 1613 | 406.183 | 406.183 | 406.183 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -110.984 | 295.199 | -3550 | -400 | -3654.801 | 91.37% | 66.57% | 95% | 0% | 1613 | -97
[5 empty] | 2019-05-17 | 12 | 3269 | 1584 | -101 | 1 | 0 | 1685 | 518.9613 | 518.9613 | 518.9613 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -115.5606 | 403.4006 | -3550 | -400 | -3546.5994 | 88.66% | 66.56% | 95% | 0% | 1685 | -101
[5 empty] | 2019-05-17 | 13 | 3269.5 | 1749 | -115 | 1 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -131.5789 | 667.7615 | -3550 | -400 | -3282.2385 | 82.06% | 66.56% | 95% | 0% | 1864 | -115
[5 empty] | 2019-05-17 | 14 | 3270 | 1939 | -127 | 1 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -145.3089 | 970.4372 | -3550 | -400 | -2979.5628 | 74.49% | 66.55% | 95% | 0% | 2066 | -127
[5 empty] | 2019-05-17 | 15 | 3270.5 | 2148 | -141 | 1 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -161.3272 | 1303.7181 | -3550 | -400 | -2646.2819 | 66.16% | 66.55% | 95% | 0% | 2289 | -141
[5 empty] | 2019-05-17 | 16 | 3271 | 2249 | -165 | 1 | 0 | 2414 | 1660.8409 | 1660.8409 | 1660.8409 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -188.7872 | 1472.0537 | -3550 | -400 | -2477.9463 | 61.95% | 66.54% | 95% | 0% | 2414 | -165
[5 empty] | 2019-05-17 | 17 | 3271.5 | 2290 | -185 | 1 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 1637.3454 | 780 | 200 | 2617.3454 | 65.43% | 95% | 0% | -211.6705 | 1544.7186 | -3550 | -400 | -2405.2814 | 60.13% | 66.54% | 95% | 0% | 2475 | -185
[5 empty] | 2019-05-17 | 18 | 3272 | 2240 | -226 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 1635.7791 | 780 | 200 | 2615.7791 | 65.39% | 95% | 0% | -258.5812 | 1483.7106 | -3550 | -400 | -2466.2894 | 61.66% | 66.54% | 95% | 0% | 2466 | -226
[5 empty] | 2019-05-17 | 19 | 3272.5 | 2236 | -251 | 1 | 0 | 2487 | 1775.1855 | 1775.1855 | 1775.1855 | 1635.7791 | 780 | 200 | 2615.7791 | 65.39% | 95% | 0% | -287.1854 | 1488.0001 | -3550 | -400 | -2461.9999 | 61.55% | 66.54% | 95% | 0% | 2487 | -251
[5 empty] | 2019-05-17 | 20 | 3273 | 2231 | -273 | 1 | 0 | 2504 | 1801.8137 | 1801.8137 | 1801.8137 | 1635.7791 | 780 | 200 | 2615.7791 | 65.39% | 95% | 0% | -312.357 | 1489.4567 | -3550 | -400 | -2460.5433 | 61.51% | 66.53% | 95% | 0% | 2504 | -273
[5 empty] | 2019-05-17 | 21 | 3273.5 | 2198 | -273 | 1 | 0 | 2471 | 1750.1237 | 1750.1237 | 1750.1237 | 1635.7791 | 780 | 200 | 2615.7791 | 65.39% | 95% | 0% | -312.357 | 1437.7667 | -3550 | -400 | -2512.2333 | 62.81% | 66.53% | 95% | 0% | 2471 | -273
[5 empty] | 2019-05-17 | 22 | 3274 | 2152 | -291 | 1 | 0 | 2443 | 1706.2655 | 1706.2655 | 1706.2655 | 1635.7791 | 780 | 200 | 2615.7791 | 65.39% | 95% | 0% | -332.9519 | 1373.3135 | -3550 | -400 | -2576.6865 | 64.42% | 66.53% | 95% | 0% | 2443 | -291
[5 empty] | 2019-05-17 | 23 | 3274.5 | 2104 | -319 | 1 | 0 | 2423 | 1674.9382 | 1674.9382 | 1674.9382 | 1635.7791 | 780 | 200 | 2615.7791 | 65.39% | 95% | 0% | -364.9886 | 1309.9496 | -3550 | -400 | -2640.0504 | 66% | 66.53% | 95% | 0% | 2423 | -319
[5 empty] | 2019-05-17 | 24 | 3275 | 2084 | -338 | 1 | 0 | 2422 | 1673.3718 | 1673.3718 | 1673.3718 | 1635.7791 | 780 | 200 | 2615.7791 | 65.39% | 95% | 0% | -386.7277 | 1286.6441 | -3550 | -400 | -2663.3559 | 66.58% | 66.52% | 95% | 0% | 2422 | -338
[5 empty] | 2019-05-17 | 25 | 3275.5 | 2073 | -361 | 1 | 0 | 2434 | 1692.1682 | 1692.1682 | 1692.1682 | 1635.7791 | 780 | 200 | 2615.7791 | 65.39% | 95% | 0% | -413.0435 | 1279.1247 | -3550 | -400 | -2670.8753 | 66.77% | 66.51% | 95% | 0% | 2434 | -361
[5 empty] | 2019-05-17 | 26 | 3276 | 2036 | -391 | 1 | 0 | 2427 | 1681.2036 | 1681.2036 | 1681.2036 | 1635.7791 | 780 | 200 | 2615.7791 | 65.39% | 95% | 0% | -447.3684 | 1233.8352 | -3550 | -400 | -2716.1648 | 67.9% | 66.51% | 95% | 0% | 2427 | -391
[5 empty] | 2019-05-17 | 27 | 3276.5 | 1960 | -431 | 1 | 0 | 2391 | 1624.8145 | 1624.8145 | 1624.8145 | 1635.7791 | 780 | 200 | 2615.7791 | 65.39% | 95% | 0% | -493.135 | 1131.6795 | -3550 | -400 | -2818.3205 | 70.46% | 66.51% | 95% | 0% | 2391 | -431
[5 empty] | 2019-05-17 | 28 | 3277 | 1939 | -419 | 1 | 0 | 2358 | 1573.1245 | 1573.1245 | 1573.1245 | 1635.7791 | 780 | 200 | 2615.7791 | 65.39% | 95% | 0% | -479.405 | 1093.7195 | -3550 | -400 | -2856.2805 | 71.41% | 66.51% | 95% | 0% | 2358 | -419
[5 empty] | 2019-05-17 | 29 | 3277.5 | 1942 | -399 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 1634.2127 | 780 | 200 | 2614.2127 | 65.36% | 95% | 0% | -456.5217 | 1089.9746 | -3550 | -400 | -2860.0254 | 71.5% | 66.5% | 95% | 0% | 2341 | -399
[5 empty] | 2019-05-17 | 30 | 3278 | 1980 | -342 | 1 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 1634.2127 | 780 | 200 | 2614.2127 | 65.36% | 95% | 0% | -391.3043 | 1125.431 | -3550 | -400 | -2824.569 | 70.61% | 66.5% | 95% | 0% | 2322 | -342
[5 empty] | 2019-05-17 | 31 | 3278.5 | 2000 | -315 | 1 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 1634.2127 | 780 | 200 | 2614.2127 | 65.36% | 95% | 0% | -360.4119 | 1145.3589 | -3550 | -400 | -2804.6411 | 70.12% | 66.5% | 95% | 0% | 2315 | -315
[5 empty] | 2019-05-17 | 32 | 3279 | 2040 | -317 | 1 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 1634.2127 | 780 | 200 | 2614.2127 | 65.36% | 95% | 0% | -362.7002 | 1208.8579 | -3550 | -400 | -2741.1421 | 68.53% | 66.49% | 95% | 0% | 2357 | -317
[5 empty] | 2019-05-17 | 33 | 3279.5 | 2137 | -284 | 1 | 0 | 2421 | 1671.8054 | 1671.8054 | 1671.8054 | 1634.2127 | 780 | 200 | 2614.2127 | 65.36% | 95% | 0% | -324.9428 | 1346.8626 | -3550 | -400 | -2603.1374 | 65.08% | 66.49% | 95% | 0% | 2421 | -284
[5 empty] | 2019-05-17 | 34 | 3280 | 2227 | -246 | 1 | 0 | 2473 | 1753.2564 | 1753.2564 | 1753.2564 | 1634.2127 | 780 | 200 | 2614.2127 | 65.36% | 95% | 0% | -281.4645 | 1471.7919 | -3550 | -400 | -2478.2081 | 61.96% | 66.49% | 95% | 0% | 2473 | -246
[5 empty] | 2019-05-17 | 35 | 3280.5 | 2310 | -211 | 1 | 0 | 2521 | 1828.4419 | 1828.4419 | 1828.4419 | 1634.2127 | 780 | 200 | 2614.2127 | 65.36% | 95% | 0% | -241.4188 | 1587.0231 | -3550 | -400 | -2362.9769 | 59.07% | 66.49% | 95% | 0% | 2521 | -211
[5 empty] | 2019-05-17 | 36 | 3281 | 2342 | -189 | 1 | 0 | 2531 | 1844.1055 | 1844.1055 | 1844.1055 | 1634.2127 | 780 | 200 | 2614.2127 | 65.36% | 95% | 0% | -216.2471 | 1627.8584 | -3550 | -400 | -2322.1416 | 58.05% | 66.48% | 95% | 0% | 2531 | -189
[5 empty] | 2019-05-17 | 37 | 3281.5 | 2366 | -169 | 1 | 0 | 2535 | 1850.371 | 1850.371 | 1850.371 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -193.3638 | 1657.0071 | -3550 | -400 | -2292.9929 | 57.32% | 66.48% | 95% | 0% | 2535 | -169
[5 empty] | 2019-05-17 | 38 | 3282 | 2393 | -147 | 1 | 0 | 2540 | 1858.2028 | 1858.2028 | 1858.2028 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -168.1922 | 1690.0106 | -3550 | -400 | -2259.9894 | 56.5% | 66.48% | 95% | 0% | 2540 | -147
[5 empty] | 2019-05-17 | 39 | 3282.5 | 2386 | -124 | 1 | 0 | 2510 | 1811.2119 | 1811.2119 | 1811.2119 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -141.8764 | 1669.3354 | -3550 | -400 | -2280.6646 | 57.02% | 66.48% | 95% | 0% | 2510 | -124
[5 empty] | 2019-05-17 | 40 | 3283 | 2386 | -105 | 1 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -120.1373 | 1661.3136 | -3550 | -400 | -2288.6864 | 57.22% | 66.47% | 95% | 0% | 2491 | -105
[5 empty] | 2019-05-17 | 41 | 3283.5 | 2374 | -96 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -109.8398 | 1638.7175 | -3550 | -400 | -2311.2825 | 57.78% | 66.46% | 95% | 0% | 2470 | -96
[5 empty] | 2019-05-17 | 42 | 3284 | 2352 | -92 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -105.2632 | 1602.5687 | -3550 | -400 | -2347.4313 | 58.69% | 66.46% | 95% | 0% | 2444 | -92
[5 empty] | 2019-05-17 | 43 | 3284.5 | 2330 | -89 | 1 | 0 | 2419 | 1668.6727 | 1668.6727 | 1668.6727 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -101.8307 | 1566.842 | -3550 | -400 | -2383.158 | 59.58% | 66.46% | 95% | 0% | 2419 | -89
[5 empty] | 2019-05-17 | 44 | 3285 | 2250 | -87 | 1 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -99.5423 | 1440.6885 | -3550 | -400 | -2509.3115 | 62.73% | 66.46% | 95% | 0% | 2337 | -87
[5 empty] | 2019-05-17 | 45 | 3285.5 | 2140 | -84 | 0 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -96.1098 | 1267.1218 | -2750 | -200 | -1682.8782 | 42.07% | 66.46% | 95% | 0% | 2224 | -84
[5 empty] | 2019-05-17 | 46 | 3286 | 2031 | -82 | 0 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -93.8215 | 1095.5437 | -2750 | -200 | -1854.4563 | 46.36% | 66.45% | 95% | 0% | 2113 | -82
[5 empty] | 2019-05-17 | 47 | 3286.5 | 1903 | -80 | 0 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -91.5332 | 894.2047 | -2750 | -200 | -2055.7953 | 51.39% | 66.45% | 95% | 0% | 1983 | -80
[5 empty] | 2019-05-17 | 48 | 3287 | 1798 | -78 | 0 | 0 | 1876 | 818.1369 | 818.1369 | 818.1369 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -89.2449 | 728.892 | -2750 | -200 | -2221.108 | 55.53% | 66.45% | 95% | 0% | 1876 | -78
[5 empty] | 2019-05-18 | 1 | 3287.5 | 1705 | -75 | 0 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 1632.6463 | 780 | 200 | 2612.6463 | 65.32% | 95% | 0% | -85.8124 | 581.9535 | -2750 | -200 | -2368.0465 | 59.2% | 66.45% | 95% | 0% | 1780 | -75
[5 empty] | 2019-05-18 | 2 | 3288 | 1652 | -72 | 0 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 1631.08 | 780 | 200 | 2611.08 | 65.28% | 95% | 0% | -82.3799 | 497.6696 | -2750 | -200 | -2452.3304 | 61.31% | 66.45% | 95% | 0% | 1724 | -72
[5 empty] | 2019-05-18 | 3 | 3288.5 | 1632 | -69 | 0 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 1631.08 | 780 | 200 | 2611.08 | 65.28% | 95% | 0% | -78.9474 | 465.0757 | -2750 | -200 | -2484.9243 | 62.12% | 66.45% | 95% | 0% | 1701 | -69
[5 empty] | 2019-05-18 | 4 | 3289 | 1636 | -65 | 0 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 1631.08 | 780 | 200 | 2611.08 | 65.28% | 95% | 0% | -74.3707 | 469.6524 | -2750 | -200 | -2480.3476 | 62.01% | 66.45% | 95% | 0% | 1701 | -65
[5 empty] | 2019-05-18 | 5 | 3289.5 | 1621 | -63 | 0 | 0 | 1684 | 517.3949 | 517.3949 | 517.3949 | 1631.08 | 780 | 200 | 2611.08 | 65.28% | 95% | 0% | -72.0824 | 445.3125 | -2750 | -200 | -2504.6875 | 62.62% | 66.45% | 95% | 0% | 1684 | -63
[5 empty] | 2019-05-18 | 6 | 3290 | 1588 | -61 | 0 | 0 | 1649 | 462.5721 | 462.5721 | 462.5721 | 1631.08 | 780 | 200 | 2611.08 | 65.28% | 95% | 0% | -69.7941 | 392.7781 | -2750 | -200 | -2557.2219 | 63.93% | 66.44% | 95% | 0% | 1649 | -61
[5 empty] | 2019-05-18 | 7 | 3290.5 | 1561 | -59 | 1 | 0 | 1620 | 417.1476 | 417.1476 | 417.1476 | 1631.08 | 780 | 200 | 2611.08 | 65.28% | 95% | 0% | -67.5057 | 349.6418 | -3550 | -400 | -3600.3582 | 90.01% | 66.44% | 95% | 0% | 1620 | -59
[5 empty] | 2019-05-18 | 8 | 3291 | 1546 | -57 | 1 | 0 | 1603 | 390.5194 | 390.5194 | 390.5194 | 1631.08 | 780 | 200 | 2611.08 | 65.28% | 95% | 0% | -65.2174 | 325.302 | -3550 | -400 | -3624.698 | 90.62% | 66.43% | 95% | 0% | 1603 | -57
[5 empty] | 2019-05-18 | 9 | 3291.5 | 1533 | -55 | 1 | 0 | 1588 | 367.0239 | 367.0239 | 367.0239 | 1631.08 | 780 | 200 | 2611.08 | 65.28% | 95% | 0% | -62.9291 | 304.0948 | -3550 | -400 | -3645.9052 | 91.15% | 66.43% | 95% | 0% | 1588 | -55
[5 empty] | 2019-05-18 | 10 | 3292 | 1530 | -53 | 1 | 0 | 1583 | 359.1921 | 359.1921 | 359.1921 | 1631.08 | 780 | 200 | 2611.08 | 65.28% | 95% | 0% | -60.6407 | 298.5514 | -3550 | -400 | -3651.4486 | 91.29% | 66.42% | 95% | 0% | 1583 | -53
[5 empty] | 2019-05-18 | 11 | 3292.5 | 1520 | -52 | 1 | 0 | 1572 | 341.9621 | 341.9621 | 341.9621 | 1631.08 | 780 | 200 | 2611.08 | 65.28% | 95% | 0% | -59.4966 | 282.4655 | -3550 | -400 | -3667.5345 | 91.69% | 66.42% | 95% | 0% | 1572 | -52
[5 empty] | 2019-05-18 | 12 | 3293 | 1535 | -54 | 1 | 0 | 1589 | 368.5903 | 368.5903 | 368.5903 | 1629.5136 | 780 | 200 | 2609.5136 | 65.24% | 95% | 0% | -61.7849 | 306.8054 | -3550 | -400 | -3643.1946 | 91.08% | 66.42% | 95% | 0% | 1589 | -54
[5 empty] | 2019-05-18 | 13 | 3293.5 | 1616 | -61 | 1 | 0 | 1677 | 506.4303 | 506.4303 | 506.4303 | 1629.5136 | 780 | 200 | 2609.5136 | 65.24% | 95% | 0% | -69.7941 | 436.6363 | -3550 | -400 | -3513.3637 | 87.83% | 66.42% | 95% | 0% | 1677 | -61
[5 empty] | 2019-05-18 | 14 | 3294 | 1674 | -76 | 1 | 0 | 1750 | 620.7749 | 620.7749 | 620.7749 | 1629.5136 | 780 | 200 | 2609.5136 | 65.24% | 95% | 0% | -86.9565 | 533.8184 | -3550 | -400 | -3416.1816 | 85.4% | 66.41% | 95% | 0% | 1750 | -76
[5 empty] | 2019-05-18 | 15 | 3294.5 | 1786 | -92 | 1 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 1629.5136 | 780 | 200 | 2609.5136 | 65.24% | 95% | 0% | -105.2632 | 716.0064 | -3550 | -400 | -3233.9936 | 80.85% | 66.41% | 95% | 0% | 1878 | -92
[5 empty] | 2019-05-18 | 16 | 3295 | 1857 | -118 | 1 | 0 | 1975 | 973.2069 | 973.2069 | 973.2069 | 1629.5136 | 780 | 200 | 2609.5136 | 65.24% | 95% | 0% | -135.0114 | 838.1955 | -3550 | -400 | -3111.8045 | 77.8% | 66.41% | 95% | 0% | 1975 | -118
[5 empty] | 2019-05-18 | 17 | 3295.5 | 1936 | -150 | 1 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 1629.5136 | 780 | 200 | 2609.5136 | 65.24% | 95% | 0% | -171.6247 | 975.4487 | -3550 | -400 | -2974.5513 | 74.36% | 66.41% | 95% | 0% | 2086 | -150
[5 empty] | 2019-05-18 | 18 | 3296 | 1946 | -179 | 1 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 1629.5136 | 780 | 200 | 2609.5136 | 65.24% | 95% | 0% | -204.8055 | 1003.3561 | -3550 | -400 | -2946.6439 | 73.67% | 66.4% | 95% | 0% | 2125 | -179
[5 empty] | 2019-05-18 | 19 | 3296.5 | 1968 | -210 | 1 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 1629.5136 | 780 | 200 | 2609.5136 | 65.24% | 95% | 0% | -240.2746 | 1050.9043 | -3550 | -400 | -2899.0957 | 72.48% | 66.39% | 95% | 0% | 2178 | -210
[5 empty] | 2019-05-18 | 20 | 3297 | 1939 | -230 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 1629.5136 | 780 | 200 | 2609.5136 | 65.24% | 95% | 0% | -263.1579 | 1013.9237 | -3550 | -400 | -2936.0763 | 73.4% | 66.39% | 95% | 0% | 2169 | -230
[5 empty] | 2019-05-18 | 21 | 3297.5 | 1908 | -243 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1629.5136 | 780 | 200 | 2609.5136 | 65.24% | 95% | 0% | -278.032 | 970.855 | -3550 | -400 | -2979.145 | 74.48% | 66.39% | 95% | 0% | 2151 | -243
[5 empty] | 2019-05-18 | 22 | 3298 | 1874 | -264 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1627.9472 | 780 | 200 | 2607.9472 | 65.2% | 95% | 0% | -302.0595 | 926.4648 | -3550 | -400 | -3023.5352 | 75.59% | 66.39% | 95% | 0% | 2138 | -264
[5 empty] | 2019-05-18 | 23 | 3298.5 | 1819 | -310 | 1 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 1627.9472 | 780 | 200 | 2607.9472 | 65.2% | 95% | 0% | -354.6911 | 859.736 | -3550 | -400 | -3090.264 | 77.26% | 66.38% | 95% | 0% | 2129 | -310
[5 empty] | 2019-05-18 | 24 | 3299 | 1799 | -340 | 1 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 1627.9472 | 780 | 200 | 2607.9472 | 65.2% | 95% | 0% | -389.016 | 841.0747 | -3550 | -400 | -3108.9253 | 77.72% | 66.38% | 95% | 0% | 2139 | -340
[5 empty] | 2019-05-18 | 25 | 3299.5 | 1808 | -343 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1627.9472 | 780 | 200 | 2607.9472 | 65.2% | 95% | 0% | -392.4485 | 856.4385 | -3550 | -400 | -3093.5615 | 77.34% | 66.38% | 95% | 0% | 2151 | -343
[5 empty] | 2019-05-18 | 26 | 3300 | 1801 | -345 | 1 | 0 | 2146 | 1241.0552 | 1241.0552 | 1241.0552 | 1627.9472 | 780 | 200 | 2607.9472 | 65.2% | 95% | 0% | -394.7368 | 846.3184 | -3550 | -400 | -3103.6816 | 77.59% | 66.37% | 95% | 0% | 2146 | -345
[5 empty] | 2019-05-18 | 27 | 3300.5 | 1769 | -355 | 1 | 0 | 2124 | 1206.5952 | 1206.5952 | 1206.5952 | 1627.9472 | 780 | 200 | 2607.9472 | 65.2% | 95% | 0% | -406.1785 | 800.4167 | -3550 | -400 | -3149.5833 | 78.74% | 66.36% | 95% | 0% | 2124 | -355
[5 empty] | 2019-05-18 | 28 | 3301 | 1738 | -342 | 1 | 0 | 2080 | 1137.6752 | 1137.6752 | 1137.6752 | 1627.9472 | 780 | 200 | 2607.9472 | 65.2% | 95% | 0% | -391.3043 | 746.3708 | -3550 | -400 | -3203.6292 | 80.09% | 66.36% | 95% | 0% | 2080 | -342
[5 empty] | 2019-05-18 | 29 | 3301.5 | 1745 | -315 | 1 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 1627.9472 | 780 | 200 | 2607.9472 | 65.2% | 95% | 0% | -360.4119 | 745.936 | -3550 | -400 | -3204.064 | 80.1% | 66.36% | 95% | 0% | 2060 | -315
[5 empty] | 2019-05-18 | 30 | 3302 | 1745 | -294 | 1 | 0 | 2039 | 1073.4542 | 1073.4542 | 1073.4542 | 1627.9472 | 780 | 200 | 2607.9472 | 65.2% | 95% | 0% | -336.3844 | 737.0698 | -3550 | -400 | -3212.9302 | 80.32% | 66.35% | 95% | 0% | 2039 | -294
[5 empty] | 2019-05-18 | 31 | 3302.5 | 1751 | -277 | 1 | 0 | 2028 | 1056.2242 | 1056.2242 | 1056.2242 | 1626.3809 | 780 | 200 | 2606.3809 | 65.16% | 95% | 0% | -316.9336 | 739.2906 | -3550 | -400 | -3210.7094 | 80.27% | 66.35% | 95% | 0% | 2028 | -277
[5 empty] | 2019-05-18 | 32 | 3303 | 1808 | -248 | 1 | 0 | 2056 | 1100.0824 | 1100.0824 | 1100.0824 | 1626.3809 | 780 | 200 | 2606.3809 | 65.16% | 95% | 0% | -283.7529 | 816.3296 | -3550 | -400 | -3133.6704 | 78.34% | 66.35% | 95% | 0% | 2056 | -248
[5 empty] | 2019-05-18 | 33 | 3303.5 | 1894 | -222 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1626.3809 | 780 | 200 | 2606.3809 | 65.16% | 95% | 0% | -254.0046 | 940.0597 | -3550 | -400 | -3009.9403 | 75.25% | 66.35% | 95% | 0% | 2116 | -222
[5 empty] | 2019-05-18 | 34 | 3304 | 1969 | -201 | 1 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 1626.3809 | 780 | 200 | 2606.3809 | 65.16% | 95% | 0% | -229.9771 | 1048.6709 | -3550 | -400 | -2901.3291 | 72.53% | 66.35% | 95% | 0% | 2170 | -201
[5 empty] | 2019-05-18 | 35 | 3304.5 | 2069 | -171 | 1 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 1626.3809 | 780 | 200 | 2606.3809 | 65.16% | 95% | 0% | -195.6522 | 1192.6413 | -3550 | -400 | -2757.3587 | 68.93% | 66.34% | 95% | 0% | 2240 | -171
[5 empty] | 2019-05-18 | 36 | 3305 | 2119 | -154 | 1 | 0 | 2273 | 1439.9835 | 1439.9835 | 1439.9835 | 1626.3809 | 780 | 200 | 2606.3809 | 65.16% | 95% | 0% | -176.2014 | 1263.7821 | -3550 | -400 | -2686.2179 | 67.16% | 66.34% | 95% | 0% | 2273 | -154
[5 empty] | 2019-05-18 | 37 | 3305.5 | 2150 | -122 | 1 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 1624.8145 | 780 | 200 | 2604.8145 | 65.12% | 95% | 0% | -139.5881 | 1298.829 | -3550 | -400 | -2651.171 | 66.28% | 66.33% | 95% | 0% | 2272 | -122
[5 empty] | 2019-05-18 | 38 | 3306 | 2156 | -103 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 1624.8145 | 780 | 200 | 2604.8145 | 65.12% | 95% | 0% | -117.849 | 1300.2054 | -3550 | -400 | -2649.7946 | 66.24% | 66.33% | 95% | 0% | 2259 | -103
[5 empty] | 2019-05-18 | 39 | 3306.5 | 2194 | -73 | 1 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 1624.8145 | 780 | 200 | 2604.8145 | 65.12% | 95% | 0% | -83.524 | 1347.0613 | -3550 | -400 | -2602.9387 | 65.07% | 66.33% | 95% | 0% | 2267 | -73
[5 empty] | 2019-05-18 | 40 | 3307 | 2206 | -52 | 1 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 1624.8145 | 780 | 200 | 2604.8145 | 65.12% | 95% | 0% | -59.4966 | 1356.9915 | -3550 | -400 | -2593.0085 | 64.83% | 66.33% | 95% | 0% | 2258 | -52
[5 empty] | 2019-05-18 | 41 | 3307.5 | 2198 | -34 | 1 | 0 | 2232 | 1375.7626 | 1375.7626 | 1375.7626 | 1624.8145 | 780 | 200 | 2604.8145 | 65.12% | 95% | 0% | -38.9016 | 1336.861 | -3550 | -400 | -2613.139 | 65.33% | 66.32% | 95% | 0% | 2232 | -34
[5 empty] | 2019-05-18 | 42 | 3308 | 2191 | -26 | 1 | 0 | 2217 | 1352.2671 | 1352.2671 | 1352.2671 | 1624.8145 | 780 | 200 | 2604.8145 | 65.12% | 95% | 0% | -29.7483 | 1322.5188 | -3550 | -400 | -2627.4812 | 65.69% | 66.32% | 95% | 0% | 2217 | -26
[5 empty] | 2019-05-18 | 43 | 3308.5 | 2204 | -24 | 1 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 1624.8145 | 780 | 200 | 2604.8145 | 65.12% | 95% | 0% | -27.46 | 1342.0372 | -3550 | -400 | -2607.9628 | 65.2% | 66.31% | 95% | 0% | 2228 | -24
[5 empty] | 2019-05-18 | 44 | 3309 | 2192 | -24 | 1 | 0 | 2216 | 1350.7007 | 1350.7007 | 1350.7007 | 1624.8145 | 780 | 200 | 2604.8145 | 65.12% | 95% | 0% | -27.46 | 1323.2408 | -3550 | -400 | -2626.7592 | 65.67% | 66.31% | 95% | 0% | 2216 | -24
[5 empty] | 2019-05-18 | 45 | 3309.5 | 2127 | -23 | 0 | 0 | 2150 | 1247.3207 | 1247.3207 | 1247.3207 | 1624.8145 | 780 | 200 | 2604.8145 | 65.12% | 95% | 0% | -26.3158 | 1221.0049 | -2750 | -200 | -1728.9951 | 43.22% | 66.31% | 95% | 0% | 2150 | -23
[5 empty] | 2019-05-18 | 46 | 3310 | 2026 | -22 | 0 | 0 | 2048 | 1087.5515 | 1087.5515 | 1087.5515 | 1624.8145 | 780 | 200 | 2604.8145 | 65.12% | 95% | 0% | -25.1716 | 1062.3799 | -2750 | -200 | -1887.6201 | 47.19% | 66.31% | 95% | 0% | 2048 | -22
[5 empty] | 2019-05-18 | 47 | 3310.5 | 1928 | -21 | 0 | 0 | 1949 | 932.4815 | 932.4815 | 932.4815 | 1623.2481 | 780 | 200 | 2603.2481 | 65.08% | 95% | 0% | -24.0275 | 908.454 | -2750 | -200 | -2041.546 | 51.04% | 66.31% | 95% | 0% | 1949 | -21
[5 empty] | 2019-05-18 | 48 | 3311 | 1832 | -21 | 0 | 0 | 1853 | 782.1105 | 782.1105 | 782.1105 | 1623.2481 | 780 | 200 | 2603.2481 | 65.08% | 95% | 0% | -24.0275 | 758.083 | -2750 | -200 | -2191.917 | 54.8% | 66.3% | 95% | 0% | 1853 | -21
[5 empty] | 2019-05-19 | 1 | 3311.5 | 1751 | -20 | 0 | 0 | 1771 | 653.6686 | 653.6686 | 653.6686 | 1623.2481 | 780 | 200 | 2603.2481 | 65.08% | 95% | 0% | -22.8833 | 630.7853 | -2750 | -200 | -2319.2147 | 57.98% | 66.3% | 95% | 0% | 1771 | -20
[5 empty] | 2019-05-19 | 2 | 3312 | 1697 | -19 | 0 | 0 | 1716 | 567.5185 | 567.5185 | 567.5185 | 1623.2481 | 780 | 200 | 2603.2481 | 65.08% | 95% | 0% | -21.7391 | 545.7794 | -2750 | -200 | -2404.2206 | 60.11% | 66.29% | 95% | 0% | 1716 | -19
[5 empty] | 2019-05-19 | 3 | 3312.5 | 1668 | -19 | 0 | 0 | 1687 | 522.094 | 522.094 | 522.094 | 1623.2481 | 780 | 200 | 2603.2481 | 65.08% | 95% | 0% | -21.7391 | 500.3549 | -2750 | -200 | -2449.6451 | 61.24% | 66.29% | 95% | 0% | 1687 | -19
[5 empty] | 2019-05-19 | 4 | 3313 | 1661 | -18 | 0 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 1623.2481 | 780 | 200 | 2603.2481 | 65.08% | 95% | 0% | -20.595 | 488.9681 | -2750 | -200 | -2461.0319 | 61.53% | 66.29% | 95% | 0% | 1679 | -18
[5 empty] | 2019-05-19 | 5 | 3313.5 | 1636 | -18 | 0 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 1623.2481 | 780 | 200 | 2603.2481 | 65.08% | 95% | 0% | -20.595 | 449.809 | -2750 | -200 | -2500.191 | 62.5% | 66.29% | 95% | 0% | 1654 | -18
[5 empty] | 2019-05-19 | 6 | 3314 | 1603 | -18 | 0 | 0 | 1621 | 418.7139 | 418.7139 | 418.7139 | 1623.2481 | 780 | 200 | 2603.2481 | 65.08% | 95% | 0% | -20.595 | 398.119 | -2750 | -200 | -2551.881 | 63.8% | 66.29% | 95% | 0% | 1621 | -18
[5 empty] | 2019-05-19 | 7 | 3314.5 | 1573 | -18 | 0 | 0 | 1591 | 371.723 | 371.723 | 371.723 | 1623.2481 | 780 | 200 | 2603.2481 | 65.08% | 95% | 0% | -20.595 | 351.128 | -2750 | -200 | -2598.872 | 64.97% | 66.29% | 95% | 0% | 1591 | -18
[5 empty] | 2019-05-19 | 8 | 3315 | 1553 | -19 | 0 | 0 | 1572 | 341.9621 | 341.9621 | 341.9621 | 1623.2481 | 780 | 200 | 2603.2481 | 65.08% | 95% | 0% | -21.7391 | 320.2229 | -2750 | -200 | -2629.7771 | 65.74% | 66.29% | 95% | 0% | 1572 | -19
[5 empty] | 2019-05-19 | 9 | 3315.5 | 1538 | -19 | 0 | 0 | 1557 | 318.4666 | 318.4666 | 318.4666 | 1621.6818 | 780 | 200 | 2601.6818 | 65.04% | 95% | 0% | -21.7391 | 296.7275 | -2750 | -200 | -2653.2725 | 66.33% | 66.28% | 95% | 0% | 1557 | -19
[5 empty] | 2019-05-19 | 10 | 3316 | 1514 | -20 | 0 | 0 | 1534 | 282.4402 | 282.4402 | 282.4402 | 1621.6818 | 780 | 200 | 2601.6818 | 65.04% | 95% | 0% | -22.8833 | 259.5569 | -2750 | -200 | -2690.4431 | 67.26% | 66.28% | 95% | 0% | 1534 | -20
[5 empty] | 2019-05-19 | 11 | 3316.5 | 1485 | -21 | 0 | 0 | 1506 | 238.582 | 238.582 | 238.582 | 1621.6818 | 780 | 200 | 2601.6818 | 65.04% | 95% | 0% | -24.0275 | 214.5546 | -2750 | -200 | -2735.4454 | 68.39% | 66.28% | 95% | 0% | 1506 | -21
[5 empty] | 2019-05-19 | 12 | 3317 | 1472 | -28 | 0 | 0 | 1500 | 229.1838 | 229.1838 | 229.1838 | 1621.6818 | 780 | 200 | 2601.6818 | 65.04% | 95% | 0% | -32.0366 | 197.1472 | -2750 | -200 | -2752.8528 | 68.82% | 66.28% | 95% | 0% | 1500 | -28
[5 empty] | 2019-05-19 | 13 | 3317.5 | 1504 | -49 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 1621.6818 | 780 | 200 | 2601.6818 | 65.04% | 95% | 0% | -56.0641 | 256.1371 | -2750 | -200 | -2693.8629 | 67.35% | 66.27% | 95% | 0% | 1553 | -49
[5 empty] | 2019-05-19 | 14 | 3318 | 1502 | -80 | 0 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 1621.6818 | 780 | 200 | 2601.6818 | 65.04% | 95% | 0% | -91.5332 | 266.0925 | -2750 | -200 | -2683.9075 | 67.1% | 66.27% | 95% | 0% | 1582 | -80
[5 empty] | 2019-05-19 | 15 | 3318.5 | 1528 | -118 | 1 | 0 | 1646 | 457.873 | 457.873 | 457.873 | 1621.6818 | 780 | 200 | 2601.6818 | 65.04% | 95% | 0% | -135.0114 | 322.8616 | -3550 | -400 | -3627.1384 | 90.68% | 66.26% | 95% | 0% | 1646 | -118
[5 empty] | 2019-05-19 | 16 | 3319 | 1542 | -161 | 1 | 0 | 1703 | 547.1558 | 547.1558 | 547.1558 | 1621.6818 | 780 | 200 | 2601.6818 | 65.04% | 95% | 0% | -184.2105 | 362.9453 | -3550 | -400 | -3587.0547 | 89.68% | 66.26% | 95% | 0% | 1703 | -161
[5 empty] | 2019-05-19 | 17 | 3319.5 | 1580 | -204 | 1 | 0 | 1784 | 674.0313 | 674.0313 | 674.0313 | 1621.6818 | 780 | 200 | 2601.6818 | 65.04% | 95% | 0% | -233.4096 | 440.6217 | -3550 | -400 | -3509.3783 | 87.73% | 66.26% | 95% | 0% | 1784 | -204
[5 empty] | 2019-05-19 | 18 | 3320 | 1592 | -253 | 1 | 0 | 1845 | 769.5796 | 769.5796 | 769.5796 | 1621.6818 | 780 | 200 | 2601.6818 | 65.04% | 95% | 0% | -289.4737 | 480.1059 | -3550 | -400 | -3469.8941 | 86.75% | 66.26% | 95% | 0% | 1845 | -253
[5 empty] | 2019-05-19 | 19 | 3320.5 | 1584 | -304 | 1 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 1621.6818 | 780 | 200 | 2601.6818 | 65.04% | 95% | 0% | -347.8261 | 489.1071 | -3550 | -400 | -3460.8929 | 86.52% | 66.25% | 95% | 0% | 1888 | -304
[5 empty] | 2019-05-19 | 20 | 3321 | 1562 | -355 | 1 | 0 | 1917 | 882.3578 | 882.3578 | 882.3578 | 1620.1154 | 780 | 200 | 2600.1154 | 65% | 95% | 0% | -406.1785 | 476.1793 | -3550 | -400 | -3473.8207 | 86.85% | 66.25% | 95% | 0% | 1917 | -355
[5 empty] | 2019-05-19 | 21 | 3321.5 | 1563 | -379 | 1 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 1620.1154 | 780 | 200 | 2600.1154 | 65% | 95% | 0% | -433.6384 | 487.8785 | -3550 | -400 | -3462.1215 | 86.55% | 66.25% | 95% | 0% | 1942 | -379
[5 empty] | 2019-05-19 | 22 | 3322 | 1544 | -411 | 1 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 1620.1154 | 780 | 200 | 2600.1154 | 65% | 95% | 0% | -470.2517 | 471.6279 | -3550 | -400 | -3478.3721 | 86.96% | 66.25% | 95% | 0% | 1955 | -411
[5 empty] | 2019-05-19 | 23 | 3322.5 | 1562 | -415 | 1 | 0 | 1977 | 976.3397 | 976.3397 | 976.3397 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -474.8284 | 501.5113 | -3550 | -400 | -3448.4887 | 86.21% | 66.25% | 95% | 0% | 1977 | -415
[5 empty] | 2019-05-19 | 24 | 3323 | 1564 | -429 | 1 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -490.8467 | 510.5548 | -3550 | -400 | -3439.4452 | 85.99% | 66.25% | 95% | 0% | 1993 | -429
[5 empty] | 2019-05-19 | 25 | 3323.5 | 1555 | -439 | 1 | 0 | 1994 | 1002.9678 | 1002.9678 | 1002.9678 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -502.2883 | 500.6795 | -3550 | -400 | -3449.3205 | 86.23% | 66.25% | 95% | 0% | 1994 | -439
[5 empty] | 2019-05-19 | 26 | 3324 | 1568 | -427 | 1 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -488.5584 | 515.9759 | -3550 | -400 | -3434.0241 | 85.85% | 66.25% | 95% | 0% | 1995 | -427
[5 empty] | 2019-05-19 | 27 | 3324.5 | 1562 | -424 | 1 | 0 | 1986 | 990.4369 | 990.4369 | 990.4369 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -485.1259 | 505.3111 | -3550 | -400 | -3444.6889 | 86.12% | 66.24% | 95% | 0% | 1986 | -424
[5 empty] | 2019-05-19 | 28 | 3325 | 1564 | -415 | 1 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -474.8284 | 504.644 | -3550 | -400 | -3445.356 | 86.13% | 66.24% | 95% | 0% | 1979 | -415
[5 empty] | 2019-05-19 | 29 | 3325.5 | 1584 | -392 | 1 | 0 | 1976 | 974.7733 | 974.7733 | 974.7733 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -448.5126 | 526.2607 | -3550 | -400 | -3423.7393 | 85.59% | 66.24% | 95% | 0% | 1976 | -392
[5 empty] | 2019-05-19 | 30 | 3326 | 1589 | -378 | 1 | 0 | 1967 | 960.676 | 960.676 | 960.676 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -432.4943 | 528.1817 | -3550 | -400 | -3421.8183 | 85.55% | 66.24% | 95% | 0% | 1967 | -378
[5 empty] | 2019-05-19 | 31 | 3326.5 | 1641 | -359 | 1 | 0 | 2000 | 1012.366 | 1012.366 | 1012.366 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -410.7551 | 601.6109 | -3550 | -400 | -3348.3891 | 83.71% | 66.23% | 95% | 0% | 2000 | -359
[5 empty] | 2019-05-19 | 32 | 3327 | 1722 | -324 | 1 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -370.7094 | 713.7094 | -3550 | -400 | -3236.2906 | 80.91% | 66.23% | 95% | 0% | 2046 | -324
[5 empty] | 2019-05-19 | 33 | 3327.5 | 1814 | -273 | 1 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -312.357 | 836.2828 | -3550 | -400 | -3113.7172 | 77.84% | 66.23% | 95% | 0% | 2087 | -273
[5 empty] | 2019-05-19 | 34 | 3328 | 1897 | -256 | 1 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -292.9062 | 959.1136 | -3550 | -400 | -2990.8864 | 74.77% | 66.22% | 95% | 0% | 2153 | -256
[5 empty] | 2019-05-19 | 35 | 3328.5 | 2008 | -227 | 1 | 0 | 2235 | 1380.4617 | 1380.4617 | 1380.4617 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -259.7254 | 1120.7363 | -3550 | -400 | -2829.2637 | 70.73% | 66.22% | 95% | 0% | 2235 | -227
[5 empty] | 2019-05-19 | 36 | 3329 | 2063 | -200 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -228.833 | 1195.4869 | -3550 | -400 | -2754.5131 | 68.86% | 66.22% | 95% | 0% | 2263 | -200
[5 empty] | 2019-05-19 | 37 | 3329.5 | 2104 | -163 | 1 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -186.4989 | 1244.0865 | -3550 | -400 | -2705.9135 | 67.65% | 66.22% | 95% | 0% | 2267 | -163
[5 empty] | 2019-05-19 | 38 | 3330 | 2181 | -119 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -136.1556 | 1346.1197 | -3550 | -400 | -2603.8803 | 65.1% | 66.22% | 95% | 0% | 2300 | -119
[5 empty] | 2019-05-19 | 39 | 3330.5 | 2233 | -85 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -97.254 | 1413.2159 | -3550 | -400 | -2536.7841 | 63.42% | 66.21% | 95% | 0% | 2318 | -85
[5 empty] | 2019-05-19 | 40 | 3331 | 2247 | -63 | 1 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -72.0824 | 1425.8566 | -3550 | -400 | -2524.1434 | 63.1% | 66.21% | 95% | 0% | 2310 | -63
[5 empty] | 2019-05-19 | 41 | 3331.5 | 2256 | -45 | 1 | 0 | 2301 | 1483.8417 | 1483.8417 | 1483.8417 | 1618.5491 | 780 | 200 | 2598.5491 | 64.96% | 95% | 0% | -51.4874 | 1432.3543 | -3550 | -400 | -2517.6457 | 62.94% | 66.21% | 95% | 0% | 2301 | -45
[5 empty] | 2019-05-19 | 42 | 3332 | 2253 | -35 | 1 | 0 | 2288 | 1463.479 | 1463.479 | 1463.479 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -40.0458 | 1423.4332 | -3550 | -400 | -2526.5668 | 63.16% | 66.21% | 95% | 0% | 2288 | -35
[5 empty] | 2019-05-19 | 43 | 3332.5 | 2245 | -33 | 1 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -37.7574 | 1410.0579 | -3550 | -400 | -2539.9421 | 63.5% | 66.2% | 95% | 0% | 2278 | -33
[5 empty] | 2019-05-19 | 44 | 3333 | 2199 | -32 | 1 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -36.6133 | 1337.5829 | -3550 | -400 | -2612.4171 | 65.31% | 66.2% | 95% | 0% | 2231 | -32
[5 empty] | 2019-05-19 | 45 | 3333.5 | 2120 | -31 | 0 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -35.4691 | 1213.4179 | -2750 | -200 | -1736.5821 | 43.41% | 66.2% | 95% | 0% | 2151 | -31
[5 empty] | 2019-05-19 | 46 | 3334 | 1991 | -31 | 0 | 0 | 2022 | 1046.8261 | 1046.8261 | 1046.8261 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -35.4691 | 1011.3569 | -2750 | -200 | -1938.6431 | 48.47% | 66.19% | 95% | 0% | 2022 | -31
[5 empty] | 2019-05-19 | 47 | 3334.5 | 1854 | -30 | 0 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -34.3249 | 796.3428 | -2750 | -200 | -2153.6572 | 53.84% | 66.19% | 95% | 0% | 1884 | -30
[5 empty] | 2019-05-19 | 48 | 3335 | 1752 | -29 | 0 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -33.1808 | 636.1515 | -2750 | -200 | -2313.8485 | 57.85% | 66.18% | 95% | 0% | 1781 | -29
[5 empty] | 2019-05-20 | 1 | 3335.5 | 1677 | -29 | 0 | 0 | 1706 | 551.8549 | 551.8549 | 551.8549 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -33.1808 | 518.6741 | -2750 | -200 | -2431.3259 | 60.78% | 66.18% | 95% | 0% | 1706 | -29
[5 empty] | 2019-05-20 | 2 | 3336 | 1633 | -28 | 0 | 0 | 1661 | 481.3685 | 481.3685 | 481.3685 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -32.0366 | 449.3319 | -2750 | -200 | -2500.6681 | 62.52% | 66.18% | 95% | 0% | 1661 | -28
[5 empty] | 2019-05-20 | 3 | 3336.5 | 1614 | -28 | 0 | 0 | 1642 | 451.6076 | 451.6076 | 451.6076 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -32.0366 | 419.571 | -2750 | -200 | -2530.429 | 63.26% | 66.18% | 95% | 0% | 1642 | -28
[5 empty] | 2019-05-20 | 4 | 3337 | 1625 | -28 | 0 | 0 | 1653 | 468.8376 | 468.8376 | 468.8376 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -32.0366 | 436.801 | -2750 | -200 | -2513.199 | 62.83% | 66.17% | 95% | 0% | 1653 | -28
[5 empty] | 2019-05-20 | 5 | 3337.5 | 1609 | -29 | 0 | 0 | 1638 | 445.3421 | 445.3421 | 445.3421 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -33.1808 | 412.1613 | -2750 | -200 | -2537.8387 | 63.45% | 66.17% | 95% | 0% | 1638 | -29
[5 empty] | 2019-05-20 | 6 | 3338 | 1587 | -29 | 0 | 0 | 1616 | 410.8821 | 410.8821 | 410.8821 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -33.1808 | 377.7013 | -2750 | -200 | -2572.2987 | 64.31% | 66.17% | 95% | 0% | 1616 | -29
[5 empty] | 2019-05-20 | 7 | 3338.5 | 1569 | -30 | 0 | 0 | 1599 | 384.2539 | 384.2539 | 384.2539 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -34.3249 | 349.929 | -2750 | -200 | -2600.071 | 65% | 66.17% | 95% | 0% | 1599 | -30
[5 empty] | 2019-05-20 | 8 | 3339 | 1556 | -31 | 0 | 0 | 1587 | 365.4575 | 365.4575 | 365.4575 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -35.4691 | 329.9884 | -2750 | -200 | -2620.0116 | 65.5% | 66.17% | 95% | 0% | 1587 | -31
[5 empty] | 2019-05-20 | 9 | 3339.5 | 1553 | -32 | 0 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 1616.9827 | 780 | 200 | 2596.9827 | 64.92% | 95% | 0% | -36.6133 | 325.7115 | -2750 | -200 | -2624.2885 | 65.61% | 66.17% | 95% | 0% | 1585 | -32
[5 empty] | 2019-05-20 | 10 | 3340 | 1548 | -34 | 0 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 1615.4163 | 780 | 200 | 2595.4163 | 64.89% | 95% | 0% | -38.9016 | 318.7241 | -2750 | -200 | -2631.2759 | 65.78% | 66.17% | 95% | 0% | 1582 | -34
[5 empty] | 2019-05-20 | 11 | 3340.5 | 1584 | -35 | 0 | 0 | 1619 | 415.5812 | 415.5812 | 415.5812 | 1615.4163 | 780 | 200 | 2595.4163 | 64.89% | 95% | 0% | -40.0458 | 375.5354 | -2750 | -200 | -2574.4646 | 64.36% | 66.17% | 95% | 0% | 1619 | -35
[5 empty] | 2019-05-20 | 12 | 3341 | 1654 | -41 | 0 | 0 | 1695 | 534.6249 | 534.6249 | 534.6249 | 1615.4163 | 780 | 200 | 2595.4163 | 64.89% | 95% | 0% | -46.9108 | 487.7141 | -2750 | -200 | -2462.2859 | 61.56% | 66.16% | 95% | 0% | 1695 | -41
[5 empty] | 2019-05-20 | 13 | 3341.5 | 1836 | -63 | 0 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 1615.4163 | 780 | 200 | 2595.4163 | 64.89% | 95% | 0% | -72.0824 | 782.0809 | -2750 | -200 | -2167.9191 | 54.2% | 66.16% | 95% | 0% | 1899 | -63
[5 empty] | 2019-05-20 | 14 | 3342 | 1986 | -95 | 1 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 1615.4163 | 780 | 200 | 2595.4163 | 64.89% | 95% | 0% | -108.6957 | 1030.5459 | -3550 | -400 | -2919.4541 | 72.99% | 66.16% | 95% | 0% | 2081 | -95
[5 empty] | 2019-05-20 | 15 | 3342.5 | 2133 | -133 | 1 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 1615.4163 | 780 | 200 | 2595.4163 | 64.89% | 95% | 0% | -152.1739 | 1276.845 | -3550 | -400 | -2673.155 | 66.83% | 66.16% | 95% | 0% | 2266 | -133
[5 empty] | 2019-05-20 | 16 | 3343 | 2162 | -184 | 1 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 1615.4163 | 780 | 200 | 2595.4163 | 64.89% | 95% | 0% | -210.5263 | 1343.8018 | -3550 | -400 | -2606.1982 | 65.15% | 66.15% | 95% | 0% | 2346 | -184
[5 empty] | 2019-05-20 | 17 | 3343.5 | 2172 | -236 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 1615.4163 | 780 | 200 | 2595.4163 | 64.89% | 95% | 0% | -270.0229 | 1381.4198 | -3550 | -400 | -2568.5802 | 64.21% | 66.15% | 95% | 0% | 2408 | -236
[5 empty] | 2019-05-20 | 18 | 3344 | 2105 | -294 | 1 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -336.3844 | 1300.961 | -3550 | -400 | -2649.039 | 66.23% | 66.15% | 95% | 0% | 2399 | -294
[5 empty] | 2019-05-20 | 19 | 3344.5 | 2020 | -361 | 1 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -413.0435 | 1196.1074 | -3550 | -400 | -2753.8926 | 68.85% | 66.15% | 95% | 0% | 2381 | -361
[5 empty] | 2019-05-20 | 20 | 3345 | 1941 | -423 | 1 | 0 | 2364 | 1582.5227 | 1582.5227 | 1582.5227 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -483.9817 | 1098.541 | -3550 | -400 | -2851.459 | 71.29% | 66.15% | 95% | 0% | 2364 | -423
[5 empty] | 2019-05-20 | 21 | 3345.5 | 1856 | -457 | 1 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -522.8833 | 979.7548 | -3550 | -400 | -2970.2452 | 74.26% | 66.14% | 95% | 0% | 2313 | -457
[5 empty] | 2019-05-20 | 22 | 3346 | 1790 | -499 | 1 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -570.9382 | 894.1071 | -3550 | -400 | -3055.8929 | 76.4% | 66.14% | 95% | 0% | 2289 | -499
[5 empty] | 2019-05-20 | 23 | 3346.5 | 1734 | -539 | 1 | 0 | 2273 | 1439.9835 | 1439.9835 | 1439.9835 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -616.7048 | 823.2787 | -3550 | -400 | -3126.7213 | 78.17% | 66.13% | 95% | 0% | 2273 | -539
[5 empty] | 2019-05-20 | 24 | 3347 | 1720 | -547 | 1 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -625.8581 | 804.7272 | -3550 | -400 | -3145.2728 | 78.63% | 66.13% | 95% | 0% | 2267 | -547
[5 empty] | 2019-05-20 | 25 | 3347.5 | 1695 | -554 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -633.8673 | 768.5235 | -3550 | -400 | -3181.4765 | 79.54% | 66.13% | 95% | 0% | 2249 | -554
[5 empty] | 2019-05-20 | 26 | 3348 | 1677 | -560 | 1 | 0 | 2237 | 1383.5944 | 1383.5944 | 1383.5944 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -640.7323 | 742.8621 | -3550 | -400 | -3207.1379 | 80.18% | 66.13% | 95% | 0% | 2237 | -560
[5 empty] | 2019-05-20 | 27 | 3348.5 | 1656 | -569 | 1 | 0 | 2225 | 1364.798 | 1364.798 | 1364.798 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -651.0297 | 713.7683 | -3550 | -400 | -3236.2317 | 80.91% | 66.13% | 95% | 0% | 2225 | -569
[5 empty] | 2019-05-20 | 28 | 3349 | 1693 | -515 | 1 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -589.2449 | 748.925 | -3550 | -400 | -3201.075 | 80.03% | 66.13% | 95% | 0% | 2208 | -515
[5 empty] | 2019-05-20 | 29 | 3349.5 | 1690 | -523 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -598.3982 | 747.6035 | -3550 | -400 | -3202.3965 | 80.06% | 66.12% | 95% | 0% | 2213 | -523
[5 empty] | 2019-05-20 | 30 | 3350 | 1727 | -497 | 1 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -568.6499 | 794.5818 | -3550 | -400 | -3155.4182 | 78.89% | 66.12% | 95% | 0% | 2224 | -497
[5 empty] | 2019-05-20 | 31 | 3350.5 | 1775 | -450 | 1 | 0 | 2225 | 1364.798 | 1364.798 | 1364.798 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -514.8741 | 849.9239 | -3550 | -400 | -3100.0761 | 77.5% | 66.12% | 95% | 0% | 2225 | -450
[5 empty] | 2019-05-20 | 32 | 3351 | 1835 | -420 | 1 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -480.5492 | 931.2398 | -3550 | -400 | -3018.7602 | 75.47% | 66.11% | 95% | 0% | 2255 | -420
[5 empty] | 2019-05-20 | 33 | 3351.5 | 1942 | -391 | 1 | 0 | 2333 | 1533.9654 | 1533.9654 | 1533.9654 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -447.3684 | 1086.597 | -3550 | -400 | -2863.403 | 71.59% | 66.11% | 95% | 0% | 2333 | -391
[5 empty] | 2019-05-20 | 34 | 3352 | 2052 | -345 | 1 | 0 | 2397 | 1634.2127 | 1634.2127 | 1634.2127 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -394.7368 | 1239.4759 | -3550 | -400 | -2710.5241 | 67.76% | 66.1% | 95% | 0% | 2397 | -345
[5 empty] | 2019-05-20 | 35 | 3352.5 | 2138 | -309 | 1 | 0 | 2447 | 1712.5309 | 1712.5309 | 1712.5309 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -353.5469 | 1358.984 | -3550 | -400 | -2591.016 | 64.78% | 66.1% | 95% | 0% | 2447 | -309
[5 empty] | 2019-05-20 | 36 | 3353 | 2216 | -269 | 1 | 0 | 2485 | 1772.0528 | 1772.0528 | 1772.0528 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -307.7803 | 1464.2724 | -3550 | -400 | -2485.7276 | 62.14% | 66.09% | 95% | 0% | 2485 | -269
[5 empty] | 2019-05-20 | 37 | 3353.5 | 2273 | -223 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 1613.85 | 780 | 200 | 2593.85 | 64.85% | 95% | 0% | -255.1487 | 1534.134 | -3550 | -400 | -2415.866 | 60.4% | 66.09% | 95% | 0% | 2496 | -223
[5 empty] | 2019-05-20 | 38 | 3354 | 2337 | -177 | 1 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -202.5172 | 1614.9602 | -3550 | -400 | -2335.0398 | 58.38% | 66.08% | 95% | 0% | 2514 | -177
[5 empty] | 2019-05-20 | 39 | 3354.5 | 2400 | -134 | 1 | 0 | 2534 | 1848.8046 | 1848.8046 | 1848.8046 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -153.3181 | 1695.4865 | -3550 | -400 | -2254.5135 | 56.36% | 66.08% | 95% | 0% | 2534 | -134
[5 empty] | 2019-05-20 | 40 | 3355 | 2411 | -90 | 1 | 0 | 2501 | 1797.1146 | 1797.1146 | 1797.1146 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -102.9748 | 1694.1398 | -3550 | -400 | -2255.8602 | 56.4% | 66.07% | 95% | 0% | 2501 | -90
[5 empty] | 2019-05-20 | 41 | 3355.5 | 2426 | -60 | 1 | 0 | 2486 | 1773.6191 | 1773.6191 | 1773.6191 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -68.6499 | 1704.9692 | -3550 | -400 | -2245.0308 | 56.13% | 66.07% | 95% | 0% | 2486 | -60
[5 empty] | 2019-05-20 | 42 | 3356 | 2431 | -43 | 1 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -49.1991 | 1705.6237 | -3550 | -400 | -2244.3763 | 56.11% | 66.06% | 95% | 0% | 2474 | -43
[5 empty] | 2019-05-20 | 43 | 3356.5 | 2405 | -40 | 1 | 0 | 2445 | 1709.3982 | 1709.3982 | 1709.3982 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -45.7666 | 1663.6316 | -3550 | -400 | -2286.3684 | 57.16% | 66.06% | 95% | 0% | 2445 | -40
[5 empty] | 2019-05-20 | 44 | 3357 | 2348 | -39 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -44.6224 | 1573.9266 | -3550 | -400 | -2376.0734 | 59.4% | 66.06% | 95% | 0% | 2387 | -39
[5 empty] | 2019-05-20 | 45 | 3357.5 | 2224 | -39 | 0 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -44.6224 | 1379.6974 | -2750 | -200 | -1570.3026 | 39.26% | 66.06% | 95% | 0% | 2263 | -39
[5 empty] | 2019-05-20 | 46 | 3358 | 2084 | -38 | 0 | 0 | 2122 | 1203.4625 | 1203.4625 | 1203.4625 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -43.4783 | 1159.9842 | -2750 | -200 | -1790.0158 | 44.75% | 66.05% | 95% | 0% | 2122 | -38
[5 empty] | 2019-05-20 | 47 | 3358.5 | 1945 | -38 | 0 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -43.4783 | 942.2596 | -2750 | -200 | -2007.7404 | 50.19% | 66.05% | 95% | 0% | 1983 | -38
[5 empty] | 2019-05-20 | 48 | 3359 | 1824 | -39 | 0 | 0 | 1863 | 797.7741 | 797.7741 | 797.7741 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -44.6224 | 753.1517 | -2750 | -200 | -2196.8483 | 54.92% | 66.05% | 95% | 0% | 1863 | -39
[5 empty] | 2019-05-21 | 1 | 3359.5 | 1819 | -39 | 1 | 0 | 1858 | 789.9423 | 789.9423 | 789.9423 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -44.6224 | 745.3199 | -3550 | -400 | -3204.6801 | 80.12% | 66.05% | 95% | 0% | 1858 | -39
[5 empty] | 2019-05-21 | 2 | 3360 | 1686 | -38 | 1 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 1612.2836 | 780 | 200 | 2592.2836 | 64.81% | 95% | 0% | -43.4783 | 536.5712 | -3550 | -400 | -3413.4288 | 85.34% | 66.04% | 95% | 0% | 1724 | -38
[5 empty] | 2019-05-21 | 3 | 3360.5 | 1661 | -39 | 1 | 0 | 1700 | 542.4567 | 542.4567 | 542.4567 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -44.6224 | 497.8343 | -3550 | -400 | -3452.1657 | 86.3% | 66.04% | 95% | 0% | 1700 | -39
[5 empty] | 2019-05-21 | 4 | 3361 | 1659 | -40 | 1 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -45.7666 | 495.1238 | -3550 | -400 | -3454.8762 | 86.37% | 66.04% | 95% | 0% | 1699 | -40
[5 empty] | 2019-05-21 | 5 | 3361.5 | 1637 | -41 | 1 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -46.9108 | 461.0859 | -3550 | -400 | -3488.9141 | 87.22% | 66.04% | 95% | 0% | 1678 | -41
[5 empty] | 2019-05-21 | 6 | 3362 | 1612 | -42 | 1 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -48.0549 | 422.349 | -3550 | -400 | -3527.651 | 88.19% | 66.03% | 95% | 0% | 1654 | -42
[5 empty] | 2019-05-21 | 7 | 3362.5 | 1592 | -44 | 1 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -50.3432 | 391.8661 | -3550 | -400 | -3558.1339 | 88.95% | 66.03% | 95% | 0% | 1636 | -44
[5 empty] | 2019-05-21 | 8 | 3363 | 1579 | -45 | 1 | 0 | 1624 | 423.413 | 423.413 | 423.413 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -51.4874 | 371.9256 | -3550 | -400 | -3578.0744 | 89.45% | 66.03% | 95% | 0% | 1624 | -45
[5 empty] | 2019-05-21 | 9 | 3363.5 | 1576 | -46 | 1 | 0 | 1622 | 420.2803 | 420.2803 | 420.2803 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -52.6316 | 367.6487 | -3550 | -400 | -3582.3513 | 89.56% | 66.03% | 95% | 0% | 1622 | -46
[5 empty] | 2019-05-21 | 10 | 3364 | 1565 | -47 | 1 | 0 | 1612 | 404.6167 | 404.6167 | 404.6167 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -53.7757 | 350.8409 | -3550 | -400 | -3599.1591 | 89.98% | 66.02% | 95% | 0% | 1612 | -47
[5 empty] | 2019-05-21 | 11 | 3364.5 | 1591 | -49 | 1 | 0 | 1640 | 448.4749 | 448.4749 | 448.4749 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -56.0641 | 392.4108 | -3550 | -400 | -3557.5892 | 88.94% | 66.01% | 95% | 0% | 1640 | -49
[5 empty] | 2019-05-21 | 12 | 3365 | 1645 | -66 | 1 | 0 | 1711 | 559.6867 | 559.6867 | 559.6867 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -75.5149 | 484.1719 | -3550 | -400 | -3465.8281 | 86.65% | 66.01% | 95% | 0% | 1711 | -66
[5 empty] | 2019-05-21 | 13 | 3365.5 | 1792 | -103 | 1 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -117.849 | 730.0488 | -3550 | -400 | -3219.9512 | 80.5% | 66.01% | 95% | 0% | 1895 | -103
[5 empty] | 2019-05-21 | 14 | 3366 | 1930 | -152 | 1 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -173.913 | 966.8949 | -3550 | -400 | -2983.1051 | 74.58% | 66.01% | 95% | 0% | 2082 | -152
[5 empty] | 2019-05-21 | 15 | 3366.5 | 2048 | -204 | 1 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -233.4096 | 1173.6802 | -3550 | -400 | -2776.3198 | 69.41% | 66.01% | 95% | 0% | 2252 | -204
[5 empty] | 2019-05-21 | 16 | 3367 | 2020 | -265 | 1 | 0 | 2285 | 1458.7799 | 1458.7799 | 1458.7799 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -303.2037 | 1155.5762 | -3550 | -400 | -2794.4238 | 69.86% | 66.01% | 95% | 0% | 2285 | -265
[5 empty] | 2019-05-21 | 17 | 3367.5 | 1982 | -342 | 1 | 0 | 2324 | 1519.8681 | 1519.8681 | 1519.8681 | 1610.7172 | 780 | 200 | 2590.7172 | 64.77% | 95% | 0% | -391.3043 | 1128.5637 | -3550 | -400 | -2821.4363 | 70.54% | 66% | 95% | 0% | 2324 | -342
[5 empty] | 2019-05-21 | 18 | 3368 | 1872 | -415 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -474.8284 | 987.0842 | -3550 | -400 | -2962.9158 | 74.07% | 66% | 95% | 0% | 2287 | -415
[5 empty] | 2019-05-21 | 19 | 3368.5 | 1739 | -478 | 1 | 0 | 2217 | 1352.2671 | 1352.2671 | 1352.2671 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -546.9108 | 805.3564 | -3550 | -400 | -3144.6436 | 78.62% | 66% | 95% | 0% | 2217 | -478
[5 empty] | 2019-05-21 | 20 | 3369 | 1650 | -545 | 1 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -623.5698 | 694.2373 | -3550 | -400 | -3255.7627 | 81.39% | 66% | 95% | 0% | 2195 | -545
[5 empty] | 2019-05-21 | 21 | 3369.5 | 1545 | -600 | 1 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -686.4989 | 552.99 | -3550 | -400 | -3397.01 | 84.93% | 66% | 95% | 0% | 2145 | -600
[5 empty] | 2019-05-21 | 22 | 3370 | 1483 | -633 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -724.2563 | 469.808 | -3550 | -400 | -3480.192 | 87% | 65.99% | 95% | 0% | 2116 | -633
[5 empty] | 2019-05-21 | 23 | 3370.5 | 1444 | -657 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -751.7162 | 418.8526 | -3550 | -400 | -3531.1474 | 88.28% | 65.99% | 95% | 0% | 2101 | -657
[5 empty] | 2019-05-21 | 24 | 3371 | 1426 | -677 | 1 | 0 | 2103 | 1173.7016 | 1173.7016 | 1173.7016 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -774.5995 | 399.102 | -3550 | -400 | -3550.898 | 88.77% | 65.99% | 95% | 0% | 2103 | -677
[5 empty] | 2019-05-21 | 25 | 3371.5 | 1405 | -706 | 1 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -807.7803 | 378.4522 | -3550 | -400 | -3571.5478 | 89.29% | 65.98% | 95% | 0% | 2111 | -706
[5 empty] | 2019-05-21 | 26 | 3372 | 1379 | -716 | 1 | 0 | 2095 | 1161.1707 | 1161.1707 | 1161.1707 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -819.222 | 341.9487 | -3550 | -400 | -3608.0513 | 90.2% | 65.98% | 95% | 0% | 2095 | -716
[5 empty] | 2019-05-21 | 27 | 3372.5 | 1367 | -709 | 1 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -811.2128 | 320.1969 | -3550 | -400 | -3629.8031 | 90.75% | 65.98% | 95% | 0% | 2076 | -709
[5 empty] | 2019-05-21 | 28 | 3373 | 1371 | -690 | 1 | 0 | 2061 | 1107.9143 | 1107.9143 | 1107.9143 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -789.4737 | 318.4406 | -3550 | -400 | -3631.5594 | 90.79% | 65.97% | 95% | 0% | 2061 | -690
[5 empty] | 2019-05-21 | 29 | 3373.5 | 1358 | -693 | 1 | 0 | 2051 | 1092.2506 | 1092.2506 | 1092.2506 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -792.9062 | 299.3444 | -3550 | -400 | -3650.6556 | 91.27% | 65.97% | 95% | 0% | 2051 | -693
[5 empty] | 2019-05-21 | 30 | 3374 | 1381 | -666 | 1 | 0 | 2047 | 1085.9852 | 1085.9852 | 1085.9852 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -762.0137 | 323.9714 | -3550 | -400 | -3626.0286 | 90.65% | 65.97% | 95% | 0% | 2047 | -666
[5 empty] | 2019-05-21 | 31 | 3374.5 | 1442 | -615 | 1 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -703.6613 | 397.9875 | -3550 | -400 | -3552.0125 | 88.8% | 65.97% | 95% | 0% | 2057 | -615
[5 empty] | 2019-05-21 | 32 | 3375 | 1537 | -568 | 1 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -649.8856 | 526.9487 | -3550 | -400 | -3423.0513 | 85.58% | 65.96% | 95% | 0% | 2105 | -568
[5 empty] | 2019-05-21 | 33 | 3375.5 | 1667 | -511 | 1 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -584.6682 | 706.5107 | -3550 | -400 | -3243.4893 | 81.09% | 65.96% | 95% | 0% | 2178 | -511
[5 empty] | 2019-05-21 | 34 | 3376 | 1781 | -476 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 1609.1509 | 780 | 200 | 2589.1509 | 64.73% | 95% | 0% | -544.6224 | 870.2993 | -3550 | -400 | -3079.7007 | 76.99% | 65.95% | 95% | 0% | 2257 | -476
[5 empty] | 2019-05-21 | 35 | 3376.5 | 1925 | -410 | 1 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 1607.5845 | 780 | 200 | 2587.5845 | 64.69% | 95% | 0% | -469.1076 | 1067.9906 | -3550 | -400 | -2882.0094 | 72.05% | 65.95% | 95% | 0% | 2335 | -410
[5 empty] | 2019-05-21 | 36 | 3377 | 2035 | -351 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 1607.5845 | 780 | 200 | 2587.5845 | 64.69% | 95% | 0% | -401.6018 | 1215.3809 | -3550 | -400 | -2734.6191 | 68.37% | 65.95% | 95% | 0% | 2386 | -351
[5 empty] | 2019-05-21 | 37 | 3377.5 | 2131 | -289 | 1 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 1607.5845 | 780 | 200 | 2587.5845 | 64.69% | 95% | 0% | -330.6636 | 1339.5755 | -3550 | -400 | -2610.4245 | 65.26% | 65.95% | 95% | 0% | 2420 | -289
[5 empty] | 2019-05-21 | 38 | 3378 | 2214 | -227 | 1 | 0 | 2441 | 1703.1327 | 1703.1327 | 1703.1327 | 1607.5845 | 780 | 200 | 2587.5845 | 64.69% | 95% | 0% | -259.7254 | 1443.4073 | -3550 | -400 | -2506.5927 | 62.66% | 65.94% | 95% | 0% | 2441 | -227
[5 empty] | 2019-05-21 | 39 | 3378.5 | 2274 | -169 | 1 | 0 | 2443 | 1706.2655 | 1706.2655 | 1706.2655 | 1607.5845 | 780 | 200 | 2587.5845 | 64.69% | 95% | 0% | -193.3638 | 1512.9016 | -3550 | -400 | -2437.0984 | 60.93% | 65.94% | 95% | 0% | 2443 | -169
[5 empty] | 2019-05-21 | 40 | 3379 | 2324 | -117 | 1 | 0 | 2441 | 1703.1327 | 1703.1327 | 1703.1327 | 1607.5845 | 780 | 200 | 2587.5845 | 64.69% | 95% | 0% | -133.8673 | 1569.2655 | -3550 | -400 | -2380.7345 | 59.52% | 65.94% | 95% | 0% | 2441 | -117
[5 empty] | 2019-05-21 | 41 | 3379.5 | 2348 | -79 | 1 | 0 | 2427 | 1681.2036 | 1681.2036 | 1681.2036 | 1607.5845 | 780 | 200 | 2587.5845 | 64.69% | 95% | 0% | -90.389 | 1590.8146 | -3550 | -400 | -2359.1854 | 58.98% | 65.94% | 95% | 0% | 2427 | -79
[5 empty] | 2019-05-21 | 42 | 3380 | 2372 | -54 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1607.5845 | 780 | 200 | 2587.5845 | 64.69% | 95% | 0% | -61.7849 | 1617.8524 | -3550 | -400 | -2332.1476 | 58.3% | 65.94% | 95% | 0% | 2426 | -54
[5 empty] | 2019-05-21 | 43 | 3380.5 | 2338 | -49 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 1606.0181 | 780 | 200 | 2586.0181 | 64.65% | 95% | 0% | -56.0641 | 1562.485 | -3550 | -400 | -2387.515 | 59.69% | 65.94% | 95% | 0% | 2387 | -49
[5 empty] | 2019-05-21 | 44 | 3381 | 2319 | -48 | 1 | 0 | 2367 | 1587.2218 | 1587.2218 | 1587.2218 | 1606.0181 | 780 | 200 | 2586.0181 | 64.65% | 95% | 0% | -54.9199 | 1532.3019 | -3550 | -400 | -2417.6981 | 60.44% | 65.93% | 95% | 0% | 2367 | -48
[5 empty] | 2019-05-21 | 45 | 3381.5 | 2230 | -47 | 0 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 1606.0181 | 780 | 200 | 2586.0181 | 64.65% | 95% | 0% | -53.7757 | 1392.4732 | -2750 | -200 | -1557.5268 | 38.94% | 65.93% | 95% | 0% | 2277 | -47
[5 empty] | 2019-05-21 | 46 | 3382 | 2098 | -46 | 0 | 0 | 2144 | 1237.9225 | 1237.9225 | 1237.9225 | 1606.0181 | 780 | 200 | 2586.0181 | 64.65% | 95% | 0% | -52.6316 | 1185.2909 | -2750 | -200 | -1764.7091 | 44.12% | 65.93% | 95% | 0% | 2144 | -46
[5 empty] | 2019-05-21 | 47 | 3382.5 | 1946 | -45 | 0 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1606.0181 | 780 | 200 | 2586.0181 | 64.65% | 95% | 0% | -51.4874 | 946.7813 | -2750 | -200 | -2003.2187 | 50.08% | 65.92% | 95% | 0% | 1991 | -45
[5 empty] | 2019-05-21 | 48 | 3383 | 1820 | -45 | 0 | 0 | 1865 | 800.9068 | 800.9068 | 800.9068 | 1606.0181 | 780 | 200 | 2586.0181 | 64.65% | 95% | 0% | -51.4874 | 749.4194 | -2750 | -200 | -2200.5806 | 55.01% | 65.92% | 95% | 0% | 1865 | -45
[5 empty] | 2019-05-22 | 1 | 3383.5 | 1729 | -43 | 0 | 0 | 1772 | 655.235 | 655.235 | 655.235 | 1606.0181 | 780 | 200 | 2586.0181 | 64.65% | 95% | 0% | -49.1991 | 606.0359 | -2750 | -200 | -2343.9641 | 58.6% | 65.92% | 95% | 0% | 1772 | -43
[5 empty] | 2019-05-22 | 2 | 3384 | 1681 | -40 | 0 | 0 | 1721 | 575.3504 | 575.3504 | 575.3504 | 1606.0181 | 780 | 200 | 2586.0181 | 64.65% | 95% | 0% | -45.7666 | 529.5838 | -2750 | -200 | -2420.4162 | 60.51% | 65.92% | 95% | 0% | 1721 | -40
[5 empty] | 2019-05-22 | 3 | 3384.5 | 1653 | -42 | 0 | 0 | 1695 | 534.6249 | 534.6249 | 534.6249 | 1606.0181 | 780 | 200 | 2586.0181 | 64.65% | 95% | 0% | -48.0549 | 486.57 | -2750 | -200 | -2463.43 | 61.59% | 65.92% | 95% | 0% | 1695 | -42
[5 empty] | 2019-05-22 | 4 | 3385 | 1652 | -43 | 0 | 0 | 1695 | 534.6249 | 534.6249 | 534.6249 | 1606.0181 | 780 | 200 | 2586.0181 | 64.65% | 95% | 0% | -49.1991 | 485.4258 | -2750 | -200 | -2464.5742 | 61.61% | 65.92% | 95% | 0% | 1695 | -43
[5 empty] | 2019-05-22 | 5 | 3385.5 | 1625 | -45 | 0 | 0 | 1670 | 495.4658 | 495.4658 | 495.4658 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -51.4874 | 443.9784 | -2750 | -200 | -2506.0216 | 62.65% | 65.91% | 95% | 0% | 1670 | -45
[5 empty] | 2019-05-22 | 6 | 3386 | 1591 | -46 | 0 | 0 | 1637 | 443.7758 | 443.7758 | 443.7758 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -52.6316 | 391.1442 | -2750 | -200 | -2558.8558 | 63.97% | 65.91% | 95% | 0% | 1637 | -46
[5 empty] | 2019-05-22 | 7 | 3386.5 | 1579 | -48 | 0 | 0 | 1627 | 428.1121 | 428.1121 | 428.1121 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -54.9199 | 373.1922 | -2750 | -200 | -2576.8078 | 64.42% | 65.91% | 95% | 0% | 1627 | -48
[5 empty] | 2019-05-22 | 8 | 3387 | 1567 | -50 | 0 | 0 | 1617 | 412.4485 | 412.4485 | 412.4485 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -57.2082 | 355.2402 | -2750 | -200 | -2594.7598 | 64.87% | 65.91% | 95% | 0% | 1617 | -50
[5 empty] | 2019-05-22 | 9 | 3387.5 | 1571 | -50 | 0 | 0 | 1621 | 418.7139 | 418.7139 | 418.7139 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -57.2082 | 361.5057 | -2750 | -200 | -2588.4943 | 64.71% | 65.91% | 95% | 0% | 1621 | -50
[5 empty] | 2019-05-22 | 10 | 3388 | 1567 | -51 | 0 | 0 | 1618 | 414.0148 | 414.0148 | 414.0148 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -58.3524 | 355.6624 | -2750 | -200 | -2594.3376 | 64.86% | 65.9% | 95% | 0% | 1618 | -51
[5 empty] | 2019-05-22 | 11 | 3388.5 | 1587 | -55 | 0 | 0 | 1642 | 451.6076 | 451.6076 | 451.6076 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -62.9291 | 388.6785 | -2750 | -200 | -2561.3215 | 64.03% | 65.9% | 95% | 0% | 1642 | -55
[5 empty] | 2019-05-22 | 12 | 3389 | 1639 | -71 | 0 | 0 | 1710 | 558.1204 | 558.1204 | 558.1204 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -81.2357 | 476.8847 | -2750 | -200 | -2473.1153 | 61.83% | 65.9% | 95% | 0% | 1710 | -71
[5 empty] | 2019-05-22 | 13 | 3389.5 | 1793 | -103 | 0 | 0 | 1896 | 849.4641 | 849.4641 | 849.4641 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -117.849 | 731.6152 | -2750 | -200 | -2218.3848 | 55.46% | 65.89% | 95% | 0% | 1896 | -103
[5 empty] | 2019-05-22 | 14 | 3390 | 1940 | -136 | 1 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -155.6064 | 975.8033 | -3550 | -400 | -2974.1967 | 74.35% | 65.89% | 95% | 0% | 2076 | -136
[5 empty] | 2019-05-22 | 15 | 3390.5 | 2077 | -188 | 1 | 0 | 2265 | 1427.4526 | 1427.4526 | 1427.4526 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -215.103 | 1212.3496 | -3550 | -400 | -2737.6504 | 68.44% | 65.89% | 95% | 0% | 2265 | -188
[5 empty] | 2019-05-22 | 16 | 3391 | 2074 | -247 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -282.6087 | 1232.5603 | -3550 | -400 | -2717.4397 | 67.94% | 65.88% | 95% | 0% | 2321 | -247
[5 empty] | 2019-05-22 | 17 | 3391.5 | 2022 | -305 | 1 | 0 | 2327 | 1524.5672 | 1524.5672 | 1524.5672 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -348.9703 | 1175.5969 | -3550 | -400 | -2774.4031 | 69.36% | 65.88% | 95% | 0% | 2327 | -305
[5 empty] | 2019-05-22 | 18 | 3392 | 1931 | -378 | 1 | 0 | 2309 | 1496.3726 | 1496.3726 | 1496.3726 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -432.4943 | 1063.8784 | -3550 | -400 | -2886.1216 | 72.15% | 65.88% | 95% | 0% | 2309 | -378
[5 empty] | 2019-05-22 | 19 | 3392.5 | 1842 | -454 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -519.4508 | 956.5591 | -3550 | -400 | -2993.4409 | 74.84% | 65.88% | 95% | 0% | 2296 | -454
[5 empty] | 2019-05-22 | 20 | 3393 | 1765 | -492 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 1604.4518 | 780 | 200 | 2584.4518 | 64.61% | 95% | 0% | -562.9291 | 851.9926 | -3550 | -400 | -3098.0074 | 77.45% | 65.87% | 95% | 0% | 2257 | -492
[5 empty] | 2019-05-22 | 21 | 3393.5 | 1664 | -552 | 1 | 0 | 2216 | 1350.7007 | 1350.7007 | 1350.7007 | 1602.8854 | 780 | 200 | 2582.8854 | 64.57% | 95% | 0% | -631.5789 | 719.1218 | -3550 | -400 | -3230.8782 | 80.77% | 65.86% | 95% | 0% | 2216 | -552
[5 empty] | 2019-05-22 | 22 | 3394 | 1568 | -615 | 1 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 1602.8854 | 780 | 200 | 2582.8854 | 64.57% | 95% | 0% | -703.6613 | 595.3494 | -3550 | -400 | -3354.6506 | 83.87% | 65.86% | 95% | 0% | 2183 | -615
[5 empty] | 2019-05-22 | 23 | 3394.5 | 1511 | -662 | 1 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 1602.8854 | 780 | 200 | 2582.8854 | 64.57% | 95% | 0% | -757.4371 | 525.91 | -3550 | -400 | -3424.09 | 85.6% | 65.85% | 95% | 0% | 2173 | -662
[5 empty] | 2019-05-22 | 24 | 3395 | 1512 | -658 | 1 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 1602.8854 | 780 | 200 | 2582.8854 | 64.57% | 95% | 0% | -752.8604 | 525.7876 | -3550 | -400 | -3424.2124 | 85.61% | 65.85% | 95% | 0% | 2170 | -658
[5 empty] | 2019-05-22 | 25 | 3395.5 | 1495 | -663 | 1 | 0 | 2158 | 1259.8516 | 1259.8516 | 1259.8516 | 1602.8854 | 780 | 200 | 2582.8854 | 64.57% | 95% | 0% | -758.5812 | 501.2704 | -3550 | -400 | -3448.7296 | 86.22% | 65.85% | 95% | 0% | 2158 | -663
[5 empty] | 2019-05-22 | 26 | 3396 | 1479 | -648 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 1602.8854 | 780 | 200 | 2582.8854 | 64.57% | 95% | 0% | -741.4188 | 469.8755 | -3550 | -400 | -3480.1245 | 87% | 65.85% | 95% | 0% | 2127 | -648
[5 empty] | 2019-05-22 | 27 | 3396.5 | 1419 | -679 | 1 | 0 | 2098 | 1165.8697 | 1165.8697 | 1165.8697 | 1601.319 | 780 | 200 | 2581.319 | 64.53% | 95% | 0% | -776.8879 | 388.9819 | -3550 | -400 | -3561.0181 | 89.03% | 65.84% | 95% | 0% | 2098 | -679
[5 empty] | 2019-05-22 | 28 | 3397 | 1397 | -677 | 1 | 0 | 2074 | 1128.277 | 1128.277 | 1128.277 | 1601.319 | 780 | 200 | 2581.319 | 64.53% | 95% | 0% | -774.5995 | 353.6775 | -3550 | -400 | -3596.3225 | 89.91% | 65.84% | 95% | 0% | 2074 | -677
[5 empty] | 2019-05-22 | 29 | 3397.5 | 1384 | -680 | 1 | 0 | 2064 | 1112.6134 | 1112.6134 | 1112.6134 | 1601.319 | 780 | 200 | 2581.319 | 64.53% | 95% | 0% | -778.032 | 334.5813 | -3550 | -400 | -3615.4187 | 90.39% | 65.83% | 95% | 0% | 2064 | -680
[5 empty] | 2019-05-22 | 30 | 3398 | 1377 | -666 | 1 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 1601.319 | 780 | 200 | 2581.319 | 64.53% | 95% | 0% | -762.0137 | 317.706 | -3550 | -400 | -3632.294 | 90.81% | 65.82% | 95% | 0% | 2043 | -666
[5 empty] | 2019-05-22 | 31 | 3398.5 | 1395 | -651 | 1 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1601.319 | 780 | 200 | 2581.319 | 64.53% | 95% | 0% | -744.8513 | 339.5675 | -3550 | -400 | -3610.4325 | 90.26% | 65.82% | 95% | 0% | 2046 | -651
[5 empty] | 2019-05-22 | 32 | 3399 | 1484 | -606 | 1 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 1601.319 | 780 | 200 | 2581.319 | 64.53% | 95% | 0% | -693.3638 | 459.975 | -3550 | -400 | -3490.025 | 87.25% | 65.82% | 95% | 0% | 2090 | -606
[5 empty] | 2019-05-22 | 33 | 3399.5 | 1599 | -556 | 1 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 1601.319 | 780 | 200 | 2581.319 | 64.53% | 95% | 0% | -636.1556 | 618.9969 | -3550 | -400 | -3331.0031 | 83.28% | 65.82% | 95% | 0% | 2155 | -556
[5 empty] | 2019-05-22 | 34 | 3400 | 1730 | -505 | 1 | 0 | 2235 | 1380.4617 | 1380.4617 | 1380.4617 | 1601.319 | 780 | 200 | 2581.319 | 64.53% | 95% | 0% | -577.8032 | 802.6585 | -3550 | -400 | -3147.3415 | 78.68% | 65.81% | 95% | 0% | 2235 | -505
[5 empty] | 2019-05-22 | 35 | 3400.5 | 1860 | -439 | 1 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 1601.319 | 780 | 200 | 2581.319 | 64.53% | 95% | 0% | -502.2883 | 978.4207 | -3550 | -400 | -2971.5793 | 74.29% | 65.81% | 95% | 0% | 2299 | -439
[5 empty] | 2019-05-22 | 36 | 3401 | 1959 | -382 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 1601.319 | 780 | 200 | 2581.319 | 64.53% | 95% | 0% | -437.0709 | 1109.4254 | -3550 | -400 | -2840.5746 | 71.01% | 65.8% | 95% | 0% | 2341 | -382
[5 empty] | 2019-05-22 | 37 | 3401.5 | 2059 | -319 | 1 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 1599.7527 | 780 | 200 | 2579.7527 | 64.49% | 95% | 0% | -364.9886 | 1239.4632 | -3550 | -400 | -2710.5368 | 67.76% | 65.8% | 95% | 0% | 2378 | -319
[5 empty] | 2019-05-22 | 38 | 3402 | 2149 | -254 | 1 | 0 | 2403 | 1643.6109 | 1643.6109 | 1643.6109 | 1599.7527 | 780 | 200 | 2579.7527 | 64.49% | 95% | 0% | -290.6178 | 1352.993 | -3550 | -400 | -2597.007 | 64.93% | 65.8% | 95% | 0% | 2403 | -254
[5 empty] | 2019-05-22 | 39 | 3402.5 | 2221 | -198 | 1 | 0 | 2419 | 1668.6727 | 1668.6727 | 1668.6727 | 1599.7527 | 780 | 200 | 2579.7527 | 64.49% | 95% | 0% | -226.5446 | 1442.1281 | -3550 | -400 | -2507.8719 | 62.7% | 65.8% | 95% | 0% | 2419 | -198
[5 empty] | 2019-05-22 | 40 | 3403 | 2282 | -146 | 1 | 0 | 2428 | 1682.77 | 1682.77 | 1682.77 | 1599.7527 | 780 | 200 | 2579.7527 | 64.49% | 95% | 0% | -167.0481 | 1515.7219 | -3550 | -400 | -2434.2781 | 60.86% | 65.8% | 95% | 0% | 2428 | -146
[5 empty] | 2019-05-22 | 41 | 3403.5 | 2296 | -115 | 1 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 1599.7527 | 780 | 200 | 2579.7527 | 64.49% | 95% | 0% | -131.5789 | 1524.5628 | -3550 | -400 | -2425.4372 | 60.64% | 65.79% | 95% | 0% | 2411 | -115
[5 empty] | 2019-05-22 | 42 | 3404 | 2288 | -96 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1599.7527 | 780 | 200 | 2579.7527 | 64.49% | 95% | 0% | -109.8398 | 1504.0101 | -3550 | -400 | -2445.9899 | 61.15% | 65.79% | 95% | 0% | 2384 | -96
[5 empty] | 2019-05-22 | 43 | 3404.5 | 2265 | -92 | 1 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 1599.7527 | 780 | 200 | 2579.7527 | 64.49% | 95% | 0% | -105.2632 | 1466.295 | -3550 | -400 | -2483.705 | 62.09% | 65.79% | 95% | 0% | 2357 | -92
[5 empty] | 2019-05-22 | 44 | 3405 | 2222 | -91 | 1 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 1599.7527 | 780 | 200 | 2579.7527 | 64.49% | 95% | 0% | -104.119 | 1398.5191 | -3550 | -400 | -2551.4809 | 63.79% | 65.79% | 95% | 0% | 2313 | -91
[5 empty] | 2019-05-22 | 45 | 3405.5 | 2120 | -90 | 0 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 1599.7527 | 780 | 200 | 2579.7527 | 64.49% | 95% | 0% | -102.9748 | 1238.3277 | -2750 | -200 | -1711.6723 | 42.79% | 65.79% | 95% | 0% | 2210 | -90
[5 empty] | 2019-05-22 | 46 | 3406 | 1988 | -89 | 0 | 0 | 2077 | 1132.9761 | 1132.9761 | 1132.9761 | 1599.7527 | 780 | 200 | 2579.7527 | 64.49% | 95% | 0% | -101.8307 | 1031.1454 | -2750 | -200 | -1918.8546 | 47.97% | 65.78% | 95% | 0% | 2077 | -89
[5 empty] | 2019-05-22 | 47 | 3406.5 | 1844 | -87 | 0 | 0 | 1931 | 904.2869 | 904.2869 | 904.2869 | 1599.7527 | 780 | 200 | 2579.7527 | 64.49% | 95% | 0% | -99.5423 | 804.7446 | -2750 | -200 | -2145.2554 | 53.63% | 65.78% | 95% | 0% | 1931 | -87
[5 empty] | 2019-05-22 | 48 | 3407 | 1735 | -85 | 0 | 0 | 1820 | 730.4204 | 730.4204 | 730.4204 | 1599.7527 | 780 | 200 | 2579.7527 | 64.49% | 95% | 0% | -97.254 | 633.1664 | -2750 | -200 | -2316.8336 | 57.92% | 65.78% | 95% | 0% | 1820 | -85
[5 empty] | 2019-05-23 | 1 | 3407.5 | 1653 | -80 | 0 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 1598.1863 | 780 | 200 | 2578.1863 | 64.45% | 95% | 0% | -91.5332 | 502.6136 | -2750 | -200 | -2447.3864 | 61.18% | 65.78% | 95% | 0% | 1733 | -80
[5 empty] | 2019-05-23 | 2 | 3408 | 1609 | -74 | 0 | 0 | 1683 | 515.8285 | 515.8285 | 515.8285 | 1598.1863 | 780 | 200 | 2578.1863 | 64.45% | 95% | 0% | -84.6682 | 431.1603 | -2750 | -200 | -2518.8397 | 62.97% | 65.78% | 95% | 0% | 1683 | -74
[5 empty] | 2019-05-23 | 3 | 3408.5 | 1584 | -73 | 0 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 1598.1863 | 780 | 200 | 2578.1863 | 64.45% | 95% | 0% | -83.524 | 391.579 | -2750 | -200 | -2558.421 | 63.96% | 65.78% | 95% | 0% | 1657 | -73
[5 empty] | 2019-05-23 | 4 | 3409 | 1589 | -72 | 0 | 0 | 1661 | 481.3685 | 481.3685 | 481.3685 | 1598.1863 | 780 | 200 | 2578.1863 | 64.45% | 95% | 0% | -82.3799 | 398.9886 | -2750 | -200 | -2551.0114 | 63.78% | 65.78% | 95% | 0% | 1661 | -72
[5 empty] | 2019-05-23 | 5 | 3409.5 | 1570 | -71 | 0 | 0 | 1641 | 450.0412 | 450.0412 | 450.0412 | 1598.1863 | 780 | 200 | 2578.1863 | 64.45% | 95% | 0% | -81.2357 | 368.8055 | -2750 | -200 | -2581.1945 | 64.53% | 65.77% | 95% | 0% | 1641 | -71
[5 empty] | 2019-05-23 | 6 | 3410 | 1549 | -70 | 0 | 0 | 1619 | 415.5812 | 415.5812 | 415.5812 | 1598.1863 | 780 | 200 | 2578.1863 | 64.45% | 95% | 0% | -80.0915 | 335.4897 | -2750 | -200 | -2614.5103 | 65.36% | 65.77% | 95% | 0% | 1619 | -70
[5 empty] | 2019-05-23 | 7 | 3410.5 | 1527 | -70 | 0 | 0 | 1597 | 381.1212 | 381.1212 | 381.1212 | 1598.1863 | 780 | 200 | 2578.1863 | 64.45% | 95% | 0% | -80.0915 | 301.0297 | -2750 | -200 | -2648.9703 | 66.22% | 65.76% | 95% | 0% | 1597 | -70
[5 empty] | 2019-05-23 | 8 | 3411 | 1524 | -69 | 0 | 0 | 1593 | 374.8557 | 374.8557 | 374.8557 | 1598.1863 | 780 | 200 | 2578.1863 | 64.45% | 95% | 0% | -78.9474 | 295.9084 | -2750 | -200 | -2654.0916 | 66.35% | 65.76% | 95% | 0% | 1593 | -69
[5 empty] | 2019-05-23 | 9 | 3411.5 | 1524 | -69 | 0 | 0 | 1593 | 374.8557 | 374.8557 | 374.8557 | 1598.1863 | 780 | 200 | 2578.1863 | 64.45% | 95% | 0% | -78.9474 | 295.9084 | -2750 | -200 | -2654.0916 | 66.35% | 65.75% | 95% | 0% | 1593 | -69
[5 empty] | 2019-05-23 | 10 | 3412 | 1520 | -69 | 0 | 0 | 1589 | 368.5903 | 368.5903 | 368.5903 | 1598.1863 | 780 | 200 | 2578.1863 | 64.45% | 95% | 0% | -78.9474 | 289.6429 | -2750 | -200 | -2660.3571 | 66.51% | 65.75% | 95% | 0% | 1589 | -69
[5 empty] | 2019-05-23 | 11 | 3412.5 | 1543 | -73 | 0 | 0 | 1616 | 410.8821 | 410.8821 | 410.8821 | 1598.1863 | 780 | 200 | 2578.1863 | 64.45% | 95% | 0% | -83.524 | 327.3581 | -2750 | -200 | -2622.6419 | 65.57% | 65.74% | 95% | 0% | 1616 | -73
[5 empty] | 2019-05-23 | 12 | 3413 | 1577 | -93 | 0 | 0 | 1670 | 495.4658 | 495.4658 | 495.4658 | 1598.1863 | 780 | 200 | 2578.1863 | 64.45% | 95% | 0% | -106.4073 | 389.0585 | -2750 | -200 | -2560.9415 | 64.02% | 65.74% | 95% | 0% | 1670 | -93
[5 empty] | 2019-05-23 | 13 | 3413.5 | 1722 | -125 | 0 | 0 | 1847 | 772.7123 | 772.7123 | 772.7123 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -143.0206 | 629.6917 | -2750 | -200 | -2320.3083 | 58.01% | 65.74% | 95% | 0% | 1847 | -125
[5 empty] | 2019-05-23 | 14 | 3414 | 1849 | -169 | 1 | 0 | 2018 | 1040.5606 | 1040.5606 | 1040.5606 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -193.3638 | 847.1967 | -3550 | -400 | -3102.8033 | 77.57% | 65.74% | 95% | 0% | 2018 | -169
[5 empty] | 2019-05-23 | 15 | 3414.5 | 1984 | -221 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -252.8604 | 1080.6103 | -3550 | -400 | -2869.3897 | 71.73% | 65.74% | 95% | 0% | 2205 | -221
[5 empty] | 2019-05-23 | 16 | 3415 | 1990 | -279 | 1 | 0 | 2269 | 1433.7181 | 1433.7181 | 1433.7181 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -319.222 | 1114.4961 | -3550 | -400 | -2835.5039 | 70.89% | 65.74% | 95% | 0% | 2269 | -279
[5 empty] | 2019-05-23 | 17 | 3415.5 | 1925 | -340 | 1 | 0 | 2265 | 1427.4526 | 1427.4526 | 1427.4526 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -389.016 | 1038.4366 | -3550 | -400 | -2911.5634 | 72.79% | 65.73% | 95% | 0% | 2265 | -340
[5 empty] | 2019-05-23 | 18 | 3416 | 1853 | -401 | 1 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -458.8101 | 951.4125 | -3550 | -400 | -2998.5875 | 74.96% | 65.73% | 95% | 0% | 2254 | -401
[5 empty] | 2019-05-23 | 19 | 3416.5 | 1767 | -470 | 1 | 0 | 2237 | 1383.5944 | 1383.5944 | 1383.5944 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -537.7574 | 845.837 | -3550 | -400 | -3104.163 | 77.6% | 65.73% | 95% | 0% | 2237 | -470
[5 empty] | 2019-05-23 | 20 | 3417 | 1666 | -540 | 1 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -617.849 | 717.1881 | -3550 | -400 | -3232.8119 | 80.82% | 65.72% | 95% | 0% | 2206 | -540
[5 empty] | 2019-05-23 | 21 | 3417.5 | 1533 | -619 | 1 | 0 | 2152 | 1250.4534 | 1250.4534 | 1250.4534 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -708.238 | 542.2154 | -3550 | -400 | -3407.7846 | 85.19% | 65.72% | 95% | 0% | 2152 | -619
[5 empty] | 2019-05-23 | 22 | 3418 | 1440 | -667 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -763.1579 | 416.8091 | -3550 | -400 | -3533.1909 | 88.33% | 65.72% | 95% | 0% | 2107 | -667
[5 empty] | 2019-05-23 | 23 | 3418.5 | 1389 | -701 | 1 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -802.0595 | 351.2793 | -3550 | -400 | -3598.7207 | 89.97% | 65.72% | 95% | 0% | 2090 | -701
[5 empty] | 2019-05-23 | 24 | 3419 | 1321 | -749 | 1 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -856.9794 | 265.0321 | -3550 | -400 | -3684.9679 | 92.12% | 65.72% | 95% | 0% | 2070 | -749
[5 empty] | 2019-05-23 | 25 | 3419.5 | 1291 | -766 | 1 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 1596.62 | 780 | 200 | 2576.62 | 64.42% | 95% | 0% | -876.4302 | 225.2186 | -3550 | -400 | -3724.7814 | 93.12% | 65.72% | 95% | 0% | 2057 | -766
[5 empty] | 2019-05-23 | 26 | 3420 | 1263 | -778 | 1 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 1595.0536 | 780 | 200 | 2575.0536 | 64.38% | 95% | 0% | -890.1602 | 186.4268 | -3550 | -400 | -3763.5732 | 94.09% | 65.71% | 95% | 0% | 2041 | -778
[5 empty] | 2019-05-23 | 27 | 3420.5 | 1248 | -774 | 1 | 0 | 2022 | 1046.8261 | 1046.8261 | 1046.8261 | 1595.0536 | 780 | 200 | 2575.0536 | 64.38% | 95% | 0% | -885.5835 | 161.2425 | -3550 | -400 | -3788.7575 | 94.72% | 65.71% | 95% | 0% | 2022 | -774
[5 empty] | 2019-05-23 | 28 | 3421 | 1233 | -763 | 1 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 1595.0536 | 780 | 200 | 2575.0536 | 64.38% | 95% | 0% | -872.9977 | 133.1029 | -3550 | -400 | -3816.8971 | 95.42% | 65.71% | 95% | 0% | 1996 | -763
[5 empty] | 2019-05-23 | 29 | 3421.5 | 1258 | -731 | 1 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 1595.0536 | 780 | 200 | 2575.0536 | 64.38% | 95% | 0% | -836.3844 | 158.7516 | -3550 | -400 | -3791.2484 | 94.78% | 65.7% | 95% | 0% | 1989 | -731
[5 empty] | 2019-05-23 | 30 | 3422 | 1296 | -694 | 1 | 0 | 1990 | 996.7024 | 996.7024 | 996.7024 | 1595.0536 | 780 | 200 | 2575.0536 | 64.38% | 95% | 0% | -794.0503 | 202.652 | -3550 | -400 | -3747.348 | 93.68% | 65.7% | 95% | 0% | 1990 | -694
[5 empty] | 2019-05-23 | 31 | 3422.5 | 1327 | -668 | 1 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 1595.0536 | 780 | 200 | 2575.0536 | 64.38% | 95% | 0% | -764.3021 | 240.2322 | -3550 | -400 | -3709.7678 | 92.74% | 65.7% | 95% | 0% | 1995 | -668
[5 empty] | 2019-05-23 | 32 | 3423 | 1421 | -625 | 1 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1595.0536 | 780 | 200 | 2575.0536 | 64.38% | 95% | 0% | -715.103 | 369.3158 | -3550 | -400 | -3580.6842 | 89.52% | 65.69% | 95% | 0% | 2046 | -625
[5 empty] | 2019-05-23 | 33 | 3423.5 | 1551 | -569 | 1 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -651.0297 | 549.3 | -3550 | -400 | -3400.7 | 85.02% | 65.69% | 95% | 0% | 2120 | -569
[5 empty] | 2019-05-23 | 34 | 3424 | 1683 | -506 | 1 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -578.9474 | 729.4615 | -3550 | -400 | -3220.5385 | 80.51% | 65.69% | 95% | 0% | 2189 | -506
[5 empty] | 2019-05-23 | 35 | 3424.5 | 1825 | -434 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -496.5675 | 921.4869 | -3550 | -400 | -3028.5131 | 75.71% | 65.69% | 95% | 0% | 2259 | -434
[5 empty] | 2019-05-23 | 36 | 3425 | 1931 | -375 | 1 | 0 | 2306 | 1491.6735 | 1491.6735 | 1491.6735 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -429.0618 | 1062.6118 | -3550 | -400 | -2887.3882 | 72.18% | 65.69% | 95% | 0% | 2306 | -375
[5 empty] | 2019-05-23 | 37 | 3425.5 | 2008 | -319 | 1 | 0 | 2327 | 1524.5672 | 1524.5672 | 1524.5672 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -364.9886 | 1159.5786 | -3550 | -400 | -2790.4214 | 69.76% | 65.68% | 95% | 0% | 2327 | -319
[5 empty] | 2019-05-23 | 38 | 3426 | 2084 | -269 | 1 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -307.7803 | 1257.5123 | -3550 | -400 | -2692.4877 | 67.31% | 65.68% | 95% | 0% | 2353 | -269
[5 empty] | 2019-05-23 | 39 | 3426.5 | 2159 | -213 | 1 | 0 | 2372 | 1595.0536 | 1595.0536 | 1595.0536 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -243.7071 | 1351.3465 | -3550 | -400 | -2598.6535 | 64.97% | 65.68% | 95% | 0% | 2372 | -213
[5 empty] | 2019-05-23 | 40 | 3427 | 2219 | -167 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -191.0755 | 1425.9072 | -3550 | -400 | -2524.0928 | 63.1% | 65.67% | 95% | 0% | 2386 | -167
[5 empty] | 2019-05-23 | 41 | 3427.5 | 2235 | -129 | 1 | 0 | 2364 | 1582.5227 | 1582.5227 | 1582.5227 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -147.5973 | 1434.9254 | -3550 | -400 | -2515.0746 | 62.88% | 65.67% | 95% | 0% | 2364 | -129
[5 empty] | 2019-05-23 | 42 | 3428 | 2247 | -106 | 1 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -121.2815 | 1444.0112 | -3550 | -400 | -2505.9888 | 62.65% | 65.67% | 95% | 0% | 2353 | -106
[5 empty] | 2019-05-23 | 43 | 3428.5 | 2244 | -99 | 1 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -113.2723 | 1436.3567 | -3550 | -400 | -2513.6433 | 62.84% | 65.67% | 95% | 0% | 2343 | -99
[5 empty] | 2019-05-23 | 44 | 3429 | 2204 | -96 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -109.8398 | 1372.4355 | -3550 | -400 | -2577.5645 | 64.44% | 65.66% | 95% | 0% | 2300 | -96
[5 empty] | 2019-05-23 | 45 | 3429.5 | 2096 | -96 | 0 | 0 | 2192 | 1313.108 | 1313.108 | 1313.108 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -109.8398 | 1203.2682 | -2750 | -200 | -1746.7318 | 43.67% | 65.66% | 95% | 0% | 2192 | -96
[5 empty] | 2019-05-23 | 46 | 3430 | 1975 | -95 | 0 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 1593.4872 | 780 | 200 | 2573.4872 | 64.34% | 95% | 0% | -108.6957 | 1013.3159 | -2750 | -200 | -1936.6841 | 48.42% | 65.66% | 95% | 0% | 2070 | -95
[5 empty] | 2019-05-23 | 47 | 3430.5 | 1829 | -95 | 0 | 0 | 1924 | 893.3223 | 893.3223 | 893.3223 | 1591.9209 | 780 | 200 | 2571.9209 | 64.3% | 95% | 0% | -108.6957 | 784.6267 | -2750 | -200 | -2165.3733 | 54.13% | 65.65% | 95% | 0% | 1924 | -95
[5 empty] | 2019-05-23 | 48 | 3431 | 1705 | -94 | 0 | 0 | 1799 | 697.5268 | 697.5268 | 697.5268 | 1591.9209 | 780 | 200 | 2571.9209 | 64.3% | 95% | 0% | -107.5515 | 589.9753 | -2750 | -200 | -2360.0247 | 59% | 65.65% | 95% | 0% | 1799 | -94
[5 empty] | 2019-05-24 | 1 | 3431.5 | 1610 | -94 | 0 | 0 | 1704 | 548.7222 | 548.7222 | 548.7222 | 1591.9209 | 780 | 200 | 2571.9209 | 64.3% | 95% | 0% | -107.5515 | 441.1707 | -2750 | -200 | -2508.8293 | 62.72% | 65.65% | 95% | 0% | 1704 | -94
[5 empty] | 2019-05-24 | 2 | 3432 | 1545 | -93 | 0 | 0 | 1638 | 445.3421 | 445.3421 | 445.3421 | 1591.9209 | 780 | 200 | 2571.9209 | 64.3% | 95% | 0% | -106.4073 | 338.9348 | -2750 | -200 | -2611.0652 | 65.28% | 65.63% | 95% | 0% | 1638 | -93
[5 empty] | 2019-05-24 | 3 | 3432.5 | 1522 | -93 | 1 | 0 | 1615 | 409.3157 | 409.3157 | 409.3157 | 1591.9209 | 780 | 200 | 2571.9209 | 64.3% | 95% | 0% | -106.4073 | 302.9084 | -3550 | -400 | -3647.0916 | 91.18% | 65.63% | 95% | 0% | 1615 | -93
[5 empty] | 2019-05-24 | 4 | 3433 | 1502 | -93 | 1 | 0 | 1595 | 377.9885 | 377.9885 | 377.9885 | 1591.9209 | 780 | 200 | 2571.9209 | 64.3% | 95% | 0% | -106.4073 | 271.5811 | -3550 | -400 | -3678.4189 | 91.96% | 65.63% | 95% | 0% | 1595 | -93
[5 empty] | 2019-05-24 | 5 | 3433.5 | 1485 | -93 | 1 | 0 | 1578 | 351.3603 | 351.3603 | 351.3603 | 1591.9209 | 780 | 200 | 2571.9209 | 64.3% | 95% | 0% | -106.4073 | 244.9529 | -3550 | -400 | -3705.0471 | 92.63% | 65.62% | 95% | 0% | 1578 | -93
[5 empty] | 2019-05-24 | 6 | 3434 | 1459 | -92 | 1 | 0 | 1551 | 309.0684 | 309.0684 | 309.0684 | 1591.9209 | 780 | 200 | 2571.9209 | 64.3% | 95% | 0% | -105.2632 | 203.8053 | -3550 | -400 | -3746.1947 | 93.65% | 65.62% | 95% | 0% | 1551 | -92
[5 empty] | 2019-05-24 | 7 | 3434.5 | 1449 | -92 | 1 | 0 | 1541 | 293.4048 | 293.4048 | 293.4048 | 1591.9209 | 780 | 200 | 2571.9209 | 64.3% | 95% | 0% | -105.2632 | 188.1416 | -3550 | -400 | -3761.8584 | 94.05% | 65.62% | 95% | 0% | 1541 | -92
[5 empty] | 2019-05-24 | 8 | 3435 | 1450 | -92 | 1 | 0 | 1542 | 294.9711 | 294.9711 | 294.9711 | 1591.9209 | 780 | 200 | 2571.9209 | 64.3% | 95% | 0% | -105.2632 | 189.708 | -3550 | -400 | -3760.292 | 94.01% | 65.62% | 95% | 0% | 1542 | -92
[5 empty] | 2019-05-24 | 9 | 3435.5 | 1446 | -91 | 1 | 0 | 1537 | 287.1393 | 287.1393 | 287.1393 | 1590.3545 | 780 | 200 | 2570.3545 | 64.26% | 95% | 0% | -104.119 | 183.0203 | -3550 | -400 | -3766.9797 | 94.17% | 65.61% | 95% | 0% | 1537 | -91
[5 empty] | 2019-05-24 | 10 | 3436 | 1434 | -90 | 1 | 0 | 1524 | 266.7766 | 266.7766 | 266.7766 | 1590.3545 | 780 | 200 | 2570.3545 | 64.26% | 95% | 0% | -102.9748 | 163.8018 | -3550 | -400 | -3786.1982 | 94.65% | 65.61% | 95% | 0% | 1524 | -90
[5 empty] | 2019-05-24 | 11 | 3436.5 | 1466 | -93 | 1 | 0 | 1559 | 321.5993 | 321.5993 | 321.5993 | 1590.3545 | 780 | 200 | 2570.3545 | 64.26% | 95% | 0% | -106.4073 | 215.192 | -3550 | -400 | -3734.808 | 93.37% | 65.61% | 95% | 0% | 1559 | -93
[5 empty] | 2019-05-24 | 12 | 3437 | 1518 | -112 | 1 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 1590.3545 | 780 | 200 | 2570.3545 | 64.26% | 95% | 0% | -128.1465 | 304.6648 | -3550 | -400 | -3645.3352 | 91.13% | 65.61% | 95% | 0% | 1630 | -112
[5 empty] | 2019-05-24 | 13 | 3437.5 | 1672 | -149 | 1 | 0 | 1821 | 731.9868 | 731.9868 | 731.9868 | 1590.3545 | 780 | 200 | 2570.3545 | 64.26% | 95% | 0% | -170.4805 | 561.5063 | -3550 | -400 | -3388.4937 | 84.71% | 65.6% | 95% | 0% | 1821 | -149
[5 empty] | 2019-05-24 | 14 | 3438 | 1784 | -193 | 1 | 0 | 1977 | 976.3397 | 976.3397 | 976.3397 | 1590.3545 | 780 | 200 | 2570.3545 | 64.26% | 95% | 0% | -220.8238 | 755.5159 | -3550 | -400 | -3194.4841 | 79.86% | 65.6% | 95% | 0% | 1977 | -193
[5 empty] | 2019-05-24 | 15 | 3438.5 | 1928 | -241 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 1590.3545 | 780 | 200 | 2570.3545 | 64.26% | 95% | 0% | -275.7437 | 1001.3379 | -3550 | -400 | -2948.6621 | 73.72% | 65.59% | 95% | 0% | 2169 | -241
[5 empty] | 2019-05-24 | 16 | 3439 | 1957 | -300 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 1590.3545 | 780 | 200 | 2570.3545 | 64.26% | 95% | 0% | -343.2494 | 1071.6723 | -3550 | -400 | -2878.3277 | 71.96% | 65.59% | 95% | 0% | 2257 | -300
[5 empty] | 2019-05-24 | 17 | 3439.5 | 1939 | -360 | 1 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 1590.3545 | 780 | 200 | 2570.3545 | 64.26% | 95% | 0% | -411.8993 | 1068.8097 | -3550 | -400 | -2881.1903 | 72.03% | 65.59% | 95% | 0% | 2299 | -360
[5 empty] | 2019-05-24 | 18 | 3440 | 1840 | -422 | 1 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 1588.7881 | 780 | 200 | 2568.7881 | 64.22% | 95% | 0% | -482.8375 | 939.916 | -3550 | -400 | -3010.084 | 75.25% | 65.59% | 95% | 0% | 2262 | -422
[5 empty] | 2019-05-24 | 19 | 3440.5 | 1752 | -488 | 1 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 1588.7881 | 780 | 200 | 2568.7881 | 64.22% | 95% | 0% | -558.3524 | 829.9411 | -3550 | -400 | -3120.0589 | 78% | 65.59% | 95% | 0% | 2240 | -488
[5 empty] | 2019-05-24 | 20 | 3441 | 1652 | -548 | 1 | 0 | 2200 | 1325.6389 | 1325.6389 | 1325.6389 | 1588.7881 | 780 | 200 | 2568.7881 | 64.22% | 95% | 0% | -627.0023 | 698.6366 | -3550 | -400 | -3251.3634 | 81.28% | 65.59% | 95% | 0% | 2200 | -548
[5 empty] | 2019-05-24 | 21 | 3441.5 | 1555 | -595 | 1 | 0 | 2150 | 1247.3207 | 1247.3207 | 1247.3207 | 1588.7881 | 780 | 200 | 2568.7881 | 64.22% | 95% | 0% | -680.778 | 566.5427 | -3550 | -400 | -3383.4573 | 84.59% | 65.58% | 95% | 0% | 2150 | -595
[5 empty] | 2019-05-24 | 22 | 3442 | 1487 | -641 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1588.7881 | 780 | 200 | 2568.7881 | 64.22% | 95% | 0% | -733.4096 | 479.4511 | -3550 | -400 | -3470.5489 | 86.76% | 65.58% | 95% | 0% | 2128 | -641
[5 empty] | 2019-05-24 | 23 | 3442.5 | 1459 | -662 | 1 | 0 | 2121 | 1201.8961 | 1201.8961 | 1201.8961 | 1588.7881 | 780 | 200 | 2568.7881 | 64.22% | 95% | 0% | -757.4371 | 444.4591 | -3550 | -400 | -3505.5409 | 87.64% | 65.58% | 95% | 0% | 2121 | -662
[5 empty] | 2019-05-24 | 24 | 3443 | 1443 | -669 | 1 | 0 | 2112 | 1187.7988 | 1187.7988 | 1187.7988 | 1588.7881 | 780 | 200 | 2568.7881 | 64.22% | 95% | 0% | -765.4462 | 422.3526 | -3550 | -400 | -3527.6474 | 88.19% | 65.58% | 95% | 0% | 2112 | -669
[5 empty] | 2019-05-24 | 25 | 3443.5 | 1434 | -680 | 1 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -778.032 | 412.8995 | -3550 | -400 | -3537.1005 | 88.43% | 65.57% | 95% | 0% | 2114 | -680
[5 empty] | 2019-05-24 | 26 | 3444 | 1467 | -636 | 1 | 0 | 2103 | 1173.7016 | 1173.7016 | 1173.7016 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -727.6888 | 446.0128 | -3550 | -400 | -3503.9872 | 87.6% | 65.57% | 95% | 0% | 2103 | -636
[5 empty] | 2019-05-24 | 27 | 3444.5 | 1506 | -588 | 1 | 0 | 2094 | 1159.6043 | 1159.6043 | 1159.6043 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -672.7689 | 486.8354 | -3550 | -400 | -3463.1646 | 86.58% | 65.57% | 95% | 0% | 2094 | -588
[5 empty] | 2019-05-24 | 28 | 3445 | 1504 | -570 | 1 | 0 | 2074 | 1128.277 | 1128.277 | 1128.277 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -652.1739 | 476.1031 | -3550 | -400 | -3473.8969 | 86.85% | 65.57% | 95% | 0% | 2074 | -570
[5 empty] | 2019-05-24 | 29 | 3445.5 | 1545 | -517 | 1 | 0 | 2062 | 1109.4806 | 1109.4806 | 1109.4806 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -591.5332 | 517.9474 | -3550 | -400 | -3432.0526 | 85.8% | 65.57% | 95% | 0% | 2062 | -517
[5 empty] | 2019-05-24 | 30 | 3446 | 1555 | -514 | 1 | 0 | 2069 | 1120.4452 | 1120.4452 | 1120.4452 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -588.1007 | 532.3445 | -3550 | -400 | -3417.6555 | 85.44% | 65.57% | 95% | 0% | 2069 | -514
[5 empty] | 2019-05-24 | 31 | 3446.5 | 1591 | -494 | 1 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -565.2174 | 580.2896 | -3550 | -400 | -3369.7104 | 84.24% | 65.57% | 95% | 0% | 2085 | -494
[5 empty] | 2019-05-24 | 32 | 3447 | 1653 | -460 | 1 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -526.3158 | 663.0494 | -3550 | -400 | -3286.9506 | 82.17% | 65.57% | 95% | 0% | 2113 | -460
[5 empty] | 2019-05-24 | 33 | 3447.5 | 1748 | -403 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -461.0984 | 787.7887 | -3550 | -400 | -3162.2113 | 79.06% | 65.56% | 95% | 0% | 2151 | -403
[5 empty] | 2019-05-24 | 34 | 3448 | 1862 | -361 | 1 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -413.0435 | 948.6218 | -3550 | -400 | -3001.3782 | 75.03% | 65.56% | 95% | 0% | 2223 | -361
[5 empty] | 2019-05-24 | 35 | 3448.5 | 1963 | -320 | 1 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -366.1327 | 1089.5144 | -3550 | -400 | -2860.4856 | 71.51% | 65.56% | 95% | 0% | 2283 | -320
[5 empty] | 2019-05-24 | 36 | 3449 | 2009 | -280 | 1 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -320.3661 | 1144.6792 | -3550 | -400 | -2805.3208 | 70.13% | 65.56% | 95% | 0% | 2289 | -280
[5 empty] | 2019-05-24 | 37 | 3449.5 | 2066 | -238 | 1 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 1587.2218 | 780 | 200 | 2567.2218 | 64.18% | 95% | 0% | -272.3112 | 1216.2296 | -3550 | -400 | -2733.7704 | 68.34% | 65.56% | 95% | 0% | 2304 | -238
[5 empty] | 2019-05-24 | 38 | 3450 | 2117 | -198 | 1 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 1585.6554 | 780 | 200 | 2565.6554 | 64.14% | 95% | 0% | -226.5446 | 1279.2262 | -3550 | -400 | -2670.7738 | 66.77% | 65.55% | 95% | 0% | 2315 | -198
[5 empty] | 2019-05-24 | 39 | 3450.5 | 2163 | -152 | 1 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 1585.6554 | 780 | 200 | 2565.6554 | 64.14% | 95% | 0% | -173.913 | 1331.8578 | -3550 | -400 | -2618.1422 | 65.45% | 65.55% | 95% | 0% | 2315 | -152
[5 empty] | 2019-05-24 | 40 | 3451 | 2184 | -118 | 1 | 0 | 2302 | 1485.4081 | 1485.4081 | 1485.4081 | 1585.6554 | 780 | 200 | 2565.6554 | 64.14% | 95% | 0% | -135.0114 | 1350.3966 | -3550 | -400 | -2599.6034 | 64.99% | 65.55% | 95% | 0% | 2302 | -118
[5 empty] | 2019-05-24 | 41 | 3451.5 | 2193 | -90 | 1 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 1585.6554 | 780 | 200 | 2565.6554 | 64.14% | 95% | 0% | -102.9748 | 1352.6723 | -3550 | -400 | -2597.3277 | 64.93% | 65.54% | 95% | 0% | 2283 | -90
[5 empty] | 2019-05-24 | 42 | 3452 | 2189 | -70 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 1585.6554 | 780 | 200 | 2565.6554 | 64.14% | 95% | 0% | -80.0915 | 1337.9629 | -3550 | -400 | -2612.0371 | 65.3% | 65.54% | 95% | 0% | 2259 | -70
[5 empty] | 2019-05-24 | 43 | 3452.5 | 2186 | -65 | 1 | 0 | 2251 | 1405.5235 | 1405.5235 | 1405.5235 | 1585.6554 | 780 | 200 | 2565.6554 | 64.14% | 95% | 0% | -74.3707 | 1331.1528 | -3550 | -400 | -2618.8472 | 65.47% | 65.54% | 95% | 0% | 2251 | -65
[5 empty] | 2019-05-24 | 44 | 3453 | 2168 | -62 | 1 | 0 | 2230 | 1372.6298 | 1372.6298 | 1372.6298 | 1585.6554 | 780 | 200 | 2565.6554 | 64.14% | 95% | 0% | -70.9382 | 1301.6916 | -3550 | -400 | -2648.3084 | 66.21% | 65.54% | 95% | 0% | 2230 | -62
[5 empty] | 2019-05-24 | 45 | 3453.5 | 2094 | -61 | 0 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 1585.6554 | 780 | 200 | 2565.6554 | 64.14% | 95% | 0% | -69.7941 | 1185.3585 | -2750 | -200 | -1764.6415 | 44.12% | 65.53% | 95% | 0% | 2155 | -61
[5 empty] | 2019-05-24 | 46 | 3454 | 1990 | -60 | 0 | 0 | 2050 | 1090.6843 | 1090.6843 | 1090.6843 | 1585.6554 | 780 | 200 | 2565.6554 | 64.14% | 95% | 0% | -68.6499 | 1022.0344 | -2750 | -200 | -1927.9656 | 48.2% | 65.53% | 95% | 0% | 2050 | -60
[5 empty] | 2019-05-24 | 47 | 3454.5 | 1871 | -58 | 0 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 1585.6554 | 780 | 200 | 2565.6554 | 64.14% | 95% | 0% | -66.3616 | 834.7926 | -2750 | -200 | -2115.2074 | 52.88% | 65.53% | 95% | 0% | 1929 | -58
[5 empty] | 2019-05-24 | 48 | 3455 | 1766 | -57 | 0 | 0 | 1823 | 735.1195 | 735.1195 | 735.1195 | 1585.6554 | 780 | 200 | 2565.6554 | 64.14% | 95% | 0% | -65.2174 | 669.9021 | -2750 | -200 | -2280.0979 | 57% | 65.53% | 95% | 0% | 1823 | -57
[5 empty] | 2019-05-25 | 1 | 3455.5 | 1674 | -54 | 0 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 1584.089 | 780 | 200 | 2564.089 | 64.1% | 95% | 0% | -61.7849 | 524.53 | -2750 | -200 | -2425.47 | 60.64% | 65.53% | 95% | 0% | 1728 | -54
[5 empty] | 2019-05-25 | 2 | 3456 | 1609 | -51 | 0 | 0 | 1660 | 479.8021 | 479.8021 | 479.8021 | 1584.089 | 780 | 200 | 2564.089 | 64.1% | 95% | 0% | -58.3524 | 421.4497 | -2750 | -200 | -2528.5503 | 63.21% | 65.52% | 95% | 0% | 1660 | -51
[5 empty] | 2019-05-25 | 3 | 3456.5 | 1572 | -49 | 0 | 0 | 1621 | 418.7139 | 418.7139 | 418.7139 | 1584.089 | 780 | 200 | 2564.089 | 64.1% | 95% | 0% | -56.0641 | 362.6499 | -2750 | -200 | -2587.3501 | 64.68% | 65.52% | 95% | 0% | 1621 | -49
[5 empty] | 2019-05-25 | 4 | 3457 | 1569 | -47 | 1 | 0 | 1616 | 410.8821 | 410.8821 | 410.8821 | 1584.089 | 780 | 200 | 2564.089 | 64.1% | 95% | 0% | -53.7757 | 357.1064 | -3550 | -400 | -3592.8936 | 89.82% | 65.52% | 95% | 0% | 1616 | -47
[5 empty] | 2019-05-25 | 5 | 3457.5 | 1548 | -45 | 1 | 0 | 1593 | 374.8557 | 374.8557 | 374.8557 | 1584.089 | 780 | 200 | 2564.089 | 64.1% | 95% | 0% | -51.4874 | 323.3683 | -3550 | -400 | -3626.6317 | 90.67% | 65.52% | 95% | 0% | 1593 | -45
[5 empty] | 2019-05-25 | 6 | 3458 | 1511 | -44 | 1 | 0 | 1555 | 315.3339 | 315.3339 | 315.3339 | 1584.089 | 780 | 200 | 2564.089 | 64.1% | 95% | 0% | -50.3432 | 264.9906 | -3550 | -400 | -3685.0094 | 92.13% | 65.51% | 95% | 0% | 1555 | -44
[5 empty] | 2019-05-25 | 7 | 3458.5 | 1484 | -44 | 1 | 0 | 1528 | 273.042 | 273.042 | 273.042 | 1584.089 | 780 | 200 | 2564.089 | 64.1% | 95% | 0% | -50.3432 | 222.6988 | -3550 | -400 | -3727.3012 | 93.18% | 65.51% | 95% | 0% | 1528 | -44
[5 empty] | 2019-05-25 | 8 | 3459 | 1476 | -43 | 1 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 1584.089 | 780 | 200 | 2564.089 | 64.1% | 95% | 0% | -49.1991 | 209.7457 | -3550 | -400 | -3740.2543 | 93.51% | 65.51% | 95% | 0% | 1519 | -43
[5 empty] | 2019-05-25 | 9 | 3459.5 | 1470 | -41 | 1 | 0 | 1511 | 246.4138 | 246.4138 | 246.4138 | 1584.089 | 780 | 200 | 2564.089 | 64.1% | 95% | 0% | -46.9108 | 199.5031 | -3550 | -400 | -3750.4969 | 93.76% | 65.51% | 95% | 0% | 1511 | -41
[5 empty] | 2019-05-25 | 10 | 3460 | 1450 | -39 | 1 | 0 | 1489 | 211.9538 | 211.9538 | 211.9538 | 1582.5227 | 780 | 200 | 2562.5227 | 64.06% | 95% | 0% | -44.6224 | 167.3314 | -3550 | -400 | -3782.6686 | 94.57% | 65.5% | 95% | 0% | 1489 | -39
[5 empty] | 2019-05-25 | 11 | 3460.5 | 1445 | -40 | 1 | 0 | 1485 | 205.6884 | 205.6884 | 205.6884 | 1582.5227 | 780 | 200 | 2562.5227 | 64.06% | 95% | 0% | -45.7666 | 159.9218 | -3550 | -400 | -3790.0782 | 94.75% | 65.5% | 95% | 0% | 1485 | -40
[5 empty] | 2019-05-25 | 12 | 3461 | 1452 | -55 | 1 | 0 | 1507 | 240.1484 | 240.1484 | 240.1484 | 1582.5227 | 780 | 200 | 2562.5227 | 64.06% | 95% | 0% | -62.9291 | 177.2193 | -3550 | -400 | -3772.7807 | 94.32% | 65.5% | 95% | 0% | 1507 | -55
[5 empty] | 2019-05-25 | 13 | 3461.5 | 1500 | -81 | 1 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 1582.5227 | 780 | 200 | 2562.5227 | 64.06% | 95% | 0% | -92.6773 | 263.382 | -3550 | -400 | -3686.618 | 92.17% | 65.5% | 95% | 0% | 1581 | -81
[5 empty] | 2019-05-25 | 14 | 3462 | 1518 | -121 | 1 | 0 | 1639 | 446.9085 | 446.9085 | 446.9085 | 1582.5227 | 780 | 200 | 2562.5227 | 64.06% | 95% | 0% | -138.4439 | 308.4646 | -3550 | -400 | -3641.5354 | 91.04% | 65.5% | 95% | 0% | 1639 | -121
[5 empty] | 2019-05-25 | 15 | 3462.5 | 1570 | -163 | 1 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 1582.5227 | 780 | 200 | 2562.5227 | 64.06% | 95% | 0% | -186.4989 | 407.6479 | -3550 | -400 | -3542.3521 | 88.56% | 65.5% | 95% | 0% | 1733 | -163
[5 empty] | 2019-05-25 | 16 | 3463 | 1598 | -204 | 1 | 0 | 1802 | 702.2259 | 702.2259 | 702.2259 | 1582.5227 | 780 | 200 | 2562.5227 | 64.06% | 95% | 0% | -233.4096 | 468.8163 | -3550 | -400 | -3481.1837 | 87.03% | 65.5% | 95% | 0% | 1802 | -204
[5 empty] | 2019-05-25 | 17 | 3463.5 | 1602 | -268 | 1 | 0 | 1870 | 808.7387 | 808.7387 | 808.7387 | 1582.5227 | 780 | 200 | 2562.5227 | 64.06% | 95% | 0% | -306.6362 | 502.1025 | -3550 | -400 | -3447.8975 | 86.2% | 65.5% | 95% | 0% | 1870 | -268
[5 empty] | 2019-05-25 | 18 | 3464 | 1545 | -338 | 1 | 0 | 1883 | 829.1014 | 829.1014 | 829.1014 | 1582.5227 | 780 | 200 | 2562.5227 | 64.06% | 95% | 0% | -386.7277 | 442.3737 | -3550 | -400 | -3507.6263 | 87.69% | 65.48% | 95% | 0% | 1883 | -338
[5 empty] | 2019-05-25 | 19 | 3464.5 | 1498 | -403 | 1 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 1582.5227 | 780 | 200 | 2562.5227 | 64.06% | 95% | 0% | -461.0984 | 396.1976 | -3550 | -400 | -3553.8024 | 88.85% | 65.48% | 95% | 0% | 1901 | -403
[5 empty] | 2019-05-25 | 20 | 3465 | 1435 | -454 | 1 | 0 | 1889 | 838.4996 | 838.4996 | 838.4996 | 1582.5227 | 780 | 200 | 2562.5227 | 64.06% | 95% | 0% | -519.4508 | 319.0488 | -3550 | -400 | -3630.9512 | 90.77% | 65.48% | 95% | 0% | 1889 | -454
[5 empty] | 2019-05-25 | 21 | 3465.5 | 1339 | -527 | 1 | 0 | 1866 | 802.4732 | 802.4732 | 802.4732 | 1582.5227 | 780 | 200 | 2562.5227 | 64.06% | 95% | 0% | -602.9748 | 199.4984 | -3550 | -400 | -3750.5016 | 93.76% | 65.48% | 95% | 0% | 1866 | -527
[5 empty] | 2019-05-25 | 22 | 3466 | 1282 | -557 | 1 | 0 | 1839 | 760.1814 | 760.1814 | 760.1814 | 1580.9563 | 780 | 200 | 2560.9563 | 64.02% | 95% | 0% | -637.2998 | 122.8816 | -3550 | -400 | -3827.1184 | 95.68% | 65.48% | 95% | 0% | 1839 | -557
[5 empty] | 2019-05-25 | 23 | 3466.5 | 1258 | -568 | 1 | 0 | 1826 | 739.8186 | 739.8186 | 739.8186 | 1580.9563 | 780 | 200 | 2560.9563 | 64.02% | 95% | 0% | -649.8856 | 89.933 | -3550 | -400 | -3860.067 | 96.5% | 65.47% | 95% | 0% | 1826 | -568
[5 empty] | 2019-05-25 | 24 | 3467 | 1220 | -599 | 1 | 0 | 1819 | 728.8541 | 728.8541 | 728.8541 | 1580.9563 | 780 | 200 | 2560.9563 | 64.02% | 95% | 0% | -685.3547 | 43.4994 | -3550 | -400 | -3906.5006 | 97.66% | 65.47% | 95% | 0% | 1819 | -599
[5 empty] | 2019-05-25 | 25 | 3467.5 | 1192 | -609 | 1 | 0 | 1801 | 700.6595 | 700.6595 | 700.6595 | 1580.9563 | 780 | 200 | 2560.9563 | 64.02% | 95% | 0% | -696.7963 | 3.8632 | -3550 | -400 | -3946.1368 | 98.65% | 65.47% | 95% | 0% | 1801 | -609
[5 empty] | 2019-05-25 | 26 | 3468 | 1173 | -604 | 1 | 0 | 1777 | 663.0668 | 663.0668 | 663.0668 | 1580.9563 | 780 | 200 | 2560.9563 | 64.02% | 95% | 0% | -691.0755 | -28.0087 | -3550 | -400 | -3978.0087 | 99.45% | 65.47% | 95% | 0% | 1777 | -604
[5 empty] | 2019-05-25 | 27 | 3468.5 | 1156 | -602 | 1 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 1580.9563 | 780 | 200 | 2560.9563 | 64.02% | 95% | 0% | -688.7872 | -55.4813 | -3550 | -400 | -4005.4813 | 100.1% | 65.47% | 95% | 0% | 1758 | -602
[5 empty] | 2019-05-25 | 28 | 3469 | 1145 | -588 | 1 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 1580.9563 | 780 | 200 | 2560.9563 | 64.02% | 95% | 0% | -672.7689 | -78.6221 | -3550 | -400 | -4028.6221 | 100.7% | 65.47% | 95% | 0% | 1733 | -588
[5 empty] | 2019-05-25 | 29 | 3469.5 | 1175 | -553 | 1 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 1580.9563 | 780 | 200 | 2560.9563 | 64.02% | 95% | 0% | -632.7231 | -46.4082 | -3550 | -400 | -3996.4082 | 99.91% | 65.47% | 95% | 0% | 1728 | -553
[5 empty] | 2019-05-25 | 30 | 3470 | 1207 | -527 | 1 | 0 | 1734 | 595.7131 | 595.7131 | 595.7131 | 1580.9563 | 780 | 200 | 2560.9563 | 64.02% | 95% | 0% | -602.9748 | -7.2617 | -3550 | -400 | -3957.2617 | 98.93% | 65.46% | 95% | 0% | 1734 | -527
[5 empty] | 2019-05-25 | 31 | 3470.5 | 1271 | -475 | 1 | 0 | 1746 | 614.5095 | 614.5095 | 614.5095 | 1580.9563 | 780 | 200 | 2560.9563 | 64.02% | 95% | 0% | -543.4783 | 71.0312 | -3550 | -400 | -3878.9688 | 96.97% | 65.46% | 95% | 0% | 1746 | -475
[5 empty] | 2019-05-25 | 32 | 3471 | 1356 | -426 | 1 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 1580.9563 | 780 | 200 | 2560.9563 | 64.02% | 95% | 0% | -487.4142 | 183.4844 | -3550 | -400 | -3766.5156 | 94.16% | 65.46% | 95% | 0% | 1782 | -426
[5 empty] | 2019-05-25 | 33 | 3471.5 | 1482 | -370 | 1 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 1580.9563 | 780 | 200 | 2560.9563 | 64.02% | 95% | 0% | -423.341 | 357.2031 | -3550 | -400 | -3592.7969 | 89.82% | 65.45% | 95% | 0% | 1852 | -370
[5 empty] | 2019-05-25 | 34 | 3472 | 1607 | -322 | 1 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 1579.3899 | 780 | 200 | 2559.3899 | 63.98% | 95% | 0% | -368.4211 | 532.7331 | -3550 | -400 | -3417.2669 | 85.43% | 65.45% | 95% | 0% | 1929 | -322
[5 empty] | 2019-05-25 | 35 | 3472.5 | 1744 | -272 | 1 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 1579.3899 | 780 | 200 | 2559.3899 | 63.98% | 95% | 0% | -311.2128 | 726.2151 | -3550 | -400 | -3223.7849 | 80.59% | 65.45% | 95% | 0% | 2016 | -272
[5 empty] | 2019-05-25 | 36 | 3473 | 1861 | -224 | 1 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 1579.3899 | 780 | 200 | 2559.3899 | 63.98% | 95% | 0% | -256.2929 | 889.2141 | -3550 | -400 | -3060.7859 | 76.52% | 65.45% | 95% | 0% | 2085 | -224
[5 empty] | 2019-05-25 | 37 | 3473.5 | 1929 | -197 | 1 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 1579.3899 | 780 | 200 | 2559.3899 | 63.98% | 95% | 0% | -225.4005 | 984.3275 | -3550 | -400 | -2965.6725 | 74.14% | 65.44% | 95% | 0% | 2126 | -197
[5 empty] | 2019-05-25 | 38 | 3474 | 1986 | -165 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1579.3899 | 780 | 200 | 2559.3899 | 63.98% | 95% | 0% | -188.7872 | 1060.0999 | -3550 | -400 | -2889.9001 | 72.25% | 65.43% | 95% | 0% | 2151 | -165
[5 empty] | 2019-05-25 | 39 | 3474.5 | 2006 | -132 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1579.3899 | 780 | 200 | 2559.3899 | 63.98% | 95% | 0% | -151.0297 | 1077.4946 | -3550 | -400 | -2872.5054 | 71.81% | 65.43% | 95% | 0% | 2138 | -132
[5 empty] | 2019-05-25 | 40 | 3475 | 2011 | -105 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1579.3899 | 780 | 200 | 2559.3899 | 63.98% | 95% | 0% | -120.1373 | 1073.927 | -3550 | -400 | -2876.073 | 71.9% | 65.43% | 95% | 0% | 2116 | -105
[5 empty] | 2019-05-25 | 41 | 3475.5 | 2011 | -90 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 1579.3899 | 780 | 200 | 2559.3899 | 63.98% | 95% | 0% | -102.9748 | 1067.594 | -3550 | -400 | -2882.406 | 72.06% | 65.43% | 95% | 0% | 2101 | -90
[5 empty] | 2019-05-25 | 42 | 3476 | 1997 | -83 | 1 | 0 | 2080 | 1137.6752 | 1137.6752 | 1137.6752 | 1579.3899 | 780 | 200 | 2559.3899 | 63.98% | 95% | 0% | -94.9657 | 1042.7095 | -3550 | -400 | -2907.2905 | 72.68% | 65.43% | 95% | 0% | 2080 | -83
[5 empty] | 2019-05-25 | 43 | 3476.5 | 1977 | -83 | 1 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 1579.3899 | 780 | 200 | 2559.3899 | 63.98% | 95% | 0% | -94.9657 | 1011.3822 | -3550 | -400 | -2938.6178 | 73.47% | 65.43% | 95% | 0% | 2060 | -83
[5 empty] | 2019-05-25 | 44 | 3477 | 1964 | -85 | 0 | 0 | 2049 | 1089.1179 | 1089.1179 | 1089.1179 | 1579.3899 | 780 | 200 | 2559.3899 | 63.98% | 95% | 0% | -97.254 | 991.8639 | -2750 | -200 | -1958.1361 | 48.95% | 65.42% | 95% | 0% | 2049 | -85
[5 empty] | 2019-05-25 | 45 | 3477.5 | 1894 | -86 | 0 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 1577.8236 | 780 | 200 | 2557.8236 | 63.95% | 95% | 0% | -98.3982 | 882.6406 | -2750 | -200 | -2067.3594 | 51.68% | 65.42% | 95% | 0% | 1980 | -86
[5 empty] | 2019-05-25 | 46 | 3478 | 1790 | -87 | 0 | 0 | 1877 | 819.7032 | 819.7032 | 819.7032 | 1577.8236 | 780 | 200 | 2557.8236 | 63.95% | 95% | 0% | -99.5423 | 720.1609 | -2750 | -200 | -2229.8391 | 55.75% | 65.41% | 95% | 0% | 1877 | -87
[5 empty] | 2019-05-25 | 47 | 3478.5 | 1674 | -88 | 0 | 0 | 1762 | 639.5713 | 639.5713 | 639.5713 | 1577.8236 | 780 | 200 | 2557.8236 | 63.95% | 95% | 0% | -100.6865 | 538.8848 | -2750 | -200 | -2411.1152 | 60.28% | 65.41% | 95% | 0% | 1762 | -88
[5 empty] | 2019-05-25 | 48 | 3479 | 1568 | -89 | 0 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 1577.8236 | 780 | 200 | 2557.8236 | 63.95% | 95% | 0% | -101.8307 | 373.2724 | -2750 | -200 | -2576.7276 | 64.42% | 65.41% | 95% | 0% | 1657 | -89
[5 empty] | 2019-05-26 | 1 | 3479.5 | 1493 | -87 | 0 | 0 | 1580 | 354.493 | 354.493 | 354.493 | 1577.8236 | 780 | 200 | 2557.8236 | 63.95% | 95% | 0% | -99.5423 | 254.9507 | -2750 | -200 | -2695.0493 | 67.38% | 65.4% | 95% | 0% | 1580 | -87
[5 empty] | 2019-05-26 | 2 | 3480 | 1448 | -85 | 0 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 1577.8236 | 780 | 200 | 2557.8236 | 63.95% | 95% | 0% | -97.254 | 183.6199 | -2750 | -200 | -2766.3801 | 69.16% | 65.4% | 95% | 0% | 1533 | -85
[5 empty] | 2019-05-26 | 3 | 3480.5 | 1416 | -86 | 0 | 0 | 1502 | 232.3166 | 232.3166 | 232.3166 | 1577.8236 | 780 | 200 | 2557.8236 | 63.95% | 95% | 0% | -98.3982 | 133.9184 | -2750 | -200 | -2816.0816 | 70.4% | 65.4% | 95% | 0% | 1502 | -86
[5 empty] | 2019-05-26 | 4 | 3481 | 1406 | -86 | 0 | 0 | 1492 | 216.6529 | 216.6529 | 216.6529 | 1577.8236 | 780 | 200 | 2557.8236 | 63.95% | 95% | 0% | -98.3982 | 118.2548 | -2750 | -200 | -2831.7452 | 70.79% | 65.4% | 95% | 0% | 1492 | -86
[5 empty] | 2019-05-26 | 5 | 3481.5 | 1367 | -87 | 0 | 0 | 1454 | 157.1311 | 157.1311 | 157.1311 | 1576.2572 | 780 | 200 | 2556.2572 | 63.91% | 95% | 0% | -99.5423 | 57.5887 | -2750 | -200 | -2892.4113 | 72.31% | 65.39% | 95% | 0% | 1454 | -87
[5 empty] | 2019-05-26 | 6 | 3482 | 1339 | -88 | 0 | 0 | 1427 | 114.8392 | 114.8392 | 114.8392 | 1576.2572 | 780 | 200 | 2556.2572 | 63.91% | 95% | 0% | -100.6865 | 14.1527 | -2750 | -200 | -2935.8473 | 73.4% | 65.39% | 95% | 0% | 1427 | -88
[5 empty] | 2019-05-26 | 7 | 3482.5 | 1313 | -90 | 0 | 0 | 1403 | 77.2465 | 77.2465 | 77.2465 | 1576.2572 | 780 | 200 | 2556.2572 | 63.91% | 95% | 0% | -102.9748 | -25.7283 | -2750 | -200 | -2975.7283 | 74.39% | 65.38% | 95% | 0% | 1403 | -90
[5 empty] | 2019-05-26 | 8 | 3483 | 1299 | -93 | 1 | 0 | 1392 | 60.0165 | 60.0165 | 60.0165 | 1576.2572 | 780 | 200 | 2556.2572 | 63.91% | 95% | 0% | -106.4073 | -46.3908 | -3550 | -400 | -3996.3908 | 99.91% | 65.38% | 95% | 0% | 1392 | -93
[5 empty] | 2019-05-26 | 9 | 3483.5 | 1277 | -96 | 1 | 0 | 1373 | 30.2556 | 30.2556 | 30.2556 | 1576.2572 | 780 | 200 | 2556.2572 | 63.91% | 95% | 0% | -109.8398 | -79.5843 | -3550 | -400 | -4029.5843 | 100.7% | 65.38% | 95% | 0% | 1373 | -96
[5 empty] | 2019-05-26 | 10 | 3484 | 1234 | -100 | 1 | 0 | 1334 | -30.8326 | -30.8326 | -30.8326 | 1576.2572 | 780 | 200 | 2556.2572 | 63.91% | 95% | 0% | -114.4165 | -145.2491 | -3550 | -400 | -4095.2491 | 102.4% | 65.38% | 95% | 0% | 1334 | -100
[5 empty] | 2019-05-26 | 11 | 3484.5 | 1210 | -103 | 1 | 0 | 1313 | -63.7263 | -63.7263 | -63.7263 | 1576.2572 | 780 | 200 | 2556.2572 | 63.91% | 95% | 0% | -117.849 | -181.5753 | -3550 | -400 | -4131.5753 | 103.3% | 65.38% | 95% | 0% | 1313 | -103
[5 empty] | 2019-05-26 | 12 | 3485 | 1199 | -112 | 1 | 0 | 1311 | -66.859 | -66.859 | -66.859 | 1576.2572 | 780 | 200 | 2556.2572 | 63.91% | 95% | 0% | -128.1465 | -195.0055 | -3550 | -400 | -4145.0055 | 103.6% | 65.37% | 95% | 0% | 1311 | -112
[5 empty] | 2019-05-26 | 13 | 3485.5 | 1204 | -129 | 1 | 0 | 1333 | -32.399 | -32.399 | -32.399 | 1576.2572 | 780 | 200 | 2556.2572 | 63.91% | 95% | 0% | -147.5973 | -179.9963 | -3550 | -400 | -4129.9963 | 103.2% | 65.37% | 95% | 0% | 1333 | -129
[5 empty] | 2019-05-26 | 14 | 3486 | 1205 | -153 | 1 | 0 | 1358 | 6.7601 | 6.7601 | 6.7601 | 1576.2572 | 780 | 200 | 2556.2572 | 63.91% | 95% | 0% | -175.0572 | -168.2971 | -3550 | -400 | -4118.2971 | 103% | 65.37% | 95% | 0% | 1358 | -153
[5 empty] | 2019-05-26 | 15 | 3486.5 | 1231 | -187 | 1 | 0 | 1418 | 100.742 | 100.742 | 100.742 | 1576.2572 | 780 | 200 | 2556.2572 | 63.91% | 95% | 0% | -213.9588 | -113.2168 | -3550 | -400 | -4063.2168 | 101.6% | 65.37% | 95% | 0% | 1418 | -187
[5 empty] | 2019-05-26 | 16 | 3487 | 1256 | -221 | 1 | 0 | 1477 | 193.1575 | 193.1575 | 193.1575 | 1576.2572 | 780 | 200 | 2556.2572 | 63.91% | 95% | 0% | -252.8604 | -59.703 | -3550 | -400 | -4009.703 | 100.2% | 65.37% | 95% | 0% | 1477 | -221
[5 empty] | 2019-05-26 | 17 | 3487.5 | 1302 | -272 | 1 | 0 | 1574 | 345.0948 | 345.0948 | 345.0948 | 1574.6908 | 780 | 200 | 2554.6908 | 63.87% | 95% | 0% | -311.2128 | 33.882 | -3550 | -400 | -3916.118 | 97.9% | 65.36% | 95% | 0% | 1574 | -272
[5 empty] | 2019-05-26 | 18 | 3488 | 1317 | -319 | 1 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 1574.6908 | 780 | 200 | 2554.6908 | 63.87% | 95% | 0% | -364.9886 | 77.2208 | -3550 | -400 | -3872.7792 | 96.82% | 65.36% | 95% | 0% | 1636 | -319
[5 empty] | 2019-05-26 | 19 | 3488.5 | 1316 | -377 | 1 | 0 | 1693 | 531.4922 | 531.4922 | 531.4922 | 1574.6908 | 780 | 200 | 2554.6908 | 63.87% | 95% | 0% | -431.3501 | 100.1421 | -3550 | -400 | -3849.8579 | 96.25% | 65.36% | 95% | 0% | 1693 | -377
[5 empty] | 2019-05-26 | 20 | 3489 | 1319 | -408 | 1 | 0 | 1727 | 584.7486 | 584.7486 | 584.7486 | 1574.6908 | 780 | 200 | 2554.6908 | 63.87% | 95% | 0% | -466.8192 | 117.9293 | -3550 | -400 | -3832.0707 | 95.8% | 65.36% | 95% | 0% | 1727 | -408
[5 empty] | 2019-05-26 | 21 | 3489.5 | 1328 | -425 | 1 | 0 | 1753 | 625.474 | 625.474 | 625.474 | 1574.6908 | 780 | 200 | 2554.6908 | 63.87% | 95% | 0% | -486.27 | 139.204 | -3550 | -400 | -3810.796 | 95.27% | 65.35% | 95% | 0% | 1753 | -425
[5 empty] | 2019-05-26 | 22 | 3490 | 1310 | -448 | 1 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 1574.6908 | 780 | 200 | 2554.6908 | 63.87% | 95% | 0% | -512.5858 | 120.72 | -3550 | -400 | -3829.28 | 95.73% | 65.35% | 95% | 0% | 1758 | -448
[5 empty] | 2019-05-26 | 23 | 3490.5 | 1283 | -476 | 1 | 0 | 1759 | 634.8722 | 634.8722 | 634.8722 | 1574.6908 | 780 | 200 | 2554.6908 | 63.87% | 95% | 0% | -544.6224 | 90.2498 | -3550 | -400 | -3859.7502 | 96.49% | 65.35% | 95% | 0% | 1759 | -476
[5 empty] | 2019-05-26 | 24 | 3491 | 1261 | -506 | 1 | 0 | 1767 | 647.4031 | 647.4031 | 647.4031 | 1574.6908 | 780 | 200 | 2554.6908 | 63.87% | 95% | 0% | -578.9474 | 68.4558 | -3550 | -400 | -3881.5442 | 97.04% | 65.35% | 95% | 0% | 1767 | -506
[5 empty] | 2019-05-26 | 25 | 3491.5 | 1286 | -506 | 1 | 0 | 1792 | 686.5622 | 686.5622 | 686.5622 | 1574.6908 | 780 | 200 | 2554.6908 | 63.87% | 95% | 0% | -578.9474 | 107.6149 | -3550 | -400 | -3842.3851 | 96.06% | 65.35% | 95% | 0% | 1792 | -506
[5 empty] | 2019-05-26 | 26 | 3492 | 1296 | -499 | 1 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 1574.6908 | 780 | 200 | 2554.6908 | 63.87% | 95% | 0% | -570.9382 | 120.3231 | -3550 | -400 | -3829.6769 | 95.74% | 65.35% | 95% | 0% | 1795 | -499
[5 empty] | 2019-05-26 | 27 | 3492.5 | 1306 | -480 | 1 | 0 | 1786 | 677.1641 | 677.1641 | 677.1641 | 1574.6908 | 780 | 200 | 2554.6908 | 63.87% | 95% | 0% | -549.1991 | 127.965 | -3550 | -400 | -3822.035 | 95.55% | 65.35% | 95% | 0% | 1786 | -480
[5 empty] | 2019-05-26 | 28 | 3493 | 1244 | -519 | 1 | 0 | 1763 | 641.1377 | 641.1377 | 641.1377 | 1573.1245 | 780 | 200 | 2553.1245 | 63.83% | 95% | 0% | -593.8215 | 47.3162 | -3550 | -400 | -3902.6838 | 97.57% | 65.33% | 95% | 0% | 1763 | -519
[5 empty] | 2019-05-26 | 29 | 3493.5 | 1226 | -506 | 1 | 0 | 1732 | 592.5804 | 592.5804 | 592.5804 | 1573.1245 | 780 | 200 | 2553.1245 | 63.83% | 95% | 0% | -578.9474 | 13.633 | -3550 | -400 | -3936.367 | 98.41% | 65.33% | 95% | 0% | 1732 | -506
[5 empty] | 2019-05-26 | 30 | 3494 | 1198 | -504 | 1 | 0 | 1702 | 545.5894 | 545.5894 | 545.5894 | 1573.1245 | 780 | 200 | 2553.1245 | 63.83% | 95% | 0% | -576.659 | -31.0696 | -3550 | -400 | -3981.0696 | 99.53% | 65.33% | 95% | 0% | 1702 | -504
[5 empty] | 2019-05-26 | 31 | 3494.5 | 1191 | -494 | 1 | 0 | 1685 | 518.9613 | 518.9613 | 518.9613 | 1573.1245 | 780 | 200 | 2553.1245 | 63.83% | 95% | 0% | -565.2174 | -46.2561 | -3550 | -400 | -3996.2561 | 99.91% | 65.33% | 95% | 0% | 1685 | -494
[5 empty] | 2019-05-26 | 32 | 3495 | 1221 | -452 | 1 | 0 | 1673 | 500.1649 | 500.1649 | 500.1649 | 1573.1245 | 780 | 200 | 2553.1245 | 63.83% | 95% | 0% | -517.1625 | -16.9976 | -3550 | -400 | -3966.9976 | 99.17% | 65.33% | 95% | 0% | 1673 | -452
[5 empty] | 2019-05-26 | 33 | 3495.5 | 1268 | -444 | 1 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 1573.1245 | 780 | 200 | 2553.1245 | 63.83% | 95% | 0% | -508.0092 | 53.2439 | -3550 | -400 | -3896.7561 | 97.42% | 65.33% | 95% | 0% | 1712 | -444
[5 empty] | 2019-05-26 | 34 | 3496 | 1354 | -420 | 1 | 0 | 1774 | 658.3677 | 658.3677 | 658.3677 | 1573.1245 | 780 | 200 | 2553.1245 | 63.83% | 95% | 0% | -480.5492 | 177.8185 | -3550 | -400 | -3772.1815 | 94.3% | 65.33% | 95% | 0% | 1774 | -420
[5 empty] | 2019-05-26 | 35 | 3496.5 | 1387 | -434 | 1 | 0 | 1821 | 731.9868 | 731.9868 | 731.9868 | 1573.1245 | 780 | 200 | 2553.1245 | 63.83% | 95% | 0% | -496.5675 | 235.4193 | -3550 | -400 | -3714.5807 | 92.86% | 65.33% | 95% | 0% | 1821 | -434
[5 empty] | 2019-05-26 | 36 | 3497 | 1450 | -398 | 1 | 0 | 1848 | 774.2786 | 774.2786 | 774.2786 | 1573.1245 | 780 | 200 | 2553.1245 | 63.83% | 95% | 0% | -455.3776 | 318.9011 | -3550 | -400 | -3631.0989 | 90.78% | 65.33% | 95% | 0% | 1848 | -398
[5 empty] | 2019-05-26 | 37 | 3497.5 | 1515 | -355 | 1 | 0 | 1870 | 808.7387 | 808.7387 | 808.7387 | 1573.1245 | 780 | 200 | 2553.1245 | 63.83% | 95% | 0% | -406.1785 | 402.5602 | -3550 | -400 | -3547.4398 | 88.69% | 65.32% | 95% | 0% | 1870 | -355
[5 empty] | 2019-05-26 | 38 | 3498 | 1569 | -312 | 1 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 1573.1245 | 780 | 200 | 2553.1245 | 63.83% | 95% | 0% | -356.9794 | 468.9893 | -3550 | -400 | -3481.0107 | 87.03% | 65.32% | 95% | 0% | 1881 | -312
[5 empty] | 2019-05-26 | 39 | 3498.5 | 1629 | -277 | 1 | 0 | 1906 | 865.1278 | 865.1278 | 865.1278 | 1573.1245 | 780 | 200 | 2553.1245 | 63.83% | 95% | 0% | -316.9336 | 548.1941 | -3550 | -400 | -3401.8059 | 85.05% | 65.32% | 95% | 0% | 1906 | -277
[5 empty] | 2019-05-26 | 40 | 3499 | 1668 | -233 | 0 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -266.5904 | 590.7056 | -2750 | -200 | -2359.2944 | 58.98% | 65.32% | 95% | 0% | 1901 | -233
[5 empty] | 2019-05-26 | 41 | 3499.5 | 1707 | -192 | 1 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -219.6796 | 634.4836 | -3550 | -400 | -3315.5164 | 82.89% | 65.32% | 95% | 0% | 1899 | -192
[5 empty] | 2019-05-26 | 42 | 3500 | 1748 | -163 | 1 | 0 | 1911 | 872.9596 | 872.9596 | 872.9596 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -186.4989 | 686.4607 | -3550 | -400 | -3263.5393 | 81.59% | 65.32% | 95% | 0% | 1911 | -163
[5 empty] | 2019-05-26 | 43 | 3500.5 | 1773 | -154 | 1 | 0 | 1927 | 898.0214 | 898.0214 | 898.0214 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -176.2014 | 721.8201 | -3550 | -400 | -3228.1799 | 80.7% | 65.32% | 95% | 0% | 1927 | -154
[5 empty] | 2019-05-26 | 44 | 3501 | 1774 | -152 | 1 | 0 | 1926 | 896.4551 | 896.4551 | 896.4551 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -173.913 | 722.542 | -3550 | -400 | -3227.458 | 80.69% | 65.32% | 95% | 0% | 1926 | -152
[5 empty] | 2019-05-26 | 45 | 3501.5 | 1733 | -153 | 0 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -175.0572 | 658.7433 | -2750 | -200 | -2291.2567 | 57.28% | 65.32% | 95% | 0% | 1886 | -153
[5 empty] | 2019-05-26 | 46 | 3502 | 1646 | -154 | 0 | 0 | 1800 | 699.0932 | 699.0932 | 699.0932 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -176.2014 | 522.8918 | -2750 | -200 | -2427.1082 | 60.68% | 65.31% | 95% | 0% | 1800 | -154
[5 empty] | 2019-05-26 | 47 | 3502.5 | 1529 | -154 | 0 | 0 | 1683 | 515.8285 | 515.8285 | 515.8285 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -176.2014 | 339.6272 | -2750 | -200 | -2610.3728 | 65.26% | 65.31% | 95% | 0% | 1683 | -154
[5 empty] | 2019-05-26 | 48 | 3503 | 1424 | -154 | 0 | 0 | 1578 | 351.3603 | 351.3603 | 351.3603 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -176.2014 | 175.1589 | -2750 | -200 | -2774.8411 | 69.37% | 65.31% | 95% | 0% | 1578 | -154
[5 empty] | 2019-05-27 | 1 | 3503.5 | 1325 | -151 | 0 | 0 | 1476 | 191.5911 | 191.5911 | 191.5911 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -172.7689 | 18.8222 | -2750 | -200 | -2931.1778 | 73.28% | 65.3% | 95% | 0% | 1476 | -151
[5 empty] | 2019-05-27 | 2 | 3504 | 1282 | -147 | 0 | 0 | 1429 | 117.972 | 117.972 | 117.972 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -168.1922 | -50.2202 | -2750 | -200 | -3000.2202 | 75.01% | 65.3% | 95% | 0% | 1429 | -147
[5 empty] | 2019-05-27 | 3 | 3504.5 | 1247 | -146 | 0 | 0 | 1393 | 61.5829 | 61.5829 | 61.5829 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -167.0481 | -105.4652 | -2750 | -200 | -3055.4652 | 76.39% | 65.3% | 95% | 0% | 1393 | -146
[5 empty] | 2019-05-27 | 4 | 3505 | 1241 | -145 | 0 | 0 | 1386 | 50.6183 | 50.6183 | 50.6183 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -165.9039 | -115.2856 | -2750 | -200 | -3065.2856 | 76.63% | 65.3% | 95% | 0% | 1386 | -145
[5 empty] | 2019-05-27 | 5 | 3505.5 | 1213 | -143 | 0 | 0 | 1356 | 3.6274 | 3.6274 | 3.6274 | 1571.5581 | 780 | 200 | 2551.5581 | 63.79% | 95% | 0% | -163.6156 | -159.9882 | -2750 | -200 | -3109.9882 | 77.75% | 65.3% | 95% | 0% | 1356 | -143
[5 empty] | 2019-05-27 | 6 | 3506 | 1190 | -140 | 0 | 0 | 1330 | -37.0981 | -37.0981 | -37.0981 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -160.1831 | -197.2812 | -2750 | -200 | -3147.2812 | 78.68% | 65.3% | 95% | 0% | 1330 | -140
[5 empty] | 2019-05-27 | 7 | 3506.5 | 1175 | -138 | 0 | 0 | 1313 | -63.7263 | -63.7263 | -63.7263 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -157.8947 | -221.621 | -2750 | -200 | -3171.621 | 79.29% | 65.3% | 95% | 0% | 1313 | -138
[5 empty] | 2019-05-27 | 8 | 3507 | 1175 | -135 | 0 | 0 | 1310 | -68.4254 | -68.4254 | -68.4254 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -154.4622 | -222.8876 | -2750 | -200 | -3172.8876 | 79.32% | 65.29% | 95% | 0% | 1310 | -135
[5 empty] | 2019-05-27 | 9 | 3507.5 | 1178 | -131 | 0 | 0 | 1309 | -69.9918 | -69.9918 | -69.9918 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -149.8856 | -219.8773 | -2750 | -200 | -3169.8773 | 79.25% | 65.29% | 95% | 0% | 1309 | -131
[5 empty] | 2019-05-27 | 10 | 3508 | 1157 | -126 | 0 | 0 | 1283 | -110.7172 | -110.7172 | -110.7172 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -144.1648 | -254.882 | -2750 | -200 | -3204.882 | 80.12% | 65.29% | 95% | 0% | 1283 | -126
[5 empty] | 2019-05-27 | 11 | 3508.5 | 1168 | -127 | 0 | 0 | 1295 | -91.9209 | -91.9209 | -91.9209 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -145.3089 | -237.2298 | -2750 | -200 | -3187.2298 | 79.68% | 65.28% | 95% | 0% | 1295 | -127
[5 empty] | 2019-05-27 | 12 | 3509 | 1182 | -140 | 0 | 0 | 1322 | -49.629 | -49.629 | -49.629 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -160.1831 | -209.8121 | -2750 | -200 | -3159.8121 | 79% | 65.28% | 95% | 0% | 1322 | -140
[5 empty] | 2019-05-27 | 13 | 3509.5 | 1241 | -159 | 1 | 0 | 1400 | 72.5474 | 72.5474 | 72.5474 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -181.9222 | -109.3748 | -3550 | -400 | -4059.3748 | 101.5% | 65.28% | 95% | 0% | 1400 | -159
[5 empty] | 2019-05-27 | 14 | 3510 | 1270 | -180 | 1 | 0 | 1450 | 150.8656 | 150.8656 | 150.8656 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -205.9497 | -55.084 | -3550 | -400 | -4005.084 | 100.1% | 65.27% | 95% | 0% | 1450 | -180
[5 empty] | 2019-05-27 | 15 | 3510.5 | 1317 | -205 | 1 | 0 | 1522 | 263.6439 | 263.6439 | 263.6439 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -234.5538 | 29.0901 | -3550 | -400 | -3920.9099 | 98.02% | 65.27% | 95% | 0% | 1522 | -205
[5 empty] | 2019-05-27 | 16 | 3511 | 1347 | -237 | 1 | 0 | 1584 | 360.7585 | 360.7585 | 360.7585 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -271.167 | 89.5914 | -3550 | -400 | -3860.4086 | 96.51% | 65.27% | 95% | 0% | 1584 | -237
[5 empty] | 2019-05-27 | 17 | 3511.5 | 1405 | -268 | 1 | 0 | 1673 | 500.1649 | 500.1649 | 500.1649 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -306.6362 | 193.5287 | -3550 | -400 | -3756.4713 | 93.91% | 65.27% | 95% | 0% | 1673 | -268
[5 empty] | 2019-05-27 | 18 | 3512 | 1367 | -329 | 1 | 0 | 1696 | 536.1913 | 536.1913 | 536.1913 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -376.4302 | 159.7611 | -3550 | -400 | -3790.2389 | 94.76% | 65.27% | 95% | 0% | 1696 | -329
[5 empty] | 2019-05-27 | 19 | 3512.5 | 1343 | -407 | 1 | 0 | 1750 | 620.7749 | 620.7749 | 620.7749 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -465.6751 | 155.0999 | -3550 | -400 | -3794.9001 | 94.87% | 65.27% | 95% | 0% | 1750 | -407
[5 empty] | 2019-05-27 | 20 | 3513 | 1291 | -470 | 1 | 0 | 1761 | 638.0049 | 638.0049 | 638.0049 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -537.7574 | 100.2475 | -3550 | -400 | -3849.7525 | 96.24% | 65.26% | 95% | 0% | 1761 | -470
[5 empty] | 2019-05-27 | 21 | 3513.5 | 1289 | -505 | 1 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -577.8032 | 111.8918 | -3550 | -400 | -3838.1082 | 95.95% | 65.26% | 95% | 0% | 1794 | -505
[5 empty] | 2019-05-27 | 22 | 3514 | 1231 | -551 | 1 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -630.4348 | 40.4638 | -3550 | -400 | -3909.5362 | 97.74% | 65.26% | 95% | 0% | 1782 | -551
[5 empty] | 2019-05-27 | 23 | 3514.5 | 1202 | -591 | 1 | 0 | 1793 | 688.1286 | 688.1286 | 688.1286 | 1569.9918 | 780 | 200 | 2549.9918 | 63.75% | 95% | 0% | -676.2014 | 11.9272 | -3550 | -400 | -3938.0728 | 98.45% | 65.26% | 95% | 0% | 1793 | -591
[5 empty] | 2019-05-27 | 24 | 3515 | 1246 | -571 | 1 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 1568.4254 | 780 | 200 | 2548.4254 | 63.71% | 95% | 0% | -653.3181 | 72.4033 | -3550 | -400 | -3877.5967 | 96.94% | 65.25% | 95% | 0% | 1817 | -571
[5 empty] | 2019-05-27 | 25 | 3515.5 | 1334 | -516 | 1 | 0 | 1850 | 777.4114 | 777.4114 | 777.4114 | 1568.4254 | 780 | 200 | 2548.4254 | 63.71% | 95% | 0% | -590.389 | 187.0224 | -3550 | -400 | -3762.9776 | 94.07% | 65.25% | 95% | 0% | 1850 | -516
[5 empty] | 2019-05-27 | 26 | 3516 | 1280 | -551 | 1 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 1568.4254 | 780 | 200 | 2548.4254 | 63.71% | 95% | 0% | -630.4348 | 117.2157 | -3550 | -400 | -3832.7843 | 95.82% | 65.24% | 95% | 0% | 1831 | -551
[5 empty] | 2019-05-27 | 27 | 3516.5 | 1291 | -542 | 1 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 1568.4254 | 780 | 200 | 2548.4254 | 63.71% | 95% | 0% | -620.1373 | 130.6459 | -3550 | -400 | -3819.3541 | 95.48% | 65.24% | 95% | 0% | 1833 | -542
[5 empty] | 2019-05-27 | 28 | 3517 | 1294 | -514 | 1 | 0 | 1808 | 711.6241 | 711.6241 | 711.6241 | 1568.4254 | 780 | 200 | 2548.4254 | 63.71% | 95% | 0% | -588.1007 | 123.5234 | -3550 | -400 | -3826.4766 | 95.66% | 65.24% | 95% | 0% | 1808 | -514
[5 empty] | 2019-05-27 | 29 | 3517.5 | 1272 | -516 | 1 | 0 | 1788 | 680.2968 | 680.2968 | 680.2968 | 1568.4254 | 780 | 200 | 2548.4254 | 63.71% | 95% | 0% | -590.389 | 89.9078 | -3550 | -400 | -3860.0922 | 96.5% | 65.24% | 95% | 0% | 1788 | -516
[5 empty] | 2019-05-27 | 30 | 3518 | 1302 | -475 | 1 | 0 | 1777 | 663.0668 | 663.0668 | 663.0668 | 1568.4254 | 780 | 200 | 2548.4254 | 63.71% | 95% | 0% | -543.4783 | 119.5885 | -3550 | -400 | -3830.4115 | 95.76% | 65.24% | 95% | 0% | 1777 | -475
[5 empty] | 2019-05-27 | 31 | 3518.5 | 1339 | -462 | 1 | 0 | 1801 | 700.6595 | 700.6595 | 700.6595 | 1568.4254 | 780 | 200 | 2548.4254 | 63.71% | 95% | 0% | -528.6041 | 172.0554 | -3550 | -400 | -3777.9446 | 94.45% | 65.23% | 95% | 0% | 1801 | -462
[5 empty] | 2019-05-27 | 32 | 3519 | 1388 | -425 | 1 | 0 | 1813 | 719.4559 | 719.4559 | 719.4559 | 1568.4254 | 780 | 200 | 2548.4254 | 63.71% | 95% | 0% | -486.27 | 233.1859 | -3550 | -400 | -3716.8141 | 92.92% | 65.22% | 95% | 0% | 1813 | -425
[5 empty] | 2019-05-27 | 33 | 3519.5 | 1519 | -376 | 1 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 1568.4254 | 780 | 200 | 2548.4254 | 63.71% | 95% | 0% | -430.2059 | 417.6918 | -3550 | -400 | -3532.3082 | 88.31% | 65.22% | 95% | 0% | 1895 | -376
[5 empty] | 2019-05-27 | 34 | 3520 | 1646 | -340 | 1 | 0 | 1986 | 990.4369 | 990.4369 | 990.4369 | 1568.4254 | 780 | 200 | 2548.4254 | 63.71% | 95% | 0% | -389.016 | 601.4209 | -3550 | -400 | -3348.5791 | 83.71% | 65.22% | 95% | 0% | 1986 | -340
[5 empty] | 2019-05-27 | 35 | 3520.5 | 1784 | -301 | 1 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -344.3936 | 801.1134 | -3550 | -400 | -3148.8866 | 78.72% | 65.22% | 95% | 0% | 2085 | -301
[5 empty] | 2019-05-27 | 36 | 3521 | 1898 | -254 | 1 | 0 | 2152 | 1250.4534 | 1250.4534 | 1250.4534 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -290.6178 | 959.8356 | -3550 | -400 | -2990.1644 | 74.75% | 65.21% | 95% | 0% | 2152 | -254
[5 empty] | 2019-05-27 | 37 | 3521.5 | 1982 | -207 | 1 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -236.8421 | 1071.5668 | -3550 | -400 | -2878.4332 | 71.96% | 65.21% | 95% | 0% | 2189 | -207
[5 empty] | 2019-05-27 | 38 | 3522 | 2049 | -156 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -178.4897 | 1154.981 | -3550 | -400 | -2795.019 | 69.88% | 65.21% | 95% | 0% | 2205 | -156
[5 empty] | 2019-05-27 | 39 | 3522.5 | 2099 | -121 | 1 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -138.4439 | 1218.5223 | -3550 | -400 | -2731.4777 | 68.29% | 65.2% | 95% | 0% | 2220 | -121
[5 empty] | 2019-05-27 | 40 | 3523 | 2118 | -96 | 1 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -109.8398 | 1237.7282 | -3550 | -400 | -2712.2718 | 67.81% | 65.2% | 95% | 0% | 2214 | -96
[5 empty] | 2019-05-27 | 41 | 3523.5 | 2125 | -72 | 1 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -82.3799 | 1238.56 | -3550 | -400 | -2711.44 | 67.79% | 65.2% | 95% | 0% | 2197 | -72
[5 empty] | 2019-05-27 | 42 | 3524 | 2129 | -60 | 1 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -68.6499 | 1239.759 | -3550 | -400 | -2710.241 | 67.76% | 65.2% | 95% | 0% | 2189 | -60
[5 empty] | 2019-05-27 | 43 | 3524.5 | 2111 | -55 | 1 | 0 | 2166 | 1272.3825 | 1272.3825 | 1272.3825 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -62.9291 | 1209.4535 | -3550 | -400 | -2740.5465 | 68.51% | 65.19% | 95% | 0% | 2166 | -55
[5 empty] | 2019-05-27 | 44 | 3525 | 2084 | -53 | 1 | 0 | 2137 | 1226.958 | 1226.958 | 1226.958 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -60.6407 | 1166.3172 | -3550 | -400 | -2783.6828 | 69.59% | 65.18% | 95% | 0% | 2137 | -53
[5 empty] | 2019-05-27 | 45 | 3525.5 | 2036 | -53 | 0 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -60.6407 | 1091.1317 | -2750 | -200 | -1858.8683 | 46.47% | 65.18% | 95% | 0% | 2089 | -53
[5 empty] | 2019-05-27 | 46 | 3526 | 1936 | -53 | 0 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -60.6407 | 934.4953 | -2750 | -200 | -2015.5047 | 50.39% | 65.18% | 95% | 0% | 1989 | -53
[5 empty] | 2019-05-27 | 47 | 3526.5 | 1791 | -53 | 0 | 0 | 1844 | 768.0132 | 768.0132 | 768.0132 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -60.6407 | 707.3725 | -2750 | -200 | -2242.6275 | 56.07% | 65.17% | 95% | 0% | 1844 | -53
[5 empty] | 2019-05-27 | 48 | 3527 | 1691 | -53 | 0 | 0 | 1744 | 611.3768 | 611.3768 | 611.3768 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -60.6407 | 550.736 | -2750 | -200 | -2399.264 | 59.98% | 65.16% | 95% | 0% | 1744 | -53
[5 empty] | 2019-05-28 | 1 | 3527.5 | 1609 | -52 | 0 | 0 | 1661 | 481.3685 | 481.3685 | 481.3685 | 1566.859 | 780 | 200 | 2546.859 | 63.67% | 95% | 0% | -59.4966 | 421.8719 | -2750 | -200 | -2528.1281 | 63.2% | 65.16% | 95% | 0% | 1661 | -52
[5 empty] | 2019-05-28 | 2 | 3528 | 1552 | -51 | 0 | 0 | 1603 | 390.5194 | 390.5194 | 390.5194 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -58.3524 | 332.167 | -2750 | -200 | -2617.833 | 65.45% | 65.16% | 95% | 0% | 1603 | -51
[5 empty] | 2019-05-28 | 3 | 3528.5 | 1519 | -53 | 0 | 0 | 1572 | 341.9621 | 341.9621 | 341.9621 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -60.6407 | 281.3213 | -2750 | -200 | -2668.6787 | 66.72% | 65.16% | 95% | 0% | 1572 | -53
[5 empty] | 2019-05-28 | 4 | 3529 | 1517 | -56 | 0 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -64.0732 | 279.4552 | -2750 | -200 | -2670.5448 | 66.76% | 65.16% | 95% | 0% | 1573 | -56
[5 empty] | 2019-05-28 | 5 | 3529.5 | 1492 | -57 | 0 | 0 | 1549 | 305.9357 | 305.9357 | 305.9357 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -65.2174 | 240.7183 | -2750 | -200 | -2709.2817 | 67.73% | 65.16% | 95% | 0% | 1549 | -57
[5 empty] | 2019-05-28 | 6 | 3530 | 1470 | -59 | 0 | 0 | 1529 | 274.6084 | 274.6084 | 274.6084 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -67.5057 | 207.1027 | -2750 | -200 | -2742.8973 | 68.57% | 65.15% | 95% | 0% | 1529 | -59
[5 empty] | 2019-05-28 | 7 | 3530.5 | 1453 | -61 | 0 | 0 | 1514 | 251.1129 | 251.1129 | 251.1129 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -69.7941 | 181.3189 | -2750 | -200 | -2768.6811 | 69.22% | 65.15% | 95% | 0% | 1514 | -61
[5 empty] | 2019-05-28 | 8 | 3531 | 1446 | -63 | 0 | 0 | 1509 | 243.2811 | 243.2811 | 243.2811 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -72.0824 | 171.1987 | -2750 | -200 | -2778.8013 | 69.47% | 65.15% | 95% | 0% | 1509 | -63
[5 empty] | 2019-05-28 | 9 | 3531.5 | 1438 | -64 | 0 | 0 | 1502 | 232.3166 | 232.3166 | 232.3166 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -73.2265 | 159.09 | -2750 | -200 | -2790.91 | 69.77% | 65.15% | 95% | 0% | 1502 | -64
[5 empty] | 2019-05-28 | 10 | 3532 | 1432 | -64 | 0 | 0 | 1496 | 222.9184 | 222.9184 | 222.9184 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -73.2265 | 149.6918 | -2750 | -200 | -2800.3082 | 70.01% | 65.15% | 95% | 0% | 1496 | -64
[5 empty] | 2019-05-28 | 11 | 3532.5 | 1459 | -67 | 0 | 0 | 1526 | 269.9093 | 269.9093 | 269.9093 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -76.659 | 193.2503 | -2750 | -200 | -2756.7497 | 68.92% | 65.14% | 95% | 0% | 1526 | -67
[5 empty] | 2019-05-28 | 12 | 3533 | 1518 | -81 | 0 | 0 | 1599 | 384.2539 | 384.2539 | 384.2539 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -92.6773 | 291.5766 | -2750 | -200 | -2658.4234 | 66.46% | 65.14% | 95% | 0% | 1599 | -81
[5 empty] | 2019-05-28 | 13 | 3533.5 | 1661 | -108 | 1 | 0 | 1769 | 650.5359 | 650.5359 | 650.5359 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -123.5698 | 526.9661 | -3550 | -400 | -3423.0339 | 85.58% | 65.14% | 95% | 0% | 1769 | -108
[5 empty] | 2019-05-28 | 14 | 3534 | 1766 | -142 | 1 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -162.4714 | 705.7891 | -3550 | -400 | -3244.2109 | 81.11% | 65.14% | 95% | 0% | 1908 | -142
[5 empty] | 2019-05-28 | 15 | 3534.5 | 1901 | -182 | 1 | 0 | 2083 | 1142.3743 | 1142.3743 | 1142.3743 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -208.238 | 934.1363 | -3550 | -400 | -3015.8637 | 75.4% | 65.14% | 95% | 0% | 2083 | -182
[5 empty] | 2019-05-28 | 16 | 3535 | 1951 | -233 | 1 | 0 | 2184 | 1300.5771 | 1300.5771 | 1300.5771 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -266.5904 | 1033.9867 | -3550 | -400 | -2916.0133 | 72.9% | 65.12% | 95% | 0% | 2184 | -233
[5 empty] | 2019-05-28 | 17 | 3535.5 | 1978 | -293 | 1 | 0 | 2271 | 1436.8508 | 1436.8508 | 1436.8508 | 1565.2927 | 780 | 200 | 2545.2927 | 63.63% | 95% | 0% | -335.2403 | 1101.6105 | -3550 | -400 | -2848.3895 | 71.21% | 65.12% | 95% | 0% | 2271 | -293
[5 empty] | 2019-05-28 | 18 | 3536 | 1979 | -313 | 1 | 0 | 2292 | 1469.7444 | 1469.7444 | 1469.7444 | 1563.7263 | 780 | 200 | 2543.7263 | 63.59% | 95% | 0% | -358.1236 | 1111.6209 | -3550 | -400 | -2838.3791 | 70.96% | 65.12% | 95% | 0% | 2292 | -313
[5 empty] | 2019-05-28 | 19 | 3536.5 | 1974 | -344 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 1563.7263 | 780 | 200 | 2543.7263 | 63.59% | 95% | 0% | -393.5927 | 1116.8772 | -3550 | -400 | -2833.1228 | 70.83% | 65.12% | 95% | 0% | 2318 | -344
[5 empty] | 2019-05-28 | 20 | 3537 | 1929 | -367 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1563.7263 | 780 | 200 | 2543.7263 | 63.59% | 95% | 0% | -419.9085 | 1056.1014 | -3550 | -400 | -2893.8986 | 72.35% | 65.12% | 95% | 0% | 2296 | -367
[5 empty] | 2019-05-28 | 21 | 3537.5 | 1907 | -389 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1563.7263 | 780 | 200 | 2543.7263 | 63.59% | 95% | 0% | -445.0801 | 1030.9298 | -3550 | -400 | -2919.0702 | 72.98% | 65.11% | 95% | 0% | 2296 | -389
[5 empty] | 2019-05-28 | 22 | 3538 | 1871 | -403 | 1 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 1563.7263 | 780 | 200 | 2543.7263 | 63.59% | 95% | 0% | -461.0984 | 980.4515 | -3550 | -400 | -2969.5485 | 74.24% | 65.11% | 95% | 0% | 2274 | -403
[5 empty] | 2019-05-28 | 23 | 3538.5 | 1838 | -424 | 1 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 1563.7263 | 780 | 200 | 2543.7263 | 63.59% | 95% | 0% | -485.1259 | 937.6276 | -3550 | -400 | -3012.3724 | 75.31% | 65.11% | 95% | 0% | 2262 | -424
[5 empty] | 2019-05-28 | 24 | 3539 | 1837 | -418 | 1 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 1563.7263 | 780 | 200 | 2543.7263 | 63.59% | 95% | 0% | -478.2609 | 933.5281 | -3550 | -400 | -3016.4719 | 75.41% | 65.1% | 95% | 0% | 2255 | -418
[5 empty] | 2019-05-28 | 25 | 3539.5 | 1792 | -447 | 1 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 1563.7263 | 780 | 200 | 2543.7263 | 63.59% | 95% | 0% | -511.4416 | 875.2855 | -3550 | -400 | -3074.7145 | 76.87% | 65.1% | 95% | 0% | 2239 | -447
[5 empty] | 2019-05-28 | 26 | 3540 | 1785 | -459 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1563.7263 | 780 | 200 | 2543.7263 | 63.59% | 95% | 0% | -525.1716 | 869.3873 | -3550 | -400 | -3080.6127 | 77.02% | 65.1% | 95% | 0% | 2244 | -459
[5 empty] | 2019-05-28 | 27 | 3540.5 | 1751 | -477 | 1 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 1563.7263 | 780 | 200 | 2543.7263 | 63.59% | 95% | 0% | -545.7666 | 823.7305 | -3550 | -400 | -3126.2695 | 78.16% | 65.1% | 95% | 0% | 2228 | -477
[5 empty] | 2019-05-28 | 28 | 3541 | 1741 | -469 | 1 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 1563.7263 | 780 | 200 | 2543.7263 | 63.59% | 95% | 0% | -536.6133 | 804.6893 | -3550 | -400 | -3145.3107 | 78.63% | 65.1% | 95% | 0% | 2210 | -469
[5 empty] | 2019-05-28 | 29 | 3541.5 | 1663 | -523 | 1 | 0 | 2186 | 1303.7098 | 1303.7098 | 1303.7098 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -598.3982 | 705.3116 | -3550 | -400 | -3244.6884 | 81.12% | 65.08% | 95% | 0% | 2186 | -523
[5 empty] | 2019-05-28 | 30 | 3542 | 1642 | -514 | 1 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -588.1007 | 668.6182 | -3550 | -400 | -3281.3818 | 82.03% | 65.08% | 95% | 0% | 2156 | -514
[5 empty] | 2019-05-28 | 31 | 3542.5 | 1673 | -480 | 1 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -549.1991 | 702.8207 | -3550 | -400 | -3247.1793 | 81.18% | 65.08% | 95% | 0% | 2153 | -480
[5 empty] | 2019-05-28 | 32 | 3543 | 1753 | -426 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -487.4142 | 805.3311 | -3550 | -400 | -3144.6689 | 78.62% | 65.08% | 95% | 0% | 2179 | -426
[5 empty] | 2019-05-28 | 33 | 3543.5 | 1765 | -440 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -503.4325 | 830.0382 | -3550 | -400 | -3119.9618 | 78% | 65.08% | 95% | 0% | 2205 | -440
[5 empty] | 2019-05-28 | 34 | 3544 | 1870 | -385 | 1 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -440.5034 | 971.2855 | -3550 | -400 | -2978.7145 | 74.47% | 65.07% | 95% | 0% | 2255 | -385
[5 empty] | 2019-05-28 | 35 | 3544.5 | 1973 | -366 | 1 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -418.7643 | 1124.5993 | -3550 | -400 | -2825.4007 | 70.64% | 65.07% | 95% | 0% | 2339 | -366
[5 empty] | 2019-05-28 | 36 | 3545 | 2077 | -310 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -354.6911 | 1263.858 | -3550 | -400 | -2686.142 | 67.15% | 65.07% | 95% | 0% | 2387 | -310
[5 empty] | 2019-05-28 | 37 | 3545.5 | 2154 | -257 | 1 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -294.0503 | 1362.0915 | -3550 | -400 | -2587.9085 | 64.7% | 65.07% | 95% | 0% | 2411 | -257
[5 empty] | 2019-05-28 | 38 | 3546 | 2236 | -205 | 1 | 0 | 2441 | 1703.1327 | 1703.1327 | 1703.1327 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -234.5538 | 1468.579 | -3550 | -400 | -2481.421 | 62.04% | 65.06% | 95% | 0% | 2441 | -205
[5 empty] | 2019-05-28 | 39 | 3546.5 | 2302 | -143 | 1 | 0 | 2445 | 1709.3982 | 1709.3982 | 1709.3982 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -163.6156 | 1545.7826 | -3550 | -400 | -2404.2174 | 60.11% | 65.06% | 95% | 0% | 2445 | -143
[5 empty] | 2019-05-28 | 40 | 3547 | 2338 | -100 | 1 | 0 | 2438 | 1698.4336 | 1698.4336 | 1698.4336 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -114.4165 | 1584.0172 | -3550 | -400 | -2365.9828 | 59.15% | 65.06% | 95% | 0% | 2438 | -100
[5 empty] | 2019-05-28 | 41 | 3547.5 | 2345 | -63 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 1562.1599 | 780 | 200 | 2542.1599 | 63.55% | 95% | 0% | -72.0824 | 1579.3603 | -3550 | -400 | -2370.6397 | 59.27% | 65.06% | 95% | 0% | 2408 | -63
[5 empty] | 2019-05-28 | 42 | 3548 | 2341 | -41 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 1560.5936 | 780 | 200 | 2540.5936 | 63.51% | 95% | 0% | -46.9108 | 1563.8065 | -3550 | -400 | -2386.1935 | 59.65% | 65.05% | 95% | 0% | 2382 | -41
[5 empty] | 2019-05-28 | 43 | 3548.5 | 2331 | -35 | 1 | 0 | 2366 | 1585.6554 | 1585.6554 | 1585.6554 | 1560.5936 | 780 | 200 | 2540.5936 | 63.51% | 95% | 0% | -40.0458 | 1545.6096 | -3550 | -400 | -2404.3904 | 60.11% | 65.05% | 95% | 0% | 2366 | -35
[5 empty] | 2019-05-28 | 44 | 3549 | 2305 | -33 | 1 | 0 | 2338 | 1541.7972 | 1541.7972 | 1541.7972 | 1560.5936 | 780 | 200 | 2540.5936 | 63.51% | 95% | 0% | -37.7574 | 1504.0398 | -3550 | -400 | -2445.9602 | 61.15% | 65.05% | 95% | 0% | 2338 | -33
[5 empty] | 2019-05-28 | 45 | 3549.5 | 2235 | -31 | 1 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 1560.5936 | 780 | 200 | 2540.5936 | 63.51% | 95% | 0% | -35.4691 | 1393.5499 | -3550 | -400 | -2556.4501 | 63.91% | 65.05% | 95% | 0% | 2266 | -31
[5 empty] | 2019-05-28 | 46 | 3550 | 2108 | -29 | 0 | 0 | 2137 | 1226.958 | 1226.958 | 1226.958 | 1560.5936 | 780 | 200 | 2540.5936 | 63.51% | 95% | 0% | -33.1808 | 1193.7772 | -2750 | -200 | -1756.2228 | 43.91% | 65.04% | 95% | 0% | 2137 | -29
[5 empty] | 2019-05-28 | 47 | 3550.5 | 1950 | -28 | 0 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 1560.5936 | 780 | 200 | 2540.5936 | 63.51% | 95% | 0% | -32.0366 | 945.8694 | -2750 | -200 | -2004.1306 | 50.1% | 65.04% | 95% | 0% | 1978 | -28
[5 empty] | 2019-05-28 | 48 | 3551 | 1841 | -27 | 0 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 1560.5936 | 780 | 200 | 2540.5936 | 63.51% | 95% | 0% | -30.8924 | 774.7135 | -2750 | -200 | -2175.2865 | 54.38% | 65.03% | 95% | 0% | 1868 | -27
[5 empty] | 2019-05-29 | 1 | 3551.5 | 1742 | -26 | 0 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 1560.5936 | 780 | 200 | 2540.5936 | 63.51% | 95% | 0% | -29.7483 | 619.2212 | -2750 | -200 | -2330.7788 | 58.27% | 65.03% | 95% | 0% | 1768 | -26
[5 empty] | 2019-05-29 | 2 | 3552 | 1689 | -25 | 0 | 0 | 1714 | 564.3858 | 564.3858 | 564.3858 | 1560.5936 | 780 | 200 | 2540.5936 | 63.51% | 95% | 0% | -28.6041 | 535.7817 | -2750 | -200 | -2414.2183 | 60.36% | 65.03% | 95% | 0% | 1714 | -25
[5 empty] | 2019-05-29 | 3 | 3552.5 | 1659 | -25 | 0 | 0 | 1684 | 517.3949 | 517.3949 | 517.3949 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -28.6041 | 488.7908 | -2750 | -200 | -2461.2092 | 61.53% | 65.03% | 95% | 0% | 1684 | -25
[5 empty] | 2019-05-29 | 4 | 3553 | 1654 | -26 | 0 | 0 | 1680 | 511.1294 | 511.1294 | 511.1294 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -29.7483 | 481.3811 | -2750 | -200 | -2468.6189 | 61.72% | 65.03% | 95% | 0% | 1680 | -26
[5 empty] | 2019-05-29 | 5 | 3553.5 | 1633 | -27 | 0 | 0 | 1660 | 479.8021 | 479.8021 | 479.8021 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -30.8924 | 448.9097 | -2750 | -200 | -2501.0903 | 62.53% | 65.03% | 95% | 0% | 1660 | -27
[5 empty] | 2019-05-29 | 6 | 3554 | 1609 | -28 | 0 | 0 | 1637 | 443.7758 | 443.7758 | 443.7758 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -32.0366 | 411.7391 | -2750 | -200 | -2538.2609 | 63.46% | 65.03% | 95% | 0% | 1637 | -28
[5 empty] | 2019-05-29 | 7 | 3554.5 | 1578 | -30 | 0 | 0 | 1608 | 398.3512 | 398.3512 | 398.3512 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -34.3249 | 364.0263 | -2750 | -200 | -2585.9737 | 64.65% | 65.02% | 95% | 0% | 1608 | -30
[5 empty] | 2019-05-29 | 8 | 3555 | 1562 | -31 | 0 | 0 | 1593 | 374.8557 | 374.8557 | 374.8557 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -35.4691 | 339.3866 | -2750 | -200 | -2610.6134 | 65.27% | 65.02% | 95% | 0% | 1593 | -31
[5 empty] | 2019-05-29 | 9 | 3555.5 | 1553 | -34 | 0 | 0 | 1587 | 365.4575 | 365.4575 | 365.4575 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -38.9016 | 326.5559 | -2750 | -200 | -2623.4441 | 65.59% | 65.01% | 95% | 0% | 1587 | -34
[5 empty] | 2019-05-29 | 10 | 3556 | 1530 | -37 | 0 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -42.3341 | 291.7962 | -2750 | -200 | -2658.2038 | 66.46% | 65% | 95% | 0% | 1567 | -37
[5 empty] | 2019-05-29 | 11 | 3556.5 | 1550 | -47 | 0 | 0 | 1597 | 381.1212 | 381.1212 | 381.1212 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -53.7757 | 327.3454 | -2750 | -200 | -2622.6546 | 65.57% | 65% | 95% | 0% | 1597 | -47
[5 empty] | 2019-05-29 | 12 | 3557 | 1590 | -67 | 1 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -76.659 | 398.444 | -3550 | -400 | -3551.556 | 88.79% | 65% | 95% | 0% | 1657 | -67
[5 empty] | 2019-05-29 | 13 | 3557.5 | 1729 | -96 | 1 | 0 | 1825 | 738.2523 | 738.2523 | 738.2523 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -109.8398 | 628.4125 | -3550 | -400 | -3321.5875 | 83.04% | 65% | 95% | 0% | 1825 | -96
[5 empty] | 2019-05-29 | 14 | 3558 | 1837 | -129 | 1 | 0 | 1966 | 959.1096 | 959.1096 | 959.1096 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -147.5973 | 811.5124 | -3550 | -400 | -3138.4876 | 78.46% | 64.99% | 95% | 0% | 1966 | -129
[5 empty] | 2019-05-29 | 15 | 3558.5 | 1976 | -165 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1559.0272 | 780 | 200 | 2539.0272 | 63.48% | 95% | 0% | -188.7872 | 1044.4362 | -3550 | -400 | -2905.5638 | 72.64% | 64.99% | 95% | 0% | 2141 | -165
[5 empty] | 2019-05-29 | 16 | 3559 | 2056 | -193 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1557.4608 | 780 | 200 | 2537.4608 | 63.44% | 95% | 0% | -220.8238 | 1181.567 | -3550 | -400 | -2768.433 | 69.21% | 64.99% | 95% | 0% | 2249 | -193
[5 empty] | 2019-05-29 | 17 | 3559.5 | 2092 | -245 | 1 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 1557.4608 | 780 | 200 | 2537.4608 | 63.44% | 95% | 0% | -280.3204 | 1259.9105 | -3550 | -400 | -2690.0895 | 67.25% | 64.99% | 95% | 0% | 2337 | -245
[5 empty] | 2019-05-29 | 18 | 3560 | 2068 | -295 | 1 | 0 | 2363 | 1580.9563 | 1580.9563 | 1580.9563 | 1557.4608 | 780 | 200 | 2537.4608 | 63.44% | 95% | 0% | -337.5286 | 1243.4277 | -3550 | -400 | -2706.5723 | 67.66% | 64.99% | 95% | 0% | 2363 | -295
[5 empty] | 2019-05-29 | 19 | 3560.5 | 2044 | -341 | 1 | 0 | 2385 | 1615.4163 | 1615.4163 | 1615.4163 | 1557.4608 | 780 | 200 | 2537.4608 | 63.44% | 95% | 0% | -390.1602 | 1225.2561 | -3550 | -400 | -2724.7439 | 68.12% | 64.98% | 95% | 0% | 2385 | -341
[5 empty] | 2019-05-29 | 20 | 3561 | 2000 | -384 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1557.4608 | 780 | 200 | 2537.4608 | 63.44% | 95% | 0% | -439.3593 | 1174.4907 | -3550 | -400 | -2775.5093 | 69.39% | 64.98% | 95% | 0% | 2384 | -384
[5 empty] | 2019-05-29 | 21 | 3561.5 | 2001 | -381 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 1557.4608 | 780 | 200 | 2537.4608 | 63.44% | 95% | 0% | -435.9268 | 1174.7905 | -3550 | -400 | -2775.2095 | 69.38% | 64.98% | 95% | 0% | 2382 | -381
[5 empty] | 2019-05-29 | 22 | 3562 | 1983 | -391 | 1 | 0 | 2374 | 1598.1863 | 1598.1863 | 1598.1863 | 1557.4608 | 780 | 200 | 2537.4608 | 63.44% | 95% | 0% | -447.3684 | 1150.8179 | -3550 | -400 | -2799.1821 | 69.98% | 64.98% | 95% | 0% | 2374 | -391
[5 empty] | 2019-05-29 | 23 | 3562.5 | 1974 | -402 | 1 | 0 | 2376 | 1601.319 | 1601.319 | 1601.319 | 1557.4608 | 780 | 200 | 2537.4608 | 63.44% | 95% | 0% | -459.9542 | 1141.3648 | -3550 | -400 | -2808.6352 | 70.22% | 64.97% | 95% | 0% | 2376 | -402
[5 empty] | 2019-05-29 | 24 | 3563 | 1968 | -410 | 1 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 1557.4608 | 780 | 200 | 2537.4608 | 63.44% | 95% | 0% | -469.1076 | 1135.3442 | -3550 | -400 | -2814.6558 | 70.37% | 64.97% | 95% | 0% | 2378 | -410
[5 empty] | 2019-05-29 | 25 | 3563.5 | 1985 | -406 | 1 | 0 | 2391 | 1624.8145 | 1624.8145 | 1624.8145 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -464.5309 | 1160.2836 | -3550 | -400 | -2789.7164 | 69.74% | 64.97% | 95% | 0% | 2391 | -406
[5 empty] | 2019-05-29 | 26 | 3564 | 2007 | -377 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -431.3501 | 1182.4998 | -3550 | -400 | -2767.5002 | 69.19% | 64.97% | 95% | 0% | 2384 | -377
[5 empty] | 2019-05-29 | 27 | 3564.5 | 2033 | -353 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -403.8902 | 1213.0925 | -3550 | -400 | -2736.9075 | 68.42% | 64.97% | 95% | 0% | 2386 | -353
[5 empty] | 2019-05-29 | 28 | 3565 | 2047 | -337 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -385.5835 | 1228.2664 | -3550 | -400 | -2721.7336 | 68.04% | 64.97% | 95% | 0% | 2384 | -337
[5 empty] | 2019-05-29 | 29 | 3565.5 | 2091 | -296 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -338.6728 | 1279.8763 | -3550 | -400 | -2670.1237 | 66.75% | 64.96% | 95% | 0% | 2387 | -296
[5 empty] | 2019-05-29 | 30 | 3566 | 2098 | -284 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -324.9428 | 1285.7744 | -3550 | -400 | -2664.2256 | 66.61% | 64.96% | 95% | 0% | 2382 | -284
[5 empty] | 2019-05-29 | 31 | 3566.5 | 2127 | -278 | 1 | 0 | 2405 | 1646.7436 | 1646.7436 | 1646.7436 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -318.0778 | 1328.6658 | -3550 | -400 | -2621.3342 | 65.53% | 64.96% | 95% | 0% | 2405 | -278
[5 empty] | 2019-05-29 | 32 | 3567 | 2157 | -275 | 1 | 0 | 2432 | 1689.0354 | 1689.0354 | 1689.0354 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -314.6453 | 1374.3901 | -3550 | -400 | -2575.6099 | 64.39% | 64.96% | 95% | 0% | 2432 | -275
[5 empty] | 2019-05-29 | 33 | 3567.5 | 2237 | -227 | 1 | 0 | 2464 | 1739.1591 | 1739.1591 | 1739.1591 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -259.7254 | 1479.4337 | -3550 | -400 | -2470.5663 | 61.76% | 64.96% | 95% | 0% | 2464 | -227
[5 empty] | 2019-05-29 | 34 | 3568 | 2318 | -209 | 1 | 0 | 2527 | 1837.8401 | 1837.8401 | 1837.8401 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -239.1304 | 1598.7096 | -3550 | -400 | -2351.2904 | 58.78% | 64.96% | 95% | 0% | 2527 | -209
[5 empty] | 2019-05-29 | 35 | 3568.5 | 2375 | -190 | 1 | 0 | 2565 | 1897.3619 | 1897.3619 | 1897.3619 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -217.3913 | 1679.9706 | -3550 | -400 | -2270.0294 | 56.75% | 64.95% | 95% | 0% | 2565 | -190
[5 empty] | 2019-05-29 | 36 | 3569 | 2418 | -175 | 1 | 0 | 2593 | 1941.2201 | 1941.2201 | 1941.2201 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -200.2288 | 1740.9913 | -3550 | -400 | -2209.0087 | 55.23% | 64.94% | 95% | 0% | 2593 | -175
[5 empty] | 2019-05-29 | 37 | 3569.5 | 2458 | -156 | 1 | 0 | 2614 | 1974.1138 | 1974.1138 | 1974.1138 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -178.4897 | 1795.6241 | -3550 | -400 | -2154.3759 | 53.86% | 64.94% | 95% | 0% | 2614 | -156
[5 empty] | 2019-05-29 | 38 | 3570 | 2469 | -142 | 1 | 0 | 2611 | 1969.4147 | 1969.4147 | 1969.4147 | 1555.8945 | 780 | 200 | 2535.8945 | 63.4% | 95% | 0% | -162.4714 | 1806.9433 | -3550 | -400 | -2143.0567 | 53.58% | 64.93% | 95% | 0% | 2611 | -142
[5 empty] | 2019-05-29 | 39 | 3570.5 | 2462 | -126 | 1 | 0 | 2588 | 1933.3883 | 1933.3883 | 1933.3883 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -144.1648 | 1789.2235 | -3550 | -400 | -2160.7765 | 54.02% | 64.93% | 95% | 0% | 2588 | -126
[5 empty] | 2019-05-29 | 40 | 3571 | 2437 | -115 | 1 | 0 | 2552 | 1876.9992 | 1876.9992 | 1876.9992 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -131.5789 | 1745.4202 | -3550 | -400 | -2204.5798 | 55.11% | 64.93% | 95% | 0% | 2552 | -115
[5 empty] | 2019-05-29 | 41 | 3571.5 | 2378 | -105 | 1 | 0 | 2483 | 1768.92 | 1768.92 | 1768.92 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -120.1373 | 1648.7827 | -3550 | -400 | -2301.2173 | 57.53% | 64.93% | 95% | 0% | 2483 | -105
[5 empty] | 2019-05-29 | 42 | 3572 | 2332 | -100 | 1 | 0 | 2432 | 1689.0354 | 1689.0354 | 1689.0354 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -114.4165 | 1574.619 | -3550 | -400 | -2375.381 | 59.38% | 64.92% | 95% | 0% | 2432 | -100
[5 empty] | 2019-05-29 | 43 | 3572.5 | 2277 | -98 | 1 | 0 | 2375 | 1599.7527 | 1599.7527 | 1599.7527 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -112.1281 | 1487.6245 | -3550 | -400 | -2462.3755 | 61.56% | 64.92% | 95% | 0% | 2375 | -98
[5 empty] | 2019-05-29 | 44 | 3573 | 2180 | -97 | 1 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -110.984 | 1335.265 | -3550 | -400 | -2614.735 | 65.37% | 64.92% | 95% | 0% | 2277 | -97
[5 empty] | 2019-05-29 | 45 | 3573.5 | 2067 | -99 | 1 | 0 | 2166 | 1272.3825 | 1272.3825 | 1272.3825 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -113.2723 | 1159.1102 | -3550 | -400 | -2790.8898 | 69.77% | 64.92% | 95% | 0% | 2166 | -99
[5 empty] | 2019-05-29 | 46 | 3574 | 1933 | -100 | 0 | 0 | 2033 | 1064.0561 | 1064.0561 | 1064.0561 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -114.4165 | 949.6396 | -2750 | -200 | -2000.3604 | 50.01% | 64.91% | 95% | 0% | 2033 | -100
[5 empty] | 2019-05-29 | 47 | 3574.5 | 1777 | -102 | 0 | 0 | 1879 | 822.8359 | 822.8359 | 822.8359 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -116.7048 | 706.1311 | -2750 | -200 | -2243.8689 | 56.1% | 64.91% | 95% | 0% | 1879 | -102
[5 empty] | 2019-05-29 | 48 | 3575 | 1641 | -104 | 0 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -118.9931 | 493.95 | -2750 | -200 | -2456.05 | 61.4% | 64.91% | 95% | 0% | 1745 | -104
[5 empty] | 2019-05-30 | 1 | 3575.5 | 1545 | -105 | 0 | 0 | 1650 | 464.1385 | 464.1385 | 464.1385 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -120.1373 | 344.0012 | -2750 | -200 | -2605.9988 | 65.15% | 64.9% | 95% | 0% | 1650 | -105
[5 empty] | 2019-05-30 | 2 | 3576 | 1475 | -106 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -121.2815 | 234.7779 | -2750 | -200 | -2715.2221 | 67.88% | 64.9% | 95% | 0% | 1581 | -106
[5 empty] | 2019-05-30 | 3 | 3576.5 | 1436 | -110 | 0 | 0 | 1546 | 301.2366 | 301.2366 | 301.2366 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -125.8581 | 175.3785 | -2750 | -200 | -2774.6215 | 69.37% | 64.9% | 95% | 0% | 1546 | -110
[5 empty] | 2019-05-30 | 4 | 3577 | 1411 | -113 | 0 | 0 | 1524 | 266.7766 | 266.7766 | 266.7766 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -129.2906 | 137.486 | -2750 | -200 | -2812.514 | 70.31% | 64.9% | 95% | 0% | 1524 | -113
[5 empty] | 2019-05-30 | 5 | 3577.5 | 1377 | -115 | 0 | 0 | 1492 | 216.6529 | 216.6529 | 216.6529 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -131.5789 | 85.074 | -2750 | -200 | -2864.926 | 71.62% | 64.9% | 95% | 0% | 1492 | -115
[5 empty] | 2019-05-30 | 6 | 3578 | 1342 | -117 | 0 | 0 | 1459 | 164.9629 | 164.9629 | 164.9629 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -133.8673 | 31.0956 | -2750 | -200 | -2918.9044 | 72.97% | 64.89% | 95% | 0% | 1459 | -117
[5 empty] | 2019-05-30 | 7 | 3578.5 | 1316 | -120 | 0 | 0 | 1436 | 128.9365 | 128.9365 | 128.9365 | 1554.3281 | 780 | 200 | 2534.3281 | 63.36% | 95% | 0% | -137.2998 | -8.3633 | -2750 | -200 | -2958.3633 | 73.96% | 64.89% | 95% | 0% | 1436 | -120
[5 empty] | 2019-05-30 | 8 | 3579 | 1298 | -123 | 0 | 0 | 1421 | 105.4411 | 105.4411 | 105.4411 | 1552.7617 | 780 | 200 | 2532.7617 | 63.32% | 95% | 0% | -140.7323 | -35.2912 | -2750 | -200 | -2985.2912 | 74.63% | 64.89% | 95% | 0% | 1421 | -123
[5 empty] | 2019-05-30 | 9 | 3579.5 | 1282 | -125 | 0 | 0 | 1407 | 83.512 | 83.512 | 83.512 | 1552.7617 | 780 | 200 | 2532.7617 | 63.32% | 95% | 0% | -143.0206 | -59.5086 | -2750 | -200 | -3009.5086 | 75.24% | 64.89% | 95% | 0% | 1407 | -125
[5 empty] | 2019-05-30 | 10 | 3580 | 1279 | -126 | 0 | 0 | 1405 | 80.3792 | 80.3792 | 80.3792 | 1552.7617 | 780 | 200 | 2532.7617 | 63.32% | 95% | 0% | -144.1648 | -63.7855 | -2750 | -200 | -3013.7855 | 75.34% | 64.89% | 95% | 0% | 1405 | -126
[5 empty] | 2019-05-30 | 11 | 3580.5 | 1300 | -129 | 0 | 0 | 1429 | 117.972 | 117.972 | 117.972 | 1552.7617 | 780 | 200 | 2532.7617 | 63.32% | 95% | 0% | -147.5973 | -29.6253 | -2750 | -200 | -2979.6253 | 74.49% | 64.88% | 95% | 0% | 1429 | -129
[5 empty] | 2019-05-30 | 12 | 3581 | 1335 | -144 | 0 | 0 | 1479 | 196.2902 | 196.2902 | 196.2902 | 1552.7617 | 780 | 200 | 2532.7617 | 63.32% | 95% | 0% | -164.7597 | 31.5305 | -2750 | -200 | -2918.4695 | 72.96% | 64.87% | 95% | 0% | 1479 | -144
[5 empty] | 2019-05-30 | 13 | 3581.5 | 1480 | -167 | 1 | 0 | 1647 | 459.4394 | 459.4394 | 459.4394 | 1552.7617 | 780 | 200 | 2532.7617 | 63.32% | 95% | 0% | -191.0755 | 268.3639 | -3550 | -400 | -3681.6361 | 92.04% | 64.87% | 95% | 0% | 1647 | -167
[5 empty] | 2019-05-30 | 14 | 3582 | 1604 | -199 | 1 | 0 | 1803 | 703.7923 | 703.7923 | 703.7923 | 1552.7617 | 780 | 200 | 2532.7617 | 63.32% | 95% | 0% | -227.6888 | 476.1035 | -3550 | -400 | -3473.8965 | 86.85% | 64.87% | 95% | 0% | 1803 | -199
[5 empty] | 2019-05-30 | 15 | 3582.5 | 1700 | -245 | 1 | 0 | 1945 | 926.216 | 926.216 | 926.216 | 1552.7617 | 780 | 200 | 2532.7617 | 63.32% | 95% | 0% | -280.3204 | 645.8956 | -3550 | -400 | -3304.1044 | 82.6% | 64.87% | 95% | 0% | 1945 | -245
[5 empty] | 2019-05-30 | 16 | 3583 | 1759 | -289 | 1 | 0 | 2048 | 1087.5515 | 1087.5515 | 1087.5515 | 1552.7617 | 780 | 200 | 2532.7617 | 63.32% | 95% | 0% | -330.6636 | 756.8879 | -3550 | -400 | -3193.1121 | 79.83% | 64.87% | 95% | 0% | 2048 | -289
[5 empty] | 2019-05-30 | 17 | 3583.5 | 1798 | -332 | 1 | 0 | 2130 | 1215.9934 | 1215.9934 | 1215.9934 | 1552.7617 | 780 | 200 | 2532.7617 | 63.32% | 95% | 0% | -379.8627 | 836.1307 | -3550 | -400 | -3113.8693 | 77.85% | 64.86% | 95% | 0% | 2130 | -332
[5 empty] | 2019-05-30 | 18 | 3584 | 1777 | -378 | 1 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 1551.1954 | 780 | 200 | 2531.1954 | 63.28% | 95% | 0% | -432.4943 | 822.6582 | -3550 | -400 | -3127.3418 | 78.18% | 64.86% | 95% | 0% | 2155 | -378
[5 empty] | 2019-05-30 | 19 | 3584.5 | 1753 | -418 | 1 | 0 | 2171 | 1280.2143 | 1280.2143 | 1280.2143 | 1551.1954 | 780 | 200 | 2531.1954 | 63.28% | 95% | 0% | -478.2609 | 801.9535 | -3550 | -400 | -3148.0465 | 78.7% | 64.86% | 95% | 0% | 2171 | -418
[5 empty] | 2019-05-30 | 20 | 3585 | 1698 | -452 | 1 | 0 | 2150 | 1247.3207 | 1247.3207 | 1247.3207 | 1551.1954 | 780 | 200 | 2531.1954 | 63.28% | 95% | 0% | -517.1625 | 730.1582 | -3550 | -400 | -3219.8418 | 80.5% | 64.86% | 95% | 0% | 2150 | -452
[5 empty] | 2019-05-30 | 21 | 3585.5 | 1608 | -510 | 1 | 0 | 2118 | 1197.197 | 1197.197 | 1197.197 | 1551.1954 | 780 | 200 | 2531.1954 | 63.28% | 95% | 0% | -583.524 | 613.673 | -3550 | -400 | -3336.327 | 83.41% | 64.86% | 95% | 0% | 2118 | -510
[5 empty] | 2019-05-30 | 22 | 3586 | 1558 | -553 | 1 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 1551.1954 | 780 | 200 | 2531.1954 | 63.28% | 95% | 0% | -632.7231 | 553.5094 | -3550 | -400 | -3396.4906 | 84.91% | 64.86% | 95% | 0% | 2111 | -553
[5 empty] | 2019-05-30 | 23 | 3586.5 | 1531 | -576 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1551.1954 | 780 | 200 | 2531.1954 | 63.28% | 95% | 0% | -659.0389 | 520.9281 | -3550 | -400 | -3429.0719 | 85.73% | 64.86% | 95% | 0% | 2107 | -576
[5 empty] | 2019-05-30 | 24 | 3587 | 1510 | -598 | 1 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 1551.1954 | 780 | 200 | 2531.1954 | 63.28% | 95% | 0% | -684.2105 | 497.3229 | -3550 | -400 | -3452.6771 | 86.32% | 64.86% | 95% | 0% | 2108 | -598
[5 empty] | 2019-05-30 | 25 | 3587.5 | 1519 | -603 | 1 | 0 | 2122 | 1203.4625 | 1203.4625 | 1203.4625 | 1551.1954 | 780 | 200 | 2531.1954 | 63.28% | 95% | 0% | -689.9314 | 513.5311 | -3550 | -400 | -3436.4689 | 85.91% | 64.85% | 95% | 0% | 2122 | -603
[5 empty] | 2019-05-30 | 26 | 3588 | 1552 | -559 | 1 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 1551.1954 | 780 | 200 | 2531.1954 | 63.28% | 95% | 0% | -639.5881 | 546.6444 | -3550 | -400 | -3403.3556 | 85.08% | 64.85% | 95% | 0% | 2111 | -559
[5 empty] | 2019-05-30 | 27 | 3588.5 | 1549 | -573 | 1 | 0 | 2122 | 1203.4625 | 1203.4625 | 1203.4625 | 1551.1954 | 780 | 200 | 2531.1954 | 63.28% | 95% | 0% | -655.6064 | 547.8561 | -3550 | -400 | -3402.1439 | 85.05% | 64.85% | 95% | 0% | 2122 | -573
[5 empty] | 2019-05-30 | 28 | 3589 | 1563 | -556 | 1 | 0 | 2119 | 1198.7634 | 1198.7634 | 1198.7634 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -636.1556 | 562.6078 | -3550 | -400 | -3387.3922 | 84.68% | 64.84% | 95% | 0% | 2119 | -556
[5 empty] | 2019-05-30 | 29 | 3589.5 | 1584 | -524 | 1 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -599.5423 | 581.9911 | -3550 | -400 | -3368.0089 | 84.2% | 64.83% | 95% | 0% | 2108 | -524
[5 empty] | 2019-05-30 | 30 | 3590 | 1624 | -493 | 1 | 0 | 2117 | 1195.6307 | 1195.6307 | 1195.6307 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -564.0732 | 631.5574 | -3550 | -400 | -3318.4426 | 82.96% | 64.83% | 95% | 0% | 2117 | -493
[5 empty] | 2019-05-30 | 31 | 3590.5 | 1663 | -472 | 1 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -540.0458 | 683.7795 | -3550 | -400 | -3266.2205 | 81.66% | 64.83% | 95% | 0% | 2135 | -472
[5 empty] | 2019-05-30 | 32 | 3591 | 1693 | -471 | 1 | 0 | 2164 | 1269.2498 | 1269.2498 | 1269.2498 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -538.9016 | 730.3482 | -3550 | -400 | -3219.6518 | 80.49% | 64.83% | 95% | 0% | 2164 | -471
[5 empty] | 2019-05-30 | 33 | 3591.5 | 1761 | -449 | 1 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -513.73 | 827.5726 | -3550 | -400 | -3122.4274 | 78.06% | 64.82% | 95% | 0% | 2210 | -449
[5 empty] | 2019-05-30 | 34 | 3592 | 1892 | -381 | 1 | 0 | 2273 | 1439.9835 | 1439.9835 | 1439.9835 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -435.9268 | 1004.0567 | -3550 | -400 | -2945.9433 | 73.65% | 64.82% | 95% | 0% | 2273 | -381
[5 empty] | 2019-05-30 | 35 | 3592.5 | 1985 | -321 | 1 | 0 | 2306 | 1491.6735 | 1491.6735 | 1491.6735 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -367.2769 | 1124.3966 | -3550 | -400 | -2825.6034 | 70.64% | 64.82% | 95% | 0% | 2306 | -321
[5 empty] | 2019-05-30 | 36 | 3593 | 2073 | -277 | 1 | 0 | 2350 | 1560.5936 | 1560.5936 | 1560.5936 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -316.9336 | 1243.6599 | -3550 | -400 | -2706.3401 | 67.66% | 64.82% | 95% | 0% | 2350 | -277
[5 empty] | 2019-05-30 | 37 | 3593.5 | 2129 | -247 | 1 | 0 | 2376 | 1601.319 | 1601.319 | 1601.319 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -282.6087 | 1318.7103 | -3550 | -400 | -2631.2897 | 65.78% | 64.81% | 95% | 0% | 2376 | -247
[5 empty] | 2019-05-30 | 38 | 3594 | 2182 | -210 | 1 | 0 | 2392 | 1626.3809 | 1626.3809 | 1626.3809 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -240.2746 | 1386.1063 | -3550 | -400 | -2563.8937 | 64.1% | 64.81% | 95% | 0% | 2392 | -210
[5 empty] | 2019-05-30 | 39 | 3594.5 | 2209 | -177 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -202.5172 | 1414.4655 | -3550 | -400 | -2535.5345 | 63.39% | 64.81% | 95% | 0% | 2386 | -177
[5 empty] | 2019-05-30 | 40 | 3595 | 2239 | -149 | 1 | 0 | 2388 | 1620.1154 | 1620.1154 | 1620.1154 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -170.4805 | 1449.6349 | -3550 | -400 | -2500.3651 | 62.51% | 64.81% | 95% | 0% | 2388 | -149
[5 empty] | 2019-05-30 | 41 | 3595.5 | 2233 | -124 | 1 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -141.8764 | 1429.6817 | -3550 | -400 | -2520.3183 | 63.01% | 64.81% | 95% | 0% | 2357 | -124
[5 empty] | 2019-05-30 | 42 | 3596 | 2209 | -110 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -125.8581 | 1386.1782 | -3550 | -400 | -2563.8218 | 64.1% | 64.8% | 95% | 0% | 2319 | -110
[5 empty] | 2019-05-30 | 43 | 3596.5 | 2211 | -105 | 1 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 1549.629 | 780 | 200 | 2529.629 | 63.24% | 95% | 0% | -120.1373 | 1387.1999 | -3550 | -400 | -2562.8001 | 64.07% | 64.8% | 95% | 0% | 2316 | -105
[5 empty] | 2019-05-30 | 44 | 3597 | 2186 | -103 | 1 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -117.849 | 1347.1964 | -3550 | -400 | -2602.8036 | 65.07% | 64.79% | 95% | 0% | 2289 | -103
[5 empty] | 2019-05-30 | 45 | 3597.5 | 2100 | -101 | 0 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -115.5606 | 1211.6446 | -2750 | -200 | -1738.3554 | 43.46% | 64.79% | 95% | 0% | 2201 | -101
[5 empty] | 2019-05-30 | 46 | 3598 | 1969 | -99 | 0 | 0 | 2068 | 1118.8788 | 1118.8788 | 1118.8788 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -113.2723 | 1005.6065 | -2750 | -200 | -1944.3935 | 48.61% | 64.79% | 95% | 0% | 2068 | -99
[5 empty] | 2019-05-30 | 47 | 3598.5 | 1816 | -96 | 0 | 0 | 1912 | 874.526 | 874.526 | 874.526 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -109.8398 | 764.6862 | -2750 | -200 | -2185.3138 | 54.63% | 64.79% | 95% | 0% | 1912 | -96
[5 empty] | 2019-05-30 | 48 | 3599 | 1699 | -94 | 0 | 0 | 1793 | 688.1286 | 688.1286 | 688.1286 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -107.5515 | 580.5771 | -2750 | -200 | -2369.4229 | 59.24% | 64.78% | 95% | 0% | 1793 | -94
[5 empty] | 2019-05-31 | 1 | 3599.5 | 1629 | -89 | 0 | 0 | 1718 | 570.6513 | 570.6513 | 570.6513 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -101.8307 | 468.8206 | -2750 | -200 | -2481.1794 | 62.03% | 64.78% | 95% | 0% | 1718 | -89
[5 empty] | 2019-05-31 | 2 | 3600 | 1562 | -85 | 0 | 0 | 1647 | 459.4394 | 459.4394 | 459.4394 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -97.254 | 362.1854 | -2750 | -200 | -2587.8146 | 64.7% | 64.77% | 95% | 0% | 1647 | -85
[5 empty] | 2019-05-31 | 3 | 3600.5 | 1525 | -84 | 0 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -96.1098 | 303.8077 | -2750 | -200 | -2646.1923 | 66.15% | 64.77% | 95% | 0% | 1609 | -84
[5 empty] | 2019-05-31 | 4 | 3601 | 1523 | -83 | 0 | 0 | 1606 | 395.2185 | 395.2185 | 395.2185 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -94.9657 | 300.2528 | -2750 | -200 | -2649.7472 | 66.24% | 64.77% | 95% | 0% | 1606 | -83
[5 empty] | 2019-05-31 | 5 | 3601.5 | 1499 | -82 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -93.8215 | 262.2378 | -2750 | -200 | -2687.7622 | 67.19% | 64.77% | 95% | 0% | 1581 | -82
[5 empty] | 2019-05-31 | 6 | 3602 | 1474 | -81 | 1 | 0 | 1555 | 315.3339 | 315.3339 | 315.3339 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -92.6773 | 222.6565 | -3550 | -400 | -3727.3435 | 93.18% | 64.76% | 95% | 0% | 1555 | -81
[5 empty] | 2019-05-31 | 7 | 3602.5 | 1453 | -80 | 1 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -91.5332 | 189.3407 | -3550 | -400 | -3760.6593 | 94.02% | 64.76% | 95% | 0% | 1533 | -80
[5 empty] | 2019-05-31 | 8 | 3603 | 1438 | -79 | 1 | 0 | 1517 | 255.812 | 255.812 | 255.812 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -90.389 | 165.423 | -3550 | -400 | -3784.577 | 94.61% | 64.76% | 95% | 0% | 1517 | -79
[5 empty] | 2019-05-31 | 9 | 3603.5 | 1449 | -80 | 1 | 0 | 1529 | 274.6084 | 274.6084 | 274.6084 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -91.5332 | 183.0752 | -3550 | -400 | -3766.9248 | 94.17% | 64.76% | 95% | 0% | 1529 | -80
[5 empty] | 2019-05-31 | 10 | 3604 | 1433 | -81 | 1 | 0 | 1514 | 251.1129 | 251.1129 | 251.1129 | 1548.0627 | 780 | 200 | 2528.0627 | 63.2% | 95% | 0% | -92.6773 | 158.4356 | -3550 | -400 | -3791.5644 | 94.79% | 64.76% | 95% | 0% | 1514 | -81
[5 empty] | 2019-05-31 | 11 | 3604.5 | 1452 | -85 | 1 | 0 | 1537 | 287.1393 | 287.1393 | 287.1393 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -97.254 | 189.8853 | -3550 | -400 | -3760.1147 | 94% | 64.76% | 95% | 0% | 1537 | -85
[5 empty] | 2019-05-31 | 12 | 3605 | 1490 | -101 | 1 | 0 | 1591 | 371.723 | 371.723 | 371.723 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -115.5606 | 256.1624 | -3550 | -400 | -3693.8376 | 92.35% | 64.76% | 95% | 0% | 1591 | -101
[5 empty] | 2019-05-31 | 13 | 3605.5 | 1628 | -125 | 1 | 0 | 1753 | 625.474 | 625.474 | 625.474 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -143.0206 | 482.4534 | -3550 | -400 | -3467.5466 | 86.69% | 64.75% | 95% | 0% | 1753 | -125
[5 empty] | 2019-05-31 | 14 | 3606 | 1728 | -157 | 1 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -179.6339 | 652.6003 | -3550 | -400 | -3297.3997 | 82.43% | 64.75% | 95% | 0% | 1885 | -157
[5 empty] | 2019-05-31 | 15 | 3606.5 | 1878 | -197 | 1 | 0 | 2075 | 1129.8434 | 1129.8434 | 1129.8434 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -225.4005 | 904.4429 | -3550 | -400 | -3045.5571 | 76.14% | 64.75% | 95% | 0% | 2075 | -197
[5 empty] | 2019-05-31 | 16 | 3607 | 1935 | -235 | 1 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -268.8787 | 1009.7693 | -3550 | -400 | -2940.2307 | 73.51% | 64.75% | 95% | 0% | 2170 | -235
[5 empty] | 2019-05-31 | 17 | 3607.5 | 1978 | -272 | 1 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -311.2128 | 1092.7443 | -3550 | -400 | -2857.2557 | 71.43% | 64.74% | 95% | 0% | 2250 | -272
[5 empty] | 2019-05-31 | 18 | 3608 | 1980 | -317 | 1 | 0 | 2297 | 1477.5763 | 1477.5763 | 1477.5763 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -362.7002 | 1114.876 | -3550 | -400 | -2835.124 | 70.88% | 64.74% | 95% | 0% | 2297 | -317
[5 empty] | 2019-05-31 | 19 | 3608.5 | 1950 | -348 | 1 | 0 | 2298 | 1479.1426 | 1479.1426 | 1479.1426 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -398.1693 | 1080.9733 | -3550 | -400 | -2869.0267 | 71.73% | 64.74% | 95% | 0% | 2298 | -348
[5 empty] | 2019-05-31 | 20 | 3609 | 1905 | -382 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -437.0709 | 1024.8417 | -3550 | -400 | -2925.1583 | 73.13% | 64.74% | 95% | 0% | 2287 | -382
[5 empty] | 2019-05-31 | 21 | 3609.5 | 1886 | -397 | 1 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -454.2334 | 1001.4137 | -3550 | -400 | -2948.5863 | 73.71% | 64.73% | 95% | 0% | 2283 | -397
[5 empty] | 2019-05-31 | 22 | 3610 | 1913 | -387 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -442.7918 | 1039.4836 | -3550 | -400 | -2910.5164 | 72.76% | 64.72% | 95% | 0% | 2300 | -387
[5 empty] | 2019-05-31 | 23 | 3610.5 | 1918 | -380 | 1 | 0 | 2298 | 1479.1426 | 1479.1426 | 1479.1426 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -434.7826 | 1044.36 | -3550 | -400 | -2905.64 | 72.64% | 64.71% | 95% | 0% | 2298 | -380
[5 empty] | 2019-05-31 | 24 | 3611 | 1911 | -366 | 1 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -418.7643 | 1027.4847 | -3550 | -400 | -2922.5153 | 73.06% | 64.71% | 95% | 0% | 2277 | -366
[5 empty] | 2019-05-31 | 25 | 3611.5 | 1853 | -398 | 1 | 0 | 2251 | 1405.5235 | 1405.5235 | 1405.5235 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -455.3776 | 950.1459 | -3550 | -400 | -2999.8541 | 75% | 64.71% | 95% | 0% | 2251 | -398
[5 empty] | 2019-05-31 | 26 | 3612 | 1775 | -430 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 1546.4963 | 780 | 200 | 2526.4963 | 63.16% | 95% | 0% | -491.9908 | 841.4799 | -3550 | -400 | -3108.5201 | 77.71% | 64.71% | 95% | 0% | 2205 | -430
[5 empty] | 2019-05-31 | 27 | 3612.5 | 1722 | -432 | 1 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 1544.9299 | 780 | 200 | 2524.9299 | 63.12% | 95% | 0% | -494.2792 | 759.307 | -3550 | -400 | -3190.693 | 79.77% | 64.71% | 95% | 0% | 2154 | -432
[5 empty] | 2019-05-31 | 28 | 3613 | 1642 | -460 | 1 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 1544.9299 | 780 | 200 | 2524.9299 | 63.12% | 95% | 0% | -526.3158 | 645.8194 | -3550 | -400 | -3304.1806 | 82.6% | 64.71% | 95% | 0% | 2102 | -460
[5 empty] | 2019-05-31 | 29 | 3613.5 | 1585 | -464 | 1 | 0 | 2049 | 1089.1179 | 1089.1179 | 1089.1179 | 1544.9299 | 780 | 200 | 2524.9299 | 63.12% | 95% | 0% | -530.8924 | 558.2254 | -3550 | -400 | -3391.7746 | 84.79% | 64.71% | 95% | 0% | 2049 | -464
[5 empty] | 2019-05-31 | 30 | 3614 | 1526 | -472 | 1 | 0 | 1998 | 1009.2333 | 1009.2333 | 1009.2333 | 1544.9299 | 780 | 200 | 2524.9299 | 63.12% | 95% | 0% | -540.0458 | 469.1875 | -3550 | -400 | -3480.8125 | 87.02% | 64.7% | 95% | 0% | 1998 | -472
[5 empty] | 2019-05-31 | 31 | 3614.5 | 1494 | -505 | 1 | 0 | 1999 | 1010.7997 | 1010.7997 | 1010.7997 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -577.8032 | 432.9965 | -3550 | -400 | -3517.0035 | 87.93% | 64.7% | 95% | 0% | 1999 | -505
[5 empty] | 2019-05-31 | 32 | 3615 | 1476 | -507 | 1 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -580.0915 | 405.6463 | -3550 | -400 | -3544.3537 | 88.61% | 64.7% | 95% | 0% | 1983 | -507
[5 empty] | 2019-05-31 | 33 | 3615.5 | 1517 | -482 | 1 | 0 | 1999 | 1010.7997 | 1010.7997 | 1010.7997 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -551.4874 | 459.3123 | -3550 | -400 | -3490.6877 | 87.27% | 64.7% | 95% | 0% | 1999 | -482
[5 empty] | 2019-05-31 | 34 | 3616 | 1556 | -470 | 1 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -537.7574 | 515.3341 | -3550 | -400 | -3434.6659 | 85.87% | 64.7% | 95% | 0% | 2026 | -470
[5 empty] | 2019-05-31 | 35 | 3616.5 | 1641 | -432 | 1 | 0 | 2073 | 1126.7106 | 1126.7106 | 1126.7106 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -494.2792 | 632.4315 | -3550 | -400 | -3317.5685 | 82.94% | 64.7% | 95% | 0% | 2073 | -432
[5 empty] | 2019-05-31 | 36 | 3617 | 1698 | -391 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -447.3684 | 704.404 | -3550 | -400 | -3245.596 | 81.14% | 64.7% | 95% | 0% | 2089 | -391
[5 empty] | 2019-05-31 | 37 | 3617.5 | 1781 | -340 | 1 | 0 | 2121 | 1201.8961 | 1201.8961 | 1201.8961 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -389.016 | 812.8801 | -3550 | -400 | -3137.1199 | 78.43% | 64.7% | 95% | 0% | 2121 | -340
[5 empty] | 2019-05-31 | 38 | 3618 | 1851 | -290 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -331.8078 | 901.4156 | -3550 | -400 | -3048.5844 | 76.21% | 64.7% | 95% | 0% | 2141 | -290
[5 empty] | 2019-05-31 | 39 | 3618.5 | 1911 | -238 | 1 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -272.3112 | 973.4431 | -3550 | -400 | -2976.5569 | 74.41% | 64.69% | 95% | 0% | 2149 | -238
[5 empty] | 2019-05-31 | 40 | 3619 | 1965 | -196 | 1 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -224.2563 | 1040.2944 | -3550 | -400 | -2909.7056 | 72.74% | 64.69% | 95% | 0% | 2161 | -196
[5 empty] | 2019-05-31 | 41 | 3619.5 | 1970 | -162 | 1 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -185.3547 | 1033.7714 | -3550 | -400 | -2916.2286 | 72.91% | 64.68% | 95% | 0% | 2132 | -162
[5 empty] | 2019-05-31 | 42 | 3620 | 1958 | -137 | 1 | 0 | 2095 | 1161.1707 | 1161.1707 | 1161.1707 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -156.7506 | 1004.4201 | -3550 | -400 | -2945.5799 | 73.64% | 64.68% | 95% | 0% | 2095 | -137
[5 empty] | 2019-05-31 | 43 | 3620.5 | 1957 | -129 | 1 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -147.5973 | 999.4761 | -3550 | -400 | -2950.5239 | 73.76% | 64.68% | 95% | 0% | 2086 | -129
[5 empty] | 2019-05-31 | 44 | 3621 | 1965 | -127 | 1 | 0 | 2092 | 1156.4716 | 1156.4716 | 1156.4716 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -145.3089 | 1011.1626 | -3550 | -400 | -2938.8374 | 73.47% | 64.68% | 95% | 0% | 2092 | -127
[5 empty] | 2019-05-31 | 45 | 3621.5 | 1915 | -126 | 1 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 1543.3636 | 780 | 200 | 2523.3636 | 63.08% | 95% | 0% | -144.1648 | 932.4222 | -3550 | -400 | -3017.5778 | 75.44% | 64.67% | 95% | 0% | 2041 | -126
[5 empty] | 2019-05-31 | 46 | 3622 | 1800 | -125 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -143.0206 | 751.8681 | -2750 | -200 | -2198.1319 | 54.95% | 64.67% | 95% | 0% | 1925 | -125
[5 empty] | 2019-05-31 | 47 | 3622.5 | 1696 | -124 | 0 | 0 | 1820 | 730.4204 | 730.4204 | 730.4204 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -141.8764 | 588.544 | -2750 | -200 | -2361.456 | 59.04% | 64.66% | 95% | 0% | 1820 | -124
[5 empty] | 2019-05-31 | 48 | 3623 | 1595 | -123 | 0 | 0 | 1718 | 570.6513 | 570.6513 | 570.6513 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -140.7323 | 429.919 | -2750 | -200 | -2520.081 | 63% | 64.66% | 95% | 0% | 1718 | -123
[5 empty] | 2019-06-01 | 1 | 3623.5 | 1512 | -120 | 0 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -137.2998 | 298.6442 | -2750 | -200 | -2651.3558 | 66.28% | 64.65% | 95% | 0% | 1632 | -120
[5 empty] | 2019-06-01 | 2 | 3624 | 1463 | -116 | 0 | 0 | 1579 | 352.9266 | 352.9266 | 352.9266 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -132.7231 | 220.2035 | -2750 | -200 | -2729.7965 | 68.24% | 64.65% | 95% | 0% | 1579 | -116
[5 empty] | 2019-06-01 | 3 | 3624.5 | 1449 | -111 | 0 | 0 | 1560 | 323.1657 | 323.1657 | 323.1657 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -127.0023 | 196.1634 | -2750 | -200 | -2753.8366 | 68.85% | 64.65% | 95% | 0% | 1560 | -111
[5 empty] | 2019-06-01 | 4 | 3625 | 1450 | -107 | 0 | 0 | 1557 | 318.4666 | 318.4666 | 318.4666 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -122.4256 | 196.041 | -2750 | -200 | -2753.959 | 68.85% | 64.64% | 95% | 0% | 1557 | -107
[5 empty] | 2019-06-01 | 5 | 3625.5 | 1438 | -102 | 0 | 0 | 1540 | 291.8384 | 291.8384 | 291.8384 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -116.7048 | 175.1336 | -2750 | -200 | -2774.8664 | 69.37% | 64.64% | 95% | 0% | 1540 | -102
[5 empty] | 2019-06-01 | 6 | 3626 | 1418 | -97 | 0 | 0 | 1515 | 252.6793 | 252.6793 | 252.6793 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -110.984 | 141.6953 | -2750 | -200 | -2808.3047 | 70.21% | 64.64% | 95% | 0% | 1515 | -97
[5 empty] | 2019-06-01 | 7 | 3626.5 | 1406 | -93 | 0 | 0 | 1499 | 227.6175 | 227.6175 | 227.6175 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -106.4073 | 121.2102 | -2750 | -200 | -2828.7898 | 70.72% | 64.63% | 95% | 0% | 1499 | -93
[5 empty] | 2019-06-01 | 8 | 3627 | 1410 | -89 | 0 | 0 | 1499 | 227.6175 | 227.6175 | 227.6175 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -101.8307 | 125.7868 | -2750 | -200 | -2824.2132 | 70.61% | 64.63% | 95% | 0% | 1499 | -89
[5 empty] | 2019-06-01 | 9 | 3627.5 | 1406 | -85 | 1 | 0 | 1491 | 215.0866 | 215.0866 | 215.0866 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -97.254 | 117.8326 | -3550 | -400 | -3832.1674 | 95.8% | 64.62% | 95% | 0% | 1491 | -85
[5 empty] | 2019-06-01 | 10 | 3628 | 1375 | -82 | 1 | 0 | 1457 | 161.8302 | 161.8302 | 161.8302 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -93.8215 | 68.0087 | -3550 | -400 | -3881.9913 | 97.05% | 64.62% | 95% | 0% | 1457 | -82
[5 empty] | 2019-06-01 | 11 | 3628.5 | 1382 | -83 | 1 | 0 | 1465 | 174.3611 | 174.3611 | 174.3611 | 1541.7972 | 780 | 200 | 2521.7972 | 63.04% | 95% | 0% | -94.9657 | 79.3954 | -3550 | -400 | -3870.6046 | 96.77% | 64.61% | 95% | 0% | 1465 | -83
[5 empty] | 2019-06-01 | 12 | 3629 | 1381 | -96 | 1 | 0 | 1477 | 193.1575 | 193.1575 | 193.1575 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -109.8398 | 83.3176 | -3550 | -400 | -3866.6824 | 96.67% | 64.61% | 95% | 0% | 1477 | -96
[5 empty] | 2019-06-01 | 13 | 3629.5 | 1430 | -119 | 1 | 0 | 1549 | 305.9357 | 305.9357 | 305.9357 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -136.1556 | 169.7801 | -3550 | -400 | -3780.2199 | 94.51% | 64.6% | 95% | 0% | 1549 | -119
[5 empty] | 2019-06-01 | 14 | 3630 | 1457 | -156 | 1 | 0 | 1613 | 406.183 | 406.183 | 406.183 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -178.4897 | 227.6933 | -3550 | -400 | -3722.3067 | 93.06% | 64.6% | 95% | 0% | 1613 | -156
[5 empty] | 2019-06-01 | 15 | 3630.5 | 1491 | -208 | 1 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -237.9863 | 302.9041 | -3550 | -400 | -3647.0959 | 91.18% | 64.6% | 95% | 0% | 1699 | -208
[5 empty] | 2019-06-01 | 16 | 3631 | 1492 | -261 | 1 | 0 | 1753 | 625.474 | 625.474 | 625.474 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -298.627 | 326.847 | -3550 | -400 | -3623.153 | 90.58% | 64.6% | 95% | 0% | 1753 | -261
[5 empty] | 2019-06-01 | 17 | 3631.5 | 1500 | -314 | 1 | 0 | 1814 | 721.0223 | 721.0223 | 721.0223 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -359.2677 | 361.7545 | -3550 | -400 | -3588.2455 | 89.71% | 64.6% | 95% | 0% | 1814 | -314
[5 empty] | 2019-06-01 | 18 | 3632 | 1458 | -377 | 1 | 0 | 1835 | 753.9159 | 753.9159 | 753.9159 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -431.3501 | 322.5658 | -3550 | -400 | -3627.4342 | 90.69% | 64.6% | 95% | 0% | 1835 | -377
[5 empty] | 2019-06-01 | 19 | 3632.5 | 1441 | -426 | 1 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -487.4142 | 316.6254 | -3550 | -400 | -3633.3746 | 90.83% | 64.6% | 95% | 0% | 1867 | -426
[5 empty] | 2019-06-01 | 20 | 3633 | 1392 | -470 | 1 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -537.7574 | 258.4503 | -3550 | -400 | -3691.5497 | 92.29% | 64.59% | 95% | 0% | 1862 | -470
[5 empty] | 2019-06-01 | 21 | 3633.5 | 1340 | -514 | 1 | 0 | 1854 | 783.6768 | 783.6768 | 783.6768 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -588.1007 | 195.5761 | -3550 | -400 | -3754.4239 | 93.86% | 64.58% | 95% | 0% | 1854 | -514
[5 empty] | 2019-06-01 | 22 | 3634 | 1273 | -565 | 1 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -646.4531 | 112.1619 | -3550 | -400 | -3837.8381 | 95.95% | 64.58% | 95% | 0% | 1838 | -565
[5 empty] | 2019-06-01 | 23 | 3634.5 | 1203 | -611 | 1 | 0 | 1814 | 721.0223 | 721.0223 | 721.0223 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -699.0847 | 21.9376 | -3550 | -400 | -3928.0624 | 98.2% | 64.57% | 95% | 0% | 1814 | -611
[5 empty] | 2019-06-01 | 24 | 3635 | 1164 | -640 | 1 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -732.2654 | -26.9068 | -3550 | -400 | -3976.9068 | 99.42% | 64.57% | 95% | 0% | 1804 | -640
[5 empty] | 2019-06-01 | 25 | 3635.5 | 1165 | -624 | 1 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 1540.2308 | 780 | 200 | 2520.2308 | 63.01% | 95% | 0% | -713.9588 | -32.0957 | -3550 | -400 | -3982.0957 | 99.55% | 64.56% | 95% | 0% | 1789 | -624
[5 empty] | 2019-06-01 | 26 | 3636 | 1134 | -635 | 1 | 0 | 1769 | 650.5359 | 650.5359 | 650.5359 | 1538.6645 | 780 | 200 | 2518.6645 | 62.97% | 95% | 0% | -726.5446 | -76.0088 | -3550 | -400 | -4026.0088 | 100.7% | 64.56% | 95% | 0% | 1769 | -635
[5 empty] | 2019-06-01 | 27 | 3636.5 | 1117 | -622 | 1 | 0 | 1739 | 603.5449 | 603.5449 | 603.5449 | 1538.6645 | 780 | 200 | 2518.6645 | 62.97% | 95% | 0% | -711.6705 | -108.1256 | -3550 | -400 | -4058.1256 | 101.5% | 64.56% | 95% | 0% | 1739 | -622
[5 empty] | 2019-06-01 | 28 | 3637 | 1128 | -595 | 1 | 0 | 1723 | 578.4831 | 578.4831 | 578.4831 | 1538.6645 | 780 | 200 | 2518.6645 | 62.97% | 95% | 0% | -680.778 | -102.2949 | -3550 | -400 | -4052.2949 | 101.3% | 64.56% | 95% | 0% | 1723 | -595
[5 empty] | 2019-06-01 | 29 | 3637.5 | 1142 | -575 | 1 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 1538.6645 | 780 | 200 | 2518.6645 | 62.97% | 95% | 0% | -657.8947 | -88.8098 | -3550 | -400 | -4038.8098 | 101% | 64.56% | 95% | 0% | 1717 | -575
[5 empty] | 2019-06-01 | 30 | 3638 | 1168 | -545 | 1 | 0 | 1713 | 562.8195 | 562.8195 | 562.8195 | 1538.6645 | 780 | 200 | 2518.6645 | 62.97% | 95% | 0% | -623.5698 | -60.7503 | -3550 | -400 | -4010.7503 | 100.3% | 64.55% | 95% | 0% | 1713 | -545
[5 empty] | 2019-06-01 | 31 | 3638.5 | 1210 | -527 | 1 | 0 | 1737 | 600.4122 | 600.4122 | 600.4122 | 1538.6645 | 780 | 200 | 2518.6645 | 62.97% | 95% | 0% | -602.9748 | -2.5626 | -3550 | -400 | -3952.5626 | 98.81% | 64.55% | 95% | 0% | 1737 | -527
[5 empty] | 2019-06-01 | 32 | 3639 | 1268 | -500 | 1 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 1538.6645 | 780 | 200 | 2518.6645 | 62.97% | 95% | 0% | -572.0824 | 76.8871 | -3550 | -400 | -3873.1129 | 96.83% | 64.55% | 95% | 0% | 1768 | -500
[5 empty] | 2019-06-01 | 33 | 3639.5 | 1394 | -439 | 1 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 1538.6645 | 780 | 200 | 2518.6645 | 62.97% | 95% | 0% | -502.2883 | 248.4949 | -3550 | -400 | -3701.5051 | 92.54% | 64.54% | 95% | 0% | 1833 | -439
[5 empty] | 2019-06-01 | 34 | 3640 | 1521 | -382 | 1 | 0 | 1903 | 860.4287 | 860.4287 | 860.4287 | 1538.6645 | 780 | 200 | 2518.6645 | 62.97% | 95% | 0% | -437.0709 | 423.3578 | -3550 | -400 | -3526.6422 | 88.17% | 64.53% | 95% | 0% | 1903 | -382
[5 empty] | 2019-06-01 | 35 | 3640.5 | 1672 | -313 | 1 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 1538.6645 | 780 | 200 | 2518.6645 | 62.97% | 95% | 0% | -358.1236 | 630.747 | -3550 | -400 | -3319.253 | 82.98% | 64.53% | 95% | 0% | 1985 | -313
[5 empty] | 2019-06-01 | 36 | 3641 | 1769 | -259 | 1 | 0 | 2028 | 1056.2242 | 1056.2242 | 1056.2242 | 1538.6645 | 780 | 200 | 2518.6645 | 62.97% | 95% | 0% | -296.3387 | 759.8856 | -3550 | -400 | -3190.1144 | 79.75% | 64.53% | 95% | 0% | 2028 | -259
[5 empty] | 2019-06-01 | 37 | 3641.5 | 1851 | -222 | 1 | 0 | 2073 | 1126.7106 | 1126.7106 | 1126.7106 | 1538.6645 | 780 | 200 | 2518.6645 | 62.97% | 95% | 0% | -254.0046 | 872.7061 | -3550 | -400 | -3077.2939 | 76.93% | 64.53% | 95% | 0% | 2073 | -222
[5 empty] | 2019-06-01 | 38 | 3642 | 1914 | -182 | 1 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -208.238 | 954.499 | -3550 | -400 | -2995.501 | 74.89% | 64.53% | 95% | 0% | 2096 | -182
[5 empty] | 2019-06-01 | 39 | 3642.5 | 1950 | -142 | 1 | 0 | 2092 | 1156.4716 | 1156.4716 | 1156.4716 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -162.4714 | 994.0002 | -3550 | -400 | -2955.9998 | 73.9% | 64.52% | 95% | 0% | 2092 | -142
[5 empty] | 2019-06-01 | 40 | 3643 | 1977 | -112 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -128.1465 | 1023.626 | -3550 | -400 | -2926.374 | 73.16% | 64.5% | 95% | 0% | 2089 | -112
[5 empty] | 2019-06-01 | 41 | 3643.5 | 1980 | -86 | 1 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -98.3982 | 1017.3479 | -3550 | -400 | -2932.6521 | 73.32% | 64.5% | 95% | 0% | 2066 | -86
[5 empty] | 2019-06-01 | 42 | 3644 | 1992 | -68 | 1 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -77.8032 | 1028.5447 | -3550 | -400 | -2921.4553 | 73.04% | 64.5% | 95% | 0% | 2060 | -68
[5 empty] | 2019-06-01 | 43 | 3644.5 | 2000 | -66 | 1 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -75.5149 | 1040.2312 | -3550 | -400 | -2909.7688 | 72.74% | 64.49% | 95% | 0% | 2066 | -66
[5 empty] | 2019-06-01 | 44 | 3645 | 1966 | -69 | 1 | 0 | 2035 | 1067.1888 | 1067.1888 | 1067.1888 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -78.9474 | 988.2414 | -3550 | -400 | -2961.7586 | 74.04% | 64.47% | 95% | 0% | 2035 | -69
[5 empty] | 2019-06-01 | 45 | 3645.5 | 1939 | -71 | 1 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -81.2357 | 946.794 | -3550 | -400 | -3003.206 | 75.08% | 64.47% | 95% | 0% | 2010 | -71
[5 empty] | 2019-06-01 | 46 | 3646 | 1879 | -74 | 0 | 0 | 1953 | 938.7469 | 938.7469 | 938.7469 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -84.6682 | 854.0787 | -2750 | -200 | -2095.9213 | 52.4% | 64.47% | 95% | 0% | 1953 | -74
[5 empty] | 2019-06-01 | 47 | 3646.5 | 1758 | -77 | 0 | 0 | 1835 | 753.9159 | 753.9159 | 753.9159 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -88.1007 | 665.8152 | -2750 | -200 | -2284.1848 | 57.1% | 64.47% | 95% | 0% | 1835 | -77
[5 empty] | 2019-06-01 | 48 | 3647 | 1653 | -80 | 0 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -91.5332 | 502.6136 | -2750 | -200 | -2447.3864 | 61.18% | 64.46% | 95% | 0% | 1733 | -80
[5 empty] | 2019-06-02 | 1 | 3647.5 | 1569 | -86 | 0 | 0 | 1655 | 471.9703 | 471.9703 | 471.9703 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -98.3982 | 373.5722 | -2750 | -200 | -2576.4278 | 64.41% | 64.46% | 95% | 0% | 1655 | -86
[5 empty] | 2019-06-02 | 2 | 3648 | 1501 | -93 | 0 | 0 | 1594 | 376.4221 | 376.4221 | 376.4221 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -106.4073 | 270.0148 | -2750 | -200 | -2679.9852 | 67% | 64.46% | 95% | 0% | 1594 | -93
[5 empty] | 2019-06-02 | 3 | 3648.5 | 1454 | -96 | 0 | 0 | 1550 | 307.5021 | 307.5021 | 307.5021 | 1537.0981 | 780 | 200 | 2517.0981 | 62.93% | 95% | 0% | -109.8398 | 197.6622 | -2750 | -200 | -2752.3378 | 68.81% | 64.46% | 95% | 0% | 1550 | -96
[5 empty] | 2019-06-02 | 4 | 3649 | 1436 | -100 | 0 | 0 | 1536 | 285.573 | 285.573 | 285.573 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -114.4165 | 171.1565 | -2750 | -200 | -2778.8435 | 69.47% | 64.46% | 95% | 0% | 1536 | -100
[5 empty] | 2019-06-02 | 5 | 3649.5 | 1399 | -103 | 0 | 0 | 1502 | 232.3166 | 232.3166 | 232.3166 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -117.849 | 114.4676 | -2750 | -200 | -2835.5324 | 70.89% | 64.45% | 95% | 0% | 1502 | -103
[5 empty] | 2019-06-02 | 6 | 3650 | 1366 | -106 | 0 | 0 | 1472 | 185.3256 | 185.3256 | 185.3256 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -121.2815 | 64.0442 | -2750 | -200 | -2885.9558 | 72.15% | 64.45% | 95% | 0% | 1472 | -106
[5 empty] | 2019-06-02 | 7 | 3650.5 | 1331 | -109 | 0 | 0 | 1440 | 135.202 | 135.202 | 135.202 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -124.714 | 10.488 | -2750 | -200 | -2939.512 | 73.49% | 64.45% | 95% | 0% | 1440 | -109
[5 empty] | 2019-06-02 | 8 | 3651 | 1306 | -112 | 0 | 0 | 1418 | 100.742 | 100.742 | 100.742 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -128.1465 | -27.4045 | -2750 | -200 | -2977.4045 | 74.44% | 64.45% | 95% | 0% | 1418 | -112
[5 empty] | 2019-06-02 | 9 | 3651.5 | 1282 | -114 | 1 | 0 | 1396 | 66.2819 | 66.2819 | 66.2819 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -130.4348 | -64.1528 | -3550 | -400 | -4014.1528 | 100.4% | 64.45% | 95% | 0% | 1396 | -114
[5 empty] | 2019-06-02 | 10 | 3652 | 1229 | -117 | 1 | 0 | 1346 | -12.0363 | -12.0363 | -12.0363 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -133.8673 | -145.9036 | -3550 | -400 | -4095.9036 | 102.4% | 64.44% | 95% | 0% | 1346 | -117
[5 empty] | 2019-06-02 | 11 | 3652.5 | 1202 | -124 | 1 | 0 | 1326 | -43.3636 | -43.3636 | -43.3636 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -141.8764 | -185.24 | -3550 | -400 | -4135.24 | 103.4% | 64.44% | 95% | 0% | 1326 | -124
[5 empty] | 2019-06-02 | 12 | 3653 | 1180 | -140 | 1 | 0 | 1320 | -52.7617 | -52.7617 | -52.7617 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -160.1831 | -212.9448 | -3550 | -400 | -4162.9448 | 104.1% | 64.44% | 95% | 0% | 1320 | -140
[5 empty] | 2019-06-02 | 13 | 3653.5 | 1175 | -169 | 1 | 0 | 1344 | -15.169 | -15.169 | -15.169 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -193.3638 | -208.5328 | -3550 | -400 | -4158.5328 | 104% | 64.43% | 95% | 0% | 1344 | -169
[5 empty] | 2019-06-02 | 14 | 3654 | 1171 | -199 | 1 | 0 | 1370 | 25.5565 | 25.5565 | 25.5565 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -227.6888 | -202.1323 | -3550 | -400 | -4152.1323 | 103.8% | 64.43% | 95% | 0% | 1370 | -199
[5 empty] | 2019-06-02 | 15 | 3654.5 | 1178 | -241 | 1 | 0 | 1419 | 102.3083 | 102.3083 | 102.3083 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -275.7437 | -173.4354 | -3550 | -400 | -4123.4354 | 103.1% | 64.42% | 95% | 0% | 1419 | -241
[5 empty] | 2019-06-02 | 16 | 3655 | 1202 | -274 | 1 | 0 | 1476 | 191.5911 | 191.5911 | 191.5911 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -313.5011 | -121.91 | -3550 | -400 | -4071.91 | 101.8% | 64.42% | 95% | 0% | 1476 | -274
[5 empty] | 2019-06-02 | 17 | 3655.5 | 1225 | -317 | 1 | 0 | 1542 | 294.9711 | 294.9711 | 294.9711 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -362.7002 | -67.7291 | -3550 | -400 | -4017.7291 | 100.4% | 64.42% | 95% | 0% | 1542 | -317
[5 empty] | 2019-06-02 | 18 | 3656 | 1192 | -372 | 1 | 0 | 1564 | 329.4312 | 329.4312 | 329.4312 | 1535.5317 | 780 | 200 | 2515.5317 | 62.89% | 95% | 0% | -425.6293 | -96.1981 | -3550 | -400 | -4046.1981 | 101.2% | 64.42% | 95% | 0% | 1564 | -372
[5 empty] | 2019-06-02 | 19 | 3656.5 | 1244 | -411 | 1 | 0 | 1655 | 471.9703 | 471.9703 | 471.9703 | 1533.9654 | 780 | 200 | 2513.9654 | 62.85% | 95% | 0% | -470.2517 | 1.7186 | -3550 | -400 | -3948.2814 | 98.71% | 64.42% | 95% | 0% | 1655 | -411
[5 empty] | 2019-06-02 | 20 | 3657 | 1265 | -436 | 1 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 1533.9654 | 780 | 200 | 2513.9654 | 62.85% | 95% | 0% | -498.8558 | 45.1672 | -3550 | -400 | -3904.8328 | 97.62% | 64.42% | 95% | 0% | 1701 | -436
[5 empty] | 2019-06-02 | 21 | 3657.5 | 1275 | -486 | 1 | 0 | 1761 | 638.0049 | 638.0049 | 638.0049 | 1533.9654 | 780 | 200 | 2513.9654 | 62.85% | 95% | 0% | -556.0641 | 81.9409 | -3550 | -400 | -3868.0591 | 96.7% | 64.42% | 95% | 0% | 1761 | -486
[5 empty] | 2019-06-02 | 22 | 3658 | 1253 | -523 | 1 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 1533.9654 | 780 | 200 | 2513.9654 | 62.85% | 95% | 0% | -598.3982 | 63.1022 | -3550 | -400 | -3886.8978 | 97.17% | 64.42% | 95% | 0% | 1776 | -523
[5 empty] | 2019-06-02 | 23 | 3658.5 | 1244 | -538 | 1 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 1533.9654 | 780 | 200 | 2513.9654 | 62.85% | 95% | 0% | -615.5606 | 55.338 | -3550 | -400 | -3894.662 | 97.37% | 64.42% | 95% | 0% | 1782 | -538
[5 empty] | 2019-06-02 | 24 | 3659 | 1255 | -537 | 1 | 0 | 1792 | 686.5622 | 686.5622 | 686.5622 | 1533.9654 | 780 | 200 | 2513.9654 | 62.85% | 95% | 0% | -614.4165 | 72.1458 | -3550 | -400 | -3877.8542 | 96.95% | 64.41% | 95% | 0% | 1792 | -537
[5 empty] | 2019-06-02 | 25 | 3659.5 | 1237 | -568 | 1 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 1533.9654 | 780 | 200 | 2513.9654 | 62.85% | 95% | 0% | -649.8856 | 57.0394 | -3550 | -400 | -3892.9606 | 97.32% | 64.41% | 95% | 0% | 1805 | -568
[5 empty] | 2019-06-02 | 26 | 3660 | 1233 | -554 | 1 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 1533.9654 | 780 | 200 | 2513.9654 | 62.85% | 95% | 0% | -633.8673 | 44.8631 | -3550 | -400 | -3905.1369 | 97.63% | 64.41% | 95% | 0% | 1787 | -554
[5 empty] | 2019-06-02 | 27 | 3660.5 | 1222 | -543 | 1 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 1533.9654 | 780 | 200 | 2513.9654 | 62.85% | 95% | 0% | -621.2815 | 22.9889 | -3550 | -400 | -3927.0111 | 98.18% | 64.41% | 95% | 0% | 1765 | -543
[5 empty] | 2019-06-02 | 28 | 3661 | 1228 | -531 | 1 | 0 | 1759 | 634.8722 | 634.8722 | 634.8722 | 1532.399 | 780 | 200 | 2512.399 | 62.81% | 95% | 0% | -607.5515 | 27.3207 | -3550 | -400 | -3922.6793 | 98.07% | 64.41% | 95% | 0% | 1759 | -531
[5 empty] | 2019-06-02 | 29 | 3661.5 | 1245 | -526 | 1 | 0 | 1771 | 653.6686 | 653.6686 | 653.6686 | 1532.399 | 780 | 200 | 2512.399 | 62.81% | 95% | 0% | -601.8307 | 51.8379 | -3550 | -400 | -3898.1621 | 97.45% | 64.41% | 95% | 0% | 1771 | -526
[5 empty] | 2019-06-02 | 30 | 3662 | 1269 | -496 | 1 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 1532.399 | 780 | 200 | 2512.399 | 62.81% | 95% | 0% | -567.5057 | 76.7647 | -3550 | -400 | -3873.2353 | 96.83% | 64.41% | 95% | 0% | 1765 | -496
[5 empty] | 2019-06-02 | 31 | 3662.5 | 1301 | -465 | 1 | 0 | 1766 | 645.8368 | 645.8368 | 645.8368 | 1532.399 | 780 | 200 | 2512.399 | 62.81% | 95% | 0% | -532.0366 | 113.8002 | -3550 | -400 | -3836.1998 | 95.9% | 64.41% | 95% | 0% | 1766 | -465
[5 empty] | 2019-06-02 | 32 | 3663 | 1351 | -442 | 1 | 0 | 1793 | 688.1286 | 688.1286 | 688.1286 | 1532.399 | 780 | 200 | 2512.399 | 62.81% | 95% | 0% | -505.7208 | 182.4078 | -3550 | -400 | -3767.5922 | 94.19% | 64.4% | 95% | 0% | 1793 | -442
[5 empty] | 2019-06-02 | 33 | 3663.5 | 1381 | -423 | 1 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 1532.399 | 780 | 200 | 2512.399 | 62.81% | 95% | 0% | -483.9817 | 221.3769 | -3550 | -400 | -3728.6231 | 93.22% | 64.4% | 95% | 0% | 1804 | -423
[5 empty] | 2019-06-02 | 34 | 3664 | 1406 | -415 | 1 | 0 | 1821 | 731.9868 | 731.9868 | 731.9868 | 1532.399 | 780 | 200 | 2512.399 | 62.81% | 95% | 0% | -474.8284 | 257.1584 | -3550 | -400 | -3692.8416 | 92.32% | 64.4% | 95% | 0% | 1821 | -415
[5 empty] | 2019-06-02 | 35 | 3664.5 | 1421 | -407 | 1 | 0 | 1828 | 742.9514 | 742.9514 | 742.9514 | 1532.399 | 780 | 200 | 2512.399 | 62.81% | 95% | 0% | -465.6751 | 277.2763 | -3550 | -400 | -3672.7237 | 91.82% | 64.39% | 95% | 0% | 1828 | -407
[5 empty] | 2019-06-02 | 36 | 3665 | 1472 | -378 | 1 | 0 | 1850 | 777.4114 | 777.4114 | 777.4114 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -432.4943 | 344.9171 | -3550 | -400 | -3605.0829 | 90.13% | 64.39% | 95% | 0% | 1850 | -378
[5 empty] | 2019-06-02 | 37 | 3665.5 | 1529 | -340 | 1 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -389.016 | 418.1563 | -3550 | -400 | -3531.8437 | 88.3% | 64.39% | 95% | 0% | 1869 | -340
[5 empty] | 2019-06-02 | 38 | 3666 | 1584 | -299 | 1 | 0 | 1883 | 829.1014 | 829.1014 | 829.1014 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -342.1053 | 486.9961 | -3550 | -400 | -3463.0039 | 86.58% | 64.39% | 95% | 0% | 1883 | -299
[5 empty] | 2019-06-02 | 39 | 3666.5 | 1618 | -271 | 1 | 0 | 1889 | 838.4996 | 838.4996 | 838.4996 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -310.0686 | 528.4309 | -3550 | -400 | -3421.5691 | 85.54% | 64.38% | 95% | 0% | 1889 | -271
[5 empty] | 2019-06-02 | 40 | 3667 | 1652 | -234 | 1 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -267.7346 | 566.0659 | -3550 | -400 | -3383.9341 | 84.6% | 64.38% | 95% | 0% | 1886 | -234
[5 empty] | 2019-06-02 | 41 | 3667.5 | 1697 | -205 | 1 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -234.5538 | 624.3085 | -3550 | -400 | -3325.6915 | 83.14% | 64.38% | 95% | 0% | 1902 | -205
[5 empty] | 2019-06-02 | 42 | 3668 | 1729 | -184 | 1 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -210.5263 | 665.566 | -3550 | -400 | -3284.434 | 82.11% | 64.38% | 95% | 0% | 1913 | -184
[5 empty] | 2019-06-02 | 43 | 3668.5 | 1719 | -178 | 1 | 0 | 1897 | 851.0305 | 851.0305 | 851.0305 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -203.6613 | 647.3692 | -3550 | -400 | -3302.6308 | 82.57% | 64.38% | 95% | 0% | 1897 | -178
[5 empty] | 2019-06-02 | 44 | 3669 | 1715 | -178 | 1 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -203.6613 | 641.1037 | -3550 | -400 | -3308.8963 | 82.72% | 64.37% | 95% | 0% | 1893 | -178
[5 empty] | 2019-06-02 | 45 | 3669.5 | 1671 | -179 | 0 | 0 | 1850 | 777.4114 | 777.4114 | 777.4114 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -204.8055 | 572.6059 | -2750 | -200 | -2377.3941 | 59.43% | 64.37% | 95% | 0% | 1850 | -179
[5 empty] | 2019-06-02 | 46 | 3670 | 1578 | -180 | 0 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -205.9497 | 427.3562 | -2750 | -200 | -2522.6438 | 63.07% | 64.37% | 95% | 0% | 1758 | -180
[5 empty] | 2019-06-02 | 47 | 3670.5 | 1443 | -180 | 1 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -205.9497 | 215.897 | -3550 | -400 | -3734.103 | 93.35% | 64.36% | 95% | 0% | 1623 | -180
[5 empty] | 2019-06-02 | 48 | 3671 | 1339 | -179 | 1 | 0 | 1518 | 257.3784 | 257.3784 | 257.3784 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -204.8055 | 52.5729 | -3550 | -400 | -3897.4271 | 97.44% | 64.36% | 95% | 0% | 1518 | -179
[5 empty] | 2019-06-03 | 1 | 3671.5 | 1253 | -179 | 1 | 0 | 1432 | 122.6711 | 122.6711 | 122.6711 | 1530.8326 | 780 | 200 | 2510.8326 | 62.77% | 95% | 0% | -204.8055 | -82.1344 | -3550 | -400 | -4032.1344 | 100.8% | 64.36% | 95% | 0% | 1432 | -179
[5 empty] | 2019-06-03 | 2 | 3672 | 1206 | -178 | 1 | 0 | 1384 | 47.4856 | 47.4856 | 47.4856 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -203.6613 | -156.1758 | -3550 | -400 | -4106.1758 | 102.7% | 64.36% | 95% | 0% | 1384 | -178
[5 empty] | 2019-06-03 | 3 | 3672.5 | 1172 | -177 | 1 | 0 | 1349 | -7.3372 | -7.3372 | -7.3372 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -202.5172 | -209.8543 | -3550 | -400 | -4159.8543 | 104% | 64.36% | 95% | 0% | 1349 | -177
[5 empty] | 2019-06-03 | 4 | 3673 | 1173 | -175 | 1 | 0 | 1348 | -8.9035 | -8.9035 | -8.9035 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -200.2288 | -209.1324 | -3550 | -400 | -4159.1324 | 104% | 64.36% | 95% | 0% | 1348 | -175
[5 empty] | 2019-06-03 | 5 | 3673.5 | 1163 | -173 | 0 | 0 | 1336 | -27.6999 | -27.6999 | -27.6999 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -197.9405 | -225.6404 | -2750 | -200 | -3175.6404 | 79.39% | 64.36% | 95% | 0% | 1336 | -173
[5 empty] | 2019-06-03 | 6 | 3674 | 1149 | -171 | 0 | 0 | 1320 | -52.7617 | -52.7617 | -52.7617 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -195.6522 | -248.4139 | -2750 | -200 | -3198.4139 | 79.96% | 64.36% | 95% | 0% | 1320 | -171
[5 empty] | 2019-06-03 | 7 | 3674.5 | 1135 | -170 | 0 | 0 | 1305 | -76.2572 | -76.2572 | -76.2572 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -194.508 | -270.7652 | -2750 | -200 | -3220.7652 | 80.52% | 64.35% | 95% | 0% | 1305 | -170
[5 empty] | 2019-06-03 | 8 | 3675 | 1145 | -169 | 1 | 0 | 1314 | -62.1599 | -62.1599 | -62.1599 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -193.3638 | -255.5238 | -3550 | -400 | -4205.5238 | 105.1% | 64.35% | 95% | 0% | 1314 | -169
[5 empty] | 2019-06-03 | 9 | 3675.5 | 1144 | -165 | 1 | 0 | 1309 | -69.9918 | -69.9918 | -69.9918 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -188.7872 | -258.7789 | -3550 | -400 | -4208.7789 | 105.2% | 64.35% | 95% | 0% | 1309 | -165
[5 empty] | 2019-06-03 | 10 | 3676 | 1150 | -161 | 1 | 0 | 1311 | -66.859 | -66.859 | -66.859 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -184.2105 | -251.0696 | -3550 | -400 | -4201.0696 | 105% | 64.35% | 95% | 0% | 1311 | -161
[5 empty] | 2019-06-03 | 11 | 3676.5 | 1190 | -164 | 1 | 0 | 1354 | 0.49464 | 0.49464 | 0.49464 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -187.643 | -187.1484 | -3550 | -400 | -4137.1484 | 103.4% | 64.34% | 95% | 0% | 1354 | -164
[5 empty] | 2019-06-03 | 12 | 3677 | 1245 | -181 | 1 | 0 | 1426 | 113.2729 | 113.2729 | 113.2729 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -207.0938 | -93.8209 | -3550 | -400 | -4043.8209 | 101.1% | 64.34% | 95% | 0% | 1426 | -181
[5 empty] | 2019-06-03 | 13 | 3677.5 | 1399 | -212 | 1 | 0 | 1611 | 403.0503 | 403.0503 | 403.0503 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -242.5629 | 160.4874 | -3550 | -400 | -3789.5126 | 94.74% | 64.34% | 95% | 0% | 1611 | -212
[5 empty] | 2019-06-03 | 14 | 3678 | 1528 | -257 | 1 | 0 | 1785 | 675.5977 | 675.5977 | 675.5977 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -294.0503 | 381.5473 | -3550 | -400 | -3568.4527 | 89.21% | 64.33% | 95% | 0% | 1785 | -257
[5 empty] | 2019-06-03 | 15 | 3678.5 | 1665 | -315 | 1 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -360.4119 | 620.6268 | -3550 | -400 | -3329.3732 | 83.23% | 64.32% | 95% | 0% | 1980 | -315
[5 empty] | 2019-06-03 | 16 | 3679 | 1674 | -369 | 1 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -422.1968 | 657.5229 | -3550 | -400 | -3292.4771 | 82.31% | 64.32% | 95% | 0% | 2043 | -369
[5 empty] | 2019-06-03 | 17 | 3679.5 | 1642 | -440 | 1 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -503.4325 | 637.3754 | -3550 | -400 | -3312.6246 | 82.82% | 64.32% | 95% | 0% | 2082 | -440
[5 empty] | 2019-06-03 | 18 | 3680 | 1567 | -510 | 1 | 0 | 2077 | 1132.9761 | 1132.9761 | 1132.9761 | 1529.2663 | 780 | 200 | 2509.2663 | 62.73% | 95% | 0% | -583.524 | 549.4521 | -3550 | -400 | -3400.5479 | 85.01% | 64.31% | 95% | 0% | 2077 | -510
[5 empty] | 2019-06-03 | 19 | 3680.5 | 1485 | -573 | 1 | 0 | 2058 | 1103.2152 | 1103.2152 | 1103.2152 | 1527.6999 | 780 | 200 | 2507.6999 | 62.69% | 95% | 0% | -655.6064 | 447.6088 | -3550 | -400 | -3502.3912 | 87.56% | 64.31% | 95% | 0% | 2058 | -573
[5 empty] | 2019-06-03 | 20 | 3681 | 1416 | -610 | 1 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 1527.6999 | 780 | 200 | 2507.6999 | 62.69% | 95% | 0% | -697.9405 | 355.151 | -3550 | -400 | -3594.849 | 89.87% | 64.31% | 95% | 0% | 2026 | -610
[5 empty] | 2019-06-03 | 21 | 3681.5 | 1348 | -658 | 1 | 0 | 2006 | 1021.7642 | 1021.7642 | 1021.7642 | 1527.6999 | 780 | 200 | 2507.6999 | 62.69% | 95% | 0% | -752.8604 | 268.9038 | -3550 | -400 | -3681.0962 | 92.03% | 64.31% | 95% | 0% | 2006 | -658
[5 empty] | 2019-06-03 | 22 | 3682 | 1314 | -681 | 1 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 1527.6999 | 780 | 200 | 2507.6999 | 62.69% | 95% | 0% | -779.1762 | 225.358 | -3550 | -400 | -3724.642 | 93.12% | 64.3% | 95% | 0% | 1995 | -681
[5 empty] | 2019-06-03 | 23 | 3682.5 | 1329 | -679 | 1 | 0 | 2008 | 1024.8969 | 1024.8969 | 1024.8969 | 1527.6999 | 780 | 200 | 2507.6999 | 62.69% | 95% | 0% | -776.8879 | 248.0091 | -3550 | -400 | -3701.9909 | 92.55% | 64.3% | 95% | 0% | 2008 | -679
[5 empty] | 2019-06-03 | 24 | 3683 | 1328 | -687 | 1 | 0 | 2015 | 1035.8615 | 1035.8615 | 1035.8615 | 1527.6999 | 780 | 200 | 2507.6999 | 62.69% | 95% | 0% | -786.0412 | 249.8203 | -3550 | -400 | -3700.1797 | 92.5% | 64.3% | 95% | 0% | 2015 | -687
[5 empty] | 2019-06-03 | 25 | 3683.5 | 1286 | -716 | 1 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 1527.6999 | 780 | 200 | 2507.6999 | 62.69% | 95% | 0% | -819.222 | 196.2768 | -3550 | -400 | -3753.7232 | 93.84% | 64.3% | 95% | 0% | 2002 | -716
[5 empty] | 2019-06-03 | 26 | 3684 | 1256 | -738 | 1 | 0 | 1994 | 1002.9678 | 1002.9678 | 1002.9678 | 1527.6999 | 780 | 200 | 2507.6999 | 62.69% | 95% | 0% | -844.3936 | 158.5743 | -3550 | -400 | -3791.4257 | 94.79% | 64.3% | 95% | 0% | 1994 | -738
[5 empty] | 2019-06-03 | 27 | 3684.5 | 1241 | -732 | 1 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 1527.6999 | 780 | 200 | 2507.6999 | 62.69% | 95% | 0% | -837.5286 | 132.5456 | -3550 | -400 | -3817.4544 | 95.44% | 64.29% | 95% | 0% | 1973 | -732
[5 empty] | 2019-06-03 | 28 | 3685 | 1214 | -734 | 1 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 1527.6999 | 780 | 200 | 2507.6999 | 62.69% | 95% | 0% | -839.8169 | 91.0982 | -3550 | -400 | -3858.9018 | 96.47% | 64.29% | 95% | 0% | 1948 | -734
[5 empty] | 2019-06-03 | 29 | 3685.5 | 1252 | -711 | 1 | 0 | 1963 | 954.4106 | 954.4106 | 954.4106 | 1527.6999 | 780 | 200 | 2507.6999 | 62.69% | 95% | 0% | -813.5011 | 140.9094 | -3550 | -400 | -3809.0906 | 95.23% | 64.29% | 95% | 0% | 1963 | -711
[5 empty] | 2019-06-03 | 30 | 3686 | 1278 | -681 | 1 | 0 | 1959 | 948.1451 | 948.1451 | 948.1451 | 1527.6999 | 780 | 200 | 2507.6999 | 62.69% | 95% | 0% | -779.1762 | 168.9689 | -3550 | -400 | -3781.0311 | 94.53% | 64.28% | 95% | 0% | 1959 | -681
[5 empty] | 2019-06-03 | 31 | 3686.5 | 1331 | -639 | 1 | 0 | 1970 | 965.3751 | 965.3751 | 965.3751 | 1526.1336 | 780 | 200 | 2506.1336 | 62.65% | 95% | 0% | -731.1213 | 234.2538 | -3550 | -400 | -3715.7462 | 92.89% | 64.28% | 95% | 0% | 1970 | -639
[5 empty] | 2019-06-03 | 32 | 3687 | 1413 | -579 | 1 | 0 | 1992 | 999.8351 | 999.8351 | 999.8351 | 1526.1336 | 780 | 200 | 2506.1336 | 62.65% | 95% | 0% | -662.4714 | 337.3637 | -3550 | -400 | -3612.6363 | 90.32% | 64.28% | 95% | 0% | 1992 | -579
[5 empty] | 2019-06-03 | 33 | 3687.5 | 1555 | -545 | 1 | 0 | 2100 | 1169.0025 | 1169.0025 | 1169.0025 | 1526.1336 | 780 | 200 | 2506.1336 | 62.65% | 95% | 0% | -623.5698 | 545.4327 | -3550 | -400 | -3404.5673 | 85.11% | 64.27% | 95% | 0% | 2100 | -545
[5 empty] | 2019-06-03 | 34 | 3688 | 1703 | -477 | 1 | 0 | 2180 | 1294.3116 | 1294.3116 | 1294.3116 | 1526.1336 | 780 | 200 | 2506.1336 | 62.65% | 95% | 0% | -545.7666 | 748.545 | -3550 | -400 | -3201.455 | 80.04% | 64.27% | 95% | 0% | 2180 | -477
[5 empty] | 2019-06-03 | 35 | 3688.5 | 1794 | -429 | 1 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 1526.1336 | 780 | 200 | 2506.1336 | 62.65% | 95% | 0% | -490.8467 | 870.8186 | -3550 | -400 | -3079.1814 | 76.98% | 64.27% | 95% | 0% | 2223 | -429
[5 empty] | 2019-06-03 | 36 | 3689 | 1893 | -376 | 1 | 0 | 2269 | 1433.7181 | 1433.7181 | 1433.7181 | 1526.1336 | 780 | 200 | 2506.1336 | 62.65% | 95% | 0% | -430.2059 | 1003.5121 | -3550 | -400 | -2946.4879 | 73.66% | 64.26% | 95% | 0% | 2269 | -376
[5 empty] | 2019-06-03 | 37 | 3689.5 | 1991 | -316 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1526.1336 | 780 | 200 | 2506.1336 | 62.65% | 95% | 0% | -361.5561 | 1131.6838 | -3550 | -400 | -2818.3162 | 70.46% | 64.26% | 95% | 0% | 2307 | -316
[5 empty] | 2019-06-03 | 38 | 3690 | 2060 | -268 | 1 | 0 | 2328 | 1526.1336 | 1526.1336 | 1526.1336 | 1526.1336 | 780 | 200 | 2506.1336 | 62.65% | 95% | 0% | -306.6362 | 1219.4974 | -3550 | -400 | -2730.5026 | 68.26% | 64.25% | 95% | 0% | 2328 | -268
[5 empty] | 2019-06-03 | 39 | 3690.5 | 2129 | -210 | 1 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 1526.1336 | 780 | 200 | 2506.1336 | 62.65% | 95% | 0% | -240.2746 | 1303.089 | -3550 | -400 | -2646.911 | 66.17% | 64.25% | 95% | 0% | 2339 | -210
[5 empty] | 2019-06-03 | 40 | 3691 | 2143 | -170 | 1 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 1526.1336 | 780 | 200 | 2506.1336 | 62.65% | 95% | 0% | -194.508 | 1308.1301 | -3550 | -400 | -2641.8699 | 66.05% | 64.25% | 95% | 0% | 2313 | -170
[5 empty] | 2019-06-03 | 41 | 3691.5 | 2160 | -140 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 1526.1336 | 780 | 200 | 2506.1336 | 62.65% | 95% | 0% | -160.1831 | 1322.0923 | -3550 | -400 | -2627.9077 | 65.7% | 64.25% | 95% | 0% | 2300 | -140
[5 empty] | 2019-06-03 | 42 | 3692 | 2191 | -116 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1524.5672 | 780 | 200 | 2504.5672 | 62.61% | 95% | 0% | -132.7231 | 1360.5168 | -3550 | -400 | -2589.4832 | 64.74% | 64.25% | 95% | 0% | 2307 | -116
[5 empty] | 2019-06-03 | 43 | 3692.5 | 2188 | -105 | 1 | 0 | 2293 | 1471.3108 | 1471.3108 | 1471.3108 | 1524.5672 | 780 | 200 | 2504.5672 | 62.61% | 95% | 0% | -120.1373 | 1351.1735 | -3550 | -400 | -2598.8265 | 64.97% | 64.25% | 95% | 0% | 2293 | -105
[5 empty] | 2019-06-03 | 44 | 3693 | 2153 | -100 | 1 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 1524.5672 | 780 | 200 | 2504.5672 | 62.61% | 95% | 0% | -114.4165 | 1294.2397 | -3550 | -400 | -2655.7603 | 66.39% | 64.24% | 95% | 0% | 2253 | -100
[5 empty] | 2019-06-03 | 45 | 3693.5 | 2079 | -98 | 1 | 0 | 2177 | 1289.6125 | 1289.6125 | 1289.6125 | 1524.5672 | 780 | 200 | 2504.5672 | 62.61% | 95% | 0% | -112.1281 | 1177.4844 | -3550 | -400 | -2772.5156 | 69.31% | 64.24% | 95% | 0% | 2177 | -98
[5 empty] | 2019-06-03 | 46 | 3694 | 1961 | -95 | 0 | 0 | 2056 | 1100.0824 | 1100.0824 | 1100.0824 | 1524.5672 | 780 | 200 | 2504.5672 | 62.61% | 95% | 0% | -108.6957 | 991.3868 | -2750 | -200 | -1958.6132 | 48.97% | 64.24% | 95% | 0% | 2056 | -95
[5 empty] | 2019-06-03 | 47 | 3694.5 | 1835 | -93 | 0 | 0 | 1928 | 899.5878 | 899.5878 | 899.5878 | 1524.5672 | 780 | 200 | 2504.5672 | 62.61% | 95% | 0% | -106.4073 | 793.1805 | -2750 | -200 | -2156.8195 | 53.92% | 64.24% | 95% | 0% | 1928 | -93
[5 empty] | 2019-06-03 | 48 | 3695 | 1731 | -91 | 0 | 0 | 1822 | 733.5532 | 733.5532 | 733.5532 | 1524.5672 | 780 | 200 | 2504.5672 | 62.61% | 95% | 0% | -104.119 | 629.4342 | -2750 | -200 | -2320.5658 | 58.01% | 64.24% | 95% | 0% | 1822 | -91
[5 empty] | 2019-06-04 | 1 | 3695.5 | 1649 | -84 | 1 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 1524.5672 | 780 | 200 | 2504.5672 | 62.61% | 95% | 0% | -96.1098 | 498.0369 | -3550 | -400 | -3451.9631 | 86.3% | 64.23% | 95% | 0% | 1733 | -84
[5 empty] | 2019-06-04 | 2 | 3696 | 1600 | -77 | 1 | 0 | 1677 | 506.4303 | 506.4303 | 506.4303 | 1524.5672 | 780 | 200 | 2504.5672 | 62.61% | 95% | 0% | -88.1007 | 418.3297 | -3550 | -400 | -3531.6703 | 88.29% | 64.23% | 95% | 0% | 1677 | -77
[5 empty] | 2019-06-04 | 3 | 3696.5 | 1582 | -75 | 1 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 1524.5672 | 780 | 200 | 2504.5672 | 62.61% | 95% | 0% | -85.8124 | 389.2907 | -3550 | -400 | -3560.7093 | 89.02% | 64.23% | 95% | 0% | 1657 | -75
[5 empty] | 2019-06-04 | 4 | 3697 | 1575 | -73 | 1 | 0 | 1648 | 461.0058 | 461.0058 | 461.0058 | 1524.5672 | 780 | 200 | 2504.5672 | 62.61% | 95% | 0% | -83.524 | 377.4817 | -3550 | -400 | -3572.5183 | 89.31% | 64.23% | 95% | 0% | 1648 | -73
[5 empty] | 2019-06-04 | 5 | 3697.5 | 1560 | -70 | 1 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -80.0915 | 352.7197 | -3550 | -400 | -3597.2803 | 89.93% | 64.23% | 95% | 0% | 1630 | -70
[5 empty] | 2019-06-04 | 6 | 3698 | 1536 | -67 | 1 | 0 | 1603 | 390.5194 | 390.5194 | 390.5194 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -76.659 | 313.8603 | -3550 | -400 | -3636.1397 | 90.9% | 64.23% | 95% | 0% | 1603 | -67
[5 empty] | 2019-06-04 | 7 | 3698.5 | 1523 | -65 | 1 | 0 | 1588 | 367.0239 | 367.0239 | 367.0239 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -74.3707 | 292.6532 | -3550 | -400 | -3657.3468 | 91.43% | 64.23% | 95% | 0% | 1588 | -65
[5 empty] | 2019-06-04 | 8 | 3699 | 1514 | -63 | 1 | 0 | 1577 | 349.7939 | 349.7939 | 349.7939 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -72.0824 | 277.7115 | -3550 | -400 | -3672.2885 | 91.81% | 64.22% | 95% | 0% | 1577 | -63
[5 empty] | 2019-06-04 | 9 | 3699.5 | 1523 | -60 | 1 | 0 | 1583 | 359.1921 | 359.1921 | 359.1921 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -68.6499 | 290.5422 | -3550 | -400 | -3659.4578 | 91.49% | 64.21% | 95% | 0% | 1583 | -60
[5 empty] | 2019-06-04 | 10 | 3700 | 1514 | -58 | 1 | 0 | 1572 | 341.9621 | 341.9621 | 341.9621 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -66.3616 | 275.6005 | -3550 | -400 | -3674.3995 | 91.86% | 64.21% | 95% | 0% | 1572 | -58
[5 empty] | 2019-06-04 | 11 | 3700.5 | 1554 | -61 | 1 | 0 | 1615 | 409.3157 | 409.3157 | 409.3157 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -69.7941 | 339.5217 | -3550 | -400 | -3610.4783 | 90.26% | 64.21% | 95% | 0% | 1615 | -61
[5 empty] | 2019-06-04 | 12 | 3701 | 1622 | -73 | 1 | 0 | 1695 | 534.6249 | 534.6249 | 534.6249 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -83.524 | 451.1009 | -3550 | -400 | -3498.8991 | 87.47% | 64.2% | 95% | 0% | 1695 | -73
[5 empty] | 2019-06-04 | 13 | 3701.5 | 1755 | -95 | 1 | 0 | 1850 | 777.4114 | 777.4114 | 777.4114 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -108.6957 | 668.7157 | -3550 | -400 | -3281.2843 | 82.03% | 64.2% | 95% | 0% | 1850 | -95
[5 empty] | 2019-06-04 | 14 | 3702 | 1898 | -113 | 1 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -129.2906 | 900.3054 | -3550 | -400 | -3049.6946 | 76.24% | 64.2% | 95% | 0% | 2011 | -113
[5 empty] | 2019-06-04 | 15 | 3702.5 | 2087 | -144 | 1 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -164.7597 | 1209.4365 | -3550 | -400 | -2740.5635 | 68.51% | 64.2% | 95% | 0% | 2231 | -144
[5 empty] | 2019-06-04 | 16 | 3703 | 2150 | -184 | 1 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -210.5263 | 1325.0054 | -3550 | -400 | -2624.9946 | 65.62% | 64.2% | 95% | 0% | 2334 | -184
[5 empty] | 2019-06-04 | 17 | 3703.5 | 2177 | -236 | 1 | 0 | 2413 | 1659.2745 | 1659.2745 | 1659.2745 | 1523.0008 | 780 | 200 | 2503.0008 | 62.58% | 95% | 0% | -270.0229 | 1389.2516 | -3550 | -400 | -2560.7484 | 64.02% | 64.2% | 95% | 0% | 2413 | -236
[5 empty] | 2019-06-04 | 18 | 3704 | 2100 | -278 | 1 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 1521.4345 | 780 | 200 | 2501.4345 | 62.54% | 95% | 0% | -318.0778 | 1286.374 | -3550 | -400 | -2663.626 | 66.59% | 64.19% | 95% | 0% | 2378 | -278
[5 empty] | 2019-06-04 | 19 | 3704.5 | 2046 | -340 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 1521.4345 | 780 | 200 | 2501.4345 | 62.54% | 95% | 0% | -389.016 | 1227.9667 | -3550 | -400 | -2722.0333 | 68.05% | 64.19% | 95% | 0% | 2386 | -340
[5 empty] | 2019-06-04 | 20 | 3705 | 1997 | -381 | 1 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 1521.4345 | 780 | 200 | 2501.4345 | 62.54% | 95% | 0% | -435.9268 | 1168.525 | -3550 | -400 | -2781.475 | 69.54% | 64.19% | 95% | 0% | 2378 | -381
[5 empty] | 2019-06-04 | 21 | 3705.5 | 2004 | -383 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 1521.4345 | 780 | 200 | 2501.4345 | 62.54% | 95% | 0% | -438.2151 | 1180.3339 | -3550 | -400 | -2769.6661 | 69.24% | 64.18% | 95% | 0% | 2387 | -383
[5 empty] | 2019-06-04 | 22 | 3706 | 1977 | -407 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1521.4345 | 780 | 200 | 2501.4345 | 62.54% | 95% | 0% | -465.6751 | 1148.1749 | -3550 | -400 | -2801.8251 | 70.05% | 64.18% | 95% | 0% | 2384 | -407
[5 empty] | 2019-06-04 | 23 | 3706.5 | 2021 | -370 | 1 | 0 | 2391 | 1624.8145 | 1624.8145 | 1624.8145 | 1521.4345 | 780 | 200 | 2501.4345 | 62.54% | 95% | 0% | -423.341 | 1201.4735 | -3550 | -400 | -2748.5265 | 68.71% | 64.18% | 95% | 0% | 2391 | -370
[5 empty] | 2019-06-04 | 24 | 3707 | 2063 | -340 | 1 | 0 | 2403 | 1643.6109 | 1643.6109 | 1643.6109 | 1521.4345 | 780 | 200 | 2501.4345 | 62.54% | 95% | 0% | -389.016 | 1254.5949 | -3550 | -400 | -2695.4051 | 67.39% | 64.18% | 95% | 0% | 2403 | -340
[5 empty] | 2019-06-04 | 25 | 3707.5 | 2147 | -282 | 1 | 0 | 2429 | 1684.3364 | 1684.3364 | 1684.3364 | 1521.4345 | 780 | 200 | 2501.4345 | 62.54% | 95% | 0% | -322.6545 | 1361.6819 | -3550 | -400 | -2588.3181 | 64.71% | 64.17% | 95% | 0% | 2429 | -282
[5 empty] | 2019-06-04 | 26 | 3708 | 2182 | -259 | 1 | 0 | 2441 | 1703.1327 | 1703.1327 | 1703.1327 | 1521.4345 | 780 | 200 | 2501.4345 | 62.54% | 95% | 0% | -296.3387 | 1406.7941 | -3550 | -400 | -2543.2059 | 63.58% | 64.17% | 95% | 0% | 2441 | -259
[5 empty] | 2019-06-04 | 27 | 3708.5 | 2210 | -234 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 1521.4345 | 780 | 200 | 2501.4345 | 62.54% | 95% | 0% | -267.7346 | 1440.0973 | -3550 | -400 | -2509.9027 | 62.75% | 64.17% | 95% | 0% | 2444 | -234
[5 empty] | 2019-06-04 | 28 | 3709 | 2230 | -226 | 1 | 0 | 2456 | 1726.6282 | 1726.6282 | 1726.6282 | 1521.4345 | 780 | 200 | 2501.4345 | 62.54% | 95% | 0% | -258.5812 | 1468.047 | -3550 | -400 | -2481.953 | 62.05% | 64.17% | 95% | 0% | 2456 | -226
[5 empty] | 2019-06-04 | 29 | 3709.5 | 2216 | -223 | 1 | 0 | 2439 | 1700 | 1700 | 1700 | 1519.8681 | 780 | 200 | 2499.8681 | 62.5% | 95% | 0% | -255.1487 | 1444.8513 | -3550 | -400 | -2505.1487 | 62.63% | 64.16% | 95% | 0% | 2439 | -223
[5 empty] | 2019-06-04 | 30 | 3710 | 2230 | -209 | 1 | 0 | 2439 | 1700 | 1700 | 1700 | 1519.8681 | 780 | 200 | 2499.8681 | 62.5% | 95% | 0% | -239.1304 | 1460.8696 | -3550 | -400 | -2489.1304 | 62.23% | 64.16% | 95% | 0% | 2439 | -209
[5 empty] | 2019-06-04 | 31 | 3710.5 | 2261 | -206 | 1 | 0 | 2467 | 1743.8582 | 1743.8582 | 1743.8582 | 1519.8681 | 780 | 200 | 2499.8681 | 62.5% | 95% | 0% | -235.6979 | 1508.1603 | -3550 | -400 | -2441.8397 | 61.05% | 64.16% | 95% | 0% | 2467 | -206
[5 empty] | 2019-06-04 | 32 | 3711 | 2291 | -214 | 1 | 0 | 2505 | 1803.38 | 1803.38 | 1803.38 | 1519.8681 | 780 | 200 | 2499.8681 | 62.5% | 95% | 0% | -244.8513 | 1558.5288 | -3550 | -400 | -2391.4712 | 59.79% | 64.16% | 95% | 0% | 2505 | -214
[5 empty] | 2019-06-04 | 33 | 3711.5 | 2335 | -208 | 1 | 0 | 2543 | 1862.9019 | 1862.9019 | 1862.9019 | 1519.8681 | 780 | 200 | 2499.8681 | 62.5% | 95% | 0% | -237.9863 | 1624.9156 | -3550 | -400 | -2325.0844 | 58.13% | 64.16% | 95% | 0% | 2543 | -208
[5 empty] | 2019-06-04 | 34 | 3712 | 2369 | -192 | 1 | 0 | 2561 | 1891.0965 | 1891.0965 | 1891.0965 | 1519.8681 | 780 | 200 | 2499.8681 | 62.5% | 95% | 0% | -219.6796 | 1671.4168 | -3550 | -400 | -2278.5832 | 56.96% | 64.16% | 95% | 0% | 2561 | -192
[5 empty] | 2019-06-04 | 35 | 3712.5 | 2391 | -187 | 1 | 0 | 2578 | 1917.7246 | 1917.7246 | 1917.7246 | 1519.8681 | 780 | 200 | 2499.8681 | 62.5% | 95% | 0% | -213.9588 | 1703.7658 | -3550 | -400 | -2246.2342 | 56.16% | 64.16% | 95% | 0% | 2578 | -187
[5 empty] | 2019-06-04 | 36 | 3713 | 2416 | -162 | 1 | 0 | 2578 | 1917.7246 | 1917.7246 | 1917.7246 | 1519.8681 | 780 | 200 | 2499.8681 | 62.5% | 95% | 0% | -185.3547 | 1732.37 | -3550 | -400 | -2217.63 | 55.44% | 64.16% | 95% | 0% | 2578 | -162
[5 empty] | 2019-06-04 | 37 | 3713.5 | 2412 | -149 | 1 | 0 | 2561 | 1891.0965 | 1891.0965 | 1891.0965 | 1518.3017 | 780 | 200 | 2498.3017 | 62.46% | 95% | 0% | -170.4805 | 1720.6159 | -3550 | -400 | -2229.3841 | 55.73% | 64.15% | 95% | 0% | 2561 | -149
[5 empty] | 2019-06-04 | 38 | 3714 | 2421 | -141 | 1 | 0 | 2562 | 1892.6628 | 1892.6628 | 1892.6628 | 1518.3017 | 780 | 200 | 2498.3017 | 62.46% | 95% | 0% | -161.3272 | 1731.3356 | -3550 | -400 | -2218.6644 | 55.47% | 64.15% | 95% | 0% | 2562 | -141
[5 empty] | 2019-06-04 | 39 | 3714.5 | 2444 | -114 | 1 | 0 | 2558 | 1886.3974 | 1886.3974 | 1886.3974 | 1518.3017 | 780 | 200 | 2498.3017 | 62.46% | 95% | 0% | -130.4348 | 1755.9626 | -3550 | -400 | -2194.0374 | 54.85% | 64.15% | 95% | 0% | 2558 | -114
[5 empty] | 2019-06-04 | 40 | 3715 | 2435 | -101 | 1 | 0 | 2536 | 1851.9373 | 1851.9373 | 1851.9373 | 1518.3017 | 780 | 200 | 2498.3017 | 62.46% | 95% | 0% | -115.5606 | 1736.3767 | -3550 | -400 | -2213.6233 | 55.34% | 64.14% | 95% | 0% | 2536 | -101
[5 empty] | 2019-06-04 | 41 | 3715.5 | 2387 | -90 | 1 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 1518.3017 | 780 | 200 | 2498.3017 | 62.46% | 95% | 0% | -102.9748 | 1656.547 | -3550 | -400 | -2293.453 | 57.34% | 64.14% | 95% | 0% | 2477 | -90
[5 empty] | 2019-06-04 | 42 | 3716 | 2346 | -81 | 1 | 0 | 2427 | 1681.2036 | 1681.2036 | 1681.2036 | 1518.3017 | 780 | 200 | 2498.3017 | 62.46% | 95% | 0% | -92.6773 | 1588.5263 | -3550 | -400 | -2361.4737 | 59.04% | 64.13% | 95% | 0% | 2427 | -81
[5 empty] | 2019-06-04 | 43 | 3716.5 | 2304 | -79 | 1 | 0 | 2383 | 1612.2836 | 1612.2836 | 1612.2836 | 1518.3017 | 780 | 200 | 2498.3017 | 62.46% | 95% | 0% | -90.389 | 1521.8946 | -3550 | -400 | -2428.1054 | 60.7% | 64.13% | 95% | 0% | 2383 | -79
[5 empty] | 2019-06-04 | 44 | 3717 | 2244 | -82 | 1 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 1518.3017 | 780 | 200 | 2498.3017 | 62.46% | 95% | 0% | -93.8215 | 1429.1793 | -3550 | -400 | -2520.8207 | 63.02% | 64.13% | 95% | 0% | 2326 | -82
[5 empty] | 2019-06-04 | 45 | 3717.5 | 2138 | -83 | 1 | 0 | 2221 | 1358.5326 | 1358.5326 | 1358.5326 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -94.9657 | 1263.5669 | -3550 | -400 | -2686.4331 | 67.16% | 64.13% | 95% | 0% | 2221 | -83
[5 empty] | 2019-06-04 | 46 | 3718 | 1988 | -84 | 0 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -96.1098 | 1029.0344 | -2750 | -200 | -1920.9656 | 48.02% | 64.12% | 95% | 0% | 2072 | -84
[5 empty] | 2019-06-04 | 47 | 3718.5 | 1847 | -86 | 0 | 0 | 1933 | 907.4196 | 907.4196 | 907.4196 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -98.3982 | 809.0215 | -2750 | -200 | -2140.9785 | 53.52% | 64.12% | 95% | 0% | 1933 | -86
[5 empty] | 2019-06-04 | 48 | 3719 | 1721 | -88 | 0 | 0 | 1809 | 713.1904 | 713.1904 | 713.1904 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -100.6865 | 612.5039 | -2750 | -200 | -2337.4961 | 58.44% | 64.12% | 95% | 0% | 1809 | -88
[5 empty] | 2019-06-05 | 1 | 3719.5 | 1607 | -92 | 0 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -105.2632 | 435.6272 | -2750 | -200 | -2514.3728 | 62.86% | 64.12% | 95% | 0% | 1699 | -92
[5 empty] | 2019-06-05 | 2 | 3720 | 1540 | -97 | 0 | 0 | 1637 | 443.7758 | 443.7758 | 443.7758 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -110.984 | 332.7918 | -2750 | -200 | -2617.2082 | 65.43% | 64.11% | 95% | 0% | 1637 | -97
[5 empty] | 2019-06-05 | 3 | 3720.5 | 1497 | -99 | 0 | 0 | 1596 | 379.5548 | 379.5548 | 379.5548 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -113.2723 | 266.2825 | -2750 | -200 | -2683.7175 | 67.09% | 64.11% | 95% | 0% | 1596 | -99
[5 empty] | 2019-06-05 | 4 | 3721 | 1480 | -101 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -115.5606 | 240.4987 | -2750 | -200 | -2709.5013 | 67.74% | 64.11% | 95% | 0% | 1581 | -101
[5 empty] | 2019-06-05 | 5 | 3721.5 | 1449 | -102 | 0 | 0 | 1551 | 309.0684 | 309.0684 | 309.0684 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -116.7048 | 192.3636 | -2750 | -200 | -2757.6364 | 68.94% | 64.11% | 95% | 0% | 1551 | -102
[5 empty] | 2019-06-05 | 6 | 3722 | 1425 | -103 | 1 | 0 | 1528 | 273.042 | 273.042 | 273.042 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -117.849 | 155.1931 | -3550 | -400 | -3794.8069 | 94.87% | 64.1% | 95% | 0% | 1528 | -103
[5 empty] | 2019-06-05 | 7 | 3722.5 | 1409 | -103 | 1 | 0 | 1512 | 247.9802 | 247.9802 | 247.9802 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -117.849 | 130.1312 | -3550 | -400 | -3819.8688 | 95.5% | 64.1% | 95% | 0% | 1512 | -103
[5 empty] | 2019-06-05 | 8 | 3723 | 1403 | -103 | 1 | 0 | 1506 | 238.582 | 238.582 | 238.582 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -117.849 | 120.7331 | -3550 | -400 | -3829.2669 | 95.73% | 64.1% | 95% | 0% | 1506 | -103
[5 empty] | 2019-06-05 | 9 | 3723.5 | 1403 | -102 | 1 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -116.7048 | 120.3109 | -3550 | -400 | -3829.6891 | 95.74% | 64.1% | 95% | 0% | 1505 | -102
[5 empty] | 2019-06-05 | 10 | 3724 | 1386 | -101 | 1 | 0 | 1487 | 208.8211 | 208.8211 | 208.8211 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -115.5606 | 93.2605 | -3550 | -400 | -3856.7395 | 96.42% | 64.1% | 95% | 0% | 1487 | -101
[5 empty] | 2019-06-05 | 11 | 3724.5 | 1417 | -102 | 1 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 1516.7354 | 780 | 200 | 2496.7354 | 62.42% | 95% | 0% | -116.7048 | 142.24 | -3550 | -400 | -3807.76 | 95.19% | 64.09% | 95% | 0% | 1519 | -102
[5 empty] | 2019-06-05 | 12 | 3725 | 1477 | -115 | 1 | 0 | 1592 | 373.2894 | 373.2894 | 373.2894 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -131.5789 | 241.7104 | -3550 | -400 | -3708.2896 | 92.71% | 64.09% | 95% | 0% | 1592 | -115
[5 empty] | 2019-06-05 | 13 | 3725.5 | 1634 | -141 | 1 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -161.3272 | 498.6068 | -3550 | -400 | -3451.3932 | 86.28% | 64.09% | 95% | 0% | 1775 | -141
[5 empty] | 2019-06-05 | 14 | 3726 | 1792 | -170 | 1 | 0 | 1962 | 952.8442 | 952.8442 | 952.8442 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -194.508 | 758.3362 | -3550 | -400 | -3191.6638 | 79.79% | 64.09% | 95% | 0% | 1962 | -170
[5 empty] | 2019-06-05 | 15 | 3726.5 | 1943 | -210 | 1 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -240.2746 | 1011.7452 | -3550 | -400 | -2938.2548 | 73.46% | 64.09% | 95% | 0% | 2153 | -210
[5 empty] | 2019-06-05 | 16 | 3727 | 1982 | -258 | 1 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -295.1945 | 1093.099 | -3550 | -400 | -2856.901 | 71.42% | 64.09% | 95% | 0% | 2240 | -258
[5 empty] | 2019-06-05 | 17 | 3727.5 | 1981 | -300 | 1 | 0 | 2281 | 1452.5144 | 1452.5144 | 1452.5144 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -343.2494 | 1109.265 | -3550 | -400 | -2840.735 | 71.02% | 64.09% | 95% | 0% | 2281 | -300
[5 empty] | 2019-06-05 | 18 | 3728 | 1932 | -338 | 1 | 0 | 2270 | 1435.2844 | 1435.2844 | 1435.2844 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -386.7277 | 1048.5567 | -3550 | -400 | -2901.4433 | 72.54% | 64.09% | 95% | 0% | 2270 | -338
[5 empty] | 2019-06-05 | 19 | 3728.5 | 1908 | -378 | 1 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -432.4943 | 1027.852 | -3550 | -400 | -2922.148 | 73.05% | 64.08% | 95% | 0% | 2286 | -378
[5 empty] | 2019-06-05 | 20 | 3729 | 1874 | -402 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -459.9542 | 984.7284 | -3550 | -400 | -2965.2716 | 74.13% | 64.08% | 95% | 0% | 2276 | -402
[5 empty] | 2019-06-05 | 21 | 3729.5 | 1804 | -429 | 1 | 0 | 2233 | 1377.3289 | 1377.3289 | 1377.3289 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -490.8467 | 886.4823 | -3550 | -400 | -3063.5177 | 76.59% | 64.08% | 95% | 0% | 2233 | -429
[5 empty] | 2019-06-05 | 22 | 3730 | 1760 | -467 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -534.3249 | 833.6058 | -3550 | -400 | -3116.3942 | 77.91% | 64.08% | 95% | 0% | 2227 | -467
[5 empty] | 2019-06-05 | 23 | 3730.5 | 1757 | -473 | 1 | 0 | 2230 | 1372.6298 | 1372.6298 | 1372.6298 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -541.1899 | 831.4399 | -3550 | -400 | -3118.5601 | 77.96% | 64.07% | 95% | 0% | 2230 | -473
[5 empty] | 2019-06-05 | 24 | 3731 | 1744 | -483 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -552.6316 | 815.2992 | -3550 | -400 | -3134.7008 | 78.37% | 64.07% | 95% | 0% | 2227 | -483
[5 empty] | 2019-06-05 | 25 | 3731.5 | 1752 | -490 | 1 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -560.6407 | 830.7855 | -3550 | -400 | -3119.2145 | 77.98% | 64.07% | 95% | 0% | 2242 | -490
[5 empty] | 2019-06-05 | 26 | 3732 | 1742 | -493 | 1 | 0 | 2235 | 1380.4617 | 1380.4617 | 1380.4617 | 1515.169 | 780 | 200 | 2495.169 | 62.38% | 95% | 0% | -564.0732 | 816.3884 | -3550 | -400 | -3133.6116 | 78.34% | 64.07% | 95% | 0% | 2235 | -493
[5 empty] | 2019-06-05 | 27 | 3732.5 | 1731 | -483 | 1 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 1513.6026 | 780 | 200 | 2493.6026 | 62.34% | 95% | 0% | -552.6316 | 794.9364 | -3550 | -400 | -3155.0636 | 78.88% | 64.07% | 95% | 0% | 2214 | -483
[5 empty] | 2019-06-05 | 28 | 3733 | 1726 | -473 | 1 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 1513.6026 | 780 | 200 | 2493.6026 | 62.34% | 95% | 0% | -541.1899 | 782.8826 | -3550 | -400 | -3167.1174 | 79.18% | 64.07% | 95% | 0% | 2199 | -473
[5 empty] | 2019-06-05 | 29 | 3733.5 | 1763 | -455 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 1513.6026 | 780 | 200 | 2493.6026 | 62.34% | 95% | 0% | -520.595 | 833.2385 | -3550 | -400 | -3116.7615 | 77.92% | 64.07% | 95% | 0% | 2218 | -455
[5 empty] | 2019-06-05 | 30 | 3734 | 1789 | -431 | 1 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 1513.6026 | 780 | 200 | 2493.6026 | 62.34% | 95% | 0% | -493.135 | 863.8312 | -3550 | -400 | -3086.1688 | 77.15% | 64.07% | 95% | 0% | 2220 | -431
[5 empty] | 2019-06-05 | 31 | 3734.5 | 1839 | -398 | 1 | 0 | 2237 | 1383.5944 | 1383.5944 | 1383.5944 | 1513.6026 | 780 | 200 | 2493.6026 | 62.34% | 95% | 0% | -455.3776 | 928.2168 | -3550 | -400 | -3021.7832 | 75.54% | 64.06% | 95% | 0% | 2237 | -398
[5 empty] | 2019-06-05 | 32 | 3735 | 1911 | -363 | 1 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 1513.6026 | 780 | 200 | 2493.6026 | 62.34% | 95% | 0% | -415.3318 | 1026.2181 | -3550 | -400 | -2923.7819 | 73.09% | 64.06% | 95% | 0% | 2274 | -363
[5 empty] | 2019-06-05 | 33 | 3735.5 | 2015 | -336 | 1 | 0 | 2351 | 1562.1599 | 1562.1599 | 1562.1599 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -384.4394 | 1177.7206 | -3550 | -400 | -2772.2794 | 69.31% | 64.04% | 95% | 0% | 2351 | -336
[5 empty] | 2019-06-05 | 34 | 3736 | 2117 | -299 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -342.1053 | 1321.8684 | -3550 | -400 | -2628.1316 | 65.7% | 64.04% | 95% | 0% | 2416 | -299
[5 empty] | 2019-06-05 | 35 | 3736.5 | 2214 | -266 | 1 | 0 | 2480 | 1764.2209 | 1764.2209 | 1764.2209 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -304.3478 | 1459.8731 | -3550 | -400 | -2490.1269 | 62.25% | 64.04% | 95% | 0% | 2480 | -266
[5 empty] | 2019-06-05 | 36 | 3737 | 2258 | -241 | 1 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -275.7437 | 1518.2382 | -3550 | -400 | -2431.7618 | 60.79% | 64.04% | 95% | 0% | 2499 | -241
[5 empty] | 2019-06-05 | 37 | 3737.5 | 2282 | -213 | 1 | 0 | 2495 | 1787.7164 | 1787.7164 | 1787.7164 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -243.7071 | 1544.0093 | -3550 | -400 | -2405.9907 | 60.15% | 64.04% | 95% | 0% | 2495 | -213
[5 empty] | 2019-06-05 | 38 | 3738 | 2322 | -182 | 1 | 0 | 2504 | 1801.8137 | 1801.8137 | 1801.8137 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -208.238 | 1593.5757 | -3550 | -400 | -2356.4243 | 58.91% | 64.03% | 95% | 0% | 2504 | -182
[5 empty] | 2019-06-05 | 39 | 3738.5 | 2356 | -148 | 1 | 0 | 2504 | 1801.8137 | 1801.8137 | 1801.8137 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -169.3364 | 1632.4773 | -3550 | -400 | -2317.5227 | 57.94% | 64.02% | 95% | 0% | 2504 | -148
[5 empty] | 2019-06-05 | 40 | 3739 | 2384 | -115 | 1 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -131.5789 | 1662.4029 | -3550 | -400 | -2287.5971 | 57.19% | 64.02% | 95% | 0% | 2499 | -115
[5 empty] | 2019-06-05 | 41 | 3739.5 | 2384 | -88 | 1 | 0 | 2472 | 1751.69 | 1751.69 | 1751.69 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -100.6865 | 1651.0035 | -3550 | -400 | -2298.9965 | 57.47% | 64.02% | 95% | 0% | 2472 | -88
[5 empty] | 2019-06-05 | 42 | 3740 | 2361 | -66 | 1 | 0 | 2427 | 1681.2036 | 1681.2036 | 1681.2036 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -75.5149 | 1605.6888 | -3550 | -400 | -2344.3112 | 58.61% | 64.02% | 95% | 0% | 2427 | -66
[5 empty] | 2019-06-05 | 43 | 3740.5 | 2342 | -55 | 1 | 0 | 2397 | 1634.2127 | 1634.2127 | 1634.2127 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -62.9291 | 1571.2836 | -3550 | -400 | -2378.7164 | 59.47% | 64.02% | 95% | 0% | 2397 | -55
[5 empty] | 2019-06-05 | 44 | 3741 | 2283 | -52 | 1 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -59.4966 | 1477.6015 | -3550 | -400 | -2472.3985 | 61.81% | 64.01% | 95% | 0% | 2335 | -52
[5 empty] | 2019-06-05 | 45 | 3741.5 | 2197 | -51 | 0 | 0 | 2248 | 1400.8244 | 1400.8244 | 1400.8244 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -58.3524 | 1342.472 | -2750 | -200 | -1607.528 | 40.19% | 64.01% | 95% | 0% | 2248 | -51
[5 empty] | 2019-06-05 | 46 | 3742 | 2070 | -50 | 0 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -57.2082 | 1143.1215 | -2750 | -200 | -1806.8785 | 45.17% | 64.01% | 95% | 0% | 2120 | -50
[5 empty] | 2019-06-05 | 47 | 3742.5 | 1924 | -49 | 0 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -56.0641 | 914.0101 | -2750 | -200 | -2035.9899 | 50.9% | 64.01% | 95% | 0% | 1973 | -49
[5 empty] | 2019-06-05 | 48 | 3743 | 1800 | -48 | 0 | 0 | 1848 | 774.2786 | 774.2786 | 774.2786 | 1512.0363 | 780 | 200 | 2492.0363 | 62.3% | 95% | 0% | -54.9199 | 719.3587 | -2750 | -200 | -2230.6413 | 55.77% | 64.01% | 95% | 0% | 1848 | -48
[5 empty] | 2019-06-06 | 1 | 3743.5 | 1706 | -45 | 0 | 0 | 1751 | 622.3413 | 622.3413 | 622.3413 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -51.4874 | 570.8539 | -2750 | -200 | -2379.1461 | 59.48% | 64.01% | 95% | 0% | 1751 | -45
[5 empty] | 2019-06-06 | 2 | 3744 | 1659 | -43 | 0 | 0 | 1702 | 545.5894 | 545.5894 | 545.5894 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -49.1991 | 496.3904 | -2750 | -200 | -2453.6096 | 61.34% | 64.01% | 95% | 0% | 1702 | -43
[5 empty] | 2019-06-06 | 3 | 3744.5 | 1626 | -43 | 0 | 0 | 1669 | 493.8994 | 493.8994 | 493.8994 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -49.1991 | 444.7003 | -2750 | -200 | -2505.2997 | 62.63% | 64% | 95% | 0% | 1669 | -43
[5 empty] | 2019-06-06 | 4 | 3745 | 1612 | -44 | 0 | 0 | 1656 | 473.5367 | 473.5367 | 473.5367 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -50.3432 | 423.1934 | -2750 | -200 | -2526.8066 | 63.17% | 64% | 95% | 0% | 1656 | -44
[5 empty] | 2019-06-06 | 5 | 3745.5 | 1589 | -44 | 0 | 0 | 1633 | 437.5103 | 437.5103 | 437.5103 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -50.3432 | 387.1671 | -2750 | -200 | -2562.8329 | 64.07% | 64% | 95% | 0% | 1633 | -44
[5 empty] | 2019-06-06 | 6 | 3746 | 1560 | -45 | 0 | 0 | 1605 | 393.6521 | 393.6521 | 393.6521 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -51.4874 | 342.1647 | -2750 | -200 | -2607.8353 | 65.2% | 64% | 95% | 0% | 1605 | -45
[5 empty] | 2019-06-06 | 7 | 3746.5 | 1542 | -45 | 0 | 0 | 1587 | 365.4575 | 365.4575 | 365.4575 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -51.4874 | 313.9701 | -2750 | -200 | -2636.0299 | 65.9% | 64% | 95% | 0% | 1587 | -45
[5 empty] | 2019-06-06 | 8 | 3747 | 1532 | -45 | 0 | 0 | 1577 | 349.7939 | 349.7939 | 349.7939 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -51.4874 | 298.3065 | -2750 | -200 | -2651.6935 | 66.29% | 63.99% | 95% | 0% | 1577 | -45
[5 empty] | 2019-06-06 | 9 | 3747.5 | 1524 | -46 | 0 | 0 | 1570 | 338.8293 | 338.8293 | 338.8293 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -52.6316 | 286.1978 | -2750 | -200 | -2663.8022 | 66.6% | 63.99% | 95% | 0% | 1570 | -46
[5 empty] | 2019-06-06 | 10 | 3748 | 1505 | -48 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -54.9199 | 257.2812 | -2750 | -200 | -2692.7188 | 67.32% | 63.99% | 95% | 0% | 1553 | -48
[5 empty] | 2019-06-06 | 11 | 3748.5 | 1533 | -52 | 0 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -59.4966 | 302.8282 | -2750 | -200 | -2647.1718 | 66.18% | 63.99% | 95% | 0% | 1585 | -52
[5 empty] | 2019-06-06 | 12 | 3749 | 1584 | -78 | 0 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -89.2449 | 393.69 | -2750 | -200 | -2556.31 | 63.91% | 63.98% | 95% | 0% | 1662 | -78
[5 empty] | 2019-06-06 | 13 | 3749.5 | 1739 | -113 | 0 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -129.2906 | 651.2535 | -2750 | -200 | -2298.7465 | 57.47% | 63.98% | 95% | 0% | 1852 | -113
[5 empty] | 2019-06-06 | 14 | 3750 | 1861 | -157 | 1 | 0 | 2018 | 1040.5606 | 1040.5606 | 1040.5606 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -179.6339 | 860.9267 | -3550 | -400 | -3089.0733 | 77.23% | 63.98% | 95% | 0% | 2018 | -157
[5 empty] | 2019-06-06 | 15 | 3750.5 | 1959 | -217 | 1 | 0 | 2176 | 1288.0462 | 1288.0462 | 1288.0462 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -248.2838 | 1039.7624 | -3550 | -400 | -2910.2376 | 72.76% | 63.98% | 95% | 0% | 2176 | -217
[5 empty] | 2019-06-06 | 16 | 3751 | 1965 | -275 | 1 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -314.6453 | 1073.6482 | -3550 | -400 | -2876.3518 | 71.91% | 63.97% | 95% | 0% | 2240 | -275
[5 empty] | 2019-06-06 | 17 | 3751.5 | 1912 | -338 | 1 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -386.7277 | 1017.2294 | -3550 | -400 | -2932.7706 | 73.32% | 63.97% | 95% | 0% | 2250 | -338
[5 empty] | 2019-06-06 | 18 | 3752 | 1815 | -404 | 1 | 0 | 2219 | 1355.3998 | 1355.3998 | 1355.3998 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -462.2426 | 893.1573 | -3550 | -400 | -3056.8427 | 76.42% | 63.97% | 95% | 0% | 2219 | -404
[5 empty] | 2019-06-06 | 19 | 3752.5 | 1768 | -457 | 1 | 0 | 2225 | 1364.798 | 1364.798 | 1364.798 | 1510.4699 | 780 | 200 | 2490.4699 | 62.26% | 95% | 0% | -522.8833 | 841.9147 | -3550 | -400 | -3108.0853 | 77.7% | 63.97% | 95% | 0% | 2225 | -457
[5 empty] | 2019-06-06 | 20 | 3753 | 1697 | -499 | 1 | 0 | 2196 | 1319.3735 | 1319.3735 | 1319.3735 | 1508.9035 | 780 | 200 | 2488.9035 | 62.22% | 95% | 0% | -570.9382 | 748.4352 | -3550 | -400 | -3201.5648 | 80.04% | 63.97% | 95% | 0% | 2196 | -499
[5 empty] | 2019-06-06 | 21 | 3753.5 | 1635 | -520 | 1 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 1508.9035 | 780 | 200 | 2488.9035 | 62.22% | 95% | 0% | -594.9657 | 660.1868 | -3550 | -400 | -3289.8132 | 82.25% | 63.97% | 95% | 0% | 2155 | -520
[5 empty] | 2019-06-06 | 22 | 3754 | 1615 | -543 | 1 | 0 | 2158 | 1259.8516 | 1259.8516 | 1259.8516 | 1508.9035 | 780 | 200 | 2488.9035 | 62.22% | 95% | 0% | -621.2815 | 638.5701 | -3550 | -400 | -3311.4299 | 82.79% | 63.97% | 95% | 0% | 2158 | -543
[5 empty] | 2019-06-06 | 23 | 3754.5 | 1580 | -579 | 1 | 0 | 2159 | 1261.418 | 1261.418 | 1261.418 | 1508.9035 | 780 | 200 | 2488.9035 | 62.22% | 95% | 0% | -662.4714 | 598.9466 | -3550 | -400 | -3351.0534 | 83.78% | 63.96% | 95% | 0% | 2159 | -579
[5 empty] | 2019-06-06 | 24 | 3755 | 1495 | -649 | 1 | 0 | 2144 | 1237.9225 | 1237.9225 | 1237.9225 | 1508.9035 | 780 | 200 | 2488.9035 | 62.22% | 95% | 0% | -742.5629 | 495.3596 | -3550 | -400 | -3454.6404 | 86.37% | 63.96% | 95% | 0% | 2144 | -649
[5 empty] | 2019-06-06 | 25 | 3755.5 | 1532 | -610 | 1 | 0 | 2142 | 1234.7898 | 1234.7898 | 1234.7898 | 1508.9035 | 780 | 200 | 2488.9035 | 62.22% | 95% | 0% | -697.9405 | 536.8493 | -3550 | -400 | -3413.1507 | 85.33% | 63.96% | 95% | 0% | 2142 | -610
[5 empty] | 2019-06-06 | 26 | 3756 | 1482 | -648 | 1 | 0 | 2130 | 1215.9934 | 1215.9934 | 1215.9934 | 1508.9035 | 780 | 200 | 2488.9035 | 62.22% | 95% | 0% | -741.4188 | 474.5746 | -3550 | -400 | -3475.4254 | 86.89% | 63.95% | 95% | 0% | 2130 | -648
[5 empty] | 2019-06-06 | 27 | 3756.5 | 1431 | -657 | 1 | 0 | 2088 | 1150.2061 | 1150.2061 | 1150.2061 | 1508.9035 | 780 | 200 | 2488.9035 | 62.22% | 95% | 0% | -751.7162 | 398.4899 | -3550 | -400 | -3551.5101 | 88.79% | 63.95% | 95% | 0% | 2088 | -657
[5 empty] | 2019-06-06 | 28 | 3757 | 1444 | -598 | 1 | 0 | 2042 | 1078.1533 | 1078.1533 | 1078.1533 | 1508.9035 | 780 | 200 | 2488.9035 | 62.22% | 95% | 0% | -684.2105 | 393.9428 | -3550 | -400 | -3556.0572 | 88.9% | 63.94% | 95% | 0% | 2042 | -598
[5 empty] | 2019-06-06 | 29 | 3757.5 | 1397 | -635 | 1 | 0 | 2032 | 1062.4897 | 1062.4897 | 1062.4897 | 1508.9035 | 780 | 200 | 2488.9035 | 62.22% | 95% | 0% | -726.5446 | 335.9451 | -3550 | -400 | -3614.0549 | 90.35% | 63.94% | 95% | 0% | 2032 | -635
[5 empty] | 2019-06-06 | 30 | 3758 | 1422 | -599 | 1 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 1508.9035 | 780 | 200 | 2488.9035 | 62.22% | 95% | 0% | -685.3547 | 359.905 | -3550 | -400 | -3590.095 | 89.75% | 63.93% | 95% | 0% | 2021 | -599
[5 empty] | 2019-06-06 | 31 | 3758.5 | 1423 | -592 | 1 | 0 | 2015 | 1035.8615 | 1035.8615 | 1035.8615 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -677.3455 | 358.516 | -3550 | -400 | -3591.484 | 89.79% | 63.93% | 95% | 0% | 2015 | -592
[5 empty] | 2019-06-06 | 32 | 3759 | 1473 | -573 | 1 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -655.6064 | 428.8124 | -3550 | -400 | -3521.1876 | 88.03% | 63.93% | 95% | 0% | 2046 | -573
[5 empty] | 2019-06-06 | 33 | 3759.5 | 1582 | -518 | 1 | 0 | 2100 | 1169.0025 | 1169.0025 | 1169.0025 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -592.6773 | 576.3251 | -3550 | -400 | -3373.6749 | 84.34% | 63.93% | 95% | 0% | 2100 | -518
[5 empty] | 2019-06-06 | 34 | 3760 | 1675 | -494 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -565.2174 | 711.8642 | -3550 | -400 | -3238.1358 | 80.95% | 63.93% | 95% | 0% | 2169 | -494
[5 empty] | 2019-06-06 | 35 | 3760.5 | 1789 | -444 | 1 | 0 | 2233 | 1377.3289 | 1377.3289 | 1377.3289 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -508.0092 | 869.3198 | -3550 | -400 | -3080.6802 | 77.02% | 63.93% | 95% | 0% | 2233 | -444
[5 empty] | 2019-06-06 | 36 | 3761 | 1878 | -386 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -441.6476 | 984.2386 | -3550 | -400 | -2965.7614 | 74.14% | 63.92% | 95% | 0% | 2264 | -386
[5 empty] | 2019-06-06 | 37 | 3761.5 | 1968 | -323 | 1 | 0 | 2291 | 1468.1781 | 1468.1781 | 1468.1781 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -369.5652 | 1098.6129 | -3550 | -400 | -2851.3871 | 71.28% | 63.92% | 95% | 0% | 2291 | -323
[5 empty] | 2019-06-06 | 38 | 3762 | 2071 | -259 | 1 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -296.3387 | 1232.9276 | -3550 | -400 | -2717.0724 | 67.93% | 63.91% | 95% | 0% | 2330 | -259
[5 empty] | 2019-06-06 | 39 | 3762.5 | 2154 | -188 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -215.103 | 1332.9597 | -3550 | -400 | -2617.0403 | 65.43% | 63.91% | 95% | 0% | 2342 | -188
[5 empty] | 2019-06-06 | 40 | 3763 | 2207 | -143 | 1 | 0 | 2350 | 1560.5936 | 1560.5936 | 1560.5936 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -163.6156 | 1396.978 | -3550 | -400 | -2553.022 | 63.83% | 63.91% | 95% | 0% | 2350 | -143
[5 empty] | 2019-06-06 | 41 | 3763.5 | 2217 | -104 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -118.9931 | 1396.1759 | -3550 | -400 | -2553.8241 | 63.85% | 63.91% | 95% | 0% | 2321 | -104
[5 empty] | 2019-06-06 | 42 | 3764 | 2214 | -72 | 1 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -82.3799 | 1377.9664 | -3550 | -400 | -2572.0336 | 64.3% | 63.91% | 95% | 0% | 2286 | -72
[5 empty] | 2019-06-06 | 43 | 3764.5 | 2214 | -61 | 1 | 0 | 2275 | 1443.1162 | 1443.1162 | 1443.1162 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -69.7941 | 1373.3222 | -3550 | -400 | -2576.6778 | 64.42% | 63.91% | 95% | 0% | 2275 | -61
[5 empty] | 2019-06-06 | 44 | 3765 | 2200 | -59 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -67.5057 | 1350.5487 | -3550 | -400 | -2599.4513 | 64.99% | 63.9% | 95% | 0% | 2259 | -59
[5 empty] | 2019-06-06 | 45 | 3765.5 | 2130 | -60 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1507.3372 | 780 | 200 | 2487.3372 | 62.18% | 95% | 0% | -68.6499 | 1241.3254 | -3550 | -400 | -2708.6746 | 67.72% | 63.9% | 95% | 0% | 2190 | -60
[5 empty] | 2019-06-06 | 46 | 3766 | 2009 | -62 | 0 | 0 | 2071 | 1123.5779 | 1123.5779 | 1123.5779 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -70.9382 | 1052.6397 | -2750 | -200 | -1897.3603 | 47.43% | 63.9% | 95% | 0% | 2071 | -62
[5 empty] | 2019-06-06 | 47 | 3766.5 | 1867 | -63 | 0 | 0 | 1930 | 902.7205 | 902.7205 | 902.7205 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -72.0824 | 830.6381 | -2750 | -200 | -2119.3619 | 52.98% | 63.89% | 95% | 0% | 1930 | -63
[5 empty] | 2019-06-06 | 48 | 3767 | 1743 | -64 | 0 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -73.2265 | 636.8312 | -2750 | -200 | -2313.1688 | 57.83% | 63.89% | 95% | 0% | 1807 | -64
[5 empty] | 2019-06-07 | 1 | 3767.5 | 1648 | -64 | 0 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -73.2265 | 488.0265 | -2750 | -200 | -2461.9735 | 61.55% | 63.89% | 95% | 0% | 1712 | -64
[5 empty] | 2019-06-07 | 2 | 3768 | 1584 | -63 | 0 | 0 | 1647 | 459.4394 | 459.4394 | 459.4394 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -72.0824 | 387.357 | -2750 | -200 | -2562.643 | 64.07% | 63.88% | 95% | 0% | 1647 | -63
[5 empty] | 2019-06-07 | 3 | 3768.5 | 1553 | -64 | 0 | 0 | 1617 | 412.4485 | 412.4485 | 412.4485 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -73.2265 | 339.2219 | -2750 | -200 | -2610.7781 | 65.27% | 63.88% | 95% | 0% | 1617 | -64
[5 empty] | 2019-06-07 | 4 | 3769 | 1540 | -64 | 0 | 0 | 1604 | 392.0857 | 392.0857 | 392.0857 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -73.2265 | 318.8592 | -2750 | -200 | -2631.1408 | 65.78% | 63.88% | 95% | 0% | 1604 | -64
[5 empty] | 2019-06-07 | 5 | 3769.5 | 1518 | -65 | 0 | 0 | 1583 | 359.1921 | 359.1921 | 359.1921 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -74.3707 | 284.8214 | -2750 | -200 | -2665.1786 | 66.63% | 63.88% | 95% | 0% | 1583 | -65
[5 empty] | 2019-06-07 | 6 | 3770 | 1492 | -65 | 0 | 0 | 1557 | 318.4666 | 318.4666 | 318.4666 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -74.3707 | 244.0959 | -2750 | -200 | -2705.9041 | 67.65% | 63.87% | 95% | 0% | 1557 | -65
[5 empty] | 2019-06-07 | 7 | 3770.5 | 1470 | -67 | 0 | 0 | 1537 | 287.1393 | 287.1393 | 287.1393 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -76.659 | 210.4803 | -2750 | -200 | -2739.5197 | 68.49% | 63.87% | 95% | 0% | 1537 | -67
[5 empty] | 2019-06-07 | 8 | 3771 | 1472 | -68 | 0 | 0 | 1540 | 291.8384 | 291.8384 | 291.8384 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -77.8032 | 214.0352 | -2750 | -200 | -2735.9648 | 68.4% | 63.87% | 95% | 0% | 1540 | -68
[5 empty] | 2019-06-07 | 9 | 3771.5 | 1465 | -71 | 0 | 0 | 1536 | 285.573 | 285.573 | 285.573 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -81.2357 | 204.3373 | -2750 | -200 | -2745.6627 | 68.64% | 63.87% | 95% | 0% | 1536 | -71
[5 empty] | 2019-06-07 | 10 | 3772 | 1445 | -74 | 0 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -84.6682 | 174.2766 | -2750 | -200 | -2775.7234 | 69.39% | 63.87% | 95% | 0% | 1519 | -74
[5 empty] | 2019-06-07 | 11 | 3772.5 | 1477 | -80 | 0 | 0 | 1557 | 318.4666 | 318.4666 | 318.4666 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -91.5332 | 226.9334 | -2750 | -200 | -2723.0666 | 68.08% | 63.87% | 95% | 0% | 1557 | -80
[5 empty] | 2019-06-07 | 12 | 3773 | 1528 | -96 | 0 | 0 | 1624 | 423.413 | 423.413 | 423.413 | 1505.7708 | 780 | 200 | 2485.7708 | 62.14% | 95% | 0% | -109.8398 | 313.5732 | -2750 | -200 | -2636.4268 | 65.91% | 63.86% | 95% | 0% | 1624 | -96
[5 empty] | 2019-06-07 | 13 | 3773.5 | 1674 | -121 | 1 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 1504.2045 | 780 | 200 | 2484.2045 | 62.11% | 95% | 0% | -138.4439 | 552.8174 | -3550 | -400 | -3397.1826 | 84.93% | 63.86% | 95% | 0% | 1795 | -121
[5 empty] | 2019-06-07 | 14 | 3774 | 1801 | -153 | 1 | 0 | 1954 | 940.3133 | 940.3133 | 940.3133 | 1504.2045 | 780 | 200 | 2484.2045 | 62.11% | 95% | 0% | -175.0572 | 765.2561 | -3550 | -400 | -3184.7439 | 79.62% | 63.86% | 95% | 0% | 1954 | -153
[5 empty] | 2019-06-07 | 15 | 3774.5 | 2002 | -179 | 1 | 0 | 2181 | 1295.878 | 1295.878 | 1295.878 | 1504.2045 | 780 | 200 | 2484.2045 | 62.11% | 95% | 0% | -204.8055 | 1091.0725 | -3550 | -400 | -2858.9275 | 71.47% | 63.85% | 95% | 0% | 2181 | -179
[5 empty] | 2019-06-07 | 16 | 3775 | 2079 | -210 | 1 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 1504.2045 | 780 | 200 | 2484.2045 | 62.11% | 95% | 0% | -240.2746 | 1224.7707 | -3550 | -400 | -2725.2293 | 68.13% | 63.85% | 95% | 0% | 2289 | -210
[5 empty] | 2019-06-07 | 17 | 3775.5 | 2132 | -235 | 1 | 0 | 2367 | 1587.2218 | 1587.2218 | 1587.2218 | 1504.2045 | 780 | 200 | 2484.2045 | 62.11% | 95% | 0% | -268.8787 | 1318.343 | -3550 | -400 | -2631.657 | 65.79% | 63.84% | 95% | 0% | 2367 | -235
[5 empty] | 2019-06-07 | 18 | 3776 | 2113 | -253 | 1 | 0 | 2366 | 1585.6554 | 1585.6554 | 1585.6554 | 1504.2045 | 780 | 200 | 2484.2045 | 62.11% | 95% | 0% | -289.4737 | 1296.1817 | -3550 | -400 | -2653.8183 | 66.35% | 63.84% | 95% | 0% | 2366 | -253
[5 empty] | 2019-06-07 | 19 | 3776.5 | 2113 | -274 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 1504.2045 | 780 | 200 | 2484.2045 | 62.11% | 95% | 0% | -313.5011 | 1305.0479 | -3550 | -400 | -2644.9521 | 66.12% | 63.84% | 95% | 0% | 2387 | -274
[5 empty] | 2019-06-07 | 20 | 3777 | 2134 | -272 | 1 | 0 | 2406 | 1648.31 | 1648.31 | 1648.31 | 1504.2045 | 780 | 200 | 2484.2045 | 62.11% | 95% | 0% | -311.2128 | 1337.0972 | -3550 | -400 | -2612.9028 | 65.32% | 63.84% | 95% | 0% | 2406 | -272
[5 empty] | 2019-06-07 | 21 | 3777.5 | 2130 | -284 | 1 | 0 | 2414 | 1660.8409 | 1660.8409 | 1660.8409 | 1504.2045 | 780 | 200 | 2484.2045 | 62.11% | 95% | 0% | -324.9428 | 1335.8981 | -3550 | -400 | -2614.1019 | 65.35% | 63.84% | 95% | 0% | 2414 | -284
[5 empty] | 2019-06-07 | 22 | 3778 | 2115 | -304 | 1 | 0 | 2419 | 1668.6727 | 1668.6727 | 1668.6727 | 1504.2045 | 780 | 200 | 2484.2045 | 62.11% | 95% | 0% | -347.8261 | 1320.8466 | -3550 | -400 | -2629.1534 | 65.73% | 63.83% | 95% | 0% | 2419 | -304
[5 empty] | 2019-06-07 | 23 | 3778.5 | 2108 | -309 | 1 | 0 | 2417 | 1665.54 | 1665.54 | 1665.54 | 1504.2045 | 780 | 200 | 2484.2045 | 62.11% | 95% | 0% | -353.5469 | 1311.9931 | -3550 | -400 | -2638.0069 | 65.95% | 63.83% | 95% | 0% | 2417 | -309
[5 empty] | 2019-06-07 | 24 | 3779 | 2127 | -319 | 1 | 0 | 2446 | 1710.9646 | 1710.9646 | 1710.9646 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -364.9886 | 1345.976 | -3550 | -400 | -2604.024 | 65.1% | 63.83% | 95% | 0% | 2446 | -319
[5 empty] | 2019-06-07 | 25 | 3779.5 | 2140 | -304 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -347.8261 | 1360.0057 | -3550 | -400 | -2589.9943 | 64.75% | 63.83% | 95% | 0% | 2444 | -304
[5 empty] | 2019-06-07 | 26 | 3780 | 2117 | -300 | 1 | 0 | 2417 | 1665.54 | 1665.54 | 1665.54 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -343.2494 | 1322.2906 | -3550 | -400 | -2627.7094 | 65.69% | 63.82% | 95% | 0% | 2417 | -300
[5 empty] | 2019-06-07 | 27 | 3780.5 | 2090 | -313 | 1 | 0 | 2403 | 1643.6109 | 1643.6109 | 1643.6109 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -358.1236 | 1285.4873 | -3550 | -400 | -2664.5127 | 66.61% | 63.82% | 95% | 0% | 2403 | -313
[5 empty] | 2019-06-07 | 28 | 3781 | 2042 | -313 | 1 | 0 | 2355 | 1568.4254 | 1568.4254 | 1568.4254 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -358.1236 | 1210.3018 | -3550 | -400 | -2739.6982 | 68.49% | 63.82% | 95% | 0% | 2355 | -313
[5 empty] | 2019-06-07 | 29 | 3781.5 | 2032 | -296 | 1 | 0 | 2328 | 1526.1336 | 1526.1336 | 1526.1336 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -338.6728 | 1187.4608 | -3550 | -400 | -2762.5392 | 69.06% | 63.82% | 95% | 0% | 2328 | -296
[5 empty] | 2019-06-07 | 30 | 3782 | 1965 | -327 | 1 | 0 | 2292 | 1469.7444 | 1469.7444 | 1469.7444 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -374.1419 | 1095.6026 | -3550 | -400 | -2854.3974 | 71.36% | 63.82% | 95% | 0% | 2292 | -327
[5 empty] | 2019-06-07 | 31 | 3782.5 | 1933 | -343 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -392.4485 | 1052.2341 | -3550 | -400 | -2897.7659 | 72.44% | 63.82% | 95% | 0% | 2276 | -343
[5 empty] | 2019-06-07 | 32 | 3783 | 1976 | -331 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -378.7185 | 1114.5214 | -3550 | -400 | -2835.4786 | 70.89% | 63.81% | 95% | 0% | 2307 | -331
[5 empty] | 2019-06-07 | 33 | 3783.5 | 2031 | -312 | 1 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -356.9794 | 1192.6496 | -3550 | -400 | -2757.3504 | 68.93% | 63.81% | 95% | 0% | 2343 | -312
[5 empty] | 2019-06-07 | 34 | 3784 | 2092 | -292 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -334.0961 | 1279.7538 | -3550 | -400 | -2670.2462 | 66.76% | 63.81% | 95% | 0% | 2384 | -292
[5 empty] | 2019-06-07 | 35 | 3784.5 | 2143 | -267 | 1 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -305.492 | 1349.0834 | -3550 | -400 | -2600.9166 | 65.02% | 63.81% | 95% | 0% | 2410 | -267
[5 empty] | 2019-06-07 | 36 | 3785 | 2186 | -242 | 1 | 0 | 2428 | 1682.77 | 1682.77 | 1682.77 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -276.8879 | 1405.8821 | -3550 | -400 | -2544.1179 | 63.6% | 63.81% | 95% | 0% | 2428 | -242
[5 empty] | 2019-06-07 | 37 | 3785.5 | 2234 | -201 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -229.9771 | 1463.7574 | -3550 | -400 | -2486.2426 | 62.16% | 63.8% | 95% | 0% | 2435 | -201
[5 empty] | 2019-06-07 | 38 | 3786 | 2270 | -172 | 1 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 1502.6381 | 780 | 200 | 2482.6381 | 62.07% | 95% | 0% | -196.7963 | 1507.9028 | -3550 | -400 | -2442.0972 | 61.05% | 63.8% | 95% | 0% | 2442 | -172
[5 empty] | 2019-06-07 | 39 | 3786.5 | 2268 | -143 | 1 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 1501.0717 | 780 | 200 | 2481.0717 | 62.03% | 95% | 0% | -163.6156 | 1492.5262 | -3550 | -400 | -2457.4738 | 61.44% | 63.8% | 95% | 0% | 2411 | -143
[5 empty] | 2019-06-07 | 40 | 3787 | 2249 | -120 | 1 | 0 | 2369 | 1590.3545 | 1590.3545 | 1590.3545 | 1501.0717 | 780 | 200 | 2481.0717 | 62.03% | 95% | 0% | -137.2998 | 1453.0547 | -3550 | -400 | -2496.9453 | 62.42% | 63.8% | 95% | 0% | 2369 | -120
[5 empty] | 2019-06-07 | 41 | 3787.5 | 2224 | -103 | 1 | 0 | 2327 | 1524.5672 | 1524.5672 | 1524.5672 | 1501.0717 | 780 | 200 | 2481.0717 | 62.03% | 95% | 0% | -117.849 | 1406.7182 | -3550 | -400 | -2543.2818 | 63.58% | 63.8% | 95% | 0% | 2327 | -103
[5 empty] | 2019-06-07 | 42 | 3788 | 2196 | -94 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 1501.0717 | 780 | 200 | 2481.0717 | 62.03% | 95% | 0% | -107.5515 | 1359.0602 | -3550 | -400 | -2590.9398 | 64.77% | 63.8% | 95% | 0% | 2290 | -94
[5 empty] | 2019-06-07 | 43 | 3788.5 | 2154 | -90 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1501.0717 | 780 | 200 | 2481.0717 | 62.03% | 95% | 0% | -102.9748 | 1291.5841 | -3550 | -400 | -2658.4159 | 66.46% | 63.8% | 95% | 0% | 2244 | -90
[5 empty] | 2019-06-07 | 44 | 3789 | 2125 | -88 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 1501.0717 | 780 | 200 | 2481.0717 | 62.03% | 95% | 0% | -100.6865 | 1245.3151 | -3550 | -400 | -2704.6849 | 67.62% | 63.79% | 95% | 0% | 2213 | -88
[5 empty] | 2019-06-07 | 45 | 3789.5 | 2036 | -88 | 1 | 0 | 2124 | 1206.5952 | 1206.5952 | 1206.5952 | 1501.0717 | 780 | 200 | 2481.0717 | 62.03% | 95% | 0% | -100.6865 | 1105.9087 | -3550 | -400 | -2844.0913 | 71.1% | 63.79% | 95% | 0% | 2124 | -88
[5 empty] | 2019-06-07 | 46 | 3790 | 1941 | -88 | 0 | 0 | 2029 | 1057.7906 | 1057.7906 | 1057.7906 | 1501.0717 | 780 | 200 | 2481.0717 | 62.03% | 95% | 0% | -100.6865 | 957.1041 | -2750 | -200 | -1992.8959 | 49.82% | 63.78% | 95% | 0% | 2029 | -88
[5 empty] | 2019-06-07 | 47 | 3790.5 | 1802 | -91 | 0 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 1501.0717 | 780 | 200 | 2481.0717 | 62.03% | 95% | 0% | -104.119 | 740.6461 | -2750 | -200 | -2209.3539 | 55.23% | 63.78% | 95% | 0% | 1893 | -91
[5 empty] | 2019-06-07 | 48 | 3791 | 1689 | -94 | 0 | 0 | 1783 | 672.465 | 672.465 | 672.465 | 1501.0717 | 780 | 200 | 2481.0717 | 62.03% | 95% | 0% | -107.5515 | 564.9135 | -2750 | -200 | -2385.0865 | 59.63% | 63.78% | 95% | 0% | 1783 | -94
[5 empty] | 2019-06-08 | 1 | 3791.5 | 1580 | -99 | 0 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 1501.0717 | 780 | 200 | 2481.0717 | 62.03% | 95% | 0% | -113.2723 | 396.2908 | -2750 | -200 | -2553.7092 | 63.84% | 63.78% | 95% | 0% | 1679 | -99
[5 empty] | 2019-06-08 | 2 | 3792 | 1494 | -104 | 0 | 0 | 1598 | 382.6876 | 382.6876 | 382.6876 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -118.9931 | 263.6944 | -2750 | -200 | -2686.3056 | 67.16% | 63.77% | 95% | 0% | 1598 | -104
[5 empty] | 2019-06-08 | 3 | 3792.5 | 1445 | -106 | 0 | 0 | 1551 | 309.0684 | 309.0684 | 309.0684 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -121.2815 | 187.787 | -2750 | -200 | -2762.213 | 69.06% | 63.77% | 95% | 0% | 1551 | -106
[5 empty] | 2019-06-08 | 4 | 3793 | 1432 | -108 | 0 | 0 | 1540 | 291.8384 | 291.8384 | 291.8384 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -123.5698 | 168.2686 | -2750 | -200 | -2781.7314 | 69.54% | 63.77% | 95% | 0% | 1540 | -108
[5 empty] | 2019-06-08 | 5 | 3793.5 | 1383 | -111 | 0 | 0 | 1494 | 219.7857 | 219.7857 | 219.7857 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -127.0023 | 92.7834 | -2750 | -200 | -2857.2166 | 71.43% | 63.76% | 95% | 0% | 1494 | -111
[5 empty] | 2019-06-08 | 6 | 3794 | 1347 | -113 | 0 | 0 | 1460 | 166.5293 | 166.5293 | 166.5293 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -129.2906 | 37.2386 | -2750 | -200 | -2912.7614 | 72.82% | 63.76% | 95% | 0% | 1460 | -113
[5 empty] | 2019-06-08 | 7 | 3794.5 | 1339 | -114 | 0 | 0 | 1453 | 155.5647 | 155.5647 | 155.5647 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -130.4348 | 25.1299 | -2750 | -200 | -2924.8701 | 73.12% | 63.76% | 95% | 0% | 1453 | -114
[5 empty] | 2019-06-08 | 8 | 3795 | 1320 | -116 | 0 | 0 | 1436 | 128.9365 | 128.9365 | 128.9365 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -132.7231 | -3.7866 | -2750 | -200 | -2953.7866 | 73.84% | 63.76% | 95% | 0% | 1436 | -116
[5 empty] | 2019-06-08 | 9 | 3795.5 | 1317 | -116 | 0 | 0 | 1433 | 124.2374 | 124.2374 | 124.2374 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -132.7231 | -8.4857 | -2750 | -200 | -2958.4857 | 73.96% | 63.76% | 95% | 0% | 1433 | -116
[5 empty] | 2019-06-08 | 10 | 3796 | 1286 | -117 | 0 | 0 | 1403 | 77.2465 | 77.2465 | 77.2465 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -133.8673 | -56.6208 | -2750 | -200 | -3006.6208 | 75.17% | 63.76% | 95% | 0% | 1403 | -117
[5 empty] | 2019-06-08 | 11 | 3796.5 | 1287 | -121 | 0 | 0 | 1408 | 85.0783 | 85.0783 | 85.0783 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -138.4439 | -53.3656 | -2750 | -200 | -3003.3656 | 75.08% | 63.75% | 95% | 0% | 1408 | -121
[5 empty] | 2019-06-08 | 12 | 3797 | 1288 | -129 | 0 | 0 | 1417 | 99.1756 | 99.1756 | 99.1756 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -147.5973 | -48.4217 | -2750 | -200 | -2998.4217 | 74.96% | 63.75% | 95% | 0% | 1417 | -129
[5 empty] | 2019-06-08 | 13 | 3797.5 | 1356 | -141 | 1 | 0 | 1497 | 224.4847 | 224.4847 | 224.4847 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -161.3272 | 63.1575 | -3550 | -400 | -3886.8425 | 97.17% | 63.75% | 95% | 0% | 1497 | -141
[5 empty] | 2019-06-08 | 14 | 3798 | 1398 | -159 | 1 | 0 | 1557 | 318.4666 | 318.4666 | 318.4666 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -181.9222 | 136.5444 | -3550 | -400 | -3813.4556 | 95.34% | 63.75% | 95% | 0% | 1557 | -159
[5 empty] | 2019-06-08 | 15 | 3798.5 | 1488 | -179 | 1 | 0 | 1667 | 490.7667 | 490.7667 | 490.7667 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -204.8055 | 285.9612 | -3550 | -400 | -3664.0388 | 91.6% | 63.74% | 95% | 0% | 1667 | -179
[5 empty] | 2019-06-08 | 16 | 3799 | 1543 | -195 | 1 | 0 | 1738 | 601.9786 | 601.9786 | 601.9786 | 1499.5054 | 780 | 200 | 2479.5054 | 61.99% | 95% | 0% | -223.1121 | 378.8664 | -3550 | -400 | -3571.1336 | 89.28% | 63.74% | 95% | 0% | 1738 | -195
[5 empty] | 2019-06-08 | 17 | 3799.5 | 1616 | -230 | 1 | 0 | 1846 | 771.1459 | 771.1459 | 771.1459 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -263.1579 | 507.988 | -3550 | -400 | -3442.012 | 86.05% | 63.74% | 95% | 0% | 1846 | -230
[5 empty] | 2019-06-08 | 18 | 3800 | 1625 | -269 | 1 | 0 | 1894 | 846.3314 | 846.3314 | 846.3314 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -307.7803 | 538.5511 | -3550 | -400 | -3411.4489 | 85.29% | 63.73% | 95% | 0% | 1894 | -269
[5 empty] | 2019-06-08 | 19 | 3800.5 | 1633 | -301 | 1 | 0 | 1934 | 908.986 | 908.986 | 908.986 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -344.3936 | 564.5924 | -3550 | -400 | -3385.4076 | 84.64% | 63.73% | 95% | 0% | 1934 | -301
[5 empty] | 2019-06-08 | 20 | 3801 | 1618 | -330 | 1 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -377.5744 | 553.3407 | -3550 | -400 | -3396.6593 | 84.92% | 63.73% | 95% | 0% | 1948 | -330
[5 empty] | 2019-06-08 | 21 | 3801.5 | 1601 | -358 | 1 | 0 | 1959 | 948.1451 | 948.1451 | 948.1451 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -409.611 | 538.5341 | -3550 | -400 | -3411.4659 | 85.29% | 63.73% | 95% | 0% | 1959 | -358
[5 empty] | 2019-06-08 | 22 | 3802 | 1535 | -399 | 1 | 0 | 1934 | 908.986 | 908.986 | 908.986 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -456.5217 | 452.4642 | -3550 | -400 | -3497.5358 | 87.44% | 63.73% | 95% | 0% | 1934 | -399
[5 empty] | 2019-06-08 | 23 | 3802.5 | 1485 | -436 | 1 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -498.8558 | 389.7674 | -3550 | -400 | -3560.2326 | 89.01% | 63.72% | 95% | 0% | 1921 | -436
[5 empty] | 2019-06-08 | 24 | 3803 | 1424 | -488 | 1 | 0 | 1912 | 874.526 | 874.526 | 874.526 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -558.3524 | 316.1736 | -3550 | -400 | -3633.8264 | 90.85% | 63.72% | 95% | 0% | 1912 | -488
[5 empty] | 2019-06-08 | 25 | 3803.5 | 1396 | -497 | 1 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -568.6499 | 276.1152 | -3550 | -400 | -3673.8848 | 91.85% | 63.71% | 95% | 0% | 1893 | -497
[5 empty] | 2019-06-08 | 26 | 3804 | 1343 | -521 | 1 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -596.1098 | 203.2306 | -3550 | -400 | -3746.7694 | 93.67% | 63.71% | 95% | 0% | 1864 | -521
[5 empty] | 2019-06-08 | 27 | 3804.5 | 1296 | -534 | 1 | 0 | 1830 | 746.0841 | 746.0841 | 746.0841 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -610.984 | 135.1001 | -3550 | -400 | -3814.8999 | 95.37% | 63.71% | 95% | 0% | 1830 | -534
[5 empty] | 2019-06-08 | 28 | 3805 | 1251 | -546 | 1 | 0 | 1797 | 694.3941 | 694.3941 | 694.3941 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -624.714 | 69.6801 | -3550 | -400 | -3880.3199 | 97.01% | 63.71% | 95% | 0% | 1797 | -546
[5 empty] | 2019-06-08 | 29 | 3805.5 | 1218 | -550 | 1 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -629.2906 | 19.6789 | -3550 | -400 | -3930.3211 | 98.26% | 63.7% | 95% | 0% | 1768 | -550
[5 empty] | 2019-06-08 | 30 | 3806 | 1202 | -542 | 1 | 0 | 1744 | 611.3768 | 611.3768 | 611.3768 | 1497.939 | 780 | 200 | 2477.939 | 61.95% | 95% | 0% | -620.1373 | -8.7605 | -3550 | -400 | -3958.7605 | 98.97% | 63.7% | 95% | 0% | 1744 | -542
[5 empty] | 2019-06-08 | 31 | 3806.5 | 1232 | -514 | 1 | 0 | 1746 | 614.5095 | 614.5095 | 614.5095 | 1496.3726 | 780 | 200 | 2476.3726 | 61.91% | 95% | 0% | -588.1007 | 26.4088 | -3550 | -400 | -3923.5912 | 98.09% | 63.7% | 95% | 0% | 1746 | -514
[5 empty] | 2019-06-08 | 32 | 3807 | 1280 | -484 | 1 | 0 | 1764 | 642.704 | 642.704 | 642.704 | 1496.3726 | 780 | 200 | 2476.3726 | 61.91% | 95% | 0% | -553.7757 | 88.9283 | -3550 | -400 | -3861.0717 | 96.53% | 63.69% | 95% | 0% | 1764 | -484
[5 empty] | 2019-06-08 | 33 | 3807.5 | 1361 | -451 | 1 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 1496.3726 | 780 | 200 | 2476.3726 | 61.91% | 95% | 0% | -516.0183 | 201.8712 | -3550 | -400 | -3748.1288 | 93.7% | 63.69% | 95% | 0% | 1812 | -451
[5 empty] | 2019-06-08 | 34 | 3808 | 1432 | -442 | 1 | 0 | 1874 | 815.0041 | 815.0041 | 815.0041 | 1496.3726 | 780 | 200 | 2476.3726 | 61.91% | 95% | 0% | -505.7208 | 309.2833 | -3550 | -400 | -3640.7167 | 91.02% | 63.69% | 95% | 0% | 1874 | -442
[5 empty] | 2019-06-08 | 35 | 3808.5 | 1540 | -402 | 1 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 1496.3726 | 780 | 200 | 2476.3726 | 61.91% | 95% | 0% | -459.9542 | 461.5627 | -3550 | -400 | -3488.4373 | 87.21% | 63.69% | 95% | 0% | 1942 | -402
[5 empty] | 2019-06-08 | 36 | 3809 | 1637 | -352 | 1 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 1496.3726 | 780 | 200 | 2476.3726 | 61.91% | 95% | 0% | -402.746 | 592.39 | -3550 | -400 | -3357.61 | 83.94% | 63.68% | 95% | 0% | 1989 | -352
[5 empty] | 2019-06-08 | 37 | 3809.5 | 1725 | -295 | 1 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 1496.3726 | 780 | 200 | 2476.3726 | 61.91% | 95% | 0% | -337.5286 | 706.1647 | -3550 | -400 | -3243.8353 | 81.1% | 63.68% | 95% | 0% | 2020 | -295
[5 empty] | 2019-06-08 | 38 | 3810 | 1805 | -247 | 1 | 0 | 2052 | 1093.817 | 1093.817 | 1093.817 | 1496.3726 | 780 | 200 | 2476.3726 | 61.91% | 95% | 0% | -282.6087 | 811.2083 | -3550 | -400 | -3138.7917 | 78.47% | 63.67% | 95% | 0% | 2052 | -247
[5 empty] | 2019-06-08 | 39 | 3810.5 | 1852 | -206 | 1 | 0 | 2058 | 1103.2152 | 1103.2152 | 1103.2152 | 1496.3726 | 780 | 200 | 2476.3726 | 61.91% | 95% | 0% | -235.6979 | 867.5172 | -3550 | -400 | -3082.4828 | 77.06% | 63.67% | 95% | 0% | 2058 | -206
[5 empty] | 2019-06-08 | 40 | 3811 | 1894 | -169 | 1 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 1496.3726 | 780 | 200 | 2476.3726 | 61.91% | 95% | 0% | -193.3638 | 917.6831 | -3550 | -400 | -3032.3169 | 75.81% | 63.67% | 95% | 0% | 2063 | -169
[5 empty] | 2019-06-08 | 41 | 3811.5 | 1912 | -134 | 1 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1496.3726 | 780 | 200 | 2476.3726 | 61.91% | 95% | 0% | -153.3181 | 931.1007 | -3550 | -400 | -3018.8993 | 75.47% | 63.67% | 95% | 0% | 2046 | -134
[5 empty] | 2019-06-08 | 42 | 3812 | 1919 | -109 | 1 | 0 | 2028 | 1056.2242 | 1056.2242 | 1056.2242 | 1496.3726 | 780 | 200 | 2476.3726 | 61.91% | 95% | 0% | -124.714 | 931.5103 | -3550 | -400 | -3018.4897 | 75.46% | 63.65% | 95% | 0% | 2028 | -109
[5 empty] | 2019-06-08 | 43 | 3812.5 | 1925 | -100 | 1 | 0 | 2025 | 1051.5251 | 1051.5251 | 1051.5251 | 1494.8063 | 780 | 200 | 2474.8063 | 61.87% | 95% | 0% | -114.4165 | 937.1087 | -3550 | -400 | -3012.8913 | 75.32% | 63.65% | 95% | 0% | 2025 | -100
[5 empty] | 2019-06-08 | 44 | 3813 | 1908 | -97 | 0 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 1494.8063 | 780 | 200 | 2474.8063 | 61.87% | 95% | 0% | -110.984 | 909.2139 | -2750 | -200 | -2040.7861 | 51.02% | 63.65% | 95% | 0% | 2005 | -97
[5 empty] | 2019-06-08 | 45 | 3813.5 | 1883 | -95 | 0 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 1494.8063 | 780 | 200 | 2474.8063 | 61.87% | 95% | 0% | -108.6957 | 869.2104 | -2750 | -200 | -2080.7896 | 52.02% | 63.65% | 95% | 0% | 1978 | -95
[5 empty] | 2019-06-08 | 46 | 3814 | 1814 | -94 | 0 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 1494.8063 | 780 | 200 | 2474.8063 | 61.87% | 95% | 0% | -107.5515 | 760.709 | -2750 | -200 | -2189.291 | 54.73% | 63.64% | 95% | 0% | 1908 | -94
[5 empty] | 2019-06-08 | 47 | 3814.5 | 1707 | -93 | 0 | 0 | 1800 | 699.0932 | 699.0932 | 699.0932 | 1494.8063 | 780 | 200 | 2474.8063 | 61.87% | 95% | 0% | -106.4073 | 592.6858 | -2750 | -200 | -2357.3142 | 58.93% | 63.64% | 95% | 0% | 1800 | -93
[5 empty] | 2019-06-08 | 48 | 3815 | 1602 | -92 | 0 | 0 | 1694 | 533.0585 | 533.0585 | 533.0585 | 1494.8063 | 780 | 200 | 2474.8063 | 61.87% | 95% | 0% | -105.2632 | 427.7954 | -2750 | -200 | -2522.2046 | 63.06% | 63.64% | 95% | 0% | 1694 | -92
[5 empty] | 2019-06-09 | 1 | 3815.5 | 1530 | -88 | 0 | 0 | 1618 | 414.0148 | 414.0148 | 414.0148 | 1494.8063 | 780 | 200 | 2474.8063 | 61.87% | 95% | 0% | -100.6865 | 313.3283 | -2750 | -200 | -2636.6717 | 65.92% | 63.64% | 95% | 0% | 1618 | -88
[5 empty] | 2019-06-09 | 2 | 3816 | 1475 | -84 | 0 | 0 | 1559 | 321.5993 | 321.5993 | 321.5993 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -96.1098 | 225.4895 | -2750 | -200 | -2724.5105 | 68.11% | 63.64% | 95% | 0% | 1559 | -84
[5 empty] | 2019-06-09 | 3 | 3816.5 | 1438 | -84 | 0 | 0 | 1522 | 263.6439 | 263.6439 | 263.6439 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -96.1098 | 167.534 | -2750 | -200 | -2782.466 | 69.56% | 63.64% | 95% | 0% | 1522 | -84
[5 empty] | 2019-06-09 | 4 | 3817 | 1423 | -83 | 0 | 0 | 1506 | 238.582 | 238.582 | 238.582 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -94.9657 | 143.6164 | -2750 | -200 | -2806.3836 | 70.16% | 63.63% | 95% | 0% | 1506 | -83
[5 empty] | 2019-06-09 | 5 | 3817.5 | 1396 | -82 | 0 | 0 | 1478 | 194.7238 | 194.7238 | 194.7238 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -93.8215 | 100.9023 | -2750 | -200 | -2849.0977 | 71.23% | 63.63% | 95% | 0% | 1478 | -82
[5 empty] | 2019-06-09 | 6 | 3818 | 1375 | -80 | 0 | 0 | 1455 | 158.6974 | 158.6974 | 158.6974 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -91.5332 | 67.1643 | -2750 | -200 | -2882.8357 | 72.07% | 63.62% | 95% | 0% | 1455 | -80
[5 empty] | 2019-06-09 | 7 | 3818.5 | 1355 | -78 | 0 | 0 | 1433 | 124.2374 | 124.2374 | 124.2374 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -89.2449 | 34.9926 | -2750 | -200 | -2915.0074 | 72.88% | 63.62% | 95% | 0% | 1433 | -78
[5 empty] | 2019-06-09 | 8 | 3819 | 1349 | -75 | 0 | 0 | 1424 | 110.1401 | 110.1401 | 110.1401 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -85.8124 | 24.3278 | -2750 | -200 | -2925.6722 | 73.14% | 63.62% | 95% | 0% | 1424 | -75
[5 empty] | 2019-06-09 | 9 | 3819.5 | 1342 | -72 | 0 | 0 | 1414 | 94.4765 | 94.4765 | 94.4765 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -82.3799 | 12.0966 | -2750 | -200 | -2937.9034 | 73.45% | 63.61% | 95% | 0% | 1414 | -72
[5 empty] | 2019-06-09 | 10 | 3820 | 1295 | -68 | 0 | 0 | 1363 | 14.5919 | 14.5919 | 14.5919 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -77.8032 | -63.2113 | -2750 | -200 | -3013.2113 | 75.33% | 63.6% | 95% | 0% | 1363 | -68
[5 empty] | 2019-06-09 | 11 | 3820.5 | 1293 | -74 | 0 | 0 | 1367 | 20.8574 | 20.8574 | 20.8574 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -84.6682 | -63.8108 | -2750 | -200 | -3013.8108 | 75.35% | 63.6% | 95% | 0% | 1367 | -74
[5 empty] | 2019-06-09 | 12 | 3821 | 1276 | -94 | 1 | 0 | 1370 | 25.5565 | 25.5565 | 25.5565 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -107.5515 | -81.995 | -3550 | -400 | -4031.995 | 100.8% | 63.6% | 95% | 0% | 1370 | -94
[5 empty] | 2019-06-09 | 13 | 3821.5 | 1266 | -128 | 1 | 0 | 1394 | 63.1492 | 63.1492 | 63.1492 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -146.4531 | -83.3039 | -3550 | -400 | -4033.3039 | 100.8% | 63.6% | 95% | 0% | 1394 | -128
[5 empty] | 2019-06-09 | 14 | 3822 | 1263 | -169 | 1 | 0 | 1432 | 122.6711 | 122.6711 | 122.6711 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -193.3638 | -70.6928 | -3550 | -400 | -4020.6928 | 100.5% | 63.6% | 95% | 0% | 1432 | -169
[5 empty] | 2019-06-09 | 15 | 3822.5 | 1254 | -219 | 1 | 0 | 1473 | 186.892 | 186.892 | 186.892 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -250.5721 | -63.6801 | -3550 | -400 | -4013.6801 | 100.3% | 63.59% | 95% | 0% | 1473 | -219
[5 empty] | 2019-06-09 | 16 | 3823 | 1239 | -276 | 1 | 0 | 1515 | 252.6793 | 252.6793 | 252.6793 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -315.7895 | -63.1102 | -3550 | -400 | -4013.1102 | 100.3% | 63.59% | 95% | 0% | 1515 | -276
[5 empty] | 2019-06-09 | 17 | 3823.5 | 1252 | -338 | 1 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -386.7277 | -16.5711 | -3550 | -400 | -3966.5711 | 99.16% | 63.59% | 95% | 0% | 1590 | -338
[5 empty] | 2019-06-09 | 18 | 3824 | 1256 | -392 | 1 | 0 | 1648 | 461.0058 | 461.0058 | 461.0058 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -448.5126 | 12.4932 | -3550 | -400 | -3937.5068 | 98.44% | 63.58% | 95% | 0% | 1648 | -392
[5 empty] | 2019-06-09 | 19 | 3824.5 | 1245 | -456 | 1 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -521.7391 | 22.284 | -3550 | -400 | -3927.716 | 98.19% | 63.58% | 95% | 0% | 1701 | -456
[5 empty] | 2019-06-09 | 20 | 3825 | 1225 | -488 | 1 | 0 | 1713 | 562.8195 | 562.8195 | 562.8195 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -558.3524 | 4.4671 | -3550 | -400 | -3945.5329 | 98.64% | 63.58% | 95% | 0% | 1713 | -488
[5 empty] | 2019-06-09 | 21 | 3825.5 | 1239 | -521 | 1 | 0 | 1760 | 636.4386 | 636.4386 | 636.4386 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -596.1098 | 40.3287 | -3550 | -400 | -3909.6713 | 97.74% | 63.58% | 95% | 0% | 1760 | -521
[5 empty] | 2019-06-09 | 22 | 3826 | 1245 | -549 | 1 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -628.1465 | 61.5485 | -3550 | -400 | -3888.4515 | 97.21% | 63.58% | 95% | 0% | 1794 | -549
[5 empty] | 2019-06-09 | 23 | 3826.5 | 1250 | -550 | 1 | 0 | 1800 | 699.0932 | 699.0932 | 699.0932 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -629.2906 | 69.8025 | -3550 | -400 | -3880.1975 | 97% | 63.58% | 95% | 0% | 1800 | -550
[5 empty] | 2019-06-09 | 24 | 3827 | 1242 | -565 | 1 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -646.4531 | 63.6046 | -3550 | -400 | -3886.3954 | 97.16% | 63.58% | 95% | 0% | 1807 | -565
[5 empty] | 2019-06-09 | 25 | 3827.5 | 1233 | -572 | 1 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 1493.2399 | 780 | 200 | 2473.2399 | 61.83% | 95% | 0% | -654.4622 | 52.4627 | -3550 | -400 | -3897.5373 | 97.44% | 63.58% | 95% | 0% | 1805 | -572
[5 empty] | 2019-06-09 | 26 | 3828 | 1212 | -576 | 1 | 0 | 1788 | 680.2968 | 680.2968 | 680.2968 | 1491.6735 | 780 | 200 | 2471.6735 | 61.79% | 95% | 0% | -659.0389 | 21.2579 | -3550 | -400 | -3928.7421 | 98.22% | 63.58% | 95% | 0% | 1788 | -576
[5 empty] | 2019-06-09 | 27 | 3828.5 | 1253 | -546 | 1 | 0 | 1799 | 697.5268 | 697.5268 | 697.5268 | 1491.6735 | 780 | 200 | 2471.6735 | 61.79% | 95% | 0% | -624.714 | 72.8128 | -3550 | -400 | -3877.1872 | 96.93% | 63.58% | 95% | 0% | 1799 | -546
[5 empty] | 2019-06-09 | 28 | 3829 | 1232 | -563 | 1 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 1491.6735 | 780 | 200 | 2471.6735 | 61.79% | 95% | 0% | -644.1648 | 47.0966 | -3550 | -400 | -3902.9034 | 97.57% | 63.57% | 95% | 0% | 1795 | -563
[5 empty] | 2019-06-09 | 29 | 3829.5 | 1253 | -538 | 1 | 0 | 1791 | 684.9959 | 684.9959 | 684.9959 | 1491.6735 | 780 | 200 | 2471.6735 | 61.79% | 95% | 0% | -615.5606 | 69.4352 | -3550 | -400 | -3880.5648 | 97.01% | 63.57% | 95% | 0% | 1791 | -538
[5 empty] | 2019-06-09 | 30 | 3830 | 1291 | -504 | 1 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 1491.6735 | 780 | 200 | 2471.6735 | 61.79% | 95% | 0% | -576.659 | 114.6023 | -3550 | -400 | -3835.3977 | 95.88% | 63.57% | 95% | 0% | 1795 | -504
[5 empty] | 2019-06-09 | 31 | 3830.5 | 1369 | -459 | 1 | 0 | 1828 | 742.9514 | 742.9514 | 742.9514 | 1491.6735 | 780 | 200 | 2471.6735 | 61.79% | 95% | 0% | -525.1716 | 217.7797 | -3550 | -400 | -3732.2203 | 93.31% | 63.57% | 95% | 0% | 1828 | -459
[5 empty] | 2019-06-09 | 32 | 3831 | 1442 | -428 | 1 | 0 | 1870 | 808.7387 | 808.7387 | 808.7387 | 1491.6735 | 780 | 200 | 2471.6735 | 61.79% | 95% | 0% | -489.7025 | 319.0361 | -3550 | -400 | -3630.9639 | 90.77% | 63.56% | 95% | 0% | 1870 | -428
[5 empty] | 2019-06-09 | 33 | 3831.5 | 1522 | -400 | 1 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 1491.6735 | 780 | 200 | 2471.6735 | 61.79% | 95% | 0% | -457.6659 | 432.5237 | -3550 | -400 | -3517.4763 | 87.94% | 63.56% | 95% | 0% | 1922 | -400
[5 empty] | 2019-06-09 | 34 | 3832 | 1652 | -337 | 1 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 1491.6735 | 780 | 200 | 2471.6735 | 61.79% | 95% | 0% | -385.5835 | 609.5525 | -3550 | -400 | -3340.4475 | 83.51% | 63.56% | 95% | 0% | 1989 | -337
[5 empty] | 2019-06-09 | 35 | 3832.5 | 1809 | -280 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1491.6735 | 780 | 200 | 2471.6735 | 61.79% | 95% | 0% | -320.3661 | 831.4063 | -3550 | -400 | -3118.5937 | 77.96% | 63.56% | 95% | 0% | 2089 | -280
[5 empty] | 2019-06-09 | 36 | 3833 | 1871 | -246 | 1 | 0 | 2117 | 1195.6307 | 1195.6307 | 1195.6307 | 1491.6735 | 780 | 200 | 2471.6735 | 61.79% | 95% | 0% | -281.4645 | 914.1661 | -3550 | -400 | -3035.8339 | 75.9% | 63.55% | 95% | 0% | 2117 | -246
[5 empty] | 2019-06-09 | 37 | 3833.5 | 1924 | -212 | 1 | 0 | 2136 | 1225.3916 | 1225.3916 | 1225.3916 | 1491.6735 | 780 | 200 | 2471.6735 | 61.79% | 95% | 0% | -242.5629 | 982.8287 | -3550 | -400 | -2967.1713 | 74.18% | 63.55% | 95% | 0% | 2136 | -212
[5 empty] | 2019-06-09 | 38 | 3834 | 1977 | -162 | 1 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 1490.1072 | 780 | 200 | 2470.1072 | 61.75% | 95% | 0% | -185.3547 | 1044.736 | -3550 | -400 | -2905.264 | 72.63% | 63.55% | 95% | 0% | 2139 | -162
[5 empty] | 2019-06-09 | 39 | 3834.5 | 2053 | -130 | 1 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 1490.1072 | 780 | 200 | 2470.1072 | 61.75% | 95% | 0% | -148.7414 | 1150.2693 | -3550 | -400 | -2799.7307 | 69.99% | 63.55% | 95% | 0% | 2183 | -130
[5 empty] | 2019-06-09 | 40 | 3835 | 2098 | -88 | 1 | 0 | 2186 | 1303.7098 | 1303.7098 | 1303.7098 | 1490.1072 | 780 | 200 | 2470.1072 | 61.75% | 95% | 0% | -100.6865 | 1203.0233 | -3550 | -400 | -2746.9767 | 68.67% | 63.55% | 95% | 0% | 2186 | -88
[5 empty] | 2019-06-09 | 41 | 3835.5 | 2110 | -62 | 1 | 0 | 2172 | 1281.7807 | 1281.7807 | 1281.7807 | 1490.1072 | 780 | 200 | 2470.1072 | 61.75% | 95% | 0% | -70.9382 | 1210.8425 | -3550 | -400 | -2739.1575 | 68.48% | 63.55% | 95% | 0% | 2172 | -62
[5 empty] | 2019-06-09 | 42 | 3836 | 2113 | -38 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1490.1072 | 780 | 200 | 2470.1072 | 61.75% | 95% | 0% | -43.4783 | 1205.4088 | -3550 | -400 | -2744.5912 | 68.61% | 63.54% | 95% | 0% | 2151 | -38
[5 empty] | 2019-06-09 | 43 | 3836.5 | 2111 | -27 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1490.1072 | 780 | 200 | 2470.1072 | 61.75% | 95% | 0% | -30.8924 | 1197.6319 | -3550 | -400 | -2752.3681 | 68.81% | 63.54% | 95% | 0% | 2138 | -27
[5 empty] | 2019-06-09 | 44 | 3837 | 2063 | -24 | 1 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 1490.1072 | 780 | 200 | 2470.1072 | 61.75% | 95% | 0% | -27.46 | 1121.1798 | -3550 | -400 | -2828.8202 | 70.72% | 63.54% | 95% | 0% | 2087 | -24
[5 empty] | 2019-06-09 | 45 | 3837.5 | 2049 | -23 | 1 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 1490.1072 | 780 | 200 | 2470.1072 | 61.75% | 95% | 0% | -26.3158 | 1098.8285 | -3550 | -400 | -2851.1715 | 71.28% | 63.53% | 95% | 0% | 2072 | -23
[5 empty] | 2019-06-09 | 46 | 3838 | 1957 | -22 | 0 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 1490.1072 | 780 | 200 | 2470.1072 | 61.75% | 95% | 0% | -25.1716 | 954.3008 | -2750 | -200 | -1995.6992 | 49.89% | 63.53% | 95% | 0% | 1979 | -22
[5 empty] | 2019-06-09 | 47 | 3838.5 | 1827 | -21 | 0 | 0 | 1848 | 774.2786 | 774.2786 | 774.2786 | 1490.1072 | 780 | 200 | 2470.1072 | 61.75% | 95% | 0% | -24.0275 | 750.2512 | -2750 | -200 | -2199.7488 | 54.99% | 63.53% | 95% | 0% | 1848 | -21
[5 empty] | 2019-06-09 | 48 | 3839 | 1709 | -21 | 0 | 0 | 1730 | 589.4477 | 589.4477 | 589.4477 | 1490.1072 | 780 | 200 | 2470.1072 | 61.75% | 95% | 0% | -24.0275 | 565.4202 | -2750 | -200 | -2384.5798 | 59.61% | 63.52% | 95% | 0% | 1730 | -21
[5 empty] | 2019-06-10 | 1 | 3839.5 | 1637 | -20 | 0 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -22.8833 | 452.2198 | -2750 | -200 | -2497.7802 | 62.44% | 63.52% | 95% | 0% | 1657 | -20
[5 empty] | 2019-06-10 | 2 | 3840 | 1590 | -19 | 0 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -21.7391 | 378.1784 | -2750 | -200 | -2571.8216 | 64.3% | 63.51% | 95% | 0% | 1609 | -19
[5 empty] | 2019-06-10 | 3 | 3840.5 | 1574 | -19 | 0 | 0 | 1593 | 374.8557 | 374.8557 | 374.8557 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -21.7391 | 353.1166 | -2750 | -200 | -2596.8834 | 64.92% | 63.51% | 95% | 0% | 1593 | -19
[5 empty] | 2019-06-10 | 4 | 3841 | 1570 | -19 | 0 | 0 | 1589 | 368.5903 | 368.5903 | 368.5903 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -21.7391 | 346.8511 | -2750 | -200 | -2603.1489 | 65.08% | 63.51% | 95% | 0% | 1589 | -19
[5 empty] | 2019-06-10 | 5 | 3841.5 | 1556 | -20 | 0 | 0 | 1576 | 348.2275 | 348.2275 | 348.2275 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -22.8833 | 325.3442 | -2750 | -200 | -2624.6558 | 65.62% | 63.5% | 95% | 0% | 1576 | -20
[5 empty] | 2019-06-10 | 6 | 3842 | 1538 | -21 | 0 | 0 | 1559 | 321.5993 | 321.5993 | 321.5993 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -24.0275 | 297.5719 | -2750 | -200 | -2652.4281 | 66.31% | 63.5% | 95% | 0% | 1559 | -21
[5 empty] | 2019-06-10 | 7 | 3842.5 | 1525 | -21 | 0 | 0 | 1546 | 301.2366 | 301.2366 | 301.2366 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -24.0275 | 277.2091 | -2750 | -200 | -2672.7909 | 66.82% | 63.5% | 95% | 0% | 1546 | -21
[5 empty] | 2019-06-10 | 8 | 3843 | 1522 | -21 | 0 | 0 | 1543 | 296.5375 | 296.5375 | 296.5375 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -24.0275 | 272.5101 | -2750 | -200 | -2677.4899 | 66.94% | 63.5% | 95% | 0% | 1543 | -21
[5 empty] | 2019-06-10 | 9 | 3843.5 | 1517 | -22 | 1 | 0 | 1539 | 290.2721 | 290.2721 | 290.2721 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -25.1716 | 265.1004 | -3550 | -400 | -3684.8996 | 92.12% | 63.49% | 95% | 0% | 1539 | -22
[5 empty] | 2019-06-10 | 10 | 3844 | 1506 | -22 | 1 | 0 | 1528 | 273.042 | 273.042 | 273.042 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -25.1716 | 247.8704 | -3550 | -400 | -3702.1296 | 92.55% | 63.49% | 95% | 0% | 1528 | -22
[5 empty] | 2019-06-10 | 11 | 3844.5 | 1549 | -27 | 1 | 0 | 1576 | 348.2275 | 348.2275 | 348.2275 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -30.8924 | 317.3351 | -3550 | -400 | -3632.6649 | 90.82% | 63.49% | 95% | 0% | 1576 | -27
[5 empty] | 2019-06-10 | 12 | 3845 | 1596 | -40 | 1 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -45.7666 | 396.4428 | -3550 | -400 | -3553.5572 | 88.84% | 63.48% | 95% | 0% | 1636 | -40
[5 empty] | 2019-06-10 | 13 | 3845.5 | 1778 | -64 | 1 | 0 | 1842 | 764.8805 | 764.8805 | 764.8805 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -73.2265 | 691.6539 | -3550 | -400 | -3258.3461 | 81.46% | 63.48% | 95% | 0% | 1842 | -64
[5 empty] | 2019-06-10 | 14 | 3846 | 1938 | -92 | 1 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -105.2632 | 954.0938 | -3550 | -400 | -2995.9062 | 74.9% | 63.48% | 95% | 0% | 2030 | -92
[5 empty] | 2019-06-10 | 15 | 3846.5 | 2108 | -127 | 1 | 0 | 2235 | 1380.4617 | 1380.4617 | 1380.4617 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -145.3089 | 1235.1527 | -3550 | -400 | -2714.8473 | 67.87% | 63.48% | 95% | 0% | 2235 | -127
[5 empty] | 2019-06-10 | 16 | 3847 | 2200 | -165 | 1 | 0 | 2365 | 1584.089 | 1584.089 | 1584.089 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -188.7872 | 1395.3019 | -3550 | -400 | -2554.6981 | 63.87% | 63.47% | 95% | 0% | 2365 | -165
[5 empty] | 2019-06-10 | 17 | 3847.5 | 2182 | -200 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -228.833 | 1381.8843 | -3550 | -400 | -2568.1157 | 64.2% | 63.47% | 95% | 0% | 2382 | -200
[5 empty] | 2019-06-10 | 18 | 3848 | 2131 | -235 | 1 | 0 | 2366 | 1585.6554 | 1585.6554 | 1585.6554 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -268.8787 | 1316.7767 | -3550 | -400 | -2633.2233 | 65.83% | 63.46% | 95% | 0% | 2366 | -235
[5 empty] | 2019-06-10 | 19 | 3848.5 | 2122 | -265 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 1488.5408 | 780 | 200 | 2468.5408 | 61.71% | 95% | 0% | -303.2037 | 1315.3454 | -3550 | -400 | -2634.6546 | 65.87% | 63.46% | 95% | 0% | 2387 | -265
[5 empty] | 2019-06-10 | 20 | 3849 | 2110 | -280 | 1 | 0 | 2390 | 1623.2481 | 1623.2481 | 1623.2481 | 1486.9744 | 780 | 200 | 2466.9744 | 61.67% | 95% | 0% | -320.3661 | 1302.882 | -3550 | -400 | -2647.118 | 66.18% | 63.46% | 95% | 0% | 2390 | -280
[5 empty] | 2019-06-10 | 21 | 3849.5 | 2075 | -308 | 1 | 0 | 2383 | 1612.2836 | 1612.2836 | 1612.2836 | 1486.9744 | 780 | 200 | 2466.9744 | 61.67% | 95% | 0% | -352.4027 | 1259.8808 | -3550 | -400 | -2690.1192 | 67.25% | 63.45% | 95% | 0% | 2383 | -308
[5 empty] | 2019-06-10 | 22 | 3850 | 2074 | -326 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 1486.9744 | 780 | 200 | 2466.9744 | 61.67% | 95% | 0% | -372.9977 | 1265.9141 | -3550 | -400 | -2684.0859 | 67.1% | 63.45% | 95% | 0% | 2400 | -326
[5 empty] | 2019-06-10 | 23 | 3850.5 | 2098 | -322 | 1 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 1486.9744 | 780 | 200 | 2466.9744 | 61.67% | 95% | 0% | -368.4211 | 1301.818 | -3550 | -400 | -2648.182 | 66.2% | 63.45% | 95% | 0% | 2420 | -322
[5 empty] | 2019-06-10 | 24 | 3851 | 2115 | -329 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 1486.9744 | 780 | 200 | 2466.9744 | 61.67% | 95% | 0% | -376.4302 | 1331.4016 | -3550 | -400 | -2618.5984 | 65.46% | 63.45% | 95% | 0% | 2444 | -329
[5 empty] | 2019-06-10 | 25 | 3851.5 | 2113 | -352 | 1 | 0 | 2465 | 1740.7255 | 1740.7255 | 1740.7255 | 1486.9744 | 780 | 200 | 2466.9744 | 61.67% | 95% | 0% | -402.746 | 1337.9795 | -3550 | -400 | -2612.0205 | 65.3% | 63.45% | 95% | 0% | 2465 | -352
[5 empty] | 2019-06-10 | 26 | 3852 | 2095 | -378 | 1 | 0 | 2473 | 1753.2564 | 1753.2564 | 1753.2564 | 1486.9744 | 780 | 200 | 2466.9744 | 61.67% | 95% | 0% | -432.4943 | 1320.7621 | -3550 | -400 | -2629.2379 | 65.73% | 63.44% | 95% | 0% | 2473 | -378
[5 empty] | 2019-06-10 | 27 | 3852.5 | 2113 | -352 | 1 | 0 | 2465 | 1740.7255 | 1740.7255 | 1740.7255 | 1486.9744 | 780 | 200 | 2466.9744 | 61.67% | 95% | 0% | -402.746 | 1337.9795 | -3550 | -400 | -2612.0205 | 65.3% | 63.44% | 95% | 0% | 2465 | -352
[5 empty] | 2019-06-10 | 28 | 3853 | 2120 | -344 | 1 | 0 | 2464 | 1739.1591 | 1739.1591 | 1739.1591 | 1486.9744 | 780 | 200 | 2466.9744 | 61.67% | 95% | 0% | -393.5927 | 1345.5664 | -3550 | -400 | -2604.4336 | 65.11% | 63.43% | 95% | 0% | 2464 | -344
[5 empty] | 2019-06-10 | 29 | 3853.5 | 2172 | -298 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 1486.9744 | 780 | 200 | 2466.9744 | 61.67% | 95% | 0% | -340.9611 | 1407.5962 | -3550 | -400 | -2542.4038 | 63.56% | 63.43% | 95% | 0% | 2470 | -298
[5 empty] | 2019-06-10 | 30 | 3854 | 2154 | -300 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 1486.9744 | 780 | 200 | 2466.9744 | 61.67% | 95% | 0% | -343.2494 | 1380.246 | -3550 | -400 | -2569.754 | 64.24% | 63.42% | 95% | 0% | 2454 | -300
[5 empty] | 2019-06-10 | 31 | 3854.5 | 2161 | -282 | 1 | 0 | 2443 | 1706.2655 | 1706.2655 | 1706.2655 | 1486.9744 | 780 | 200 | 2466.9744 | 61.67% | 95% | 0% | -322.6545 | 1383.611 | -3550 | -400 | -2566.389 | 64.16% | 63.41% | 95% | 0% | 2443 | -282
[5 empty] | 2019-06-10 | 32 | 3855 | 2223 | -270 | 1 | 0 | 2493 | 1784.5837 | 1784.5837 | 1784.5837 | 1485.4081 | 780 | 200 | 2465.4081 | 61.64% | 95% | 0% | -308.9245 | 1475.6592 | -3550 | -400 | -2474.3408 | 61.86% | 63.41% | 95% | 0% | 2493 | -270
[5 empty] | 2019-06-10 | 33 | 3855.5 | 2291 | -252 | 1 | 0 | 2543 | 1862.9019 | 1862.9019 | 1862.9019 | 1485.4081 | 780 | 200 | 2465.4081 | 61.64% | 95% | 0% | -288.3295 | 1574.5724 | -3550 | -400 | -2375.4276 | 59.39% | 63.41% | 95% | 0% | 2543 | -252
[5 empty] | 2019-06-10 | 34 | 3856 | 2383 | -228 | 1 | 0 | 2611 | 1969.4147 | 1969.4147 | 1969.4147 | 1485.4081 | 780 | 200 | 2465.4081 | 61.64% | 95% | 0% | -260.8696 | 1708.5451 | -3550 | -400 | -2241.4549 | 56.04% | 63.41% | 95% | 0% | 2611 | -228
[5 empty] | 2019-06-10 | 35 | 3856.5 | 2449 | -199 | 1 | 0 | 2648 | 2027.3702 | 2027.3702 | 2027.3702 | 1485.4081 | 780 | 200 | 2465.4081 | 61.64% | 95% | 0% | -227.6888 | 1799.6814 | -3550 | -400 | -2150.3186 | 53.76% | 63.4% | 95% | 0% | 2648 | -199
[5 empty] | 2019-06-10 | 36 | 3857 | 2451 | -186 | 1 | 0 | 2637 | 2010.1401 | 2010.1401 | 2010.1401 | 1485.4081 | 780 | 200 | 2465.4081 | 61.64% | 95% | 0% | -212.8146 | 1797.3255 | -3550 | -400 | -2152.6745 | 53.82% | 63.39% | 95% | 0% | 2637 | -186
[5 empty] | 2019-06-10 | 37 | 3857.5 | 2474 | -165 | 1 | 0 | 2639 | 2013.2729 | 2013.2729 | 2013.2729 | 1485.4081 | 780 | 200 | 2465.4081 | 61.64% | 95% | 0% | -188.7872 | 1824.4857 | -3550 | -400 | -2125.5143 | 53.14% | 63.39% | 95% | 0% | 2639 | -165
[5 empty] | 2019-06-10 | 38 | 3858 | 2493 | -146 | 1 | 0 | 2639 | 2013.2729 | 2013.2729 | 2013.2729 | 1485.4081 | 780 | 200 | 2465.4081 | 61.64% | 95% | 0% | -167.0481 | 1846.2248 | -3550 | -400 | -2103.7752 | 52.59% | 63.39% | 95% | 0% | 2639 | -146
[5 empty] | 2019-06-10 | 39 | 3858.5 | 2460 | -129 | 1 | 0 | 2589 | 1934.9547 | 1934.9547 | 1934.9547 | 1485.4081 | 780 | 200 | 2465.4081 | 61.64% | 95% | 0% | -147.5973 | 1787.3574 | -3550 | -400 | -2162.6426 | 54.07% | 63.38% | 95% | 0% | 2589 | -129
[5 empty] | 2019-06-10 | 40 | 3859 | 2428 | -118 | 1 | 0 | 2546 | 1867.601 | 1867.601 | 1867.601 | 1485.4081 | 780 | 200 | 2465.4081 | 61.64% | 95% | 0% | -135.0114 | 1732.5895 | -3550 | -400 | -2217.4105 | 55.44% | 63.38% | 95% | 0% | 2546 | -118
[5 empty] | 2019-06-10 | 41 | 3859.5 | 2364 | -110 | 1 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -125.8581 | 1628.9646 | -3550 | -400 | -2321.0354 | 58.03% | 63.38% | 95% | 0% | 2474 | -110
[5 empty] | 2019-06-10 | 42 | 3860 | 2298 | -103 | 1 | 0 | 2401 | 1640.4782 | 1640.4782 | 1640.4782 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -117.849 | 1522.6292 | -3550 | -400 | -2427.3708 | 60.68% | 63.38% | 95% | 0% | 2401 | -103
[5 empty] | 2019-06-10 | 43 | 3860.5 | 2245 | -100 | 1 | 0 | 2345 | 1552.7617 | 1552.7617 | 1552.7617 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -114.4165 | 1438.3453 | -3550 | -400 | -2511.6547 | 62.79% | 63.38% | 95% | 0% | 2345 | -100
[5 empty] | 2019-06-10 | 44 | 3861 | 2155 | -99 | 1 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -113.2723 | 1296.9503 | -3550 | -400 | -2653.0497 | 66.33% | 63.37% | 95% | 0% | 2254 | -99
[5 empty] | 2019-06-10 | 45 | 3861.5 | 2053 | -100 | 1 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -114.4165 | 1137.6033 | -3550 | -400 | -2812.3967 | 70.31% | 63.37% | 95% | 0% | 2153 | -100
[5 empty] | 2019-06-10 | 46 | 3862 | 1905 | -101 | 0 | 0 | 2006 | 1021.7642 | 1021.7642 | 1021.7642 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -115.5606 | 906.2036 | -2750 | -200 | -2043.7964 | 51.09% | 63.37% | 95% | 0% | 2006 | -101
[5 empty] | 2019-06-10 | 47 | 3862.5 | 1743 | -103 | 0 | 0 | 1846 | 771.1459 | 771.1459 | 771.1459 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -117.849 | 653.2969 | -2750 | -200 | -2296.7031 | 57.42% | 63.37% | 95% | 0% | 1846 | -103
[5 empty] | 2019-06-10 | 48 | 3863 | 1616 | -105 | 0 | 0 | 1721 | 575.3504 | 575.3504 | 575.3504 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -120.1373 | 455.2131 | -2750 | -200 | -2494.7869 | 62.37% | 63.37% | 95% | 0% | 1721 | -105
[5 empty] | 2019-06-11 | 1 | 3863.5 | 1527 | -109 | 0 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -124.714 | 317.4954 | -2750 | -200 | -2632.5046 | 65.81% | 63.36% | 95% | 0% | 1636 | -109
[5 empty] | 2019-06-11 | 2 | 3864 | 1463 | -112 | 0 | 0 | 1575 | 346.6612 | 346.6612 | 346.6612 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -128.1465 | 218.5147 | -2750 | -200 | -2731.4853 | 68.29% | 63.35% | 95% | 0% | 1575 | -112
[5 empty] | 2019-06-11 | 3 | 3864.5 | 1428 | -115 | 0 | 0 | 1543 | 296.5375 | 296.5375 | 296.5375 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -131.5789 | 164.9586 | -2750 | -200 | -2785.0414 | 69.63% | 63.35% | 95% | 0% | 1543 | -115
[5 empty] | 2019-06-11 | 4 | 3865 | 1411 | -118 | 0 | 0 | 1529 | 274.6084 | 274.6084 | 274.6084 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -135.0114 | 139.597 | -2750 | -200 | -2810.403 | 70.26% | 63.35% | 95% | 0% | 1529 | -118
[5 empty] | 2019-06-11 | 5 | 3865.5 | 1380 | -122 | 0 | 0 | 1502 | 232.3166 | 232.3166 | 232.3166 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -139.5881 | 92.7285 | -2750 | -200 | -2857.2715 | 71.43% | 63.35% | 95% | 0% | 1502 | -122
[5 empty] | 2019-06-11 | 6 | 3866 | 1355 | -126 | 0 | 0 | 1481 | 199.4229 | 199.4229 | 199.4229 | 1483.8417 | 780 | 200 | 2463.8417 | 61.6% | 95% | 0% | -144.1648 | 55.2582 | -2750 | -200 | -2894.7418 | 72.37% | 63.34% | 95% | 0% | 1481 | -126
[5 empty] | 2019-06-11 | 7 | 3866.5 | 1321 | -128 | 0 | 0 | 1449 | 149.2993 | 149.2993 | 149.2993 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -146.4531 | 2.8462 | -2750 | -200 | -2947.1538 | 73.68% | 63.34% | 95% | 0% | 1449 | -128
[5 empty] | 2019-06-11 | 8 | 3867 | 1312 | -131 | 0 | 0 | 1443 | 139.9011 | 139.9011 | 139.9011 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -149.8856 | -9.9845 | -2750 | -200 | -2959.9845 | 74% | 63.34% | 95% | 0% | 1443 | -131
[5 empty] | 2019-06-11 | 9 | 3867.5 | 1307 | -133 | 1 | 0 | 1440 | 135.202 | 135.202 | 135.202 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -152.1739 | -16.9719 | -3550 | -400 | -3966.9719 | 99.17% | 63.34% | 95% | 0% | 1440 | -133
[5 empty] | 2019-06-11 | 10 | 3868 | 1298 | -135 | 1 | 0 | 1433 | 124.2374 | 124.2374 | 124.2374 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -154.4622 | -30.2248 | -3550 | -400 | -3980.2248 | 99.51% | 63.33% | 95% | 0% | 1433 | -135
[5 empty] | 2019-06-11 | 11 | 3868.5 | 1321 | -139 | 1 | 0 | 1460 | 166.5293 | 166.5293 | 166.5293 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -159.0389 | 7.4904 | -3550 | -400 | -3942.5096 | 98.56% | 63.33% | 95% | 0% | 1460 | -139
[5 empty] | 2019-06-11 | 12 | 3869 | 1391 | -146 | 1 | 0 | 1537 | 287.1393 | 287.1393 | 287.1393 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -167.0481 | 120.0913 | -3550 | -400 | -3829.9087 | 95.75% | 63.33% | 95% | 0% | 1537 | -146
[5 empty] | 2019-06-11 | 13 | 3869.5 | 1569 | -156 | 1 | 0 | 1725 | 581.6158 | 581.6158 | 581.6158 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -178.4897 | 403.1261 | -3550 | -400 | -3546.8739 | 88.67% | 63.33% | 95% | 0% | 1725 | -156
[5 empty] | 2019-06-11 | 14 | 3870 | 1752 | -173 | 1 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -197.9405 | 696.9482 | -3550 | -400 | -3253.0518 | 81.33% | 63.33% | 95% | 0% | 1925 | -173
[5 empty] | 2019-06-11 | 15 | 3870.5 | 1961 | -196 | 1 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -224.2563 | 1034.029 | -3550 | -400 | -2915.971 | 72.9% | 63.33% | 95% | 0% | 2157 | -196
[5 empty] | 2019-06-11 | 16 | 3871 | 2064 | -219 | 1 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -250.5721 | 1205.0751 | -3550 | -400 | -2744.9249 | 68.62% | 63.32% | 95% | 0% | 2283 | -219
[5 empty] | 2019-06-11 | 17 | 3871.5 | 2137 | -236 | 1 | 0 | 2373 | 1596.62 | 1596.62 | 1596.62 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -270.0229 | 1326.5971 | -3550 | -400 | -2623.4029 | 65.59% | 63.32% | 95% | 0% | 2373 | -236
[5 empty] | 2019-06-11 | 18 | 3872 | 2101 | -266 | 1 | 0 | 2367 | 1587.2218 | 1587.2218 | 1587.2218 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -304.3478 | 1282.8739 | -3550 | -400 | -2667.1261 | 66.68% | 63.32% | 95% | 0% | 2367 | -266
[5 empty] | 2019-06-11 | 19 | 3872.5 | 2104 | -285 | 1 | 0 | 2389 | 1621.6818 | 1621.6818 | 1621.6818 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -326.087 | 1295.5948 | -3550 | -400 | -2654.4052 | 66.36% | 63.31% | 95% | 0% | 2389 | -285
[5 empty] | 2019-06-11 | 20 | 3873 | 2100 | -294 | 1 | 0 | 2394 | 1629.5136 | 1629.5136 | 1629.5136 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -336.3844 | 1293.1292 | -3550 | -400 | -2656.8708 | 66.42% | 63.31% | 95% | 0% | 2394 | -294
[5 empty] | 2019-06-11 | 21 | 3873.5 | 2051 | -316 | 1 | 0 | 2367 | 1587.2218 | 1587.2218 | 1587.2218 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -361.5561 | 1225.6657 | -3550 | -400 | -2724.3343 | 68.11% | 63.31% | 95% | 0% | 2367 | -316
[5 empty] | 2019-06-11 | 22 | 3874 | 2023 | -341 | 1 | 0 | 2364 | 1582.5227 | 1582.5227 | 1582.5227 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -390.1602 | 1192.3625 | -3550 | -400 | -2757.6375 | 68.94% | 63.31% | 95% | 0% | 2364 | -341
[5 empty] | 2019-06-11 | 23 | 3874.5 | 2052 | -348 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -398.1693 | 1240.7425 | -3550 | -400 | -2709.2575 | 67.73% | 63.31% | 95% | 0% | 2400 | -348
[5 empty] | 2019-06-11 | 24 | 3875 | 2053 | -356 | 1 | 0 | 2409 | 1653.0091 | 1653.0091 | 1653.0091 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -407.3227 | 1245.6864 | -3550 | -400 | -2704.3136 | 67.61% | 63.31% | 95% | 0% | 2409 | -356
[5 empty] | 2019-06-11 | 25 | 3875.5 | 2046 | -360 | 1 | 0 | 2406 | 1648.31 | 1648.31 | 1648.31 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -411.8993 | 1236.4107 | -3550 | -400 | -2713.5893 | 67.84% | 63.3% | 95% | 0% | 2406 | -360
[5 empty] | 2019-06-11 | 26 | 3876 | 2018 | -361 | 1 | 0 | 2379 | 1606.0181 | 1606.0181 | 1606.0181 | 1482.2754 | 780 | 200 | 2462.2754 | 61.56% | 95% | 0% | -413.0435 | 1192.9747 | -3550 | -400 | -2757.0253 | 68.93% | 63.3% | 95% | 0% | 2379 | -361
[5 empty] | 2019-06-11 | 27 | 3876.5 | 2043 | -347 | 1 | 0 | 2390 | 1623.2481 | 1623.2481 | 1623.2481 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -397.0252 | 1226.223 | -3550 | -400 | -2723.777 | 68.09% | 63.29% | 95% | 0% | 2390 | -347
[5 empty] | 2019-06-11 | 28 | 3877 | 2032 | -357 | 1 | 0 | 2389 | 1621.6818 | 1621.6818 | 1621.6818 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -408.4668 | 1213.215 | -3550 | -400 | -2736.785 | 68.42% | 63.29% | 95% | 0% | 2389 | -357
[5 empty] | 2019-06-11 | 29 | 3877.5 | 2022 | -359 | 1 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -410.7551 | 1198.3957 | -3550 | -400 | -2751.6043 | 68.79% | 63.29% | 95% | 0% | 2381 | -359
[5 empty] | 2019-06-11 | 30 | 3878 | 2017 | -339 | 1 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -387.8719 | 1182.1199 | -3550 | -400 | -2767.8801 | 69.2% | 63.28% | 95% | 0% | 2356 | -339
[5 empty] | 2019-06-11 | 31 | 3878.5 | 2046 | -318 | 1 | 0 | 2364 | 1582.5227 | 1582.5227 | 1582.5227 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -363.8444 | 1218.6783 | -3550 | -400 | -2731.3217 | 68.28% | 63.28% | 95% | 0% | 2364 | -318
[5 empty] | 2019-06-11 | 32 | 3879 | 2103 | -307 | 1 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -351.2586 | 1303.3169 | -3550 | -400 | -2646.6831 | 66.17% | 63.27% | 95% | 0% | 2410 | -307
[5 empty] | 2019-06-11 | 33 | 3879.5 | 2189 | -285 | 1 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -326.087 | 1428.7358 | -3550 | -400 | -2521.2642 | 63.03% | 63.27% | 95% | 0% | 2474 | -285
[5 empty] | 2019-06-11 | 34 | 3880 | 2283 | -259 | 1 | 0 | 2542 | 1861.3355 | 1861.3355 | 1861.3355 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -296.3387 | 1564.9969 | -3550 | -400 | -2385.0031 | 59.63% | 63.27% | 95% | 0% | 2542 | -259
[5 empty] | 2019-06-11 | 35 | 3880.5 | 2368 | -234 | 1 | 0 | 2602 | 1955.3174 | 1955.3174 | 1955.3174 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -267.7346 | 1687.5828 | -3550 | -400 | -2262.4172 | 56.56% | 63.27% | 95% | 0% | 2602 | -234
[5 empty] | 2019-06-11 | 36 | 3881 | 2399 | -219 | 1 | 0 | 2618 | 1980.3792 | 1980.3792 | 1980.3792 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -250.5721 | 1729.8071 | -3550 | -400 | -2220.1929 | 55.5% | 63.27% | 95% | 0% | 2618 | -219
[5 empty] | 2019-06-11 | 37 | 3881.5 | 2410 | -205 | 1 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -234.5538 | 1741.1264 | -3550 | -400 | -2208.8736 | 55.22% | 63.27% | 95% | 0% | 2615 | -205
[5 empty] | 2019-06-11 | 38 | 3882 | 2403 | -187 | 1 | 0 | 2590 | 1936.521 | 1936.521 | 1936.521 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -213.9588 | 1722.5622 | -3550 | -400 | -2227.4378 | 55.69% | 63.26% | 95% | 0% | 2590 | -187
[5 empty] | 2019-06-11 | 39 | 3882.5 | 2396 | -171 | 1 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -195.6522 | 1704.8425 | -3550 | -400 | -2245.1575 | 56.13% | 63.26% | 95% | 0% | 2567 | -171
[5 empty] | 2019-06-11 | 40 | 3883 | 2368 | -157 | 1 | 0 | 2525 | 1834.7073 | 1834.7073 | 1834.7073 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -179.6339 | 1655.0735 | -3550 | -400 | -2294.9265 | 57.37% | 63.26% | 95% | 0% | 2525 | -157
[5 empty] | 2019-06-11 | 41 | 3883.5 | 2321 | -147 | 1 | 0 | 2468 | 1745.4246 | 1745.4246 | 1745.4246 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -168.1922 | 1577.2323 | -3550 | -400 | -2372.7677 | 59.32% | 63.26% | 95% | 0% | 2468 | -147
[5 empty] | 2019-06-11 | 42 | 3884 | 2303 | -139 | 1 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -159.0389 | 1545.6602 | -3550 | -400 | -2404.3398 | 60.11% | 63.26% | 95% | 0% | 2442 | -139
[5 empty] | 2019-06-11 | 43 | 3884.5 | 2243 | -136 | 1 | 0 | 2379 | 1606.0181 | 1606.0181 | 1606.0181 | 1480.709 | 780 | 200 | 2460.709 | 61.52% | 95% | 0% | -155.6064 | 1450.4117 | -3550 | -400 | -2499.5883 | 62.49% | 63.26% | 95% | 0% | 2379 | -136
[5 empty] | 2019-06-11 | 44 | 3885 | 2166 | -134 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -153.3181 | 1328.9573 | -3550 | -400 | -2621.0427 | 65.53% | 63.26% | 95% | 0% | 2300 | -134
[5 empty] | 2019-06-11 | 45 | 3885.5 | 2039 | -135 | 0 | 0 | 2174 | 1284.9134 | 1284.9134 | 1284.9134 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -154.4622 | 1130.4512 | -2750 | -200 | -1819.5488 | 45.49% | 63.25% | 95% | 0% | 2174 | -135
[5 empty] | 2019-06-11 | 46 | 3886 | 1871 | -135 | 0 | 0 | 2006 | 1021.7642 | 1021.7642 | 1021.7642 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -154.4622 | 867.302 | -2750 | -200 | -2082.698 | 52.07% | 63.25% | 95% | 0% | 2006 | -135
[5 empty] | 2019-06-11 | 47 | 3886.5 | 1717 | -136 | 0 | 0 | 1853 | 782.1105 | 782.1105 | 782.1105 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -155.6064 | 626.5041 | -2750 | -200 | -2323.4959 | 58.09% | 63.25% | 95% | 0% | 1853 | -136
[5 empty] | 2019-06-11 | 48 | 3887 | 1589 | -136 | 0 | 0 | 1725 | 581.6158 | 581.6158 | 581.6158 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -155.6064 | 426.0094 | -2750 | -200 | -2523.9906 | 63.1% | 63.25% | 95% | 0% | 1725 | -136
[5 empty] | 2019-06-12 | 1 | 3887.5 | 1485 | -135 | 0 | 0 | 1620 | 417.1476 | 417.1476 | 417.1476 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -154.4622 | 262.6853 | -2750 | -200 | -2687.3147 | 67.18% | 63.24% | 95% | 0% | 1620 | -135
[5 empty] | 2019-06-12 | 2 | 3888 | 1427 | -134 | 0 | 0 | 1561 | 324.7321 | 324.7321 | 324.7321 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -153.3181 | 171.414 | -2750 | -200 | -2778.586 | 69.46% | 63.24% | 95% | 0% | 1561 | -134
[5 empty] | 2019-06-12 | 3 | 3888.5 | 1417 | -134 | 0 | 0 | 1551 | 309.0684 | 309.0684 | 309.0684 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -153.3181 | 155.7503 | -2750 | -200 | -2794.2497 | 69.86% | 63.24% | 95% | 0% | 1551 | -134
[5 empty] | 2019-06-12 | 4 | 3889 | 1433 | -134 | 0 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -153.3181 | 180.8122 | -2750 | -200 | -2769.1878 | 69.23% | 63.24% | 95% | 0% | 1567 | -134
[5 empty] | 2019-06-12 | 5 | 3889.5 | 1405 | -134 | 0 | 0 | 1539 | 290.2721 | 290.2721 | 290.2721 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -153.3181 | 136.954 | -2750 | -200 | -2813.046 | 70.33% | 63.23% | 95% | 0% | 1539 | -134
[5 empty] | 2019-06-12 | 6 | 3890 | 1387 | -134 | 0 | 0 | 1521 | 262.0775 | 262.0775 | 262.0775 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -153.3181 | 108.7594 | -2750 | -200 | -2841.2406 | 71.03% | 63.23% | 95% | 0% | 1521 | -134
[5 empty] | 2019-06-12 | 7 | 3890.5 | 1372 | -134 | 0 | 0 | 1506 | 238.582 | 238.582 | 238.582 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -153.3181 | 85.264 | -2750 | -200 | -2864.736 | 71.62% | 63.22% | 95% | 0% | 1506 | -134
[5 empty] | 2019-06-12 | 8 | 3891 | 1365 | -134 | 0 | 0 | 1499 | 227.6175 | 227.6175 | 227.6175 | 1479.1426 | 780 | 200 | 2459.1426 | 61.48% | 95% | 0% | -153.3181 | 74.2994 | -2750 | -200 | -2875.7006 | 71.89% | 63.22% | 95% | 0% | 1499 | -134
[5 empty] | 2019-06-12 | 9 | 3891.5 | 1355 | -133 | 0 | 0 | 1488 | 210.3875 | 210.3875 | 210.3875 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -152.1739 | 58.2136 | -2750 | -200 | -2891.7864 | 72.29% | 63.21% | 95% | 0% | 1488 | -133
[5 empty] | 2019-06-12 | 10 | 3892 | 1354 | -131 | 0 | 0 | 1485 | 205.6884 | 205.6884 | 205.6884 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -149.8856 | 55.8028 | -2750 | -200 | -2894.1972 | 72.35% | 63.21% | 95% | 0% | 1485 | -131
[5 empty] | 2019-06-12 | 11 | 3892.5 | 1388 | -130 | 0 | 0 | 1518 | 257.3784 | 257.3784 | 257.3784 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -148.7414 | 108.637 | -2750 | -200 | -2841.363 | 71.03% | 63.21% | 95% | 0% | 1518 | -130
[5 empty] | 2019-06-12 | 12 | 3893 | 1478 | -134 | 0 | 0 | 1612 | 404.6167 | 404.6167 | 404.6167 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -153.3181 | 251.2986 | -2750 | -200 | -2698.7014 | 67.47% | 63.21% | 95% | 0% | 1612 | -134
[5 empty] | 2019-06-12 | 13 | 3893.5 | 1685 | -144 | 0 | 0 | 1829 | 744.5177 | 744.5177 | 744.5177 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -164.7597 | 579.758 | -2750 | -200 | -2370.242 | 59.26% | 63.21% | 95% | 0% | 1829 | -144
[5 empty] | 2019-06-12 | 14 | 3894 | 1891 | -155 | 0 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -177.3455 | 907.0733 | -2750 | -200 | -2042.9267 | 51.07% | 63.2% | 95% | 0% | 2046 | -155
[5 empty] | 2019-06-12 | 15 | 3894.5 | 2103 | -174 | 1 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -199.0847 | 1247.1643 | -3550 | -400 | -2702.8357 | 67.57% | 63.2% | 95% | 0% | 2277 | -174
[5 empty] | 2019-06-12 | 16 | 3895 | 2195 | -189 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -216.2471 | 1397.6028 | -3550 | -400 | -2552.3972 | 63.81% | 63.19% | 95% | 0% | 2384 | -189
[5 empty] | 2019-06-12 | 17 | 3895.5 | 2242 | -212 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -242.5629 | 1480.9325 | -3550 | -400 | -2469.0675 | 61.73% | 63.18% | 95% | 0% | 2454 | -212
[5 empty] | 2019-06-12 | 18 | 3896 | 2224 | -242 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -276.8879 | 1465.404 | -3550 | -400 | -2484.596 | 62.11% | 63.18% | 95% | 0% | 2466 | -242
[5 empty] | 2019-06-12 | 19 | 3896.5 | 2226 | -274 | 1 | 0 | 2500 | 1795.5482 | 1795.5482 | 1795.5482 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -313.5011 | 1482.0471 | -3550 | -400 | -2467.9529 | 61.7% | 63.17% | 95% | 0% | 2500 | -274
[5 empty] | 2019-06-12 | 20 | 3897 | 2201 | -293 | 1 | 0 | 2494 | 1786.15 | 1786.15 | 1786.15 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -335.2403 | 1450.9098 | -3550 | -400 | -2499.0902 | 62.48% | 63.17% | 95% | 0% | 2494 | -293
[5 empty] | 2019-06-12 | 21 | 3897.5 | 2163 | -311 | 1 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 1477.5763 | 780 | 200 | 2457.5763 | 61.44% | 95% | 0% | -355.8352 | 1398.9875 | -3550 | -400 | -2551.0125 | 63.78% | 63.17% | 95% | 0% | 2474 | -311
[5 empty] | 2019-06-12 | 22 | 3898 | 2182 | -321 | 1 | 0 | 2503 | 1800.2473 | 1800.2473 | 1800.2473 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -367.2769 | 1432.9704 | -3550 | -400 | -2517.0296 | 62.93% | 63.16% | 95% | 0% | 2503 | -321
[5 empty] | 2019-06-12 | 23 | 3898.5 | 2200 | -318 | 1 | 0 | 2518 | 1823.7428 | 1823.7428 | 1823.7428 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -363.8444 | 1459.8984 | -3550 | -400 | -2490.1016 | 62.25% | 63.16% | 95% | 0% | 2518 | -318
[5 empty] | 2019-06-12 | 24 | 3899 | 2214 | -320 | 1 | 0 | 2534 | 1848.8046 | 1848.8046 | 1848.8046 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -366.1327 | 1482.6719 | -3550 | -400 | -2467.3281 | 61.68% | 63.15% | 95% | 0% | 2534 | -320
[5 empty] | 2019-06-12 | 25 | 3899.5 | 2225 | -318 | 1 | 0 | 2543 | 1862.9019 | 1862.9019 | 1862.9019 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -363.8444 | 1499.0575 | -3550 | -400 | -2450.9425 | 61.27% | 63.14% | 95% | 0% | 2543 | -318
[5 empty] | 2019-06-12 | 26 | 3900 | 2208 | -321 | 1 | 0 | 2529 | 1840.9728 | 1840.9728 | 1840.9728 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -367.2769 | 1473.6959 | -3550 | -400 | -2476.3041 | 61.91% | 63.14% | 95% | 0% | 2529 | -321
[5 empty] | 2019-06-12 | 27 | 3900.5 | 2189 | -317 | 1 | 0 | 2506 | 1804.9464 | 1804.9464 | 1804.9464 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -362.7002 | 1442.2462 | -3550 | -400 | -2507.7538 | 62.69% | 63.13% | 95% | 0% | 2506 | -317
[5 empty] | 2019-06-12 | 28 | 3901 | 2173 | -305 | 1 | 0 | 2478 | 1761.0882 | 1761.0882 | 1761.0882 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -348.9703 | 1412.118 | -3550 | -400 | -2537.882 | 63.45% | 63.13% | 95% | 0% | 2478 | -305
[5 empty] | 2019-06-12 | 29 | 3901.5 | 2191 | -301 | 1 | 0 | 2492 | 1783.0173 | 1783.0173 | 1783.0173 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -344.3936 | 1438.6237 | -3550 | -400 | -2511.3763 | 62.78% | 63.13% | 95% | 0% | 2492 | -301
[5 empty] | 2019-06-12 | 30 | 3902 | 2220 | -281 | 1 | 0 | 2501 | 1797.1146 | 1797.1146 | 1797.1146 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -321.5103 | 1475.6043 | -3550 | -400 | -2474.3957 | 61.86% | 63.13% | 95% | 0% | 2501 | -281
[5 empty] | 2019-06-12 | 31 | 3902.5 | 2254 | -256 | 1 | 0 | 2510 | 1811.2119 | 1811.2119 | 1811.2119 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -292.9062 | 1518.3057 | -3550 | -400 | -2431.6943 | 60.79% | 63.12% | 95% | 0% | 2510 | -256
[5 empty] | 2019-06-12 | 32 | 3903 | 2332 | -235 | 1 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -268.8787 | 1631.6159 | -3550 | -400 | -2318.3841 | 57.96% | 63.12% | 95% | 0% | 2567 | -235
[5 empty] | 2019-06-12 | 33 | 3903.5 | 2406 | -209 | 1 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -239.1304 | 1736.5497 | -3550 | -400 | -2213.4503 | 55.34% | 63.11% | 95% | 0% | 2615 | -209
[5 empty] | 2019-06-12 | 34 | 3904 | 2473 | -193 | 1 | 0 | 2666 | 2055.5647 | 2055.5647 | 2055.5647 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -220.8238 | 1834.7409 | -3550 | -400 | -2115.2591 | 52.88% | 63.1% | 95% | 0% | 2666 | -193
[5 empty] | 2019-06-12 | 35 | 3904.5 | 2509 | -189 | 1 | 0 | 2698 | 2105.6884 | 2105.6884 | 2105.6884 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -216.2471 | 1889.4412 | -3550 | -400 | -2060.5588 | 51.51% | 63.1% | 95% | 0% | 2698 | -189
[5 empty] | 2019-06-12 | 36 | 3905 | 2524 | -172 | 1 | 0 | 2696 | 2102.5556 | 2102.5556 | 2102.5556 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -196.7963 | 1905.7593 | -3550 | -400 | -2044.2407 | 51.11% | 63.1% | 95% | 0% | 2696 | -172
[5 empty] | 2019-06-12 | 37 | 3905.5 | 2526 | -157 | 1 | 0 | 2683 | 2082.1929 | 2082.1929 | 2082.1929 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -179.6339 | 1902.559 | -3550 | -400 | -2047.441 | 51.19% | 63.1% | 95% | 0% | 2683 | -157
[5 empty] | 2019-06-12 | 38 | 3906 | 2507 | -147 | 1 | 0 | 2654 | 2036.7683 | 2036.7683 | 2036.7683 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -168.1922 | 1868.5761 | -3550 | -400 | -2081.4239 | 52.04% | 63.09% | 95% | 0% | 2654 | -147
[5 empty] | 2019-06-12 | 39 | 3906.5 | 2479 | -134 | 1 | 0 | 2613 | 1972.5474 | 1972.5474 | 1972.5474 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -153.3181 | 1819.2293 | -3550 | -400 | -2130.7707 | 53.27% | 63.09% | 95% | 0% | 2613 | -134
[5 empty] | 2019-06-12 | 40 | 3907 | 2480 | -121 | 1 | 0 | 2601 | 1953.751 | 1953.751 | 1953.751 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -138.4439 | 1815.3071 | -3550 | -400 | -2134.6929 | 53.37% | 63.09% | 95% | 0% | 2601 | -121
[5 empty] | 2019-06-12 | 41 | 3907.5 | 2425 | -115 | 1 | 0 | 2540 | 1858.2028 | 1858.2028 | 1858.2028 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -131.5789 | 1726.6239 | -3550 | -400 | -2223.3761 | 55.58% | 63.09% | 95% | 0% | 2540 | -115
[5 empty] | 2019-06-12 | 42 | 3908 | 2374 | -112 | 1 | 0 | 2486 | 1773.6191 | 1773.6191 | 1773.6191 | 1476.0099 | 780 | 200 | 2456.0099 | 61.4% | 95% | 0% | -128.1465 | 1645.4727 | -3550 | -400 | -2304.5273 | 57.61% | 63.09% | 95% | 0% | 2486 | -112
[5 empty] | 2019-06-12 | 43 | 3908.5 | 2333 | -112 | 1 | 0 | 2445 | 1709.3982 | 1709.3982 | 1709.3982 | 1474.4435 | 780 | 200 | 2454.4435 | 61.36% | 95% | 0% | -128.1465 | 1581.2517 | -3550 | -400 | -2368.7483 | 59.22% | 63.09% | 95% | 0% | 2445 | -112
[5 empty] | 2019-06-12 | 44 | 3909 | 2255 | -113 | 1 | 0 | 2368 | 1588.7881 | 1588.7881 | 1588.7881 | 1474.4435 | 780 | 200 | 2454.4435 | 61.36% | 95% | 0% | -129.2906 | 1459.4975 | -3550 | -400 | -2490.5025 | 62.26% | 63.09% | 95% | 0% | 2368 | -113
[5 empty] | 2019-06-12 | 45 | 3909.5 | 2146 | -114 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 1474.4435 | 780 | 200 | 2454.4435 | 61.36% | 95% | 0% | -130.4348 | 1289.186 | -3550 | -400 | -2660.814 | 66.52% | 63.08% | 95% | 0% | 2260 | -114
[5 empty] | 2019-06-12 | 46 | 3910 | 1998 | -115 | 0 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 1474.4435 | 780 | 200 | 2454.4435 | 61.36% | 95% | 0% | -131.5789 | 1057.7863 | -2750 | -200 | -1892.2137 | 47.31% | 63.08% | 95% | 0% | 2113 | -115
[5 empty] | 2019-06-12 | 47 | 3910.5 | 1838 | -117 | 0 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 1474.4435 | 780 | 200 | 2454.4435 | 61.36% | 95% | 0% | -133.8673 | 808.0124 | -2750 | -200 | -2141.9876 | 53.55% | 63.07% | 95% | 0% | 1955 | -117
[5 empty] | 2019-06-12 | 48 | 3911 | 1713 | -120 | 0 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 1474.4435 | 780 | 200 | 2454.4435 | 61.36% | 95% | 0% | -137.2998 | 613.4834 | -2750 | -200 | -2336.5166 | 58.41% | 63.07% | 95% | 0% | 1833 | -120
[5 empty] | 2019-06-13 | 1 | 3911.5 | 1622 | -118 | 0 | 0 | 1740 | 605.1113 | 605.1113 | 605.1113 | 1474.4435 | 780 | 200 | 2454.4435 | 61.36% | 95% | 0% | -135.0114 | 470.0999 | -2750 | -200 | -2479.9001 | 62% | 63.07% | 95% | 0% | 1740 | -118
[5 empty] | 2019-06-13 | 2 | 3912 | 1577 | -116 | 1 | 0 | 1693 | 531.4922 | 531.4922 | 531.4922 | 1474.4435 | 780 | 200 | 2454.4435 | 61.36% | 95% | 0% | -132.7231 | 398.7691 | -3550 | -400 | -3551.2309 | 88.78% | 63.07% | 95% | 0% | 1693 | -116
[5 empty] | 2019-06-13 | 3 | 3912.5 | 1552 | -117 | 1 | 0 | 1669 | 493.8994 | 493.8994 | 493.8994 | 1474.4435 | 780 | 200 | 2454.4435 | 61.36% | 95% | 0% | -133.8673 | 360.0321 | -3550 | -400 | -3589.9679 | 89.75% | 63.06% | 95% | 0% | 1669 | -117
[5 empty] | 2019-06-13 | 4 | 3913 | 1539 | -118 | 1 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 1474.4435 | 780 | 200 | 2454.4435 | 61.36% | 95% | 0% | -135.0114 | 340.0916 | -3550 | -400 | -3609.9084 | 90.25% | 63.06% | 95% | 0% | 1657 | -118
[5 empty] | 2019-06-13 | 5 | 3913.5 | 1504 | -119 | 1 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 1472.8772 | 780 | 200 | 2452.8772 | 61.32% | 95% | 0% | -136.1556 | 285.6911 | -3550 | -400 | -3664.3089 | 91.61% | 63.06% | 95% | 0% | 1623 | -119
[5 empty] | 2019-06-13 | 6 | 3914 | 1485 | -121 | 1 | 0 | 1606 | 395.2185 | 395.2185 | 395.2185 | 1472.8772 | 780 | 200 | 2452.8772 | 61.32% | 95% | 0% | -138.4439 | 256.7745 | -3550 | -400 | -3693.2255 | 92.33% | 63.06% | 95% | 0% | 1606 | -121
[5 empty] | 2019-06-13 | 7 | 3914.5 | 1455 | -122 | 1 | 0 | 1577 | 349.7939 | 349.7939 | 349.7939 | 1472.8772 | 780 | 200 | 2452.8772 | 61.32% | 95% | 0% | -139.5881 | 210.2058 | -3550 | -400 | -3739.7942 | 93.49% | 63.06% | 95% | 0% | 1577 | -122
[5 empty] | 2019-06-13 | 8 | 3915 | 1465 | -122 | 1 | 0 | 1587 | 365.4575 | 365.4575 | 365.4575 | 1472.8772 | 780 | 200 | 2452.8772 | 61.32% | 95% | 0% | -139.5881 | 225.8694 | -3550 | -400 | -3724.1306 | 93.1% | 63.05% | 95% | 0% | 1587 | -122
[5 empty] | 2019-06-13 | 9 | 3915.5 | 1439 | -121 | 1 | 0 | 1560 | 323.1657 | 323.1657 | 323.1657 | 1472.8772 | 780 | 200 | 2452.8772 | 61.32% | 95% | 0% | -138.4439 | 184.7218 | -3550 | -400 | -3765.2782 | 94.13% | 63.05% | 95% | 0% | 1560 | -121
[5 empty] | 2019-06-13 | 10 | 3916 | 1448 | -119 | 1 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 1472.8772 | 780 | 200 | 2452.8772 | 61.32% | 95% | 0% | -136.1556 | 197.9746 | -3550 | -400 | -3752.0254 | 93.8% | 63.05% | 95% | 0% | 1567 | -119
[5 empty] | 2019-06-13 | 11 | 3916.5 | 1483 | -122 | 1 | 0 | 1605 | 393.6521 | 393.6521 | 393.6521 | 1472.8772 | 780 | 200 | 2452.8772 | 61.32% | 95% | 0% | -139.5881 | 254.064 | -3550 | -400 | -3695.936 | 92.4% | 63.05% | 95% | 0% | 1605 | -122
[5 empty] | 2019-06-13 | 12 | 3917 | 1551 | -128 | 1 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 1472.8772 | 780 | 200 | 2452.8772 | 61.32% | 95% | 0% | -146.4531 | 363.11 | -3550 | -400 | -3586.89 | 89.67% | 63.04% | 95% | 0% | 1679 | -128
[5 empty] | 2019-06-13 | 13 | 3917.5 | 1732 | -140 | 1 | 0 | 1872 | 811.8714 | 811.8714 | 811.8714 | 1472.8772 | 780 | 200 | 2452.8772 | 61.32% | 95% | 0% | -160.1831 | 651.6883 | -3550 | -400 | -3298.3117 | 82.46% | 63.04% | 95% | 0% | 1872 | -140
[5 empty] | 2019-06-13 | 14 | 3918 | 1903 | -160 | 1 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 1472.8772 | 780 | 200 | 2452.8772 | 61.32% | 95% | 0% | -183.0664 | 927.9806 | -3550 | -400 | -3022.0194 | 75.55% | 63.03% | 95% | 0% | 2063 | -160
[5 empty] | 2019-06-13 | 15 | 3918.5 | 2104 | -180 | 1 | 0 | 2284 | 1457.2135 | 1457.2135 | 1457.2135 | 1472.8772 | 780 | 200 | 2452.8772 | 61.32% | 95% | 0% | -205.9497 | 1251.2639 | -3550 | -400 | -2698.7361 | 67.47% | 63.03% | 95% | 0% | 2284 | -180
[5 empty] | 2019-06-13 | 16 | 3919 | 2195 | -202 | 1 | 0 | 2397 | 1634.2127 | 1634.2127 | 1634.2127 | 1471.3108 | 780 | 200 | 2451.3108 | 61.28% | 95% | 0% | -231.1213 | 1403.0914 | -3550 | -400 | -2546.9086 | 63.67% | 63.03% | 95% | 0% | 2397 | -202
[5 empty] | 2019-06-13 | 17 | 3919.5 | 2279 | -221 | 1 | 0 | 2500 | 1795.5482 | 1795.5482 | 1795.5482 | 1471.3108 | 780 | 200 | 2451.3108 | 61.28% | 95% | 0% | -252.8604 | 1542.6878 | -3550 | -400 | -2407.3122 | 60.18% | 63.03% | 95% | 0% | 2500 | -221
[5 empty] | 2019-06-13 | 18 | 3920 | 2278 | -225 | 1 | 0 | 2503 | 1800.2473 | 1800.2473 | 1800.2473 | 1471.3108 | 780 | 200 | 2451.3108 | 61.28% | 95% | 0% | -257.4371 | 1542.8102 | -3550 | -400 | -2407.1898 | 60.18% | 63.03% | 95% | 0% | 2503 | -225
[5 empty] | 2019-06-13 | 19 | 3920.5 | 2288 | -249 | 1 | 0 | 2537 | 1853.5037 | 1853.5037 | 1853.5037 | 1471.3108 | 780 | 200 | 2451.3108 | 61.28% | 95% | 0% | -284.897 | 1568.6067 | -3550 | -400 | -2381.3933 | 59.53% | 63.03% | 95% | 0% | 2537 | -249
[5 empty] | 2019-06-13 | 20 | 3921 | 2305 | -260 | 1 | 0 | 2565 | 1897.3619 | 1897.3619 | 1897.3619 | 1471.3108 | 780 | 200 | 2451.3108 | 61.28% | 95% | 0% | -297.4828 | 1599.8791 | -3550 | -400 | -2350.1209 | 58.75% | 63.03% | 95% | 0% | 2565 | -260
[5 empty] | 2019-06-13 | 21 | 3921.5 | 2279 | -277 | 1 | 0 | 2556 | 1883.2646 | 1883.2646 | 1883.2646 | 1471.3108 | 780 | 200 | 2451.3108 | 61.28% | 95% | 0% | -316.9336 | 1566.331 | -3550 | -400 | -2383.669 | 59.59% | 63.02% | 95% | 0% | 2556 | -277
[5 empty] | 2019-06-13 | 22 | 3922 | 2236 | -306 | 1 | 0 | 2542 | 1861.3355 | 1861.3355 | 1861.3355 | 1471.3108 | 780 | 200 | 2451.3108 | 61.28% | 95% | 0% | -350.1144 | 1511.2211 | -3550 | -400 | -2438.7789 | 60.97% | 63.01% | 95% | 0% | 2542 | -306
[5 empty] | 2019-06-13 | 23 | 3922.5 | 2215 | -317 | 1 | 0 | 2532 | 1845.6719 | 1845.6719 | 1845.6719 | 1471.3108 | 780 | 200 | 2451.3108 | 61.28% | 95% | 0% | -362.7002 | 1482.9717 | -3550 | -400 | -2467.0283 | 61.68% | 63.01% | 95% | 0% | 2532 | -317
[5 empty] | 2019-06-13 | 24 | 3923 | 2224 | -320 | 1 | 0 | 2544 | 1864.4683 | 1864.4683 | 1864.4683 | 1471.3108 | 780 | 200 | 2451.3108 | 61.28% | 95% | 0% | -366.1327 | 1498.3355 | -3550 | -400 | -2451.6645 | 61.29% | 63.01% | 95% | 0% | 2544 | -320
[5 empty] | 2019-06-13 | 25 | 3923.5 | 2230 | -317 | 1 | 0 | 2547 | 1869.1674 | 1869.1674 | 1869.1674 | 1471.3108 | 780 | 200 | 2451.3108 | 61.28% | 95% | 0% | -362.7002 | 1506.4671 | -3550 | -400 | -2443.5329 | 61.09% | 63.01% | 95% | 0% | 2547 | -317
[5 empty] | 2019-06-13 | 26 | 3924 | 2209 | -326 | 1 | 0 | 2535 | 1850.371 | 1850.371 | 1850.371 | 1469.7444 | 780 | 200 | 2449.7444 | 61.24% | 95% | 0% | -372.9977 | 1477.3733 | -3550 | -400 | -2472.6267 | 61.82% | 63.01% | 95% | 0% | 2535 | -326
[5 empty] | 2019-06-13 | 27 | 3924.5 | 2194 | -329 | 1 | 0 | 2523 | 1831.5746 | 1831.5746 | 1831.5746 | 1469.7444 | 780 | 200 | 2449.7444 | 61.24% | 95% | 0% | -376.4302 | 1455.1444 | -3550 | -400 | -2494.8556 | 62.37% | 63.01% | 95% | 0% | 2523 | -329
[5 empty] | 2019-06-13 | 28 | 3925 | 2192 | -321 | 1 | 0 | 2513 | 1815.911 | 1815.911 | 1815.911 | 1469.7444 | 780 | 200 | 2449.7444 | 61.24% | 95% | 0% | -367.2769 | 1448.6341 | -3550 | -400 | -2501.3659 | 62.53% | 63% | 95% | 0% | 2513 | -321
[5 empty] | 2019-06-13 | 29 | 3925.5 | 2196 | -312 | 1 | 0 | 2508 | 1808.0791 | 1808.0791 | 1808.0791 | 1469.7444 | 780 | 200 | 2449.7444 | 61.24% | 95% | 0% | -356.9794 | 1451.0997 | -3550 | -400 | -2498.9003 | 62.47% | 63% | 95% | 0% | 2508 | -312
[5 empty] | 2019-06-13 | 30 | 3926 | 2175 | -321 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 1469.7444 | 780 | 200 | 2449.7444 | 61.24% | 95% | 0% | -367.2769 | 1422.0059 | -3550 | -400 | -2527.9941 | 63.2% | 63% | 95% | 0% | 2496 | -321
[5 empty] | 2019-06-13 | 31 | 3926.5 | 2196 | -299 | 1 | 0 | 2495 | 1787.7164 | 1787.7164 | 1787.7164 | 1469.7444 | 780 | 200 | 2449.7444 | 61.24% | 95% | 0% | -342.1053 | 1445.6111 | -3550 | -400 | -2504.3889 | 62.61% | 63% | 95% | 0% | 2495 | -299
[5 empty] | 2019-06-13 | 32 | 3927 | 2260 | -279 | 1 | 0 | 2539 | 1856.6364 | 1856.6364 | 1856.6364 | 1469.7444 | 780 | 200 | 2449.7444 | 61.24% | 95% | 0% | -319.222 | 1537.4145 | -3550 | -400 | -2412.5855 | 60.31% | 62.99% | 95% | 0% | 2539 | -279
[5 empty] | 2019-06-13 | 33 | 3927.5 | 2333 | -260 | 1 | 0 | 2593 | 1941.2201 | 1941.2201 | 1941.2201 | 1469.7444 | 780 | 200 | 2449.7444 | 61.24% | 95% | 0% | -297.4828 | 1643.7373 | -3550 | -400 | -2306.2627 | 57.66% | 62.98% | 95% | 0% | 2593 | -260
[5 empty] | 2019-06-13 | 34 | 3928 | 2391 | -247 | 1 | 0 | 2638 | 2011.7065 | 2011.7065 | 2011.7065 | 1469.7444 | 780 | 200 | 2449.7444 | 61.24% | 95% | 0% | -282.6087 | 1729.0978 | -3550 | -400 | -2220.9022 | 55.52% | 62.98% | 95% | 0% | 2638 | -247
[5 empty] | 2019-06-13 | 35 | 3928.5 | 2431 | -231 | 1 | 0 | 2662 | 2049.2993 | 2049.2993 | 2049.2993 | 1469.7444 | 780 | 200 | 2449.7444 | 61.24% | 95% | 0% | -264.3021 | 1784.9972 | -3550 | -400 | -2165.0028 | 54.13% | 62.97% | 95% | 0% | 2662 | -231
[5 empty] | 2019-06-13 | 36 | 3929 | 2461 | -205 | 1 | 0 | 2666 | 2055.5647 | 2055.5647 | 2055.5647 | 1469.7444 | 780 | 200 | 2449.7444 | 61.24% | 95% | 0% | -234.5538 | 1821.0109 | -3550 | -400 | -2128.9891 | 53.22% | 62.97% | 95% | 0% | 2666 | -205
[5 empty] | 2019-06-13 | 37 | 3929.5 | 2463 | -179 | 1 | 0 | 2642 | 2017.972 | 2017.972 | 2017.972 | 1469.7444 | 780 | 200 | 2449.7444 | 61.24% | 95% | 0% | -204.8055 | 1813.1665 | -3550 | -400 | -2136.8335 | 53.42% | 62.97% | 95% | 0% | 2642 | -179
[5 empty] | 2019-06-13 | 38 | 3930 | 2480 | -157 | 1 | 0 | 2637 | 2010.1401 | 2010.1401 | 2010.1401 | 1468.1781 | 780 | 200 | 2448.1781 | 61.2% | 95% | 0% | -179.6339 | 1830.5063 | -3550 | -400 | -2119.4937 | 52.99% | 62.97% | 95% | 0% | 2637 | -157
[5 empty] | 2019-06-13 | 39 | 3930.5 | 2477 | -125 | 1 | 0 | 2602 | 1955.3174 | 1955.3174 | 1955.3174 | 1468.1781 | 780 | 200 | 2448.1781 | 61.2% | 95% | 0% | -143.0206 | 1812.2968 | -3550 | -400 | -2137.7032 | 53.44% | 62.97% | 95% | 0% | 2602 | -125
[5 empty] | 2019-06-13 | 40 | 3931 | 2476 | -100 | 1 | 0 | 2576 | 1914.5919 | 1914.5919 | 1914.5919 | 1468.1781 | 780 | 200 | 2448.1781 | 61.2% | 95% | 0% | -114.4165 | 1800.1754 | -3550 | -400 | -2149.8246 | 53.75% | 62.96% | 95% | 0% | 2576 | -100
[5 empty] | 2019-06-13 | 41 | 3931.5 | 2463 | -83 | 1 | 0 | 2546 | 1867.601 | 1867.601 | 1867.601 | 1468.1781 | 780 | 200 | 2448.1781 | 61.2% | 95% | 0% | -94.9657 | 1772.6353 | -3550 | -400 | -2177.3647 | 54.43% | 62.96% | 95% | 0% | 2546 | -83
[5 empty] | 2019-06-13 | 42 | 3932 | 2454 | -68 | 1 | 0 | 2522 | 1830.0082 | 1830.0082 | 1830.0082 | 1468.1781 | 780 | 200 | 2448.1781 | 61.2% | 95% | 0% | -77.8032 | 1752.205 | -3550 | -400 | -2197.795 | 54.94% | 62.96% | 95% | 0% | 2522 | -68
[5 empty] | 2019-06-13 | 43 | 3932.5 | 2419 | -65 | 1 | 0 | 2484 | 1770.4864 | 1770.4864 | 1770.4864 | 1468.1781 | 780 | 200 | 2448.1781 | 61.2% | 95% | 0% | -74.3707 | 1696.1157 | -3550 | -400 | -2253.8843 | 56.35% | 62.96% | 95% | 0% | 2484 | -65
[5 empty] | 2019-06-13 | 44 | 3933 | 2347 | -64 | 1 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 1468.1781 | 780 | 200 | 2448.1781 | 61.2% | 95% | 0% | -73.2265 | 1582.9153 | -3550 | -400 | -2367.0847 | 59.18% | 62.96% | 95% | 0% | 2411 | -64
[5 empty] | 2019-06-13 | 45 | 3933.5 | 2238 | -65 | 1 | 0 | 2303 | 1486.9744 | 1486.9744 | 1486.9744 | 1468.1781 | 780 | 200 | 2448.1781 | 61.2% | 95% | 0% | -74.3707 | 1412.6037 | -3550 | -400 | -2537.3963 | 63.43% | 62.96% | 95% | 0% | 2303 | -65
[5 empty] | 2019-06-13 | 46 | 3934 | 2099 | -66 | 0 | 0 | 2165 | 1270.8162 | 1270.8162 | 1270.8162 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -75.5149 | 1195.3013 | -2750 | -200 | -1754.6987 | 43.87% | 62.96% | 95% | 0% | 2165 | -66
[5 empty] | 2019-06-13 | 47 | 3934.5 | 1971 | -66 | 0 | 0 | 2037 | 1070.3215 | 1070.3215 | 1070.3215 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -75.5149 | 994.8066 | -2750 | -200 | -1955.1934 | 48.88% | 62.95% | 95% | 0% | 2037 | -66
[5 empty] | 2019-06-13 | 48 | 3935 | 1849 | -67 | 0 | 0 | 1916 | 880.7914 | 880.7914 | 880.7914 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -76.659 | 804.1324 | -2750 | -200 | -2145.8676 | 53.65% | 62.95% | 95% | 0% | 1916 | -67
[5 empty] | 2019-06-14 | 1 | 3935.5 | 1751 | -66 | 0 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -75.5149 | 650.2065 | -2750 | -200 | -2299.7935 | 57.49% | 62.94% | 95% | 0% | 1817 | -66
[5 empty] | 2019-06-14 | 2 | 3936 | 1693 | -64 | 0 | 0 | 1757 | 631.7395 | 631.7395 | 631.7395 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -73.2265 | 558.5129 | -2750 | -200 | -2391.4871 | 59.79% | 62.94% | 95% | 0% | 1757 | -64
[5 empty] | 2019-06-14 | 3 | 3936.5 | 1673 | -65 | 0 | 0 | 1738 | 601.9786 | 601.9786 | 601.9786 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -74.3707 | 527.6079 | -2750 | -200 | -2422.3921 | 60.56% | 62.94% | 95% | 0% | 1738 | -65
[5 empty] | 2019-06-14 | 4 | 3937 | 1666 | -65 | 0 | 0 | 1731 | 591.014 | 591.014 | 591.014 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -74.3707 | 516.6433 | -2750 | -200 | -2433.3567 | 60.83% | 62.93% | 95% | 0% | 1731 | -65
[5 empty] | 2019-06-14 | 5 | 3937.5 | 1646 | -65 | 0 | 0 | 1711 | 559.6867 | 559.6867 | 559.6867 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -74.3707 | 485.316 | -2750 | -200 | -2464.684 | 61.62% | 62.93% | 95% | 0% | 1711 | -65
[5 empty] | 2019-06-14 | 6 | 3938 | 1616 | -65 | 0 | 0 | 1681 | 512.6958 | 512.6958 | 512.6958 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -74.3707 | 438.3251 | -2750 | -200 | -2511.6749 | 62.79% | 62.93% | 95% | 0% | 1681 | -65
[5 empty] | 2019-06-14 | 7 | 3938.5 | 1601 | -66 | 0 | 0 | 1667 | 490.7667 | 490.7667 | 490.7667 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -75.5149 | 415.2518 | -2750 | -200 | -2534.7482 | 63.37% | 62.93% | 95% | 0% | 1667 | -66
[5 empty] | 2019-06-14 | 8 | 3939 | 1583 | -66 | 0 | 0 | 1649 | 462.5721 | 462.5721 | 462.5721 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -75.5149 | 387.0573 | -2750 | -200 | -2562.9427 | 64.07% | 62.93% | 95% | 0% | 1649 | -66
[5 empty] | 2019-06-14 | 9 | 3939.5 | 1569 | -68 | 0 | 0 | 1637 | 443.7758 | 443.7758 | 443.7758 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -77.8032 | 365.9726 | -2750 | -200 | -2584.0274 | 64.6% | 62.92% | 95% | 0% | 1637 | -68
[5 empty] | 2019-06-14 | 10 | 3940 | 1558 | -69 | 0 | 0 | 1627 | 428.1121 | 428.1121 | 428.1121 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -78.9474 | 349.1648 | -2750 | -200 | -2600.8352 | 65.02% | 62.92% | 95% | 0% | 1627 | -69
[5 empty] | 2019-06-14 | 11 | 3940.5 | 1586 | -73 | 0 | 0 | 1659 | 478.2358 | 478.2358 | 478.2358 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -83.524 | 394.7118 | -2750 | -200 | -2555.2882 | 63.88% | 62.91% | 95% | 0% | 1659 | -73
[5 empty] | 2019-06-14 | 12 | 3941 | 1649 | -82 | 0 | 0 | 1731 | 591.014 | 591.014 | 591.014 | 1466.6117 | 780 | 200 | 2446.6117 | 61.17% | 95% | 0% | -93.8215 | 497.1925 | -2750 | -200 | -2452.8075 | 61.32% | 62.91% | 95% | 0% | 1731 | -82
[5 empty] | 2019-06-14 | 13 | 3941.5 | 1831 | -96 | 0 | 0 | 1927 | 898.0214 | 898.0214 | 898.0214 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -109.8398 | 788.1816 | -2750 | -200 | -2161.8184 | 54.05% | 62.91% | 95% | 0% | 1927 | -96
[5 empty] | 2019-06-14 | 14 | 3942 | 2001 | -119 | 1 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -136.1556 | 1064.1742 | -3550 | -400 | -2885.8258 | 72.15% | 62.89% | 95% | 0% | 2120 | -119
[5 empty] | 2019-06-14 | 15 | 3942.5 | 2161 | -152 | 1 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -173.913 | 1328.725 | -3550 | -400 | -2621.275 | 65.53% | 62.89% | 95% | 0% | 2313 | -152
[5 empty] | 2019-06-14 | 16 | 3943 | 2234 | -176 | 1 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -201.373 | 1453.2024 | -3550 | -400 | -2496.7976 | 62.42% | 62.89% | 95% | 0% | 2410 | -176
[5 empty] | 2019-06-14 | 17 | 3943.5 | 2287 | -202 | 1 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -231.1213 | 1547.1969 | -3550 | -400 | -2402.8031 | 60.07% | 62.89% | 95% | 0% | 2489 | -202
[5 empty] | 2019-06-14 | 18 | 3944 | 2226 | -239 | 1 | 0 | 2465 | 1740.7255 | 1740.7255 | 1740.7255 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -273.4554 | 1467.2701 | -3550 | -400 | -2482.7299 | 62.07% | 62.89% | 95% | 0% | 2465 | -239
[5 empty] | 2019-06-14 | 19 | 3944.5 | 2217 | -250 | 1 | 0 | 2467 | 1743.8582 | 1743.8582 | 1743.8582 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -286.0412 | 1457.817 | -3550 | -400 | -2492.183 | 62.3% | 62.88% | 95% | 0% | 2467 | -250
[5 empty] | 2019-06-14 | 20 | 3945 | 2193 | -296 | 1 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -338.6728 | 1439.6455 | -3550 | -400 | -2510.3545 | 62.76% | 62.88% | 95% | 0% | 2489 | -296
[5 empty] | 2019-06-14 | 21 | 3945.5 | 2137 | -342 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -391.3043 | 1371.3502 | -3550 | -400 | -2578.6498 | 64.47% | 62.88% | 95% | 0% | 2479 | -342
[5 empty] | 2019-06-14 | 22 | 3946 | 2048 | -398 | 1 | 0 | 2446 | 1710.9646 | 1710.9646 | 1710.9646 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -455.3776 | 1255.587 | -3550 | -400 | -2694.413 | 67.36% | 62.88% | 95% | 0% | 2446 | -398
[5 empty] | 2019-06-14 | 23 | 3946.5 | 1970 | -452 | 1 | 0 | 2422 | 1673.3718 | 1673.3718 | 1673.3718 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -517.1625 | 1156.2093 | -3550 | -400 | -2793.7907 | 69.84% | 62.87% | 95% | 0% | 2422 | -452
[5 empty] | 2019-06-14 | 24 | 3947 | 1889 | -496 | 1 | 0 | 2385 | 1615.4163 | 1615.4163 | 1615.4163 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -567.5057 | 1047.9106 | -3550 | -400 | -2902.0894 | 72.55% | 62.87% | 95% | 0% | 2385 | -496
[5 empty] | 2019-06-14 | 25 | 3947.5 | 1813 | -533 | 1 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -609.8398 | 944.4883 | -3550 | -400 | -3005.5117 | 75.14% | 62.87% | 95% | 0% | 2346 | -533
[5 empty] | 2019-06-14 | 26 | 3948 | 1729 | -572 | 1 | 0 | 2301 | 1483.8417 | 1483.8417 | 1483.8417 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -654.4622 | 829.3795 | -3550 | -400 | -3120.6205 | 78.02% | 62.87% | 95% | 0% | 2301 | -572
[5 empty] | 2019-06-14 | 27 | 3948.5 | 1746 | -514 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -588.1007 | 831.5201 | -3550 | -400 | -3118.4799 | 77.96% | 62.87% | 95% | 0% | 2260 | -514
[5 empty] | 2019-06-14 | 28 | 3949 | 1741 | -495 | 1 | 0 | 2236 | 1382.028 | 1382.028 | 1382.028 | 1465.0453 | 780 | 200 | 2445.0453 | 61.13% | 95% | 0% | -566.3616 | 815.6665 | -3550 | -400 | -3134.3335 | 78.36% | 62.86% | 95% | 0% | 2236 | -495
[5 empty] | 2019-06-14 | 29 | 3949.5 | 1680 | -537 | 1 | 0 | 2217 | 1352.2671 | 1352.2671 | 1352.2671 | 1463.479 | 780 | 200 | 2443.479 | 61.09% | 95% | 0% | -614.4165 | 737.8506 | -3550 | -400 | -3212.1494 | 80.3% | 62.86% | 95% | 0% | 2217 | -537
[5 empty] | 2019-06-14 | 30 | 3950 | 1642 | -548 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1463.479 | 780 | 200 | 2443.479 | 61.09% | 95% | 0% | -627.0023 | 682.973 | -3550 | -400 | -3267.027 | 81.68% | 62.86% | 95% | 0% | 2190 | -548
[5 empty] | 2019-06-14 | 31 | 3950.5 | 1627 | -535 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 1463.479 | 780 | 200 | 2443.479 | 61.09% | 95% | 0% | -612.1281 | 653.9889 | -3550 | -400 | -3296.0111 | 82.4% | 62.86% | 95% | 0% | 2162 | -535
[5 empty] | 2019-06-14 | 32 | 3951 | 1720 | -478 | 1 | 0 | 2198 | 1322.5062 | 1322.5062 | 1322.5062 | 1463.479 | 780 | 200 | 2443.479 | 61.09% | 95% | 0% | -546.9108 | 775.5954 | -3550 | -400 | -3174.4046 | 79.36% | 62.85% | 95% | 0% | 2198 | -478
[5 empty] | 2019-06-14 | 33 | 3951.5 | 1775 | -463 | 1 | 0 | 2238 | 1385.1608 | 1385.1608 | 1385.1608 | 1463.479 | 780 | 200 | 2443.479 | 61.09% | 95% | 0% | -529.7483 | 855.4125 | -3550 | -400 | -3094.5875 | 77.36% | 62.84% | 95% | 0% | 2238 | -463
[5 empty] | 2019-06-14 | 34 | 3952 | 1890 | -397 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1463.479 | 780 | 200 | 2443.479 | 61.09% | 95% | 0% | -454.2334 | 1007.6792 | -3550 | -400 | -2942.3208 | 73.56% | 62.84% | 95% | 0% | 2287 | -397
[5 empty] | 2019-06-14 | 35 | 3952.5 | 1967 | -351 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 1463.479 | 780 | 200 | 2443.479 | 61.09% | 95% | 0% | -401.6018 | 1108.8681 | -3550 | -400 | -2841.1319 | 71.03% | 62.84% | 95% | 0% | 2318 | -351
[5 empty] | 2019-06-14 | 36 | 3953 | 2017 | -325 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 1463.479 | 780 | 200 | 2443.479 | 61.09% | 95% | 0% | -371.8535 | 1176.2091 | -3550 | -400 | -2773.7909 | 69.34% | 62.84% | 95% | 0% | 2342 | -325
[5 empty] | 2019-06-14 | 37 | 3953.5 | 2099 | -272 | 1 | 0 | 2371 | 1593.4872 | 1593.4872 | 1593.4872 | 1463.479 | 780 | 200 | 2443.479 | 61.09% | 95% | 0% | -311.2128 | 1282.2744 | -3550 | -400 | -2667.7256 | 66.69% | 62.84% | 95% | 0% | 2371 | -272
[5 empty] | 2019-06-14 | 38 | 3954 | 2148 | -230 | 1 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -263.1579 | 1341.2939 | -3550 | -400 | -2608.7061 | 65.22% | 62.84% | 95% | 0% | 2378 | -230
[5 empty] | 2019-06-14 | 39 | 3954.5 | 2177 | -195 | 1 | 0 | 2372 | 1595.0536 | 1595.0536 | 1595.0536 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -223.1121 | 1371.9415 | -3550 | -400 | -2578.0585 | 64.45% | 62.83% | 95% | 0% | 2372 | -195
[5 empty] | 2019-06-14 | 40 | 3955 | 2199 | -159 | 1 | 0 | 2358 | 1573.1245 | 1573.1245 | 1573.1245 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -181.9222 | 1391.2023 | -3550 | -400 | -2558.7977 | 63.97% | 62.83% | 95% | 0% | 2358 | -159
[5 empty] | 2019-06-14 | 41 | 3955.5 | 2207 | -123 | 1 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -140.7323 | 1388.534 | -3550 | -400 | -2561.466 | 64.04% | 62.83% | 95% | 0% | 2330 | -123
[5 empty] | 2019-06-14 | 42 | 3956 | 2209 | -96 | 1 | 0 | 2305 | 1490.1072 | 1490.1072 | 1490.1072 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -109.8398 | 1380.2674 | -3550 | -400 | -2569.7326 | 64.24% | 62.83% | 95% | 0% | 2305 | -96
[5 empty] | 2019-06-14 | 43 | 3956.5 | 2201 | -86 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -98.3982 | 1363.5144 | -3550 | -400 | -2586.4856 | 64.66% | 62.83% | 95% | 0% | 2287 | -86
[5 empty] | 2019-06-14 | 44 | 3957 | 2158 | -85 | 1 | 0 | 2243 | 1392.9926 | 1392.9926 | 1392.9926 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -97.254 | 1295.7386 | -3550 | -400 | -2654.2614 | 66.36% | 62.82% | 95% | 0% | 2243 | -85
[5 empty] | 2019-06-14 | 45 | 3957.5 | 2105 | -87 | 1 | 0 | 2192 | 1313.108 | 1313.108 | 1313.108 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -99.5423 | 1213.5657 | -3550 | -400 | -2736.4343 | 68.41% | 62.82% | 95% | 0% | 2192 | -87
[5 empty] | 2019-06-14 | 46 | 3958 | 2019 | -88 | 0 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -100.6865 | 1079.2805 | -2750 | -200 | -1870.7195 | 46.77% | 62.82% | 95% | 0% | 2107 | -88
[5 empty] | 2019-06-14 | 47 | 3958.5 | 1884 | -89 | 0 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -101.8307 | 868.2435 | -2750 | -200 | -2081.7565 | 52.04% | 62.82% | 95% | 0% | 1973 | -89
[5 empty] | 2019-06-14 | 48 | 3959 | 1773 | -89 | 0 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -101.8307 | 694.3771 | -2750 | -200 | -2255.6229 | 56.39% | 62.82% | 95% | 0% | 1862 | -89
[5 empty] | 2019-06-15 | 1 | 3959.5 | 1668 | -89 | 0 | 0 | 1757 | 631.7395 | 631.7395 | 631.7395 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -101.8307 | 529.9088 | -2750 | -200 | -2420.0912 | 60.5% | 62.81% | 95% | 0% | 1757 | -89
[5 empty] | 2019-06-15 | 2 | 3960 | 1594 | -88 | 0 | 0 | 1682 | 514.2622 | 514.2622 | 514.2622 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -100.6865 | 413.5757 | -2750 | -200 | -2536.4243 | 63.41% | 62.81% | 95% | 0% | 1682 | -88
[5 empty] | 2019-06-15 | 3 | 3960.5 | 1555 | -88 | 0 | 0 | 1643 | 453.1739 | 453.1739 | 453.1739 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -100.6865 | 352.4875 | -2750 | -200 | -2597.5125 | 64.94% | 62.81% | 95% | 0% | 1643 | -88
[5 empty] | 2019-06-15 | 4 | 3961 | 1540 | -89 | 0 | 0 | 1629 | 431.2448 | 431.2448 | 431.2448 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -101.8307 | 329.4142 | -2750 | -200 | -2620.5858 | 65.51% | 62.8% | 95% | 0% | 1629 | -89
[5 empty] | 2019-06-15 | 5 | 3961.5 | 1508 | -90 | 0 | 0 | 1598 | 382.6876 | 382.6876 | 382.6876 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -102.9748 | 279.7127 | -2750 | -200 | -2670.2873 | 66.76% | 62.8% | 95% | 0% | 1598 | -90
[5 empty] | 2019-06-15 | 6 | 3962 | 1468 | -90 | 0 | 0 | 1558 | 320.033 | 320.033 | 320.033 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -102.9748 | 217.0581 | -2750 | -200 | -2732.9419 | 68.32% | 62.79% | 95% | 0% | 1558 | -90
[5 empty] | 2019-06-15 | 7 | 3962.5 | 1440 | -91 | 0 | 0 | 1531 | 277.7411 | 277.7411 | 277.7411 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -104.119 | 173.6221 | -2750 | -200 | -2776.3779 | 69.41% | 62.79% | 95% | 0% | 1531 | -91
[5 empty] | 2019-06-15 | 8 | 3963 | 1425 | -91 | 0 | 0 | 1516 | 254.2457 | 254.2457 | 254.2457 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -104.119 | 150.1267 | -2750 | -200 | -2799.8733 | 70% | 62.79% | 95% | 0% | 1516 | -91
[5 empty] | 2019-06-15 | 9 | 3963.5 | 1414 | -89 | 0 | 0 | 1503 | 233.8829 | 233.8829 | 233.8829 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -101.8307 | 132.0523 | -2750 | -200 | -2817.9477 | 70.45% | 62.79% | 95% | 0% | 1503 | -89
[5 empty] | 2019-06-15 | 10 | 3964 | 1379 | -88 | 0 | 0 | 1467 | 177.4938 | 177.4938 | 177.4938 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -100.6865 | 76.8073 | -2750 | -200 | -2873.1927 | 71.83% | 62.79% | 95% | 0% | 1467 | -88
[5 empty] | 2019-06-15 | 11 | 3964.5 | 1371 | -91 | 0 | 0 | 1462 | 169.662 | 169.662 | 169.662 | 1461.9126 | 780 | 200 | 2441.9126 | 61.05% | 95% | 0% | -104.119 | 65.543 | -2750 | -200 | -2884.457 | 72.11% | 62.79% | 95% | 0% | 1462 | -91
[5 empty] | 2019-06-15 | 12 | 3965 | 1398 | -102 | 0 | 0 | 1500 | 229.1838 | 229.1838 | 229.1838 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -116.7048 | 112.479 | -2750 | -200 | -2837.521 | 70.94% | 62.79% | 95% | 0% | 1500 | -102
[5 empty] | 2019-06-15 | 13 | 3965.5 | 1482 | -123 | 1 | 0 | 1605 | 393.6521 | 393.6521 | 393.6521 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -140.7323 | 252.9198 | -3550 | -400 | -3697.0802 | 92.43% | 62.78% | 95% | 0% | 1605 | -123
[5 empty] | 2019-06-15 | 14 | 3966 | 1489 | -152 | 1 | 0 | 1641 | 450.0412 | 450.0412 | 450.0412 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -173.913 | 276.1282 | -3550 | -400 | -3673.8718 | 91.85% | 62.78% | 95% | 0% | 1641 | -152
[5 empty] | 2019-06-15 | 15 | 3966.5 | 1565 | -187 | 1 | 0 | 1752 | 623.9077 | 623.9077 | 623.9077 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -213.9588 | 409.9489 | -3550 | -400 | -3540.0511 | 88.5% | 62.78% | 95% | 0% | 1752 | -187
[5 empty] | 2019-06-15 | 16 | 3967 | 1590 | -242 | 1 | 0 | 1832 | 749.2168 | 749.2168 | 749.2168 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -276.8879 | 472.3289 | -3550 | -400 | -3477.6711 | 86.94% | 62.78% | 95% | 0% | 1832 | -242
[5 empty] | 2019-06-15 | 17 | 3967.5 | 1626 | -299 | 1 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -342.1053 | 552.7834 | -3550 | -400 | -3397.2166 | 84.93% | 62.78% | 95% | 0% | 1925 | -299
[5 empty] | 2019-06-15 | 18 | 3968 | 1621 | -349 | 1 | 0 | 1970 | 965.3751 | 965.3751 | 965.3751 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -399.3135 | 566.0616 | -3550 | -400 | -3383.9384 | 84.6% | 62.78% | 95% | 0% | 1970 | -349
[5 empty] | 2019-06-15 | 19 | 3968.5 | 1616 | -379 | 1 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -433.6384 | 570.8958 | -3550 | -400 | -3379.1042 | 84.48% | 62.77% | 95% | 0% | 1995 | -379
[5 empty] | 2019-06-15 | 20 | 3969 | 1592 | -411 | 1 | 0 | 2003 | 1017.0651 | 1017.0651 | 1017.0651 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -470.2517 | 546.8134 | -3550 | -400 | -3403.1866 | 85.08% | 62.77% | 95% | 0% | 2003 | -411
[5 empty] | 2019-06-15 | 21 | 3969.5 | 1565 | -450 | 1 | 0 | 2015 | 1035.8615 | 1035.8615 | 1035.8615 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -514.8741 | 520.9874 | -3550 | -400 | -3429.0126 | 85.73% | 62.77% | 95% | 0% | 2015 | -450
[5 empty] | 2019-06-15 | 22 | 3970 | 1605 | -425 | 1 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -486.27 | 573.0869 | -3550 | -400 | -3376.9131 | 84.42% | 62.76% | 95% | 0% | 2030 | -425
[5 empty] | 2019-06-15 | 23 | 3970.5 | 1519 | -479 | 1 | 0 | 1998 | 1009.2333 | 1009.2333 | 1009.2333 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -548.0549 | 461.1784 | -3550 | -400 | -3488.8216 | 87.22% | 62.76% | 95% | 0% | 1998 | -479
[5 empty] | 2019-06-15 | 24 | 3971 | 1574 | -412 | 1 | 0 | 1986 | 990.4369 | 990.4369 | 990.4369 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -471.3959 | 519.0411 | -3550 | -400 | -3430.9589 | 85.77% | 62.76% | 95% | 0% | 1986 | -412
[5 empty] | 2019-06-15 | 25 | 3971.5 | 1573 | -418 | 1 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -478.2609 | 520.0079 | -3550 | -400 | -3429.9921 | 85.75% | 62.76% | 95% | 0% | 1991 | -418
[5 empty] | 2019-06-15 | 26 | 3972 | 1538 | -432 | 1 | 0 | 1970 | 965.3751 | 965.3751 | 965.3751 | 1460.3462 | 780 | 200 | 2440.3462 | 61.01% | 95% | 0% | -494.2792 | 471.0959 | -3550 | -400 | -3478.9041 | 86.97% | 62.76% | 95% | 0% | 1970 | -432
[5 empty] | 2019-06-15 | 27 | 3972.5 | 1526 | -436 | 1 | 0 | 1962 | 952.8442 | 952.8442 | 952.8442 | 1458.7799 | 780 | 200 | 2438.7799 | 60.97% | 95% | 0% | -498.8558 | 453.9884 | -3550 | -400 | -3496.0116 | 87.4% | 62.75% | 95% | 0% | 1962 | -436
[5 empty] | 2019-06-15 | 28 | 3973 | 1502 | -422 | 1 | 0 | 1924 | 893.3223 | 893.3223 | 893.3223 | 1458.7799 | 780 | 200 | 2438.7799 | 60.97% | 95% | 0% | -482.8375 | 410.4848 | -3550 | -400 | -3539.5152 | 88.49% | 62.75% | 95% | 0% | 1924 | -422
[5 empty] | 2019-06-15 | 29 | 3973.5 | 1496 | -402 | 1 | 0 | 1898 | 852.5969 | 852.5969 | 852.5969 | 1458.7799 | 780 | 200 | 2438.7799 | 60.97% | 95% | 0% | -459.9542 | 392.6426 | -3550 | -400 | -3557.3574 | 88.93% | 62.74% | 95% | 0% | 1898 | -402
[5 empty] | 2019-06-15 | 30 | 3974 | 1416 | -440 | 1 | 0 | 1856 | 786.8096 | 786.8096 | 786.8096 | 1458.7799 | 780 | 200 | 2438.7799 | 60.97% | 95% | 0% | -503.4325 | 283.3771 | -3550 | -400 | -3666.6229 | 91.67% | 62.74% | 95% | 0% | 1856 | -440
[5 empty] | 2019-06-15 | 31 | 3974.5 | 1359 | -478 | 1 | 0 | 1837 | 757.0486 | 757.0486 | 757.0486 | 1458.7799 | 780 | 200 | 2438.7799 | 60.97% | 95% | 0% | -546.9108 | 210.1379 | -3550 | -400 | -3739.8621 | 93.5% | 62.74% | 95% | 0% | 1837 | -478
[5 empty] | 2019-06-15 | 32 | 3975 | 1403 | -435 | 1 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 1458.7799 | 780 | 200 | 2438.7799 | 60.97% | 95% | 0% | -497.7117 | 260.9033 | -3550 | -400 | -3689.0967 | 92.23% | 62.74% | 95% | 0% | 1838 | -435
[5 empty] | 2019-06-15 | 33 | 3975.5 | 1453 | -421 | 1 | 0 | 1874 | 815.0041 | 815.0041 | 815.0041 | 1457.2135 | 780 | 200 | 2437.2135 | 60.93% | 95% | 0% | -481.6934 | 333.3108 | -3550 | -400 | -3616.6892 | 90.42% | 62.73% | 95% | 0% | 1874 | -421
[5 empty] | 2019-06-15 | 34 | 3976 | 1547 | -396 | 1 | 0 | 1943 | 923.0833 | 923.0833 | 923.0833 | 1457.2135 | 780 | 200 | 2437.2135 | 60.93% | 95% | 0% | -453.0892 | 469.994 | -3550 | -400 | -3480.006 | 87% | 62.73% | 95% | 0% | 1943 | -396
[5 empty] | 2019-06-15 | 35 | 3976.5 | 1665 | -348 | 1 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 1457.2135 | 780 | 200 | 2437.2135 | 60.93% | 95% | 0% | -398.1693 | 634.5594 | -3550 | -400 | -3315.4406 | 82.89% | 62.73% | 95% | 0% | 2013 | -348
[5 empty] | 2019-06-15 | 36 | 3977 | 1768 | -300 | 1 | 0 | 2068 | 1118.8788 | 1118.8788 | 1118.8788 | 1457.2135 | 780 | 200 | 2437.2135 | 60.93% | 95% | 0% | -343.2494 | 775.6294 | -3550 | -400 | -3174.3706 | 79.36% | 62.73% | 95% | 0% | 2068 | -300
[5 empty] | 2019-06-15 | 37 | 3977.5 | 1878 | -239 | 1 | 0 | 2117 | 1195.6307 | 1195.6307 | 1195.6307 | 1457.2135 | 780 | 200 | 2437.2135 | 60.93% | 95% | 0% | -273.4554 | 922.1753 | -3550 | -400 | -3027.8247 | 75.7% | 62.72% | 95% | 0% | 2117 | -239
[5 empty] | 2019-06-15 | 38 | 3978 | 1925 | -216 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1457.2135 | 780 | 200 | 2437.2135 | 60.93% | 95% | 0% | -247.1396 | 986.0838 | -3550 | -400 | -2963.9162 | 74.1% | 62.72% | 95% | 0% | 2141 | -216
[5 empty] | 2019-06-15 | 39 | 3978.5 | 1975 | -179 | 1 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 1457.2135 | 780 | 200 | 2437.2135 | 60.93% | 95% | 0% | -204.8055 | 1048.7807 | -3550 | -400 | -2901.2193 | 72.53% | 62.72% | 95% | 0% | 2154 | -179
[5 empty] | 2019-06-15 | 40 | 3979 | 2004 | -142 | 1 | 0 | 2146 | 1241.0552 | 1241.0552 | 1241.0552 | 1457.2135 | 780 | 200 | 2437.2135 | 60.93% | 95% | 0% | -162.4714 | 1078.5838 | -3550 | -400 | -2871.4162 | 71.79% | 62.72% | 95% | 0% | 2146 | -142
[5 empty] | 2019-06-15 | 41 | 3979.5 | 2017 | -109 | 1 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 1457.2135 | 780 | 200 | 2437.2135 | 60.93% | 95% | 0% | -124.714 | 1085.014 | -3550 | -400 | -2864.986 | 71.62% | 62.71% | 95% | 0% | 2126 | -109
[5 empty] | 2019-06-15 | 42 | 3980 | 2017 | -89 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 1457.2135 | 780 | 200 | 2437.2135 | 60.93% | 95% | 0% | -101.8307 | 1076.57 | -3550 | -400 | -2873.43 | 71.84% | 62.71% | 95% | 0% | 2106 | -89
[5 empty] | 2019-06-15 | 43 | 3980.5 | 1998 | -79 | 1 | 0 | 2077 | 1132.9761 | 1132.9761 | 1132.9761 | 1457.2135 | 780 | 200 | 2437.2135 | 60.93% | 95% | 0% | -90.389 | 1042.5871 | -3550 | -400 | -2907.4129 | 72.69% | 62.71% | 95% | 0% | 2077 | -79
[5 empty] | 2019-06-15 | 44 | 3981 | 1999 | -77 | 1 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -88.1007 | 1043.309 | -3550 | -400 | -2906.691 | 72.67% | 62.71% | 95% | 0% | 2076 | -77
[5 empty] | 2019-06-15 | 45 | 3981.5 | 1974 | -77 | 1 | 0 | 2051 | 1092.2506 | 1092.2506 | 1092.2506 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -88.1007 | 1004.1499 | -3550 | -400 | -2945.8501 | 73.65% | 62.7% | 95% | 0% | 2051 | -77
[5 empty] | 2019-06-15 | 46 | 3982 | 1895 | -76 | 0 | 0 | 1971 | 966.9415 | 966.9415 | 966.9415 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -86.9565 | 879.9849 | -2750 | -200 | -2070.0151 | 51.75% | 62.7% | 95% | 0% | 1971 | -76
[5 empty] | 2019-06-15 | 47 | 3982.5 | 1789 | -75 | 0 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -85.8124 | 713.5281 | -2750 | -200 | -2236.4719 | 55.91% | 62.7% | 95% | 0% | 1864 | -75
[5 empty] | 2019-06-15 | 48 | 3983 | 1678 | -75 | 0 | 0 | 1753 | 625.474 | 625.474 | 625.474 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -85.8124 | 539.6617 | -2750 | -200 | -2410.3383 | 60.26% | 62.7% | 95% | 0% | 1753 | -75
[5 empty] | 2019-06-16 | 1 | 3983.5 | 1592 | -74 | 0 | 0 | 1666 | 489.2003 | 489.2003 | 489.2003 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -84.6682 | 404.5321 | -2750 | -200 | -2545.4679 | 63.64% | 62.69% | 95% | 0% | 1666 | -74
[5 empty] | 2019-06-16 | 2 | 3984 | 1526 | -73 | 0 | 0 | 1599 | 384.2539 | 384.2539 | 384.2539 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -83.524 | 300.7299 | -2750 | -200 | -2649.2701 | 66.23% | 62.68% | 95% | 0% | 1599 | -73
[5 empty] | 2019-06-16 | 3 | 3984.5 | 1492 | -73 | 0 | 0 | 1565 | 330.9975 | 330.9975 | 330.9975 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -83.524 | 247.4735 | -2750 | -200 | -2702.5265 | 67.56% | 62.68% | 95% | 0% | 1565 | -73
[5 empty] | 2019-06-16 | 4 | 3985 | 1477 | -72 | 0 | 0 | 1549 | 305.9357 | 305.9357 | 305.9357 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -82.3799 | 223.5558 | -2750 | -200 | -2726.4442 | 68.16% | 62.67% | 95% | 0% | 1549 | -72
[5 empty] | 2019-06-16 | 5 | 3985.5 | 1449 | -71 | 0 | 0 | 1520 | 260.5111 | 260.5111 | 260.5111 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -81.2357 | 179.2754 | -2750 | -200 | -2770.7246 | 69.27% | 62.67% | 95% | 0% | 1520 | -71
[5 empty] | 2019-06-16 | 6 | 3986 | 1419 | -70 | 0 | 0 | 1489 | 211.9538 | 211.9538 | 211.9538 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -80.0915 | 131.8623 | -2750 | -200 | -2818.1377 | 70.45% | 62.67% | 95% | 0% | 1489 | -70
[5 empty] | 2019-06-16 | 7 | 3986.5 | 1397 | -69 | 0 | 0 | 1466 | 175.9275 | 175.9275 | 175.9275 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -78.9474 | 96.9801 | -2750 | -200 | -2853.0199 | 71.33% | 62.67% | 95% | 0% | 1466 | -69
[5 empty] | 2019-06-16 | 8 | 3987 | 1397 | -69 | 0 | 0 | 1466 | 175.9275 | 175.9275 | 175.9275 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -78.9474 | 96.9801 | -2750 | -200 | -2853.0199 | 71.33% | 62.66% | 95% | 0% | 1466 | -69
[5 empty] | 2019-06-16 | 9 | 3987.5 | 1362 | -70 | 0 | 0 | 1432 | 122.6711 | 122.6711 | 122.6711 | 1455.6472 | 780 | 200 | 2435.6472 | 60.89% | 95% | 0% | -80.0915 | 42.5795 | -2750 | -200 | -2907.4205 | 72.69% | 62.66% | 95% | 0% | 1432 | -70
[5 empty] | 2019-06-16 | 10 | 3988 | 1322 | -72 | 0 | 0 | 1394 | 63.1492 | 63.1492 | 63.1492 | 1454.0808 | 780 | 200 | 2434.0808 | 60.85% | 95% | 0% | -82.3799 | -19.2306 | -2750 | -200 | -2969.2306 | 74.23% | 62.66% | 95% | 0% | 1394 | -72
[5 empty] | 2019-06-16 | 11 | 3988.5 | 1308 | -82 | 0 | 0 | 1390 | 56.8838 | 56.8838 | 56.8838 | 1454.0808 | 780 | 200 | 2434.0808 | 60.85% | 95% | 0% | -93.8215 | -36.9378 | -2750 | -200 | -2986.9378 | 74.67% | 62.65% | 95% | 0% | 1390 | -82
[5 empty] | 2019-06-16 | 12 | 3989 | 1283 | -104 | 0 | 0 | 1387 | 52.1847 | 52.1847 | 52.1847 | 1454.0808 | 780 | 200 | 2434.0808 | 60.85% | 95% | 0% | -118.9931 | -66.8085 | -2750 | -200 | -3016.8085 | 75.42% | 62.65% | 95% | 0% | 1387 | -104
[5 empty] | 2019-06-16 | 13 | 3989.5 | 1315 | -126 | 1 | 0 | 1441 | 136.7683 | 136.7683 | 136.7683 | 1454.0808 | 780 | 200 | 2434.0808 | 60.85% | 95% | 0% | -144.1648 | -7.3964 | -3550 | -400 | -3957.3964 | 98.93% | 62.65% | 95% | 0% | 1441 | -126
[5 empty] | 2019-06-16 | 14 | 3990 | 1307 | -161 | 1 | 0 | 1468 | 179.0602 | 179.0602 | 179.0602 | 1454.0808 | 780 | 200 | 2434.0808 | 60.85% | 95% | 0% | -184.2105 | -5.1503 | -3550 | -400 | -3955.1503 | 98.88% | 62.65% | 95% | 0% | 1468 | -161
[5 empty] | 2019-06-16 | 15 | 3990.5 | 1310 | -203 | 1 | 0 | 1513 | 249.5466 | 249.5466 | 249.5466 | 1454.0808 | 780 | 200 | 2434.0808 | 60.85% | 95% | 0% | -232.2654 | 17.2811 | -3550 | -400 | -3932.7189 | 98.32% | 62.64% | 95% | 0% | 1513 | -203
[5 empty] | 2019-06-16 | 16 | 3991 | 1344 | -234 | 1 | 0 | 1578 | 351.3603 | 351.3603 | 351.3603 | 1454.0808 | 780 | 200 | 2434.0808 | 60.85% | 95% | 0% | -267.7346 | 83.6257 | -3550 | -400 | -3866.3743 | 96.66% | 62.63% | 95% | 0% | 1578 | -234
[5 empty] | 2019-06-16 | 17 | 3991.5 | 1385 | -278 | 1 | 0 | 1663 | 484.5012 | 484.5012 | 484.5012 | 1454.0808 | 780 | 200 | 2434.0808 | 60.85% | 95% | 0% | -318.0778 | 166.4234 | -3550 | -400 | -3783.5766 | 94.59% | 62.63% | 95% | 0% | 1663 | -278
[5 empty] | 2019-06-16 | 18 | 3992 | 1433 | -311 | 1 | 0 | 1744 | 611.3768 | 611.3768 | 611.3768 | 1452.5144 | 780 | 200 | 2432.5144 | 60.81% | 95% | 0% | -355.8352 | 255.5415 | -3550 | -400 | -3694.4585 | 92.36% | 62.63% | 95% | 0% | 1744 | -311
[5 empty] | 2019-06-16 | 19 | 3992.5 | 1473 | -339 | 1 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 1452.5144 | 780 | 200 | 2432.5144 | 60.81% | 95% | 0% | -387.8719 | 330.0177 | -3550 | -400 | -3619.9823 | 90.5% | 62.63% | 95% | 0% | 1812 | -339
[5 empty] | 2019-06-16 | 20 | 3993 | 1462 | -376 | 1 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 1452.5144 | 780 | 200 | 2432.5144 | 60.81% | 95% | 0% | -430.2059 | 328.4091 | -3550 | -400 | -3621.5909 | 90.54% | 62.63% | 95% | 0% | 1838 | -376
[5 empty] | 2019-06-16 | 21 | 3993.5 | 1445 | -425 | 1 | 0 | 1870 | 808.7387 | 808.7387 | 808.7387 | 1452.5144 | 780 | 200 | 2432.5144 | 60.81% | 95% | 0% | -486.27 | 322.4686 | -3550 | -400 | -3627.5314 | 90.69% | 62.62% | 95% | 0% | 1870 | -425
[5 empty] | 2019-06-16 | 22 | 3994 | 1401 | -462 | 1 | 0 | 1863 | 797.7741 | 797.7741 | 797.7741 | 1452.5144 | 780 | 200 | 2432.5144 | 60.81% | 95% | 0% | -528.6041 | 269.17 | -3550 | -400 | -3680.83 | 92.02% | 62.62% | 95% | 0% | 1863 | -462
[5 empty] | 2019-06-16 | 23 | 3994.5 | 1381 | -492 | 1 | 0 | 1873 | 813.4378 | 813.4378 | 813.4378 | 1452.5144 | 780 | 200 | 2432.5144 | 60.81% | 95% | 0% | -562.9291 | 250.5087 | -3550 | -400 | -3699.4913 | 92.49% | 62.62% | 95% | 0% | 1873 | -492
[5 empty] | 2019-06-16 | 24 | 3995 | 1296 | -565 | 1 | 0 | 1861 | 794.6414 | 794.6414 | 794.6414 | 1452.5144 | 780 | 200 | 2432.5144 | 60.81% | 95% | 0% | -646.4531 | 148.1883 | -3550 | -400 | -3801.8117 | 95.05% | 62.62% | 95% | 0% | 1861 | -565
[5 empty] | 2019-06-16 | 25 | 3995.5 | 1337 | -537 | 1 | 0 | 1874 | 815.0041 | 815.0041 | 815.0041 | 1452.5144 | 780 | 200 | 2432.5144 | 60.81% | 95% | 0% | -614.4165 | 200.5876 | -3550 | -400 | -3749.4124 | 93.74% | 62.62% | 95% | 0% | 1874 | -537
[5 empty] | 2019-06-16 | 26 | 3996 | 1238 | -614 | 1 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 1452.5144 | 780 | 200 | 2432.5144 | 60.81% | 95% | 0% | -702.5172 | 78.0269 | -3550 | -400 | -3871.9731 | 96.8% | 62.61% | 95% | 0% | 1852 | -614
[5 empty] | 2019-06-16 | 27 | 3996.5 | 1214 | -603 | 1 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 1452.5144 | 780 | 200 | 2432.5144 | 60.81% | 95% | 0% | -689.9314 | 35.79 | -3550 | -400 | -3914.21 | 97.86% | 62.61% | 95% | 0% | 1817 | -603
[5 empty] | 2019-06-16 | 28 | 3997 | 1242 | -546 | 1 | 0 | 1788 | 680.2968 | 680.2968 | 680.2968 | 1452.5144 | 780 | 200 | 2432.5144 | 60.81% | 95% | 0% | -624.714 | 55.5828 | -3550 | -400 | -3894.4172 | 97.36% | 62.61% | 95% | 0% | 1788 | -546
[5 empty] | 2019-06-16 | 29 | 3997.5 | 1236 | -555 | 1 | 0 | 1791 | 684.9959 | 684.9959 | 684.9959 | 1452.5144 | 780 | 200 | 2432.5144 | 60.81% | 95% | 0% | -635.0114 | 49.9844 | -3550 | -400 | -3900.0156 | 97.5% | 62.61% | 95% | 0% | 1791 | -555
[5 empty] | 2019-06-16 | 30 | 3998 | 1275 | -511 | 1 | 0 | 1786 | 677.1641 | 677.1641 | 677.1641 | 1450.9481 | 780 | 200 | 2430.9481 | 60.77% | 95% | 0% | -584.6682 | 92.4959 | -3550 | -400 | -3857.5041 | 96.44% | 62.6% | 95% | 0% | 1786 | -511
[5 empty] | 2019-06-16 | 31 | 3998.5 | 1278 | -508 | 1 | 0 | 1786 | 677.1641 | 677.1641 | 677.1641 | 1450.9481 | 780 | 200 | 2430.9481 | 60.77% | 95% | 0% | -581.2357 | 95.9284 | -3550 | -400 | -3854.0716 | 96.35% | 62.6% | 95% | 0% | 1786 | -508
[5 empty] | 2019-06-16 | 32 | 3999 | 1375 | -437 | 1 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 1450.9481 | 780 | 200 | 2430.9481 | 60.77% | 95% | 0% | -500 | 217.8895 | -3550 | -400 | -3732.1105 | 93.3% | 62.6% | 95% | 0% | 1812 | -437
[5 empty] | 2019-06-16 | 33 | 3999.5 | 1419 | -433 | 1 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 1450.9481 | 780 | 200 | 2430.9481 | 60.77% | 95% | 0% | -495.4233 | 285.1208 | -3550 | -400 | -3664.8792 | 91.62% | 62.6% | 95% | 0% | 1852 | -433
[5 empty] | 2019-06-16 | 34 | 4000 | 1538 | -380 | 1 | 0 | 1918 | 883.9242 | 883.9242 | 883.9242 | 1450.9481 | 780 | 200 | 2430.9481 | 60.77% | 95% | 0% | -434.7826 | 449.1415 | -3550 | -400 | -3500.8585 | 87.52% | 62.6% | 95% | 0% | 1918 | -380
[5 empty] | 2019-06-16 | 35 | 4000.5 | 1652 | -333 | 1 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 1450.9481 | 780 | 200 | 2430.9481 | 60.77% | 95% | 0% | -381.0069 | 607.8637 | -3550 | -400 | -3342.1363 | 83.55% | 62.59% | 95% | 0% | 1985 | -333
[5 empty] | 2019-06-16 | 36 | 4001 | 1769 | -290 | 1 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 1450.9481 | 780 | 200 | 2430.9481 | 60.77% | 95% | 0% | -331.8078 | 772.9738 | -3550 | -400 | -3177.0262 | 79.43% | 62.59% | 95% | 0% | 2059 | -290
[5 empty] | 2019-06-16 | 37 | 4001.5 | 1862 | -247 | 1 | 0 | 2109 | 1183.0998 | 1183.0998 | 1183.0998 | 1450.9481 | 780 | 200 | 2430.9481 | 60.77% | 95% | 0% | -282.6087 | 900.4911 | -3550 | -400 | -3049.5089 | 76.24% | 62.58% | 95% | 0% | 2109 | -247
[5 empty] | 2019-06-16 | 38 | 4002 | 1921 | -205 | 1 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 1450.9481 | 780 | 200 | 2430.9481 | 60.77% | 95% | 0% | -234.5538 | 975.1742 | -3550 | -400 | -2974.8258 | 74.37% | 62.58% | 95% | 0% | 2126 | -205
[5 empty] | 2019-06-16 | 39 | 4002.5 | 1933 | -183 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1450.9481 | 780 | 200 | 2430.9481 | 60.77% | 95% | 0% | -209.3822 | 984.6822 | -3550 | -400 | -2965.3178 | 74.13% | 62.57% | 95% | 0% | 2116 | -183
[5 empty] | 2019-06-16 | 40 | 4003 | 1957 | -149 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 1450.9481 | 780 | 200 | 2430.9481 | 60.77% | 95% | 0% | -170.4805 | 1007.9201 | -3550 | -400 | -2942.0799 | 73.55% | 62.57% | 95% | 0% | 2106 | -149
[5 empty] | 2019-06-16 | 41 | 4003.5 | 1980 | -131 | 1 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 1450.9481 | 780 | 200 | 2430.9481 | 60.77% | 95% | 0% | -149.8856 | 1036.3469 | -3550 | -400 | -2913.6531 | 72.84% | 62.57% | 95% | 0% | 2111 | -131
[5 empty] | 2019-06-16 | 42 | 4004 | 1975 | -117 | 1 | 0 | 2092 | 1156.4716 | 1156.4716 | 1156.4716 | 1449.3817 | 780 | 200 | 2429.3817 | 60.73% | 95% | 0% | -133.8673 | 1022.6043 | -3550 | -400 | -2927.3957 | 73.18% | 62.57% | 95% | 0% | 2092 | -117
[5 empty] | 2019-06-16 | 43 | 4004.5 | 1951 | -114 | 1 | 0 | 2065 | 1114.1797 | 1114.1797 | 1114.1797 | 1449.3817 | 780 | 200 | 2429.3817 | 60.73% | 95% | 0% | -130.4348 | 983.7449 | -3550 | -400 | -2966.2551 | 74.16% | 62.57% | 95% | 0% | 2065 | -114
[5 empty] | 2019-06-16 | 44 | 4005 | 1889 | -116 | 0 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 1449.3817 | 780 | 200 | 2429.3817 | 60.73% | 95% | 0% | -132.7231 | 887.4747 | -2750 | -200 | -2062.5253 | 51.56% | 62.56% | 95% | 0% | 2005 | -116
[5 empty] | 2019-06-16 | 45 | 4005.5 | 1848 | -119 | 0 | 0 | 1967 | 960.676 | 960.676 | 960.676 | 1449.3817 | 780 | 200 | 2429.3817 | 60.73% | 95% | 0% | -136.1556 | 824.5204 | -2750 | -200 | -2125.4796 | 53.14% | 62.56% | 95% | 0% | 1967 | -119
[5 empty] | 2019-06-16 | 46 | 4006 | 1734 | -122 | 0 | 0 | 1856 | 786.8096 | 786.8096 | 786.8096 | 1449.3817 | 780 | 200 | 2429.3817 | 60.73% | 95% | 0% | -139.5881 | 647.2215 | -2750 | -200 | -2302.7785 | 57.57% | 62.55% | 95% | 0% | 1856 | -122
[5 empty] | 2019-06-16 | 47 | 4006.5 | 1572 | -126 | 0 | 0 | 1698 | 539.324 | 539.324 | 539.324 | 1449.3817 | 780 | 200 | 2429.3817 | 60.73% | 95% | 0% | -144.1648 | 395.1592 | -2750 | -200 | -2554.8408 | 63.87% | 62.55% | 95% | 0% | 1698 | -126
[5 empty] | 2019-06-16 | 48 | 4007 | 1449 | -129 | 0 | 0 | 1578 | 351.3603 | 351.3603 | 351.3603 | 1449.3817 | 780 | 200 | 2429.3817 | 60.73% | 95% | 0% | -147.5973 | 203.763 | -2750 | -200 | -2746.237 | 68.66% | 62.54% | 95% | 0% | 1578 | -129
[5 empty] | 2019-06-17 | 1 | 4007.5 | 1360 | -134 | 0 | 0 | 1494 | 219.7857 | 219.7857 | 219.7857 | 1449.3817 | 780 | 200 | 2429.3817 | 60.73% | 95% | 0% | -153.3181 | 66.4676 | -2750 | -200 | -2883.5324 | 72.09% | 62.54% | 95% | 0% | 1494 | -134
[5 empty] | 2019-06-17 | 2 | 4008 | 1298 | -139 | 0 | 0 | 1437 | 130.5029 | 130.5029 | 130.5029 | 1449.3817 | 780 | 200 | 2429.3817 | 60.73% | 95% | 0% | -159.0389 | -28.536 | -2750 | -200 | -2978.536 | 74.46% | 62.53% | 95% | 0% | 1437 | -139
[5 empty] | 2019-06-17 | 3 | 4008.5 | 1282 | -139 | 0 | 0 | 1421 | 105.4411 | 105.4411 | 105.4411 | 1449.3817 | 780 | 200 | 2429.3817 | 60.73% | 95% | 0% | -159.0389 | -53.5978 | -2750 | -200 | -3003.5978 | 75.09% | 62.53% | 95% | 0% | 1421 | -139
[5 empty] | 2019-06-17 | 4 | 4009 | 1272 | -139 | 0 | 0 | 1411 | 89.7774 | 89.7774 | 89.7774 | 1449.3817 | 780 | 200 | 2429.3817 | 60.73% | 95% | 0% | -159.0389 | -69.2615 | -2750 | -200 | -3019.2615 | 75.48% | 62.53% | 95% | 0% | 1411 | -139
[5 empty] | 2019-06-17 | 5 | 4009.5 | 1246 | -139 | 0 | 0 | 1385 | 49.0519 | 49.0519 | 49.0519 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -159.0389 | -109.987 | -2750 | -200 | -3059.987 | 76.5% | 62.53% | 95% | 0% | 1385 | -139
[5 empty] | 2019-06-17 | 6 | 4010 | 1222 | -139 | 0 | 0 | 1361 | 11.4592 | 11.4592 | 11.4592 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -159.0389 | -147.5797 | -2750 | -200 | -3097.5797 | 77.44% | 62.52% | 95% | 0% | 1361 | -139
[5 empty] | 2019-06-17 | 7 | 4010.5 | 1212 | -139 | 0 | 0 | 1351 | -4.2045 | -4.2045 | -4.2045 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -159.0389 | -163.2434 | -2750 | -200 | -3113.2434 | 77.83% | 62.52% | 95% | 0% | 1351 | -139
[5 empty] | 2019-06-17 | 8 | 4011 | 1210 | -138 | 0 | 0 | 1348 | -8.9035 | -8.9035 | -8.9035 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -157.8947 | -166.7983 | -2750 | -200 | -3116.7983 | 77.92% | 62.52% | 95% | 0% | 1348 | -138
[5 empty] | 2019-06-17 | 9 | 4011.5 | 1212 | -136 | 0 | 0 | 1348 | -8.9035 | -8.9035 | -8.9035 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -155.6064 | -164.51 | -2750 | -200 | -3114.51 | 77.86% | 62.52% | 95% | 0% | 1348 | -136
[5 empty] | 2019-06-17 | 10 | 4012 | 1206 | -135 | 0 | 0 | 1341 | -19.8681 | -19.8681 | -19.8681 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -154.4622 | -174.3303 | -2750 | -200 | -3124.3303 | 78.11% | 62.52% | 95% | 0% | 1341 | -135
[5 empty] | 2019-06-17 | 11 | 4012.5 | 1258 | -138 | 0 | 0 | 1396 | 66.2819 | 66.2819 | 66.2819 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -157.8947 | -91.6128 | -2750 | -200 | -3041.6128 | 76.04% | 62.51% | 95% | 0% | 1396 | -138
[5 empty] | 2019-06-17 | 12 | 4013 | 1329 | -151 | 1 | 0 | 1480 | 197.8566 | 197.8566 | 197.8566 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -172.7689 | 25.0877 | -3550 | -400 | -3924.9123 | 98.12% | 62.51% | 95% | 0% | 1480 | -151
[5 empty] | 2019-06-17 | 13 | 4013.5 | 1505 | -173 | 1 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -197.9405 | 310.0562 | -3550 | -400 | -3639.9438 | 91% | 62.51% | 95% | 0% | 1678 | -173
[5 empty] | 2019-06-17 | 14 | 4014 | 1659 | -208 | 1 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -237.9863 | 566.0533 | -3550 | -400 | -3383.9467 | 84.6% | 62.5% | 95% | 0% | 1867 | -208
[5 empty] | 2019-06-17 | 15 | 4014.5 | 1815 | -255 | 1 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -291.762 | 830.2495 | -3550 | -400 | -3119.7505 | 77.99% | 62.5% | 95% | 0% | 2070 | -255
[5 empty] | 2019-06-17 | 16 | 4015 | 1885 | -303 | 1 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -346.6819 | 960.1606 | -3550 | -400 | -2989.8394 | 74.75% | 62.5% | 95% | 0% | 2188 | -303
[5 empty] | 2019-06-17 | 17 | 4015.5 | 1894 | -360 | 1 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -411.8993 | 998.3233 | -3550 | -400 | -2951.6767 | 73.79% | 62.49% | 95% | 0% | 2254 | -360
[5 empty] | 2019-06-17 | 18 | 4016 | 1845 | -395 | 1 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 1447.8153 | 780 | 200 | 2427.8153 | 60.7% | 95% | 0% | -451.9451 | 936.3484 | -3550 | -400 | -3013.6516 | 75.34% | 62.49% | 95% | 0% | 2240 | -395
[5 empty] | 2019-06-17 | 19 | 4016.5 | 1855 | -403 | 1 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -461.0984 | 955.3896 | -3550 | -400 | -2994.6104 | 74.87% | 62.49% | 95% | 0% | 2258 | -403
[5 empty] | 2019-06-17 | 20 | 4017 | 1812 | -451 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -516.0183 | 908.3016 | -3550 | -400 | -3041.6984 | 76.04% | 62.49% | 95% | 0% | 2263 | -451
[5 empty] | 2019-06-17 | 21 | 4017.5 | 1766 | -472 | 1 | 0 | 2238 | 1385.1608 | 1385.1608 | 1385.1608 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -540.0458 | 845.115 | -3550 | -400 | -3104.885 | 77.62% | 62.49% | 95% | 0% | 2238 | -472
[5 empty] | 2019-06-17 | 22 | 4018 | 1718 | -502 | 1 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -574.3707 | 782.5955 | -3550 | -400 | -3167.4045 | 79.19% | 62.49% | 95% | 0% | 2220 | -502
[5 empty] | 2019-06-17 | 23 | 4018.5 | 1688 | -515 | 1 | 0 | 2203 | 1330.338 | 1330.338 | 1330.338 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -589.2449 | 741.0932 | -3550 | -400 | -3208.9068 | 80.22% | 62.48% | 95% | 0% | 2203 | -515
[5 empty] | 2019-06-17 | 24 | 4019 | 1639 | -554 | 1 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -633.8673 | 680.8071 | -3550 | -400 | -3269.1929 | 81.73% | 62.48% | 95% | 0% | 2193 | -554
[5 empty] | 2019-06-17 | 25 | 4019.5 | 1634 | -559 | 1 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -639.5881 | 675.0863 | -3550 | -400 | -3274.9137 | 81.87% | 62.47% | 95% | 0% | 2193 | -559
[5 empty] | 2019-06-17 | 26 | 4020 | 1601 | -575 | 1 | 0 | 2176 | 1288.0462 | 1288.0462 | 1288.0462 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -657.8947 | 630.1514 | -3550 | -400 | -3319.8486 | 83% | 62.47% | 95% | 0% | 2176 | -575
[5 empty] | 2019-06-17 | 27 | 4020.5 | 1552 | -590 | 1 | 0 | 2142 | 1234.7898 | 1234.7898 | 1234.7898 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -675.0572 | 559.7326 | -3550 | -400 | -3390.2674 | 84.76% | 62.47% | 95% | 0% | 2142 | -590
[5 empty] | 2019-06-17 | 28 | 4021 | 1510 | -596 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -681.9222 | 496.4785 | -3550 | -400 | -3453.5215 | 86.34% | 62.47% | 95% | 0% | 2106 | -596
[5 empty] | 2019-06-17 | 29 | 4021.5 | 1485 | -602 | 1 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -688.7872 | 459.8526 | -3550 | -400 | -3490.1474 | 87.25% | 62.46% | 95% | 0% | 2087 | -602
[5 empty] | 2019-06-17 | 30 | 4022 | 1469 | -610 | 1 | 0 | 2079 | 1136.1088 | 1136.1088 | 1136.1088 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -697.9405 | 438.1683 | -3550 | -400 | -3511.8317 | 87.8% | 62.46% | 95% | 0% | 2079 | -610
[5 empty] | 2019-06-17 | 31 | 4022.5 | 1491 | -580 | 1 | 0 | 2071 | 1123.5779 | 1123.5779 | 1123.5779 | 1446.249 | 780 | 200 | 2426.249 | 60.66% | 95% | 0% | -663.6156 | 459.9623 | -3550 | -400 | -3490.0377 | 87.25% | 62.45% | 95% | 0% | 2071 | -580
[5 empty] | 2019-06-17 | 32 | 4023 | 1592 | -541 | 1 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -618.9931 | 601.6994 | -3550 | -400 | -3348.3006 | 83.71% | 62.45% | 95% | 0% | 2133 | -541
[5 empty] | 2019-06-17 | 33 | 4023.5 | 1702 | -493 | 1 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -564.0732 | 753.7339 | -3550 | -400 | -3196.2661 | 79.91% | 62.45% | 95% | 0% | 2195 | -493
[5 empty] | 2019-06-17 | 34 | 4024 | 1801 | -466 | 1 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -533.1808 | 897.4045 | -3550 | -400 | -3052.5955 | 76.31% | 62.45% | 95% | 0% | 2267 | -466
[5 empty] | 2019-06-17 | 35 | 4024.5 | 1920 | -417 | 1 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -477.1167 | 1063.1141 | -3550 | -400 | -2886.8859 | 72.17% | 62.44% | 95% | 0% | 2337 | -417
[5 empty] | 2019-06-17 | 36 | 4025 | 2016 | -362 | 1 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -414.1876 | 1190.2641 | -3550 | -400 | -2759.7359 | 68.99% | 62.43% | 95% | 0% | 2378 | -362
[5 empty] | 2019-06-17 | 37 | 4025.5 | 2051 | -317 | 1 | 0 | 2368 | 1588.7881 | 1588.7881 | 1588.7881 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -362.7002 | 1226.0879 | -3550 | -400 | -2723.9121 | 68.1% | 62.43% | 95% | 0% | 2368 | -317
[5 empty] | 2019-06-17 | 38 | 4026 | 2109 | -265 | 1 | 0 | 2374 | 1598.1863 | 1598.1863 | 1598.1863 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -303.2037 | 1294.9827 | -3550 | -400 | -2655.0173 | 66.38% | 62.43% | 95% | 0% | 2374 | -265
[5 empty] | 2019-06-17 | 39 | 4026.5 | 2143 | -215 | 1 | 0 | 2358 | 1573.1245 | 1573.1245 | 1573.1245 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -245.9954 | 1327.1291 | -3550 | -400 | -2622.8709 | 65.57% | 62.42% | 95% | 0% | 2358 | -215
[5 empty] | 2019-06-17 | 40 | 4027 | 2160 | -176 | 1 | 0 | 2336 | 1538.6645 | 1538.6645 | 1538.6645 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -201.373 | 1337.2915 | -3550 | -400 | -2612.7085 | 65.32% | 62.42% | 95% | 0% | 2336 | -176
[5 empty] | 2019-06-17 | 41 | 4027.5 | 2193 | -143 | 1 | 0 | 2336 | 1538.6645 | 1538.6645 | 1538.6645 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -163.6156 | 1375.0489 | -3550 | -400 | -2574.9511 | 64.37% | 62.42% | 95% | 0% | 2336 | -143
[5 empty] | 2019-06-17 | 42 | 4028 | 2223 | -109 | 1 | 0 | 2332 | 1532.399 | 1532.399 | 1532.399 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -124.714 | 1407.6851 | -3550 | -400 | -2542.3149 | 63.56% | 62.42% | 95% | 0% | 2332 | -109
[5 empty] | 2019-06-17 | 43 | 4028.5 | 2222 | -93 | 1 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -106.4073 | 1399.3635 | -3550 | -400 | -2550.6365 | 63.77% | 62.42% | 95% | 0% | 2315 | -93
[5 empty] | 2019-06-17 | 44 | 4029 | 2155 | -87 | 1 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -99.5423 | 1291.8839 | -3550 | -400 | -2658.1161 | 66.45% | 62.41% | 95% | 0% | 2242 | -87
[5 empty] | 2019-06-17 | 45 | 4029.5 | 2118 | -86 | 1 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -98.3982 | 1233.5062 | -3550 | -400 | -2716.4938 | 67.91% | 62.4% | 95% | 0% | 2204 | -86
[5 empty] | 2019-06-17 | 46 | 4030 | 1986 | -86 | 0 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -98.3982 | 1026.7461 | -2750 | -200 | -1923.2539 | 48.08% | 62.4% | 95% | 0% | 2072 | -86
[5 empty] | 2019-06-17 | 47 | 4030.5 | 1835 | -86 | 0 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -98.3982 | 790.2251 | -2750 | -200 | -2159.7749 | 53.99% | 62.38% | 95% | 0% | 1921 | -86
[5 empty] | 2019-06-17 | 48 | 4031 | 1721 | -85 | 0 | 0 | 1806 | 708.4913 | 708.4913 | 708.4913 | 1444.6826 | 780 | 200 | 2424.6826 | 60.62% | 95% | 0% | -97.254 | 611.2373 | -2750 | -200 | -2338.7627 | 58.47% | 62.38% | 95% | 0% | 1806 | -85
[5 empty] | 2019-06-18 | 1 | 4031.5 | 1632 | -83 | 0 | 0 | 1715 | 565.9522 | 565.9522 | 565.9522 | 1443.1162 | 780 | 200 | 2423.1162 | 60.58% | 95% | 0% | -94.9657 | 470.9865 | -2750 | -200 | -2479.0135 | 61.98% | 62.38% | 95% | 0% | 1715 | -83
[5 empty] | 2019-06-18 | 2 | 4032 | 1589 | -80 | 0 | 0 | 1669 | 493.8994 | 493.8994 | 493.8994 | 1443.1162 | 780 | 200 | 2423.1162 | 60.58% | 95% | 0% | -91.5332 | 402.3662 | -2750 | -200 | -2547.6338 | 63.69% | 62.37% | 95% | 0% | 1669 | -80
[5 empty] | 2019-06-18 | 3 | 4032.5 | 1558 | -80 | 0 | 0 | 1638 | 445.3421 | 445.3421 | 445.3421 | 1443.1162 | 780 | 200 | 2423.1162 | 60.58% | 95% | 0% | -91.5332 | 353.8089 | -2750 | -200 | -2596.1911 | 64.9% | 62.37% | 95% | 0% | 1638 | -80
[5 empty] | 2019-06-18 | 4 | 4033 | 1550 | -79 | 0 | 0 | 1629 | 431.2448 | 431.2448 | 431.2448 | 1443.1162 | 780 | 200 | 2423.1162 | 60.58% | 95% | 0% | -90.389 | 340.8558 | -2750 | -200 | -2609.1442 | 65.23% | 62.37% | 95% | 0% | 1629 | -79
[5 empty] | 2019-06-18 | 5 | 4033.5 | 1536 | -78 | 0 | 0 | 1614 | 407.7494 | 407.7494 | 407.7494 | 1443.1162 | 780 | 200 | 2423.1162 | 60.58% | 95% | 0% | -89.2449 | 318.5045 | -2750 | -200 | -2631.4955 | 65.79% | 62.37% | 95% | 0% | 1614 | -78
[5 empty] | 2019-06-18 | 6 | 4034 | 1514 | -77 | 0 | 0 | 1591 | 371.723 | 371.723 | 371.723 | 1443.1162 | 780 | 200 | 2423.1162 | 60.58% | 95% | 0% | -88.1007 | 283.6223 | -2750 | -200 | -2666.3777 | 66.66% | 62.37% | 95% | 0% | 1591 | -77
[5 empty] | 2019-06-18 | 7 | 4034.5 | 1496 | -77 | 0 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 1443.1162 | 780 | 200 | 2423.1162 | 60.58% | 95% | 0% | -88.1007 | 255.4278 | -2750 | -200 | -2694.5722 | 67.36% | 62.36% | 95% | 0% | 1573 | -77
[5 empty] | 2019-06-18 | 8 | 4035 | 1506 | -76 | 0 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 1443.1162 | 780 | 200 | 2423.1162 | 60.58% | 95% | 0% | -86.9565 | 270.6692 | -2750 | -200 | -2679.3308 | 66.98% | 62.36% | 95% | 0% | 1582 | -76
[5 empty] | 2019-06-18 | 9 | 4035.5 | 1493 | -76 | 1 | 0 | 1569 | 337.263 | 337.263 | 337.263 | 1443.1162 | 780 | 200 | 2423.1162 | 60.58% | 95% | 0% | -86.9565 | 250.3065 | -3550 | -400 | -3699.6935 | 92.49% | 62.36% | 95% | 0% | 1569 | -76
[5 empty] | 2019-06-18 | 10 | 4036 | 1470 | -75 | 1 | 0 | 1545 | 299.6702 | 299.6702 | 299.6702 | 1443.1162 | 780 | 200 | 2423.1162 | 60.58% | 95% | 0% | -85.8124 | 213.8579 | -3550 | -400 | -3736.1421 | 93.4% | 62.36% | 95% | 0% | 1545 | -75
[5 empty] | 2019-06-18 | 11 | 4036.5 | 1490 | -83 | 1 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -94.9657 | 248.5628 | -3550 | -400 | -3701.4372 | 92.54% | 62.36% | 95% | 0% | 1573 | -83
[5 empty] | 2019-06-18 | 12 | 4037 | 1550 | -108 | 1 | 0 | 1658 | 476.6694 | 476.6694 | 476.6694 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -123.5698 | 353.0996 | -3550 | -400 | -3596.9004 | 89.92% | 62.35% | 95% | 0% | 1658 | -108
[5 empty] | 2019-06-18 | 13 | 4037.5 | 1688 | -134 | 1 | 0 | 1822 | 733.5532 | 733.5532 | 733.5532 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -153.3181 | 580.2351 | -3550 | -400 | -3369.7649 | 84.24% | 62.35% | 95% | 0% | 1822 | -134
[5 empty] | 2019-06-18 | 14 | 4038 | 1833 | -170 | 1 | 0 | 2003 | 1017.0651 | 1017.0651 | 1017.0651 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -194.508 | 822.5571 | -3550 | -400 | -3127.4429 | 78.19% | 62.34% | 95% | 0% | 2003 | -170
[5 empty] | 2019-06-18 | 15 | 4038.5 | 1988 | -221 | 1 | 0 | 2209 | 1339.7362 | 1339.7362 | 1339.7362 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -252.8604 | 1086.8758 | -3550 | -400 | -2863.1242 | 71.58% | 62.34% | 95% | 0% | 2209 | -221
[5 empty] | 2019-06-18 | 16 | 4039 | 2053 | -261 | 1 | 0 | 2314 | 1504.2045 | 1504.2045 | 1504.2045 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -298.627 | 1205.5774 | -3550 | -400 | -2744.4226 | 68.61% | 62.33% | 95% | 0% | 2314 | -261
[5 empty] | 2019-06-18 | 17 | 4039.5 | 2066 | -305 | 1 | 0 | 2371 | 1593.4872 | 1593.4872 | 1593.4872 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -348.9703 | 1244.517 | -3550 | -400 | -2705.483 | 67.64% | 62.33% | 95% | 0% | 2371 | -305
[5 empty] | 2019-06-18 | 18 | 4040 | 2000 | -343 | 1 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -392.4485 | 1157.1805 | -3550 | -400 | -2792.8195 | 69.82% | 62.33% | 95% | 0% | 2343 | -343
[5 empty] | 2019-06-18 | 19 | 4040.5 | 1974 | -380 | 1 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -434.7826 | 1132.0764 | -3550 | -400 | -2817.9236 | 70.45% | 62.32% | 95% | 0% | 2354 | -380
[5 empty] | 2019-06-18 | 20 | 4041 | 1889 | -445 | 1 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -509.1533 | 1026.3784 | -3550 | -400 | -2923.6216 | 73.09% | 62.32% | 95% | 0% | 2334 | -445
[5 empty] | 2019-06-18 | 21 | 4041.5 | 1825 | -482 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -551.4874 | 941.7525 | -3550 | -400 | -3008.2475 | 75.21% | 62.31% | 95% | 0% | 2307 | -482
[5 empty] | 2019-06-18 | 22 | 4042 | 1821 | -490 | 1 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -560.6407 | 938.8646 | -3550 | -400 | -3011.1354 | 75.28% | 62.31% | 95% | 0% | 2311 | -490
[5 empty] | 2019-06-18 | 23 | 4042.5 | 1822 | -489 | 1 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -559.4966 | 940.0088 | -3550 | -400 | -3009.9912 | 75.25% | 62.31% | 95% | 0% | 2311 | -489
[5 empty] | 2019-06-18 | 24 | 4043 | 1852 | -475 | 1 | 0 | 2327 | 1524.5672 | 1524.5672 | 1524.5672 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -543.4783 | 981.0889 | -3550 | -400 | -2968.9111 | 74.22% | 62.3% | 95% | 0% | 2327 | -475
[5 empty] | 2019-06-18 | 25 | 4043.5 | 1896 | -451 | 1 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -516.0183 | 1039.8762 | -3550 | -400 | -2910.1238 | 72.75% | 62.3% | 95% | 0% | 2347 | -451
[5 empty] | 2019-06-18 | 26 | 4044 | 1884 | -471 | 1 | 0 | 2355 | 1568.4254 | 1568.4254 | 1568.4254 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -538.9016 | 1029.5238 | -3550 | -400 | -2920.4762 | 73.01% | 62.3% | 95% | 0% | 2355 | -471
[5 empty] | 2019-06-18 | 27 | 4044.5 | 1900 | -456 | 1 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 1441.5499 | 780 | 200 | 2421.5499 | 60.54% | 95% | 0% | -521.7391 | 1048.2526 | -3550 | -400 | -2901.7474 | 72.54% | 62.29% | 95% | 0% | 2356 | -456
[5 empty] | 2019-06-18 | 28 | 4045 | 1946 | -411 | 1 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 1439.9835 | 780 | 200 | 2419.9835 | 60.5% | 95% | 0% | -470.2517 | 1101.3064 | -3550 | -400 | -2848.6936 | 71.22% | 62.28% | 95% | 0% | 2357 | -411
[5 empty] | 2019-06-18 | 29 | 4045.5 | 2005 | -377 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 1439.9835 | 780 | 200 | 2419.9835 | 60.5% | 95% | 0% | -431.3501 | 1179.3671 | -3550 | -400 | -2770.6329 | 69.27% | 62.28% | 95% | 0% | 2382 | -377
[5 empty] | 2019-06-18 | 30 | 4046 | 2066 | -335 | 1 | 0 | 2401 | 1640.4782 | 1640.4782 | 1640.4782 | 1439.9835 | 780 | 200 | 2419.9835 | 60.5% | 95% | 0% | -383.2952 | 1257.183 | -3550 | -400 | -2692.817 | 67.32% | 62.27% | 95% | 0% | 2401 | -335
[5 empty] | 2019-06-18 | 31 | 4046.5 | 2105 | -303 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 1439.9835 | 780 | 200 | 2419.9835 | 60.5% | 95% | 0% | -346.6819 | 1304.7608 | -3550 | -400 | -2645.2392 | 66.13% | 62.26% | 95% | 0% | 2408 | -303
[5 empty] | 2019-06-18 | 32 | 4047 | 2188 | -280 | 1 | 0 | 2468 | 1745.4246 | 1745.4246 | 1745.4246 | 1439.9835 | 780 | 200 | 2419.9835 | 60.5% | 95% | 0% | -320.3661 | 1425.0584 | -3550 | -400 | -2524.9416 | 63.12% | 62.25% | 95% | 0% | 2468 | -280
[5 empty] | 2019-06-18 | 33 | 4047.5 | 2221 | -270 | 1 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 1439.9835 | 780 | 200 | 2419.9835 | 60.5% | 95% | 0% | -308.9245 | 1472.5265 | -3550 | -400 | -2477.4735 | 61.94% | 62.25% | 95% | 0% | 2491 | -270
[5 empty] | 2019-06-18 | 34 | 4048 | 2291 | -245 | 1 | 0 | 2536 | 1851.9373 | 1851.9373 | 1851.9373 | 1439.9835 | 780 | 200 | 2419.9835 | 60.5% | 95% | 0% | -280.3204 | 1571.617 | -3550 | -400 | -2378.383 | 59.46% | 62.25% | 95% | 0% | 2536 | -245
[5 empty] | 2019-06-18 | 35 | 4048.5 | 2380 | -196 | 1 | 0 | 2576 | 1914.5919 | 1914.5919 | 1914.5919 | 1439.9835 | 780 | 200 | 2419.9835 | 60.5% | 95% | 0% | -224.2563 | 1690.3356 | -3550 | -400 | -2259.6644 | 56.49% | 62.25% | 95% | 0% | 2576 | -196
[5 empty] | 2019-06-18 | 36 | 4049 | 2432 | -163 | 1 | 0 | 2595 | 1944.3528 | 1944.3528 | 1944.3528 | 1439.9835 | 780 | 200 | 2419.9835 | 60.5% | 95% | 0% | -186.4989 | 1757.854 | -3550 | -400 | -2192.146 | 54.8% | 62.25% | 95% | 0% | 2595 | -163
[5 empty] | 2019-06-18 | 37 | 4049.5 | 2462 | -136 | 1 | 0 | 2598 | 1949.0519 | 1949.0519 | 1949.0519 | 1439.9835 | 780 | 200 | 2419.9835 | 60.5% | 95% | 0% | -155.6064 | 1793.4455 | -3550 | -400 | -2156.5545 | 53.91% | 62.25% | 95% | 0% | 2598 | -136
[5 empty] | 2019-06-18 | 38 | 4050 | 2475 | -115 | 1 | 0 | 2590 | 1936.521 | 1936.521 | 1936.521 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -131.5789 | 1804.9421 | -3550 | -400 | -2145.0579 | 53.63% | 62.25% | 95% | 0% | 2590 | -115
[5 empty] | 2019-06-18 | 39 | 4050.5 | 2460 | -98 | 1 | 0 | 2558 | 1886.3974 | 1886.3974 | 1886.3974 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -112.1281 | 1774.2692 | -3550 | -400 | -2175.7308 | 54.39% | 62.25% | 95% | 0% | 2558 | -98
[5 empty] | 2019-06-18 | 40 | 4051 | 2457 | -76 | 1 | 0 | 2533 | 1847.2383 | 1847.2383 | 1847.2383 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -86.9565 | 1760.2817 | -3550 | -400 | -2189.7183 | 54.74% | 62.25% | 95% | 0% | 2533 | -76
[5 empty] | 2019-06-18 | 41 | 4051.5 | 2470 | -62 | 1 | 0 | 2532 | 1845.6719 | 1845.6719 | 1845.6719 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -70.9382 | 1774.7337 | -3550 | -400 | -2175.2663 | 54.38% | 62.24% | 95% | 0% | 2532 | -62
[5 empty] | 2019-06-18 | 42 | 4052 | 2443 | -52 | 1 | 0 | 2495 | 1787.7164 | 1787.7164 | 1787.7164 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -59.4966 | 1728.2198 | -3550 | -400 | -2221.7802 | 55.54% | 62.24% | 95% | 0% | 2495 | -52
[5 empty] | 2019-06-18 | 43 | 4052.5 | 2384 | -47 | 1 | 0 | 2431 | 1687.4691 | 1687.4691 | 1687.4691 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -53.7757 | 1633.6933 | -3550 | -400 | -2316.3067 | 57.91% | 62.24% | 95% | 0% | 2431 | -47
[5 empty] | 2019-06-18 | 44 | 4053 | 2328 | -45 | 1 | 0 | 2373 | 1596.62 | 1596.62 | 1596.62 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -51.4874 | 1545.1325 | -3550 | -400 | -2404.8675 | 60.12% | 62.24% | 95% | 0% | 2373 | -45
[5 empty] | 2019-06-18 | 45 | 4053.5 | 2237 | -46 | 1 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -52.6316 | 1403.0156 | -3550 | -400 | -2546.9844 | 63.67% | 62.24% | 95% | 0% | 2283 | -46
[5 empty] | 2019-06-18 | 46 | 4054 | 2115 | -46 | 0 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -52.6316 | 1211.9191 | -2750 | -200 | -1738.0809 | 43.45% | 62.23% | 95% | 0% | 2161 | -46
[5 empty] | 2019-06-18 | 47 | 4054.5 | 1963 | -46 | 0 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -52.6316 | 973.8317 | -2750 | -200 | -1976.1683 | 49.4% | 62.23% | 95% | 0% | 2009 | -46
[5 empty] | 2019-06-18 | 48 | 4055 | 1827 | -47 | 0 | 0 | 1874 | 815.0041 | 815.0041 | 815.0041 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -53.7757 | 761.2284 | -2750 | -200 | -2188.7716 | 54.72% | 62.23% | 95% | 0% | 1874 | -47
[5 empty] | 2019-06-19 | 1 | 4055.5 | 1743 | -45 | 0 | 0 | 1788 | 680.2968 | 680.2968 | 680.2968 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -51.4874 | 628.8094 | -2750 | -200 | -2321.1906 | 58.03% | 62.22% | 95% | 0% | 1788 | -45
[5 empty] | 2019-06-19 | 2 | 4056 | 1668 | -43 | 0 | 0 | 1711 | 559.6867 | 559.6867 | 559.6867 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -49.1991 | 510.4876 | -2750 | -200 | -2439.5124 | 60.99% | 62.22% | 95% | 0% | 1711 | -43
[5 empty] | 2019-06-19 | 3 | 4056.5 | 1629 | -41 | 0 | 0 | 1670 | 495.4658 | 495.4658 | 495.4658 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -46.9108 | 448.555 | -2750 | -200 | -2501.445 | 62.54% | 62.22% | 95% | 0% | 1670 | -41
[5 empty] | 2019-06-19 | 4 | 4057 | 1627 | -40 | 0 | 0 | 1667 | 490.7667 | 490.7667 | 490.7667 | 1438.4171 | 780 | 200 | 2418.4171 | 60.46% | 95% | 0% | -45.7666 | 445.0001 | -2750 | -200 | -2504.9999 | 62.62% | 62.22% | 95% | 0% | 1667 | -40
[5 empty] | 2019-06-19 | 5 | 4057.5 | 1603 | -39 | 0 | 0 | 1642 | 451.6076 | 451.6076 | 451.6076 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -44.6224 | 406.9852 | -2750 | -200 | -2543.0148 | 63.58% | 62.22% | 95% | 0% | 1642 | -39
[5 empty] | 2019-06-19 | 6 | 4058 | 1593 | -38 | 0 | 0 | 1631 | 434.3776 | 434.3776 | 434.3776 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -43.4783 | 390.8993 | -2750 | -200 | -2559.1007 | 63.98% | 62.22% | 95% | 0% | 1631 | -38
[5 empty] | 2019-06-19 | 7 | 4058.5 | 1584 | -37 | 0 | 0 | 1621 | 418.7139 | 418.7139 | 418.7139 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -42.3341 | 376.3798 | -2750 | -200 | -2573.6202 | 64.34% | 62.21% | 95% | 0% | 1621 | -37
[5 empty] | 2019-06-19 | 8 | 4059 | 1593 | -36 | 0 | 0 | 1629 | 431.2448 | 431.2448 | 431.2448 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -41.1899 | 390.0549 | -2750 | -200 | -2559.9451 | 64% | 62.21% | 95% | 0% | 1629 | -36
[5 empty] | 2019-06-19 | 9 | 4059.5 | 1597 | -35 | 1 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -40.0458 | 395.8982 | -3550 | -400 | -3554.1018 | 88.85% | 62.21% | 95% | 0% | 1632 | -35
[5 empty] | 2019-06-19 | 10 | 4060 | 1589 | -34 | 1 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -38.9016 | 382.9451 | -3550 | -400 | -3567.0549 | 89.18% | 62.21% | 95% | 0% | 1623 | -34
[5 empty] | 2019-06-19 | 11 | 4060.5 | 1617 | -35 | 1 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -40.0458 | 427.2255 | -3550 | -400 | -3522.7745 | 88.07% | 62.21% | 95% | 0% | 1652 | -35
[5 empty] | 2019-06-19 | 12 | 4061 | 1662 | -42 | 1 | 0 | 1704 | 548.7222 | 548.7222 | 548.7222 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -48.0549 | 500.6673 | -3550 | -400 | -3449.3327 | 86.23% | 62.21% | 95% | 0% | 1704 | -42
[5 empty] | 2019-06-19 | 13 | 4061.5 | 1829 | -59 | 1 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -67.5057 | 769.4275 | -3550 | -400 | -3180.5725 | 79.51% | 62.2% | 95% | 0% | 1888 | -59
[5 empty] | 2019-06-19 | 14 | 4062 | 1988 | -84 | 1 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -96.1098 | 1029.0344 | -3550 | -400 | -2920.9656 | 73.02% | 62.2% | 95% | 0% | 2072 | -84
[5 empty] | 2019-06-19 | 15 | 4062.5 | 2182 | -115 | 1 | 0 | 2297 | 1477.5763 | 1477.5763 | 1477.5763 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -131.5789 | 1345.9973 | -3550 | -400 | -2604.0027 | 65.1% | 62.19% | 95% | 0% | 2297 | -115
[5 empty] | 2019-06-19 | 16 | 4063 | 2287 | -128 | 1 | 0 | 2415 | 1662.4073 | 1662.4073 | 1662.4073 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -146.4531 | 1515.9542 | -3550 | -400 | -2434.0458 | 60.85% | 62.19% | 95% | 0% | 2415 | -128
[5 empty] | 2019-06-19 | 17 | 4063.5 | 2343 | -144 | 1 | 0 | 2487 | 1775.1855 | 1775.1855 | 1775.1855 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -164.7597 | 1610.4258 | -3550 | -400 | -2339.5742 | 58.49% | 62.19% | 95% | 0% | 2487 | -144
[5 empty] | 2019-06-19 | 18 | 4064 | 2335 | -164 | 1 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 1436.8508 | 780 | 200 | 2416.8508 | 60.42% | 95% | 0% | -187.643 | 1606.3388 | -3550 | -400 | -2343.6612 | 58.59% | 62.18% | 95% | 0% | 2499 | -164
[5 empty] | 2019-06-19 | 19 | 4064.5 | 2324 | -184 | 1 | 0 | 2508 | 1808.0791 | 1808.0791 | 1808.0791 | 1435.2844 | 780 | 200 | 2415.2844 | 60.38% | 95% | 0% | -210.5263 | 1597.5528 | -3550 | -400 | -2352.4472 | 58.81% | 62.17% | 95% | 0% | 2508 | -184
[5 empty] | 2019-06-19 | 20 | 4065 | 2303 | -205 | 1 | 0 | 2508 | 1808.0791 | 1808.0791 | 1808.0791 | 1435.2844 | 780 | 200 | 2415.2844 | 60.38% | 95% | 0% | -234.5538 | 1573.5254 | -3550 | -400 | -2376.4746 | 59.41% | 62.17% | 95% | 0% | 2508 | -205
[5 empty] | 2019-06-19 | 21 | 4065.5 | 2242 | -248 | 1 | 0 | 2490 | 1779.8846 | 1779.8846 | 1779.8846 | 1435.2844 | 780 | 200 | 2415.2844 | 60.38% | 95% | 0% | -283.7529 | 1496.1317 | -3550 | -400 | -2453.8683 | 61.35% | 62.17% | 95% | 0% | 2490 | -248
[5 empty] | 2019-06-19 | 22 | 4066 | 2167 | -287 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 1435.2844 | 780 | 200 | 2415.2844 | 60.38% | 95% | 0% | -328.3753 | 1395.1202 | -3550 | -400 | -2554.8798 | 63.87% | 62.16% | 95% | 0% | 2454 | -287
[5 empty] | 2019-06-19 | 23 | 4066.5 | 2089 | -336 | 1 | 0 | 2425 | 1678.0709 | 1678.0709 | 1678.0709 | 1435.2844 | 780 | 200 | 2415.2844 | 60.38% | 95% | 0% | -384.4394 | 1293.6315 | -3550 | -400 | -2656.3685 | 66.41% | 62.16% | 95% | 0% | 2425 | -336
[5 empty] | 2019-06-19 | 24 | 4067 | 2045 | -374 | 1 | 0 | 2419 | 1668.6727 | 1668.6727 | 1668.6727 | 1435.2844 | 780 | 200 | 2415.2844 | 60.38% | 95% | 0% | -427.9176 | 1240.7551 | -3550 | -400 | -2709.2449 | 67.73% | 62.16% | 95% | 0% | 2419 | -374
[5 empty] | 2019-06-19 | 25 | 4067.5 | 2040 | -395 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1435.2844 | 780 | 200 | 2415.2844 | 60.38% | 95% | 0% | -451.9451 | 1241.7895 | -3550 | -400 | -2708.2105 | 67.71% | 62.16% | 95% | 0% | 2435 | -395
[5 empty] | 2019-06-19 | 26 | 4068 | 2032 | -391 | 1 | 0 | 2423 | 1674.9382 | 1674.9382 | 1674.9382 | 1435.2844 | 780 | 200 | 2415.2844 | 60.38% | 95% | 0% | -447.3684 | 1227.5697 | -3550 | -400 | -2722.4303 | 68.06% | 62.15% | 95% | 0% | 2423 | -391
[5 empty] | 2019-06-19 | 27 | 4068.5 | 2026 | -368 | 1 | 0 | 2394 | 1629.5136 | 1629.5136 | 1629.5136 | 1435.2844 | 780 | 200 | 2415.2844 | 60.38% | 95% | 0% | -421.0526 | 1208.461 | -3550 | -400 | -2741.539 | 68.54% | 62.14% | 95% | 0% | 2394 | -368
[5 empty] | 2019-06-19 | 28 | 4069 | 1977 | -394 | 1 | 0 | 2371 | 1593.4872 | 1593.4872 | 1593.4872 | 1435.2844 | 780 | 200 | 2415.2844 | 60.38% | 95% | 0% | -450.8009 | 1142.6863 | -3550 | -400 | -2807.3137 | 70.18% | 62.14% | 95% | 0% | 2371 | -394
[5 empty] | 2019-06-19 | 29 | 4069.5 | 1957 | -397 | 1 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 1435.2844 | 780 | 200 | 2415.2844 | 60.38% | 95% | 0% | -454.2334 | 1112.6256 | -3550 | -400 | -2837.3744 | 70.93% | 62.14% | 95% | 0% | 2354 | -397
[5 empty] | 2019-06-19 | 30 | 4070 | 1946 | -400 | 1 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 1433.7181 | 780 | 200 | 2413.7181 | 60.34% | 95% | 0% | -457.6659 | 1096.6622 | -3550 | -400 | -2853.3378 | 71.33% | 62.13% | 95% | 0% | 2346 | -400
[5 empty] | 2019-06-19 | 31 | 4070.5 | 1965 | -352 | 1 | 0 | 2317 | 1508.9035 | 1508.9035 | 1508.9035 | 1433.7181 | 780 | 200 | 2413.7181 | 60.34% | 95% | 0% | -402.746 | 1106.1575 | -3550 | -400 | -2843.8425 | 71.1% | 62.12% | 95% | 0% | 2317 | -352
[5 empty] | 2019-06-19 | 32 | 4071 | 1995 | -340 | 1 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 1433.7181 | 780 | 200 | 2413.7181 | 60.34% | 95% | 0% | -389.016 | 1148.0821 | -3550 | -400 | -2801.9179 | 70.05% | 62.12% | 95% | 0% | 2335 | -340
[5 empty] | 2019-06-19 | 33 | 4071.5 | 2053 | -336 | 1 | 0 | 2389 | 1621.6818 | 1621.6818 | 1621.6818 | 1433.7181 | 780 | 200 | 2413.7181 | 60.34% | 95% | 0% | -384.4394 | 1237.2424 | -3550 | -400 | -2712.7576 | 67.82% | 62.12% | 95% | 0% | 2389 | -336
[5 empty] | 2019-06-19 | 34 | 4072 | 2126 | -311 | 1 | 0 | 2437 | 1696.8673 | 1696.8673 | 1696.8673 | 1433.7181 | 780 | 200 | 2413.7181 | 60.34% | 95% | 0% | -355.8352 | 1341.032 | -3550 | -400 | -2608.968 | 65.22% | 62.12% | 95% | 0% | 2437 | -311
[5 empty] | 2019-06-19 | 35 | 4072.5 | 2168 | -281 | 1 | 0 | 2449 | 1715.6636 | 1715.6636 | 1715.6636 | 1433.7181 | 780 | 200 | 2413.7181 | 60.34% | 95% | 0% | -321.5103 | 1394.1533 | -3550 | -400 | -2555.8467 | 63.9% | 62.12% | 95% | 0% | 2449 | -281
[5 empty] | 2019-06-19 | 36 | 4073 | 2201 | -247 | 1 | 0 | 2448 | 1714.0973 | 1714.0973 | 1714.0973 | 1433.7181 | 780 | 200 | 2413.7181 | 60.34% | 95% | 0% | -282.6087 | 1431.4886 | -3550 | -400 | -2518.5114 | 62.96% | 62.11% | 95% | 0% | 2448 | -247
[5 empty] | 2019-06-19 | 37 | 4073.5 | 2245 | -206 | 1 | 0 | 2451 | 1718.7964 | 1718.7964 | 1718.7964 | 1433.7181 | 780 | 200 | 2413.7181 | 60.34% | 95% | 0% | -235.6979 | 1483.0984 | -3550 | -400 | -2466.9016 | 61.67% | 62.11% | 95% | 0% | 2451 | -206
[5 empty] | 2019-06-19 | 38 | 4074 | 2271 | -183 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 1433.7181 | 780 | 200 | 2413.7181 | 60.34% | 95% | 0% | -209.3822 | 1514.1133 | -3550 | -400 | -2435.8867 | 60.9% | 62.1% | 95% | 0% | 2454 | -183
[5 empty] | 2019-06-19 | 39 | 4074.5 | 2296 | -155 | 1 | 0 | 2451 | 1718.7964 | 1718.7964 | 1718.7964 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -177.3455 | 1541.4508 | -3550 | -400 | -2408.5492 | 60.21% | 62.1% | 95% | 0% | 2451 | -155
[5 empty] | 2019-06-19 | 40 | 4075 | 2323 | -121 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -138.4439 | 1569.3879 | -3550 | -400 | -2380.6121 | 59.52% | 62.1% | 95% | 0% | 2444 | -121
[5 empty] | 2019-06-19 | 41 | 4075.5 | 2350 | -87 | 1 | 0 | 2437 | 1696.8673 | 1696.8673 | 1696.8673 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -99.5423 | 1597.3249 | -3550 | -400 | -2352.6751 | 58.82% | 62.1% | 95% | 0% | 2437 | -87
[5 empty] | 2019-06-19 | 42 | 4076 | 2340 | -64 | 1 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -73.2265 | 1571.9507 | -3550 | -400 | -2378.0493 | 59.45% | 62.1% | 95% | 0% | 2404 | -64
[5 empty] | 2019-06-19 | 43 | 4076.5 | 2315 | -54 | 1 | 0 | 2369 | 1590.3545 | 1590.3545 | 1590.3545 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -61.7849 | 1528.5696 | -3550 | -400 | -2421.4304 | 60.54% | 62.09% | 95% | 0% | 2369 | -54
[5 empty] | 2019-06-19 | 44 | 4077 | 2270 | -52 | 1 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -59.4966 | 1457.2388 | -3550 | -400 | -2492.7612 | 62.32% | 62.09% | 95% | 0% | 2322 | -52
[5 empty] | 2019-06-19 | 45 | 4077.5 | 2196 | -53 | 0 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -60.6407 | 1341.75 | -2750 | -200 | -1608.25 | 40.21% | 62.09% | 95% | 0% | 2249 | -53
[5 empty] | 2019-06-19 | 46 | 4078 | 2063 | -54 | 0 | 0 | 2117 | 1195.6307 | 1195.6307 | 1195.6307 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -61.7849 | 1133.8458 | -2750 | -200 | -1816.1542 | 45.4% | 62.09% | 95% | 0% | 2117 | -54
[5 empty] | 2019-06-19 | 47 | 4078.5 | 1907 | -56 | 0 | 0 | 1963 | 954.4106 | 954.4106 | 954.4106 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -64.0732 | 890.3373 | -2750 | -200 | -2059.6627 | 51.49% | 62.09% | 95% | 0% | 1963 | -56
[5 empty] | 2019-06-19 | 48 | 4079 | 1798 | -57 | 0 | 0 | 1855 | 785.2432 | 785.2432 | 785.2432 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -65.2174 | 720.0258 | -2750 | -200 | -2229.9742 | 55.75% | 62.09% | 95% | 0% | 1855 | -57
[5 empty] | 2019-06-20 | 1 | 4079.5 | 1698 | -55 | 0 | 0 | 1753 | 625.474 | 625.474 | 625.474 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -62.9291 | 562.545 | -2750 | -200 | -2387.455 | 59.69% | 62.08% | 95% | 0% | 1753 | -55
[5 empty] | 2019-06-20 | 2 | 4080 | 1639 | -53 | 0 | 0 | 1692 | 529.9258 | 529.9258 | 529.9258 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -60.6407 | 469.2851 | -2750 | -200 | -2480.7149 | 62.02% | 62.08% | 95% | 0% | 1692 | -53
[5 empty] | 2019-06-20 | 3 | 4080.5 | 1600 | -55 | 0 | 0 | 1655 | 471.9703 | 471.9703 | 471.9703 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -62.9291 | 409.0413 | -2750 | -200 | -2540.9587 | 63.52% | 62.08% | 95% | 0% | 1655 | -55
[5 empty] | 2019-06-20 | 4 | 4081 | 1595 | -57 | 0 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 1432.1517 | 780 | 200 | 2412.1517 | 60.3% | 95% | 0% | -65.2174 | 402.0538 | -2750 | -200 | -2547.9462 | 63.7% | 62.08% | 95% | 0% | 1652 | -57
[5 empty] | 2019-06-20 | 5 | 4081.5 | 1562 | -60 | 0 | 0 | 1622 | 420.2803 | 420.2803 | 420.2803 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -68.6499 | 351.6304 | -2750 | -200 | -2598.3696 | 64.96% | 62.07% | 95% | 0% | 1622 | -60
[5 empty] | 2019-06-20 | 6 | 4082 | 1535 | -62 | 0 | 0 | 1597 | 381.1212 | 381.1212 | 381.1212 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -70.9382 | 310.183 | -2750 | -200 | -2639.817 | 66% | 62.07% | 95% | 0% | 1597 | -62
[5 empty] | 2019-06-20 | 7 | 4082.5 | 1482 | -64 | 0 | 0 | 1546 | 301.2366 | 301.2366 | 301.2366 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -73.2265 | 228.0101 | -2750 | -200 | -2721.9899 | 68.05% | 62.07% | 95% | 0% | 1546 | -64
[5 empty] | 2019-06-20 | 8 | 4083 | 1474 | -66 | 0 | 0 | 1540 | 291.8384 | 291.8384 | 291.8384 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -75.5149 | 216.3235 | -2750 | -200 | -2733.6765 | 68.34% | 62.07% | 95% | 0% | 1540 | -66
[5 empty] | 2019-06-20 | 9 | 4083.5 | 1455 | -67 | 0 | 0 | 1522 | 263.6439 | 263.6439 | 263.6439 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -76.659 | 186.9848 | -2750 | -200 | -2763.0152 | 69.08% | 62.06% | 95% | 0% | 1522 | -67
[5 empty] | 2019-06-20 | 10 | 4084 | 1451 | -67 | 0 | 0 | 1518 | 257.3784 | 257.3784 | 257.3784 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -76.659 | 180.7194 | -2750 | -200 | -2769.2806 | 69.23% | 62.06% | 95% | 0% | 1518 | -67
[5 empty] | 2019-06-20 | 11 | 4084.5 | 1497 | -74 | 0 | 0 | 1571 | 340.3957 | 340.3957 | 340.3957 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -84.6682 | 255.7275 | -2750 | -200 | -2694.2725 | 67.36% | 62.06% | 95% | 0% | 1571 | -74
[5 empty] | 2019-06-20 | 12 | 4085 | 1540 | -92 | 0 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -105.2632 | 330.6808 | -2750 | -200 | -2619.3192 | 65.48% | 62.05% | 95% | 0% | 1632 | -92
[5 empty] | 2019-06-20 | 13 | 4085.5 | 1687 | -124 | 0 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -141.8764 | 574.4467 | -2750 | -200 | -2375.5533 | 59.39% | 62.05% | 95% | 0% | 1811 | -124
[5 empty] | 2019-06-20 | 14 | 4086 | 1825 | -165 | 0 | 0 | 1990 | 996.7024 | 996.7024 | 996.7024 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -188.7872 | 807.9152 | -2750 | -200 | -2142.0848 | 53.55% | 62.05% | 95% | 0% | 1990 | -165
[5 empty] | 2019-06-20 | 15 | 4086.5 | 1948 | -215 | 1 | 0 | 2163 | 1267.6834 | 1267.6834 | 1267.6834 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -245.9954 | 1021.688 | -3550 | -400 | -2928.312 | 73.21% | 62.05% | 95% | 0% | 2163 | -215
[5 empty] | 2019-06-20 | 16 | 4087 | 1955 | -275 | 1 | 0 | 2230 | 1372.6298 | 1372.6298 | 1372.6298 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -314.6453 | 1057.9845 | -3550 | -400 | -2892.0155 | 72.3% | 62.05% | 95% | 0% | 2230 | -275
[5 empty] | 2019-06-20 | 17 | 4087.5 | 1899 | -340 | 1 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -389.016 | 997.7111 | -3550 | -400 | -2952.2889 | 73.81% | 62.05% | 95% | 0% | 2239 | -340
[5 empty] | 2019-06-20 | 18 | 4088 | 1809 | -406 | 1 | 0 | 2215 | 1349.1344 | 1349.1344 | 1349.1344 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -464.5309 | 884.6035 | -3550 | -400 | -3065.3965 | 76.63% | 62.05% | 95% | 0% | 2215 | -406
[5 empty] | 2019-06-20 | 19 | 4088.5 | 1734 | -464 | 1 | 0 | 2198 | 1322.5062 | 1322.5062 | 1322.5062 | 1430.5853 | 780 | 200 | 2410.5853 | 60.26% | 95% | 0% | -530.8924 | 791.6137 | -3550 | -400 | -3158.3863 | 78.96% | 62.04% | 95% | 0% | 2198 | -464
[5 empty] | 2019-06-20 | 20 | 4089 | 1664 | -509 | 1 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -582.3799 | 700.9672 | -3550 | -400 | -3249.0328 | 81.23% | 62.04% | 95% | 0% | 2173 | -509
[5 empty] | 2019-06-20 | 21 | 4089.5 | 1628 | -543 | 1 | 0 | 2171 | 1280.2143 | 1280.2143 | 1280.2143 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -621.2815 | 658.9329 | -3550 | -400 | -3291.0671 | 82.28% | 62.04% | 95% | 0% | 2171 | -543
[5 empty] | 2019-06-20 | 22 | 4090 | 1645 | -545 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -623.5698 | 686.4055 | -3550 | -400 | -3263.5945 | 81.59% | 62.04% | 95% | 0% | 2190 | -545
[5 empty] | 2019-06-20 | 23 | 4090.5 | 1646 | -555 | 1 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -635.0114 | 692.1938 | -3550 | -400 | -3257.8062 | 81.45% | 62.04% | 95% | 0% | 2201 | -555
[5 empty] | 2019-06-20 | 24 | 4091 | 1595 | -588 | 1 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -672.7689 | 626.2418 | -3550 | -400 | -3323.7582 | 83.09% | 62.03% | 95% | 0% | 2183 | -588
[5 empty] | 2019-06-20 | 25 | 4091.5 | 1616 | -574 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -656.7506 | 653.2247 | -3550 | -400 | -3296.7753 | 82.42% | 62.03% | 95% | 0% | 2190 | -574
[5 empty] | 2019-06-20 | 26 | 4092 | 1599 | -563 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -644.1648 | 621.9523 | -3550 | -400 | -3328.0477 | 83.2% | 62.03% | 95% | 0% | 2162 | -563
[5 empty] | 2019-06-20 | 27 | 4092.5 | 1568 | -582 | 1 | 0 | 2150 | 1247.3207 | 1247.3207 | 1247.3207 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -665.9039 | 581.4168 | -3550 | -400 | -3368.5832 | 84.21% | 62.03% | 95% | 0% | 2150 | -582
[5 empty] | 2019-06-20 | 28 | 4093 | 1513 | -609 | 1 | 0 | 2122 | 1203.4625 | 1203.4625 | 1203.4625 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -696.7963 | 506.6662 | -3550 | -400 | -3443.3338 | 86.08% | 62.03% | 95% | 0% | 2122 | -609
[5 empty] | 2019-06-20 | 29 | 4093.5 | 1552 | -566 | 1 | 0 | 2118 | 1197.197 | 1197.197 | 1197.197 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -647.5973 | 549.5998 | -3550 | -400 | -3400.4002 | 85.01% | 62.03% | 95% | 0% | 2118 | -566
[5 empty] | 2019-06-20 | 30 | 4094 | 1542 | -564 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -645.3089 | 533.0917 | -3550 | -400 | -3416.9083 | 85.42% | 62.02% | 95% | 0% | 2106 | -564
[5 empty] | 2019-06-20 | 31 | 4094.5 | 1530 | -551 | 1 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -630.4348 | 508.8068 | -3550 | -400 | -3441.1932 | 86.03% | 62.02% | 95% | 0% | 2081 | -551
[5 empty] | 2019-06-20 | 32 | 4095 | 1611 | -509 | 1 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -582.3799 | 617.9499 | -3550 | -400 | -3332.0501 | 83.3% | 62.02% | 95% | 0% | 2120 | -509
[5 empty] | 2019-06-20 | 33 | 4095.5 | 1681 | -458 | 1 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -524.0275 | 706.0632 | -3550 | -400 | -3243.9368 | 81.1% | 62.01% | 95% | 0% | 2139 | -458
[5 empty] | 2019-06-20 | 34 | 4096 | 1762 | -424 | 1 | 0 | 2186 | 1303.7098 | 1303.7098 | 1303.7098 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -485.1259 | 818.584 | -3550 | -400 | -3131.416 | 78.29% | 62.01% | 95% | 0% | 2186 | -424
[5 empty] | 2019-06-20 | 35 | 4096.5 | 1807 | -417 | 1 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 1429.019 | 780 | 200 | 2409.019 | 60.23% | 95% | 0% | -477.1167 | 886.115 | -3550 | -400 | -3063.885 | 76.6% | 62.01% | 95% | 0% | 2224 | -417
[5 empty] | 2019-06-20 | 36 | 4097 | 1895 | -354 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1427.4526 | 780 | 200 | 2407.4526 | 60.19% | 95% | 0% | -405.0343 | 997.3564 | -3550 | -400 | -2952.6436 | 73.82% | 62.01% | 95% | 0% | 2249 | -354
[5 empty] | 2019-06-20 | 37 | 4097.5 | 1934 | -333 | 1 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 1427.4526 | 780 | 200 | 2407.4526 | 60.19% | 95% | 0% | -381.0069 | 1049.5785 | -3550 | -400 | -2900.4215 | 72.51% | 62.01% | 95% | 0% | 2267 | -333
[5 empty] | 2019-06-20 | 38 | 4098 | 2041 | -262 | 1 | 0 | 2303 | 1486.9744 | 1486.9744 | 1486.9744 | 1427.4526 | 780 | 200 | 2407.4526 | 60.19% | 95% | 0% | -299.7712 | 1187.2033 | -3550 | -400 | -2762.7967 | 69.07% | 62% | 95% | 0% | 2303 | -262
[5 empty] | 2019-06-20 | 39 | 4098.5 | 2145 | -213 | 1 | 0 | 2358 | 1573.1245 | 1573.1245 | 1573.1245 | 1427.4526 | 780 | 200 | 2407.4526 | 60.19% | 95% | 0% | -243.7071 | 1329.4174 | -3550 | -400 | -2620.5826 | 65.51% | 62% | 95% | 0% | 2358 | -213
[5 empty] | 2019-06-20 | 40 | 4099 | 2210 | -165 | 1 | 0 | 2375 | 1599.7527 | 1599.7527 | 1599.7527 | 1427.4526 | 780 | 200 | 2407.4526 | 60.19% | 95% | 0% | -188.7872 | 1410.9655 | -3550 | -400 | -2539.0345 | 63.48% | 62% | 95% | 0% | 2375 | -165
[5 empty] | 2019-06-20 | 41 | 4099.5 | 2205 | -130 | 1 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 1427.4526 | 780 | 200 | 2407.4526 | 60.19% | 95% | 0% | -148.7414 | 1388.3567 | -3550 | -400 | -2561.6433 | 64.04% | 61.99% | 95% | 0% | 2335 | -130
[5 empty] | 2019-06-20 | 42 | 4100 | 2212 | -101 | 1 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 1427.4526 | 780 | 200 | 2407.4526 | 60.19% | 95% | 0% | -115.5606 | 1387.0774 | -3550 | -400 | -2562.9226 | 64.07% | 61.98% | 95% | 0% | 2313 | -101
[5 empty] | 2019-06-20 | 43 | 4100.5 | 2210 | -86 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1427.4526 | 780 | 200 | 2407.4526 | 60.19% | 95% | 0% | -98.3982 | 1377.6117 | -3550 | -400 | -2572.3883 | 64.31% | 61.98% | 95% | 0% | 2296 | -86
[5 empty] | 2019-06-20 | 44 | 4101 | 2167 | -80 | 1 | 0 | 2247 | 1399.258 | 1399.258 | 1399.258 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -91.5332 | 1307.7249 | -3550 | -400 | -2642.2751 | 66.06% | 61.98% | 95% | 0% | 2247 | -80
[5 empty] | 2019-06-20 | 45 | 4101.5 | 2098 | -79 | 1 | 0 | 2177 | 1289.6125 | 1289.6125 | 1289.6125 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -90.389 | 1199.2235 | -3550 | -400 | -2750.7765 | 68.77% | 61.98% | 95% | 0% | 2177 | -79
[5 empty] | 2019-06-20 | 46 | 4102 | 1993 | -77 | 0 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -88.1007 | 1033.9109 | -2750 | -200 | -1916.0891 | 47.9% | 61.97% | 95% | 0% | 2070 | -77
[5 empty] | 2019-06-20 | 47 | 4102.5 | 1850 | -77 | 0 | 0 | 1927 | 898.0214 | 898.0214 | 898.0214 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -88.1007 | 809.9207 | -2750 | -200 | -2140.0793 | 53.5% | 61.97% | 95% | 0% | 1927 | -77
[5 empty] | 2019-06-20 | 48 | 4103 | 1744 | -77 | 0 | 0 | 1821 | 731.9868 | 731.9868 | 731.9868 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -88.1007 | 643.8861 | -2750 | -200 | -2306.1139 | 57.65% | 61.97% | 95% | 0% | 1821 | -77
[5 empty] | 2019-06-21 | 1 | 4103.5 | 1649 | -74 | 0 | 0 | 1723 | 578.4831 | 578.4831 | 578.4831 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -84.6682 | 493.8149 | -2750 | -200 | -2456.1851 | 61.4% | 61.97% | 95% | 0% | 1723 | -74
[5 empty] | 2019-06-21 | 2 | 4104 | 1598 | -72 | 1 | 0 | 1670 | 495.4658 | 495.4658 | 495.4658 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -82.3799 | 413.0859 | -3550 | -400 | -3536.9141 | 88.42% | 61.97% | 95% | 0% | 1670 | -72
[5 empty] | 2019-06-21 | 3 | 4104.5 | 1575 | -72 | 1 | 0 | 1647 | 459.4394 | 459.4394 | 459.4394 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -82.3799 | 377.0595 | -3550 | -400 | -3572.9405 | 89.32% | 61.96% | 95% | 0% | 1647 | -72
[5 empty] | 2019-06-21 | 4 | 4105 | 1546 | -73 | 1 | 0 | 1619 | 415.5812 | 415.5812 | 415.5812 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -83.524 | 332.0572 | -3550 | -400 | -3617.9428 | 90.45% | 61.96% | 95% | 0% | 1619 | -73
[5 empty] | 2019-06-21 | 5 | 4105.5 | 1525 | -74 | 1 | 0 | 1599 | 384.2539 | 384.2539 | 384.2539 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -84.6682 | 299.5857 | -3550 | -400 | -3650.4143 | 91.26% | 61.96% | 95% | 0% | 1599 | -74
[5 empty] | 2019-06-21 | 6 | 4106 | 1492 | -75 | 1 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -85.8124 | 248.3179 | -3550 | -400 | -3701.6821 | 92.54% | 61.96% | 95% | 0% | 1567 | -75
[5 empty] | 2019-06-21 | 7 | 4106.5 | 1471 | -75 | 1 | 0 | 1546 | 301.2366 | 301.2366 | 301.2366 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -85.8124 | 215.4242 | -3550 | -400 | -3734.5758 | 93.36% | 61.95% | 95% | 0% | 1546 | -75
[5 empty] | 2019-06-21 | 8 | 4107 | 1466 | -76 | 1 | 0 | 1542 | 294.9711 | 294.9711 | 294.9711 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -86.9565 | 208.0146 | -3550 | -400 | -3741.9854 | 93.55% | 61.95% | 95% | 0% | 1542 | -76
[5 empty] | 2019-06-21 | 9 | 4107.5 | 1462 | -75 | 1 | 0 | 1537 | 287.1393 | 287.1393 | 287.1393 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -85.8124 | 201.327 | -3550 | -400 | -3748.673 | 93.72% | 61.95% | 95% | 0% | 1537 | -75
[5 empty] | 2019-06-21 | 10 | 4108 | 1448 | -73 | 1 | 0 | 1521 | 262.0775 | 262.0775 | 262.0775 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -83.524 | 178.5535 | -3550 | -400 | -3771.4465 | 94.29% | 61.95% | 95% | 0% | 1521 | -73
[5 empty] | 2019-06-21 | 11 | 4108.5 | 1479 | -80 | 1 | 0 | 1559 | 321.5993 | 321.5993 | 321.5993 | 1425.8862 | 780 | 200 | 2405.8862 | 60.15% | 95% | 0% | -91.5332 | 230.0662 | -3550 | -400 | -3719.9338 | 93% | 61.94% | 95% | 0% | 1559 | -80
[5 empty] | 2019-06-21 | 12 | 4109 | 1529 | -101 | 1 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -115.5606 | 317.2506 | -3550 | -400 | -3632.7494 | 90.82% | 61.94% | 95% | 0% | 1630 | -101
[5 empty] | 2019-06-21 | 13 | 4109.5 | 1679 | -139 | 1 | 0 | 1818 | 727.2877 | 727.2877 | 727.2877 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -159.0389 | 568.2488 | -3550 | -400 | -3381.7512 | 84.54% | 61.94% | 95% | 0% | 1818 | -139
[5 empty] | 2019-06-21 | 14 | 4110 | 1796 | -183 | 1 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -209.3822 | 770.0902 | -3550 | -400 | -3179.9098 | 79.5% | 61.94% | 95% | 0% | 1979 | -183
[5 empty] | 2019-06-21 | 15 | 4110.5 | 1922 | -238 | 1 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -272.3112 | 990.6731 | -3550 | -400 | -2959.3269 | 73.98% | 61.94% | 95% | 0% | 2160 | -238
[5 empty] | 2019-06-21 | 16 | 4111 | 1923 | -303 | 1 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -346.6819 | 1019.6825 | -3550 | -400 | -2930.3175 | 73.26% | 61.94% | 95% | 0% | 2226 | -303
[5 empty] | 2019-06-21 | 17 | 4111.5 | 1898 | -360 | 1 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -411.8993 | 1004.5887 | -3550 | -400 | -2945.4113 | 73.64% | 61.94% | 95% | 0% | 2258 | -360
[5 empty] | 2019-06-21 | 18 | 4112 | 1792 | -420 | 1 | 0 | 2212 | 1344.4353 | 1344.4353 | 1344.4353 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -480.5492 | 863.8861 | -3550 | -400 | -3086.1139 | 77.15% | 61.94% | 95% | 0% | 2212 | -420
[5 empty] | 2019-06-21 | 19 | 4112.5 | 1711 | -479 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -548.0549 | 761.9203 | -3550 | -400 | -3188.0797 | 79.7% | 61.94% | 95% | 0% | 2190 | -479
[5 empty] | 2019-06-21 | 20 | 4113 | 1627 | -529 | 1 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -605.2632 | 651.4557 | -3550 | -400 | -3298.5443 | 82.46% | 61.94% | 95% | 0% | 2156 | -529
[5 empty] | 2019-06-21 | 21 | 4113.5 | 1576 | -563 | 1 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -644.1648 | 585.9259 | -3550 | -400 | -3364.0741 | 84.1% | 61.94% | 95% | 0% | 2139 | -563
[5 empty] | 2019-06-21 | 22 | 4114 | 1533 | -603 | 1 | 0 | 2136 | 1225.3916 | 1225.3916 | 1225.3916 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -689.9314 | 535.4602 | -3550 | -400 | -3414.5398 | 85.36% | 61.94% | 95% | 0% | 2136 | -603
[5 empty] | 2019-06-21 | 23 | 4114.5 | 1550 | -590 | 1 | 0 | 2140 | 1231.657 | 1231.657 | 1231.657 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -675.0572 | 556.5998 | -3550 | -400 | -3393.4002 | 84.84% | 61.93% | 95% | 0% | 2140 | -590
[5 empty] | 2019-06-21 | 24 | 4115 | 1508 | -624 | 1 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -713.9588 | 505.1673 | -3550 | -400 | -3444.8327 | 86.12% | 61.93% | 95% | 0% | 2132 | -624
[5 empty] | 2019-06-21 | 25 | 4115.5 | 1485 | -639 | 1 | 0 | 2124 | 1206.5952 | 1206.5952 | 1206.5952 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -731.1213 | 475.4739 | -3550 | -400 | -3474.5261 | 86.86% | 61.93% | 95% | 0% | 2124 | -639
[5 empty] | 2019-06-21 | 26 | 4116 | 1468 | -628 | 1 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -718.5355 | 444.2015 | -3550 | -400 | -3505.7985 | 87.64% | 61.93% | 95% | 0% | 2096 | -628
[5 empty] | 2019-06-21 | 27 | 4116.5 | 1403 | -654 | 1 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 1424.3199 | 780 | 200 | 2404.3199 | 60.11% | 95% | 0% | -748.2838 | 353.3651 | -3550 | -400 | -3596.6349 | 89.92% | 61.92% | 95% | 0% | 2057 | -654
[5 empty] | 2019-06-21 | 28 | 4117 | 1380 | -644 | 1 | 0 | 2024 | 1049.9588 | 1049.9588 | 1049.9588 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -736.8421 | 313.1167 | -3550 | -400 | -3636.8833 | 90.92% | 61.92% | 95% | 0% | 2024 | -644
[5 empty] | 2019-06-21 | 29 | 4117.5 | 1362 | -647 | 1 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -740.2746 | 286.1887 | -3550 | -400 | -3663.8113 | 91.6% | 61.91% | 95% | 0% | 2009 | -647
[5 empty] | 2019-06-21 | 30 | 4118 | 1397 | -611 | 1 | 0 | 2008 | 1024.8969 | 1024.8969 | 1024.8969 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -699.0847 | 325.8123 | -3550 | -400 | -3624.1877 | 90.6% | 61.91% | 95% | 0% | 2008 | -611
[5 empty] | 2019-06-21 | 31 | 4118.5 | 1416 | -587 | 1 | 0 | 2003 | 1017.0651 | 1017.0651 | 1017.0651 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -671.6247 | 345.4404 | -3550 | -400 | -3604.5596 | 90.11% | 61.91% | 95% | 0% | 2003 | -587
[5 empty] | 2019-06-21 | 32 | 4119 | 1503 | -533 | 1 | 0 | 2036 | 1068.7552 | 1068.7552 | 1068.7552 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -609.8398 | 458.9153 | -3550 | -400 | -3491.0847 | 87.28% | 61.91% | 95% | 0% | 2036 | -533
[5 empty] | 2019-06-21 | 33 | 4119.5 | 1633 | -461 | 1 | 0 | 2094 | 1159.6043 | 1159.6043 | 1159.6043 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -527.46 | 632.1443 | -3550 | -400 | -3317.8557 | 82.95% | 61.91% | 95% | 0% | 2094 | -461
[5 empty] | 2019-06-21 | 34 | 4120 | 1720 | -426 | 1 | 0 | 2146 | 1241.0552 | 1241.0552 | 1241.0552 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -487.4142 | 753.641 | -3550 | -400 | -3196.359 | 79.91% | 61.91% | 95% | 0% | 2146 | -426
[5 empty] | 2019-06-21 | 35 | 4120.5 | 1833 | -378 | 1 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -432.4943 | 910.3746 | -3550 | -400 | -3039.6254 | 75.99% | 61.9% | 95% | 0% | 2211 | -378
[5 empty] | 2019-06-21 | 36 | 4121 | 1914 | -329 | 1 | 0 | 2243 | 1392.9926 | 1392.9926 | 1392.9926 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -376.4302 | 1016.5624 | -3550 | -400 | -2933.4376 | 73.34% | 61.9% | 95% | 0% | 2243 | -329
[5 empty] | 2019-06-21 | 37 | 4121.5 | 1988 | -266 | 1 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -304.3478 | 1105.8748 | -3550 | -400 | -2844.1252 | 71.1% | 61.89% | 95% | 0% | 2254 | -266
[5 empty] | 2019-06-21 | 38 | 4122 | 2058 | -217 | 1 | 0 | 2275 | 1443.1162 | 1443.1162 | 1443.1162 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -248.2838 | 1194.8325 | -3550 | -400 | -2755.1675 | 68.88% | 61.89% | 95% | 0% | 2275 | -217
[5 empty] | 2019-06-21 | 39 | 4122.5 | 2099 | -167 | 1 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -191.0755 | 1237.9434 | -3550 | -400 | -2712.0566 | 67.8% | 61.89% | 95% | 0% | 2266 | -167
[5 empty] | 2019-06-21 | 40 | 4123 | 2150 | -121 | 1 | 0 | 2271 | 1436.8508 | 1436.8508 | 1436.8508 | 1422.7535 | 780 | 200 | 2402.7535 | 60.07% | 95% | 0% | -138.4439 | 1298.4068 | -3550 | -400 | -2651.5932 | 66.29% | 61.89% | 95% | 0% | 2271 | -121
[5 empty] | 2019-06-21 | 41 | 4123.5 | 2182 | -87 | 1 | 0 | 2269 | 1433.7181 | 1433.7181 | 1433.7181 | 1421.1871 | 780 | 200 | 2401.1871 | 60.03% | 95% | 0% | -99.5423 | 1334.1757 | -3550 | -400 | -2615.8243 | 65.4% | 61.88% | 95% | 0% | 2269 | -87
[5 empty] | 2019-06-21 | 42 | 4124 | 2192 | -53 | 1 | 0 | 2245 | 1396.1253 | 1396.1253 | 1396.1253 | 1421.1871 | 780 | 200 | 2401.1871 | 60.03% | 95% | 0% | -60.6407 | 1335.4846 | -3550 | -400 | -2614.5154 | 65.36% | 61.88% | 95% | 0% | 2245 | -53
[5 empty] | 2019-06-21 | 43 | 4124.5 | 2176 | -36 | 1 | 0 | 2212 | 1344.4353 | 1344.4353 | 1344.4353 | 1421.1871 | 780 | 200 | 2401.1871 | 60.03% | 95% | 0% | -41.1899 | 1303.2454 | -3550 | -400 | -2646.7546 | 66.17% | 61.88% | 95% | 0% | 2212 | -36
[5 empty] | 2019-06-21 | 44 | 4125 | 2162 | -33 | 1 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 1421.1871 | 780 | 200 | 2401.1871 | 60.03% | 95% | 0% | -37.7574 | 1280.0497 | -3550 | -400 | -2669.9503 | 66.75% | 61.88% | 95% | 0% | 2195 | -33
[5 empty] | 2019-06-21 | 45 | 4125.5 | 2126 | -32 | 1 | 0 | 2158 | 1259.8516 | 1259.8516 | 1259.8516 | 1421.1871 | 780 | 200 | 2401.1871 | 60.03% | 95% | 0% | -36.6133 | 1223.2383 | -3550 | -400 | -2726.7617 | 68.17% | 61.88% | 95% | 0% | 2158 | -32
[5 empty] | 2019-06-21 | 46 | 4126 | 2042 | -32 | 0 | 0 | 2074 | 1128.277 | 1128.277 | 1128.277 | 1421.1871 | 780 | 200 | 2401.1871 | 60.03% | 95% | 0% | -36.6133 | 1091.6637 | -2750 | -200 | -1858.3363 | 46.46% | 61.88% | 95% | 0% | 2074 | -32
[5 empty] | 2019-06-21 | 47 | 4126.5 | 1920 | -31 | 0 | 0 | 1951 | 935.6142 | 935.6142 | 935.6142 | 1421.1871 | 780 | 200 | 2401.1871 | 60.03% | 95% | 0% | -35.4691 | 900.1451 | -2750 | -200 | -2049.8549 | 51.25% | 61.87% | 95% | 0% | 1951 | -31
[5 empty] | 2019-06-21 | 48 | 4127 | 1800 | -31 | 0 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 1421.1871 | 780 | 200 | 2401.1871 | 60.03% | 95% | 0% | -35.4691 | 712.1813 | -2750 | -200 | -2237.8187 | 55.95% | 61.87% | 95% | 0% | 1831 | -31
[5 empty] | 2019-06-22 | 1 | 4127.5 | 1715 | -30 | 0 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 1421.1871 | 780 | 200 | 2401.1871 | 60.03% | 95% | 0% | -34.3249 | 578.6182 | -2750 | -200 | -2371.3818 | 59.28% | 61.87% | 95% | 0% | 1745 | -30
[5 empty] | 2019-06-22 | 2 | 4128 | 1652 | -30 | 0 | 0 | 1682 | 514.2622 | 514.2622 | 514.2622 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -34.3249 | 479.9372 | -2750 | -200 | -2470.0628 | 61.75% | 61.87% | 95% | 0% | 1682 | -30
[5 empty] | 2019-06-22 | 3 | 4128.5 | 1612 | -30 | 0 | 0 | 1642 | 451.6076 | 451.6076 | 451.6076 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -34.3249 | 417.2826 | -2750 | -200 | -2532.7174 | 63.32% | 61.86% | 95% | 0% | 1642 | -30
[5 empty] | 2019-06-22 | 4 | 4129 | 1591 | -31 | 0 | 0 | 1622 | 420.2803 | 420.2803 | 420.2803 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -35.4691 | 384.8112 | -2750 | -200 | -2565.1888 | 64.13% | 61.86% | 95% | 0% | 1622 | -31
[5 empty] | 2019-06-22 | 5 | 4129.5 | 1559 | -31 | 0 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -35.4691 | 334.6875 | -2750 | -200 | -2615.3125 | 65.38% | 61.86% | 95% | 0% | 1590 | -31
[5 empty] | 2019-06-22 | 6 | 4130 | 1525 | -32 | 0 | 0 | 1557 | 318.4666 | 318.4666 | 318.4666 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -36.6133 | 281.8533 | -2750 | -200 | -2668.1467 | 66.7% | 61.86% | 95% | 0% | 1557 | -32
[5 empty] | 2019-06-22 | 7 | 4130.5 | 1502 | -32 | 0 | 0 | 1534 | 282.4402 | 282.4402 | 282.4402 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -36.6133 | 245.827 | -2750 | -200 | -2704.173 | 67.6% | 61.85% | 95% | 0% | 1534 | -32
[5 empty] | 2019-06-22 | 8 | 4131 | 1486 | -33 | 0 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -37.7574 | 221.1873 | -2750 | -200 | -2728.8127 | 68.22% | 61.85% | 95% | 0% | 1519 | -33
[5 empty] | 2019-06-22 | 9 | 4131.5 | 1461 | -35 | 0 | 0 | 1496 | 222.9184 | 222.9184 | 222.9184 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -40.0458 | 182.8726 | -2750 | -200 | -2767.1274 | 69.18% | 61.84% | 95% | 0% | 1496 | -35
[5 empty] | 2019-06-22 | 10 | 4132 | 1427 | -37 | 0 | 0 | 1464 | 172.7947 | 172.7947 | 172.7947 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -42.3341 | 130.4606 | -2750 | -200 | -2819.5394 | 70.49% | 61.84% | 95% | 0% | 1464 | -37
[5 empty] | 2019-06-22 | 11 | 4132.5 | 1430 | -43 | 0 | 0 | 1473 | 186.892 | 186.892 | 186.892 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -49.1991 | 137.6929 | -2750 | -200 | -2812.3071 | 70.31% | 61.83% | 95% | 0% | 1473 | -43
[5 empty] | 2019-06-22 | 12 | 4133 | 1424 | -63 | 0 | 0 | 1487 | 208.8211 | 208.8211 | 208.8211 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -72.0824 | 136.7387 | -2750 | -200 | -2813.2613 | 70.33% | 61.83% | 95% | 0% | 1487 | -63
[5 empty] | 2019-06-22 | 13 | 4133.5 | 1470 | -97 | 1 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -110.984 | 223.1463 | -3550 | -400 | -3726.8537 | 93.17% | 61.83% | 95% | 0% | 1567 | -97
[5 empty] | 2019-06-22 | 14 | 4134 | 1485 | -141 | 1 | 0 | 1626 | 426.5458 | 426.5458 | 426.5458 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -161.3272 | 265.2185 | -3550 | -400 | -3684.7815 | 92.12% | 61.82% | 95% | 0% | 1626 | -141
[5 empty] | 2019-06-22 | 15 | 4134.5 | 1520 | -189 | 1 | 0 | 1709 | 556.554 | 556.554 | 556.554 | 1419.6208 | 780 | 200 | 2399.6208 | 59.99% | 95% | 0% | -216.2471 | 340.3069 | -3550 | -400 | -3609.6931 | 90.24% | 61.82% | 95% | 0% | 1709 | -189
[5 empty] | 2019-06-22 | 16 | 4135 | 1519 | -246 | 1 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -281.4645 | 362.8059 | -3550 | -400 | -3587.1941 | 89.68% | 61.82% | 95% | 0% | 1765 | -246
[5 empty] | 2019-06-22 | 17 | 4135.5 | 1533 | -298 | 1 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -340.9611 | 406.6894 | -3550 | -400 | -3543.3106 | 88.58% | 61.81% | 95% | 0% | 1831 | -298
[5 empty] | 2019-06-22 | 18 | 4136 | 1480 | -375 | 1 | 0 | 1855 | 785.2432 | 785.2432 | 785.2432 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -429.0618 | 356.1814 | -3550 | -400 | -3593.8186 | 89.85% | 61.8% | 95% | 0% | 1855 | -375
[5 empty] | 2019-06-22 | 19 | 4136.5 | 1430 | -444 | 1 | 0 | 1874 | 815.0041 | 815.0041 | 815.0041 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -508.0092 | 306.995 | -3550 | -400 | -3643.005 | 91.08% | 61.8% | 95% | 0% | 1874 | -444
[5 empty] | 2019-06-22 | 20 | 4137 | 1342 | -513 | 1 | 0 | 1855 | 785.2432 | 785.2432 | 785.2432 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -586.9565 | 198.2867 | -3550 | -400 | -3751.7133 | 93.79% | 61.79% | 95% | 0% | 1855 | -513
[5 empty] | 2019-06-22 | 21 | 4137.5 | 1253 | -580 | 1 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -663.6156 | 87.1676 | -3550 | -400 | -3862.8324 | 96.57% | 61.79% | 95% | 0% | 1833 | -580
[5 empty] | 2019-06-22 | 22 | 4138 | 1180 | -631 | 1 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -721.968 | -5.6448 | -3550 | -400 | -3955.6448 | 98.89% | 61.79% | 95% | 0% | 1811 | -631
[5 empty] | 2019-06-22 | 23 | 4138.5 | 1130 | -660 | 1 | 0 | 1790 | 683.4295 | 683.4295 | 683.4295 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -755.1487 | -71.7192 | -3550 | -400 | -4021.7192 | 100.5% | 61.79% | 95% | 0% | 1790 | -660
[5 empty] | 2019-06-22 | 24 | 4139 | 1108 | -675 | 1 | 0 | 1783 | 672.465 | 672.465 | 672.465 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -772.3112 | -99.8462 | -3550 | -400 | -4049.8462 | 101.2% | 61.79% | 95% | 0% | 1783 | -675
[5 empty] | 2019-06-22 | 25 | 4139.5 | 1087 | -678 | 1 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -775.7437 | -131.4733 | -3550 | -400 | -4081.4733 | 102% | 61.78% | 95% | 0% | 1765 | -678
[5 empty] | 2019-06-22 | 26 | 4140 | 1090 | -648 | 1 | 0 | 1738 | 601.9786 | 601.9786 | 601.9786 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -741.4188 | -139.4402 | -3550 | -400 | -4089.4402 | 102.2% | 61.78% | 95% | 0% | 1738 | -648
[5 empty] | 2019-06-22 | 27 | 4140.5 | 1028 | -672 | 1 | 0 | 1700 | 542.4567 | 542.4567 | 542.4567 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -768.8787 | -226.422 | -3550 | -400 | -4176.422 | 104.4% | 61.78% | 95% | 0% | 1700 | -672
[5 empty] | 2019-06-22 | 28 | 4141 | 1033 | -645 | 1 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -737.9863 | -229.9896 | -3550 | -400 | -4179.9896 | 104.5% | 61.78% | 95% | 0% | 1678 | -645
[5 empty] | 2019-06-22 | 29 | 4141.5 | 1012 | -644 | 1 | 0 | 1656 | 473.5367 | 473.5367 | 473.5367 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -736.8421 | -263.3054 | -3550 | -400 | -4213.3054 | 105.3% | 61.78% | 95% | 0% | 1656 | -644
[5 empty] | 2019-06-22 | 30 | 4142 | 991 | -633 | 1 | 0 | 1624 | 423.413 | 423.413 | 423.413 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -724.2563 | -300.8433 | -3550 | -400 | -4250.8433 | 106.3% | 61.78% | 95% | 0% | 1624 | -633
[5 empty] | 2019-06-22 | 31 | 4142.5 | 1044 | -592 | 1 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -677.3455 | -235.1361 | -3550 | -400 | -4185.1361 | 104.6% | 61.78% | 95% | 0% | 1636 | -592
[5 empty] | 2019-06-22 | 32 | 4143 | 1115 | -539 | 1 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -616.7048 | -146.3008 | -3550 | -400 | -4096.3008 | 102.4% | 61.77% | 95% | 0% | 1654 | -539
[5 empty] | 2019-06-22 | 33 | 4143.5 | 1218 | -487 | 1 | 0 | 1705 | 550.2885 | 550.2885 | 550.2885 | 1418.0544 | 780 | 200 | 2398.0544 | 59.95% | 95% | 0% | -557.2082 | -6.9197 | -3550 | -400 | -3956.9197 | 98.92% | 61.77% | 95% | 0% | 1705 | -487
[5 empty] | 2019-06-22 | 34 | 4144 | 1349 | -436 | 1 | 0 | 1785 | 675.5977 | 675.5977 | 675.5977 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -498.8558 | 176.7419 | -3550 | -400 | -3773.2581 | 94.33% | 61.77% | 95% | 0% | 1785 | -436
[5 empty] | 2019-06-22 | 35 | 4144.5 | 1480 | -384 | 1 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -439.3593 | 359.9812 | -3550 | -400 | -3590.0188 | 89.75% | 61.77% | 95% | 0% | 1864 | -384
[5 empty] | 2019-06-22 | 36 | 4145 | 1603 | -317 | 1 | 0 | 1920 | 887.0569 | 887.0569 | 887.0569 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -362.7002 | 524.3567 | -3550 | -400 | -3425.6433 | 85.64% | 61.77% | 95% | 0% | 1920 | -317
[5 empty] | 2019-06-22 | 37 | 4145.5 | 1701 | -279 | 1 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -319.222 | 661.8168 | -3550 | -400 | -3288.1832 | 82.2% | 61.76% | 95% | 0% | 1980 | -279
[5 empty] | 2019-06-22 | 38 | 4146 | 1794 | -222 | 1 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -254.0046 | 783.4233 | -3550 | -400 | -3166.5767 | 79.16% | 61.76% | 95% | 0% | 2016 | -222
[5 empty] | 2019-06-22 | 39 | 4146.5 | 1857 | -174 | 1 | 0 | 2031 | 1060.9233 | 1060.9233 | 1060.9233 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -199.0847 | 861.8387 | -3550 | -400 | -3088.1613 | 77.2% | 61.76% | 95% | 0% | 2031 | -174
[5 empty] | 2019-06-22 | 40 | 4147 | 1897 | -131 | 1 | 0 | 2028 | 1056.2242 | 1056.2242 | 1056.2242 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -149.8856 | 906.3387 | -3550 | -400 | -3043.6613 | 76.09% | 61.76% | 95% | 0% | 2028 | -131
[5 empty] | 2019-06-22 | 41 | 4147.5 | 1924 | -97 | 1 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -110.984 | 934.2757 | -3550 | -400 | -3015.7243 | 75.39% | 61.76% | 95% | 0% | 2021 | -97
[5 empty] | 2019-06-22 | 42 | 4148 | 1937 | -68 | 1 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -77.8032 | 942.3947 | -3550 | -400 | -3007.6053 | 75.19% | 61.75% | 95% | 0% | 2005 | -68
[5 empty] | 2019-06-22 | 43 | 4148.5 | 1942 | -56 | 1 | 0 | 1998 | 1009.2333 | 1009.2333 | 1009.2333 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -64.0732 | 945.1601 | -3550 | -400 | -3004.8399 | 75.12% | 61.75% | 95% | 0% | 1998 | -56
[5 empty] | 2019-06-22 | 44 | 4149 | 1941 | -55 | 1 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -62.9291 | 943.1715 | -3550 | -400 | -3006.8285 | 75.17% | 61.75% | 95% | 0% | 1996 | -55
[5 empty] | 2019-06-22 | 45 | 4149.5 | 1922 | -57 | 1 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -65.2174 | 914.255 | -3550 | -400 | -3035.745 | 75.89% | 61.75% | 95% | 0% | 1979 | -57
[5 empty] | 2019-06-22 | 46 | 4150 | 1850 | -60 | 0 | 0 | 1910 | 871.3932 | 871.3932 | 871.3932 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -68.6499 | 802.7434 | -2750 | -200 | -2147.2566 | 53.68% | 61.74% | 95% | 0% | 1910 | -60
[5 empty] | 2019-06-22 | 47 | 4150.5 | 1736 | -62 | 0 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -70.9382 | 625.0222 | -2750 | -200 | -2324.9778 | 58.12% | 61.74% | 95% | 0% | 1798 | -62
[5 empty] | 2019-06-22 | 48 | 4151 | 1631 | -64 | 0 | 0 | 1695 | 534.6249 | 534.6249 | 534.6249 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -73.2265 | 461.3984 | -2750 | -200 | -2488.6016 | 62.22% | 61.74% | 95% | 0% | 1695 | -64
[5 empty] | 2019-06-23 | 1 | 4151.5 | 1550 | -63 | 0 | 0 | 1613 | 406.183 | 406.183 | 406.183 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -72.0824 | 334.1006 | -2750 | -200 | -2615.8994 | 65.4% | 61.74% | 95% | 0% | 1613 | -63
[5 empty] | 2019-06-23 | 2 | 4152 | 1497 | -63 | 0 | 0 | 1560 | 323.1657 | 323.1657 | 323.1657 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -72.0824 | 251.0833 | -2750 | -200 | -2698.9167 | 67.47% | 61.73% | 95% | 0% | 1560 | -63
[5 empty] | 2019-06-23 | 3 | 4152.5 | 1470 | -63 | 0 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -72.0824 | 208.7915 | -2750 | -200 | -2741.2085 | 68.53% | 61.73% | 95% | 0% | 1533 | -63
[5 empty] | 2019-06-23 | 4 | 4153 | 1455 | -63 | 0 | 0 | 1518 | 257.3784 | 257.3784 | 257.3784 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -72.0824 | 185.296 | -2750 | -200 | -2764.704 | 69.12% | 61.73% | 95% | 0% | 1518 | -63
[5 empty] | 2019-06-23 | 5 | 4153.5 | 1420 | -63 | 0 | 0 | 1483 | 202.5556 | 202.5556 | 202.5556 | 1416.488 | 780 | 200 | 2396.488 | 59.91% | 95% | 0% | -72.0824 | 130.4733 | -2750 | -200 | -2819.5267 | 70.49% | 61.73% | 95% | 0% | 1483 | -63
[5 empty] | 2019-06-23 | 6 | 4154 | 1391 | -63 | 0 | 0 | 1454 | 157.1311 | 157.1311 | 157.1311 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -72.0824 | 85.0487 | -2750 | -200 | -2864.9513 | 71.62% | 61.72% | 95% | 0% | 1454 | -63
[5 empty] | 2019-06-23 | 7 | 4154.5 | 1368 | -62 | 0 | 0 | 1430 | 119.5383 | 119.5383 | 119.5383 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -70.9382 | 48.6001 | -2750 | -200 | -2901.3999 | 72.53% | 61.72% | 95% | 0% | 1430 | -62
[5 empty] | 2019-06-23 | 8 | 4155 | 1351 | -62 | 0 | 0 | 1413 | 92.9101 | 92.9101 | 92.9101 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -70.9382 | 21.9719 | -2750 | -200 | -2928.0281 | 73.2% | 61.71% | 95% | 0% | 1413 | -62
[5 empty] | 2019-06-23 | 9 | 4155.5 | 1329 | -64 | 0 | 0 | 1393 | 61.5829 | 61.5829 | 61.5829 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -73.2265 | -11.6437 | -2750 | -200 | -2961.6437 | 74.04% | 61.7% | 95% | 0% | 1393 | -64
[5 empty] | 2019-06-23 | 10 | 4156 | 1287 | -66 | 0 | 0 | 1353 | -1.0717 | -1.0717 | -1.0717 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -75.5149 | -76.5866 | -2750 | -200 | -3026.5866 | 75.66% | 61.7% | 95% | 0% | 1353 | -66
[5 empty] | 2019-06-23 | 11 | 4156.5 | 1271 | -74 | 0 | 0 | 1345 | -13.6026 | -13.6026 | -13.6026 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -84.6682 | -98.2708 | -2750 | -200 | -3048.2708 | 76.21% | 61.7% | 95% | 0% | 1345 | -74
[5 empty] | 2019-06-23 | 12 | 4157 | 1255 | -90 | 0 | 0 | 1345 | -13.6026 | -13.6026 | -13.6026 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -102.9748 | -116.5775 | -2750 | -200 | -3066.5775 | 76.66% | 61.7% | 95% | 0% | 1345 | -90
[5 empty] | 2019-06-23 | 13 | 4157.5 | 1276 | -113 | 0 | 0 | 1389 | 55.3174 | 55.3174 | 55.3174 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -129.2906 | -73.9732 | -2750 | -200 | -3023.9732 | 75.6% | 61.69% | 95% | 0% | 1389 | -113
[5 empty] | 2019-06-23 | 14 | 4158 | 1258 | -151 | 1 | 0 | 1409 | 86.6447 | 86.6447 | 86.6447 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -172.7689 | -86.1242 | -3550 | -400 | -4036.1242 | 100.9% | 61.69% | 95% | 0% | 1409 | -151
[5 empty] | 2019-06-23 | 15 | 4158.5 | 1276 | -184 | 1 | 0 | 1460 | 166.5293 | 166.5293 | 166.5293 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -210.5263 | -43.997 | -3550 | -400 | -3993.997 | 99.85% | 61.69% | 95% | 0% | 1460 | -184
[5 empty] | 2019-06-23 | 16 | 4159 | 1327 | -207 | 1 | 0 | 1534 | 282.4402 | 282.4402 | 282.4402 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -236.8421 | 45.5981 | -3550 | -400 | -3904.4019 | 97.61% | 61.69% | 95% | 0% | 1534 | -207
[5 empty] | 2019-06-23 | 17 | 4159.5 | 1397 | -242 | 1 | 0 | 1639 | 446.9085 | 446.9085 | 446.9085 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -276.8879 | 170.0206 | -3550 | -400 | -3779.9794 | 94.5% | 61.69% | 95% | 0% | 1639 | -242
[5 empty] | 2019-06-23 | 18 | 4160 | 1419 | -281 | 1 | 0 | 1700 | 542.4567 | 542.4567 | 542.4567 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -321.5103 | 220.9464 | -3550 | -400 | -3729.0536 | 93.23% | 61.69% | 95% | 0% | 1700 | -281
[5 empty] | 2019-06-23 | 19 | 4160.5 | 1447 | -327 | 1 | 0 | 1774 | 658.3677 | 658.3677 | 658.3677 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -374.1419 | 284.2258 | -3550 | -400 | -3665.7742 | 91.64% | 61.68% | 95% | 0% | 1774 | -327
[5 empty] | 2019-06-23 | 20 | 4161 | 1461 | -354 | 1 | 0 | 1815 | 722.5886 | 722.5886 | 722.5886 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -405.0343 | 317.5543 | -3550 | -400 | -3632.4457 | 90.81% | 61.68% | 95% | 0% | 1815 | -354
[5 empty] | 2019-06-23 | 21 | 4161.5 | 1432 | -400 | 1 | 0 | 1832 | 749.2168 | 749.2168 | 749.2168 | 1414.9217 | 780 | 200 | 2394.9217 | 59.87% | 95% | 0% | -457.6659 | 291.5509 | -3550 | -400 | -3658.4491 | 91.46% | 61.68% | 95% | 0% | 1832 | -400
[5 empty] | 2019-06-23 | 22 | 4162 | 1402 | -429 | 1 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 1413.3553 | 780 | 200 | 2393.3553 | 59.83% | 95% | 0% | -490.8467 | 256.8038 | -3550 | -400 | -3693.1962 | 92.33% | 61.68% | 95% | 0% | 1831 | -429
[5 empty] | 2019-06-23 | 23 | 4162.5 | 1322 | -503 | 1 | 0 | 1825 | 738.2523 | 738.2523 | 738.2523 | 1413.3553 | 780 | 200 | 2393.3553 | 59.83% | 95% | 0% | -575.5149 | 162.7374 | -3550 | -400 | -3787.2626 | 94.68% | 61.68% | 95% | 0% | 1825 | -503
[5 empty] | 2019-06-23 | 24 | 4163 | 1359 | -486 | 1 | 0 | 1845 | 769.5796 | 769.5796 | 769.5796 | 1413.3553 | 780 | 200 | 2393.3553 | 59.83% | 95% | 0% | -556.0641 | 213.5155 | -3550 | -400 | -3736.4845 | 93.41% | 61.67% | 95% | 0% | 1845 | -486
[5 empty] | 2019-06-23 | 25 | 4163.5 | 1388 | -481 | 1 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 1413.3553 | 780 | 200 | 2393.3553 | 59.83% | 95% | 0% | -550.3432 | 256.8291 | -3550 | -400 | -3693.1709 | 92.33% | 61.67% | 95% | 0% | 1869 | -481
[5 empty] | 2019-06-23 | 26 | 4164 | 1388 | -499 | 1 | 0 | 1887 | 835.3669 | 835.3669 | 835.3669 | 1413.3553 | 780 | 200 | 2393.3553 | 59.83% | 95% | 0% | -570.9382 | 264.4286 | -3550 | -400 | -3685.5714 | 92.14% | 61.67% | 95% | 0% | 1887 | -499
[5 empty] | 2019-06-23 | 27 | 4164.5 | 1437 | -464 | 1 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 1413.3553 | 780 | 200 | 2393.3553 | 59.83% | 95% | 0% | -530.8924 | 326.4035 | -3550 | -400 | -3623.5965 | 90.59% | 61.67% | 95% | 0% | 1901 | -464
[5 empty] | 2019-06-23 | 28 | 4165 | 1465 | -441 | 1 | 0 | 1906 | 865.1278 | 865.1278 | 865.1278 | 1413.3553 | 780 | 200 | 2393.3553 | 59.83% | 95% | 0% | -504.5767 | 360.5511 | -3550 | -400 | -3589.4489 | 89.74% | 61.66% | 95% | 0% | 1906 | -441
[5 empty] | 2019-06-23 | 29 | 4165.5 | 1518 | -395 | 1 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 1413.3553 | 780 | 200 | 2393.3553 | 59.83% | 95% | 0% | -451.9451 | 424.1473 | -3550 | -400 | -3525.8527 | 88.15% | 61.65% | 95% | 0% | 1913 | -395
[5 empty] | 2019-06-23 | 30 | 4166 | 1577 | -344 | 1 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -393.5927 | 495.0306 | -3550 | -400 | -3454.9694 | 86.37% | 61.65% | 95% | 0% | 1921 | -344
[5 empty] | 2019-06-23 | 31 | 4166.5 | 1642 | -319 | 1 | 0 | 1961 | 951.2778 | 951.2778 | 951.2778 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -364.9886 | 586.2893 | -3550 | -400 | -3363.7107 | 84.09% | 61.65% | 95% | 0% | 1961 | -319
[5 empty] | 2019-06-23 | 32 | 4167 | 1728 | -283 | 1 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -323.7986 | 705.7974 | -3550 | -400 | -3244.2026 | 81.11% | 61.65% | 95% | 0% | 2011 | -283
[5 empty] | 2019-06-23 | 33 | 4167.5 | 1820 | -256 | 1 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -292.9062 | 838.5035 | -3550 | -400 | -3111.4965 | 77.79% | 61.64% | 95% | 0% | 2076 | -256
[5 empty] | 2019-06-23 | 34 | 4168 | 1866 | -244 | 1 | 0 | 2110 | 1184.6661 | 1184.6661 | 1184.6661 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -279.1762 | 905.4899 | -3550 | -400 | -3044.5101 | 76.11% | 61.64% | 95% | 0% | 2110 | -244
[5 empty] | 2019-06-23 | 35 | 4168.5 | 1932 | -228 | 1 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -260.8696 | 1002.1148 | -3550 | -400 | -2947.8852 | 73.7% | 61.64% | 95% | 0% | 2160 | -228
[5 empty] | 2019-06-23 | 36 | 4169 | 1989 | -199 | 1 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -227.6888 | 1079.1538 | -3550 | -400 | -2870.8462 | 71.77% | 61.64% | 95% | 0% | 2188 | -199
[5 empty] | 2019-06-23 | 37 | 4169.5 | 2006 | -176 | 1 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -201.373 | 1096.0714 | -3550 | -400 | -2853.9286 | 71.35% | 61.64% | 95% | 0% | 2182 | -176
[5 empty] | 2019-06-23 | 38 | 4170 | 2013 | -157 | 1 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -179.6339 | 1099.0141 | -3550 | -400 | -2850.9859 | 71.27% | 61.63% | 95% | 0% | 2170 | -157
[5 empty] | 2019-06-23 | 39 | 4170.5 | 2023 | -136 | 1 | 0 | 2159 | 1261.418 | 1261.418 | 1261.418 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -155.6064 | 1105.8116 | -3550 | -400 | -2844.1884 | 71.1% | 61.63% | 95% | 0% | 2159 | -136
[5 empty] | 2019-06-23 | 40 | 4171 | 2018 | -123 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -140.7323 | 1092.4911 | -3550 | -400 | -2857.5089 | 71.44% | 61.62% | 95% | 0% | 2141 | -123
[5 empty] | 2019-06-23 | 41 | 4171.5 | 2006 | -113 | 0 | 0 | 2119 | 1198.7634 | 1198.7634 | 1198.7634 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -129.2906 | 1069.4728 | -2750 | -200 | -1880.5272 | 47.01% | 61.62% | 95% | 0% | 2119 | -113
[5 empty] | 2019-06-23 | 42 | 4172 | 2000 | -106 | 0 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -121.2815 | 1057.1192 | -2750 | -200 | -1892.8808 | 47.32% | 61.62% | 95% | 0% | 2106 | -106
[5 empty] | 2019-06-23 | 43 | 4172.5 | 1969 | -104 | 1 | 0 | 2073 | 1126.7106 | 1126.7106 | 1126.7106 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -118.9931 | 1007.7175 | -3550 | -400 | -2942.2825 | 73.56% | 61.62% | 95% | 0% | 2073 | -104
[5 empty] | 2019-06-23 | 44 | 4173 | 1936 | -103 | 1 | 0 | 2039 | 1073.4542 | 1073.4542 | 1073.4542 | 1411.789 | 780 | 200 | 2391.789 | 59.79% | 95% | 0% | -117.849 | 955.6053 | -3550 | -400 | -2994.3947 | 74.86% | 61.62% | 95% | 0% | 2039 | -103
[5 empty] | 2019-06-23 | 45 | 4173.5 | 1881 | -102 | 0 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -116.7048 | 869.033 | -2750 | -200 | -2080.967 | 52.02% | 61.61% | 95% | 0% | 1983 | -102
[5 empty] | 2019-06-23 | 46 | 4174 | 1780 | -101 | 0 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -115.5606 | 710.408 | -2750 | -200 | -2239.592 | 55.99% | 61.61% | 95% | 0% | 1881 | -101
[5 empty] | 2019-06-23 | 47 | 4174.5 | 1658 | -100 | 0 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -114.4165 | 518.8894 | -2750 | -200 | -2431.1106 | 60.78% | 61.61% | 95% | 0% | 1758 | -100
[5 empty] | 2019-06-23 | 48 | 4175 | 1560 | -99 | 0 | 0 | 1659 | 478.2358 | 478.2358 | 478.2358 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -113.2723 | 364.9635 | -2750 | -200 | -2585.0365 | 64.63% | 61.61% | 95% | 0% | 1659 | -99
[5 empty] | 2019-06-24 | 1 | 4175.5 | 1486 | -97 | 0 | 0 | 1583 | 359.1921 | 359.1921 | 359.1921 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -110.984 | 248.2081 | -2750 | -200 | -2701.7919 | 67.54% | 61.6% | 95% | 0% | 1583 | -97
[5 empty] | 2019-06-24 | 2 | 4176 | 1435 | -95 | 0 | 0 | 1530 | 276.1748 | 276.1748 | 276.1748 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -108.6957 | 167.4791 | -2750 | -200 | -2782.5209 | 69.56% | 61.59% | 95% | 0% | 1530 | -95
[5 empty] | 2019-06-24 | 3 | 4176.5 | 1408 | -95 | 0 | 0 | 1503 | 233.8829 | 233.8829 | 233.8829 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -108.6957 | 125.1873 | -2750 | -200 | -2824.8127 | 70.62% | 61.59% | 95% | 0% | 1503 | -95
[5 empty] | 2019-06-24 | 4 | 4177 | 1405 | -95 | 0 | 0 | 1500 | 229.1838 | 229.1838 | 229.1838 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -108.6957 | 120.4882 | -2750 | -200 | -2829.5118 | 70.74% | 61.59% | 95% | 0% | 1500 | -95
[5 empty] | 2019-06-24 | 5 | 4177.5 | 1394 | -93 | 0 | 0 | 1487 | 208.8211 | 208.8211 | 208.8211 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -106.4073 | 102.4138 | -2750 | -200 | -2847.5862 | 71.19% | 61.59% | 95% | 0% | 1487 | -93
[5 empty] | 2019-06-24 | 6 | 4178 | 1379 | -90 | 0 | 0 | 1469 | 180.6265 | 180.6265 | 180.6265 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -102.9748 | 77.6517 | -2750 | -200 | -2872.3483 | 71.81% | 61.59% | 95% | 0% | 1469 | -90
[5 empty] | 2019-06-24 | 7 | 4178.5 | 1380 | -88 | 0 | 0 | 1468 | 179.0602 | 179.0602 | 179.0602 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -100.6865 | 78.3737 | -2750 | -200 | -2871.6263 | 71.79% | 61.58% | 95% | 0% | 1468 | -88
[5 empty] | 2019-06-24 | 8 | 4179 | 1383 | -85 | 1 | 0 | 1468 | 179.0602 | 179.0602 | 179.0602 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -97.254 | 81.8062 | -3550 | -400 | -3868.1938 | 96.7% | 61.58% | 95% | 0% | 1468 | -85
[5 empty] | 2019-06-24 | 9 | 4179.5 | 1386 | -83 | 1 | 0 | 1469 | 180.6265 | 180.6265 | 180.6265 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -94.9657 | 85.6609 | -3550 | -400 | -3864.3391 | 96.61% | 61.58% | 95% | 0% | 1469 | -83
[5 empty] | 2019-06-24 | 10 | 4180 | 1385 | -81 | 1 | 0 | 1466 | 175.9275 | 175.9275 | 175.9275 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -92.6773 | 83.2501 | -3550 | -400 | -3866.7499 | 96.67% | 61.58% | 95% | 0% | 1466 | -81
[5 empty] | 2019-06-24 | 11 | 4180.5 | 1415 | -81 | 1 | 0 | 1496 | 222.9184 | 222.9184 | 222.9184 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -92.6773 | 130.241 | -3550 | -400 | -3819.759 | 95.49% | 61.57% | 95% | 0% | 1496 | -81
[5 empty] | 2019-06-24 | 12 | 4181 | 1492 | -90 | 1 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 1410.2226 | 780 | 200 | 2390.2226 | 59.76% | 95% | 0% | -102.9748 | 254.6509 | -3550 | -400 | -3695.3491 | 92.38% | 61.57% | 95% | 0% | 1582 | -90
[5 empty] | 2019-06-24 | 13 | 4181.5 | 1685 | -105 | 1 | 0 | 1790 | 683.4295 | 683.4295 | 683.4295 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -120.1373 | 563.2922 | -3550 | -400 | -3386.7078 | 84.67% | 61.56% | 95% | 0% | 1790 | -105
[5 empty] | 2019-06-24 | 14 | 4182 | 1849 | -127 | 1 | 0 | 1976 | 974.7733 | 974.7733 | 974.7733 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -145.3089 | 829.4644 | -3550 | -400 | -3120.5356 | 78.01% | 61.56% | 95% | 0% | 1976 | -127
[5 empty] | 2019-06-24 | 15 | 4182.5 | 2046 | -159 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -181.9222 | 1151.5485 | -3550 | -400 | -2798.4515 | 69.96% | 61.56% | 95% | 0% | 2205 | -159
[5 empty] | 2019-06-24 | 16 | 4183 | 2153 | -187 | 1 | 0 | 2340 | 1544.9299 | 1544.9299 | 1544.9299 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -213.9588 | 1330.9711 | -3550 | -400 | -2619.0289 | 65.48% | 61.56% | 95% | 0% | 2340 | -187
[5 empty] | 2019-06-24 | 17 | 4183.5 | 2214 | -215 | 1 | 0 | 2429 | 1684.3364 | 1684.3364 | 1684.3364 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -245.9954 | 1438.3409 | -3550 | -400 | -2511.6591 | 62.79% | 61.56% | 95% | 0% | 2429 | -215
[5 empty] | 2019-06-24 | 18 | 4184 | 2222 | -231 | 1 | 0 | 2453 | 1721.9291 | 1721.9291 | 1721.9291 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -264.3021 | 1457.627 | -3550 | -400 | -2492.373 | 62.31% | 61.55% | 95% | 0% | 2453 | -231
[5 empty] | 2019-06-24 | 19 | 4184.5 | 2228 | -250 | 1 | 0 | 2478 | 1761.0882 | 1761.0882 | 1761.0882 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -286.0412 | 1475.047 | -3550 | -400 | -2474.953 | 61.87% | 61.55% | 95% | 0% | 2478 | -250
[5 empty] | 2019-06-24 | 20 | 4185 | 2187 | -272 | 1 | 0 | 2459 | 1731.3273 | 1731.3273 | 1731.3273 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -311.2128 | 1420.1145 | -3550 | -400 | -2529.8855 | 63.25% | 61.54% | 95% | 0% | 2459 | -272
[5 empty] | 2019-06-24 | 21 | 4185.5 | 2177 | -278 | 1 | 0 | 2455 | 1725.0618 | 1725.0618 | 1725.0618 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -318.0778 | 1406.984 | -3550 | -400 | -2543.016 | 63.58% | 61.54% | 95% | 0% | 2455 | -278
[5 empty] | 2019-06-24 | 22 | 4186 | 2162 | -296 | 1 | 0 | 2458 | 1729.7609 | 1729.7609 | 1729.7609 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -338.6728 | 1391.0882 | -3550 | -400 | -2558.9118 | 63.97% | 61.53% | 95% | 0% | 2458 | -296
[5 empty] | 2019-06-24 | 23 | 4186.5 | 2158 | -272 | 1 | 0 | 2430 | 1685.9027 | 1685.9027 | 1685.9027 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -311.2128 | 1374.6899 | -3550 | -400 | -2575.3101 | 64.38% | 61.53% | 95% | 0% | 2430 | -272
[5 empty] | 2019-06-24 | 24 | 4187 | 2136 | -299 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -342.1053 | 1351.6293 | -3550 | -400 | -2598.3707 | 64.96% | 61.53% | 95% | 0% | 2435 | -299
[5 empty] | 2019-06-24 | 25 | 4187.5 | 2128 | -298 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1408.6562 | 780 | 200 | 2388.6562 | 59.72% | 95% | 0% | -340.9611 | 1338.6762 | -3550 | -400 | -2611.3238 | 65.28% | 61.53% | 95% | 0% | 2426 | -298
[5 empty] | 2019-06-24 | 26 | 4188 | 2101 | -314 | 1 | 0 | 2415 | 1662.4073 | 1662.4073 | 1662.4073 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -359.2677 | 1303.1395 | -3550 | -400 | -2646.8605 | 66.17% | 61.53% | 95% | 0% | 2415 | -314
[5 empty] | 2019-06-24 | 27 | 4188.5 | 2072 | -335 | 1 | 0 | 2407 | 1649.8763 | 1649.8763 | 1649.8763 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -383.2952 | 1266.5811 | -3550 | -400 | -2683.4189 | 67.09% | 61.51% | 95% | 0% | 2407 | -335
[5 empty] | 2019-06-24 | 28 | 4189 | 2090 | -331 | 1 | 0 | 2421 | 1671.8054 | 1671.8054 | 1671.8054 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -378.7185 | 1293.0869 | -3550 | -400 | -2656.9131 | 66.42% | 61.51% | 95% | 0% | 2421 | -331
[5 empty] | 2019-06-24 | 29 | 4189.5 | 2094 | -336 | 1 | 0 | 2430 | 1685.9027 | 1685.9027 | 1685.9027 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -384.4394 | 1301.4634 | -3550 | -400 | -2648.5366 | 66.21% | 61.51% | 95% | 0% | 2430 | -336
[5 empty] | 2019-06-24 | 30 | 4190 | 2031 | -367 | 1 | 0 | 2398 | 1635.7791 | 1635.7791 | 1635.7791 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -419.9085 | 1215.8706 | -3550 | -400 | -2734.1294 | 68.35% | 61.5% | 95% | 0% | 2398 | -367
[5 empty] | 2019-06-24 | 31 | 4190.5 | 2025 | -354 | 1 | 0 | 2379 | 1606.0181 | 1606.0181 | 1606.0181 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -405.0343 | 1200.9838 | -3550 | -400 | -2749.0162 | 68.73% | 61.5% | 95% | 0% | 2379 | -354
[5 empty] | 2019-06-24 | 32 | 4191 | 2080 | -332 | 1 | 0 | 2412 | 1657.7082 | 1657.7082 | 1657.7082 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -379.8627 | 1277.8455 | -3550 | -400 | -2672.1545 | 66.8% | 61.5% | 95% | 0% | 2412 | -332
[5 empty] | 2019-06-24 | 33 | 4191.5 | 2106 | -336 | 1 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -384.4394 | 1320.2597 | -3550 | -400 | -2629.7403 | 65.74% | 61.5% | 95% | 0% | 2442 | -336
[5 empty] | 2019-06-24 | 34 | 4192 | 2184 | -286 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -327.2311 | 1421.3262 | -3550 | -400 | -2528.6738 | 63.22% | 61.49% | 95% | 0% | 2470 | -286
[5 empty] | 2019-06-24 | 35 | 4192.5 | 2255 | -247 | 1 | 0 | 2502 | 1798.681 | 1798.681 | 1798.681 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -282.6087 | 1516.0723 | -3550 | -400 | -2433.9277 | 60.85% | 61.49% | 95% | 0% | 2502 | -247
[5 empty] | 2019-06-24 | 36 | 4193 | 2300 | -209 | 1 | 0 | 2509 | 1809.6455 | 1809.6455 | 1809.6455 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -239.1304 | 1570.5151 | -3550 | -400 | -2379.4849 | 59.49% | 61.49% | 95% | 0% | 2509 | -209
[5 empty] | 2019-06-24 | 37 | 4193.5 | 2327 | -167 | 1 | 0 | 2494 | 1786.15 | 1786.15 | 1786.15 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -191.0755 | 1595.0745 | -3550 | -400 | -2354.9255 | 58.87% | 61.49% | 95% | 0% | 2494 | -167
[5 empty] | 2019-06-24 | 38 | 4194 | 2333 | -144 | 1 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -164.7597 | 1594.7621 | -3550 | -400 | -2355.2379 | 58.88% | 61.49% | 95% | 0% | 2477 | -144
[5 empty] | 2019-06-24 | 39 | 4194.5 | 2353 | -101 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 1407.0899 | 780 | 200 | 2387.0899 | 59.68% | 95% | 0% | -115.5606 | 1607.9348 | -3550 | -400 | -2342.0652 | 58.55% | 61.48% | 95% | 0% | 2454 | -101
[5 empty] | 2019-06-24 | 40 | 4195 | 2360 | -72 | 1 | 0 | 2432 | 1689.0354 | 1689.0354 | 1689.0354 | 1405.5235 | 780 | 200 | 2385.5235 | 59.64% | 95% | 0% | -82.3799 | 1606.6556 | -3550 | -400 | -2343.3444 | 58.58% | 61.48% | 95% | 0% | 2432 | -72
[5 empty] | 2019-06-24 | 41 | 4195.5 | 2355 | -54 | 1 | 0 | 2409 | 1653.0091 | 1653.0091 | 1653.0091 | 1405.5235 | 780 | 200 | 2385.5235 | 59.64% | 95% | 0% | -61.7849 | 1591.2242 | -3550 | -400 | -2358.7758 | 58.97% | 61.48% | 95% | 0% | 2409 | -54
[5 empty] | 2019-06-24 | 42 | 4196 | 2366 | -44 | 1 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 1405.5235 | 780 | 200 | 2385.5235 | 59.64% | 95% | 0% | -50.3432 | 1604.2322 | -3550 | -400 | -2345.7678 | 58.64% | 61.48% | 95% | 0% | 2410 | -44
[5 empty] | 2019-06-24 | 43 | 4196.5 | 2305 | -37 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 1405.5235 | 780 | 200 | 2385.5235 | 59.64% | 95% | 0% | -42.3341 | 1505.7286 | -3550 | -400 | -2444.2714 | 61.11% | 61.48% | 95% | 0% | 2342 | -37
[5 empty] | 2019-06-24 | 44 | 4197 | 2263 | -35 | 1 | 0 | 2298 | 1479.1426 | 1479.1426 | 1479.1426 | 1405.5235 | 780 | 200 | 2385.5235 | 59.64% | 95% | 0% | -40.0458 | 1439.0969 | -3550 | -400 | -2510.9031 | 62.77% | 61.48% | 95% | 0% | 2298 | -35
[5 empty] | 2019-06-24 | 45 | 4197.5 | 2211 | -35 | 1 | 0 | 2246 | 1397.6917 | 1397.6917 | 1397.6917 | 1405.5235 | 780 | 200 | 2385.5235 | 59.64% | 95% | 0% | -40.0458 | 1357.6459 | -3550 | -400 | -2592.3541 | 64.81% | 61.48% | 95% | 0% | 2246 | -35
[5 empty] | 2019-06-24 | 46 | 4198 | 2092 | -36 | 0 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1405.5235 | 780 | 200 | 2385.5235 | 59.64% | 95% | 0% | -41.1899 | 1171.6707 | -2750 | -200 | -1778.3293 | 44.46% | 61.48% | 95% | 0% | 2128 | -36
[5 empty] | 2019-06-24 | 47 | 4198.5 | 1935 | -37 | 0 | 0 | 1972 | 968.5078 | 968.5078 | 968.5078 | 1405.5235 | 780 | 200 | 2385.5235 | 59.64% | 95% | 0% | -42.3341 | 926.1737 | -2750 | -200 | -2023.8263 | 50.6% | 61.47% | 95% | 0% | 1972 | -37
[5 empty] | 2019-06-24 | 48 | 4199 | 1814 | -39 | 0 | 0 | 1853 | 782.1105 | 782.1105 | 782.1105 | 1405.5235 | 780 | 200 | 2385.5235 | 59.64% | 95% | 0% | -44.6224 | 737.488 | -2750 | -200 | -2212.512 | 55.31% | 61.47% | 95% | 0% | 1853 | -39
[5 empty] | 2019-06-25 | 1 | 4199.5 | 1718 | -41 | 0 | 0 | 1759 | 634.8722 | 634.8722 | 634.8722 | 1405.5235 | 780 | 200 | 2385.5235 | 59.64% | 95% | 0% | -46.9108 | 587.9615 | -2750 | -200 | -2362.0385 | 59.05% | 61.46% | 95% | 0% | 1759 | -41
[5 empty] | 2019-06-25 | 2 | 4200 | 1657 | -43 | 0 | 0 | 1700 | 542.4567 | 542.4567 | 542.4567 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -49.1991 | 493.2576 | -2750 | -200 | -2456.7424 | 61.42% | 61.45% | 95% | 0% | 1700 | -43
[5 empty] | 2019-06-25 | 3 | 4200.5 | 1627 | -45 | 0 | 0 | 1672 | 498.5985 | 498.5985 | 498.5985 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -51.4874 | 447.1111 | -2750 | -200 | -2502.8889 | 62.57% | 61.45% | 95% | 0% | 1672 | -45
[5 empty] | 2019-06-25 | 4 | 4201 | 1619 | -47 | 0 | 0 | 1666 | 489.2003 | 489.2003 | 489.2003 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -53.7757 | 435.4246 | -2750 | -200 | -2514.5754 | 62.86% | 61.45% | 95% | 0% | 1666 | -47
[5 empty] | 2019-06-25 | 5 | 4201.5 | 1579 | -49 | 0 | 0 | 1628 | 429.6785 | 429.6785 | 429.6785 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -56.0641 | 373.6144 | -2750 | -200 | -2576.3856 | 64.41% | 61.44% | 95% | 0% | 1628 | -49
[5 empty] | 2019-06-25 | 6 | 4202 | 1548 | -52 | 0 | 0 | 1600 | 385.8203 | 385.8203 | 385.8203 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -59.4966 | 326.3237 | -2750 | -200 | -2623.6763 | 65.59% | 61.44% | 95% | 0% | 1600 | -52
[5 empty] | 2019-06-25 | 7 | 4202.5 | 1527 | -55 | 0 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -62.9291 | 294.6967 | -2750 | -200 | -2655.3033 | 66.38% | 61.44% | 95% | 0% | 1582 | -55
[5 empty] | 2019-06-25 | 8 | 4203 | 1518 | -57 | 0 | 0 | 1575 | 346.6612 | 346.6612 | 346.6612 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -65.2174 | 281.4438 | -2750 | -200 | -2668.5562 | 66.71% | 61.43% | 95% | 0% | 1575 | -57
[5 empty] | 2019-06-25 | 9 | 4203.5 | 1516 | -61 | 0 | 0 | 1577 | 349.7939 | 349.7939 | 349.7939 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -69.7941 | 279.9998 | -2750 | -200 | -2670.0002 | 66.75% | 61.43% | 95% | 0% | 1577 | -61
[5 empty] | 2019-06-25 | 10 | 4204 | 1504 | -65 | 1 | 0 | 1569 | 337.263 | 337.263 | 337.263 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -74.3707 | 262.8923 | -3550 | -400 | -3687.1077 | 92.18% | 61.43% | 95% | 0% | 1569 | -65
[5 empty] | 2019-06-25 | 11 | 4204.5 | 1534 | -67 | 1 | 0 | 1601 | 387.3866 | 387.3866 | 387.3866 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -76.659 | 310.7276 | -3550 | -400 | -3639.2724 | 90.98% | 61.43% | 95% | 0% | 1601 | -67
[5 empty] | 2019-06-25 | 12 | 4205 | 1608 | -70 | 1 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -80.0915 | 427.9052 | -3550 | -400 | -3522.0948 | 88.05% | 61.43% | 95% | 0% | 1678 | -70
[5 empty] | 2019-06-25 | 13 | 4205.5 | 1793 | -76 | 1 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -86.9565 | 720.2158 | -3550 | -400 | -3229.7842 | 80.74% | 61.43% | 95% | 0% | 1869 | -76
[5 empty] | 2019-06-25 | 14 | 4206 | 1968 | -85 | 1 | 0 | 2053 | 1095.3833 | 1095.3833 | 1095.3833 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -97.254 | 998.1293 | -3550 | -400 | -2951.8707 | 73.8% | 61.43% | 95% | 0% | 2053 | -85
[5 empty] | 2019-06-25 | 15 | 4206.5 | 2173 | -103 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -117.849 | 1326.8336 | -3550 | -400 | -2623.1664 | 65.58% | 61.42% | 95% | 0% | 2276 | -103
[5 empty] | 2019-06-25 | 16 | 4207 | 2258 | -124 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -141.8764 | 1468.8408 | -3550 | -400 | -2481.1592 | 62.03% | 61.41% | 95% | 0% | 2382 | -124
[5 empty] | 2019-06-25 | 17 | 4207.5 | 2315 | -152 | 1 | 0 | 2467 | 1743.8582 | 1743.8582 | 1743.8582 | 1403.9571 | 780 | 200 | 2383.9571 | 59.6% | 95% | 0% | -173.913 | 1569.9452 | -3550 | -400 | -2380.0548 | 59.5% | 61.41% | 95% | 0% | 2467 | -152
[5 empty] | 2019-06-25 | 18 | 4208 | 2317 | -179 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -204.8055 | 1584.4773 | -3550 | -400 | -2365.5227 | 59.14% | 61.41% | 95% | 0% | 2496 | -179
[5 empty] | 2019-06-25 | 19 | 4208.5 | 2336 | -195 | 1 | 0 | 2531 | 1844.1055 | 1844.1055 | 1844.1055 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -223.1121 | 1620.9934 | -3550 | -400 | -2329.0066 | 58.23% | 61.4% | 95% | 0% | 2531 | -195
[5 empty] | 2019-06-25 | 20 | 4209 | 2324 | -202 | 1 | 0 | 2526 | 1836.2737 | 1836.2737 | 1836.2737 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -231.1213 | 1605.1524 | -3550 | -400 | -2344.8476 | 58.62% | 61.4% | 95% | 0% | 2526 | -202
[5 empty] | 2019-06-25 | 21 | 4209.5 | 2295 | -231 | 1 | 0 | 2526 | 1836.2737 | 1836.2737 | 1836.2737 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -264.3021 | 1571.9716 | -3550 | -400 | -2378.0284 | 59.45% | 61.4% | 95% | 0% | 2526 | -231
[5 empty] | 2019-06-25 | 22 | 4210 | 2273 | -258 | 1 | 0 | 2531 | 1844.1055 | 1844.1055 | 1844.1055 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -295.1945 | 1548.911 | -3550 | -400 | -2401.089 | 60.03% | 61.4% | 95% | 0% | 2531 | -258
[5 empty] | 2019-06-25 | 23 | 4210.5 | 2253 | -268 | 1 | 0 | 2521 | 1828.4419 | 1828.4419 | 1828.4419 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -306.6362 | 1521.8057 | -3550 | -400 | -2428.1943 | 60.7% | 61.4% | 95% | 0% | 2521 | -268
[5 empty] | 2019-06-25 | 24 | 4211 | 2237 | -279 | 1 | 0 | 2516 | 1820.6101 | 1820.6101 | 1820.6101 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -319.222 | 1501.3881 | -3550 | -400 | -2448.6119 | 61.22% | 61.4% | 95% | 0% | 2516 | -279
[5 empty] | 2019-06-25 | 25 | 4211.5 | 2218 | -278 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -318.0778 | 1471.205 | -3550 | -400 | -2478.795 | 61.97% | 61.4% | 95% | 0% | 2496 | -278
[5 empty] | 2019-06-25 | 26 | 4212 | 2192 | -274 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -313.5011 | 1428.7907 | -3550 | -400 | -2521.2093 | 63.03% | 61.4% | 95% | 0% | 2466 | -274
[5 empty] | 2019-06-25 | 27 | 4212.5 | 2156 | -277 | 1 | 0 | 2433 | 1690.6018 | 1690.6018 | 1690.6018 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -316.9336 | 1373.6682 | -3550 | -400 | -2576.3318 | 64.41% | 61.39% | 95% | 0% | 2433 | -277
[5 empty] | 2019-06-25 | 28 | 4213 | 2124 | -296 | 1 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -338.6728 | 1331.5663 | -3550 | -400 | -2618.4337 | 65.46% | 61.39% | 95% | 0% | 2420 | -296
[5 empty] | 2019-06-25 | 29 | 4213.5 | 2135 | -300 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -343.2494 | 1350.4851 | -3550 | -400 | -2599.5149 | 64.99% | 61.39% | 95% | 0% | 2435 | -300
[5 empty] | 2019-06-25 | 30 | 4214 | 2119 | -309 | 1 | 0 | 2428 | 1682.77 | 1682.77 | 1682.77 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -353.5469 | 1329.2231 | -3550 | -400 | -2620.7769 | 65.52% | 61.39% | 95% | 0% | 2428 | -309
[5 empty] | 2019-06-25 | 31 | 4214.5 | 2131 | -294 | 1 | 0 | 2425 | 1678.0709 | 1678.0709 | 1678.0709 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -336.3844 | 1341.6865 | -3550 | -400 | -2608.3135 | 65.21% | 61.39% | 95% | 0% | 2425 | -294
[5 empty] | 2019-06-25 | 32 | 4215 | 2191 | -267 | 1 | 0 | 2458 | 1729.7609 | 1729.7609 | 1729.7609 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -305.492 | 1424.2689 | -3550 | -400 | -2525.7311 | 63.14% | 61.39% | 95% | 0% | 2458 | -267
[5 empty] | 2019-06-25 | 33 | 4215.5 | 2245 | -250 | 1 | 0 | 2495 | 1787.7164 | 1787.7164 | 1787.7164 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -286.0412 | 1501.6752 | -3550 | -400 | -2448.3248 | 61.21% | 61.39% | 95% | 0% | 2495 | -250
[5 empty] | 2019-06-25 | 34 | 4216 | 2276 | -233 | 1 | 0 | 2509 | 1809.6455 | 1809.6455 | 1809.6455 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -266.5904 | 1543.0551 | -3550 | -400 | -2406.9449 | 60.17% | 61.38% | 95% | 0% | 2509 | -233
[5 empty] | 2019-06-25 | 35 | 4216.5 | 2287 | -234 | 1 | 0 | 2521 | 1828.4419 | 1828.4419 | 1828.4419 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -267.7346 | 1560.7073 | -3550 | -400 | -2389.2927 | 59.73% | 61.38% | 95% | 0% | 2521 | -234
[5 empty] | 2019-06-25 | 36 | 4217 | 2324 | -214 | 1 | 0 | 2538 | 1855.0701 | 1855.0701 | 1855.0701 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -244.8513 | 1610.2188 | -3550 | -400 | -2339.7812 | 58.49% | 61.38% | 95% | 0% | 2538 | -214
[5 empty] | 2019-06-25 | 37 | 4217.5 | 2340 | -188 | 1 | 0 | 2528 | 1839.4064 | 1839.4064 | 1839.4064 | 1402.3908 | 780 | 200 | 2382.3908 | 59.56% | 95% | 0% | -215.103 | 1624.3035 | -3550 | -400 | -2325.6965 | 58.14% | 61.38% | 95% | 0% | 2528 | -188
[5 empty] | 2019-06-25 | 38 | 4218 | 2360 | -165 | 1 | 0 | 2525 | 1834.7073 | 1834.7073 | 1834.7073 | 1400.8244 | 780 | 200 | 2380.8244 | 59.52% | 95% | 0% | -188.7872 | 1645.9202 | -3550 | -400 | -2304.0798 | 57.6% | 61.38% | 95% | 0% | 2525 | -165
[5 empty] | 2019-06-25 | 39 | 4218.5 | 2364 | -134 | 1 | 0 | 2498 | 1792.4155 | 1792.4155 | 1792.4155 | 1400.8244 | 780 | 200 | 2380.8244 | 59.52% | 95% | 0% | -153.3181 | 1639.0974 | -3550 | -400 | -2310.9026 | 57.77% | 61.37% | 95% | 0% | 2498 | -134
[5 empty] | 2019-06-25 | 40 | 4219 | 2333 | -113 | 1 | 0 | 2446 | 1710.9646 | 1710.9646 | 1710.9646 | 1400.8244 | 780 | 200 | 2380.8244 | 59.52% | 95% | 0% | -129.2906 | 1581.6739 | -3550 | -400 | -2368.3261 | 59.21% | 61.37% | 95% | 0% | 2446 | -113
[5 empty] | 2019-06-25 | 41 | 4219.5 | 2306 | -98 | 1 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 1400.8244 | 780 | 200 | 2380.8244 | 59.52% | 95% | 0% | -112.1281 | 1533.0491 | -3550 | -400 | -2416.9509 | 60.42% | 61.37% | 95% | 0% | 2404 | -98
[5 empty] | 2019-06-25 | 42 | 4220 | 2296 | -85 | 1 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 1400.8244 | 780 | 200 | 2380.8244 | 59.52% | 95% | 0% | -97.254 | 1511.8969 | -3550 | -400 | -2438.1031 | 60.95% | 61.37% | 95% | 0% | 2381 | -85
[5 empty] | 2019-06-25 | 43 | 4220.5 | 2256 | -80 | 1 | 0 | 2336 | 1538.6645 | 1538.6645 | 1538.6645 | 1400.8244 | 780 | 200 | 2380.8244 | 59.52% | 95% | 0% | -91.5332 | 1447.1313 | -3550 | -400 | -2502.8687 | 62.57% | 61.37% | 95% | 0% | 2336 | -80
[5 empty] | 2019-06-25 | 44 | 4221 | 2213 | -78 | 1 | 0 | 2291 | 1468.1781 | 1468.1781 | 1468.1781 | 1400.8244 | 780 | 200 | 2380.8244 | 59.52% | 95% | 0% | -89.2449 | 1378.9332 | -3550 | -400 | -2571.0668 | 64.28% | 61.36% | 95% | 0% | 2291 | -78
[5 empty] | 2019-06-25 | 45 | 4221.5 | 2130 | -77 | 0 | 0 | 2207 | 1336.6035 | 1336.6035 | 1336.6035 | 1400.8244 | 780 | 200 | 2380.8244 | 59.52% | 95% | 0% | -88.1007 | 1248.5028 | -2750 | -200 | -1701.4972 | 42.54% | 61.36% | 95% | 0% | 2207 | -77
[5 empty] | 2019-06-25 | 46 | 4222 | 1985 | -76 | 0 | 0 | 2061 | 1107.9143 | 1107.9143 | 1107.9143 | 1399.258 | 780 | 200 | 2379.258 | 59.48% | 95% | 0% | -86.9565 | 1020.9577 | -2750 | -200 | -1929.0423 | 48.23% | 61.35% | 95% | 0% | 2061 | -76
[5 empty] | 2019-06-25 | 47 | 4222.5 | 1842 | -75 | 0 | 0 | 1917 | 882.3578 | 882.3578 | 882.3578 | 1399.258 | 780 | 200 | 2379.258 | 59.48% | 95% | 0% | -85.8124 | 796.5454 | -2750 | -200 | -2153.4546 | 53.84% | 61.35% | 95% | 0% | 1917 | -75
[5 empty] | 2019-06-25 | 48 | 4223 | 1728 | -75 | 0 | 0 | 1803 | 703.7923 | 703.7923 | 703.7923 | 1399.258 | 780 | 200 | 2379.258 | 59.48% | 95% | 0% | -85.8124 | 617.9799 | -2750 | -200 | -2332.0201 | 58.3% | 61.35% | 95% | 0% | 1803 | -75
[5 empty] | 2019-06-26 | 1 | 4223.5 | 1628 | -79 | 0 | 0 | 1707 | 553.4213 | 553.4213 | 553.4213 | 1399.258 | 780 | 200 | 2379.258 | 59.48% | 95% | 0% | -90.389 | 463.0323 | -2750 | -200 | -2486.9677 | 62.17% | 61.35% | 95% | 0% | 1707 | -79
[5 empty] | 2019-06-26 | 2 | 4224 | 1572 | -82 | 0 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 1399.258 | 780 | 200 | 2379.258 | 59.48% | 95% | 0% | -93.8215 | 376.5824 | -2750 | -200 | -2573.4176 | 64.34% | 61.35% | 95% | 0% | 1654 | -82
[5 empty] | 2019-06-26 | 3 | 4224.5 | 1537 | -81 | 0 | 0 | 1618 | 414.0148 | 414.0148 | 414.0148 | 1399.258 | 780 | 200 | 2379.258 | 59.48% | 95% | 0% | -92.6773 | 321.3375 | -2750 | -200 | -2628.6625 | 65.72% | 61.34% | 95% | 0% | 1618 | -81
[5 empty] | 2019-06-26 | 4 | 4225 | 1519 | -79 | 0 | 0 | 1598 | 382.6876 | 382.6876 | 382.6876 | 1399.258 | 780 | 200 | 2379.258 | 59.48% | 95% | 0% | -90.389 | 292.2985 | -2750 | -200 | -2657.7015 | 66.44% | 61.34% | 95% | 0% | 1598 | -79
[5 empty] | 2019-06-26 | 5 | 4225.5 | 1496 | -79 | 0 | 0 | 1575 | 346.6612 | 346.6612 | 346.6612 | 1399.258 | 780 | 200 | 2379.258 | 59.48% | 95% | 0% | -90.389 | 256.2722 | -2750 | -200 | -2693.7278 | 67.34% | 61.34% | 95% | 0% | 1575 | -79
[5 empty] | 2019-06-26 | 6 | 4226 | 1476 | -79 | 0 | 0 | 1555 | 315.3339 | 315.3339 | 315.3339 | 1399.258 | 780 | 200 | 2379.258 | 59.48% | 95% | 0% | -90.389 | 224.9449 | -2750 | -200 | -2725.0551 | 68.13% | 61.34% | 95% | 0% | 1555 | -79
[5 empty] | 2019-06-26 | 7 | 4226.5 | 1467 | -78 | 0 | 0 | 1545 | 299.6702 | 299.6702 | 299.6702 | 1399.258 | 780 | 200 | 2379.258 | 59.48% | 95% | 0% | -89.2449 | 210.4254 | -2750 | -200 | -2739.5746 | 68.49% | 61.34% | 95% | 0% | 1545 | -78
[5 empty] | 2019-06-26 | 8 | 4227 | 1456 | -77 | 0 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 1399.258 | 780 | 200 | 2379.258 | 59.48% | 95% | 0% | -88.1007 | 192.7732 | -2750 | -200 | -2757.2268 | 68.93% | 61.33% | 95% | 0% | 1533 | -77
[5 empty] | 2019-06-26 | 9 | 4227.5 | 1456 | -78 | 1 | 0 | 1534 | 282.4402 | 282.4402 | 282.4402 | 1399.258 | 780 | 200 | 2379.258 | 59.48% | 95% | 0% | -89.2449 | 193.1954 | -3550 | -400 | -3756.8046 | 93.92% | 61.33% | 95% | 0% | 1534 | -78
[5 empty] | 2019-06-26 | 10 | 4228 | 1452 | -79 | 1 | 0 | 1531 | 277.7411 | 277.7411 | 277.7411 | 1397.6917 | 780 | 200 | 2377.6917 | 59.44% | 95% | 0% | -90.389 | 187.3521 | -3550 | -400 | -3762.6479 | 94.07% | 61.33% | 95% | 0% | 1531 | -79
[5 empty] | 2019-06-26 | 11 | 4228.5 | 1485 | -80 | 1 | 0 | 1565 | 330.9975 | 330.9975 | 330.9975 | 1397.6917 | 780 | 200 | 2377.6917 | 59.44% | 95% | 0% | -91.5332 | 239.4643 | -3550 | -400 | -3710.5357 | 92.76% | 61.32% | 95% | 0% | 1565 | -80
[5 empty] | 2019-06-26 | 12 | 4229 | 1554 | -85 | 1 | 0 | 1639 | 446.9085 | 446.9085 | 446.9085 | 1397.6917 | 780 | 200 | 2377.6917 | 59.44% | 95% | 0% | -97.254 | 349.6545 | -3550 | -400 | -3600.3455 | 90.01% | 61.32% | 95% | 0% | 1639 | -85
[5 empty] | 2019-06-26 | 13 | 4229.5 | 1740 | -91 | 1 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 1397.6917 | 780 | 200 | 2377.6917 | 59.44% | 95% | 0% | -104.119 | 643.5315 | -3550 | -400 | -3306.4685 | 82.66% | 61.32% | 95% | 0% | 1831 | -91
[5 empty] | 2019-06-26 | 14 | 4230 | 1918 | -102 | 1 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 1397.6917 | 780 | 200 | 2377.6917 | 59.44% | 95% | 0% | -116.7048 | 926.9885 | -3550 | -400 | -3023.0115 | 75.58% | 61.32% | 95% | 0% | 2020 | -102
[5 empty] | 2019-06-26 | 15 | 4230.5 | 2124 | -118 | 1 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 1397.6917 | 780 | 200 | 2377.6917 | 59.44% | 95% | 0% | -135.0114 | 1256.4148 | -3550 | -400 | -2693.5852 | 67.34% | 61.32% | 95% | 0% | 2242 | -118
[5 empty] | 2019-06-26 | 16 | 4231 | 2216 | -133 | 1 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 1397.6917 | 780 | 200 | 2377.6917 | 59.44% | 95% | 0% | -152.1739 | 1406.8533 | -3550 | -400 | -2543.1467 | 63.58% | 61.31% | 95% | 0% | 2349 | -133
[5 empty] | 2019-06-26 | 17 | 4231.5 | 2273 | -145 | 1 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 1397.6917 | 780 | 200 | 2377.6917 | 59.44% | 95% | 0% | -165.9039 | 1501.2025 | -3550 | -400 | -2448.7975 | 61.22% | 61.31% | 95% | 0% | 2418 | -145
[5 empty] | 2019-06-26 | 18 | 4232 | 2234 | -173 | 1 | 0 | 2407 | 1649.8763 | 1649.8763 | 1649.8763 | 1397.6917 | 780 | 200 | 2377.6917 | 59.44% | 95% | 0% | -197.9405 | 1451.9358 | -3550 | -400 | -2498.0642 | 62.45% | 61.3% | 95% | 0% | 2407 | -173
[5 empty] | 2019-06-26 | 19 | 4232.5 | 2243 | -199 | 1 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 1397.6917 | 780 | 200 | 2377.6917 | 59.44% | 95% | 0% | -227.6888 | 1477.0103 | -3550 | -400 | -2472.9897 | 61.82% | 61.3% | 95% | 0% | 2442 | -199
[5 empty] | 2019-06-26 | 20 | 4233 | 2230 | -228 | 1 | 0 | 2458 | 1729.7609 | 1729.7609 | 1729.7609 | 1397.6917 | 780 | 200 | 2377.6917 | 59.44% | 95% | 0% | -260.8696 | 1468.8914 | -3550 | -400 | -2481.1086 | 62.03% | 61.29% | 95% | 0% | 2458 | -228
[5 empty] | 2019-06-26 | 21 | 4233.5 | 2188 | -267 | 1 | 0 | 2455 | 1725.0618 | 1725.0618 | 1725.0618 | 1396.1253 | 780 | 200 | 2376.1253 | 59.4% | 95% | 0% | -305.492 | 1419.5698 | -3550 | -400 | -2530.4302 | 63.26% | 61.29% | 95% | 0% | 2455 | -267
[5 empty] | 2019-06-26 | 22 | 4234 | 2126 | -301 | 1 | 0 | 2427 | 1681.2036 | 1681.2036 | 1681.2036 | 1396.1253 | 780 | 200 | 2376.1253 | 59.4% | 95% | 0% | -344.3936 | 1336.81 | -3550 | -400 | -2613.19 | 65.33% | 61.29% | 95% | 0% | 2427 | -301
[5 empty] | 2019-06-26 | 23 | 4234.5 | 2111 | -343 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 1396.1253 | 780 | 200 | 2376.1253 | 59.4% | 95% | 0% | -392.4485 | 1331.047 | -3550 | -400 | -2618.953 | 65.47% | 61.29% | 95% | 0% | 2454 | -343
[5 empty] | 2019-06-26 | 24 | 4235 | 2070 | -378 | 1 | 0 | 2448 | 1714.0973 | 1714.0973 | 1714.0973 | 1396.1253 | 780 | 200 | 2376.1253 | 59.4% | 95% | 0% | -432.4943 | 1281.603 | -3550 | -400 | -2668.397 | 66.71% | 61.29% | 95% | 0% | 2448 | -378
[5 empty] | 2019-06-26 | 25 | 4235.5 | 1999 | -404 | 1 | 0 | 2403 | 1643.6109 | 1643.6109 | 1643.6109 | 1396.1253 | 780 | 200 | 2376.1253 | 59.4% | 95% | 0% | -462.2426 | 1181.3683 | -3550 | -400 | -2768.6317 | 69.22% | 61.28% | 95% | 0% | 2403 | -404
[5 empty] | 2019-06-26 | 26 | 4236 | 1952 | -429 | 1 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 1396.1253 | 780 | 200 | 2376.1253 | 59.4% | 95% | 0% | -490.8467 | 1118.3042 | -3550 | -400 | -2831.6958 | 70.79% | 61.28% | 95% | 0% | 2381 | -429
[5 empty] | 2019-06-26 | 27 | 4236.5 | 1896 | -460 | 1 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 1396.1253 | 780 | 200 | 2376.1253 | 59.4% | 95% | 0% | -526.3158 | 1043.676 | -3550 | -400 | -2906.324 | 72.66% | 61.28% | 95% | 0% | 2356 | -460
[5 empty] | 2019-06-26 | 28 | 4237 | 1839 | -480 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -549.1991 | 962.8372 | -3550 | -400 | -2987.1628 | 74.68% | 61.28% | 95% | 0% | 2319 | -480
[5 empty] | 2019-06-26 | 29 | 4237.5 | 1787 | -497 | 1 | 0 | 2284 | 1457.2135 | 1457.2135 | 1457.2135 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -568.6499 | 888.5636 | -3550 | -400 | -3061.4364 | 76.54% | 61.27% | 95% | 0% | 2284 | -497
[5 empty] | 2019-06-26 | 30 | 4238 | 1761 | -498 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -569.7941 | 848.2604 | -3550 | -400 | -3101.7396 | 77.54% | 61.27% | 95% | 0% | 2259 | -498
[5 empty] | 2019-06-26 | 31 | 4238.5 | 1735 | -497 | 1 | 0 | 2232 | 1375.7626 | 1375.7626 | 1375.7626 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -568.6499 | 807.1127 | -3550 | -400 | -3142.8873 | 78.57% | 61.26% | 95% | 0% | 2232 | -497
[5 empty] | 2019-06-26 | 32 | 4239 | 1790 | -476 | 1 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -544.6224 | 884.3965 | -3550 | -400 | -3065.6035 | 76.64% | 61.26% | 95% | 0% | 2266 | -476
[5 empty] | 2019-06-26 | 33 | 4239.5 | 1854 | -452 | 1 | 0 | 2306 | 1491.6735 | 1491.6735 | 1491.6735 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -517.1625 | 974.5111 | -3550 | -400 | -2975.4889 | 74.39% | 61.26% | 95% | 0% | 2306 | -452
[5 empty] | 2019-06-26 | 34 | 4240 | 1960 | -407 | 1 | 0 | 2367 | 1587.2218 | 1587.2218 | 1587.2218 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -465.6751 | 1121.5467 | -3550 | -400 | -2828.4533 | 70.71% | 61.26% | 95% | 0% | 2367 | -407
[5 empty] | 2019-06-26 | 35 | 4240.5 | 2053 | -363 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -415.3318 | 1248.6418 | -3550 | -400 | -2701.3582 | 67.53% | 61.25% | 95% | 0% | 2416 | -363
[5 empty] | 2019-06-26 | 36 | 4241 | 2143 | -307 | 1 | 0 | 2450 | 1717.23 | 1717.23 | 1717.23 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -351.2586 | 1365.9714 | -3550 | -400 | -2584.0286 | 64.6% | 61.25% | 95% | 0% | 2450 | -307
[5 empty] | 2019-06-26 | 37 | 4241.5 | 2204 | -252 | 1 | 0 | 2456 | 1726.6282 | 1726.6282 | 1726.6282 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -288.3295 | 1438.2987 | -3550 | -400 | -2511.7013 | 62.79% | 61.24% | 95% | 0% | 2456 | -252
[5 empty] | 2019-06-26 | 38 | 4242 | 2242 | -207 | 1 | 0 | 2449 | 1715.6636 | 1715.6636 | 1715.6636 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -236.8421 | 1478.8215 | -3550 | -400 | -2471.1785 | 61.78% | 61.24% | 95% | 0% | 2449 | -207
[5 empty] | 2019-06-26 | 39 | 4242.5 | 2279 | -170 | 1 | 0 | 2449 | 1715.6636 | 1715.6636 | 1715.6636 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -194.508 | 1521.1556 | -3550 | -400 | -2428.8444 | 60.72% | 61.24% | 95% | 0% | 2449 | -170
[5 empty] | 2019-06-26 | 40 | 4243 | 2282 | -141 | 1 | 0 | 2423 | 1674.9382 | 1674.9382 | 1674.9382 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -161.3272 | 1513.6109 | -3550 | -400 | -2436.3891 | 60.91% | 61.23% | 95% | 0% | 2423 | -141
[5 empty] | 2019-06-26 | 41 | 4243.5 | 2263 | -115 | 1 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -131.5789 | 1472.8728 | -3550 | -400 | -2477.1272 | 61.93% | 61.23% | 95% | 0% | 2378 | -115
[5 empty] | 2019-06-26 | 42 | 4244 | 2238 | -98 | 1 | 0 | 2336 | 1538.6645 | 1538.6645 | 1538.6645 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -112.1281 | 1426.5363 | -3550 | -400 | -2523.4637 | 63.09% | 61.22% | 95% | 0% | 2336 | -98
[5 empty] | 2019-06-26 | 43 | 4244.5 | 2206 | -92 | 1 | 0 | 2298 | 1479.1426 | 1479.1426 | 1479.1426 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -105.2632 | 1373.8795 | -3550 | -400 | -2576.1205 | 64.4% | 61.22% | 95% | 0% | 2298 | -92
[5 empty] | 2019-06-26 | 44 | 4245 | 2157 | -90 | 1 | 0 | 2247 | 1399.258 | 1399.258 | 1399.258 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -102.9748 | 1296.2832 | -3550 | -400 | -2653.7168 | 66.34% | 61.22% | 95% | 0% | 2247 | -90
[5 empty] | 2019-06-26 | 45 | 4245.5 | 2088 | -90 | 0 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -102.9748 | 1188.2041 | -2750 | -200 | -1761.7959 | 44.04% | 61.22% | 95% | 0% | 2178 | -90
[5 empty] | 2019-06-26 | 46 | 4246 | 1972 | -89 | 0 | 0 | 2061 | 1107.9143 | 1107.9143 | 1107.9143 | 1394.5589 | 780 | 200 | 2374.5589 | 59.36% | 95% | 0% | -101.8307 | 1006.0836 | -2750 | -200 | -1943.9164 | 48.6% | 61.21% | 95% | 0% | 2061 | -89
[5 empty] | 2019-06-26 | 47 | 4246.5 | 1828 | -88 | 0 | 0 | 1916 | 880.7914 | 880.7914 | 880.7914 | 1392.9926 | 780 | 200 | 2372.9926 | 59.32% | 95% | 0% | -100.6865 | 780.1049 | -2750 | -200 | -2169.8951 | 54.25% | 61.21% | 95% | 0% | 1916 | -88
[5 empty] | 2019-06-26 | 48 | 4247 | 1714 | -87 | 0 | 0 | 1801 | 700.6595 | 700.6595 | 700.6595 | 1392.9926 | 780 | 200 | 2372.9926 | 59.32% | 95% | 0% | -99.5423 | 601.1172 | -2750 | -200 | -2348.8828 | 58.72% | 61.21% | 95% | 0% | 1801 | -87
[5 empty] | 2019-06-27 | 1 | 4247.5 | 1622 | -86 | 0 | 0 | 1708 | 554.9876 | 554.9876 | 554.9876 | 1392.9926 | 780 | 200 | 2372.9926 | 59.32% | 95% | 0% | -98.3982 | 456.5895 | -2750 | -200 | -2493.4105 | 62.34% | 61.2% | 95% | 0% | 1708 | -86
[5 empty] | 2019-06-27 | 2 | 4248 | 1559 | -85 | 0 | 0 | 1644 | 454.7403 | 454.7403 | 454.7403 | 1392.9926 | 780 | 200 | 2372.9926 | 59.32% | 95% | 0% | -97.254 | 357.4863 | -2750 | -200 | -2592.5137 | 64.81% | 61.19% | 95% | 0% | 1644 | -85
[5 empty] | 2019-06-27 | 3 | 4248.5 | 1526 | -83 | 0 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 1392.9926 | 780 | 200 | 2372.9926 | 59.32% | 95% | 0% | -94.9657 | 304.9519 | -2750 | -200 | -2645.0481 | 66.13% | 61.19% | 95% | 0% | 1609 | -83
[5 empty] | 2019-06-27 | 4 | 4249 | 1517 | -82 | 0 | 0 | 1599 | 384.2539 | 384.2539 | 384.2539 | 1392.9926 | 780 | 200 | 2372.9926 | 59.32% | 95% | 0% | -93.8215 | 290.4324 | -2750 | -200 | -2659.5676 | 66.49% | 61.19% | 95% | 0% | 1599 | -82
[5 empty] | 2019-06-27 | 5 | 4249.5 | 1500 | -81 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 1392.9926 | 780 | 200 | 2372.9926 | 59.32% | 95% | 0% | -92.6773 | 263.382 | -2750 | -200 | -2686.618 | 67.17% | 61.18% | 95% | 0% | 1581 | -81
[5 empty] | 2019-06-27 | 6 | 4250 | 1473 | -80 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 1392.9926 | 780 | 200 | 2372.9926 | 59.32% | 95% | 0% | -91.5332 | 220.668 | -2750 | -200 | -2729.332 | 68.23% | 61.18% | 95% | 0% | 1553 | -80
[5 empty] | 2019-06-27 | 7 | 4250.5 | 1460 | -79 | 0 | 0 | 1539 | 290.2721 | 290.2721 | 290.2721 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -90.389 | 199.883 | -2750 | -200 | -2750.117 | 68.75% | 61.18% | 95% | 0% | 1539 | -79
[5 empty] | 2019-06-27 | 8 | 4251 | 1451 | -79 | 0 | 0 | 1530 | 276.1748 | 276.1748 | 276.1748 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -90.389 | 185.7858 | -2750 | -200 | -2764.2142 | 69.11% | 61.18% | 95% | 0% | 1530 | -79
[5 empty] | 2019-06-27 | 9 | 4251.5 | 1444 | -78 | 0 | 0 | 1522 | 263.6439 | 263.6439 | 263.6439 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -89.2449 | 174.399 | -2750 | -200 | -2775.601 | 69.39% | 61.18% | 95% | 0% | 1522 | -78
[5 empty] | 2019-06-27 | 10 | 4252 | 1429 | -78 | 1 | 0 | 1507 | 240.1484 | 240.1484 | 240.1484 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -89.2449 | 150.9035 | -3550 | -400 | -3799.0965 | 94.98% | 61.17% | 95% | 0% | 1507 | -78
[5 empty] | 2019-06-27 | 11 | 4252.5 | 1458 | -82 | 1 | 0 | 1540 | 291.8384 | 291.8384 | 291.8384 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -93.8215 | 198.0169 | -3550 | -400 | -3751.9831 | 93.8% | 61.17% | 95% | 0% | 1540 | -82
[5 empty] | 2019-06-27 | 12 | 4253 | 1522 | -99 | 1 | 0 | 1621 | 418.7139 | 418.7139 | 418.7139 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -113.2723 | 305.4416 | -3550 | -400 | -3644.5584 | 91.11% | 61.17% | 95% | 0% | 1621 | -99
[5 empty] | 2019-06-27 | 13 | 4253.5 | 1675 | -129 | 1 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -147.5973 | 557.7614 | -3550 | -400 | -3392.2386 | 84.81% | 61.17% | 95% | 0% | 1804 | -129
[5 empty] | 2019-06-27 | 14 | 4254 | 1815 | -167 | 1 | 0 | 1982 | 984.1715 | 984.1715 | 984.1715 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -191.0755 | 793.096 | -3550 | -400 | -3156.904 | 78.92% | 61.17% | 95% | 0% | 1982 | -167
[5 empty] | 2019-06-27 | 15 | 4254.5 | 1951 | -215 | 1 | 0 | 2166 | 1272.3825 | 1272.3825 | 1272.3825 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -245.9954 | 1026.3871 | -3550 | -400 | -2923.6129 | 73.09% | 61.16% | 95% | 0% | 2166 | -215
[5 empty] | 2019-06-27 | 16 | 4255 | 1978 | -273 | 1 | 0 | 2251 | 1405.5235 | 1405.5235 | 1405.5235 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -312.357 | 1093.1665 | -3550 | -400 | -2856.8335 | 71.42% | 61.16% | 95% | 0% | 2251 | -273
[5 empty] | 2019-06-27 | 17 | 4255.5 | 1936 | -342 | 1 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -391.3043 | 1056.511 | -3550 | -400 | -2893.489 | 72.34% | 61.15% | 95% | 0% | 2278 | -342
[5 empty] | 2019-06-27 | 18 | 4256 | 1811 | -416 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -475.9725 | 891.9582 | -3550 | -400 | -3058.0418 | 76.45% | 61.15% | 95% | 0% | 2227 | -416
[5 empty] | 2019-06-27 | 19 | 4256.5 | 1714 | -496 | 1 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 1391.4262 | 780 | 200 | 2371.4262 | 59.29% | 95% | 0% | -567.5057 | 773.7968 | -3550 | -400 | -3176.2032 | 79.41% | 61.15% | 95% | 0% | 2210 | -496
[5 empty] | 2019-06-27 | 20 | 4257 | 1603 | -565 | 1 | 0 | 2168 | 1275.5153 | 1275.5153 | 1275.5153 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -646.4531 | 629.0622 | -3550 | -400 | -3320.9378 | 83.02% | 61.15% | 95% | 0% | 2168 | -565
[5 empty] | 2019-06-27 | 21 | 4257.5 | 1497 | -628 | 1 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -718.5355 | 489.6261 | -3550 | -400 | -3460.3739 | 86.51% | 61.14% | 95% | 0% | 2125 | -628
[5 empty] | 2019-06-27 | 22 | 4258 | 1403 | -684 | 1 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -782.6087 | 366.031 | -3550 | -400 | -3583.969 | 89.6% | 61.14% | 95% | 0% | 2087 | -684
[5 empty] | 2019-06-27 | 23 | 4258.5 | 1320 | -730 | 1 | 0 | 2050 | 1090.6843 | 1090.6843 | 1090.6843 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -835.2403 | 255.444 | -3550 | -400 | -3694.556 | 92.36% | 61.14% | 95% | 0% | 2050 | -730
[5 empty] | 2019-06-27 | 24 | 4259 | 1278 | -766 | 1 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -876.4302 | 204.8559 | -3550 | -400 | -3745.1441 | 93.63% | 61.14% | 95% | 0% | 2044 | -766
[5 empty] | 2019-06-27 | 25 | 4259.5 | 1250 | -794 | 1 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -908.4668 | 172.8192 | -3550 | -400 | -3777.1808 | 94.43% | 61.14% | 95% | 0% | 2044 | -794
[5 empty] | 2019-06-27 | 26 | 4260 | 1219 | -803 | 1 | 0 | 2022 | 1046.8261 | 1046.8261 | 1046.8261 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -918.7643 | 128.0617 | -3550 | -400 | -3821.9383 | 95.55% | 61.13% | 95% | 0% | 2022 | -803
[5 empty] | 2019-06-27 | 27 | 4260.5 | 1186 | -804 | 1 | 0 | 1990 | 996.7024 | 996.7024 | 996.7024 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -919.9085 | 76.7939 | -3550 | -400 | -3873.2061 | 96.83% | 61.13% | 95% | 0% | 1990 | -804
[5 empty] | 2019-06-27 | 28 | 4261 | 1169 | -802 | 1 | 0 | 1971 | 966.9415 | 966.9415 | 966.9415 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -917.6201 | 49.3213 | -3550 | -400 | -3900.6787 | 97.52% | 61.13% | 95% | 0% | 1971 | -802
[5 empty] | 2019-06-27 | 29 | 4261.5 | 1171 | -787 | 1 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -900.4577 | 46.1211 | -3550 | -400 | -3903.8789 | 97.6% | 61.13% | 95% | 0% | 1958 | -787
[5 empty] | 2019-06-27 | 30 | 4262 | 1211 | -753 | 1 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -861.5561 | 94.4209 | -3550 | -400 | -3855.5791 | 96.39% | 61.12% | 95% | 0% | 1964 | -753
[5 empty] | 2019-06-27 | 31 | 4262.5 | 1240 | -721 | 1 | 0 | 1961 | 951.2778 | 951.2778 | 951.2778 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -824.9428 | 126.335 | -3550 | -400 | -3823.665 | 95.59% | 61.12% | 95% | 0% | 1961 | -721
[5 empty] | 2019-06-27 | 32 | 4263 | 1327 | -679 | 1 | 0 | 2006 | 1021.7642 | 1021.7642 | 1021.7642 | 1389.8599 | 780 | 200 | 2369.8599 | 59.25% | 95% | 0% | -776.8879 | 244.8763 | -3550 | -400 | -3705.1237 | 92.63% | 61.12% | 95% | 0% | 2006 | -679
[5 empty] | 2019-06-27 | 33 | 4263.5 | 1446 | -621 | 1 | 0 | 2067 | 1117.3124 | 1117.3124 | 1117.3124 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -710.5263 | 406.7861 | -3550 | -400 | -3543.2139 | 88.58% | 61.11% | 95% | 0% | 2067 | -621
[5 empty] | 2019-06-27 | 34 | 4264 | 1573 | -559 | 1 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -639.5881 | 579.538 | -3550 | -400 | -3370.462 | 84.26% | 61.11% | 95% | 0% | 2132 | -559
[5 empty] | 2019-06-27 | 35 | 4264.5 | 1710 | -489 | 1 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -559.4966 | 764.576 | -3550 | -400 | -3185.424 | 79.64% | 61.11% | 95% | 0% | 2199 | -489
[5 empty] | 2019-06-27 | 36 | 4265 | 1826 | -418 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -478.2609 | 916.2981 | -3550 | -400 | -3033.7019 | 75.84% | 61.11% | 95% | 0% | 2244 | -418
[5 empty] | 2019-06-27 | 37 | 4265.5 | 1900 | -349 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -399.3135 | 1003.0773 | -3550 | -400 | -2946.9227 | 73.67% | 61.11% | 95% | 0% | 2249 | -349
[5 empty] | 2019-06-27 | 38 | 4266 | 1986 | -287 | 1 | 0 | 2273 | 1439.9835 | 1439.9835 | 1439.9835 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -328.3753 | 1111.6082 | -3550 | -400 | -2838.3918 | 70.96% | 61.11% | 95% | 0% | 2273 | -287
[5 empty] | 2019-06-27 | 39 | 4266.5 | 2079 | -232 | 1 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -265.4462 | 1234.0591 | -3550 | -400 | -2715.9409 | 67.9% | 61.11% | 95% | 0% | 2311 | -232
[5 empty] | 2019-06-27 | 40 | 4267 | 2145 | -187 | 1 | 0 | 2332 | 1532.399 | 1532.399 | 1532.399 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -213.9588 | 1318.4402 | -3550 | -400 | -2631.5598 | 65.79% | 61.11% | 95% | 0% | 2332 | -187
[5 empty] | 2019-06-27 | 41 | 4267.5 | 2158 | -148 | 1 | 0 | 2306 | 1491.6735 | 1491.6735 | 1491.6735 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -169.3364 | 1322.3372 | -3550 | -400 | -2627.6628 | 65.69% | 61.1% | 95% | 0% | 2306 | -148
[5 empty] | 2019-06-27 | 42 | 4268 | 2165 | -119 | 1 | 0 | 2284 | 1457.2135 | 1457.2135 | 1457.2135 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -136.1556 | 1321.0579 | -3550 | -400 | -2628.9421 | 65.72% | 61.09% | 95% | 0% | 2284 | -119
[5 empty] | 2019-06-27 | 43 | 4268.5 | 2134 | -105 | 1 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -120.1373 | 1266.5898 | -3550 | -400 | -2683.4102 | 67.09% | 61.09% | 95% | 0% | 2239 | -105
[5 empty] | 2019-06-27 | 44 | 4269 | 2089 | -102 | 1 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -116.7048 | 1194.8368 | -3550 | -400 | -2755.1632 | 68.88% | 61.08% | 95% | 0% | 2191 | -102
[5 empty] | 2019-06-27 | 45 | 4269.5 | 2047 | -102 | 1 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -116.7048 | 1129.0495 | -3550 | -400 | -2820.9505 | 70.52% | 61.08% | 95% | 0% | 2149 | -102
[5 empty] | 2019-06-27 | 46 | 4270 | 1947 | -101 | 0 | 0 | 2048 | 1087.5515 | 1087.5515 | 1087.5515 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -115.5606 | 971.9909 | -2750 | -200 | -1978.0091 | 49.45% | 61.08% | 95% | 0% | 2048 | -101
[5 empty] | 2019-06-27 | 47 | 4270.5 | 1802 | -100 | 0 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 1388.2935 | 780 | 200 | 2368.2935 | 59.21% | 95% | 0% | -114.4165 | 744.4458 | -2750 | -200 | -2205.5542 | 55.14% | 61.08% | 95% | 0% | 1902 | -100
[5 empty] | 2019-06-27 | 48 | 4271 | 1683 | -99 | 0 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -113.2723 | 557.6263 | -2750 | -200 | -2392.3737 | 59.81% | 61.07% | 95% | 0% | 1782 | -99
[5 empty] | 2019-06-28 | 1 | 4271.5 | 1581 | -99 | 0 | 0 | 1680 | 511.1294 | 511.1294 | 511.1294 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -113.2723 | 397.8571 | -2750 | -200 | -2552.1429 | 63.8% | 61.07% | 95% | 0% | 1680 | -99
[5 empty] | 2019-06-28 | 2 | 4272 | 1521 | -99 | 0 | 0 | 1620 | 417.1476 | 417.1476 | 417.1476 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -113.2723 | 303.8753 | -2750 | -200 | -2646.1247 | 66.15% | 61.07% | 95% | 0% | 1620 | -99
[5 empty] | 2019-06-28 | 3 | 4272.5 | 1484 | -97 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -110.984 | 245.0754 | -2750 | -200 | -2704.9246 | 67.62% | 61.07% | 95% | 0% | 1581 | -97
[5 empty] | 2019-06-28 | 4 | 4273 | 1461 | -94 | 0 | 0 | 1555 | 315.3339 | 315.3339 | 315.3339 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -107.5515 | 207.7824 | -2750 | -200 | -2742.2176 | 68.56% | 61.06% | 95% | 0% | 1555 | -94
[5 empty] | 2019-06-28 | 5 | 4273.5 | 1437 | -93 | 0 | 0 | 1530 | 276.1748 | 276.1748 | 276.1748 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -106.4073 | 169.7675 | -2750 | -200 | -2780.2325 | 69.51% | 61.06% | 95% | 0% | 1530 | -93
[5 empty] | 2019-06-28 | 6 | 4274 | 1411 | -92 | 0 | 0 | 1503 | 233.8829 | 233.8829 | 233.8829 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -105.2632 | 128.6198 | -2750 | -200 | -2821.3802 | 70.53% | 61.06% | 95% | 0% | 1503 | -92
[5 empty] | 2019-06-28 | 7 | 4274.5 | 1406 | -92 | 0 | 0 | 1498 | 226.0511 | 226.0511 | 226.0511 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -105.2632 | 120.788 | -2750 | -200 | -2829.212 | 70.73% | 61.06% | 95% | 0% | 1498 | -92
[5 empty] | 2019-06-28 | 8 | 4275 | 1405 | -91 | 0 | 0 | 1496 | 222.9184 | 222.9184 | 222.9184 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -104.119 | 118.7994 | -2750 | -200 | -2831.2006 | 70.78% | 61.06% | 95% | 0% | 1496 | -91
[5 empty] | 2019-06-28 | 9 | 4275.5 | 1396 | -93 | 0 | 0 | 1489 | 211.9538 | 211.9538 | 211.9538 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -106.4073 | 105.5465 | -2750 | -200 | -2844.4535 | 71.11% | 61.05% | 95% | 0% | 1489 | -93
[5 empty] | 2019-06-28 | 10 | 4276 | 1373 | -95 | 0 | 0 | 1468 | 179.0602 | 179.0602 | 179.0602 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -108.6957 | 70.3645 | -2750 | -200 | -2879.6355 | 71.99% | 61.05% | 95% | 0% | 1468 | -95
[5 empty] | 2019-06-28 | 11 | 4276.5 | 1401 | -98 | 1 | 0 | 1499 | 227.6175 | 227.6175 | 227.6175 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -112.1281 | 115.4893 | -3550 | -400 | -3834.5107 | 95.86% | 61.05% | 95% | 0% | 1499 | -98
[5 empty] | 2019-06-28 | 12 | 4277 | 1455 | -112 | 1 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -128.1465 | 205.9838 | -3550 | -400 | -3744.0162 | 93.6% | 61.05% | 95% | 0% | 1567 | -112
[5 empty] | 2019-06-28 | 13 | 4277.5 | 1601 | -136 | 1 | 0 | 1737 | 600.4122 | 600.4122 | 600.4122 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -155.6064 | 444.8058 | -3550 | -400 | -3505.1942 | 87.63% | 61.05% | 95% | 0% | 1737 | -136
[5 empty] | 2019-06-28 | 14 | 4278 | 1724 | -169 | 1 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -193.3638 | 651.4012 | -3550 | -400 | -3298.5988 | 82.46% | 61.04% | 95% | 0% | 1893 | -169
[5 empty] | 2019-06-28 | 15 | 4278.5 | 1889 | -208 | 1 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 1386.7271 | 780 | 200 | 2366.7271 | 59.17% | 95% | 0% | -237.9863 | 926.3171 | -3550 | -400 | -3023.6829 | 75.59% | 61.04% | 95% | 0% | 2097 | -208
[5 empty] | 2019-06-28 | 16 | 4279 | 1957 | -256 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 1385.1608 | 780 | 200 | 2365.1608 | 59.13% | 95% | 0% | -292.9062 | 1053.0955 | -3550 | -400 | -2896.9045 | 72.42% | 61.03% | 95% | 0% | 2213 | -256
[5 empty] | 2019-06-28 | 17 | 4279.5 | 1948 | -312 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 1385.1608 | 780 | 200 | 2365.1608 | 59.13% | 95% | 0% | -356.9794 | 1062.6414 | -3550 | -400 | -2887.3586 | 72.18% | 61.03% | 95% | 0% | 2260 | -312
[5 empty] | 2019-06-28 | 18 | 4280 | 1853 | -378 | 1 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 1385.1608 | 780 | 200 | 2365.1608 | 59.13% | 95% | 0% | -432.4943 | 941.7019 | -3550 | -400 | -3008.2981 | 75.21% | 61.03% | 95% | 0% | 2231 | -378
[5 empty] | 2019-06-28 | 19 | 4280.5 | 1760 | -456 | 1 | 0 | 2216 | 1350.7007 | 1350.7007 | 1350.7007 | 1385.1608 | 780 | 200 | 2365.1608 | 59.13% | 95% | 0% | -521.7391 | 828.9616 | -3550 | -400 | -3121.0384 | 78.03% | 61.03% | 95% | 0% | 2216 | -456
[5 empty] | 2019-06-28 | 20 | 4281 | 1644 | -529 | 1 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 1385.1608 | 780 | 200 | 2365.1608 | 59.13% | 95% | 0% | -605.2632 | 678.0839 | -3550 | -400 | -3271.9161 | 81.8% | 61.03% | 95% | 0% | 2173 | -529
[5 empty] | 2019-06-28 | 21 | 4281.5 | 1494 | -611 | 1 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 1385.1608 | 780 | 200 | 2365.1608 | 59.13% | 95% | 0% | -699.0847 | 477.7496 | -3550 | -400 | -3472.2504 | 86.81% | 61.02% | 95% | 0% | 2105 | -611
[5 empty] | 2019-06-28 | 22 | 4282 | 1356 | -690 | 1 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1385.1608 | 780 | 200 | 2365.1608 | 59.13% | 95% | 0% | -789.4737 | 294.9451 | -3550 | -400 | -3655.0549 | 91.38% | 61.01% | 95% | 0% | 2046 | -690
[5 empty] | 2019-06-28 | 23 | 4282.5 | 1257 | -752 | 1 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 1385.1608 | 780 | 200 | 2365.1608 | 59.13% | 95% | 0% | -860.4119 | 166.0514 | -3550 | -400 | -3783.9486 | 94.6% | 61.01% | 95% | 0% | 2009 | -752
[5 empty] | 2019-06-28 | 24 | 4283 | 1188 | -797 | 1 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 1385.1608 | 780 | 200 | 2365.1608 | 59.13% | 95% | 0% | -911.8993 | 76.9713 | -3550 | -400 | -3873.0287 | 96.83% | 61.01% | 95% | 0% | 1985 | -797
[5 empty] | 2019-06-28 | 25 | 4283.5 | 1149 | -826 | 1 | 0 | 1975 | 973.2069 | 973.2069 | 973.2069 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -945.0801 | 28.1268 | -3550 | -400 | -3921.8732 | 98.05% | 61.01% | 95% | 0% | 1975 | -826
[5 empty] | 2019-06-28 | 26 | 4284 | 1106 | -841 | 1 | 0 | 1947 | 929.3487 | 929.3487 | 929.3487 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -962.2426 | -32.8938 | -3550 | -400 | -3982.8938 | 99.57% | 61% | 95% | 0% | 1947 | -841
[5 empty] | 2019-06-28 | 27 | 4284.5 | 1079 | -833 | 1 | 0 | 1912 | 874.526 | 874.526 | 874.526 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -953.0892 | -78.5633 | -3550 | -400 | -4028.5633 | 100.7% | 60.99% | 95% | 0% | 1912 | -833
[5 empty] | 2019-06-28 | 28 | 4285 | 1053 | -829 | 1 | 0 | 1882 | 827.535 | 827.535 | 827.535 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -948.5126 | -120.9775 | -3550 | -400 | -4070.9775 | 101.8% | 60.99% | 95% | 0% | 1882 | -829
[5 empty] | 2019-06-28 | 29 | 4285.5 | 1073 | -809 | 1 | 0 | 1882 | 827.535 | 827.535 | 827.535 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -925.6293 | -98.0943 | -3550 | -400 | -4048.0943 | 101.2% | 60.99% | 95% | 0% | 1882 | -809
[5 empty] | 2019-06-28 | 30 | 4286 | 1099 | -775 | 1 | 0 | 1874 | 815.0041 | 815.0041 | 815.0041 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -886.7277 | -71.7236 | -3550 | -400 | -4021.7236 | 100.5% | 60.99% | 95% | 0% | 1874 | -775
[5 empty] | 2019-06-28 | 31 | 4286.5 | 1145 | -731 | 1 | 0 | 1876 | 818.1369 | 818.1369 | 818.1369 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -836.3844 | -18.2476 | -3550 | -400 | -3968.2476 | 99.21% | 60.99% | 95% | 0% | 1876 | -731
[5 empty] | 2019-06-28 | 32 | 4287 | 1238 | -674 | 1 | 0 | 1912 | 874.526 | 874.526 | 874.526 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -771.167 | 103.3589 | -3550 | -400 | -3846.6411 | 96.17% | 60.99% | 95% | 0% | 1912 | -674
[5 empty] | 2019-06-28 | 33 | 4287.5 | 1353 | -620 | 1 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -709.3822 | 260.692 | -3550 | -400 | -3689.308 | 92.23% | 60.98% | 95% | 0% | 1973 | -620
[5 empty] | 2019-06-28 | 34 | 4288 | 1469 | -556 | 1 | 0 | 2025 | 1051.5251 | 1051.5251 | 1051.5251 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -636.1556 | 415.3695 | -3550 | -400 | -3534.6305 | 88.37% | 60.98% | 95% | 0% | 2025 | -556
[5 empty] | 2019-06-28 | 35 | 4288.5 | 1600 | -485 | 1 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -554.9199 | 590.5871 | -3550 | -400 | -3359.4129 | 83.99% | 60.97% | 95% | 0% | 2085 | -485
[5 empty] | 2019-06-28 | 36 | 4289 | 1720 | -415 | 1 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -474.8284 | 748.9969 | -3550 | -400 | -3201.0031 | 80.03% | 60.97% | 95% | 0% | 2135 | -415
[5 empty] | 2019-06-28 | 37 | 4289.5 | 1821 | -344 | 1 | 0 | 2165 | 1270.8162 | 1270.8162 | 1270.8162 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -393.5927 | 877.2235 | -3550 | -400 | -3072.7765 | 76.82% | 60.97% | 95% | 0% | 2165 | -344
[5 empty] | 2019-06-28 | 38 | 4290 | 1910 | -282 | 1 | 0 | 2192 | 1313.108 | 1313.108 | 1313.108 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -322.6545 | 990.4535 | -3550 | -400 | -2959.5465 | 73.99% | 60.97% | 95% | 0% | 2192 | -282
[5 empty] | 2019-06-28 | 39 | 4290.5 | 1972 | -224 | 1 | 0 | 2196 | 1319.3735 | 1319.3735 | 1319.3735 | 1383.5944 | 780 | 200 | 2363.5944 | 59.09% | 95% | 0% | -256.2929 | 1063.0805 | -3550 | -400 | -2886.9195 | 72.17% | 60.97% | 95% | 0% | 2196 | -224
[5 empty] | 2019-06-28 | 40 | 4291 | 2041 | -177 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 1382.028 | 780 | 200 | 2362.028 | 59.05% | 95% | 0% | -202.5172 | 1151.3163 | -3550 | -400 | -2798.6837 | 69.97% | 60.97% | 95% | 0% | 2218 | -177
[5 empty] | 2019-06-28 | 41 | 4291.5 | 2054 | -141 | 1 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 1382.028 | 780 | 200 | 2362.028 | 59.05% | 95% | 0% | -161.3272 | 1156.4799 | -3550 | -400 | -2793.5201 | 69.84% | 60.96% | 95% | 0% | 2195 | -141
[5 empty] | 2019-06-28 | 42 | 4292 | 2058 | -114 | 1 | 0 | 2172 | 1281.7807 | 1281.7807 | 1281.7807 | 1382.028 | 780 | 200 | 2362.028 | 59.05% | 95% | 0% | -130.4348 | 1151.3459 | -3550 | -400 | -2798.6541 | 69.97% | 60.96% | 95% | 0% | 2172 | -114
[5 empty] | 2019-06-28 | 43 | 4292.5 | 2032 | -100 | 1 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 1382.028 | 780 | 200 | 2362.028 | 59.05% | 95% | 0% | -114.4165 | 1104.7097 | -3550 | -400 | -2845.2903 | 71.13% | 60.96% | 95% | 0% | 2132 | -100
[5 empty] | 2019-06-28 | 44 | 4293 | 2017 | -97 | 1 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 1382.028 | 780 | 200 | 2362.028 | 59.05% | 95% | 0% | -110.984 | 1079.9476 | -3550 | -400 | -2870.0524 | 71.75% | 60.96% | 95% | 0% | 2114 | -97
[5 empty] | 2019-06-28 | 45 | 4293.5 | 2012 | -96 | 1 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 1382.028 | 780 | 200 | 2362.028 | 59.05% | 95% | 0% | -109.8398 | 1071.6936 | -3550 | -400 | -2878.3064 | 71.96% | 60.96% | 95% | 0% | 2108 | -96
[5 empty] | 2019-06-28 | 46 | 4294 | 1924 | -95 | 0 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 1382.028 | 780 | 200 | 2362.028 | 59.05% | 95% | 0% | -108.6957 | 933.4313 | -2750 | -200 | -2016.5687 | 50.41% | 60.96% | 95% | 0% | 2019 | -95
[5 empty] | 2019-06-28 | 47 | 4294.5 | 1822 | -93 | 0 | 0 | 1915 | 879.2251 | 879.2251 | 879.2251 | 1382.028 | 780 | 200 | 2362.028 | 59.05% | 95% | 0% | -106.4073 | 772.8177 | -2750 | -200 | -2177.1823 | 54.43% | 60.95% | 95% | 0% | 1915 | -93
[5 empty] | 2019-06-28 | 48 | 4295 | 1714 | -91 | 0 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -104.119 | 602.806 | -2750 | -200 | -2347.194 | 58.68% | 60.95% | 95% | 0% | 1805 | -91
[5 empty] | 2019-06-29 | 1 | 4295.5 | 1652 | -86 | 0 | 0 | 1738 | 601.9786 | 601.9786 | 601.9786 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -98.3982 | 503.5804 | -2750 | -200 | -2446.4196 | 61.16% | 60.95% | 95% | 0% | 1738 | -86
[5 empty] | 2019-06-29 | 2 | 4296 | 1591 | -82 | 0 | 0 | 1673 | 500.1649 | 500.1649 | 500.1649 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -93.8215 | 406.3434 | -2750 | -200 | -2543.6566 | 63.59% | 60.95% | 95% | 0% | 1673 | -82
[5 empty] | 2019-06-29 | 3 | 4296.5 | 1544 | -80 | 1 | 0 | 1624 | 423.413 | 423.413 | 423.413 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -91.5332 | 331.8798 | -3550 | -400 | -3618.1202 | 90.45% | 60.95% | 95% | 0% | 1624 | -80
[5 empty] | 2019-06-29 | 4 | 4297 | 1524 | -78 | 1 | 0 | 1602 | 388.953 | 388.953 | 388.953 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -89.2449 | 299.7082 | -3550 | -400 | -3650.2918 | 91.26% | 60.95% | 95% | 0% | 1602 | -78
[5 empty] | 2019-06-29 | 5 | 4297.5 | 1487 | -78 | 1 | 0 | 1565 | 330.9975 | 330.9975 | 330.9975 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -89.2449 | 241.7527 | -3550 | -400 | -3708.2473 | 92.71% | 60.94% | 95% | 0% | 1565 | -78
[5 empty] | 2019-06-29 | 6 | 4298 | 1458 | -77 | 1 | 0 | 1535 | 284.0066 | 284.0066 | 284.0066 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -88.1007 | 195.9059 | -3550 | -400 | -3754.0941 | 93.85% | 60.93% | 95% | 0% | 1535 | -77
[5 empty] | 2019-06-29 | 7 | 4298.5 | 1436 | -73 | 1 | 0 | 1509 | 243.2811 | 243.2811 | 243.2811 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -83.524 | 159.7571 | -3550 | -400 | -3790.2429 | 94.76% | 60.93% | 95% | 0% | 1509 | -73
[5 empty] | 2019-06-29 | 8 | 4299 | 1431 | -70 | 1 | 0 | 1501 | 230.7502 | 230.7502 | 230.7502 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -80.0915 | 150.6587 | -3550 | -400 | -3799.3413 | 94.98% | 60.93% | 95% | 0% | 1501 | -70
[5 empty] | 2019-06-29 | 9 | 4299.5 | 1423 | -67 | 1 | 0 | 1490 | 213.5202 | 213.5202 | 213.5202 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -76.659 | 136.8612 | -3550 | -400 | -3813.1388 | 95.33% | 60.92% | 95% | 0% | 1490 | -67
[5 empty] | 2019-06-29 | 10 | 4300 | 1401 | -63 | 1 | 0 | 1464 | 172.7947 | 172.7947 | 172.7947 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -72.0824 | 100.7123 | -3550 | -400 | -3849.2877 | 96.23% | 60.92% | 95% | 0% | 1464 | -63
[5 empty] | 2019-06-29 | 11 | 4300.5 | 1395 | -67 | 1 | 0 | 1462 | 169.662 | 169.662 | 169.662 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -76.659 | 93.003 | -3550 | -400 | -3856.997 | 96.42% | 60.92% | 95% | 0% | 1462 | -67
[5 empty] | 2019-06-29 | 12 | 4301 | 1392 | -83 | 1 | 0 | 1475 | 190.0247 | 190.0247 | 190.0247 | 1380.4617 | 780 | 200 | 2360.4617 | 59.01% | 95% | 0% | -94.9657 | 95.0591 | -3550 | -400 | -3854.9409 | 96.37% | 60.92% | 95% | 0% | 1475 | -83
[5 empty] | 2019-06-29 | 13 | 4301.5 | 1412 | -105 | 1 | 0 | 1517 | 255.812 | 255.812 | 255.812 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -120.1373 | 135.6747 | -3550 | -400 | -3814.3253 | 95.36% | 60.92% | 95% | 0% | 1517 | -105
[5 empty] | 2019-06-29 | 14 | 4302 | 1434 | -138 | 1 | 0 | 1572 | 341.9621 | 341.9621 | 341.9621 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -157.8947 | 184.0673 | -3550 | -400 | -3765.9327 | 94.15% | 60.91% | 95% | 0% | 1572 | -138
[5 empty] | 2019-06-29 | 15 | 4302.5 | 1500 | -179 | 1 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -204.8055 | 304.7576 | -3550 | -400 | -3645.2424 | 91.13% | 60.91% | 95% | 0% | 1679 | -179
[5 empty] | 2019-06-29 | 16 | 4303 | 1523 | -224 | 1 | 0 | 1747 | 616.0758 | 616.0758 | 616.0758 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -256.2929 | 359.7829 | -3550 | -400 | -3590.2171 | 89.76% | 60.91% | 95% | 0% | 1747 | -224
[5 empty] | 2019-06-29 | 17 | 4303.5 | 1558 | -284 | 1 | 0 | 1842 | 764.8805 | 764.8805 | 764.8805 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -324.9428 | 439.9377 | -3550 | -400 | -3510.0623 | 87.75% | 60.91% | 95% | 0% | 1842 | -284
[5 empty] | 2019-06-29 | 18 | 4304 | 1522 | -358 | 1 | 0 | 1880 | 824.4023 | 824.4023 | 824.4023 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -409.611 | 414.7913 | -3550 | -400 | -3535.2087 | 88.38% | 60.91% | 95% | 0% | 1880 | -358
[5 empty] | 2019-06-29 | 19 | 4304.5 | 1492 | -424 | 1 | 0 | 1916 | 880.7914 | 880.7914 | 880.7914 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -485.1259 | 395.6656 | -3550 | -400 | -3554.3344 | 88.86% | 60.91% | 95% | 0% | 1916 | -424
[5 empty] | 2019-06-29 | 20 | 4305 | 1449 | -472 | 1 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -540.0458 | 348.5775 | -3550 | -400 | -3601.4225 | 90.04% | 60.9% | 95% | 0% | 1921 | -472
[5 empty] | 2019-06-29 | 21 | 4305.5 | 1369 | -523 | 1 | 0 | 1892 | 843.1987 | 843.1987 | 843.1987 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -598.3982 | 244.8005 | -3550 | -400 | -3705.1995 | 92.63% | 60.9% | 95% | 0% | 1892 | -523
[5 empty] | 2019-06-29 | 22 | 4306 | 1294 | -571 | 1 | 0 | 1865 | 800.9068 | 800.9068 | 800.9068 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -653.3181 | 147.5888 | -3550 | -400 | -3802.4112 | 95.06% | 60.9% | 95% | 0% | 1865 | -571
[5 empty] | 2019-06-29 | 23 | 4306.5 | 1228 | -614 | 1 | 0 | 1842 | 764.8805 | 764.8805 | 764.8805 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -702.5172 | 62.3633 | -3550 | -400 | -3887.6367 | 97.19% | 60.9% | 95% | 0% | 1842 | -614
[5 empty] | 2019-06-29 | 24 | 4307 | 1170 | -650 | 1 | 0 | 1820 | 730.4204 | 730.4204 | 730.4204 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -743.7071 | -13.2866 | -3550 | -400 | -3963.2866 | 99.08% | 60.9% | 95% | 0% | 1820 | -650
[5 empty] | 2019-06-29 | 25 | 4307.5 | 1144 | -667 | 1 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -763.1579 | -46.8347 | -3550 | -400 | -3996.8347 | 99.92% | 60.88% | 95% | 0% | 1811 | -667
[5 empty] | 2019-06-29 | 26 | 4308 | 1100 | -682 | 1 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -780.3204 | -109.4218 | -3550 | -400 | -4059.4218 | 101.5% | 60.88% | 95% | 0% | 1782 | -682
[5 empty] | 2019-06-29 | 27 | 4308.5 | 1072 | -681 | 1 | 0 | 1753 | 625.474 | 625.474 | 625.474 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -779.1762 | -153.7022 | -3550 | -400 | -4103.7022 | 102.6% | 60.88% | 95% | 0% | 1753 | -681
[5 empty] | 2019-06-29 | 28 | 4309 | 1093 | -671 | 1 | 0 | 1764 | 642.704 | 642.704 | 642.704 | 1378.8953 | 780 | 200 | 2358.8953 | 58.97% | 95% | 0% | -767.7346 | -125.0305 | -3550 | -400 | -4075.0305 | 101.9% | 60.88% | 95% | 0% | 1764 | -671
[5 empty] | 2019-06-29 | 29 | 4309.5 | 1101 | -650 | 1 | 0 | 1751 | 622.3413 | 622.3413 | 622.3413 | 1377.3289 | 780 | 200 | 2357.3289 | 58.93% | 95% | 0% | -743.7071 | -121.3658 | -3550 | -400 | -4071.3658 | 101.8% | 60.87% | 95% | 0% | 1751 | -650
[5 empty] | 2019-06-29 | 30 | 4310 | 1113 | -626 | 1 | 0 | 1739 | 603.5449 | 603.5449 | 603.5449 | 1377.3289 | 780 | 200 | 2357.3289 | 58.93% | 95% | 0% | -716.2471 | -112.7022 | -3550 | -400 | -4062.7022 | 101.6% | 60.87% | 95% | 0% | 1739 | -626
[5 empty] | 2019-06-29 | 31 | 4310.5 | 1176 | -582 | 1 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 1377.3289 | 780 | 200 | 2357.3289 | 58.93% | 95% | 0% | -665.9039 | -32.598 | -3550 | -400 | -3982.598 | 99.56% | 60.87% | 95% | 0% | 1758 | -582
[5 empty] | 2019-06-29 | 32 | 4311 | 1285 | -508 | 1 | 0 | 1793 | 688.1286 | 688.1286 | 688.1286 | 1377.3289 | 780 | 200 | 2357.3289 | 58.93% | 95% | 0% | -581.2357 | 106.8929 | -3550 | -400 | -3843.1071 | 96.08% | 60.87% | 95% | 0% | 1793 | -508
[5 empty] | 2019-06-29 | 33 | 4311.5 | 1406 | -450 | 1 | 0 | 1856 | 786.8096 | 786.8096 | 786.8096 | 1377.3289 | 780 | 200 | 2357.3289 | 58.93% | 95% | 0% | -514.8741 | 271.9354 | -3550 | -400 | -3678.0646 | 91.95% | 60.87% | 95% | 0% | 1856 | -450
[5 empty] | 2019-06-29 | 34 | 4312 | 1552 | -391 | 1 | 0 | 1943 | 923.0833 | 923.0833 | 923.0833 | 1377.3289 | 780 | 200 | 2357.3289 | 58.93% | 95% | 0% | -447.3684 | 475.7148 | -3550 | -400 | -3474.2852 | 86.86% | 60.86% | 95% | 0% | 1943 | -391
[5 empty] | 2019-06-29 | 35 | 4312.5 | 1700 | -330 | 1 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 1377.3289 | 780 | 200 | 2357.3289 | 58.93% | 95% | 0% | -377.5744 | 681.7826 | -3550 | -400 | -3268.2174 | 81.71% | 60.86% | 95% | 0% | 2030 | -330
[5 empty] | 2019-06-29 | 36 | 4313 | 1798 | -285 | 1 | 0 | 2083 | 1142.3743 | 1142.3743 | 1142.3743 | 1377.3289 | 780 | 200 | 2357.3289 | 58.93% | 95% | 0% | -326.087 | 816.2873 | -3550 | -400 | -3133.7127 | 78.34% | 60.86% | 95% | 0% | 2083 | -285
[5 empty] | 2019-06-29 | 37 | 4313.5 | 1875 | -237 | 1 | 0 | 2112 | 1187.7988 | 1187.7988 | 1187.7988 | 1375.7626 | 780 | 200 | 2355.7626 | 58.89% | 95% | 0% | -271.167 | 916.6318 | -3550 | -400 | -3033.3682 | 75.83% | 60.86% | 95% | 0% | 2112 | -237
[5 empty] | 2019-06-29 | 38 | 4314 | 1947 | -197 | 1 | 0 | 2144 | 1237.9225 | 1237.9225 | 1237.9225 | 1375.7626 | 780 | 200 | 2355.7626 | 58.89% | 95% | 0% | -225.4005 | 1012.522 | -3550 | -400 | -2937.478 | 73.44% | 60.86% | 95% | 0% | 2144 | -197
[5 empty] | 2019-06-29 | 39 | 4314.5 | 1990 | -158 | 1 | 0 | 2148 | 1244.188 | 1244.188 | 1244.188 | 1375.7626 | 780 | 200 | 2355.7626 | 58.89% | 95% | 0% | -180.778 | 1063.4099 | -3550 | -400 | -2886.5901 | 72.16% | 60.86% | 95% | 0% | 2148 | -158
[5 empty] | 2019-06-29 | 40 | 4315 | 2004 | -125 | 1 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 1375.7626 | 780 | 200 | 2355.7626 | 58.89% | 95% | 0% | -143.0206 | 1071.4064 | -3550 | -400 | -2878.5936 | 71.96% | 60.85% | 95% | 0% | 2129 | -125
[5 empty] | 2019-06-29 | 41 | 4315.5 | 2005 | -102 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1375.7626 | 780 | 200 | 2355.7626 | 58.89% | 95% | 0% | -116.7048 | 1063.2622 | -3550 | -400 | -2886.7378 | 72.17% | 60.85% | 95% | 0% | 2107 | -102
[5 empty] | 2019-06-29 | 42 | 4316 | 1999 | -83 | 1 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 1375.7626 | 780 | 200 | 2355.7626 | 58.89% | 95% | 0% | -94.9657 | 1045.8422 | -3550 | -400 | -2904.1578 | 72.6% | 60.85% | 95% | 0% | 2082 | -83
[5 empty] | 2019-06-29 | 43 | 4316.5 | 2011 | -78 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1375.7626 | 780 | 200 | 2355.7626 | 58.89% | 95% | 0% | -89.2449 | 1062.5276 | -3550 | -400 | -2887.4724 | 72.19% | 60.85% | 95% | 0% | 2089 | -78
[5 empty] | 2019-06-29 | 44 | 4317 | 2011 | -81 | 1 | 0 | 2092 | 1156.4716 | 1156.4716 | 1156.4716 | 1375.7626 | 780 | 200 | 2355.7626 | 58.89% | 95% | 0% | -92.6773 | 1063.7942 | -3550 | -400 | -2886.2058 | 72.16% | 60.85% | 95% | 0% | 2092 | -81
[5 empty] | 2019-06-29 | 45 | 4317.5 | 1991 | -84 | 0 | 0 | 2075 | 1129.8434 | 1129.8434 | 1129.8434 | 1375.7626 | 780 | 200 | 2355.7626 | 58.89% | 95% | 0% | -96.1098 | 1033.7335 | -2750 | -200 | -1916.2665 | 47.91% | 60.85% | 95% | 0% | 2075 | -84
[5 empty] | 2019-06-29 | 46 | 4318 | 1917 | -87 | 0 | 0 | 2004 | 1018.6315 | 1018.6315 | 1018.6315 | 1375.7626 | 780 | 200 | 2355.7626 | 58.89% | 95% | 0% | -99.5423 | 919.0892 | -2750 | -200 | -2030.9108 | 50.77% | 60.84% | 95% | 0% | 2004 | -87
[5 empty] | 2019-06-29 | 47 | 4318.5 | 1795 | -90 | 0 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -102.9748 | 729.2593 | -2750 | -200 | -2220.7407 | 55.52% | 60.84% | 95% | 0% | 1885 | -90
[5 empty] | 2019-06-29 | 48 | 4319 | 1688 | -93 | 0 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -106.4073 | 562.9249 | -2750 | -200 | -2387.0751 | 59.68% | 60.84% | 95% | 0% | 1781 | -93
[5 empty] | 2019-06-30 | 1 | 4319.5 | 1580 | -99 | 0 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -113.2723 | 396.2908 | -2750 | -200 | -2553.7092 | 63.84% | 60.84% | 95% | 0% | 1679 | -99
[5 empty] | 2019-06-30 | 2 | 4320 | 1504 | -105 | 0 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -120.1373 | 279.7803 | -2750 | -200 | -2670.2197 | 66.76% | 60.83% | 95% | 0% | 1609 | -105
[5 empty] | 2019-06-30 | 3 | 4320.5 | 1448 | -110 | 0 | 0 | 1558 | 320.033 | 320.033 | 320.033 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -125.8581 | 194.1749 | -2750 | -200 | -2755.8251 | 68.9% | 60.83% | 95% | 0% | 1558 | -110
[5 empty] | 2019-06-30 | 4 | 4321 | 1387 | -115 | 0 | 0 | 1502 | 232.3166 | 232.3166 | 232.3166 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -131.5789 | 100.7376 | -2750 | -200 | -2849.2624 | 71.23% | 60.83% | 95% | 0% | 1502 | -115
[5 empty] | 2019-06-30 | 5 | 4321.5 | 1341 | -119 | 0 | 0 | 1460 | 166.5293 | 166.5293 | 166.5293 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -136.1556 | 30.3737 | -2750 | -200 | -2919.6263 | 72.99% | 60.82% | 95% | 0% | 1460 | -119
[5 empty] | 2019-06-30 | 6 | 4322 | 1290 | -122 | 0 | 0 | 1412 | 91.3438 | 91.3438 | 91.3438 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -139.5881 | -48.2443 | -2750 | -200 | -2998.2443 | 74.96% | 60.82% | 95% | 0% | 1412 | -122
[5 empty] | 2019-06-30 | 7 | 4322.5 | 1260 | -126 | 0 | 0 | 1386 | 50.6183 | 50.6183 | 50.6183 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -144.1648 | -93.5465 | -2750 | -200 | -3043.5465 | 76.09% | 60.82% | 95% | 0% | 1386 | -126
[5 empty] | 2019-06-30 | 8 | 4323 | 1232 | -129 | 0 | 0 | 1361 | 11.4592 | 11.4592 | 11.4592 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -147.5973 | -136.1381 | -2750 | -200 | -3086.1381 | 77.15% | 60.81% | 95% | 0% | 1361 | -129
[5 empty] | 2019-06-30 | 9 | 4323.5 | 1202 | -131 | 0 | 0 | 1333 | -32.399 | -32.399 | -32.399 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -149.8856 | -182.2846 | -2750 | -200 | -3132.2846 | 78.31% | 60.81% | 95% | 0% | 1333 | -131
[5 empty] | 2019-06-30 | 10 | 4324 | 1179 | -132 | 0 | 0 | 1311 | -66.859 | -66.859 | -66.859 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -151.0297 | -217.8888 | -2750 | -200 | -3167.8888 | 79.2% | 60.81% | 95% | 0% | 1311 | -132
[5 empty] | 2019-06-30 | 11 | 4324.5 | 1162 | -138 | 0 | 0 | 1300 | -84.089 | -84.089 | -84.089 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -157.8947 | -241.9838 | -2750 | -200 | -3191.9838 | 79.8% | 60.8% | 95% | 0% | 1300 | -138
[5 empty] | 2019-06-30 | 12 | 4325 | 1157 | -155 | 0 | 0 | 1312 | -65.2927 | -65.2927 | -65.2927 | 1374.1962 | 780 | 200 | 2354.1962 | 58.85% | 95% | 0% | -177.3455 | -242.6382 | -2750 | -200 | -3192.6382 | 79.82% | 60.8% | 95% | 0% | 1312 | -155
[5 empty] | 2019-06-30 | 13 | 4325.5 | 1177 | -184 | 1 | 0 | 1361 | 11.4592 | 11.4592 | 11.4592 | 1372.6298 | 780 | 200 | 2352.6298 | 58.82% | 95% | 0% | -210.5263 | -199.0671 | -3550 | -400 | -4149.0671 | 103.7% | 60.8% | 95% | 0% | 1361 | -184
[5 empty] | 2019-06-30 | 14 | 4326 | 1168 | -223 | 1 | 0 | 1391 | 58.4501 | 58.4501 | 58.4501 | 1372.6298 | 780 | 200 | 2352.6298 | 58.82% | 95% | 0% | -255.1487 | -196.6986 | -3550 | -400 | -4146.6986 | 103.7% | 60.8% | 95% | 0% | 1391 | -223
[5 empty] | 2019-06-30 | 15 | 4326.5 | 1157 | -270 | 1 | 0 | 1427 | 114.8392 | 114.8392 | 114.8392 | 1372.6298 | 780 | 200 | 2352.6298 | 58.82% | 95% | 0% | -308.9245 | -194.0852 | -3550 | -400 | -4144.0852 | 103.6% | 60.79% | 95% | 0% | 1427 | -270
[5 empty] | 2019-06-30 | 16 | 4327 | 1149 | -322 | 1 | 0 | 1471 | 183.7593 | 183.7593 | 183.7593 | 1372.6298 | 780 | 200 | 2352.6298 | 58.82% | 95% | 0% | -368.4211 | -184.6618 | -3550 | -400 | -4134.6618 | 103.4% | 60.79% | 95% | 0% | 1471 | -322
[5 empty] | 2019-06-30 | 17 | 4327.5 | 1164 | -376 | 1 | 0 | 1540 | 291.8384 | 291.8384 | 291.8384 | 1372.6298 | 780 | 200 | 2352.6298 | 58.82% | 95% | 0% | -430.2059 | -138.3675 | -3550 | -400 | -4088.3675 | 102.2% | 60.79% | 95% | 0% | 1540 | -376
[5 empty] | 2019-06-30 | 18 | 4328 | 1171 | -425 | 1 | 0 | 1596 | 379.5548 | 379.5548 | 379.5548 | 1372.6298 | 780 | 200 | 2352.6298 | 58.82% | 95% | 0% | -486.27 | -106.7152 | -3550 | -400 | -4056.7152 | 101.4% | 60.79% | 95% | 0% | 1596 | -425
[5 empty] | 2019-06-30 | 19 | 4328.5 | 1204 | -450 | 1 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 1372.6298 | 780 | 200 | 2352.6298 | 58.82% | 95% | 0% | -514.8741 | -44.4702 | -3550 | -400 | -3994.4702 | 99.86% | 60.78% | 95% | 0% | 1654 | -450
[5 empty] | 2019-06-30 | 20 | 4329 | 1209 | -478 | 1 | 0 | 1687 | 522.094 | 522.094 | 522.094 | 1371.0635 | 780 | 200 | 2351.0635 | 58.78% | 95% | 0% | -546.9108 | -24.8168 | -3550 | -400 | -3974.8168 | 99.37% | 60.78% | 95% | 0% | 1687 | -478
[5 empty] | 2019-06-30 | 21 | 4329.5 | 1185 | -518 | 1 | 0 | 1703 | 547.1558 | 547.1558 | 547.1558 | 1371.0635 | 780 | 200 | 2351.0635 | 58.78% | 95% | 0% | -592.6773 | -45.5215 | -3550 | -400 | -3995.5215 | 99.89% | 60.78% | 95% | 0% | 1703 | -518
[5 empty] | 2019-06-30 | 22 | 4330 | 1131 | -568 | 1 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 1371.0635 | 780 | 200 | 2351.0635 | 58.78% | 95% | 0% | -649.8856 | -108.9952 | -3550 | -400 | -4058.9952 | 101.5% | 60.78% | 95% | 0% | 1699 | -568
[5 empty] | 2019-06-30 | 23 | 4330.5 | 1083 | -609 | 1 | 0 | 1692 | 529.9258 | 529.9258 | 529.9258 | 1371.0635 | 780 | 200 | 2351.0635 | 58.78% | 95% | 0% | -696.7963 | -166.8705 | -3550 | -400 | -4116.8705 | 102.9% | 60.77% | 95% | 0% | 1692 | -609
[5 empty] | 2019-06-30 | 24 | 4331 | 1036 | -636 | 1 | 0 | 1672 | 498.5985 | 498.5985 | 498.5985 | 1371.0635 | 780 | 200 | 2351.0635 | 58.78% | 95% | 0% | -727.6888 | -229.0903 | -3550 | -400 | -4179.0903 | 104.5% | 60.77% | 95% | 0% | 1672 | -636
[5 empty] | 2019-06-30 | 25 | 4331.5 | 997 | -672 | 1 | 0 | 1669 | 493.8994 | 493.8994 | 493.8994 | 1371.0635 | 780 | 200 | 2351.0635 | 58.78% | 95% | 0% | -768.8787 | -274.9793 | -3550 | -400 | -4224.9793 | 105.6% | 60.77% | 95% | 0% | 1669 | -672
[5 empty] | 2019-06-30 | 26 | 4332 | 989 | -689 | 1 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 1371.0635 | 780 | 200 | 2351.0635 | 58.78% | 95% | 0% | -788.3295 | -280.3328 | -3550 | -400 | -4230.3328 | 105.8% | 60.77% | 95% | 0% | 1678 | -689
[5 empty] | 2019-06-30 | 27 | 4332.5 | 957 | -695 | 1 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 1371.0635 | 780 | 200 | 2351.0635 | 58.78% | 95% | 0% | -795.1945 | -327.9233 | -3550 | -400 | -4277.9233 | 106.9% | 60.76% | 95% | 0% | 1652 | -695
[5 empty] | 2019-06-30 | 28 | 4333 | 904 | -691 | 1 | 0 | 1595 | 377.9885 | 377.9885 | 377.9885 | 1371.0635 | 780 | 200 | 2351.0635 | 58.78% | 95% | 0% | -790.6178 | -412.6294 | -3550 | -400 | -4362.6294 | 109.1% | 60.76% | 95% | 0% | 1595 | -691
[5 empty] | 2019-06-30 | 29 | 4333.5 | 867 | -697 | 1 | 0 | 1564 | 329.4312 | 329.4312 | 329.4312 | 1371.0635 | 780 | 200 | 2351.0635 | 58.78% | 95% | 0% | -797.4828 | -468.0517 | -3550 | -400 | -4418.0517 | 110.5% | 60.76% | 95% | 0% | 1564 | -697
[5 empty] | 2019-06-30 | 30 | 4334 | 868 | -688 | 1 | 0 | 1556 | 316.9002 | 316.9002 | 316.9002 | 1371.0635 | 780 | 200 | 2351.0635 | 58.78% | 95% | 0% | -787.1854 | -470.2851 | -3550 | -400 | -4420.2851 | 110.5% | 60.75% | 95% | 0% | 1556 | -688
[5 empty] | 2019-06-30 | 31 | 4334.5 | 923 | -632 | 1 | 0 | 1555 | 315.3339 | 315.3339 | 315.3339 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -723.1121 | -407.7782 | -3550 | -400 | -4357.7782 | 108.9% | 60.75% | 95% | 0% | 1555 | -632
[5 empty] | 2019-06-30 | 32 | 4335 | 965 | -618 | 1 | 0 | 1583 | 359.1921 | 359.1921 | 359.1921 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -707.0938 | -347.9017 | -3550 | -400 | -4297.9017 | 107.4% | 60.75% | 95% | 0% | 1583 | -618
[5 empty] | 2019-06-30 | 33 | 4335.5 | 1063 | -569 | 1 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -651.0297 | -215.0858 | -3550 | -400 | -4165.0858 | 104.1% | 60.74% | 95% | 0% | 1632 | -569
[5 empty] | 2019-06-30 | 34 | 4336 | 1165 | -538 | 1 | 0 | 1703 | 547.1558 | 547.1558 | 547.1558 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -615.5606 | -68.4048 | -3550 | -400 | -4018.4048 | 100.5% | 60.73% | 95% | 0% | 1703 | -538
[5 empty] | 2019-06-30 | 35 | 4336.5 | 1286 | -496 | 1 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -567.5057 | 103.3929 | -3550 | -400 | -3846.6071 | 96.17% | 60.73% | 95% | 0% | 1782 | -496
[5 empty] | 2019-06-30 | 36 | 4337 | 1396 | -447 | 1 | 0 | 1843 | 766.4468 | 766.4468 | 766.4468 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -511.4416 | 255.0052 | -3550 | -400 | -3694.9948 | 92.37% | 60.73% | 95% | 0% | 1843 | -447
[5 empty] | 2019-06-30 | 37 | 4337.5 | 1517 | -390 | 1 | 0 | 1907 | 866.6941 | 866.6941 | 866.6941 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -446.2243 | 420.4699 | -3550 | -400 | -3529.5301 | 88.24% | 60.73% | 95% | 0% | 1907 | -390
[5 empty] | 2019-06-30 | 38 | 4338 | 1603 | -333 | 1 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -381.0069 | 531.1118 | -3550 | -400 | -3418.8882 | 85.47% | 60.72% | 95% | 0% | 1936 | -333
[5 empty] | 2019-06-30 | 39 | 4338.5 | 1678 | -282 | 1 | 0 | 1960 | 949.7115 | 949.7115 | 949.7115 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -322.6545 | 627.057 | -3550 | -400 | -3322.943 | 83.07% | 60.72% | 95% | 0% | 1960 | -282
[5 empty] | 2019-06-30 | 40 | 4339 | 1743 | -231 | 1 | 0 | 1974 | 971.6406 | 971.6406 | 971.6406 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -264.3021 | 707.3385 | -3550 | -400 | -3242.6615 | 81.07% | 60.72% | 95% | 0% | 1974 | -231
[5 empty] | 2019-06-30 | 41 | 4339.5 | 1794 | -189 | 1 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -216.2471 | 769.4907 | -3550 | -400 | -3180.5093 | 79.51% | 60.72% | 95% | 0% | 1983 | -189
[5 empty] | 2019-06-30 | 42 | 4340 | 1806 | -162 | 1 | 0 | 1968 | 962.2424 | 962.2424 | 962.2424 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -185.3547 | 776.8877 | -3550 | -400 | -3173.1123 | 79.33% | 60.71% | 95% | 0% | 1968 | -162
[5 empty] | 2019-06-30 | 43 | 4340.5 | 1825 | -148 | 1 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -169.3364 | 800.7378 | -3550 | -400 | -3149.2622 | 78.73% | 60.71% | 95% | 0% | 1973 | -148
[5 empty] | 2019-06-30 | 44 | 4341 | 1806 | -144 | 1 | 0 | 1950 | 934.0478 | 934.0478 | 934.0478 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -164.7597 | 769.2881 | -3550 | -400 | -3180.7119 | 79.52% | 60.71% | 95% | 0% | 1950 | -144
[5 empty] | 2019-06-30 | 45 | 4341.5 | 1794 | -146 | 0 | 0 | 1940 | 918.3842 | 918.3842 | 918.3842 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -167.0481 | 751.3361 | -2750 | -200 | -2198.6639 | 54.97% | 60.71% | 95% | 0% | 1940 | -146
[5 empty] | 2019-06-30 | 46 | 4342 | 1712 | -148 | 0 | 0 | 1860 | 793.075 | 793.075 | 793.075 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -169.3364 | 623.7386 | -2750 | -200 | -2326.2614 | 58.16% | 60.7% | 95% | 0% | 1860 | -148
[5 empty] | 2019-06-30 | 47 | 4342.5 | 1556 | -151 | 0 | 0 | 1707 | 553.4213 | 553.4213 | 553.4213 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -172.7689 | 380.6524 | -2750 | -200 | -2569.3476 | 64.23% | 60.7% | 95% | 0% | 1707 | -151
[5 empty] | 2019-06-30 | 48 | 4343 | 1444 | -154 | 0 | 0 | 1598 | 382.6876 | 382.6876 | 382.6876 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -176.2014 | 206.4862 | -2750 | -200 | -2743.5138 | 68.59% | 60.7% | 95% | 0% | 1598 | -154
[5 empty] | 2019-07-01 | 1 | 4343.5 | 1338 | -153 | 0 | 0 | 1491 | 215.0866 | 215.0866 | 215.0866 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -175.0572 | 40.0294 | -2750 | -200 | -2909.9706 | 72.75% | 60.7% | 95% | 0% | 1491 | -153
[5 empty] | 2019-07-01 | 2 | 4344 | 1302 | -152 | 0 | 0 | 1454 | 157.1311 | 157.1311 | 157.1311 | 1369.4971 | 780 | 200 | 2349.4971 | 58.74% | 95% | 0% | -173.913 | -16.782 | -2750 | -200 | -2966.782 | 74.17% | 60.7% | 95% | 0% | 1454 | -152
[5 empty] | 2019-07-01 | 3 | 4344.5 | 1258 | -154 | 0 | 0 | 1412 | 91.3438 | 91.3438 | 91.3438 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -176.2014 | -84.8576 | -2750 | -200 | -3034.8576 | 75.87% | 60.69% | 95% | 0% | 1412 | -154
[5 empty] | 2019-07-01 | 4 | 4345 | 1239 | -155 | 0 | 0 | 1394 | 63.1492 | 63.1492 | 63.1492 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -177.3455 | -114.1963 | -2750 | -200 | -3064.1963 | 76.6% | 60.69% | 95% | 0% | 1394 | -155
[5 empty] | 2019-07-01 | 5 | 4345.5 | 1213 | -156 | 0 | 0 | 1369 | 23.9901 | 23.9901 | 23.9901 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -178.4897 | -154.4996 | -2750 | -200 | -3104.4996 | 77.61% | 60.69% | 95% | 0% | 1369 | -156
[5 empty] | 2019-07-01 | 6 | 4346 | 1191 | -158 | 0 | 0 | 1349 | -7.3372 | -7.3372 | -7.3372 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -180.778 | -188.1152 | -2750 | -200 | -3138.1152 | 78.45% | 60.69% | 95% | 0% | 1349 | -158
[5 empty] | 2019-07-01 | 7 | 4346.5 | 1167 | -159 | 0 | 0 | 1326 | -43.3636 | -43.3636 | -43.3636 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -181.9222 | -225.2858 | -2750 | -200 | -3175.2858 | 79.38% | 60.69% | 95% | 0% | 1326 | -159
[5 empty] | 2019-07-01 | 8 | 4347 | 1168 | -160 | 0 | 0 | 1328 | -40.2308 | -40.2308 | -40.2308 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -183.0664 | -223.2972 | -2750 | -200 | -3173.2972 | 79.33% | 60.69% | 95% | 0% | 1328 | -160
[5 empty] | 2019-07-01 | 9 | 4347.5 | 1163 | -159 | 1 | 0 | 1322 | -49.629 | -49.629 | -49.629 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -181.9222 | -231.5512 | -3550 | -400 | -4181.5512 | 104.5% | 60.68% | 95% | 0% | 1322 | -159
[5 empty] | 2019-07-01 | 10 | 4348 | 1149 | -158 | 1 | 0 | 1307 | -73.1245 | -73.1245 | -73.1245 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -180.778 | -253.9025 | -3550 | -400 | -4203.9025 | 105.1% | 60.68% | 95% | 0% | 1307 | -158
[5 empty] | 2019-07-01 | 11 | 4348.5 | 1162 | -164 | 1 | 0 | 1326 | -43.3636 | -43.3636 | -43.3636 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -187.643 | -231.0066 | -3550 | -400 | -4181.0066 | 104.5% | 60.68% | 95% | 0% | 1326 | -164
[5 empty] | 2019-07-01 | 12 | 4349 | 1258 | -179 | 1 | 0 | 1437 | 130.5029 | 130.5029 | 130.5029 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -204.8055 | -74.3026 | -3550 | -400 | -4024.3026 | 100.6% | 60.68% | 95% | 0% | 1437 | -179
[5 empty] | 2019-07-01 | 13 | 4349.5 | 1418 | -205 | 1 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -234.5538 | 187.2929 | -3550 | -400 | -3762.7071 | 94.07% | 60.68% | 95% | 0% | 1623 | -205
[5 empty] | 2019-07-01 | 14 | 4350 | 1538 | -241 | 1 | 0 | 1779 | 666.1995 | 666.1995 | 666.1995 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -275.7437 | 390.4558 | -3550 | -400 | -3559.5442 | 88.99% | 60.67% | 95% | 0% | 1779 | -241
[5 empty] | 2019-07-01 | 15 | 4350.5 | 1686 | -283 | 1 | 0 | 1969 | 963.8087 | 963.8087 | 963.8087 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -323.7986 | 640.0101 | -3550 | -400 | -3309.9899 | 82.75% | 60.67% | 95% | 0% | 1969 | -283
[5 empty] | 2019-07-01 | 16 | 4351 | 1736 | -329 | 1 | 0 | 2065 | 1114.1797 | 1114.1797 | 1114.1797 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -376.4302 | 737.7495 | -3550 | -400 | -3212.2505 | 80.31% | 60.67% | 95% | 0% | 2065 | -329
[5 empty] | 2019-07-01 | 17 | 4351.5 | 1769 | -359 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -410.7551 | 802.1055 | -3550 | -400 | -3147.8945 | 78.7% | 60.66% | 95% | 0% | 2128 | -359
[5 empty] | 2019-07-01 | 18 | 4352 | 1727 | -394 | 1 | 0 | 2121 | 1201.8961 | 1201.8961 | 1201.8961 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -450.8009 | 751.0952 | -3550 | -400 | -3198.9048 | 79.97% | 60.66% | 95% | 0% | 2121 | -394
[5 empty] | 2019-07-01 | 19 | 4352.5 | 1687 | -452 | 1 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -517.1625 | 712.9282 | -3550 | -400 | -3237.0718 | 80.93% | 60.65% | 95% | 0% | 2139 | -452
[5 empty] | 2019-07-01 | 20 | 4353 | 1651 | -468 | 1 | 0 | 2119 | 1198.7634 | 1198.7634 | 1198.7634 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -535.4691 | 663.2943 | -3550 | -400 | -3286.7057 | 82.17% | 60.65% | 95% | 0% | 2119 | -468
[5 empty] | 2019-07-01 | 21 | 4353.5 | 1579 | -507 | 1 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -580.0915 | 566.9818 | -3550 | -400 | -3383.0182 | 84.58% | 60.65% | 95% | 0% | 2086 | -507
[5 empty] | 2019-07-01 | 22 | 4354 | 1508 | -551 | 1 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -630.4348 | 474.3468 | -3550 | -400 | -3475.6532 | 86.89% | 60.64% | 95% | 0% | 2059 | -551
[5 empty] | 2019-07-01 | 23 | 4354.5 | 1450 | -593 | 1 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 1367.9308 | 780 | 200 | 2347.9308 | 58.7% | 95% | 0% | -678.4897 | 401.23 | -3550 | -400 | -3548.77 | 88.72% | 60.64% | 95% | 0% | 2043 | -593
[5 empty] | 2019-07-01 | 24 | 4355 | 1389 | -634 | 1 | 0 | 2023 | 1048.3924 | 1048.3924 | 1048.3924 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -725.4005 | 322.992 | -3550 | -400 | -3627.008 | 90.68% | 60.64% | 95% | 0% | 2023 | -634
[5 empty] | 2019-07-01 | 25 | 4355.5 | 1364 | -659 | 1 | 0 | 2023 | 1048.3924 | 1048.3924 | 1048.3924 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -754.0046 | 294.3878 | -3550 | -400 | -3655.6122 | 91.39% | 60.64% | 95% | 0% | 2023 | -659
[5 empty] | 2019-07-01 | 26 | 4356 | 1311 | -680 | 1 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -778.032 | 220.2367 | -3550 | -400 | -3729.7633 | 93.24% | 60.64% | 95% | 0% | 1991 | -680
[5 empty] | 2019-07-01 | 27 | 4356.5 | 1309 | -683 | 1 | 0 | 1992 | 999.8351 | 999.8351 | 999.8351 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -781.4645 | 218.3706 | -3550 | -400 | -3731.6294 | 93.29% | 60.64% | 95% | 0% | 1992 | -683
[5 empty] | 2019-07-01 | 28 | 4357 | 1317 | -673 | 1 | 0 | 1990 | 996.7024 | 996.7024 | 996.7024 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -770.0229 | 226.6795 | -3550 | -400 | -3723.3205 | 93.08% | 60.64% | 95% | 0% | 1990 | -673
[5 empty] | 2019-07-01 | 29 | 4357.5 | 1361 | -645 | 1 | 0 | 2006 | 1021.7642 | 1021.7642 | 1021.7642 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -737.9863 | 283.778 | -3550 | -400 | -3666.222 | 91.66% | 60.64% | 95% | 0% | 2006 | -645
[5 empty] | 2019-07-01 | 30 | 4358 | 1413 | -621 | 1 | 0 | 2034 | 1065.6224 | 1065.6224 | 1065.6224 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -710.5263 | 355.0961 | -3550 | -400 | -3594.9039 | 89.87% | 60.63% | 95% | 0% | 2034 | -621
[5 empty] | 2019-07-01 | 31 | 4358.5 | 1440 | -602 | 1 | 0 | 2042 | 1078.1533 | 1078.1533 | 1078.1533 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -688.7872 | 389.3662 | -3550 | -400 | -3560.6338 | 89.02% | 60.62% | 95% | 0% | 2042 | -602
[5 empty] | 2019-07-01 | 32 | 4359 | 1503 | -573 | 1 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -655.6064 | 475.8033 | -3550 | -400 | -3474.1967 | 86.85% | 60.62% | 95% | 0% | 2076 | -573
[5 empty] | 2019-07-01 | 33 | 4359.5 | 1622 | -520 | 1 | 0 | 2142 | 1234.7898 | 1234.7898 | 1234.7898 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -594.9657 | 639.8241 | -3550 | -400 | -3310.1759 | 82.75% | 60.62% | 95% | 0% | 2142 | -520
[5 empty] | 2019-07-01 | 34 | 4360 | 1740 | -473 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -541.1899 | 804.8117 | -3550 | -400 | -3145.1883 | 78.63% | 60.62% | 95% | 0% | 2213 | -473
[5 empty] | 2019-07-01 | 35 | 4360.5 | 1842 | -436 | 1 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -498.8558 | 948.9595 | -3550 | -400 | -3001.0405 | 75.03% | 60.62% | 95% | 0% | 2278 | -436
[5 empty] | 2019-07-01 | 36 | 4361 | 1889 | -397 | 1 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -454.2334 | 1006.1128 | -3550 | -400 | -2943.8872 | 73.6% | 60.61% | 95% | 0% | 2286 | -397
[5 empty] | 2019-07-01 | 37 | 4361.5 | 1935 | -343 | 1 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -392.4485 | 1055.3668 | -3550 | -400 | -2894.6332 | 72.37% | 60.61% | 95% | 0% | 2278 | -343
[5 empty] | 2019-07-01 | 38 | 4362 | 1974 | -303 | 1 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 1366.3644 | 780 | 200 | 2346.3644 | 58.66% | 95% | 0% | -346.6819 | 1099.567 | -3550 | -400 | -2850.433 | 71.26% | 60.6% | 95% | 0% | 2277 | -303
[5 empty] | 2019-07-01 | 39 | 4362.5 | 2028 | -253 | 1 | 0 | 2281 | 1452.5144 | 1452.5144 | 1452.5144 | 1364.798 | 780 | 200 | 2344.798 | 58.62% | 95% | 0% | -289.4737 | 1163.0407 | -3550 | -400 | -2786.9593 | 69.67% | 60.6% | 95% | 0% | 2281 | -253
[5 empty] | 2019-07-01 | 40 | 4363 | 2058 | -206 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 1364.798 | 780 | 200 | 2344.798 | 58.62% | 95% | 0% | -235.6979 | 1190.1883 | -3550 | -400 | -2759.8117 | 69% | 60.59% | 95% | 0% | 2264 | -206
[5 empty] | 2019-07-01 | 41 | 4363.5 | 2073 | -161 | 1 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 1364.798 | 780 | 200 | 2344.798 | 58.62% | 95% | 0% | -184.2105 | 1194.6848 | -3550 | -400 | -2755.3152 | 68.88% | 60.59% | 95% | 0% | 2234 | -161
[5 empty] | 2019-07-01 | 42 | 4364 | 2085 | -122 | 1 | 0 | 2207 | 1336.6035 | 1336.6035 | 1336.6035 | 1364.798 | 780 | 200 | 2344.798 | 58.62% | 95% | 0% | -139.5881 | 1197.0154 | -3550 | -400 | -2752.9846 | 68.82% | 60.59% | 95% | 0% | 2207 | -122
[5 empty] | 2019-07-01 | 43 | 4364.5 | 2099 | -100 | 1 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 1364.798 | 780 | 200 | 2344.798 | 58.62% | 95% | 0% | -114.4165 | 1209.6561 | -3550 | -400 | -2740.3439 | 68.51% | 60.59% | 95% | 0% | 2199 | -100
[5 empty] | 2019-07-01 | 44 | 4365 | 2079 | -90 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 1364.798 | 780 | 200 | 2344.798 | 58.62% | 95% | 0% | -102.9748 | 1174.1068 | -3550 | -400 | -2775.8932 | 69.4% | 60.58% | 95% | 0% | 2169 | -90
[5 empty] | 2019-07-01 | 45 | 4365.5 | 2036 | -88 | 1 | 0 | 2124 | 1206.5952 | 1206.5952 | 1206.5952 | 1364.798 | 780 | 200 | 2344.798 | 58.62% | 95% | 0% | -100.6865 | 1105.9087 | -3550 | -400 | -2844.0913 | 71.1% | 60.58% | 95% | 0% | 2124 | -88
[5 empty] | 2019-07-01 | 46 | 4366 | 1952 | -85 | 0 | 0 | 2037 | 1070.3215 | 1070.3215 | 1070.3215 | 1364.798 | 780 | 200 | 2344.798 | 58.62% | 95% | 0% | -97.254 | 973.0675 | -2750 | -200 | -1976.9325 | 49.42% | 60.58% | 95% | 0% | 2037 | -85
[5 empty] | 2019-07-01 | 47 | 4366.5 | 1817 | -85 | 0 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 1364.798 | 780 | 200 | 2344.798 | 58.62% | 95% | 0% | -97.254 | 761.6083 | -2750 | -200 | -2188.3917 | 54.71% | 60.57% | 95% | 0% | 1902 | -85
[5 empty] | 2019-07-01 | 48 | 4367 | 1698 | -84 | 0 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 1364.798 | 780 | 200 | 2344.798 | 58.62% | 95% | 0% | -96.1098 | 574.7888 | -2750 | -200 | -2375.2112 | 59.38% | 60.57% | 95% | 0% | 1782 | -84
[5 empty] | 2019-07-02 | 1 | 4367.5 | 1629 | -80 | 0 | 0 | 1709 | 556.554 | 556.554 | 556.554 | 1364.798 | 780 | 200 | 2344.798 | 58.62% | 95% | 0% | -91.5332 | 465.0208 | -2750 | -200 | -2484.9792 | 62.12% | 60.57% | 95% | 0% | 1709 | -80
[5 empty] | 2019-07-02 | 2 | 4368 | 1588 | -77 | 0 | 0 | 1665 | 487.634 | 487.634 | 487.634 | 1364.798 | 780 | 200 | 2344.798 | 58.62% | 95% | 0% | -88.1007 | 399.5333 | -2750 | -200 | -2550.4667 | 63.76% | 60.56% | 95% | 0% | 1665 | -77
[5 empty] | 2019-07-02 | 3 | 4368.5 | 1550 | -77 | 0 | 0 | 1627 | 428.1121 | 428.1121 | 428.1121 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -88.1007 | 340.0114 | -2750 | -200 | -2609.9886 | 65.25% | 60.56% | 95% | 0% | 1627 | -77
[5 empty] | 2019-07-02 | 4 | 4369 | 1527 | -77 | 0 | 0 | 1604 | 392.0857 | 392.0857 | 392.0857 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -88.1007 | 303.9851 | -2750 | -200 | -2646.0149 | 66.15% | 60.56% | 95% | 0% | 1604 | -77
[5 empty] | 2019-07-02 | 5 | 4369.5 | 1503 | -76 | 0 | 0 | 1579 | 352.9266 | 352.9266 | 352.9266 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -86.9565 | 265.9701 | -2750 | -200 | -2684.0299 | 67.1% | 60.55% | 95% | 0% | 1579 | -76
[5 empty] | 2019-07-02 | 6 | 4370 | 1478 | -75 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -85.8124 | 226.3888 | -2750 | -200 | -2723.6112 | 68.09% | 60.55% | 95% | 0% | 1553 | -75
[5 empty] | 2019-07-02 | 7 | 4370.5 | 1460 | -74 | 0 | 0 | 1534 | 282.4402 | 282.4402 | 282.4402 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -84.6682 | 197.772 | -2750 | -200 | -2752.228 | 68.81% | 60.55% | 95% | 0% | 1534 | -74
[5 empty] | 2019-07-02 | 8 | 4371 | 1456 | -73 | 0 | 0 | 1529 | 274.6084 | 274.6084 | 274.6084 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -83.524 | 191.0844 | -2750 | -200 | -2758.9156 | 68.97% | 60.55% | 95% | 0% | 1529 | -73
[5 empty] | 2019-07-02 | 9 | 4371.5 | 1453 | -73 | 0 | 0 | 1526 | 269.9093 | 269.9093 | 269.9093 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -83.524 | 186.3853 | -2750 | -200 | -2763.6147 | 69.09% | 60.54% | 95% | 0% | 1526 | -73
[5 empty] | 2019-07-02 | 10 | 4372 | 1437 | -73 | 0 | 0 | 1510 | 244.8475 | 244.8475 | 244.8475 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -83.524 | 161.3235 | -2750 | -200 | -2788.6765 | 69.72% | 60.54% | 95% | 0% | 1510 | -73
[5 empty] | 2019-07-02 | 11 | 4372.5 | 1475 | -78 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -89.2449 | 222.9563 | -2750 | -200 | -2727.0437 | 68.18% | 60.54% | 95% | 0% | 1553 | -78
[5 empty] | 2019-07-02 | 12 | 4373 | 1527 | -101 | 0 | 0 | 1628 | 429.6785 | 429.6785 | 429.6785 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -115.5606 | 314.1178 | -2750 | -200 | -2635.8822 | 65.9% | 60.53% | 95% | 0% | 1628 | -101
[5 empty] | 2019-07-02 | 13 | 4373.5 | 1674 | -136 | 1 | 0 | 1810 | 714.7568 | 714.7568 | 714.7568 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -155.6064 | 559.1504 | -3550 | -400 | -3390.8496 | 84.77% | 60.52% | 95% | 0% | 1810 | -136
[5 empty] | 2019-07-02 | 14 | 4374 | 1806 | -172 | 1 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -196.7963 | 781.1097 | -3550 | -400 | -3168.8903 | 79.22% | 60.51% | 95% | 0% | 1978 | -172
[5 empty] | 2019-07-02 | 15 | 4374.5 | 1932 | -223 | 1 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -255.1487 | 1000.0038 | -3550 | -400 | -2949.9962 | 73.75% | 60.51% | 95% | 0% | 2155 | -223
[5 empty] | 2019-07-02 | 16 | 4375 | 1925 | -286 | 1 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 1363.2317 | 780 | 200 | 2343.2317 | 58.58% | 95% | 0% | -327.2311 | 1015.6378 | -3550 | -400 | -2934.3622 | 73.36% | 60.51% | 95% | 0% | 2211 | -286
[5 empty] | 2019-07-02 | 17 | 4375.5 | 1893 | -349 | 1 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -399.3135 | 992.1127 | -3550 | -400 | -2957.8873 | 73.95% | 60.51% | 95% | 0% | 2242 | -349
[5 empty] | 2019-07-02 | 18 | 4376 | 1820 | -400 | 1 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -457.6659 | 899.3003 | -3550 | -400 | -3050.6997 | 76.27% | 60.5% | 95% | 0% | 2220 | -400
[5 empty] | 2019-07-02 | 19 | 4376.5 | 1748 | -460 | 1 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -526.3158 | 811.854 | -3550 | -400 | -3138.146 | 78.45% | 60.5% | 95% | 0% | 2208 | -460
[5 empty] | 2019-07-02 | 20 | 4377 | 1663 | -515 | 1 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -589.2449 | 701.934 | -3550 | -400 | -3248.066 | 81.2% | 60.5% | 95% | 0% | 2178 | -515
[5 empty] | 2019-07-02 | 21 | 4377.5 | 1630 | -545 | 1 | 0 | 2175 | 1286.4798 | 1286.4798 | 1286.4798 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -623.5698 | 662.91 | -3550 | -400 | -3287.09 | 82.18% | 60.5% | 95% | 0% | 2175 | -545
[5 empty] | 2019-07-02 | 22 | 4378 | 1624 | -552 | 1 | 0 | 2176 | 1288.0462 | 1288.0462 | 1288.0462 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -631.5789 | 656.4672 | -3550 | -400 | -3293.5328 | 82.34% | 60.5% | 95% | 0% | 2176 | -552
[5 empty] | 2019-07-02 | 23 | 4378.5 | 1644 | -543 | 1 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -621.2815 | 683.9947 | -3550 | -400 | -3266.0053 | 81.65% | 60.49% | 95% | 0% | 2187 | -543
[5 empty] | 2019-07-02 | 24 | 4379 | 1615 | -558 | 1 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -638.4439 | 644.9031 | -3550 | -400 | -3305.0969 | 82.63% | 60.49% | 95% | 0% | 2173 | -558
[5 empty] | 2019-07-02 | 25 | 4379.5 | 1622 | -557 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -637.2998 | 655.4455 | -3550 | -400 | -3294.5545 | 82.36% | 60.49% | 95% | 0% | 2179 | -557
[5 empty] | 2019-07-02 | 26 | 4380 | 1619 | -553 | 1 | 0 | 2172 | 1281.7807 | 1281.7807 | 1281.7807 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -632.7231 | 649.0576 | -3550 | -400 | -3300.9424 | 82.52% | 60.49% | 95% | 0% | 2172 | -553
[5 empty] | 2019-07-02 | 27 | 4380.5 | 1604 | -557 | 1 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -637.2998 | 627.2509 | -3550 | -400 | -3322.7491 | 83.07% | 60.48% | 95% | 0% | 2161 | -557
[5 empty] | 2019-07-02 | 28 | 4381 | 1589 | -550 | 1 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -629.2906 | 600.8001 | -3550 | -400 | -3349.1999 | 83.73% | 60.48% | 95% | 0% | 2139 | -550
[5 empty] | 2019-07-02 | 29 | 4381.5 | 1605 | -548 | 1 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -627.0023 | 625.0175 | -3550 | -400 | -3324.9825 | 83.12% | 60.47% | 95% | 0% | 2153 | -548
[5 empty] | 2019-07-02 | 30 | 4382 | 1617 | -540 | 1 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -617.849 | 640.4363 | -3550 | -400 | -3309.5637 | 82.74% | 60.46% | 95% | 0% | 2157 | -540
[5 empty] | 2019-07-02 | 31 | 4382.5 | 1637 | -513 | 1 | 0 | 2150 | 1247.3207 | 1247.3207 | 1247.3207 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -586.9565 | 660.3642 | -3550 | -400 | -3289.6358 | 82.24% | 60.46% | 95% | 0% | 2150 | -513
[5 empty] | 2019-07-02 | 32 | 4383 | 1666 | -520 | 1 | 0 | 2186 | 1303.7098 | 1303.7098 | 1303.7098 | 1361.6653 | 780 | 200 | 2341.6653 | 58.54% | 95% | 0% | -594.9657 | 708.7441 | -3550 | -400 | -3241.2559 | 81.03% | 60.46% | 95% | 0% | 2186 | -520
[5 empty] | 2019-07-02 | 33 | 4383.5 | 1775 | -464 | 1 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 1360.0989 | 780 | 200 | 2340.0989 | 58.5% | 95% | 0% | -530.8924 | 855.8347 | -3550 | -400 | -3094.1653 | 77.35% | 60.45% | 95% | 0% | 2239 | -464
[5 empty] | 2019-07-02 | 34 | 4384 | 1868 | -434 | 1 | 0 | 2302 | 1485.4081 | 1485.4081 | 1485.4081 | 1360.0989 | 780 | 200 | 2340.0989 | 58.5% | 95% | 0% | -496.5675 | 988.8406 | -3550 | -400 | -2961.1594 | 74.03% | 60.45% | 95% | 0% | 2302 | -434
[5 empty] | 2019-07-02 | 35 | 4384.5 | 1968 | -392 | 1 | 0 | 2360 | 1576.2572 | 1576.2572 | 1576.2572 | 1360.0989 | 780 | 200 | 2340.0989 | 58.5% | 95% | 0% | -448.5126 | 1127.7446 | -3550 | -400 | -2822.2554 | 70.56% | 60.45% | 95% | 0% | 2360 | -392
[5 empty] | 2019-07-02 | 36 | 4385 | 2049 | -334 | 1 | 0 | 2383 | 1612.2836 | 1612.2836 | 1612.2836 | 1360.0989 | 780 | 200 | 2340.0989 | 58.5% | 95% | 0% | -382.151 | 1230.1326 | -3550 | -400 | -2719.8674 | 68% | 60.44% | 95% | 0% | 2383 | -334
[5 empty] | 2019-07-02 | 37 | 4385.5 | 2097 | -284 | 1 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 1360.0989 | 780 | 200 | 2340.0989 | 58.5% | 95% | 0% | -324.9428 | 1284.2081 | -3550 | -400 | -2665.7919 | 66.64% | 60.44% | 95% | 0% | 2381 | -284
[5 empty] | 2019-07-02 | 38 | 4386 | 2156 | -245 | 1 | 0 | 2401 | 1640.4782 | 1640.4782 | 1640.4782 | 1360.0989 | 780 | 200 | 2340.0989 | 58.5% | 95% | 0% | -280.3204 | 1360.1578 | -3550 | -400 | -2589.8422 | 64.75% | 60.44% | 95% | 0% | 2401 | -245
[5 empty] | 2019-07-02 | 39 | 4386.5 | 2227 | -193 | 1 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 1360.0989 | 780 | 200 | 2340.0989 | 58.5% | 95% | 0% | -220.8238 | 1449.4153 | -3550 | -400 | -2500.5847 | 62.51% | 60.43% | 95% | 0% | 2420 | -193
[5 empty] | 2019-07-02 | 40 | 4387 | 2248 | -154 | 1 | 0 | 2402 | 1642.0445 | 1642.0445 | 1642.0445 | 1360.0989 | 780 | 200 | 2340.0989 | 58.5% | 95% | 0% | -176.2014 | 1465.8431 | -3550 | -400 | -2484.1569 | 62.1% | 60.42% | 95% | 0% | 2402 | -154
[5 empty] | 2019-07-02 | 41 | 4387.5 | 2246 | -114 | 1 | 0 | 2360 | 1576.2572 | 1576.2572 | 1576.2572 | 1358.5326 | 780 | 200 | 2338.5326 | 58.46% | 95% | 0% | -130.4348 | 1445.8224 | -3550 | -400 | -2504.1776 | 62.6% | 60.42% | 95% | 0% | 2360 | -114
[5 empty] | 2019-07-02 | 42 | 4388 | 2255 | -86 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 1358.5326 | 780 | 200 | 2338.5326 | 58.46% | 95% | 0% | -98.3982 | 1448.0981 | -3550 | -400 | -2501.9019 | 62.55% | 60.42% | 95% | 0% | 2341 | -86
[5 empty] | 2019-07-02 | 43 | 4388.5 | 2229 | -74 | 1 | 0 | 2303 | 1486.9744 | 1486.9744 | 1486.9744 | 1358.5326 | 780 | 200 | 2338.5326 | 58.46% | 95% | 0% | -84.6682 | 1402.3063 | -3550 | -400 | -2547.6937 | 63.69% | 60.41% | 95% | 0% | 2303 | -74
[5 empty] | 2019-07-02 | 44 | 4389 | 2188 | -71 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 1358.5326 | 780 | 200 | 2338.5326 | 58.46% | 95% | 0% | -81.2357 | 1336.8187 | -3550 | -400 | -2613.1813 | 65.33% | 60.41% | 95% | 0% | 2259 | -71
[5 empty] | 2019-07-02 | 45 | 4389.5 | 2157 | -71 | 1 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 1358.5326 | 780 | 200 | 2338.5326 | 58.46% | 95% | 0% | -81.2357 | 1288.2614 | -3550 | -400 | -2661.7386 | 66.54% | 60.4% | 95% | 0% | 2228 | -71
[5 empty] | 2019-07-02 | 46 | 4390 | 2064 | -71 | 0 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 1358.5326 | 780 | 200 | 2338.5326 | 58.46% | 95% | 0% | -81.2357 | 1142.5895 | -2750 | -200 | -1807.4105 | 45.19% | 60.4% | 95% | 0% | 2135 | -71
[5 empty] | 2019-07-02 | 47 | 4390.5 | 1907 | -71 | 0 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 1358.5326 | 780 | 200 | 2338.5326 | 58.46% | 95% | 0% | -81.2357 | 896.6703 | -2750 | -200 | -2053.3297 | 51.33% | 60.4% | 95% | 0% | 1978 | -71
[5 empty] | 2019-07-02 | 48 | 4391 | 1794 | -71 | 0 | 0 | 1865 | 800.9068 | 800.9068 | 800.9068 | 1358.5326 | 780 | 200 | 2338.5326 | 58.46% | 95% | 0% | -81.2357 | 719.6711 | -2750 | -200 | -2230.3289 | 55.76% | 60.4% | 95% | 0% | 1865 | -71
[5 empty] | 2019-07-03 | 1 | 4391.5 | 1698 | -68 | 0 | 0 | 1766 | 645.8368 | 645.8368 | 645.8368 | 1358.5326 | 780 | 200 | 2338.5326 | 58.46% | 95% | 0% | -77.8032 | 568.0336 | -2750 | -200 | -2381.9664 | 59.55% | 60.4% | 95% | 0% | 1766 | -68
[5 empty] | 2019-07-03 | 2 | 4392 | 1637 | -64 | 0 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 1358.5326 | 780 | 200 | 2338.5326 | 58.46% | 95% | 0% | -73.2265 | 470.7965 | -2750 | -200 | -2479.2035 | 61.98% | 60.4% | 95% | 0% | 1701 | -64
[5 empty] | 2019-07-03 | 3 | 4392.5 | 1603 | -63 | 0 | 0 | 1666 | 489.2003 | 489.2003 | 489.2003 | 1358.5326 | 780 | 200 | 2338.5326 | 58.46% | 95% | 0% | -72.0824 | 417.1179 | -2750 | -200 | -2532.8821 | 63.32% | 60.39% | 95% | 0% | 1666 | -63
[5 empty] | 2019-07-03 | 4 | 4393 | 1591 | -61 | 0 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -69.7941 | 397.4772 | -2750 | -200 | -2552.5228 | 63.81% | 60.39% | 95% | 0% | 1652 | -61
[5 empty] | 2019-07-03 | 5 | 4393.5 | 1579 | -59 | 0 | 0 | 1638 | 445.3421 | 445.3421 | 445.3421 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -67.5057 | 377.8364 | -2750 | -200 | -2572.1636 | 64.3% | 60.38% | 95% | 0% | 1638 | -59
[5 empty] | 2019-07-03 | 6 | 4394 | 1546 | -57 | 0 | 0 | 1603 | 390.5194 | 390.5194 | 390.5194 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -65.2174 | 325.302 | -2750 | -200 | -2624.698 | 65.62% | 60.38% | 95% | 0% | 1603 | -57
[5 empty] | 2019-07-03 | 7 | 4394.5 | 1544 | -55 | 0 | 0 | 1599 | 384.2539 | 384.2539 | 384.2539 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -62.9291 | 321.3249 | -2750 | -200 | -2628.6751 | 65.72% | 60.38% | 95% | 0% | 1599 | -55
[5 empty] | 2019-07-03 | 8 | 4395 | 1538 | -53 | 0 | 0 | 1591 | 371.723 | 371.723 | 371.723 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -60.6407 | 311.0823 | -2750 | -200 | -2638.9177 | 65.97% | 60.37% | 95% | 0% | 1591 | -53
[5 empty] | 2019-07-03 | 9 | 4395.5 | 1542 | -51 | 0 | 0 | 1593 | 374.8557 | 374.8557 | 374.8557 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -58.3524 | 316.5033 | -2750 | -200 | -2633.4967 | 65.84% | 60.37% | 95% | 0% | 1593 | -51
[5 empty] | 2019-07-03 | 10 | 4396 | 1532 | -49 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -56.0641 | 299.9953 | -2750 | -200 | -2650.0047 | 66.25% | 60.37% | 95% | 0% | 1581 | -49
[5 empty] | 2019-07-03 | 11 | 4396.5 | 1569 | -53 | 0 | 0 | 1622 | 420.2803 | 420.2803 | 420.2803 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -60.6407 | 359.6396 | -2750 | -200 | -2590.3604 | 64.76% | 60.36% | 95% | 0% | 1622 | -53
[5 empty] | 2019-07-03 | 12 | 4397 | 1611 | -74 | 0 | 0 | 1685 | 518.9613 | 518.9613 | 518.9613 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -84.6682 | 434.2931 | -2750 | -200 | -2515.7069 | 62.89% | 60.36% | 95% | 0% | 1685 | -74
[5 empty] | 2019-07-03 | 13 | 4397.5 | 1756 | -108 | 0 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -123.5698 | 675.7707 | -2750 | -200 | -2274.2293 | 56.86% | 60.35% | 95% | 0% | 1864 | -108
[5 empty] | 2019-07-03 | 14 | 4398 | 1880 | -151 | 1 | 0 | 2031 | 1060.9233 | 1060.9233 | 1060.9233 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -172.7689 | 888.1545 | -3550 | -400 | -3061.8455 | 76.55% | 60.35% | 95% | 0% | 2031 | -151
[5 empty] | 2019-07-03 | 15 | 4398.5 | 1986 | -204 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -233.4096 | 1076.5657 | -3550 | -400 | -2873.4343 | 71.84% | 60.35% | 95% | 0% | 2190 | -204
[5 empty] | 2019-07-03 | 16 | 4399 | 1970 | -262 | 1 | 0 | 2232 | 1375.7626 | 1375.7626 | 1375.7626 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -299.7712 | 1075.9914 | -3550 | -400 | -2874.0086 | 71.85% | 60.35% | 95% | 0% | 2232 | -262
[5 empty] | 2019-07-03 | 17 | 4399.5 | 1907 | -326 | 1 | 0 | 2233 | 1377.3289 | 1377.3289 | 1377.3289 | 1356.9662 | 780 | 200 | 2336.9662 | 58.42% | 95% | 0% | -372.9977 | 1004.3312 | -3550 | -400 | -2945.6688 | 73.64% | 60.33% | 95% | 0% | 2233 | -326
[5 empty] | 2019-07-03 | 18 | 4400 | 1834 | -384 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 1355.3998 | 780 | 200 | 2335.3998 | 58.38% | 95% | 0% | -439.3593 | 914.4742 | -3550 | -400 | -3035.5258 | 75.89% | 60.33% | 95% | 0% | 2218 | -384
[5 empty] | 2019-07-03 | 19 | 4400.5 | 1780 | -452 | 1 | 0 | 2232 | 1375.7626 | 1375.7626 | 1375.7626 | 1355.3998 | 780 | 200 | 2335.3998 | 58.38% | 95% | 0% | -517.1625 | 858.6001 | -3550 | -400 | -3091.3999 | 77.28% | 60.32% | 95% | 0% | 2232 | -452
[5 empty] | 2019-07-03 | 20 | 4401 | 1683 | -513 | 1 | 0 | 2196 | 1319.3735 | 1319.3735 | 1319.3735 | 1355.3998 | 780 | 200 | 2335.3998 | 58.38% | 95% | 0% | -586.9565 | 732.4169 | -3550 | -400 | -3217.5831 | 80.44% | 60.32% | 95% | 0% | 2196 | -513
[5 empty] | 2019-07-03 | 21 | 4401.5 | 1636 | -548 | 1 | 0 | 2184 | 1300.5771 | 1300.5771 | 1300.5771 | 1355.3998 | 780 | 200 | 2335.3998 | 58.38% | 95% | 0% | -627.0023 | 673.5748 | -3550 | -400 | -3276.4252 | 81.91% | 60.32% | 95% | 0% | 2184 | -548
[5 empty] | 2019-07-03 | 22 | 4402 | 1627 | -553 | 1 | 0 | 2180 | 1294.3116 | 1294.3116 | 1294.3116 | 1355.3998 | 780 | 200 | 2335.3998 | 58.38% | 95% | 0% | -632.7231 | 661.5885 | -3550 | -400 | -3288.4115 | 82.21% | 60.32% | 95% | 0% | 2180 | -553
[5 empty] | 2019-07-03 | 23 | 4402.5 | 1620 | -574 | 1 | 0 | 2194 | 1316.2407 | 1316.2407 | 1316.2407 | 1355.3998 | 780 | 200 | 2335.3998 | 58.38% | 95% | 0% | -656.7506 | 659.4902 | -3550 | -400 | -3290.5098 | 82.26% | 60.32% | 95% | 0% | 2194 | -574
[5 empty] | 2019-07-03 | 24 | 4403 | 1624 | -573 | 1 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -655.6064 | 665.3334 | -3550 | -400 | -3284.6666 | 82.12% | 60.32% | 95% | 0% | 2197 | -573
[5 empty] | 2019-07-03 | 25 | 4403.5 | 1640 | -594 | 1 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -679.6339 | 699.2614 | -3550 | -400 | -3250.7386 | 81.27% | 60.31% | 95% | 0% | 2234 | -594
[5 empty] | 2019-07-03 | 26 | 4404 | 1606 | -625 | 1 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -715.103 | 659.0932 | -3550 | -400 | -3290.9068 | 82.27% | 60.31% | 95% | 0% | 2231 | -625
[5 empty] | 2019-07-03 | 27 | 4404.5 | 1557 | -634 | 1 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -725.4005 | 586.1412 | -3550 | -400 | -3363.8588 | 84.1% | 60.3% | 95% | 0% | 2191 | -634
[5 empty] | 2019-07-03 | 28 | 4405 | 1510 | -646 | 1 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -739.1304 | 517.5884 | -3550 | -400 | -3432.4116 | 85.81% | 60.3% | 95% | 0% | 2156 | -646
[5 empty] | 2019-07-03 | 29 | 4405.5 | 1500 | -634 | 1 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -725.4005 | 496.8584 | -3550 | -400 | -3453.1416 | 86.33% | 60.3% | 95% | 0% | 2134 | -634
[5 empty] | 2019-07-03 | 30 | 4406 | 1468 | -641 | 1 | 0 | 2109 | 1183.0998 | 1183.0998 | 1183.0998 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -733.4096 | 449.6901 | -3550 | -400 | -3500.3099 | 87.51% | 60.29% | 95% | 0% | 2109 | -641
[5 empty] | 2019-07-03 | 31 | 4406.5 | 1493 | -616 | 1 | 0 | 2109 | 1183.0998 | 1183.0998 | 1183.0998 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -704.8055 | 478.2943 | -3550 | -400 | -3471.7057 | 86.79% | 60.29% | 95% | 0% | 2109 | -616
[5 empty] | 2019-07-03 | 32 | 4407 | 1571 | -581 | 1 | 0 | 2152 | 1250.4534 | 1250.4534 | 1250.4534 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -664.7597 | 585.6937 | -3550 | -400 | -3364.3063 | 84.11% | 60.29% | 95% | 0% | 2152 | -581
[5 empty] | 2019-07-03 | 33 | 4407.5 | 1672 | -530 | 1 | 0 | 2202 | 1328.7716 | 1328.7716 | 1328.7716 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -606.4073 | 722.3643 | -3550 | -400 | -3227.6357 | 80.69% | 60.29% | 95% | 0% | 2202 | -530
[5 empty] | 2019-07-03 | 34 | 4408 | 1786 | -483 | 1 | 0 | 2269 | 1433.7181 | 1433.7181 | 1433.7181 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -552.6316 | 881.0865 | -3550 | -400 | -3068.9135 | 76.72% | 60.29% | 95% | 0% | 2269 | -483
[5 empty] | 2019-07-03 | 35 | 4408.5 | 1899 | -438 | 1 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -501.1442 | 1039.0867 | -3550 | -400 | -2910.9133 | 72.77% | 60.29% | 95% | 0% | 2337 | -438
[5 empty] | 2019-07-03 | 36 | 4409 | 1996 | -373 | 1 | 0 | 2369 | 1590.3545 | 1590.3545 | 1590.3545 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -426.7735 | 1163.581 | -3550 | -400 | -2786.419 | 69.66% | 60.28% | 95% | 0% | 2369 | -373
[5 empty] | 2019-07-03 | 37 | 4409.5 | 2079 | -313 | 1 | 0 | 2392 | 1626.3809 | 1626.3809 | 1626.3809 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -358.1236 | 1268.2573 | -3550 | -400 | -2681.7427 | 67.04% | 60.28% | 95% | 0% | 2392 | -313
[5 empty] | 2019-07-03 | 38 | 4410 | 2170 | -249 | 1 | 0 | 2419 | 1668.6727 | 1668.6727 | 1668.6727 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -284.897 | 1383.7757 | -3550 | -400 | -2566.2243 | 64.16% | 60.28% | 95% | 0% | 2419 | -249
[5 empty] | 2019-07-03 | 39 | 4410.5 | 2220 | -197 | 1 | 0 | 2417 | 1665.54 | 1665.54 | 1665.54 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -225.4005 | 1440.1395 | -3550 | -400 | -2509.8605 | 62.75% | 60.26% | 95% | 0% | 2417 | -197
[5 empty] | 2019-07-03 | 40 | 4411 | 2263 | -153 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -175.0572 | 1488.9164 | -3550 | -400 | -2461.0836 | 61.53% | 60.26% | 95% | 0% | 2416 | -153
[5 empty] | 2019-07-03 | 41 | 4411.5 | 2280 | -115 | 1 | 0 | 2395 | 1631.08 | 1631.08 | 1631.08 | 1353.8335 | 780 | 200 | 2333.8335 | 58.35% | 95% | 0% | -131.5789 | 1499.501 | -3550 | -400 | -2450.499 | 61.26% | 60.25% | 95% | 0% | 2395 | -115
[5 empty] | 2019-07-03 | 42 | 4412 | 2287 | -84 | 1 | 0 | 2371 | 1593.4872 | 1593.4872 | 1593.4872 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -96.1098 | 1497.3774 | -3550 | -400 | -2452.6226 | 61.32% | 60.25% | 95% | 0% | 2371 | -84
[5 empty] | 2019-07-03 | 43 | 4412.5 | 2243 | -68 | 1 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -77.8032 | 1421.7022 | -3550 | -400 | -2528.2978 | 63.21% | 60.24% | 95% | 0% | 2311 | -68
[5 empty] | 2019-07-03 | 44 | 4413 | 2211 | -65 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -74.3707 | 1370.3119 | -3550 | -400 | -2579.6881 | 64.49% | 60.24% | 95% | 0% | 2276 | -65
[5 empty] | 2019-07-03 | 45 | 4413.5 | 2188 | -62 | 1 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -70.9382 | 1333.0189 | -3550 | -400 | -2616.9811 | 65.42% | 60.24% | 95% | 0% | 2250 | -62
[5 empty] | 2019-07-03 | 46 | 4414 | 2065 | -60 | 0 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -68.6499 | 1139.5117 | -2750 | -200 | -1810.4883 | 45.26% | 60.23% | 95% | 0% | 2125 | -60
[5 empty] | 2019-07-03 | 47 | 4414.5 | 1925 | -58 | 0 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -66.3616 | 919.3763 | -2750 | -200 | -2030.6237 | 50.77% | 60.23% | 95% | 0% | 1983 | -58
[5 empty] | 2019-07-03 | 48 | 4415 | 1804 | -57 | 0 | 0 | 1861 | 794.6414 | 794.6414 | 794.6414 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -65.2174 | 729.424 | -2750 | -200 | -2220.576 | 55.51% | 60.23% | 95% | 0% | 1861 | -57
[5 empty] | 2019-07-04 | 1 | 4415.5 | 1707 | -56 | 0 | 0 | 1763 | 641.1377 | 641.1377 | 641.1377 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -64.0732 | 577.0644 | -2750 | -200 | -2372.9356 | 59.32% | 60.23% | 95% | 0% | 1763 | -56
[5 empty] | 2019-07-04 | 2 | 4416 | 1645 | -54 | 0 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -61.7849 | 479.1055 | -2750 | -200 | -2470.8945 | 61.77% | 60.23% | 95% | 0% | 1699 | -54
[5 empty] | 2019-07-04 | 3 | 4416.5 | 1605 | -53 | 0 | 0 | 1658 | 476.6694 | 476.6694 | 476.6694 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -60.6407 | 416.0287 | -2750 | -200 | -2533.9713 | 63.35% | 60.23% | 95% | 0% | 1658 | -53
[5 empty] | 2019-07-04 | 4 | 4417 | 1580 | -52 | 0 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -59.4966 | 376.4474 | -2750 | -200 | -2573.5526 | 64.34% | 60.22% | 95% | 0% | 1632 | -52
[5 empty] | 2019-07-04 | 5 | 4417.5 | 1550 | -53 | 0 | 0 | 1603 | 390.5194 | 390.5194 | 390.5194 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -60.6407 | 329.8786 | -2750 | -200 | -2620.1214 | 65.5% | 60.21% | 95% | 0% | 1603 | -53
[5 empty] | 2019-07-04 | 6 | 4418 | 1525 | -53 | 0 | 0 | 1578 | 351.3603 | 351.3603 | 351.3603 | 1352.2671 | 780 | 200 | 2332.2671 | 58.31% | 95% | 0% | -60.6407 | 290.7195 | -2750 | -200 | -2659.2805 | 66.48% | 60.21% | 95% | 0% | 1578 | -53
[5 empty] | 2019-07-04 | 7 | 4418.5 | 1508 | -54 | 0 | 0 | 1562 | 326.2984 | 326.2984 | 326.2984 | 1350.7007 | 780 | 200 | 2330.7007 | 58.27% | 95% | 0% | -61.7849 | 264.5135 | -2750 | -200 | -2685.4865 | 67.14% | 60.21% | 95% | 0% | 1562 | -54
[5 empty] | 2019-07-04 | 8 | 4419 | 1505 | -54 | 0 | 0 | 1559 | 321.5993 | 321.5993 | 321.5993 | 1350.7007 | 780 | 200 | 2330.7007 | 58.27% | 95% | 0% | -61.7849 | 259.8144 | -2750 | -200 | -2690.1856 | 67.25% | 60.21% | 95% | 0% | 1559 | -54
[5 empty] | 2019-07-04 | 9 | 4419.5 | 1505 | -56 | 0 | 0 | 1561 | 324.7321 | 324.7321 | 324.7321 | 1350.7007 | 780 | 200 | 2330.7007 | 58.27% | 95% | 0% | -64.0732 | 260.6588 | -2750 | -200 | -2689.3412 | 67.23% | 60.21% | 95% | 0% | 1561 | -56
[5 empty] | 2019-07-04 | 10 | 4420 | 1477 | -57 | 0 | 0 | 1534 | 282.4402 | 282.4402 | 282.4402 | 1350.7007 | 780 | 200 | 2330.7007 | 58.27% | 95% | 0% | -65.2174 | 217.2228 | -2750 | -200 | -2732.7772 | 68.32% | 60.2% | 95% | 0% | 1534 | -57
[5 empty] | 2019-07-04 | 11 | 4420.5 | 1505 | -63 | 0 | 0 | 1568 | 335.6966 | 335.6966 | 335.6966 | 1350.7007 | 780 | 200 | 2330.7007 | 58.27% | 95% | 0% | -72.0824 | 263.6142 | -2750 | -200 | -2686.3858 | 67.16% | 60.2% | 95% | 0% | 1568 | -63
[5 empty] | 2019-07-04 | 12 | 4421 | 1561 | -82 | 0 | 0 | 1643 | 453.1739 | 453.1739 | 453.1739 | 1350.7007 | 780 | 200 | 2330.7007 | 58.27% | 95% | 0% | -93.8215 | 359.3524 | -2750 | -200 | -2590.6476 | 64.77% | 60.2% | 95% | 0% | 1643 | -82
[5 empty] | 2019-07-04 | 13 | 4421.5 | 1693 | -115 | 0 | 0 | 1808 | 711.6241 | 711.6241 | 711.6241 | 1350.7007 | 780 | 200 | 2330.7007 | 58.27% | 95% | 0% | -131.5789 | 580.0451 | -2750 | -200 | -2369.9549 | 59.25% | 60.2% | 95% | 0% | 1808 | -115
[5 empty] | 2019-07-04 | 14 | 4422 | 1797 | -157 | 1 | 0 | 1954 | 940.3133 | 940.3133 | 940.3133 | 1350.7007 | 780 | 200 | 2330.7007 | 58.27% | 95% | 0% | -179.6339 | 760.6794 | -3550 | -400 | -3189.3206 | 79.73% | 60.2% | 95% | 0% | 1954 | -157
[5 empty] | 2019-07-04 | 15 | 4422.5 | 1928 | -210 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1350.7007 | 780 | 200 | 2330.7007 | 58.27% | 95% | 0% | -240.2746 | 988.2497 | -3550 | -400 | -2961.7503 | 74.04% | 60.2% | 95% | 0% | 2138 | -210
[5 empty] | 2019-07-04 | 16 | 4423 | 1912 | -269 | 1 | 0 | 2181 | 1295.878 | 1295.878 | 1295.878 | 1350.7007 | 780 | 200 | 2330.7007 | 58.27% | 95% | 0% | -307.7803 | 988.0977 | -3550 | -400 | -2961.9023 | 74.05% | 60.2% | 95% | 0% | 2181 | -269
[5 empty] | 2019-07-04 | 17 | 4423.5 | 1843 | -340 | 1 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 1350.7007 | 780 | 200 | 2330.7007 | 58.27% | 95% | 0% | -389.016 | 909.9947 | -3550 | -400 | -3040.0053 | 76% | 60.2% | 95% | 0% | 2183 | -340
[5 empty] | 2019-07-04 | 18 | 4424 | 1755 | -414 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 1350.7007 | 780 | 200 | 2330.7007 | 58.27% | 95% | 0% | -473.6842 | 803.3974 | -3550 | -400 | -3146.6026 | 78.67% | 60.19% | 95% | 0% | 2169 | -414
[5 empty] | 2019-07-04 | 19 | 4424.5 | 1667 | -480 | 1 | 0 | 2147 | 1242.6216 | 1242.6216 | 1242.6216 | 1349.1344 | 780 | 200 | 2329.1344 | 58.23% | 95% | 0% | -549.1991 | 693.4225 | -3550 | -400 | -3256.5775 | 81.41% | 60.19% | 95% | 0% | 2147 | -480
[5 empty] | 2019-07-04 | 20 | 4425 | 1563 | -555 | 1 | 0 | 2118 | 1197.197 | 1197.197 | 1197.197 | 1349.1344 | 780 | 200 | 2329.1344 | 58.23% | 95% | 0% | -635.0114 | 562.1856 | -3550 | -400 | -3387.8144 | 84.7% | 60.19% | 95% | 0% | 2118 | -555
[5 empty] | 2019-07-04 | 21 | 4425.5 | 1453 | -621 | 1 | 0 | 2074 | 1128.277 | 1128.277 | 1128.277 | 1349.1344 | 780 | 200 | 2329.1344 | 58.23% | 95% | 0% | -710.5263 | 417.7507 | -3550 | -400 | -3532.2493 | 88.31% | 60.19% | 95% | 0% | 2074 | -621
[5 empty] | 2019-07-04 | 22 | 4426 | 1379 | -670 | 1 | 0 | 2049 | 1089.1179 | 1089.1179 | 1089.1179 | 1349.1344 | 780 | 200 | 2329.1344 | 58.23% | 95% | 0% | -766.5904 | 322.5275 | -3550 | -400 | -3627.4725 | 90.69% | 60.18% | 95% | 0% | 2049 | -670
[5 empty] | 2019-07-04 | 23 | 4426.5 | 1316 | -711 | 1 | 0 | 2027 | 1054.6579 | 1054.6579 | 1054.6579 | 1349.1344 | 780 | 200 | 2329.1344 | 58.23% | 95% | 0% | -813.5011 | 241.1567 | -3550 | -400 | -3708.8433 | 92.72% | 60.18% | 95% | 0% | 2027 | -711
[5 empty] | 2019-07-04 | 24 | 4427 | 1270 | -752 | 1 | 0 | 2022 | 1046.8261 | 1046.8261 | 1046.8261 | 1349.1344 | 780 | 200 | 2329.1344 | 58.23% | 95% | 0% | -860.4119 | 186.4142 | -3550 | -400 | -3763.5858 | 94.09% | 60.18% | 95% | 0% | 2022 | -752
[5 empty] | 2019-07-04 | 25 | 4427.5 | 1226 | -779 | 1 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 1349.1344 | 780 | 200 | 2329.1344 | 58.23% | 95% | 0% | -891.3043 | 128.8935 | -3550 | -400 | -3821.1065 | 95.53% | 60.18% | 95% | 0% | 2005 | -779
[5 empty] | 2019-07-04 | 26 | 4428 | 1183 | -790 | 1 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 1349.1344 | 780 | 200 | 2329.1344 | 58.23% | 95% | 0% | -903.8902 | 66.184 | -3550 | -400 | -3883.816 | 97.1% | 60.18% | 95% | 0% | 1973 | -790
[5 empty] | 2019-07-04 | 27 | 4428.5 | 1154 | -795 | 1 | 0 | 1949 | 932.4815 | 932.4815 | 932.4815 | 1349.1344 | 780 | 200 | 2329.1344 | 58.23% | 95% | 0% | -909.611 | 22.8705 | -3550 | -400 | -3927.1295 | 98.18% | 60.18% | 95% | 0% | 1949 | -795
[5 empty] | 2019-07-04 | 28 | 4429 | 1159 | -779 | 1 | 0 | 1938 | 915.2514 | 915.2514 | 915.2514 | 1349.1344 | 780 | 200 | 2329.1344 | 58.23% | 95% | 0% | -891.3043 | 23.9471 | -3550 | -400 | -3926.0529 | 98.15% | 60.17% | 95% | 0% | 1938 | -779
[5 empty] | 2019-07-04 | 29 | 4429.5 | 1199 | -755 | 1 | 0 | 1954 | 940.3133 | 940.3133 | 940.3133 | 1349.1344 | 780 | 200 | 2329.1344 | 58.23% | 95% | 0% | -863.8444 | 76.4689 | -3550 | -400 | -3873.5311 | 96.84% | 60.17% | 95% | 0% | 1954 | -755
[5 empty] | 2019-07-04 | 30 | 4430 | 1230 | -728 | 1 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 1349.1344 | 780 | 200 | 2329.1344 | 58.23% | 95% | 0% | -832.9519 | 113.6268 | -3550 | -400 | -3836.3732 | 95.91% | 60.17% | 95% | 0% | 1958 | -728
[5 empty] | 2019-07-04 | 31 | 4430.5 | 1315 | -668 | 1 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -764.3021 | 221.4358 | -3550 | -400 | -3728.5642 | 93.21% | 60.17% | 95% | 0% | 1983 | -668
[5 empty] | 2019-07-04 | 32 | 4431 | 1428 | -604 | 1 | 0 | 2032 | 1062.4897 | 1062.4897 | 1062.4897 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -691.0755 | 371.4142 | -3550 | -400 | -3578.5858 | 89.46% | 60.17% | 95% | 0% | 2032 | -604
[5 empty] | 2019-07-04 | 33 | 4431.5 | 1572 | -553 | 1 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -632.7231 | 575.4385 | -3550 | -400 | -3374.5615 | 84.36% | 60.16% | 95% | 0% | 2125 | -553
[5 empty] | 2019-07-04 | 34 | 4432 | 1715 | -492 | 1 | 0 | 2207 | 1336.6035 | 1336.6035 | 1336.6035 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -562.9291 | 773.6744 | -3550 | -400 | -3176.3256 | 79.41% | 60.16% | 95% | 0% | 2207 | -492
[5 empty] | 2019-07-04 | 35 | 4432.5 | 1846 | -421 | 1 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -481.6934 | 948.892 | -3550 | -400 | -3001.108 | 75.03% | 60.16% | 95% | 0% | 2267 | -421
[5 empty] | 2019-07-04 | 36 | 4433 | 1946 | -363 | 1 | 0 | 2309 | 1496.3726 | 1496.3726 | 1496.3726 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -415.3318 | 1081.0408 | -3550 | -400 | -2868.9592 | 71.72% | 60.16% | 95% | 0% | 2309 | -363
[5 empty] | 2019-07-04 | 37 | 4433.5 | 2021 | -310 | 1 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -354.6911 | 1176.1416 | -3550 | -400 | -2773.8584 | 69.35% | 60.15% | 95% | 0% | 2331 | -310
[5 empty] | 2019-07-04 | 38 | 4434 | 2090 | -255 | 1 | 0 | 2345 | 1552.7617 | 1552.7617 | 1552.7617 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -291.762 | 1260.9997 | -3550 | -400 | -2689.0003 | 67.23% | 60.15% | 95% | 0% | 2345 | -255
[5 empty] | 2019-07-04 | 39 | 4434.5 | 2175 | -198 | 1 | 0 | 2373 | 1596.62 | 1596.62 | 1596.62 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -226.5446 | 1370.0753 | -3550 | -400 | -2579.9247 | 64.5% | 60.15% | 95% | 0% | 2373 | -198
[5 empty] | 2019-07-04 | 40 | 4435 | 2226 | -157 | 1 | 0 | 2383 | 1612.2836 | 1612.2836 | 1612.2836 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -179.6339 | 1432.6497 | -3550 | -400 | -2517.3503 | 62.93% | 60.15% | 95% | 0% | 2383 | -157
[5 empty] | 2019-07-04 | 41 | 4435.5 | 2247 | -127 | 1 | 0 | 2374 | 1598.1863 | 1598.1863 | 1598.1863 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -145.3089 | 1452.8774 | -3550 | -400 | -2497.1226 | 62.43% | 60.15% | 95% | 0% | 2374 | -127
[5 empty] | 2019-07-04 | 42 | 4436 | 2239 | -98 | 1 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -112.1281 | 1428.1027 | -3550 | -400 | -2521.8973 | 63.05% | 60.14% | 95% | 0% | 2337 | -98
[5 empty] | 2019-07-04 | 43 | 4436.5 | 2225 | -87 | 1 | 0 | 2312 | 1501.0717 | 1501.0717 | 1501.0717 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -99.5423 | 1401.5294 | -3550 | -400 | -2548.4706 | 63.71% | 60.13% | 95% | 0% | 2312 | -87
[5 empty] | 2019-07-04 | 44 | 4437 | 2178 | -84 | 1 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -96.1098 | 1326.6437 | -3550 | -400 | -2623.3563 | 65.58% | 60.13% | 95% | 0% | 2262 | -84
[5 empty] | 2019-07-04 | 45 | 4437.5 | 2111 | -83 | 1 | 0 | 2194 | 1316.2407 | 1316.2407 | 1316.2407 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -94.9657 | 1221.2751 | -3550 | -400 | -2728.7249 | 68.22% | 60.13% | 95% | 0% | 2194 | -83
[5 empty] | 2019-07-04 | 46 | 4438 | 1990 | -82 | 0 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 1347.568 | 780 | 200 | 2327.568 | 58.19% | 95% | 0% | -93.8215 | 1031.3228 | -2750 | -200 | -1918.6772 | 47.97% | 60.13% | 95% | 0% | 2072 | -82
[5 empty] | 2019-07-04 | 47 | 4438.5 | 1856 | -81 | 0 | 0 | 1937 | 913.6851 | 913.6851 | 913.6851 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -92.6773 | 821.0077 | -2750 | -200 | -2128.9923 | 53.22% | 60.12% | 95% | 0% | 1937 | -81
[5 empty] | 2019-07-04 | 48 | 4439 | 1748 | -80 | 0 | 0 | 1828 | 742.9514 | 742.9514 | 742.9514 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -91.5332 | 651.4182 | -2750 | -200 | -2298.5818 | 57.46% | 60.12% | 95% | 0% | 1828 | -80
[5 empty] | 2019-07-05 | 1 | 4439.5 | 1655 | -78 | 0 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -89.2449 | 504.9019 | -2750 | -200 | -2445.0981 | 61.13% | 60.12% | 95% | 0% | 1733 | -78
[5 empty] | 2019-07-05 | 2 | 4440 | 1595 | -75 | 1 | 0 | 1670 | 495.4658 | 495.4658 | 495.4658 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -85.8124 | 409.6534 | -3550 | -400 | -3540.3466 | 88.51% | 60.11% | 95% | 0% | 1670 | -75
[5 empty] | 2019-07-05 | 3 | 4440.5 | 1550 | -74 | 1 | 0 | 1624 | 423.413 | 423.413 | 423.413 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -84.6682 | 338.7448 | -3550 | -400 | -3611.2552 | 90.28% | 60.11% | 95% | 0% | 1624 | -74
[5 empty] | 2019-07-05 | 4 | 4441 | 1522 | -74 | 1 | 0 | 1596 | 379.5548 | 379.5548 | 379.5548 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -84.6682 | 294.8866 | -3550 | -400 | -3655.1134 | 91.38% | 60.11% | 95% | 0% | 1596 | -74
[5 empty] | 2019-07-05 | 5 | 4441.5 | 1502 | -73 | 1 | 0 | 1575 | 346.6612 | 346.6612 | 346.6612 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -83.524 | 263.1371 | -3550 | -400 | -3686.8629 | 92.17% | 60.11% | 95% | 0% | 1575 | -73
[5 empty] | 2019-07-05 | 6 | 4442 | 1478 | -72 | 1 | 0 | 1550 | 307.5021 | 307.5021 | 307.5021 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -82.3799 | 225.1222 | -3550 | -400 | -3724.8778 | 93.12% | 60.11% | 95% | 0% | 1550 | -72
[5 empty] | 2019-07-05 | 7 | 4442.5 | 1462 | -71 | 1 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -81.2357 | 199.6382 | -3550 | -400 | -3750.3618 | 93.76% | 60.11% | 95% | 0% | 1533 | -71
[5 empty] | 2019-07-05 | 8 | 4443 | 1452 | -71 | 1 | 0 | 1523 | 265.2102 | 265.2102 | 265.2102 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -81.2357 | 183.9745 | -3550 | -400 | -3766.0255 | 94.15% | 60.1% | 95% | 0% | 1523 | -71
[5 empty] | 2019-07-05 | 9 | 4443.5 | 1457 | -69 | 1 | 0 | 1526 | 269.9093 | 269.9093 | 269.9093 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -78.9474 | 190.9619 | -3550 | -400 | -3759.0381 | 93.98% | 60.1% | 95% | 0% | 1526 | -69
[5 empty] | 2019-07-05 | 10 | 4444 | 1447 | -67 | 1 | 0 | 1514 | 251.1129 | 251.1129 | 251.1129 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -76.659 | 174.4539 | -3550 | -400 | -3775.5461 | 94.39% | 60.1% | 95% | 0% | 1514 | -67
[5 empty] | 2019-07-05 | 11 | 4444.5 | 1481 | -67 | 1 | 0 | 1548 | 304.3693 | 304.3693 | 304.3693 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -76.659 | 227.7103 | -3550 | -400 | -3722.2897 | 93.06% | 60.1% | 95% | 0% | 1548 | -67
[5 empty] | 2019-07-05 | 12 | 4445 | 1537 | -78 | 1 | 0 | 1615 | 409.3157 | 409.3157 | 409.3157 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -89.2449 | 320.0709 | -3550 | -400 | -3629.9291 | 90.75% | 60.1% | 95% | 0% | 1615 | -78
[5 empty] | 2019-07-05 | 13 | 4445.5 | 1694 | -104 | 1 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -118.9931 | 576.9673 | -3550 | -400 | -3373.0327 | 84.33% | 60.09% | 95% | 0% | 1798 | -104
[5 empty] | 2019-07-05 | 14 | 4446 | 1811 | -143 | 1 | 0 | 1954 | 940.3133 | 940.3133 | 940.3133 | 1346.0016 | 780 | 200 | 2326.0016 | 58.15% | 95% | 0% | -163.6156 | 776.6977 | -3550 | -400 | -3173.3023 | 79.33% | 60.09% | 95% | 0% | 1954 | -143
[5 empty] | 2019-07-05 | 15 | 4446.5 | 1964 | -185 | 1 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 1344.4353 | 780 | 200 | 2324.4353 | 58.11% | 95% | 0% | -211.6705 | 1034.0838 | -3550 | -400 | -2915.9162 | 72.9% | 60.09% | 95% | 0% | 2149 | -185
[5 empty] | 2019-07-05 | 16 | 4447 | 1957 | -235 | 1 | 0 | 2192 | 1313.108 | 1313.108 | 1313.108 | 1344.4353 | 780 | 200 | 2324.4353 | 58.11% | 95% | 0% | -268.8787 | 1044.2293 | -3550 | -400 | -2905.7707 | 72.64% | 60.08% | 95% | 0% | 2192 | -235
[5 empty] | 2019-07-05 | 17 | 4447.5 | 1903 | -294 | 1 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 1344.4353 | 780 | 200 | 2324.4353 | 58.11% | 95% | 0% | -336.3844 | 984.5554 | -3550 | -400 | -2965.4446 | 74.14% | 60.07% | 95% | 0% | 2197 | -294
[5 empty] | 2019-07-05 | 18 | 4448 | 1830 | -355 | 1 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 1344.4353 | 780 | 200 | 2324.4353 | 58.11% | 95% | 0% | -406.1785 | 895.965 | -3550 | -400 | -3054.035 | 76.35% | 60.07% | 95% | 0% | 2185 | -355
[5 empty] | 2019-07-05 | 19 | 4448.5 | 1774 | -411 | 1 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 1344.4353 | 780 | 200 | 2324.4353 | 58.11% | 95% | 0% | -470.2517 | 831.8917 | -3550 | -400 | -3118.1083 | 77.95% | 60.07% | 95% | 0% | 2185 | -411
[5 empty] | 2019-07-05 | 20 | 4449 | 1680 | -473 | 1 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 1344.4353 | 780 | 200 | 2324.4353 | 58.11% | 95% | 0% | -541.1899 | 710.8299 | -3550 | -400 | -3239.1701 | 80.98% | 60.07% | 95% | 0% | 2153 | -473
[5 empty] | 2019-07-05 | 21 | 4449.5 | 1603 | -520 | 1 | 0 | 2123 | 1205.0289 | 1205.0289 | 1205.0289 | 1344.4353 | 780 | 200 | 2324.4353 | 58.11% | 95% | 0% | -594.9657 | 610.0632 | -3550 | -400 | -3339.9368 | 83.5% | 60.07% | 95% | 0% | 2123 | -520
[5 empty] | 2019-07-05 | 22 | 4450 | 1551 | -575 | 1 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -657.8947 | 551.8332 | -3550 | -400 | -3398.1668 | 84.95% | 60.06% | 95% | 0% | 2126 | -575
[5 empty] | 2019-07-05 | 23 | 4450.5 | 1505 | -606 | 1 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -693.3638 | 492.8686 | -3550 | -400 | -3457.1314 | 86.43% | 60.06% | 95% | 0% | 2111 | -606
[5 empty] | 2019-07-05 | 24 | 4451 | 1494 | -613 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -701.373 | 478.594 | -3550 | -400 | -3471.406 | 86.79% | 60.06% | 95% | 0% | 2107 | -613
[5 empty] | 2019-07-05 | 25 | 4451.5 | 1464 | -633 | 1 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -724.2563 | 440.0471 | -3550 | -400 | -3509.9529 | 87.75% | 60.05% | 95% | 0% | 2097 | -633
[5 empty] | 2019-07-05 | 26 | 4452 | 1421 | -661 | 1 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -756.2929 | 384.515 | -3550 | -400 | -3565.485 | 89.14% | 60.04% | 95% | 0% | 2082 | -661
[5 empty] | 2019-07-05 | 27 | 4452.5 | 1398 | -673 | 1 | 0 | 2071 | 1123.5779 | 1123.5779 | 1123.5779 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -770.0229 | 353.555 | -3550 | -400 | -3596.445 | 89.91% | 60.04% | 95% | 0% | 2071 | -673
[5 empty] | 2019-07-05 | 28 | 4453 | 1384 | -683 | 1 | 0 | 2067 | 1117.3124 | 1117.3124 | 1117.3124 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -781.4645 | 335.8479 | -3550 | -400 | -3614.1521 | 90.35% | 60.04% | 95% | 0% | 2067 | -683
[5 empty] | 2019-07-05 | 29 | 4453.5 | 1398 | -665 | 1 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -760.8696 | 350.1774 | -3550 | -400 | -3599.8226 | 90% | 60.04% | 95% | 0% | 2063 | -665
[5 empty] | 2019-07-05 | 30 | 4454 | 1417 | -630 | 1 | 0 | 2047 | 1085.9852 | 1085.9852 | 1085.9852 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -720.8238 | 365.1614 | -3550 | -400 | -3584.8386 | 89.62% | 60.04% | 95% | 0% | 2047 | -630
[5 empty] | 2019-07-05 | 31 | 4454.5 | 1448 | -594 | 1 | 0 | 2042 | 1078.1533 | 1078.1533 | 1078.1533 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -679.6339 | 398.5195 | -3550 | -400 | -3551.4805 | 88.79% | 60.04% | 95% | 0% | 2042 | -594
[5 empty] | 2019-07-05 | 32 | 4455 | 1516 | -555 | 1 | 0 | 2071 | 1123.5779 | 1123.5779 | 1123.5779 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -635.0114 | 488.5665 | -3550 | -400 | -3461.4335 | 86.54% | 60.03% | 95% | 0% | 2071 | -555
[5 empty] | 2019-07-05 | 33 | 4455.5 | 1609 | -506 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -578.9474 | 613.5506 | -3550 | -400 | -3336.4494 | 83.41% | 60.03% | 95% | 0% | 2115 | -506
[5 empty] | 2019-07-05 | 34 | 4456 | 1706 | -460 | 1 | 0 | 2166 | 1272.3825 | 1272.3825 | 1272.3825 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -526.3158 | 746.0667 | -3550 | -400 | -3203.9333 | 80.1% | 60.03% | 95% | 0% | 2166 | -460
[5 empty] | 2019-07-05 | 35 | 4456.5 | 1812 | -406 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -464.5309 | 889.3026 | -3550 | -400 | -3060.6974 | 76.52% | 60.02% | 95% | 0% | 2218 | -406
[5 empty] | 2019-07-05 | 36 | 4457 | 1906 | -347 | 1 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -397.0252 | 1011.6311 | -3550 | -400 | -2938.3689 | 73.46% | 60.02% | 95% | 0% | 2253 | -347
[5 empty] | 2019-07-05 | 37 | 4457.5 | 1979 | -297 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -339.8169 | 1104.8657 | -3550 | -400 | -2845.1343 | 71.13% | 60% | 95% | 0% | 2276 | -297
[5 empty] | 2019-07-05 | 38 | 4458 | 2032 | -248 | 1 | 0 | 2280 | 1450.9481 | 1450.9481 | 1450.9481 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -283.7529 | 1167.1952 | -3550 | -400 | -2782.8048 | 69.57% | 60% | 95% | 0% | 2280 | -248
[5 empty] | 2019-07-05 | 39 | 4458.5 | 2068 | -207 | 1 | 0 | 2275 | 1443.1162 | 1443.1162 | 1443.1162 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -236.8421 | 1206.2741 | -3550 | -400 | -2743.7259 | 68.59% | 59.99% | 95% | 0% | 2275 | -207
[5 empty] | 2019-07-05 | 40 | 4459 | 2105 | -173 | 1 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 1342.8689 | 780 | 200 | 2322.8689 | 58.07% | 95% | 0% | -197.9405 | 1249.8748 | -3550 | -400 | -2700.1252 | 67.5% | 59.99% | 95% | 0% | 2278 | -173
[5 empty] | 2019-07-05 | 41 | 4459.5 | 2081 | -141 | 1 | 0 | 2222 | 1360.0989 | 1360.0989 | 1360.0989 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -161.3272 | 1198.7717 | -3550 | -400 | -2751.2283 | 68.78% | 59.99% | 95% | 0% | 2222 | -141
[5 empty] | 2019-07-05 | 42 | 4460 | 2073 | -113 | 1 | 0 | 2186 | 1303.7098 | 1303.7098 | 1303.7098 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -129.2906 | 1174.4192 | -3550 | -400 | -2775.5808 | 69.39% | 59.98% | 95% | 0% | 2186 | -113
[5 empty] | 2019-07-05 | 43 | 4460.5 | 2050 | -101 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -115.5606 | 1133.3264 | -3550 | -400 | -2816.6736 | 70.42% | 59.97% | 95% | 0% | 2151 | -101
[5 empty] | 2019-07-05 | 44 | 4461 | 2015 | -100 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -114.4165 | 1078.0815 | -3550 | -400 | -2871.9185 | 71.8% | 59.97% | 95% | 0% | 2115 | -100
[5 empty] | 2019-07-05 | 45 | 4461.5 | 1998 | -99 | 1 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -113.2723 | 1051.0311 | -3550 | -400 | -2898.9689 | 72.47% | 59.97% | 95% | 0% | 2097 | -99
[5 empty] | 2019-07-05 | 46 | 4462 | 1913 | -98 | 0 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -112.1281 | 917.4679 | -2750 | -200 | -2032.5321 | 50.81% | 59.97% | 95% | 0% | 2011 | -98
[5 empty] | 2019-07-05 | 47 | 4462.5 | 1797 | -97 | 0 | 0 | 1894 | 846.3314 | 846.3314 | 846.3314 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -110.984 | 735.3474 | -2750 | -200 | -2214.6526 | 55.37% | 59.96% | 95% | 0% | 1894 | -97
[5 empty] | 2019-07-05 | 48 | 4463 | 1686 | -96 | 0 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -109.8398 | 561.0588 | -2750 | -200 | -2388.9412 | 59.72% | 59.96% | 95% | 0% | 1782 | -96
[5 empty] | 2019-07-06 | 1 | 4463.5 | 1591 | -93 | 0 | 0 | 1684 | 517.3949 | 517.3949 | 517.3949 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -106.4073 | 410.9876 | -2750 | -200 | -2539.0124 | 63.48% | 59.96% | 95% | 0% | 1684 | -93
[5 empty] | 2019-07-06 | 2 | 4464 | 1534 | -90 | 0 | 0 | 1624 | 423.413 | 423.413 | 423.413 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -102.9748 | 320.4382 | -2750 | -200 | -2629.5618 | 65.74% | 59.95% | 95% | 0% | 1624 | -90
[5 empty] | 2019-07-06 | 3 | 4464.5 | 1486 | -90 | 0 | 0 | 1576 | 348.2275 | 348.2275 | 348.2275 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -102.9748 | 245.2527 | -2750 | -200 | -2704.7473 | 67.62% | 59.95% | 95% | 0% | 1576 | -90
[5 empty] | 2019-07-06 | 4 | 4465 | 1453 | -91 | 0 | 0 | 1544 | 298.1039 | 298.1039 | 298.1039 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -104.119 | 193.9849 | -2750 | -200 | -2756.0151 | 68.9% | 59.95% | 95% | 0% | 1544 | -91
[5 empty] | 2019-07-06 | 5 | 4465.5 | 1414 | -91 | 0 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -104.119 | 132.8967 | -2750 | -200 | -2817.1033 | 70.43% | 59.95% | 95% | 0% | 1505 | -91
[5 empty] | 2019-07-06 | 6 | 4466 | 1380 | -92 | 0 | 0 | 1472 | 185.3256 | 185.3256 | 185.3256 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -105.2632 | 80.0625 | -2750 | -200 | -2869.9375 | 71.75% | 59.94% | 95% | 0% | 1472 | -92
[5 empty] | 2019-07-06 | 7 | 4466.5 | 1362 | -91 | 0 | 0 | 1453 | 155.5647 | 155.5647 | 155.5647 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -104.119 | 51.4457 | -2750 | -200 | -2898.5543 | 72.46% | 59.94% | 95% | 0% | 1453 | -91
[5 empty] | 2019-07-06 | 8 | 4467 | 1351 | -91 | 0 | 0 | 1442 | 138.3347 | 138.3347 | 138.3347 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -104.119 | 34.2157 | -2750 | -200 | -2915.7843 | 72.89% | 59.94% | 95% | 0% | 1442 | -91
[5 empty] | 2019-07-06 | 9 | 4467.5 | 1340 | -89 | 0 | 0 | 1429 | 117.972 | 117.972 | 117.972 | 1341.3026 | 780 | 200 | 2321.3026 | 58.03% | 95% | 0% | -101.8307 | 16.1413 | -2750 | -200 | -2933.8587 | 73.35% | 59.94% | 95% | 0% | 1429 | -89
[5 empty] | 2019-07-06 | 10 | 4468 | 1330 | -87 | 0 | 0 | 1417 | 99.1756 | 99.1756 | 99.1756 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -99.5423 | -0.36674 | -2750 | -200 | -2950.3667 | 73.76% | 59.94% | 95% | 0% | 1417 | -87
[5 empty] | 2019-07-06 | 11 | 4468.5 | 1344 | -89 | 0 | 0 | 1433 | 124.2374 | 124.2374 | 124.2374 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -101.8307 | 22.4068 | -2750 | -200 | -2927.5932 | 73.19% | 59.94% | 95% | 0% | 1433 | -89
[5 empty] | 2019-07-06 | 12 | 4469 | 1353 | -105 | 0 | 0 | 1458 | 163.3965 | 163.3965 | 163.3965 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -120.1373 | 43.2592 | -2750 | -200 | -2906.7408 | 72.67% | 59.93% | 95% | 0% | 1458 | -105
[5 empty] | 2019-07-06 | 13 | 4469.5 | 1417 | -130 | 1 | 0 | 1547 | 302.803 | 302.803 | 302.803 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -148.7414 | 154.0615 | -3550 | -400 | -3795.9385 | 94.9% | 59.92% | 95% | 0% | 1547 | -130
[5 empty] | 2019-07-06 | 14 | 4470 | 1451 | -161 | 1 | 0 | 1612 | 404.6167 | 404.6167 | 404.6167 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -184.2105 | 220.4061 | -3550 | -400 | -3729.5939 | 93.24% | 59.92% | 95% | 0% | 1612 | -161
[5 empty] | 2019-07-06 | 15 | 4470.5 | 1515 | -194 | 1 | 0 | 1709 | 556.554 | 556.554 | 556.554 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -221.968 | 334.586 | -3550 | -400 | -3615.414 | 90.39% | 59.91% | 95% | 0% | 1709 | -194
[5 empty] | 2019-07-06 | 16 | 4471 | 1562 | -228 | 1 | 0 | 1790 | 683.4295 | 683.4295 | 683.4295 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -260.8696 | 422.5599 | -3550 | -400 | -3527.4401 | 88.19% | 59.9% | 95% | 0% | 1790 | -228
[5 empty] | 2019-07-06 | 17 | 4471.5 | 1622 | -262 | 1 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -299.7712 | 530.8966 | -3550 | -400 | -3419.1034 | 85.48% | 59.9% | 95% | 0% | 1884 | -262
[5 empty] | 2019-07-06 | 18 | 4472 | 1634 | -300 | 1 | 0 | 1934 | 908.986 | 908.986 | 908.986 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -343.2494 | 565.7366 | -3550 | -400 | -3384.2634 | 84.61% | 59.9% | 95% | 0% | 1934 | -300
[5 empty] | 2019-07-06 | 19 | 4472.5 | 1650 | -330 | 1 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -377.5744 | 603.4644 | -3550 | -400 | -3346.5356 | 83.66% | 59.9% | 95% | 0% | 1980 | -330
[5 empty] | 2019-07-06 | 20 | 4473 | 1650 | -359 | 1 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -410.7551 | 615.7082 | -3550 | -400 | -3334.2918 | 83.36% | 59.89% | 95% | 0% | 2009 | -359
[5 empty] | 2019-07-06 | 21 | 4473.5 | 1618 | -381 | 1 | 0 | 1999 | 1010.7997 | 1010.7997 | 1010.7997 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -435.9268 | 574.8729 | -3550 | -400 | -3375.1271 | 84.38% | 59.89% | 95% | 0% | 1999 | -381
[5 empty] | 2019-07-06 | 22 | 4474 | 1603 | -394 | 1 | 0 | 1997 | 1007.6669 | 1007.6669 | 1007.6669 | 1339.7362 | 780 | 200 | 2319.7362 | 57.99% | 95% | 0% | -450.8009 | 556.866 | -3550 | -400 | -3393.134 | 84.83% | 59.89% | 95% | 0% | 1997 | -394
[5 empty] | 2019-07-06 | 23 | 4474.5 | 1596 | -398 | 1 | 0 | 1994 | 1002.9678 | 1002.9678 | 1002.9678 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -455.3776 | 547.5903 | -3550 | -400 | -3402.4097 | 85.06% | 59.88% | 95% | 0% | 1994 | -398
[5 empty] | 2019-07-06 | 24 | 4475 | 1598 | -407 | 1 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -465.6751 | 554.5228 | -3550 | -400 | -3395.4772 | 84.89% | 59.88% | 95% | 0% | 2005 | -407
[5 empty] | 2019-07-06 | 25 | 4475.5 | 1559 | -436 | 1 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -498.8558 | 505.6784 | -3550 | -400 | -3444.3216 | 86.11% | 59.87% | 95% | 0% | 1995 | -436
[5 empty] | 2019-07-06 | 26 | 4476 | 1530 | -449 | 1 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -513.73 | 465.7424 | -3550 | -400 | -3484.2576 | 87.11% | 59.87% | 95% | 0% | 1979 | -449
[5 empty] | 2019-07-06 | 27 | 4476.5 | 1523 | -437 | 1 | 0 | 1960 | 949.7115 | 949.7115 | 949.7115 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -500 | 449.7115 | -3550 | -400 | -3500.2885 | 87.51% | 59.87% | 95% | 0% | 1960 | -437
[5 empty] | 2019-07-06 | 28 | 4477 | 1503 | -429 | 1 | 0 | 1932 | 905.8533 | 905.8533 | 905.8533 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -490.8467 | 415.0066 | -3550 | -400 | -3534.9934 | 88.37% | 59.86% | 95% | 0% | 1932 | -429
[5 empty] | 2019-07-06 | 29 | 4477.5 | 1495 | -419 | 1 | 0 | 1914 | 877.6587 | 877.6587 | 877.6587 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -479.405 | 398.2537 | -3550 | -400 | -3551.7463 | 88.79% | 59.86% | 95% | 0% | 1914 | -419
[5 empty] | 2019-07-06 | 30 | 4478 | 1500 | -393 | 1 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -449.6568 | 395.1083 | -3550 | -400 | -3554.8917 | 88.87% | 59.86% | 95% | 0% | 1893 | -393
[5 empty] | 2019-07-06 | 31 | 4478.5 | 1511 | -368 | 1 | 0 | 1879 | 822.8359 | 822.8359 | 822.8359 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -421.0526 | 401.7833 | -3550 | -400 | -3548.2167 | 88.71% | 59.85% | 95% | 0% | 1879 | -368
[5 empty] | 2019-07-06 | 32 | 4479 | 1518 | -371 | 1 | 0 | 1889 | 838.4996 | 838.4996 | 838.4996 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -424.4851 | 414.0145 | -3550 | -400 | -3535.9855 | 88.4% | 59.85% | 95% | 0% | 1889 | -371
[5 empty] | 2019-07-06 | 33 | 4479.5 | 1560 | -363 | 1 | 0 | 1923 | 891.756 | 891.756 | 891.756 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -415.3318 | 476.4242 | -3550 | -400 | -3473.5758 | 86.84% | 59.85% | 95% | 0% | 1923 | -363
[5 empty] | 2019-07-06 | 34 | 4480 | 1671 | -318 | 1 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -363.8444 | 631.2916 | -3550 | -400 | -3318.7084 | 82.97% | 59.85% | 95% | 0% | 1989 | -318
[5 empty] | 2019-07-06 | 35 | 4480.5 | 1788 | -271 | 1 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -310.0686 | 794.7129 | -3550 | -400 | -3155.2871 | 78.88% | 59.85% | 95% | 0% | 2059 | -271
[5 empty] | 2019-07-06 | 36 | 4481 | 1851 | -239 | 1 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -273.4554 | 879.8835 | -3550 | -400 | -3070.1165 | 76.75% | 59.84% | 95% | 0% | 2090 | -239
[5 empty] | 2019-07-06 | 37 | 4481.5 | 1892 | -192 | 1 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -219.6796 | 924.261 | -3550 | -400 | -3025.739 | 75.64% | 59.84% | 95% | 0% | 2084 | -192
[5 empty] | 2019-07-06 | 38 | 4482 | 1947 | -152 | 1 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 1338.1698 | 780 | 200 | 2318.1698 | 57.95% | 95% | 0% | -173.913 | 993.5231 | -3550 | -400 | -2956.4769 | 73.91% | 59.83% | 95% | 0% | 2099 | -152
[5 empty] | 2019-07-06 | 39 | 4482.5 | 1979 | -125 | 1 | 0 | 2104 | 1175.2679 | 1175.2679 | 1175.2679 | 1336.6035 | 780 | 200 | 2316.6035 | 57.92% | 95% | 0% | -143.0206 | 1032.2473 | -3550 | -400 | -2917.7527 | 72.94% | 59.83% | 95% | 0% | 2104 | -125
[5 empty] | 2019-07-06 | 40 | 4483 | 1990 | -101 | 1 | 0 | 2091 | 1154.9052 | 1154.9052 | 1154.9052 | 1336.6035 | 780 | 200 | 2316.6035 | 57.92% | 95% | 0% | -115.5606 | 1039.3446 | -3550 | -400 | -2910.6554 | 72.77% | 59.83% | 95% | 0% | 2091 | -101
[5 empty] | 2019-07-06 | 41 | 4483.5 | 2008 | -73 | 1 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 1336.6035 | 780 | 200 | 2316.6035 | 57.92% | 95% | 0% | -83.524 | 1055.7175 | -3550 | -400 | -2894.2825 | 72.36% | 59.83% | 95% | 0% | 2081 | -73
[5 empty] | 2019-07-06 | 42 | 4484 | 2013 | -56 | 1 | 0 | 2069 | 1120.4452 | 1120.4452 | 1120.4452 | 1336.6035 | 780 | 200 | 2316.6035 | 57.92% | 95% | 0% | -64.0732 | 1056.372 | -3550 | -400 | -2893.628 | 72.34% | 59.82% | 95% | 0% | 2069 | -56
[5 empty] | 2019-07-06 | 43 | 4484.5 | 1982 | -48 | 1 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 1336.6035 | 780 | 200 | 2316.6035 | 57.92% | 95% | 0% | -54.9199 | 1004.4371 | -3550 | -400 | -2945.5629 | 73.64% | 59.82% | 95% | 0% | 2030 | -48
[5 empty] | 2019-07-06 | 44 | 4485 | 1968 | -46 | 1 | 0 | 2014 | 1034.2951 | 1034.2951 | 1034.2951 | 1336.6035 | 780 | 200 | 2316.6035 | 57.92% | 95% | 0% | -52.6316 | 981.6636 | -3550 | -400 | -2968.3364 | 74.21% | 59.82% | 95% | 0% | 2014 | -46
[5 empty] | 2019-07-06 | 45 | 4485.5 | 1959 | -45 | 1 | 0 | 2004 | 1018.6315 | 1018.6315 | 1018.6315 | 1336.6035 | 780 | 200 | 2316.6035 | 57.92% | 95% | 0% | -51.4874 | 967.1441 | -3550 | -400 | -2982.8559 | 74.57% | 59.81% | 95% | 0% | 2004 | -45
[5 empty] | 2019-07-06 | 46 | 4486 | 1913 | -44 | 0 | 0 | 1957 | 945.0124 | 945.0124 | 945.0124 | 1336.6035 | 780 | 200 | 2316.6035 | 57.92% | 95% | 0% | -50.3432 | 894.6691 | -2750 | -200 | -2055.3309 | 51.38% | 59.81% | 95% | 0% | 1957 | -44
[5 empty] | 2019-07-06 | 47 | 4486.5 | 1810 | -44 | 0 | 0 | 1854 | 783.6768 | 783.6768 | 783.6768 | 1336.6035 | 780 | 200 | 2316.6035 | 57.92% | 95% | 0% | -50.3432 | 733.3336 | -2750 | -200 | -2216.6664 | 55.42% | 59.81% | 95% | 0% | 1854 | -44
[5 empty] | 2019-07-06 | 48 | 4487 | 1725 | -43 | 0 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 1336.6035 | 780 | 200 | 2316.6035 | 57.92% | 95% | 0% | -49.1991 | 599.7704 | -2750 | -200 | -2350.2296 | 58.76% | 59.81% | 95% | 0% | 1768 | -43
[5 empty] | 2019-07-07 | 1 | 4487.5 | 1644 | -42 | 0 | 0 | 1686 | 520.5276 | 520.5276 | 520.5276 | 1336.6035 | 780 | 200 | 2316.6035 | 57.92% | 95% | 0% | -48.0549 | 472.4727 | -2750 | -200 | -2477.5273 | 61.94% | 59.81% | 95% | 0% | 1686 | -42
[5 empty] | 2019-07-07 | 2 | 4488 | 1588 | -41 | 0 | 0 | 1629 | 431.2448 | 431.2448 | 431.2448 | 1336.6035 | 780 | 200 | 2316.6035 | 57.92% | 95% | 0% | -46.9108 | 384.3341 | -2750 | -200 | -2565.6659 | 64.14% | 59.81% | 95% | 0% | 1629 | -41
[5 empty] | 2019-07-07 | 3 | 4488.5 | 1537 | -41 | 0 | 0 | 1578 | 351.3603 | 351.3603 | 351.3603 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -46.9108 | 304.4495 | -2750 | -200 | -2645.5505 | 66.14% | 59.81% | 95% | 0% | 1578 | -41
[5 empty] | 2019-07-07 | 4 | 4489 | 1512 | -40 | 0 | 0 | 1552 | 310.6348 | 310.6348 | 310.6348 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -45.7666 | 264.8682 | -2750 | -200 | -2685.1318 | 67.13% | 59.81% | 95% | 0% | 1552 | -40
[5 empty] | 2019-07-07 | 5 | 4489.5 | 1482 | -40 | 0 | 0 | 1522 | 263.6439 | 263.6439 | 263.6439 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -45.7666 | 217.8773 | -2750 | -200 | -2732.1227 | 68.3% | 59.8% | 95% | 0% | 1522 | -40
[5 empty] | 2019-07-07 | 6 | 4490 | 1463 | -40 | 1 | 0 | 1503 | 233.8829 | 233.8829 | 233.8829 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -45.7666 | 188.1163 | -3550 | -400 | -3761.8837 | 94.05% | 59.79% | 95% | 0% | 1503 | -40
[5 empty] | 2019-07-07 | 7 | 4490.5 | 1439 | -40 | 1 | 0 | 1479 | 196.2902 | 196.2902 | 196.2902 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -45.7666 | 150.5236 | -3550 | -400 | -3799.4764 | 94.99% | 59.79% | 95% | 0% | 1479 | -40
[5 empty] | 2019-07-07 | 8 | 4491 | 1426 | -40 | 1 | 0 | 1466 | 175.9275 | 175.9275 | 175.9275 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -45.7666 | 130.1609 | -3550 | -400 | -3819.8391 | 95.5% | 59.79% | 95% | 0% | 1466 | -40
[5 empty] | 2019-07-07 | 9 | 4491.5 | 1421 | -41 | 1 | 0 | 1462 | 169.662 | 169.662 | 169.662 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -46.9108 | 122.7512 | -3550 | -400 | -3827.2488 | 95.68% | 59.79% | 95% | 0% | 1462 | -41
[5 empty] | 2019-07-07 | 10 | 4492 | 1383 | -42 | 1 | 0 | 1425 | 111.7065 | 111.7065 | 111.7065 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -48.0549 | 63.6516 | -3550 | -400 | -3886.3484 | 97.16% | 59.79% | 95% | 0% | 1425 | -42
[5 empty] | 2019-07-07 | 11 | 4492.5 | 1368 | -45 | 1 | 0 | 1413 | 92.9101 | 92.9101 | 92.9101 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -51.4874 | 41.4227 | -3550 | -400 | -3908.5773 | 97.71% | 59.79% | 95% | 0% | 1413 | -45
[5 empty] | 2019-07-07 | 12 | 4493 | 1365 | -55 | 1 | 0 | 1420 | 103.8747 | 103.8747 | 103.8747 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -62.9291 | 40.9456 | -3550 | -400 | -3909.0544 | 97.73% | 59.79% | 95% | 0% | 1420 | -55
[5 empty] | 2019-07-07 | 13 | 4493.5 | 1382 | -76 | 1 | 0 | 1458 | 163.3965 | 163.3965 | 163.3965 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -86.9565 | 76.44 | -3550 | -400 | -3873.56 | 96.84% | 59.78% | 95% | 0% | 1458 | -76
[5 empty] | 2019-07-07 | 14 | 4494 | 1391 | -101 | 1 | 0 | 1492 | 216.6529 | 216.6529 | 216.6529 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -115.5606 | 101.0923 | -3550 | -400 | -3848.9077 | 96.22% | 59.77% | 95% | 0% | 1492 | -101
[5 empty] | 2019-07-07 | 15 | 4494.5 | 1422 | -129 | 1 | 0 | 1551 | 309.0684 | 309.0684 | 309.0684 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -147.5973 | 161.4712 | -3550 | -400 | -3788.5288 | 94.71% | 59.77% | 95% | 0% | 1551 | -129
[5 empty] | 2019-07-07 | 16 | 4495 | 1442 | -161 | 1 | 0 | 1603 | 390.5194 | 390.5194 | 390.5194 | 1335.0371 | 780 | 200 | 2315.0371 | 57.88% | 95% | 0% | -184.2105 | 206.3088 | -3550 | -400 | -3743.6912 | 93.59% | 59.77% | 95% | 0% | 1603 | -161
[5 empty] | 2019-07-07 | 17 | 4495.5 | 1479 | -206 | 1 | 0 | 1685 | 518.9613 | 518.9613 | 518.9613 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -235.6979 | 283.2633 | -3550 | -400 | -3666.7367 | 91.67% | 59.77% | 95% | 0% | 1685 | -206
[5 empty] | 2019-07-07 | 18 | 4496 | 1486 | -256 | 1 | 0 | 1742 | 608.244 | 608.244 | 608.244 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -292.9062 | 315.3378 | -3550 | -400 | -3634.6622 | 90.87% | 59.76% | 95% | 0% | 1742 | -256
[5 empty] | 2019-07-07 | 19 | 4496.5 | 1473 | -320 | 1 | 0 | 1793 | 688.1286 | 688.1286 | 688.1286 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -366.1327 | 321.9959 | -3550 | -400 | -3628.0041 | 90.7% | 59.76% | 95% | 0% | 1793 | -320
[5 empty] | 2019-07-07 | 20 | 4497 | 1425 | -390 | 1 | 0 | 1815 | 722.5886 | 722.5886 | 722.5886 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -446.2243 | 276.3644 | -3550 | -400 | -3673.6356 | 91.84% | 59.75% | 95% | 0% | 1815 | -390
[5 empty] | 2019-07-07 | 21 | 4497.5 | 1384 | -442 | 1 | 0 | 1826 | 739.8186 | 739.8186 | 739.8186 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -505.7208 | 234.0978 | -3550 | -400 | -3715.9022 | 92.9% | 59.75% | 95% | 0% | 1826 | -442
[5 empty] | 2019-07-07 | 22 | 4498 | 1341 | -482 | 1 | 0 | 1823 | 735.1195 | 735.1195 | 735.1195 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -551.4874 | 183.6321 | -3550 | -400 | -3766.3679 | 94.16% | 59.74% | 95% | 0% | 1823 | -482
[5 empty] | 2019-07-07 | 23 | 4498.5 | 1332 | -503 | 1 | 0 | 1835 | 753.9159 | 753.9159 | 753.9159 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -575.5149 | 178.401 | -3550 | -400 | -3771.599 | 94.29% | 59.74% | 95% | 0% | 1835 | -503
[5 empty] | 2019-07-07 | 24 | 4499 | 1300 | -533 | 1 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -609.8398 | 140.9434 | -3550 | -400 | -3809.0566 | 95.23% | 59.74% | 95% | 0% | 1833 | -533
[5 empty] | 2019-07-07 | 25 | 4499.5 | 1291 | -545 | 1 | 0 | 1836 | 755.4823 | 755.4823 | 755.4823 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -623.5698 | 131.9125 | -3550 | -400 | -3818.0875 | 95.45% | 59.74% | 95% | 0% | 1836 | -545
[5 empty] | 2019-07-07 | 26 | 4500 | 1258 | -559 | 1 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -639.5881 | 86.1333 | -3550 | -400 | -3863.8667 | 96.6% | 59.73% | 95% | 0% | 1817 | -559
[5 empty] | 2019-07-07 | 27 | 4500.5 | 1212 | -570 | 1 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -652.1739 | 18.7247 | -3550 | -400 | -3931.2753 | 98.28% | 59.73% | 95% | 0% | 1782 | -570
[5 empty] | 2019-07-07 | 28 | 4501 | 1199 | -550 | 1 | 0 | 1749 | 619.2086 | 619.2086 | 619.2086 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -629.2906 | -10.082 | -3550 | -400 | -3960.082 | 99% | 59.73% | 95% | 0% | 1749 | -550
[5 empty] | 2019-07-07 | 29 | 4501.5 | 1151 | -573 | 1 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -655.6064 | -75.5569 | -3550 | -400 | -4025.5569 | 100.6% | 59.73% | 95% | 0% | 1724 | -573
[5 empty] | 2019-07-07 | 30 | 4502 | 1163 | -545 | 1 | 0 | 1708 | 554.9876 | 554.9876 | 554.9876 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -623.5698 | -68.5822 | -3550 | -400 | -4018.5822 | 100.5% | 59.73% | 95% | 0% | 1708 | -545
[5 empty] | 2019-07-07 | 31 | 4502.5 | 1209 | -515 | 1 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -589.2449 | -9.1954 | -3550 | -400 | -3959.1954 | 98.98% | 59.72% | 95% | 0% | 1724 | -515
[5 empty] | 2019-07-07 | 32 | 4503 | 1293 | -472 | 1 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -540.0458 | 104.2246 | -3550 | -400 | -3845.7754 | 96.14% | 59.72% | 95% | 0% | 1765 | -472
[5 empty] | 2019-07-07 | 33 | 4503.5 | 1373 | -454 | 1 | 0 | 1827 | 741.385 | 741.385 | 741.385 | 1333.4707 | 780 | 200 | 2313.4707 | 57.84% | 95% | 0% | -519.4508 | 221.9342 | -3550 | -400 | -3728.0658 | 93.2% | 59.71% | 95% | 0% | 1827 | -454
[5 empty] | 2019-07-07 | 34 | 4504 | 1532 | -379 | 1 | 0 | 1911 | 872.9596 | 872.9596 | 872.9596 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -433.6384 | 439.3212 | -3550 | -400 | -3510.6788 | 87.77% | 59.71% | 95% | 0% | 1911 | -379
[5 empty] | 2019-07-07 | 35 | 4504.5 | 1661 | -332 | 1 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -379.8627 | 621.5388 | -3550 | -400 | -3328.4612 | 83.21% | 59.71% | 95% | 0% | 1993 | -332
[5 empty] | 2019-07-07 | 36 | 4505 | 1762 | -285 | 1 | 0 | 2047 | 1085.9852 | 1085.9852 | 1085.9852 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -326.087 | 759.8982 | -3550 | -400 | -3190.1018 | 79.75% | 59.7% | 95% | 0% | 2047 | -285
[5 empty] | 2019-07-07 | 37 | 4505.5 | 1844 | -236 | 1 | 0 | 2080 | 1137.6752 | 1137.6752 | 1137.6752 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -270.0229 | 867.6523 | -3550 | -400 | -3082.3477 | 77.06% | 59.7% | 95% | 0% | 2080 | -236
[5 empty] | 2019-07-07 | 38 | 4506 | 1909 | -192 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -219.6796 | 950.8892 | -3550 | -400 | -2999.1108 | 74.98% | 59.7% | 95% | 0% | 2101 | -192
[5 empty] | 2019-07-07 | 39 | 4506.5 | 1987 | -149 | 1 | 0 | 2136 | 1225.3916 | 1225.3916 | 1225.3916 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -170.4805 | 1054.911 | -3550 | -400 | -2895.089 | 72.38% | 59.69% | 95% | 0% | 2136 | -149
[5 empty] | 2019-07-07 | 40 | 4507 | 2029 | -113 | 1 | 0 | 2142 | 1234.7898 | 1234.7898 | 1234.7898 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -129.2906 | 1105.4992 | -3550 | -400 | -2844.5008 | 71.11% | 59.69% | 95% | 0% | 2142 | -113
[5 empty] | 2019-07-07 | 41 | 4507.5 | 2063 | -81 | 1 | 0 | 2144 | 1237.9225 | 1237.9225 | 1237.9225 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -92.6773 | 1145.2452 | -3550 | -400 | -2804.7548 | 70.12% | 59.69% | 95% | 0% | 2144 | -81
[5 empty] | 2019-07-07 | 42 | 4508 | 2065 | -55 | 1 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -62.9291 | 1137.4007 | -3550 | -400 | -2812.5993 | 70.31% | 59.69% | 95% | 0% | 2120 | -55
[5 empty] | 2019-07-07 | 43 | 4508.5 | 2056 | -40 | 1 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -45.7666 | 1116.9704 | -3550 | -400 | -2833.0296 | 70.83% | 59.68% | 95% | 0% | 2096 | -40
[5 empty] | 2019-07-07 | 44 | 4509 | 2031 | -37 | 1 | 0 | 2068 | 1118.8788 | 1118.8788 | 1118.8788 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -42.3341 | 1076.5447 | -3550 | -400 | -2873.4553 | 71.84% | 59.68% | 95% | 0% | 2068 | -37
[5 empty] | 2019-07-07 | 45 | 4509.5 | 2016 | -37 | 0 | 0 | 2053 | 1095.3833 | 1095.3833 | 1095.3833 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -42.3341 | 1053.0493 | -2750 | -200 | -1896.9507 | 47.42% | 59.68% | 95% | 0% | 2053 | -37
[5 empty] | 2019-07-07 | 46 | 4510 | 1926 | -37 | 0 | 0 | 1963 | 954.4106 | 954.4106 | 954.4106 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -42.3341 | 912.0765 | -2750 | -200 | -2037.9235 | 50.95% | 59.68% | 95% | 0% | 1963 | -37
[5 empty] | 2019-07-07 | 47 | 4510.5 | 1794 | -37 | 0 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 1331.9044 | 780 | 200 | 2311.9044 | 57.8% | 95% | 0% | -42.3341 | 705.3164 | -2750 | -200 | -2244.6836 | 56.12% | 59.67% | 95% | 0% | 1831 | -37
[5 empty] | 2019-07-07 | 48 | 4511 | 1692 | -38 | 0 | 0 | 1730 | 589.4477 | 589.4477 | 589.4477 | 1330.338 | 780 | 200 | 2310.338 | 57.76% | 95% | 0% | -43.4783 | 545.9694 | -2750 | -200 | -2404.0306 | 60.1% | 59.67% | 95% | 0% | 1730 | -38
[5 empty] | 2019-07-08 | 1 | 4511.5 | 1610 | -38 | 0 | 0 | 1648 | 461.0058 | 461.0058 | 461.0058 | 1330.338 | 780 | 200 | 2310.338 | 57.76% | 95% | 0% | -43.4783 | 417.5275 | -2750 | -200 | -2532.4725 | 63.31% | 59.67% | 95% | 0% | 1648 | -38
[5 empty] | 2019-07-08 | 2 | 4512 | 1556 | -38 | 0 | 0 | 1594 | 376.4221 | 376.4221 | 376.4221 | 1330.338 | 780 | 200 | 2310.338 | 57.76% | 95% | 0% | -43.4783 | 332.9438 | -2750 | -200 | -2617.0562 | 65.43% | 59.67% | 95% | 0% | 1594 | -38
[5 empty] | 2019-07-08 | 3 | 4512.5 | 1529 | -38 | 0 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 1330.338 | 780 | 200 | 2310.338 | 57.76% | 95% | 0% | -43.4783 | 290.652 | -2750 | -200 | -2659.348 | 66.48% | 59.67% | 95% | 0% | 1567 | -38
[5 empty] | 2019-07-08 | 4 | 4513 | 1508 | -39 | 0 | 0 | 1547 | 302.803 | 302.803 | 302.803 | 1330.338 | 780 | 200 | 2310.338 | 57.76% | 95% | 0% | -44.6224 | 258.1805 | -2750 | -200 | -2691.8195 | 67.3% | 59.66% | 95% | 0% | 1547 | -39
[5 empty] | 2019-07-08 | 5 | 4513.5 | 1487 | -39 | 0 | 0 | 1526 | 269.9093 | 269.9093 | 269.9093 | 1330.338 | 780 | 200 | 2310.338 | 57.76% | 95% | 0% | -44.6224 | 225.2869 | -2750 | -200 | -2724.7131 | 68.12% | 59.66% | 95% | 0% | 1526 | -39
[5 empty] | 2019-07-08 | 6 | 4514 | 1468 | -39 | 0 | 0 | 1507 | 240.1484 | 240.1484 | 240.1484 | 1330.338 | 780 | 200 | 2310.338 | 57.76% | 95% | 0% | -44.6224 | 195.526 | -2750 | -200 | -2754.474 | 68.86% | 59.65% | 95% | 0% | 1507 | -39
[5 empty] | 2019-07-08 | 7 | 4514.5 | 1456 | -38 | 0 | 0 | 1494 | 219.7857 | 219.7857 | 219.7857 | 1330.338 | 780 | 200 | 2310.338 | 57.76% | 95% | 0% | -43.4783 | 176.3074 | -2750 | -200 | -2773.6926 | 69.34% | 59.65% | 95% | 0% | 1494 | -38
[5 empty] | 2019-07-08 | 8 | 4515 | 1455 | -38 | 0 | 0 | 1493 | 218.2193 | 218.2193 | 218.2193 | 1330.338 | 780 | 200 | 2310.338 | 57.76% | 95% | 0% | -43.4783 | 174.741 | -2750 | -200 | -2775.259 | 69.38% | 59.65% | 95% | 0% | 1493 | -38
[5 empty] | 2019-07-08 | 9 | 4515.5 | 1454 | -38 | 0 | 0 | 1492 | 216.6529 | 216.6529 | 216.6529 | 1330.338 | 780 | 200 | 2310.338 | 57.76% | 95% | 0% | -43.4783 | 173.1747 | -2750 | -200 | -2776.8253 | 69.42% | 59.65% | 95% | 0% | 1492 | -38
[5 empty] | 2019-07-08 | 10 | 4516 | 1448 | -38 | 1 | 0 | 1486 | 207.2547 | 207.2547 | 207.2547 | 1328.7716 | 780 | 200 | 2308.7716 | 57.72% | 95% | 0% | -43.4783 | 163.7765 | -3550 | -400 | -3786.2235 | 94.66% | 59.65% | 95% | 0% | 1486 | -38
[5 empty] | 2019-07-08 | 11 | 4516.5 | 1484 | -39 | 1 | 0 | 1523 | 265.2102 | 265.2102 | 265.2102 | 1328.7716 | 780 | 200 | 2308.7716 | 57.72% | 95% | 0% | -44.6224 | 220.5878 | -3550 | -400 | -3729.4122 | 93.24% | 59.64% | 95% | 0% | 1523 | -39
[5 empty] | 2019-07-08 | 12 | 4517 | 1555 | -50 | 1 | 0 | 1605 | 393.6521 | 393.6521 | 393.6521 | 1328.7716 | 780 | 200 | 2308.7716 | 57.72% | 95% | 0% | -57.2082 | 336.4439 | -3550 | -400 | -3613.5561 | 90.34% | 59.64% | 95% | 0% | 1605 | -50
[5 empty] | 2019-07-08 | 13 | 4517.5 | 1725 | -69 | 1 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 1328.7716 | 780 | 200 | 2308.7716 | 57.72% | 95% | 0% | -78.9474 | 610.7476 | -3550 | -400 | -3339.2524 | 83.48% | 59.64% | 95% | 0% | 1794 | -69
[5 empty] | 2019-07-08 | 14 | 4518 | 1855 | -102 | 1 | 0 | 1957 | 945.0124 | 945.0124 | 945.0124 | 1328.7716 | 780 | 200 | 2308.7716 | 57.72% | 95% | 0% | -116.7048 | 828.3076 | -3550 | -400 | -3121.6924 | 78.04% | 59.64% | 95% | 0% | 1957 | -102
[5 empty] | 2019-07-08 | 15 | 4518.5 | 2019 | -134 | 1 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 1328.7716 | 780 | 200 | 2308.7716 | 57.72% | 95% | 0% | -153.3181 | 1098.7017 | -3550 | -400 | -2851.2983 | 71.28% | 59.64% | 95% | 0% | 2153 | -134
[5 empty] | 2019-07-08 | 16 | 4519 | 2076 | -175 | 1 | 0 | 2251 | 1405.5235 | 1405.5235 | 1405.5235 | 1328.7716 | 780 | 200 | 2308.7716 | 57.72% | 95% | 0% | -200.2288 | 1205.2947 | -3550 | -400 | -2744.7053 | 68.62% | 59.63% | 95% | 0% | 2251 | -175
[5 empty] | 2019-07-08 | 17 | 4519.5 | 2083 | -232 | 1 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 1328.7716 | 780 | 200 | 2308.7716 | 57.72% | 95% | 0% | -265.4462 | 1240.3246 | -3550 | -400 | -2709.6754 | 67.74% | 59.63% | 95% | 0% | 2315 | -232
[5 empty] | 2019-07-08 | 18 | 4520 | 2026 | -281 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1328.7716 | 780 | 200 | 2308.7716 | 57.72% | 95% | 0% | -321.5103 | 1171.7296 | -3550 | -400 | -2778.2704 | 69.46% | 59.63% | 95% | 0% | 2307 | -281
[5 empty] | 2019-07-08 | 19 | 4520.5 | 1984 | -326 | 1 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 1328.7716 | 780 | 200 | 2308.7716 | 57.72% | 95% | 0% | -372.9977 | 1124.9413 | -3550 | -400 | -2825.0587 | 70.63% | 59.62% | 95% | 0% | 2310 | -326
[5 empty] | 2019-07-08 | 20 | 4521 | 1919 | -371 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 1328.7716 | 780 | 200 | 2308.7716 | 57.72% | 95% | 0% | -424.4851 | 1042.1266 | -3550 | -400 | -2907.8734 | 72.7% | 59.61% | 95% | 0% | 2290 | -371
[5 empty] | 2019-07-08 | 21 | 4521.5 | 1844 | -413 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -472.54 | 942.3816 | -3550 | -400 | -3007.6184 | 75.19% | 59.61% | 95% | 0% | 2257 | -413
[5 empty] | 2019-07-08 | 22 | 4522 | 1785 | -456 | 1 | 0 | 2241 | 1389.8599 | 1389.8599 | 1389.8599 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -521.7391 | 868.1207 | -3550 | -400 | -3081.8793 | 77.05% | 59.61% | 95% | 0% | 2241 | -456
[5 empty] | 2019-07-08 | 23 | 4522.5 | 1736 | -494 | 1 | 0 | 2230 | 1372.6298 | 1372.6298 | 1372.6298 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -565.2174 | 807.4125 | -3550 | -400 | -3142.5875 | 78.56% | 59.6% | 95% | 0% | 2230 | -494
[5 empty] | 2019-07-08 | 24 | 4523 | 1705 | -515 | 1 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -589.2449 | 767.7213 | -3550 | -400 | -3182.2787 | 79.56% | 59.6% | 95% | 0% | 2220 | -515
[5 empty] | 2019-07-08 | 25 | 4523.5 | 1669 | -546 | 1 | 0 | 2215 | 1349.1344 | 1349.1344 | 1349.1344 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -624.714 | 724.4204 | -3550 | -400 | -3225.5796 | 80.64% | 59.59% | 95% | 0% | 2215 | -546
[5 empty] | 2019-07-08 | 26 | 4524 | 1631 | -573 | 1 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -655.6064 | 676.298 | -3550 | -400 | -3273.702 | 81.84% | 59.59% | 95% | 0% | 2204 | -573
[5 empty] | 2019-07-08 | 27 | 4524.5 | 1608 | -580 | 1 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -663.6156 | 643.227 | -3550 | -400 | -3306.773 | 82.67% | 59.59% | 95% | 0% | 2188 | -580
[5 empty] | 2019-07-08 | 28 | 4525 | 1622 | -560 | 1 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -640.7323 | 656.7121 | -3550 | -400 | -3293.2879 | 82.33% | 59.59% | 95% | 0% | 2182 | -560
[5 empty] | 2019-07-08 | 29 | 4525.5 | 1628 | -538 | 1 | 0 | 2166 | 1272.3825 | 1272.3825 | 1272.3825 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -615.5606 | 656.8219 | -3550 | -400 | -3293.1781 | 82.33% | 59.58% | 95% | 0% | 2166 | -538
[5 empty] | 2019-07-08 | 30 | 4526 | 1654 | -514 | 1 | 0 | 2168 | 1275.5153 | 1275.5153 | 1275.5153 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -588.1007 | 687.4146 | -3550 | -400 | -3262.5854 | 81.56% | 59.58% | 95% | 0% | 2168 | -514
[5 empty] | 2019-07-08 | 31 | 4526.5 | 1716 | -475 | 1 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -543.4783 | 768.0634 | -3550 | -400 | -3181.9366 | 79.55% | 59.57% | 95% | 0% | 2191 | -475
[5 empty] | 2019-07-08 | 32 | 4527 | 1810 | -443 | 1 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -506.865 | 901.7912 | -3550 | -400 | -3048.2088 | 76.21% | 59.57% | 95% | 0% | 2253 | -443
[5 empty] | 2019-07-08 | 33 | 4527.5 | 1904 | -403 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1327.2053 | 780 | 200 | 2307.2053 | 57.68% | 95% | 0% | -461.0984 | 1032.1415 | -3550 | -400 | -2917.8585 | 72.95% | 59.57% | 95% | 0% | 2307 | -403
[5 empty] | 2019-07-08 | 34 | 4528 | 1999 | -340 | 1 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 1325.6389 | 780 | 200 | 2305.6389 | 57.64% | 95% | 0% | -389.016 | 1154.3475 | -3550 | -400 | -2795.6525 | 69.89% | 59.57% | 95% | 0% | 2339 | -340
[5 empty] | 2019-07-08 | 35 | 4528.5 | 2116 | -277 | 1 | 0 | 2393 | 1627.9472 | 1627.9472 | 1627.9472 | 1325.6389 | 780 | 200 | 2305.6389 | 57.64% | 95% | 0% | -316.9336 | 1311.0136 | -3550 | -400 | -2638.9864 | 65.97% | 59.57% | 95% | 0% | 2393 | -277
[5 empty] | 2019-07-08 | 36 | 4529 | 2178 | -226 | 1 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 1325.6389 | 780 | 200 | 2305.6389 | 57.64% | 95% | 0% | -258.5812 | 1386.596 | -3550 | -400 | -2563.404 | 64.09% | 59.56% | 95% | 0% | 2404 | -226
[5 empty] | 2019-07-08 | 37 | 4529.5 | 2241 | -175 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 1325.6389 | 780 | 200 | 2305.6389 | 57.64% | 95% | 0% | -200.2288 | 1463.7448 | -3550 | -400 | -2486.2552 | 62.16% | 59.56% | 95% | 0% | 2416 | -175
[5 empty] | 2019-07-08 | 38 | 4530 | 2286 | -135 | 1 | 0 | 2421 | 1671.8054 | 1671.8054 | 1671.8054 | 1325.6389 | 780 | 200 | 2305.6389 | 57.64% | 95% | 0% | -154.4622 | 1517.3432 | -3550 | -400 | -2432.6568 | 60.82% | 59.55% | 95% | 0% | 2421 | -135
[5 empty] | 2019-07-08 | 39 | 4530.5 | 2321 | -105 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -120.1373 | 1559.5 | -3550 | -400 | -2390.5 | 59.76% | 59.55% | 95% | 0% | 2426 | -105
[5 empty] | 2019-07-08 | 40 | 4531 | 2358 | -76 | 1 | 0 | 2434 | 1692.1682 | 1692.1682 | 1692.1682 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -86.9565 | 1605.2117 | -3550 | -400 | -2344.7883 | 58.62% | 59.55% | 95% | 0% | 2434 | -76
[5 empty] | 2019-07-08 | 41 | 4531.5 | 2368 | -54 | 1 | 0 | 2422 | 1673.3718 | 1673.3718 | 1673.3718 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -61.7849 | 1611.5869 | -3550 | -400 | -2338.4131 | 58.46% | 59.54% | 95% | 0% | 2422 | -54
[5 empty] | 2019-07-08 | 42 | 4532 | 2346 | -40 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -45.7666 | 1571.2161 | -3550 | -400 | -2378.7839 | 59.47% | 59.54% | 95% | 0% | 2386 | -40
[5 empty] | 2019-07-08 | 43 | 4532.5 | 2318 | -35 | 1 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -40.0458 | 1525.2469 | -3550 | -400 | -2424.7531 | 60.62% | 59.54% | 95% | 0% | 2353 | -35
[5 empty] | 2019-07-08 | 44 | 4533 | 2263 | -33 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -37.7574 | 1438.2525 | -3550 | -400 | -2511.7475 | 62.79% | 59.53% | 95% | 0% | 2296 | -33
[5 empty] | 2019-07-08 | 45 | 4533.5 | 2199 | -32 | 0 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -36.6133 | 1337.5829 | -2750 | -200 | -1612.4171 | 40.31% | 59.53% | 95% | 0% | 2231 | -32
[5 empty] | 2019-07-08 | 46 | 4534 | 2063 | -32 | 0 | 0 | 2095 | 1161.1707 | 1161.1707 | 1161.1707 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -36.6133 | 1124.5574 | -2750 | -200 | -1825.4426 | 45.64% | 59.53% | 95% | 0% | 2095 | -32
[5 empty] | 2019-07-08 | 47 | 4534.5 | 1914 | -32 | 0 | 0 | 1946 | 927.7824 | 927.7824 | 927.7824 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -36.6133 | 891.1691 | -2750 | -200 | -2058.8309 | 51.47% | 59.53% | 95% | 0% | 1946 | -32
[5 empty] | 2019-07-08 | 48 | 4535 | 1800 | -31 | 0 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -35.4691 | 712.1813 | -2750 | -200 | -2237.8187 | 55.95% | 59.52% | 95% | 0% | 1831 | -31
[5 empty] | 2019-07-09 | 1 | 4535.5 | 1720 | -32 | 0 | 0 | 1752 | 623.9077 | 623.9077 | 623.9077 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -36.6133 | 587.2944 | -2750 | -200 | -2362.7056 | 59.07% | 59.52% | 95% | 0% | 1752 | -32
[5 empty] | 2019-07-09 | 2 | 4536 | 1666 | -32 | 0 | 0 | 1698 | 539.324 | 539.324 | 539.324 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -36.6133 | 502.7107 | -2750 | -200 | -2447.2893 | 61.18% | 59.52% | 95% | 0% | 1698 | -32
[5 empty] | 2019-07-09 | 3 | 4536.5 | 1630 | -32 | 0 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -36.6133 | 446.3216 | -2750 | -200 | -2503.6784 | 62.59% | 59.52% | 95% | 0% | 1662 | -32
[5 empty] | 2019-07-09 | 4 | 4537 | 1609 | -32 | 0 | 0 | 1641 | 450.0412 | 450.0412 | 450.0412 | 1324.0725 | 780 | 200 | 2304.0725 | 57.6% | 95% | 0% | -36.6133 | 413.4279 | -2750 | -200 | -2536.5721 | 63.41% | 59.52% | 95% | 0% | 1641 | -32
[5 empty] | 2019-07-09 | 5 | 4537.5 | 1591 | -32 | 0 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 1322.5062 | 780 | 200 | 2302.5062 | 57.56% | 95% | 0% | -36.6133 | 385.2334 | -2750 | -200 | -2564.7666 | 64.12% | 59.52% | 95% | 0% | 1623 | -32
[5 empty] | 2019-07-09 | 6 | 4538 | 1565 | -32 | 0 | 0 | 1597 | 381.1212 | 381.1212 | 381.1212 | 1322.5062 | 780 | 200 | 2302.5062 | 57.56% | 95% | 0% | -36.6133 | 344.5079 | -2750 | -200 | -2605.4921 | 65.14% | 59.52% | 95% | 0% | 1597 | -32
[5 empty] | 2019-07-09 | 7 | 4538.5 | 1554 | -32 | 0 | 0 | 1586 | 363.8912 | 363.8912 | 363.8912 | 1322.5062 | 780 | 200 | 2302.5062 | 57.56% | 95% | 0% | -36.6133 | 327.2779 | -2750 | -200 | -2622.7221 | 65.57% | 59.51% | 95% | 0% | 1586 | -32
[5 empty] | 2019-07-09 | 8 | 4539 | 1550 | -32 | 0 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 1322.5062 | 780 | 200 | 2302.5062 | 57.56% | 95% | 0% | -36.6133 | 321.0124 | -2750 | -200 | -2628.9876 | 65.72% | 59.51% | 95% | 0% | 1582 | -32
[5 empty] | 2019-07-09 | 9 | 4539.5 | 1548 | -34 | 0 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 1322.5062 | 780 | 200 | 2302.5062 | 57.56% | 95% | 0% | -38.9016 | 318.7241 | -2750 | -200 | -2631.2759 | 65.78% | 59.51% | 95% | 0% | 1582 | -34
[5 empty] | 2019-07-09 | 10 | 4540 | 1545 | -35 | 0 | 0 | 1580 | 354.493 | 354.493 | 354.493 | 1322.5062 | 780 | 200 | 2302.5062 | 57.56% | 95% | 0% | -40.0458 | 314.4472 | -2750 | -200 | -2635.5528 | 65.89% | 59.5% | 95% | 0% | 1580 | -35
[5 empty] | 2019-07-09 | 11 | 4540.5 | 1581 | -37 | 0 | 0 | 1618 | 414.0148 | 414.0148 | 414.0148 | 1322.5062 | 780 | 200 | 2302.5062 | 57.56% | 95% | 0% | -42.3341 | 371.6807 | -2750 | -200 | -2578.3193 | 64.46% | 59.5% | 95% | 0% | 1618 | -37
[5 empty] | 2019-07-09 | 12 | 4541 | 1640 | -41 | 0 | 0 | 1681 | 512.6958 | 512.6958 | 512.6958 | 1322.5062 | 780 | 200 | 2302.5062 | 57.56% | 95% | 0% | -46.9108 | 465.785 | -2750 | -200 | -2484.215 | 62.11% | 59.49% | 95% | 0% | 1681 | -41
[5 empty] | 2019-07-09 | 13 | 4541.5 | 1805 | -57 | 1 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 1322.5062 | 780 | 200 | 2302.5062 | 57.56% | 95% | 0% | -65.2174 | 730.9904 | -3550 | -400 | -3219.0096 | 80.48% | 59.49% | 95% | 0% | 1862 | -57
[5 empty] | 2019-07-09 | 14 | 4542 | 1962 | -72 | 1 | 0 | 2034 | 1065.6224 | 1065.6224 | 1065.6224 | 1322.5062 | 780 | 200 | 2302.5062 | 57.56% | 95% | 0% | -82.3799 | 983.2426 | -3550 | -400 | -2966.7574 | 74.17% | 59.49% | 95% | 0% | 2034 | -72
[5 empty] | 2019-07-09 | 15 | 4542.5 | 2142 | -100 | 1 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 1322.5062 | 780 | 200 | 2302.5062 | 57.56% | 95% | 0% | -114.4165 | 1277.0097 | -3550 | -400 | -2672.9903 | 66.82% | 59.49% | 95% | 0% | 2242 | -100
[5 empty] | 2019-07-09 | 16 | 4543 | 2226 | -122 | 1 | 0 | 2348 | 1557.4608 | 1557.4608 | 1557.4608 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -139.5881 | 1417.8727 | -3550 | -400 | -2532.1273 | 63.3% | 59.49% | 95% | 0% | 2348 | -122
[5 empty] | 2019-07-09 | 17 | 4543.5 | 2255 | -159 | 1 | 0 | 2414 | 1660.8409 | 1660.8409 | 1660.8409 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -181.9222 | 1478.9187 | -3550 | -400 | -2471.0813 | 61.78% | 59.49% | 95% | 0% | 2414 | -159
[5 empty] | 2019-07-09 | 18 | 4544 | 2210 | -202 | 1 | 0 | 2412 | 1657.7082 | 1657.7082 | 1657.7082 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -231.1213 | 1426.5869 | -3550 | -400 | -2523.4131 | 63.09% | 59.49% | 95% | 0% | 2412 | -202
[5 empty] | 2019-07-09 | 19 | 4544.5 | 2173 | -242 | 1 | 0 | 2415 | 1662.4073 | 1662.4073 | 1662.4073 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -276.8879 | 1385.5194 | -3550 | -400 | -2564.4806 | 64.11% | 59.48% | 95% | 0% | 2415 | -242
[5 empty] | 2019-07-09 | 20 | 4545 | 2112 | -286 | 1 | 0 | 2398 | 1635.7791 | 1635.7791 | 1635.7791 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -327.2311 | 1308.5479 | -3550 | -400 | -2641.4521 | 66.04% | 59.48% | 95% | 0% | 2398 | -286
[5 empty] | 2019-07-09 | 21 | 4545.5 | 2062 | -331 | 1 | 0 | 2393 | 1627.9472 | 1627.9472 | 1627.9472 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -378.7185 | 1249.2287 | -3550 | -400 | -2700.7713 | 67.52% | 59.48% | 95% | 0% | 2393 | -331
[5 empty] | 2019-07-09 | 22 | 4546 | 2018 | -357 | 1 | 0 | 2375 | 1599.7527 | 1599.7527 | 1599.7527 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -408.4668 | 1191.2859 | -3550 | -400 | -2758.7141 | 68.97% | 59.48% | 95% | 0% | 2375 | -357
[5 empty] | 2019-07-09 | 23 | 4546.5 | 2012 | -363 | 1 | 0 | 2375 | 1599.7527 | 1599.7527 | 1599.7527 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -415.3318 | 1184.4209 | -3550 | -400 | -2765.5791 | 69.14% | 59.47% | 95% | 0% | 2375 | -363
[5 empty] | 2019-07-09 | 24 | 4547 | 1976 | -378 | 1 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -432.4943 | 1134.3647 | -3550 | -400 | -2815.6353 | 70.39% | 59.47% | 95% | 0% | 2354 | -378
[5 empty] | 2019-07-09 | 25 | 4547.5 | 1989 | -373 | 1 | 0 | 2362 | 1579.3899 | 1579.3899 | 1579.3899 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -426.7735 | 1152.6165 | -3550 | -400 | -2797.3835 | 69.93% | 59.47% | 95% | 0% | 2362 | -373
[5 empty] | 2019-07-09 | 26 | 4548 | 1961 | -391 | 1 | 0 | 2352 | 1563.7263 | 1563.7263 | 1563.7263 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -447.3684 | 1116.3579 | -3550 | -400 | -2833.6421 | 70.84% | 59.47% | 95% | 0% | 2352 | -391
[5 empty] | 2019-07-09 | 27 | 4548.5 | 1973 | -373 | 1 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -426.7735 | 1127.5547 | -3550 | -400 | -2822.4453 | 70.56% | 59.47% | 95% | 0% | 2346 | -373
[5 empty] | 2019-07-09 | 28 | 4549 | 1983 | -339 | 1 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -387.8719 | 1128.8635 | -3550 | -400 | -2821.1365 | 70.53% | 59.46% | 95% | 0% | 2322 | -339
[5 empty] | 2019-07-09 | 29 | 4549.5 | 2017 | -313 | 1 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -358.1236 | 1171.1427 | -3550 | -400 | -2778.8573 | 69.47% | 59.46% | 95% | 0% | 2330 | -313
[5 empty] | 2019-07-09 | 30 | 4550 | 2027 | -323 | 1 | 0 | 2350 | 1560.5936 | 1560.5936 | 1560.5936 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -369.5652 | 1191.0284 | -3550 | -400 | -2758.9716 | 68.97% | 59.46% | 95% | 0% | 2350 | -323
[5 empty] | 2019-07-09 | 31 | 4550.5 | 2070 | -294 | 1 | 0 | 2364 | 1582.5227 | 1582.5227 | 1582.5227 | 1320.9398 | 780 | 200 | 2300.9398 | 57.52% | 95% | 0% | -336.3844 | 1246.1382 | -3550 | -400 | -2703.8618 | 67.6% | 59.46% | 95% | 0% | 2364 | -294
[5 empty] | 2019-07-09 | 32 | 4551 | 2147 | -269 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 1319.3735 | 780 | 200 | 2299.3735 | 57.48% | 95% | 0% | -307.7803 | 1356.1933 | -3550 | -400 | -2593.8067 | 64.85% | 59.46% | 95% | 0% | 2416 | -269
[5 empty] | 2019-07-09 | 33 | 4551.5 | 2187 | -274 | 1 | 0 | 2461 | 1734.46 | 1734.46 | 1734.46 | 1319.3735 | 780 | 200 | 2299.3735 | 57.48% | 95% | 0% | -313.5011 | 1420.9589 | -3550 | -400 | -2529.0411 | 63.23% | 59.45% | 95% | 0% | 2461 | -274
[5 empty] | 2019-07-09 | 34 | 4552 | 2246 | -256 | 1 | 0 | 2502 | 1798.681 | 1798.681 | 1798.681 | 1319.3735 | 780 | 200 | 2299.3735 | 57.48% | 95% | 0% | -292.9062 | 1505.7748 | -3550 | -400 | -2444.2252 | 61.11% | 59.45% | 95% | 0% | 2502 | -256
[5 empty] | 2019-07-09 | 35 | 4552.5 | 2302 | -231 | 1 | 0 | 2533 | 1847.2383 | 1847.2383 | 1847.2383 | 1319.3735 | 780 | 200 | 2299.3735 | 57.48% | 95% | 0% | -264.3021 | 1582.9362 | -3550 | -400 | -2367.0638 | 59.18% | 59.45% | 95% | 0% | 2533 | -231
[5 empty] | 2019-07-09 | 36 | 4553 | 2352 | -192 | 1 | 0 | 2544 | 1864.4683 | 1864.4683 | 1864.4683 | 1319.3735 | 780 | 200 | 2299.3735 | 57.48% | 95% | 0% | -219.6796 | 1644.7886 | -3550 | -400 | -2305.2114 | 57.63% | 59.45% | 95% | 0% | 2544 | -192
[5 empty] | 2019-07-09 | 37 | 4553.5 | 2383 | -151 | 1 | 0 | 2534 | 1848.8046 | 1848.8046 | 1848.8046 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -172.7689 | 1676.0357 | -3550 | -400 | -2273.9643 | 56.85% | 59.45% | 95% | 0% | 2534 | -151
[5 empty] | 2019-07-09 | 38 | 4554 | 2372 | -124 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -141.8764 | 1647.4063 | -3550 | -400 | -2302.5937 | 57.56% | 59.45% | 95% | 0% | 2496 | -124
[5 empty] | 2019-07-09 | 39 | 4554.5 | 2387 | -101 | 1 | 0 | 2488 | 1776.7519 | 1776.7519 | 1776.7519 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -115.5606 | 1661.1912 | -3550 | -400 | -2288.8088 | 57.22% | 59.44% | 95% | 0% | 2488 | -101
[5 empty] | 2019-07-09 | 40 | 4555 | 2386 | -80 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -91.5332 | 1650.7587 | -3550 | -400 | -2299.2413 | 57.48% | 59.44% | 95% | 0% | 2466 | -80
[5 empty] | 2019-07-09 | 41 | 4555.5 | 2365 | -66 | 1 | 0 | 2431 | 1687.4691 | 1687.4691 | 1687.4691 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -75.5149 | 1611.9542 | -3550 | -400 | -2338.0458 | 58.45% | 59.44% | 95% | 0% | 2431 | -66
[5 empty] | 2019-07-09 | 42 | 4556 | 2342 | -53 | 1 | 0 | 2395 | 1631.08 | 1631.08 | 1631.08 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -60.6407 | 1570.4392 | -3550 | -400 | -2379.5608 | 59.49% | 59.43% | 95% | 0% | 2395 | -53
[5 empty] | 2019-07-09 | 43 | 4556.5 | 2301 | -48 | 1 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -54.9199 | 1504.1073 | -3550 | -400 | -2445.8927 | 61.15% | 59.43% | 95% | 0% | 2349 | -48
[5 empty] | 2019-07-09 | 44 | 4557 | 2250 | -47 | 1 | 0 | 2297 | 1477.5763 | 1477.5763 | 1477.5763 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -53.7757 | 1423.8005 | -3550 | -400 | -2526.1995 | 63.15% | 59.43% | 95% | 0% | 2297 | -47
[5 empty] | 2019-07-09 | 45 | 4557.5 | 2172 | -47 | 1 | 0 | 2219 | 1355.3998 | 1355.3998 | 1355.3998 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -53.7757 | 1301.6241 | -3550 | -400 | -2648.3759 | 66.21% | 59.42% | 95% | 0% | 2219 | -47
[5 empty] | 2019-07-09 | 46 | 4558 | 2040 | -46 | 0 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -52.6316 | 1094.4418 | -2750 | -200 | -1855.5582 | 46.39% | 59.42% | 95% | 0% | 2086 | -46
[5 empty] | 2019-07-09 | 47 | 4558.5 | 1892 | -45 | 0 | 0 | 1937 | 913.6851 | 913.6851 | 913.6851 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -51.4874 | 862.1977 | -2750 | -200 | -2087.8023 | 52.2% | 59.42% | 95% | 0% | 1937 | -45
[5 empty] | 2019-07-09 | 48 | 4559 | 1784 | -44 | 0 | 0 | 1828 | 742.9514 | 742.9514 | 742.9514 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -50.3432 | 692.6081 | -2750 | -200 | -2257.3919 | 56.43% | 59.41% | 95% | 0% | 1828 | -44
[5 empty] | 2019-07-10 | 1 | 4559.5 | 1690 | -44 | 0 | 0 | 1734 | 595.7131 | 595.7131 | 595.7131 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -50.3432 | 545.3699 | -2750 | -200 | -2404.6301 | 60.12% | 59.41% | 95% | 0% | 1734 | -44
[5 empty] | 2019-07-10 | 2 | 4560 | 1634 | -44 | 1 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 1317.8071 | 780 | 200 | 2297.8071 | 57.45% | 95% | 0% | -50.3432 | 457.6535 | -3550 | -400 | -3492.3465 | 87.31% | 59.4% | 95% | 0% | 1678 | -44
[5 empty] | 2019-07-10 | 3 | 4560.5 | 1601 | -44 | 1 | 0 | 1645 | 456.3067 | 456.3067 | 456.3067 | 1316.2407 | 780 | 200 | 2296.2407 | 57.41% | 95% | 0% | -50.3432 | 405.9634 | -3550 | -400 | -3544.0366 | 88.6% | 59.4% | 95% | 0% | 1645 | -44
[5 empty] | 2019-07-10 | 4 | 4561 | 1580 | -44 | 1 | 0 | 1624 | 423.413 | 423.413 | 423.413 | 1316.2407 | 780 | 200 | 2296.2407 | 57.41% | 95% | 0% | -50.3432 | 373.0698 | -3550 | -400 | -3576.9302 | 89.42% | 59.4% | 95% | 0% | 1624 | -44
[5 empty] | 2019-07-10 | 5 | 4561.5 | 1551 | -45 | 1 | 0 | 1596 | 379.5548 | 379.5548 | 379.5548 | 1316.2407 | 780 | 200 | 2296.2407 | 57.41% | 95% | 0% | -51.4874 | 328.0674 | -3550 | -400 | -3621.9326 | 90.55% | 59.39% | 95% | 0% | 1596 | -45
[5 empty] | 2019-07-10 | 6 | 4562 | 1528 | -45 | 1 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 1316.2407 | 780 | 200 | 2296.2407 | 57.41% | 95% | 0% | -51.4874 | 292.041 | -3550 | -400 | -3657.959 | 91.45% | 59.39% | 95% | 0% | 1573 | -45
[5 empty] | 2019-07-10 | 7 | 4562.5 | 1519 | -44 | 1 | 0 | 1563 | 327.8648 | 327.8648 | 327.8648 | 1316.2407 | 780 | 200 | 2296.2407 | 57.41% | 95% | 0% | -50.3432 | 277.5215 | -3550 | -400 | -3672.4785 | 91.81% | 59.39% | 95% | 0% | 1563 | -44
[5 empty] | 2019-07-10 | 8 | 4563 | 1521 | -44 | 1 | 0 | 1565 | 330.9975 | 330.9975 | 330.9975 | 1316.2407 | 780 | 200 | 2296.2407 | 57.41% | 95% | 0% | -50.3432 | 280.6543 | -3550 | -400 | -3669.3457 | 91.73% | 59.39% | 95% | 0% | 1565 | -44
[5 empty] | 2019-07-10 | 9 | 4563.5 | 1518 | -46 | 1 | 0 | 1564 | 329.4312 | 329.4312 | 329.4312 | 1316.2407 | 780 | 200 | 2296.2407 | 57.41% | 95% | 0% | -52.6316 | 276.7996 | -3550 | -400 | -3673.2004 | 91.83% | 59.39% | 95% | 0% | 1564 | -46
[5 empty] | 2019-07-10 | 10 | 4564 | 1513 | -48 | 1 | 0 | 1561 | 324.7321 | 324.7321 | 324.7321 | 1316.2407 | 780 | 200 | 2296.2407 | 57.41% | 95% | 0% | -54.9199 | 269.8122 | -3550 | -400 | -3680.1878 | 92% | 59.39% | 95% | 0% | 1561 | -48
[5 empty] | 2019-07-10 | 11 | 4564.5 | 1539 | -48 | 1 | 0 | 1587 | 365.4575 | 365.4575 | 365.4575 | 1316.2407 | 780 | 200 | 2296.2407 | 57.41% | 95% | 0% | -54.9199 | 310.5376 | -3550 | -400 | -3639.4624 | 90.99% | 59.39% | 95% | 0% | 1587 | -48
[5 empty] | 2019-07-10 | 12 | 4565 | 1594 | -55 | 1 | 0 | 1649 | 462.5721 | 462.5721 | 462.5721 | 1316.2407 | 780 | 200 | 2296.2407 | 57.41% | 95% | 0% | -62.9291 | 399.6431 | -3550 | -400 | -3550.3569 | 88.76% | 59.38% | 95% | 0% | 1649 | -55
[5 empty] | 2019-07-10 | 13 | 4565.5 | 1762 | -71 | 1 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 1316.2407 | 780 | 200 | 2296.2407 | 57.41% | 95% | 0% | -81.2357 | 669.5475 | -3550 | -400 | -3280.4525 | 82.01% | 59.38% | 95% | 0% | 1833 | -71
[5 empty] | 2019-07-10 | 14 | 4566 | 1915 | -94 | 1 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 1316.2407 | 780 | 200 | 2296.2407 | 57.41% | 95% | 0% | -107.5515 | 918.9118 | -3550 | -400 | -3031.0882 | 75.78% | 59.38% | 95% | 0% | 2009 | -94
[5 empty] | 2019-07-10 | 15 | 4566.5 | 2081 | -127 | 1 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -145.3089 | 1192.8609 | -3550 | -400 | -2757.1391 | 68.93% | 59.38% | 95% | 0% | 2208 | -127
[5 empty] | 2019-07-10 | 16 | 4567 | 2139 | -170 | 1 | 0 | 2309 | 1496.3726 | 1496.3726 | 1496.3726 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -194.508 | 1301.8646 | -3550 | -400 | -2648.1354 | 66.2% | 59.37% | 95% | 0% | 2309 | -170
[5 empty] | 2019-07-10 | 17 | 4567.5 | 2190 | -206 | 1 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -235.6979 | 1396.9484 | -3550 | -400 | -2553.0516 | 63.83% | 59.37% | 95% | 0% | 2396 | -206
[5 empty] | 2019-07-10 | 18 | 4568 | 2154 | -248 | 1 | 0 | 2402 | 1642.0445 | 1642.0445 | 1642.0445 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -283.7529 | 1358.2917 | -3550 | -400 | -2591.7083 | 64.79% | 59.37% | 95% | 0% | 2402 | -248
[5 empty] | 2019-07-10 | 19 | 4568.5 | 2086 | -298 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -340.9611 | 1272.8889 | -3550 | -400 | -2677.1111 | 66.93% | 59.37% | 95% | 0% | 2384 | -298
[5 empty] | 2019-07-10 | 20 | 4569 | 2012 | -346 | 1 | 0 | 2358 | 1573.1245 | 1573.1245 | 1573.1245 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -395.881 | 1177.2435 | -3550 | -400 | -2772.7565 | 69.32% | 59.36% | 95% | 0% | 2358 | -346
[5 empty] | 2019-07-10 | 21 | 4569.5 | 1926 | -411 | 1 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -470.2517 | 1069.9791 | -3550 | -400 | -2880.0209 | 72% | 59.36% | 95% | 0% | 2337 | -411
[5 empty] | 2019-07-10 | 22 | 4570 | 1897 | -438 | 1 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -501.1442 | 1035.9539 | -3550 | -400 | -2914.0461 | 72.85% | 59.36% | 95% | 0% | 2335 | -438
[5 empty] | 2019-07-10 | 23 | 4570.5 | 1825 | -480 | 1 | 0 | 2305 | 1490.1072 | 1490.1072 | 1490.1072 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -549.1991 | 940.9081 | -3550 | -400 | -3009.0919 | 75.23% | 59.36% | 95% | 0% | 2305 | -480
[5 empty] | 2019-07-10 | 24 | 4571 | 1776 | -521 | 1 | 0 | 2297 | 1477.5763 | 1477.5763 | 1477.5763 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -596.1098 | 881.4664 | -3550 | -400 | -3068.5336 | 76.71% | 59.36% | 95% | 0% | 2297 | -521
[5 empty] | 2019-07-10 | 25 | 4571.5 | 1773 | -522 | 1 | 0 | 2295 | 1474.4435 | 1474.4435 | 1474.4435 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -597.254 | 877.1895 | -3550 | -400 | -3072.8105 | 76.82% | 59.35% | 95% | 0% | 2295 | -522
[5 empty] | 2019-07-10 | 26 | 4572 | 1744 | -525 | 1 | 0 | 2269 | 1433.7181 | 1433.7181 | 1433.7181 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -600.6865 | 833.0316 | -3550 | -400 | -3116.9684 | 77.92% | 59.35% | 95% | 0% | 2269 | -525
[5 empty] | 2019-07-10 | 27 | 4572.5 | 1696 | -547 | 1 | 0 | 2243 | 1392.9926 | 1392.9926 | 1392.9926 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -625.8581 | 767.1345 | -3550 | -400 | -3182.8655 | 79.57% | 59.35% | 95% | 0% | 2243 | -547
[5 empty] | 2019-07-10 | 28 | 4573 | 1668 | -555 | 1 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -635.0114 | 726.6539 | -3550 | -400 | -3223.3461 | 80.58% | 59.35% | 95% | 0% | 2223 | -555
[5 empty] | 2019-07-10 | 29 | 4573.5 | 1707 | -524 | 1 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 1314.6744 | 780 | 200 | 2294.6744 | 57.37% | 95% | 0% | -599.5423 | 774.6539 | -3550 | -400 | -3175.3461 | 79.38% | 59.35% | 95% | 0% | 2231 | -524
[5 empty] | 2019-07-10 | 30 | 4574 | 1745 | -499 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1313.108 | 780 | 200 | 2293.108 | 57.33% | 95% | 0% | -570.9382 | 823.6207 | -3550 | -400 | -3126.3793 | 78.16% | 59.35% | 95% | 0% | 2244 | -499
[5 empty] | 2019-07-10 | 31 | 4574.5 | 1771 | -473 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1313.108 | 780 | 200 | 2293.108 | 57.33% | 95% | 0% | -541.1899 | 853.369 | -3550 | -400 | -3096.631 | 77.42% | 59.34% | 95% | 0% | 2244 | -473
[5 empty] | 2019-07-10 | 32 | 4575 | 1789 | -424 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 1313.108 | 780 | 200 | 2293.108 | 57.33% | 95% | 0% | -485.1259 | 860.8758 | -3550 | -400 | -3089.1242 | 77.23% | 59.33% | 95% | 0% | 2213 | -424
[5 empty] | 2019-07-10 | 33 | 4575.5 | 1952 | -383 | 1 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 1313.108 | 780 | 200 | 2293.108 | 57.33% | 95% | 0% | -438.2151 | 1098.883 | -3550 | -400 | -2851.117 | 71.28% | 59.33% | 95% | 0% | 2335 | -383
[5 empty] | 2019-07-10 | 34 | 4576 | 2077 | -340 | 1 | 0 | 2417 | 1665.54 | 1665.54 | 1665.54 | 1313.108 | 780 | 200 | 2293.108 | 57.33% | 95% | 0% | -389.016 | 1276.524 | -3550 | -400 | -2673.476 | 66.84% | 59.33% | 95% | 0% | 2417 | -340
[5 empty] | 2019-07-10 | 35 | 4576.5 | 2166 | -298 | 1 | 0 | 2464 | 1739.1591 | 1739.1591 | 1739.1591 | 1313.108 | 780 | 200 | 2293.108 | 57.33% | 95% | 0% | -340.9611 | 1398.198 | -3550 | -400 | -2551.802 | 63.8% | 59.33% | 95% | 0% | 2464 | -298
[5 empty] | 2019-07-10 | 36 | 4577 | 2236 | -259 | 1 | 0 | 2495 | 1787.7164 | 1787.7164 | 1787.7164 | 1313.108 | 780 | 200 | 2293.108 | 57.33% | 95% | 0% | -296.3387 | 1491.3777 | -3550 | -400 | -2458.6223 | 61.47% | 59.32% | 95% | 0% | 2495 | -259
[5 empty] | 2019-07-10 | 37 | 4577.5 | 2301 | -193 | 1 | 0 | 2494 | 1786.15 | 1786.15 | 1786.15 | 1313.108 | 780 | 200 | 2293.108 | 57.33% | 95% | 0% | -220.8238 | 1565.3262 | -3550 | -400 | -2384.6738 | 59.62% | 59.32% | 95% | 0% | 2494 | -193
[5 empty] | 2019-07-10 | 38 | 4578 | 2352 | -148 | 1 | 0 | 2500 | 1795.5482 | 1795.5482 | 1795.5482 | 1313.108 | 780 | 200 | 2293.108 | 57.33% | 95% | 0% | -169.3364 | 1626.2118 | -3550 | -400 | -2323.7882 | 58.09% | 59.32% | 95% | 0% | 2500 | -148
[5 empty] | 2019-07-10 | 39 | 4578.5 | 2365 | -112 | 1 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 1313.108 | 780 | 200 | 2293.108 | 57.33% | 95% | 0% | -128.1465 | 1631.3754 | -3550 | -400 | -2318.6246 | 57.97% | 59.32% | 95% | 0% | 2477 | -112
[5 empty] | 2019-07-10 | 40 | 4579 | 2364 | -88 | 1 | 0 | 2452 | 1720.3627 | 1720.3627 | 1720.3627 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -100.6865 | 1619.6762 | -3550 | -400 | -2330.3238 | 58.26% | 59.32% | 95% | 0% | 2452 | -88
[5 empty] | 2019-07-10 | 41 | 4579.5 | 2364 | -67 | 1 | 0 | 2431 | 1687.4691 | 1687.4691 | 1687.4691 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -76.659 | 1610.81 | -3550 | -400 | -2339.19 | 58.48% | 59.32% | 95% | 0% | 2431 | -67
[5 empty] | 2019-07-10 | 42 | 4580 | 2345 | -53 | 1 | 0 | 2398 | 1635.7791 | 1635.7791 | 1635.7791 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -60.6407 | 1575.1383 | -3550 | -400 | -2374.8617 | 59.37% | 59.32% | 95% | 0% | 2398 | -53
[5 empty] | 2019-07-10 | 43 | 4580.5 | 2326 | -48 | 1 | 0 | 2374 | 1598.1863 | 1598.1863 | 1598.1863 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -54.9199 | 1543.2664 | -3550 | -400 | -2406.7336 | 60.17% | 59.32% | 95% | 0% | 2374 | -48
[5 empty] | 2019-07-10 | 44 | 4581 | 2298 | -47 | 1 | 0 | 2345 | 1552.7617 | 1552.7617 | 1552.7617 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -53.7757 | 1498.986 | -3550 | -400 | -2451.014 | 61.28% | 59.31% | 95% | 0% | 2345 | -47
[5 empty] | 2019-07-10 | 45 | 4581.5 | 2206 | -47 | 0 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -53.7757 | 1354.8805 | -2750 | -200 | -1595.1195 | 39.88% | 59.3% | 95% | 0% | 2253 | -47
[5 empty] | 2019-07-10 | 46 | 4582 | 2083 | -47 | 0 | 0 | 2130 | 1215.9934 | 1215.9934 | 1215.9934 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -53.7757 | 1162.2177 | -2750 | -200 | -1787.7823 | 44.69% | 59.3% | 95% | 0% | 2130 | -47
[5 empty] | 2019-07-10 | 47 | 4582.5 | 1947 | -47 | 0 | 0 | 1994 | 1002.9678 | 1002.9678 | 1002.9678 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -53.7757 | 949.1921 | -2750 | -200 | -2000.8079 | 50.02% | 59.29% | 95% | 0% | 1994 | -47
[5 empty] | 2019-07-10 | 48 | 4583 | 1829 | -47 | 0 | 0 | 1876 | 818.1369 | 818.1369 | 818.1369 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -53.7757 | 764.3611 | -2750 | -200 | -2185.6389 | 54.64% | 59.29% | 95% | 0% | 1876 | -47
[5 empty] | 2019-07-11 | 1 | 4583.5 | 1727 | -47 | 0 | 0 | 1774 | 658.3677 | 658.3677 | 658.3677 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -53.7757 | 604.5919 | -2750 | -200 | -2345.4081 | 58.64% | 59.28% | 95% | 0% | 1774 | -47
[5 empty] | 2019-07-11 | 2 | 4584 | 1678 | -47 | 0 | 0 | 1725 | 581.6158 | 581.6158 | 581.6158 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -53.7757 | 527.8401 | -2750 | -200 | -2422.1599 | 60.55% | 59.28% | 95% | 0% | 1725 | -47
[5 empty] | 2019-07-11 | 3 | 4584.5 | 1640 | -47 | 0 | 0 | 1687 | 522.094 | 522.094 | 522.094 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -53.7757 | 468.3182 | -2750 | -200 | -2481.6818 | 62.04% | 59.27% | 95% | 0% | 1687 | -47
[5 empty] | 2019-07-11 | 4 | 4585 | 1614 | -47 | 0 | 0 | 1661 | 481.3685 | 481.3685 | 481.3685 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -53.7757 | 427.5928 | -2750 | -200 | -2522.4072 | 63.06% | 59.27% | 95% | 0% | 1661 | -47
[5 empty] | 2019-07-11 | 5 | 4585.5 | 1582 | -48 | 0 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -54.9199 | 377.8913 | -2750 | -200 | -2572.1087 | 64.3% | 59.27% | 95% | 0% | 1630 | -48
[5 empty] | 2019-07-11 | 6 | 4586 | 1556 | -48 | 0 | 0 | 1604 | 392.0857 | 392.0857 | 392.0857 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -54.9199 | 337.1658 | -2750 | -200 | -2612.8342 | 65.32% | 59.26% | 95% | 0% | 1604 | -48
[5 empty] | 2019-07-11 | 7 | 4586.5 | 1537 | -48 | 0 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -54.9199 | 307.4049 | -2750 | -200 | -2642.5951 | 66.06% | 59.26% | 95% | 0% | 1585 | -48
[5 empty] | 2019-07-11 | 8 | 4587 | 1542 | -47 | 0 | 0 | 1589 | 368.5903 | 368.5903 | 368.5903 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -53.7757 | 314.8145 | -2750 | -200 | -2635.1855 | 65.88% | 59.25% | 95% | 0% | 1589 | -47
[5 empty] | 2019-07-11 | 9 | 4587.5 | 1545 | -45 | 0 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 1311.5416 | 780 | 200 | 2291.5416 | 57.29% | 95% | 0% | -51.4874 | 318.6692 | -2750 | -200 | -2631.3308 | 65.78% | 59.25% | 95% | 0% | 1590 | -45
[5 empty] | 2019-07-11 | 10 | 4588 | 1542 | -43 | 0 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -49.1991 | 313.1257 | -2750 | -200 | -2636.8743 | 65.92% | 59.24% | 95% | 0% | 1585 | -43
[5 empty] | 2019-07-11 | 11 | 4588.5 | 1564 | -44 | 0 | 0 | 1608 | 398.3512 | 398.3512 | 398.3512 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -50.3432 | 348.0079 | -2750 | -200 | -2601.9921 | 65.05% | 59.23% | 95% | 0% | 1608 | -44
[5 empty] | 2019-07-11 | 12 | 4589 | 1626 | -54 | 0 | 0 | 1680 | 511.1294 | 511.1294 | 511.1294 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -61.7849 | 449.3445 | -2750 | -200 | -2500.6555 | 62.52% | 59.23% | 95% | 0% | 1680 | -54
[5 empty] | 2019-07-11 | 13 | 4589.5 | 1768 | -74 | 0 | 0 | 1842 | 764.8805 | 764.8805 | 764.8805 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -84.6682 | 680.2123 | -2750 | -200 | -2269.7877 | 56.74% | 59.23% | 95% | 0% | 1842 | -74
[5 empty] | 2019-07-11 | 14 | 4590 | 1926 | -92 | 1 | 0 | 2018 | 1040.5606 | 1040.5606 | 1040.5606 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -105.2632 | 935.2974 | -3550 | -400 | -3014.7026 | 75.37% | 59.23% | 95% | 0% | 2018 | -92
[5 empty] | 2019-07-11 | 15 | 4590.5 | 2086 | -122 | 1 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -139.5881 | 1198.5817 | -3550 | -400 | -2751.4183 | 68.79% | 59.23% | 95% | 0% | 2208 | -122
[5 empty] | 2019-07-11 | 16 | 4591 | 2159 | -162 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -185.3547 | 1329.8143 | -3550 | -400 | -2620.1857 | 65.5% | 59.22% | 95% | 0% | 2321 | -162
[5 empty] | 2019-07-11 | 17 | 4591.5 | 2181 | -206 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -235.6979 | 1382.8511 | -3550 | -400 | -2567.1489 | 64.18% | 59.22% | 95% | 0% | 2387 | -206
[5 empty] | 2019-07-11 | 18 | 4592 | 2088 | -282 | 1 | 0 | 2370 | 1591.9209 | 1591.9209 | 1591.9209 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -322.6545 | 1269.2664 | -3550 | -400 | -2680.7336 | 67.02% | 59.22% | 95% | 0% | 2370 | -282
[5 empty] | 2019-07-11 | 19 | 4592.5 | 1957 | -342 | 1 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -391.3043 | 1089.4046 | -3550 | -400 | -2860.5954 | 71.51% | 59.22% | 95% | 0% | 2299 | -342
[5 empty] | 2019-07-11 | 20 | 4593 | 1876 | -397 | 1 | 0 | 2273 | 1439.9835 | 1439.9835 | 1439.9835 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -454.2334 | 985.7501 | -3550 | -400 | -2964.2499 | 74.11% | 59.22% | 95% | 0% | 2273 | -397
[5 empty] | 2019-07-11 | 21 | 4593.5 | 1804 | -444 | 1 | 0 | 2248 | 1400.8244 | 1400.8244 | 1400.8244 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -508.0092 | 892.8152 | -3550 | -400 | -3057.1848 | 76.43% | 59.22% | 95% | 0% | 2248 | -444
[5 empty] | 2019-07-11 | 22 | 4594 | 1824 | -456 | 1 | 0 | 2280 | 1450.9481 | 1450.9481 | 1450.9481 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -521.7391 | 929.2089 | -3550 | -400 | -3020.7911 | 75.52% | 59.21% | 95% | 0% | 2280 | -456
[5 empty] | 2019-07-11 | 23 | 4594.5 | 1840 | -455 | 1 | 0 | 2295 | 1474.4435 | 1474.4435 | 1474.4435 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -520.595 | 953.8486 | -3550 | -400 | -2996.1514 | 74.9% | 59.21% | 95% | 0% | 2295 | -455
[5 empty] | 2019-07-11 | 24 | 4595 | 1803 | -499 | 1 | 0 | 2302 | 1485.4081 | 1485.4081 | 1485.4081 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -570.9382 | 914.4699 | -3550 | -400 | -3035.5301 | 75.89% | 59.21% | 95% | 0% | 2302 | -499
[5 empty] | 2019-07-11 | 25 | 4595.5 | 1761 | -517 | 1 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -591.5332 | 856.2822 | -3550 | -400 | -3093.7178 | 77.34% | 59.21% | 95% | 0% | 2278 | -517
[5 empty] | 2019-07-11 | 26 | 4596 | 1744 | -525 | 1 | 0 | 2269 | 1433.7181 | 1433.7181 | 1433.7181 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -600.6865 | 833.0316 | -3550 | -400 | -3116.9684 | 77.92% | 59.2% | 95% | 0% | 2269 | -525
[5 empty] | 2019-07-11 | 27 | 4596.5 | 1805 | -491 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -561.7849 | 914.225 | -3550 | -400 | -3035.775 | 75.89% | 59.2% | 95% | 0% | 2296 | -491
[5 empty] | 2019-07-11 | 28 | 4597 | 1793 | -489 | 1 | 0 | 2282 | 1454.0808 | 1454.0808 | 1454.0808 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -559.4966 | 894.5842 | -3550 | -400 | -3055.4158 | 76.39% | 59.2% | 95% | 0% | 2282 | -489
[5 empty] | 2019-07-11 | 29 | 4597.5 | 1787 | -489 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -559.4966 | 885.186 | -3550 | -400 | -3064.814 | 76.62% | 59.2% | 95% | 0% | 2276 | -489
[5 empty] | 2019-07-11 | 30 | 4598 | 1748 | -513 | 1 | 0 | 2261 | 1421.1871 | 1421.1871 | 1421.1871 | 1309.9753 | 780 | 200 | 2289.9753 | 57.25% | 95% | 0% | -586.9565 | 834.2306 | -3550 | -400 | -3115.7694 | 77.89% | 59.2% | 95% | 0% | 2261 | -513
[5 empty] | 2019-07-11 | 31 | 4598.5 | 1755 | -507 | 1 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -580.0915 | 842.662 | -3550 | -400 | -3107.338 | 77.68% | 59.19% | 95% | 0% | 2262 | -507
[5 empty] | 2019-07-11 | 32 | 4599 | 1806 | -487 | 1 | 0 | 2293 | 1471.3108 | 1471.3108 | 1471.3108 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -557.2082 | 914.1026 | -3550 | -400 | -3035.8974 | 75.9% | 59.18% | 95% | 0% | 2293 | -487
[5 empty] | 2019-07-11 | 33 | 4599.5 | 1900 | -444 | 1 | 0 | 2344 | 1551.1954 | 1551.1954 | 1551.1954 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -508.0092 | 1043.1862 | -3550 | -400 | -2906.8138 | 72.67% | 59.18% | 95% | 0% | 2344 | -444
[5 empty] | 2019-07-11 | 34 | 4600 | 2014 | -389 | 1 | 0 | 2403 | 1643.6109 | 1643.6109 | 1643.6109 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -445.0801 | 1198.5308 | -3550 | -400 | -2751.4692 | 68.79% | 59.17% | 95% | 0% | 2403 | -389
[5 empty] | 2019-07-11 | 35 | 4600.5 | 2114 | -321 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -367.2769 | 1326.4577 | -3550 | -400 | -2623.5423 | 65.59% | 59.16% | 95% | 0% | 2435 | -321
[5 empty] | 2019-07-11 | 36 | 4601 | 2199 | -266 | 1 | 0 | 2465 | 1740.7255 | 1740.7255 | 1740.7255 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -304.3478 | 1436.3776 | -3550 | -400 | -2513.6224 | 62.84% | 59.16% | 95% | 0% | 2465 | -266
[5 empty] | 2019-07-11 | 37 | 4601.5 | 2239 | -227 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -259.7254 | 1482.5664 | -3550 | -400 | -2467.4336 | 61.69% | 59.16% | 95% | 0% | 2466 | -227
[5 empty] | 2019-07-11 | 38 | 4602 | 2270 | -181 | 1 | 0 | 2451 | 1718.7964 | 1718.7964 | 1718.7964 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -207.0938 | 1511.7026 | -3550 | -400 | -2438.2974 | 60.96% | 59.15% | 95% | 0% | 2451 | -181
[5 empty] | 2019-07-11 | 39 | 4602.5 | 2297 | -141 | 1 | 0 | 2438 | 1698.4336 | 1698.4336 | 1698.4336 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -161.3272 | 1537.1064 | -3550 | -400 | -2412.8936 | 60.32% | 59.14% | 95% | 0% | 2438 | -141
[5 empty] | 2019-07-11 | 40 | 4603 | 2319 | -108 | 1 | 0 | 2427 | 1681.2036 | 1681.2036 | 1681.2036 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -123.5698 | 1557.6338 | -3550 | -400 | -2392.3662 | 59.81% | 59.14% | 95% | 0% | 2427 | -108
[5 empty] | 2019-07-11 | 41 | 4603.5 | 2286 | -77 | 1 | 0 | 2363 | 1580.9563 | 1580.9563 | 1580.9563 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -88.1007 | 1492.8556 | -3550 | -400 | -2457.1444 | 61.43% | 59.14% | 95% | 0% | 2363 | -77
[5 empty] | 2019-07-11 | 42 | 4604 | 2299 | -59 | 1 | 0 | 2358 | 1573.1245 | 1573.1245 | 1573.1245 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -67.5057 | 1505.6188 | -3550 | -400 | -2444.3812 | 61.11% | 59.13% | 95% | 0% | 2358 | -59
[5 empty] | 2019-07-11 | 43 | 4604.5 | 2254 | -50 | 1 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -57.2082 | 1431.3326 | -3550 | -400 | -2518.6674 | 62.97% | 59.13% | 95% | 0% | 2304 | -50
[5 empty] | 2019-07-11 | 44 | 4605 | 2223 | -49 | 1 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -56.0641 | 1382.3531 | -3550 | -400 | -2567.6469 | 64.19% | 59.13% | 95% | 0% | 2272 | -49
[5 empty] | 2019-07-11 | 45 | 4605.5 | 2179 | -49 | 0 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 1308.4089 | 780 | 200 | 2288.4089 | 57.21% | 95% | 0% | -56.0641 | 1313.433 | -2750 | -200 | -1636.567 | 40.91% | 59.12% | 95% | 0% | 2228 | -49
[5 empty] | 2019-07-11 | 46 | 4606 | 2057 | -49 | 0 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -56.0641 | 1122.3366 | -2750 | -200 | -1827.6634 | 45.69% | 59.12% | 95% | 0% | 2106 | -49
[5 empty] | 2019-07-11 | 47 | 4606.5 | 1915 | -50 | 0 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -57.2082 | 900.335 | -2750 | -200 | -2049.665 | 51.24% | 59.12% | 95% | 0% | 1965 | -50
[5 empty] | 2019-07-11 | 48 | 4607 | 1804 | -51 | 0 | 0 | 1855 | 785.2432 | 785.2432 | 785.2432 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -58.3524 | 726.8908 | -2750 | -200 | -2223.1092 | 55.58% | 59.12% | 95% | 0% | 1855 | -51
[5 empty] | 2019-07-12 | 1 | 4607.5 | 1704 | -51 | 0 | 0 | 1755 | 628.6068 | 628.6068 | 628.6068 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -58.3524 | 570.2544 | -2750 | -200 | -2379.7456 | 59.49% | 59.12% | 95% | 0% | 1755 | -51
[5 empty] | 2019-07-12 | 2 | 4608 | 1648 | -52 | 0 | 0 | 1700 | 542.4567 | 542.4567 | 542.4567 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -59.4966 | 482.9602 | -2750 | -200 | -2467.0398 | 61.68% | 59.12% | 95% | 0% | 1700 | -52
[5 empty] | 2019-07-12 | 3 | 4608.5 | 1600 | -53 | 0 | 0 | 1653 | 468.8376 | 468.8376 | 468.8376 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -60.6407 | 408.1969 | -2750 | -200 | -2541.8031 | 63.55% | 59.12% | 95% | 0% | 1653 | -53
[5 empty] | 2019-07-12 | 4 | 4609 | 1579 | -53 | 0 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -60.6407 | 375.3032 | -2750 | -200 | -2574.6968 | 64.37% | 59.11% | 95% | 0% | 1632 | -53
[5 empty] | 2019-07-12 | 5 | 4609.5 | 1535 | -55 | 0 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -62.9291 | 307.2276 | -2750 | -200 | -2642.7724 | 66.07% | 59.11% | 95% | 0% | 1590 | -55
[5 empty] | 2019-07-12 | 6 | 4610 | 1517 | -56 | 0 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -64.0732 | 279.4552 | -2750 | -200 | -2670.5448 | 66.76% | 59.11% | 95% | 0% | 1573 | -56
[5 empty] | 2019-07-12 | 7 | 4610.5 | 1510 | -58 | 0 | 0 | 1568 | 335.6966 | 335.6966 | 335.6966 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -66.3616 | 269.3351 | -2750 | -200 | -2680.6649 | 67.02% | 59.1% | 95% | 0% | 1568 | -58
[5 empty] | 2019-07-12 | 8 | 4611 | 1512 | -59 | 0 | 0 | 1571 | 340.3957 | 340.3957 | 340.3957 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -67.5057 | 272.89 | -2750 | -200 | -2677.11 | 66.93% | 59.09% | 95% | 0% | 1571 | -59
[5 empty] | 2019-07-12 | 9 | 4611.5 | 1509 | -60 | 0 | 0 | 1569 | 337.263 | 337.263 | 337.263 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -68.6499 | 268.6131 | -2750 | -200 | -2681.3869 | 67.03% | 59.08% | 95% | 0% | 1569 | -60
[5 empty] | 2019-07-12 | 10 | 4612 | 1503 | -61 | 0 | 0 | 1564 | 329.4312 | 329.4312 | 329.4312 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -69.7941 | 259.6371 | -2750 | -200 | -2690.3629 | 67.26% | 59.08% | 95% | 0% | 1564 | -61
[5 empty] | 2019-07-12 | 11 | 4612.5 | 1516 | -63 | 0 | 0 | 1579 | 352.9266 | 352.9266 | 352.9266 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -72.0824 | 280.8442 | -2750 | -200 | -2669.1558 | 66.73% | 59.08% | 95% | 0% | 1579 | -63
[5 empty] | 2019-07-12 | 12 | 4613 | 1552 | -76 | 0 | 0 | 1628 | 429.6785 | 429.6785 | 429.6785 | 1306.8425 | 780 | 200 | 2286.8425 | 57.17% | 95% | 0% | -86.9565 | 342.722 | -2750 | -200 | -2607.278 | 65.18% | 59.08% | 95% | 0% | 1628 | -76
[5 empty] | 2019-07-12 | 13 | 4613.5 | 1690 | -99 | 0 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -113.2723 | 568.5908 | -2750 | -200 | -2381.4092 | 59.54% | 59.07% | 95% | 0% | 1789 | -99
[5 empty] | 2019-07-12 | 14 | 4614 | 1808 | -139 | 1 | 0 | 1947 | 929.3487 | 929.3487 | 929.3487 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -159.0389 | 770.3098 | -3550 | -400 | -3179.6902 | 79.49% | 59.07% | 95% | 0% | 1947 | -139
[5 empty] | 2019-07-12 | 15 | 4614.5 | 1958 | -177 | 1 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -202.5172 | 1021.3081 | -3550 | -400 | -2928.6919 | 73.22% | 59.06% | 95% | 0% | 2135 | -177
[5 empty] | 2019-07-12 | 16 | 4615 | 2017 | -227 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -259.7254 | 1134.8335 | -3550 | -400 | -2815.1665 | 70.38% | 59.06% | 95% | 0% | 2244 | -227
[5 empty] | 2019-07-12 | 17 | 4615.5 | 2029 | -274 | 1 | 0 | 2303 | 1486.9744 | 1486.9744 | 1486.9744 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -313.5011 | 1173.4733 | -3550 | -400 | -2776.5267 | 69.41% | 59.06% | 95% | 0% | 2303 | -274
[5 empty] | 2019-07-12 | 18 | 4616 | 1950 | -342 | 1 | 0 | 2292 | 1469.7444 | 1469.7444 | 1469.7444 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -391.3043 | 1078.4401 | -3550 | -400 | -2871.5599 | 71.79% | 59.05% | 95% | 0% | 2292 | -342
[5 empty] | 2019-07-12 | 19 | 4616.5 | 1887 | -398 | 1 | 0 | 2285 | 1458.7799 | 1458.7799 | 1458.7799 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -455.3776 | 1003.4023 | -3550 | -400 | -2946.5977 | 73.66% | 59.05% | 95% | 0% | 2285 | -398
[5 empty] | 2019-07-12 | 20 | 4617 | 1800 | -449 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -513.73 | 888.6608 | -3550 | -400 | -3061.3392 | 76.53% | 59.05% | 95% | 0% | 2249 | -449
[5 empty] | 2019-07-12 | 21 | 4617.5 | 1734 | -486 | 1 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -556.0641 | 800.9021 | -3550 | -400 | -3149.0979 | 78.73% | 59.05% | 95% | 0% | 2220 | -486
[5 empty] | 2019-07-12 | 22 | 4618 | 1703 | -498 | 1 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -569.7941 | 757.4112 | -3550 | -400 | -3192.5888 | 79.81% | 59.04% | 95% | 0% | 2201 | -498
[5 empty] | 2019-07-12 | 23 | 4618.5 | 1688 | -505 | 1 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -577.8032 | 736.8712 | -3550 | -400 | -3213.1288 | 80.33% | 59.04% | 95% | 0% | 2193 | -505
[5 empty] | 2019-07-12 | 24 | 4619 | 1690 | -495 | 1 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -566.3616 | 735.7819 | -3550 | -400 | -3214.2181 | 80.36% | 59.04% | 95% | 0% | 2185 | -495
[5 empty] | 2019-07-12 | 25 | 4619.5 | 1614 | -534 | 1 | 0 | 2148 | 1244.188 | 1244.188 | 1244.188 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -610.984 | 633.204 | -3550 | -400 | -3316.796 | 82.92% | 59.04% | 95% | 0% | 2148 | -534
[5 empty] | 2019-07-12 | 26 | 4620 | 1572 | -583 | 1 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -667.0481 | 588.1045 | -3550 | -400 | -3361.8955 | 84.05% | 59.04% | 95% | 0% | 2155 | -583
[5 empty] | 2019-07-12 | 27 | 4620.5 | 1566 | -591 | 1 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 1305.2762 | 780 | 200 | 2285.2762 | 57.13% | 95% | 0% | -676.2014 | 582.0839 | -3550 | -400 | -3367.9161 | 84.2% | 59.03% | 95% | 0% | 2157 | -591
[5 empty] | 2019-07-12 | 28 | 4621 | 1534 | -610 | 1 | 0 | 2144 | 1237.9225 | 1237.9225 | 1237.9225 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -697.9405 | 539.982 | -3550 | -400 | -3410.018 | 85.25% | 59.03% | 95% | 0% | 2144 | -610
[5 empty] | 2019-07-12 | 29 | 4621.5 | 1534 | -577 | 1 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -660.1831 | 526.0494 | -3550 | -400 | -3423.9506 | 85.6% | 59.03% | 95% | 0% | 2111 | -577
[5 empty] | 2019-07-12 | 30 | 4622 | 1498 | -587 | 1 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -671.6247 | 473.8823 | -3550 | -400 | -3476.1177 | 86.9% | 59.02% | 95% | 0% | 2085 | -587
[5 empty] | 2019-07-12 | 31 | 4622.5 | 1499 | -566 | 1 | 0 | 2065 | 1114.1797 | 1114.1797 | 1114.1797 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -647.5973 | 466.5825 | -3550 | -400 | -3483.4175 | 87.09% | 59.02% | 95% | 0% | 2065 | -566
[5 empty] | 2019-07-12 | 32 | 4623 | 1525 | -545 | 1 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -623.5698 | 498.4417 | -3550 | -400 | -3451.5583 | 86.29% | 59.02% | 95% | 0% | 2070 | -545
[5 empty] | 2019-07-12 | 33 | 4623.5 | 1628 | -480 | 1 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -549.1991 | 632.3343 | -3550 | -400 | -3317.6657 | 82.94% | 59.01% | 95% | 0% | 2108 | -480
[5 empty] | 2019-07-12 | 34 | 4624 | 1731 | -430 | 1 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -491.9908 | 772.5599 | -3550 | -400 | -3177.4401 | 79.44% | 59% | 95% | 0% | 2161 | -430
[5 empty] | 2019-07-12 | 35 | 4624.5 | 1825 | -378 | 1 | 0 | 2203 | 1330.338 | 1330.338 | 1330.338 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -432.4943 | 897.8437 | -3550 | -400 | -3052.1563 | 76.3% | 59% | 95% | 0% | 2203 | -378
[5 empty] | 2019-07-12 | 36 | 4625 | 1908 | -329 | 1 | 0 | 2237 | 1383.5944 | 1383.5944 | 1383.5944 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -376.4302 | 1007.1642 | -3550 | -400 | -2942.8358 | 73.57% | 59% | 95% | 0% | 2237 | -329
[5 empty] | 2019-07-12 | 37 | 4625.5 | 1979 | -273 | 1 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -312.357 | 1094.7329 | -3550 | -400 | -2855.2671 | 71.38% | 59% | 95% | 0% | 2252 | -273
[5 empty] | 2019-07-12 | 38 | 4626 | 2028 | -230 | 1 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -263.1579 | 1153.3302 | -3550 | -400 | -2796.6698 | 69.92% | 59% | 95% | 0% | 2258 | -230
[5 empty] | 2019-07-12 | 39 | 4626.5 | 2076 | -186 | 1 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -212.8146 | 1209.9389 | -3550 | -400 | -2740.0611 | 68.5% | 58.99% | 95% | 0% | 2262 | -186
[5 empty] | 2019-07-12 | 40 | 4627 | 2095 | -147 | 1 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 1303.7098 | 780 | 200 | 2283.7098 | 57.09% | 95% | 0% | -168.1922 | 1223.234 | -3550 | -400 | -2726.766 | 68.17% | 58.99% | 95% | 0% | 2242 | -147
[5 empty] | 2019-07-12 | 41 | 4627.5 | 2129 | -104 | 1 | 0 | 2233 | 1377.3289 | 1377.3289 | 1377.3289 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -118.9931 | 1258.3358 | -3550 | -400 | -2691.6642 | 67.29% | 58.99% | 95% | 0% | 2233 | -104
[5 empty] | 2019-07-12 | 42 | 4628 | 2137 | -80 | 1 | 0 | 2217 | 1352.2671 | 1352.2671 | 1352.2671 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -91.5332 | 1260.7339 | -3550 | -400 | -2689.2661 | 67.23% | 58.98% | 95% | 0% | 2217 | -80
[5 empty] | 2019-07-12 | 43 | 4628.5 | 2122 | -67 | 1 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -76.659 | 1231.7499 | -3550 | -400 | -2718.2501 | 67.96% | 58.98% | 95% | 0% | 2189 | -67
[5 empty] | 2019-07-12 | 44 | 4629 | 2108 | -64 | 0 | 0 | 2172 | 1281.7807 | 1281.7807 | 1281.7807 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -73.2265 | 1208.5542 | -2750 | -200 | -1741.4458 | 43.54% | 58.98% | 95% | 0% | 2172 | -64
[5 empty] | 2019-07-12 | 45 | 4629.5 | 2062 | -63 | 0 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -72.0824 | 1136.0792 | -2750 | -200 | -1813.9208 | 45.35% | 58.98% | 95% | 0% | 2125 | -63
[5 empty] | 2019-07-12 | 46 | 4630 | 1980 | -62 | 0 | 0 | 2042 | 1078.1533 | 1078.1533 | 1078.1533 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -70.9382 | 1007.2151 | -2750 | -200 | -1942.7849 | 48.57% | 58.98% | 95% | 0% | 2042 | -62
[5 empty] | 2019-07-12 | 47 | 4630.5 | 1861 | -61 | 0 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -69.7941 | 820.3956 | -2750 | -200 | -2129.6044 | 53.24% | 58.98% | 95% | 0% | 1922 | -61
[5 empty] | 2019-07-12 | 48 | 4631 | 1751 | -60 | 0 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -68.6499 | 647.6733 | -2750 | -200 | -2302.3267 | 57.56% | 58.98% | 95% | 0% | 1811 | -60
[5 empty] | 2019-07-13 | 1 | 4631.5 | 1661 | -55 | 0 | 0 | 1716 | 567.5185 | 567.5185 | 567.5185 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -62.9291 | 504.5895 | -2750 | -200 | -2445.4105 | 61.14% | 58.98% | 95% | 0% | 1716 | -55
[5 empty] | 2019-07-13 | 2 | 4632 | 1609 | -51 | 0 | 0 | 1660 | 479.8021 | 479.8021 | 479.8021 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -58.3524 | 421.4497 | -2750 | -200 | -2528.5503 | 63.21% | 58.98% | 95% | 0% | 1660 | -51
[5 empty] | 2019-07-13 | 3 | 4632.5 | 1560 | -50 | 0 | 0 | 1610 | 401.4839 | 401.4839 | 401.4839 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -57.2082 | 344.2757 | -2750 | -200 | -2605.7243 | 65.14% | 58.97% | 95% | 0% | 1610 | -50
[5 empty] | 2019-07-13 | 4 | 4633 | 1532 | -49 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -56.0641 | 299.9953 | -2750 | -200 | -2650.0047 | 66.25% | 58.97% | 95% | 0% | 1581 | -49
[5 empty] | 2019-07-13 | 5 | 4633.5 | 1501 | -49 | 0 | 0 | 1550 | 307.5021 | 307.5021 | 307.5021 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -56.0641 | 251.438 | -2750 | -200 | -2698.562 | 67.46% | 58.97% | 95% | 0% | 1550 | -49
[5 empty] | 2019-07-13 | 6 | 4634 | 1478 | -49 | 0 | 0 | 1527 | 271.4757 | 271.4757 | 271.4757 | 1302.1434 | 780 | 200 | 2282.1434 | 57.05% | 95% | 0% | -56.0641 | 215.4116 | -2750 | -200 | -2734.5884 | 68.36% | 58.97% | 95% | 0% | 1527 | -49
[5 empty] | 2019-07-13 | 7 | 4634.5 | 1448 | -49 | 0 | 0 | 1497 | 224.4847 | 224.4847 | 224.4847 | 1300.5771 | 780 | 200 | 2280.5771 | 57.01% | 95% | 0% | -56.0641 | 168.4207 | -2750 | -200 | -2781.5793 | 69.54% | 58.97% | 95% | 0% | 1497 | -49
[5 empty] | 2019-07-13 | 8 | 4635 | 1439 | -50 | 0 | 0 | 1489 | 211.9538 | 211.9538 | 211.9538 | 1300.5771 | 780 | 200 | 2280.5771 | 57.01% | 95% | 0% | -57.2082 | 154.7456 | -2750 | -200 | -2795.2544 | 69.88% | 58.97% | 95% | 0% | 1489 | -50
[5 empty] | 2019-07-13 | 9 | 4635.5 | 1430 | -49 | 0 | 0 | 1479 | 196.2902 | 196.2902 | 196.2902 | 1300.5771 | 780 | 200 | 2280.5771 | 57.01% | 95% | 0% | -56.0641 | 140.2261 | -2750 | -200 | -2809.7739 | 70.24% | 58.97% | 95% | 0% | 1479 | -49
[5 empty] | 2019-07-13 | 10 | 4636 | 1403 | -48 | 0 | 0 | 1451 | 152.432 | 152.432 | 152.432 | 1300.5771 | 780 | 200 | 2280.5771 | 57.01% | 95% | 0% | -54.9199 | 97.5121 | -2750 | -200 | -2852.4879 | 71.31% | 58.96% | 95% | 0% | 1451 | -48
[5 empty] | 2019-07-13 | 11 | 4636.5 | 1408 | -49 | 0 | 0 | 1457 | 161.8302 | 161.8302 | 161.8302 | 1300.5771 | 780 | 200 | 2280.5771 | 57.01% | 95% | 0% | -56.0641 | 105.7661 | -2750 | -200 | -2844.2339 | 71.11% | 58.96% | 95% | 0% | 1457 | -49
[5 empty] | 2019-07-13 | 12 | 4637 | 1414 | -57 | 0 | 0 | 1471 | 183.7593 | 183.7593 | 183.7593 | 1300.5771 | 780 | 200 | 2280.5771 | 57.01% | 95% | 0% | -65.2174 | 118.5419 | -2750 | -200 | -2831.4581 | 70.79% | 58.95% | 95% | 0% | 1471 | -57
[5 empty] | 2019-07-13 | 13 | 4637.5 | 1473 | -73 | 0 | 0 | 1546 | 301.2366 | 301.2366 | 301.2366 | 1300.5771 | 780 | 200 | 2280.5771 | 57.01% | 95% | 0% | -83.524 | 217.7126 | -2750 | -200 | -2732.2874 | 68.31% | 58.95% | 95% | 0% | 1546 | -73
[5 empty] | 2019-07-13 | 14 | 4638 | 1526 | -88 | 1 | 0 | 1614 | 407.7494 | 407.7494 | 407.7494 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -100.6865 | 307.0629 | -3550 | -400 | -3642.9371 | 91.07% | 58.94% | 95% | 0% | 1614 | -88
[5 empty] | 2019-07-13 | 15 | 4638.5 | 1603 | -117 | 1 | 0 | 1720 | 573.784 | 573.784 | 573.784 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -133.8673 | 439.9167 | -3550 | -400 | -3510.0833 | 87.75% | 58.94% | 95% | 0% | 1720 | -117
[5 empty] | 2019-07-13 | 16 | 4639 | 1643 | -155 | 1 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -177.3455 | 518.6149 | -3550 | -400 | -3431.3851 | 85.78% | 58.94% | 95% | 0% | 1798 | -155
[5 empty] | 2019-07-13 | 17 | 4639.5 | 1702 | -189 | 1 | 0 | 1891 | 841.6323 | 841.6323 | 841.6323 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -216.2471 | 625.3852 | -3550 | -400 | -3324.6148 | 83.12% | 58.93% | 95% | 0% | 1891 | -189
[5 empty] | 2019-07-13 | 18 | 4640 | 1694 | -231 | 1 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -264.3021 | 630.5866 | -3550 | -400 | -3319.4134 | 82.99% | 58.93% | 95% | 0% | 1925 | -231
[5 empty] | 2019-07-13 | 19 | 4640.5 | 1721 | -255 | 1 | 0 | 1976 | 974.7733 | 974.7733 | 974.7733 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -291.762 | 683.0113 | -3550 | -400 | -3266.9887 | 81.67% | 58.92% | 95% | 0% | 1976 | -255
[5 empty] | 2019-07-13 | 20 | 4641 | 1723 | -287 | 1 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -328.3753 | 699.6544 | -3550 | -400 | -3250.3456 | 81.26% | 58.92% | 95% | 0% | 2010 | -287
[5 empty] | 2019-07-13 | 21 | 4641.5 | 1721 | -308 | 1 | 0 | 2029 | 1057.7906 | 1057.7906 | 1057.7906 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -352.4027 | 705.3879 | -3550 | -400 | -3244.6121 | 81.12% | 58.92% | 95% | 0% | 2029 | -308
[5 empty] | 2019-07-13 | 22 | 4642 | 1740 | -325 | 1 | 0 | 2065 | 1114.1797 | 1114.1797 | 1114.1797 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -371.8535 | 742.3262 | -3550 | -400 | -3207.6738 | 80.19% | 58.92% | 95% | 0% | 2065 | -325
[5 empty] | 2019-07-13 | 23 | 4642.5 | 1698 | -338 | 1 | 0 | 2036 | 1068.7552 | 1068.7552 | 1068.7552 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -386.7277 | 682.0275 | -3550 | -400 | -3267.9725 | 81.7% | 58.92% | 95% | 0% | 2036 | -338
[5 empty] | 2019-07-13 | 24 | 4643 | 1679 | -336 | 1 | 0 | 2015 | 1035.8615 | 1035.8615 | 1035.8615 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -384.4394 | 651.4221 | -3550 | -400 | -3298.5779 | 82.46% | 58.91% | 95% | 0% | 2015 | -336
[5 empty] | 2019-07-13 | 25 | 4643.5 | 1644 | -353 | 1 | 0 | 1997 | 1007.6669 | 1007.6669 | 1007.6669 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -403.8902 | 603.7768 | -3550 | -400 | -3346.2232 | 83.66% | 58.91% | 95% | 0% | 1997 | -353
[5 empty] | 2019-07-13 | 26 | 4644 | 1590 | -395 | 1 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -451.9451 | 536.9255 | -3550 | -400 | -3413.0745 | 85.33% | 58.91% | 95% | 0% | 1985 | -395
[5 empty] | 2019-07-13 | 27 | 4644.5 | 1567 | -407 | 1 | 0 | 1974 | 971.6406 | 971.6406 | 971.6406 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -465.6751 | 505.9655 | -3550 | -400 | -3444.0345 | 86.1% | 58.9% | 95% | 0% | 1974 | -407
[5 empty] | 2019-07-13 | 28 | 4645 | 1539 | -409 | 1 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 1299.0107 | 780 | 200 | 2279.0107 | 56.98% | 95% | 0% | -467.9634 | 462.9517 | -3550 | -400 | -3487.0483 | 87.18% | 58.9% | 95% | 0% | 1948 | -409
[5 empty] | 2019-07-13 | 29 | 4645.5 | 1472 | -447 | 1 | 0 | 1919 | 885.4905 | 885.4905 | 885.4905 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -511.4416 | 374.0489 | -3550 | -400 | -3575.9511 | 89.4% | 58.9% | 95% | 0% | 1919 | -447
[5 empty] | 2019-07-13 | 30 | 4646 | 1462 | -418 | 1 | 0 | 1880 | 824.4023 | 824.4023 | 824.4023 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -478.2609 | 346.1414 | -3550 | -400 | -3603.8586 | 90.1% | 58.89% | 95% | 0% | 1880 | -418
[5 empty] | 2019-07-13 | 31 | 4646.5 | 1469 | -395 | 1 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -451.9451 | 347.3954 | -3550 | -400 | -3602.6046 | 90.07% | 58.89% | 95% | 0% | 1864 | -395
[5 empty] | 2019-07-13 | 32 | 4647 | 1468 | -406 | 1 | 0 | 1874 | 815.0041 | 815.0041 | 815.0041 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -464.5309 | 350.4732 | -3550 | -400 | -3599.5268 | 89.99% | 58.89% | 95% | 0% | 1874 | -406
[5 empty] | 2019-07-13 | 33 | 4647.5 | 1541 | -366 | 1 | 0 | 1907 | 866.6941 | 866.6941 | 866.6941 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -418.7643 | 447.9298 | -3550 | -400 | -3502.0702 | 87.55% | 58.88% | 95% | 0% | 1907 | -366
[5 empty] | 2019-07-13 | 34 | 4648 | 1640 | -324 | 1 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -370.7094 | 585.2675 | -3550 | -400 | -3364.7325 | 84.12% | 58.88% | 95% | 0% | 1964 | -324
[5 empty] | 2019-07-13 | 35 | 4648.5 | 1744 | -296 | 1 | 0 | 2040 | 1075.0206 | 1075.0206 | 1075.0206 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -338.6728 | 736.3478 | -3550 | -400 | -3213.6522 | 80.34% | 58.88% | 95% | 0% | 2040 | -296
[5 empty] | 2019-07-13 | 36 | 4649 | 1796 | -267 | 1 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -305.492 | 805.555 | -3550 | -400 | -3144.445 | 78.61% | 58.87% | 95% | 0% | 2063 | -267
[5 empty] | 2019-07-13 | 37 | 4649.5 | 1857 | -229 | 1 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -262.0137 | 885.0596 | -3550 | -400 | -3064.9404 | 76.62% | 58.87% | 95% | 0% | 2086 | -229
[5 empty] | 2019-07-13 | 38 | 4650 | 1901 | -195 | 1 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -223.1121 | 939.6249 | -3550 | -400 | -3010.3751 | 75.26% | 58.87% | 95% | 0% | 2096 | -195
[5 empty] | 2019-07-13 | 39 | 4650.5 | 1945 | -155 | 1 | 0 | 2100 | 1169.0025 | 1169.0025 | 1169.0025 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -177.3455 | 991.6569 | -3550 | -400 | -2958.3431 | 73.96% | 58.87% | 95% | 0% | 2100 | -155
[5 empty] | 2019-07-13 | 40 | 4651 | 1971 | -124 | 1 | 0 | 2095 | 1161.1707 | 1161.1707 | 1161.1707 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -141.8764 | 1019.2942 | -3550 | -400 | -2930.7058 | 73.27% | 58.87% | 95% | 0% | 2095 | -124
[5 empty] | 2019-07-13 | 41 | 4651.5 | 1980 | -93 | 1 | 0 | 2073 | 1126.7106 | 1126.7106 | 1126.7106 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -106.4073 | 1020.3033 | -3550 | -400 | -2929.6967 | 73.24% | 58.86% | 95% | 0% | 2073 | -93
[5 empty] | 2019-07-13 | 42 | 4652 | 1980 | -68 | 1 | 0 | 2048 | 1087.5515 | 1087.5515 | 1087.5515 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -77.8032 | 1009.7483 | -3550 | -400 | -2940.2517 | 73.51% | 58.86% | 95% | 0% | 2048 | -68
[5 empty] | 2019-07-13 | 43 | 4652.5 | 1984 | -56 | 1 | 0 | 2040 | 1075.0206 | 1075.0206 | 1075.0206 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -64.0732 | 1010.9474 | -3550 | -400 | -2939.0526 | 73.48% | 58.85% | 95% | 0% | 2040 | -56
[5 empty] | 2019-07-13 | 44 | 4653 | 1980 | -52 | 1 | 0 | 2032 | 1062.4897 | 1062.4897 | 1062.4897 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -59.4966 | 1002.9931 | -3550 | -400 | -2947.0069 | 73.68% | 58.85% | 95% | 0% | 2032 | -52
[5 empty] | 2019-07-13 | 45 | 4653.5 | 1965 | -50 | 1 | 0 | 2015 | 1035.8615 | 1035.8615 | 1035.8615 | 1297.4444 | 780 | 200 | 2277.4444 | 56.94% | 95% | 0% | -57.2082 | 978.6533 | -3550 | -400 | -2971.3467 | 74.28% | 58.85% | 95% | 0% | 2015 | -50
[5 empty] | 2019-07-13 | 46 | 4654 | 1891 | -47 | 0 | 0 | 1938 | 915.2514 | 915.2514 | 915.2514 | 1295.878 | 780 | 200 | 2275.878 | 56.9% | 95% | 0% | -53.7757 | 861.4757 | -2750 | -200 | -2088.5243 | 52.21% | 58.84% | 95% | 0% | 1938 | -47
[5 empty] | 2019-07-13 | 47 | 4654.5 | 1799 | -46 | 0 | 0 | 1845 | 769.5796 | 769.5796 | 769.5796 | 1295.878 | 780 | 200 | 2275.878 | 56.9% | 95% | 0% | -52.6316 | 716.948 | -2750 | -200 | -2233.052 | 55.83% | 58.84% | 95% | 0% | 1845 | -46
[5 empty] | 2019-07-13 | 48 | 4655 | 1720 | -45 | 0 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 1295.878 | 780 | 200 | 2275.878 | 56.9% | 95% | 0% | -51.4874 | 592.783 | -2750 | -200 | -2357.217 | 58.93% | 58.83% | 95% | 0% | 1765 | -45
[5 empty] | 2019-07-14 | 1 | 4655.5 | 1642 | -43 | 0 | 0 | 1685 | 518.9613 | 518.9613 | 518.9613 | 1295.878 | 780 | 200 | 2275.878 | 56.9% | 95% | 0% | -49.1991 | 469.7622 | -2750 | -200 | -2480.2378 | 62.01% | 58.83% | 95% | 0% | 1685 | -43
[5 empty] | 2019-07-14 | 2 | 4656 | 1577 | -42 | 1 | 0 | 1619 | 415.5812 | 415.5812 | 415.5812 | 1295.878 | 780 | 200 | 2275.878 | 56.9% | 95% | 0% | -48.0549 | 367.5263 | -3550 | -400 | -3582.4737 | 89.56% | 58.83% | 95% | 0% | 1619 | -42
[5 empty] | 2019-07-14 | 3 | 4656.5 | 1530 | -40 | 1 | 0 | 1570 | 338.8293 | 338.8293 | 338.8293 | 1295.878 | 780 | 200 | 2275.878 | 56.9% | 95% | 0% | -45.7666 | 293.0628 | -3550 | -400 | -3656.9372 | 91.42% | 58.83% | 95% | 0% | 1570 | -40
[5 empty] | 2019-07-14 | 4 | 4657 | 1506 | -38 | 1 | 0 | 1544 | 298.1039 | 298.1039 | 298.1039 | 1295.878 | 780 | 200 | 2275.878 | 56.9% | 95% | 0% | -43.4783 | 254.6256 | -3550 | -400 | -3695.3744 | 92.38% | 58.83% | 95% | 0% | 1544 | -38
[5 empty] | 2019-07-14 | 5 | 4657.5 | 1472 | -37 | 1 | 0 | 1509 | 243.2811 | 243.2811 | 243.2811 | 1295.878 | 780 | 200 | 2275.878 | 56.9% | 95% | 0% | -42.3341 | 200.947 | -3550 | -400 | -3749.053 | 93.73% | 58.82% | 95% | 0% | 1509 | -37
[5 empty] | 2019-07-14 | 6 | 4658 | 1439 | -36 | 1 | 0 | 1475 | 190.0247 | 190.0247 | 190.0247 | 1295.878 | 780 | 200 | 2275.878 | 56.9% | 95% | 0% | -41.1899 | 148.8348 | -3550 | -400 | -3801.1652 | 95.03% | 58.82% | 95% | 0% | 1475 | -36
[5 empty] | 2019-07-14 | 7 | 4658.5 | 1411 | -36 | 1 | 0 | 1447 | 146.1665 | 146.1665 | 146.1665 | 1295.878 | 780 | 200 | 2275.878 | 56.9% | 95% | 0% | -41.1899 | 104.9766 | -3550 | -400 | -3845.0234 | 96.13% | 58.82% | 95% | 0% | 1447 | -36
[5 empty] | 2019-07-14 | 8 | 4659 | 1409 | -36 | 1 | 0 | 1445 | 143.0338 | 143.0338 | 143.0338 | 1295.878 | 780 | 200 | 2275.878 | 56.9% | 95% | 0% | -41.1899 | 101.8439 | -3550 | -400 | -3848.1561 | 96.2% | 58.82% | 95% | 0% | 1445 | -36
[5 empty] | 2019-07-14 | 9 | 4659.5 | 1402 | -36 | 1 | 0 | 1438 | 132.0692 | 132.0692 | 132.0692 | 1294.3116 | 780 | 200 | 2274.3116 | 56.86% | 95% | 0% | -41.1899 | 90.8793 | -3550 | -400 | -3859.1207 | 96.48% | 58.81% | 95% | 0% | 1438 | -36
[5 empty] | 2019-07-14 | 10 | 4660 | 1380 | -36 | 1 | 0 | 1416 | 97.6092 | 97.6092 | 97.6092 | 1294.3116 | 780 | 200 | 2274.3116 | 56.86% | 95% | 0% | -41.1899 | 56.4193 | -3550 | -400 | -3893.5807 | 97.34% | 58.81% | 95% | 0% | 1416 | -36
[5 empty] | 2019-07-14 | 11 | 4660.5 | 1367 | -37 | 1 | 0 | 1404 | 78.8129 | 78.8129 | 78.8129 | 1294.3116 | 780 | 200 | 2274.3116 | 56.86% | 95% | 0% | -42.3341 | 36.4788 | -3550 | -400 | -3913.5212 | 97.84% | 58.8% | 95% | 0% | 1404 | -37
[5 empty] | 2019-07-14 | 12 | 4661 | 1366 | -43 | 1 | 0 | 1409 | 86.6447 | 86.6447 | 86.6447 | 1294.3116 | 780 | 200 | 2274.3116 | 56.86% | 95% | 0% | -49.1991 | 37.4456 | -3550 | -400 | -3912.5544 | 97.81% | 58.8% | 95% | 0% | 1409 | -43
[5 empty] | 2019-07-14 | 13 | 4661.5 | 1378 | -60 | 1 | 0 | 1438 | 132.0692 | 132.0692 | 132.0692 | 1294.3116 | 780 | 200 | 2274.3116 | 56.86% | 95% | 0% | -68.6499 | 63.4194 | -3550 | -400 | -3886.5806 | 97.16% | 58.79% | 95% | 0% | 1438 | -60
[5 empty] | 2019-07-14 | 14 | 4662 | 1384 | -86 | 1 | 0 | 1470 | 182.1929 | 182.1929 | 182.1929 | 1294.3116 | 780 | 200 | 2274.3116 | 56.86% | 95% | 0% | -98.3982 | 83.7947 | -3550 | -400 | -3866.2053 | 96.66% | 58.79% | 95% | 0% | 1470 | -86
[5 empty] | 2019-07-14 | 15 | 4662.5 | 1410 | -121 | 1 | 0 | 1531 | 277.7411 | 277.7411 | 277.7411 | 1294.3116 | 780 | 200 | 2274.3116 | 56.86% | 95% | 0% | -138.4439 | 139.2972 | -3550 | -400 | -3810.7028 | 95.27% | 58.78% | 95% | 0% | 1531 | -121
[5 empty] | 2019-07-14 | 16 | 4663 | 1423 | -162 | 1 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 1294.3116 | 780 | 200 | 2274.3116 | 56.86% | 95% | 0% | -185.3547 | 176.9701 | -3550 | -400 | -3773.0299 | 94.33% | 58.77% | 95% | 0% | 1585 | -162
[5 empty] | 2019-07-14 | 17 | 4663.5 | 1476 | -199 | 1 | 0 | 1675 | 503.2976 | 503.2976 | 503.2976 | 1294.3116 | 780 | 200 | 2274.3116 | 56.86% | 95% | 0% | -227.6888 | 275.6088 | -3550 | -400 | -3674.3912 | 91.86% | 58.77% | 95% | 0% | 1675 | -199
[5 empty] | 2019-07-14 | 18 | 4664 | 1495 | -249 | 1 | 0 | 1744 | 611.3768 | 611.3768 | 611.3768 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -284.897 | 326.4797 | -3550 | -400 | -3623.5203 | 90.59% | 58.77% | 95% | 0% | 1744 | -249
[5 empty] | 2019-07-14 | 19 | 4664.5 | 1515 | -285 | 1 | 0 | 1800 | 699.0932 | 699.0932 | 699.0932 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -326.087 | 373.0062 | -3550 | -400 | -3576.9938 | 89.42% | 58.76% | 95% | 0% | 1800 | -285
[5 empty] | 2019-07-14 | 20 | 4665 | 1519 | -329 | 1 | 0 | 1848 | 774.2786 | 774.2786 | 774.2786 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -376.4302 | 397.8484 | -3550 | -400 | -3552.1516 | 88.8% | 58.76% | 95% | 0% | 1848 | -329
[5 empty] | 2019-07-14 | 21 | 4665.5 | 1524 | -370 | 1 | 0 | 1894 | 846.3314 | 846.3314 | 846.3314 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -423.341 | 422.9904 | -3550 | -400 | -3527.0096 | 88.18% | 58.76% | 95% | 0% | 1894 | -370
[5 empty] | 2019-07-14 | 22 | 4666 | 1516 | -399 | 1 | 0 | 1915 | 879.2251 | 879.2251 | 879.2251 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -456.5217 | 422.7033 | -3550 | -400 | -3527.2967 | 88.18% | 58.75% | 95% | 0% | 1915 | -399
[5 empty] | 2019-07-14 | 23 | 4666.5 | 1533 | -399 | 1 | 0 | 1932 | 905.8533 | 905.8533 | 905.8533 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -456.5217 | 449.3315 | -3550 | -400 | -3500.6685 | 87.52% | 58.75% | 95% | 0% | 1932 | -399
[5 empty] | 2019-07-14 | 24 | 4667 | 1548 | -407 | 1 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -465.6751 | 476.2046 | -3550 | -400 | -3473.7954 | 86.84% | 58.74% | 95% | 0% | 1955 | -407
[5 empty] | 2019-07-14 | 25 | 4667.5 | 1549 | -407 | 1 | 0 | 1956 | 943.446 | 943.446 | 943.446 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -465.6751 | 477.7709 | -3550 | -400 | -3472.2291 | 86.81% | 58.74% | 95% | 0% | 1956 | -407
[5 empty] | 2019-07-14 | 26 | 4668 | 1549 | -393 | 1 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -449.6568 | 471.8601 | -3550 | -400 | -3478.1399 | 86.95% | 58.73% | 95% | 0% | 1942 | -393
[5 empty] | 2019-07-14 | 27 | 4668.5 | 1555 | -366 | 1 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -418.7643 | 469.8589 | -3550 | -400 | -3480.1411 | 87% | 58.73% | 95% | 0% | 1921 | -366
[5 empty] | 2019-07-14 | 28 | 4669 | 1483 | -401 | 1 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -458.8101 | 371.8577 | -3550 | -400 | -3578.1423 | 89.45% | 58.73% | 95% | 0% | 1884 | -401
[5 empty] | 2019-07-14 | 29 | 4669.5 | 1384 | -457 | 1 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -522.8833 | 240.4308 | -3550 | -400 | -3709.5692 | 92.74% | 58.73% | 95% | 0% | 1841 | -457
[5 empty] | 2019-07-14 | 30 | 4670 | 1387 | -430 | 1 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -491.9908 | 233.7305 | -3550 | -400 | -3716.2695 | 92.91% | 58.73% | 95% | 0% | 1817 | -430
[5 empty] | 2019-07-14 | 31 | 4670.5 | 1406 | -427 | 1 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -488.5584 | 262.2248 | -3550 | -400 | -3687.7752 | 92.19% | 58.72% | 95% | 0% | 1833 | -427
[5 empty] | 2019-07-14 | 32 | 4671 | 1445 | -407 | 1 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -465.6751 | 314.869 | -3550 | -400 | -3635.131 | 90.88% | 58.72% | 95% | 0% | 1852 | -407
[5 empty] | 2019-07-14 | 33 | 4671.5 | 1484 | -407 | 1 | 0 | 1891 | 841.6323 | 841.6323 | 841.6323 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -465.6751 | 375.9573 | -3550 | -400 | -3574.0427 | 89.35% | 58.72% | 95% | 0% | 1891 | -407
[5 empty] | 2019-07-14 | 34 | 4672 | 1586 | -373 | 1 | 0 | 1959 | 948.1451 | 948.1451 | 948.1451 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -426.7735 | 521.3716 | -3550 | -400 | -3428.6284 | 85.72% | 58.72% | 95% | 0% | 1959 | -373
[5 empty] | 2019-07-14 | 35 | 4672.5 | 1684 | -325 | 1 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 1292.7453 | 780 | 200 | 2272.7453 | 56.82% | 95% | 0% | -371.8535 | 654.6098 | -3550 | -400 | -3295.3902 | 82.38% | 58.72% | 95% | 0% | 2009 | -325
[5 empty] | 2019-07-14 | 36 | 4673 | 1761 | -275 | 1 | 0 | 2036 | 1068.7552 | 1068.7552 | 1068.7552 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -314.6453 | 754.1098 | -3550 | -400 | -3195.8902 | 79.9% | 58.72% | 95% | 0% | 2036 | -275
[5 empty] | 2019-07-14 | 37 | 4673.5 | 1809 | -244 | 1 | 0 | 2053 | 1095.3833 | 1095.3833 | 1095.3833 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -279.1762 | 816.2071 | -3550 | -400 | -3133.7929 | 78.34% | 58.72% | 95% | 0% | 2053 | -244
[5 empty] | 2019-07-14 | 38 | 4674 | 1869 | -197 | 1 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -225.4005 | 890.3456 | -3550 | -400 | -3059.6544 | 76.49% | 58.7% | 95% | 0% | 2066 | -197
[5 empty] | 2019-07-14 | 39 | 4674.5 | 1941 | -153 | 1 | 0 | 2094 | 1159.6043 | 1159.6043 | 1159.6043 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -175.0572 | 984.5471 | -3550 | -400 | -2965.4529 | 74.14% | 58.7% | 95% | 0% | 2094 | -153
[5 empty] | 2019-07-14 | 40 | 4675 | 2029 | -115 | 1 | 0 | 2144 | 1237.9225 | 1237.9225 | 1237.9225 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -131.5789 | 1106.3436 | -3550 | -400 | -2843.6564 | 71.09% | 58.7% | 95% | 0% | 2144 | -115
[5 empty] | 2019-07-14 | 41 | 4675.5 | 2075 | -83 | 1 | 0 | 2158 | 1259.8516 | 1259.8516 | 1259.8516 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -94.9657 | 1164.8859 | -3550 | -400 | -2785.1141 | 69.63% | 58.7% | 95% | 0% | 2158 | -83
[5 empty] | 2019-07-14 | 42 | 4676 | 2076 | -54 | 1 | 0 | 2130 | 1215.9934 | 1215.9934 | 1215.9934 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -61.7849 | 1154.2085 | -3550 | -400 | -2795.7915 | 69.89% | 58.69% | 95% | 0% | 2130 | -54
[5 empty] | 2019-07-14 | 43 | 4676.5 | 2073 | -42 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -48.0549 | 1144.443 | -3550 | -400 | -2805.557 | 70.14% | 58.69% | 95% | 0% | 2115 | -42
[5 empty] | 2019-07-14 | 44 | 4677 | 2052 | -40 | 1 | 0 | 2092 | 1156.4716 | 1156.4716 | 1156.4716 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -45.7666 | 1110.705 | -3550 | -400 | -2839.295 | 70.98% | 58.69% | 95% | 0% | 2092 | -40
[5 empty] | 2019-07-14 | 45 | 4677.5 | 2024 | -39 | 0 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -44.6224 | 1066.4246 | -2750 | -200 | -1883.5754 | 47.09% | 58.68% | 95% | 0% | 2063 | -39
[5 empty] | 2019-07-14 | 46 | 4678 | 1938 | -39 | 0 | 0 | 1977 | 976.3397 | 976.3397 | 976.3397 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -44.6224 | 931.7172 | -2750 | -200 | -2018.2828 | 50.46% | 58.68% | 95% | 0% | 1977 | -39
[5 empty] | 2019-07-14 | 47 | 4678.5 | 1809 | -38 | 0 | 0 | 1847 | 772.7123 | 772.7123 | 772.7123 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -43.4783 | 729.234 | -2750 | -200 | -2220.766 | 55.52% | 58.68% | 95% | 0% | 1847 | -38
[5 empty] | 2019-07-14 | 48 | 4679 | 1698 | -38 | 0 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -43.4783 | 555.3676 | -2750 | -200 | -2394.6324 | 59.87% | 58.68% | 95% | 0% | 1736 | -38
[5 empty] | 2019-07-15 | 1 | 4679.5 | 1614 | -38 | 0 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -43.4783 | 423.793 | -2750 | -200 | -2526.207 | 63.16% | 58.68% | 95% | 0% | 1652 | -38
[5 empty] | 2019-07-15 | 2 | 4680 | 1558 | -37 | 0 | 0 | 1595 | 377.9885 | 377.9885 | 377.9885 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -42.3341 | 335.6544 | -2750 | -200 | -2614.3456 | 65.36% | 58.68% | 95% | 0% | 1595 | -37
[5 empty] | 2019-07-15 | 3 | 4680.5 | 1527 | -36 | 0 | 0 | 1563 | 327.8648 | 327.8648 | 327.8648 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -41.1899 | 286.6749 | -2750 | -200 | -2663.3251 | 66.58% | 58.68% | 95% | 0% | 1563 | -36
[5 empty] | 2019-07-15 | 4 | 4681 | 1512 | -35 | 0 | 0 | 1547 | 302.803 | 302.803 | 302.803 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -40.0458 | 262.7572 | -2750 | -200 | -2687.2428 | 67.18% | 58.67% | 95% | 0% | 1547 | -35
[5 empty] | 2019-07-15 | 5 | 4681.5 | 1492 | -35 | 0 | 0 | 1527 | 271.4757 | 271.4757 | 271.4757 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -40.0458 | 231.4299 | -2750 | -200 | -2718.5701 | 67.96% | 58.67% | 95% | 0% | 1527 | -35
[5 empty] | 2019-07-15 | 6 | 4682 | 1468 | -34 | 0 | 0 | 1502 | 232.3166 | 232.3166 | 232.3166 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -38.9016 | 193.415 | -2750 | -200 | -2756.585 | 68.91% | 58.67% | 95% | 0% | 1502 | -34
[5 empty] | 2019-07-15 | 7 | 4682.5 | 1458 | -33 | 0 | 0 | 1491 | 215.0866 | 215.0866 | 215.0866 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -37.7574 | 177.3291 | -2750 | -200 | -2772.6709 | 69.32% | 58.67% | 95% | 0% | 1491 | -33
[5 empty] | 2019-07-15 | 8 | 4683 | 1460 | -32 | 0 | 0 | 1492 | 216.6529 | 216.6529 | 216.6529 | 1291.1789 | 780 | 200 | 2271.1789 | 56.78% | 95% | 0% | -36.6133 | 180.0397 | -2750 | -200 | -2769.9603 | 69.25% | 58.66% | 95% | 0% | 1492 | -32
[5 empty] | 2019-07-15 | 9 | 4683.5 | 1464 | -33 | 0 | 0 | 1497 | 224.4847 | 224.4847 | 224.4847 | 1289.6125 | 780 | 200 | 2269.6125 | 56.74% | 95% | 0% | -37.7574 | 186.7273 | -2750 | -200 | -2763.2727 | 69.08% | 58.66% | 95% | 0% | 1497 | -33
[5 empty] | 2019-07-15 | 10 | 4684 | 1457 | -33 | 0 | 0 | 1490 | 213.5202 | 213.5202 | 213.5202 | 1289.6125 | 780 | 200 | 2269.6125 | 56.74% | 95% | 0% | -37.7574 | 175.7628 | -2750 | -200 | -2774.2372 | 69.36% | 58.66% | 95% | 0% | 1490 | -33
[5 empty] | 2019-07-15 | 11 | 4684.5 | 1496 | -32 | 0 | 0 | 1528 | 273.042 | 273.042 | 273.042 | 1289.6125 | 780 | 200 | 2269.6125 | 56.74% | 95% | 0% | -36.6133 | 236.4288 | -2750 | -200 | -2713.5712 | 67.84% | 58.65% | 95% | 0% | 1528 | -32
[5 empty] | 2019-07-15 | 12 | 4685 | 1569 | -40 | 0 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 1289.6125 | 780 | 200 | 2269.6125 | 56.74% | 95% | 0% | -45.7666 | 354.151 | -2750 | -200 | -2595.849 | 64.9% | 58.65% | 95% | 0% | 1609 | -40
[5 empty] | 2019-07-15 | 13 | 4685.5 | 1729 | -61 | 0 | 0 | 1790 | 683.4295 | 683.4295 | 683.4295 | 1289.6125 | 780 | 200 | 2269.6125 | 56.74% | 95% | 0% | -69.7941 | 613.6355 | -2750 | -200 | -2336.3645 | 58.41% | 58.64% | 95% | 0% | 1790 | -61
[5 empty] | 2019-07-15 | 14 | 4686 | 1868 | -90 | 1 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 1289.6125 | 780 | 200 | 2269.6125 | 56.74% | 95% | 0% | -102.9748 | 843.6039 | -3550 | -400 | -3106.3961 | 77.66% | 58.64% | 95% | 0% | 1958 | -90
[5 empty] | 2019-07-15 | 15 | 4686.5 | 2024 | -124 | 1 | 0 | 2148 | 1244.188 | 1244.188 | 1244.188 | 1289.6125 | 780 | 200 | 2269.6125 | 56.74% | 95% | 0% | -141.8764 | 1102.3115 | -3550 | -400 | -2847.6885 | 71.19% | 58.64% | 95% | 0% | 2148 | -124
[5 empty] | 2019-07-15 | 16 | 4687 | 2100 | -162 | 1 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 1289.6125 | 780 | 200 | 2269.6125 | 56.74% | 95% | 0% | -185.3547 | 1237.3988 | -3550 | -400 | -2712.6012 | 67.82% | 58.64% | 95% | 0% | 2262 | -162
[5 empty] | 2019-07-15 | 17 | 4687.5 | 2134 | -199 | 1 | 0 | 2333 | 1533.9654 | 1533.9654 | 1533.9654 | 1288.0462 | 780 | 200 | 2268.0462 | 56.7% | 95% | 0% | -227.6888 | 1306.2766 | -3550 | -400 | -2643.7234 | 66.09% | 58.63% | 95% | 0% | 2333 | -199
[5 empty] | 2019-07-15 | 18 | 4688 | 2082 | -252 | 1 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 1288.0462 | 780 | 200 | 2268.0462 | 56.7% | 95% | 0% | -288.3295 | 1247.2022 | -3550 | -400 | -2702.7978 | 67.57% | 58.63% | 95% | 0% | 2334 | -252
[5 empty] | 2019-07-15 | 19 | 4688.5 | 2045 | -308 | 1 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 1288.0462 | 780 | 200 | 2268.0462 | 56.7% | 95% | 0% | -352.4027 | 1212.8899 | -3550 | -400 | -2737.1101 | 68.43% | 58.63% | 95% | 0% | 2353 | -308
[5 empty] | 2019-07-15 | 20 | 4689 | 1986 | -346 | 1 | 0 | 2332 | 1532.399 | 1532.399 | 1532.399 | 1288.0462 | 780 | 200 | 2268.0462 | 56.7% | 95% | 0% | -395.881 | 1136.518 | -3550 | -400 | -2813.482 | 70.34% | 58.63% | 95% | 0% | 2332 | -346
[5 empty] | 2019-07-15 | 21 | 4689.5 | 1914 | -384 | 1 | 0 | 2298 | 1479.1426 | 1479.1426 | 1479.1426 | 1288.0462 | 780 | 200 | 2268.0462 | 56.7% | 95% | 0% | -439.3593 | 1039.7834 | -3550 | -400 | -2910.2166 | 72.76% | 58.62% | 95% | 0% | 2298 | -384
[5 empty] | 2019-07-15 | 22 | 4690 | 1872 | -415 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1288.0462 | 780 | 200 | 2268.0462 | 56.7% | 95% | 0% | -474.8284 | 987.0842 | -3550 | -400 | -2962.9158 | 74.07% | 58.62% | 95% | 0% | 2287 | -415
[5 empty] | 2019-07-15 | 23 | 4690.5 | 1829 | -445 | 1 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 1288.0462 | 780 | 200 | 2268.0462 | 56.7% | 95% | 0% | -509.1533 | 932.3966 | -3550 | -400 | -3017.6034 | 75.44% | 58.62% | 95% | 0% | 2274 | -445
[5 empty] | 2019-07-15 | 24 | 4691 | 1778 | -477 | 1 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 1288.0462 | 780 | 200 | 2268.0462 | 56.7% | 95% | 0% | -545.7666 | 866.0224 | -3550 | -400 | -3083.9776 | 77.1% | 58.62% | 95% | 0% | 2255 | -477
[5 empty] | 2019-07-15 | 25 | 4691.5 | 1741 | -504 | 1 | 0 | 2245 | 1396.1253 | 1396.1253 | 1396.1253 | 1288.0462 | 780 | 200 | 2268.0462 | 56.7% | 95% | 0% | -576.659 | 819.4663 | -3550 | -400 | -3130.5337 | 78.26% | 58.62% | 95% | 0% | 2245 | -504
[5 empty] | 2019-07-15 | 26 | 4692 | 1717 | -517 | 1 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 1288.0462 | 780 | 200 | 2268.0462 | 56.7% | 95% | 0% | -591.5332 | 787.3621 | -3550 | -400 | -3162.6379 | 79.07% | 58.62% | 95% | 0% | 2234 | -517
[5 empty] | 2019-07-15 | 27 | 4692.5 | 1690 | -522 | 1 | 0 | 2212 | 1344.4353 | 1344.4353 | 1344.4353 | 1288.0462 | 780 | 200 | 2268.0462 | 56.7% | 95% | 0% | -597.254 | 747.1813 | -3550 | -400 | -3202.8187 | 80.07% | 58.61% | 95% | 0% | 2212 | -522
[5 empty] | 2019-07-15 | 28 | 4693 | 1648 | -541 | 1 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 1288.0462 | 780 | 200 | 2268.0462 | 56.7% | 95% | 0% | -618.9931 | 689.4158 | -3550 | -400 | -3260.5842 | 81.51% | 58.61% | 95% | 0% | 2189 | -541
[5 empty] | 2019-07-15 | 29 | 4693.5 | 1635 | -539 | 1 | 0 | 2174 | 1284.9134 | 1284.9134 | 1284.9134 | 1286.4798 | 780 | 200 | 2266.4798 | 56.66% | 95% | 0% | -616.7048 | 668.2086 | -3550 | -400 | -3281.7914 | 82.04% | 58.61% | 95% | 0% | 2174 | -539
[5 empty] | 2019-07-15 | 30 | 4694 | 1651 | -519 | 1 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 1286.4798 | 780 | 200 | 2266.4798 | 56.66% | 95% | 0% | -593.8215 | 684.8265 | -3550 | -400 | -3265.1735 | 81.63% | 58.61% | 95% | 0% | 2170 | -519
[5 empty] | 2019-07-15 | 31 | 4694.5 | 1686 | -485 | 1 | 0 | 2171 | 1280.2143 | 1280.2143 | 1280.2143 | 1286.4798 | 780 | 200 | 2266.4798 | 56.66% | 95% | 0% | -554.9199 | 725.2944 | -3550 | -400 | -3224.7056 | 80.62% | 58.6% | 95% | 0% | 2171 | -485
[5 empty] | 2019-07-15 | 32 | 4695 | 1750 | -465 | 1 | 0 | 2215 | 1349.1344 | 1349.1344 | 1349.1344 | 1286.4798 | 780 | 200 | 2266.4798 | 56.66% | 95% | 0% | -532.0366 | 817.0978 | -3550 | -400 | -3132.9022 | 78.32% | 58.6% | 95% | 0% | 2215 | -465
[5 empty] | 2019-07-15 | 33 | 4695.5 | 1802 | -446 | 1 | 0 | 2248 | 1400.8244 | 1400.8244 | 1400.8244 | 1286.4798 | 780 | 200 | 2266.4798 | 56.66% | 95% | 0% | -510.2975 | 890.5269 | -3550 | -400 | -3059.4731 | 76.49% | 58.6% | 95% | 0% | 2248 | -446
[5 empty] | 2019-07-15 | 34 | 4696 | 1891 | -409 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 1286.4798 | 780 | 200 | 2266.4798 | 56.66% | 95% | 0% | -467.9634 | 1014.312 | -3550 | -400 | -2935.688 | 73.39% | 58.6% | 95% | 0% | 2300 | -409
[5 empty] | 2019-07-15 | 35 | 4696.5 | 1982 | -367 | 1 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 1284.9134 | 780 | 200 | 2264.9134 | 56.62% | 95% | 0% | -419.9085 | 1139.1187 | -3550 | -400 | -2810.8813 | 70.27% | 58.6% | 95% | 0% | 2349 | -367
[5 empty] | 2019-07-15 | 36 | 4697 | 2081 | -308 | 1 | 0 | 2389 | 1621.6818 | 1621.6818 | 1621.6818 | 1284.9134 | 780 | 200 | 2264.9134 | 56.62% | 95% | 0% | -352.4027 | 1269.279 | -3550 | -400 | -2680.721 | 67.02% | 58.59% | 95% | 0% | 2389 | -308
[5 empty] | 2019-07-15 | 37 | 4697.5 | 2165 | -245 | 1 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 1284.9134 | 780 | 200 | 2264.9134 | 56.62% | 95% | 0% | -280.3204 | 1374.2551 | -3550 | -400 | -2575.7449 | 64.39% | 58.59% | 95% | 0% | 2410 | -245
[5 empty] | 2019-07-15 | 38 | 4698 | 2235 | -191 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1284.9134 | 780 | 200 | 2264.9134 | 56.62% | 95% | 0% | -218.5355 | 1461.1018 | -3550 | -400 | -2488.8982 | 62.22% | 58.59% | 95% | 0% | 2426 | -191
[5 empty] | 2019-07-15 | 39 | 4698.5 | 2300 | -141 | 1 | 0 | 2441 | 1703.1327 | 1703.1327 | 1703.1327 | 1284.9134 | 780 | 200 | 2264.9134 | 56.62% | 95% | 0% | -161.3272 | 1541.8055 | -3550 | -400 | -2408.1945 | 60.2% | 58.59% | 95% | 0% | 2441 | -141
[5 empty] | 2019-07-15 | 40 | 4699 | 2342 | -99 | 1 | 0 | 2441 | 1703.1327 | 1703.1327 | 1703.1327 | 1284.9134 | 780 | 200 | 2264.9134 | 56.62% | 95% | 0% | -113.2723 | 1589.8604 | -3550 | -400 | -2360.1396 | 59% | 58.59% | 95% | 0% | 2441 | -99
[5 empty] | 2019-07-15 | 41 | 4699.5 | 2351 | -64 | 1 | 0 | 2415 | 1662.4073 | 1662.4073 | 1662.4073 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -73.2265 | 1589.1807 | -3550 | -400 | -2360.8193 | 59.02% | 58.58% | 95% | 0% | 2415 | -64
[5 empty] | 2019-07-15 | 42 | 4700 | 2337 | -39 | 1 | 0 | 2376 | 1601.319 | 1601.319 | 1601.319 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -44.6224 | 1556.6966 | -3550 | -400 | -2393.3034 | 59.83% | 58.57% | 95% | 0% | 2376 | -39
[5 empty] | 2019-07-15 | 43 | 4700.5 | 2311 | -32 | 1 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -36.6133 | 1513.0157 | -3550 | -400 | -2436.9843 | 60.92% | 58.56% | 95% | 0% | 2343 | -32
[5 empty] | 2019-07-15 | 44 | 4701 | 2272 | -30 | 1 | 0 | 2302 | 1485.4081 | 1485.4081 | 1485.4081 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -34.3249 | 1451.0831 | -3550 | -400 | -2498.9169 | 62.47% | 58.55% | 95% | 0% | 2302 | -30
[5 empty] | 2019-07-15 | 45 | 4701.5 | 2214 | -30 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -34.3249 | 1360.234 | -3550 | -400 | -2589.766 | 64.74% | 58.55% | 95% | 0% | 2244 | -30
[5 empty] | 2019-07-15 | 46 | 4702 | 2091 | -29 | 0 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -33.1808 | 1167.149 | -2750 | -200 | -1782.851 | 44.57% | 58.55% | 95% | 0% | 2120 | -29
[5 empty] | 2019-07-15 | 47 | 4702.5 | 1946 | -28 | 0 | 0 | 1974 | 971.6406 | 971.6406 | 971.6406 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -32.0366 | 939.6039 | -2750 | -200 | -2010.3961 | 50.26% | 58.55% | 95% | 0% | 1974 | -28
[5 empty] | 2019-07-15 | 48 | 4703 | 1832 | -28 | 0 | 0 | 1860 | 793.075 | 793.075 | 793.075 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -32.0366 | 761.0384 | -2750 | -200 | -2188.9616 | 54.72% | 58.54% | 95% | 0% | 1860 | -28
[5 empty] | 2019-07-16 | 1 | 4703.5 | 1741 | -28 | 0 | 0 | 1769 | 650.5359 | 650.5359 | 650.5359 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -32.0366 | 618.4992 | -2750 | -200 | -2331.5008 | 58.29% | 58.54% | 95% | 0% | 1769 | -28
[5 empty] | 2019-07-16 | 2 | 4704 | 1681 | -28 | 0 | 0 | 1709 | 556.554 | 556.554 | 556.554 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -32.0366 | 524.5174 | -2750 | -200 | -2425.4826 | 60.64% | 58.54% | 95% | 0% | 1709 | -28
[5 empty] | 2019-07-16 | 3 | 4704.5 | 1638 | -27 | 0 | 0 | 1665 | 487.634 | 487.634 | 487.634 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -30.8924 | 456.7415 | -2750 | -200 | -2493.2585 | 62.33% | 58.54% | 95% | 0% | 1665 | -27
[5 empty] | 2019-07-16 | 4 | 4705 | 1621 | -27 | 0 | 0 | 1648 | 461.0058 | 461.0058 | 461.0058 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -30.8924 | 430.1133 | -2750 | -200 | -2519.8867 | 63% | 58.54% | 95% | 0% | 1648 | -27
[5 empty] | 2019-07-16 | 5 | 4705.5 | 1592 | -27 | 0 | 0 | 1619 | 415.5812 | 415.5812 | 415.5812 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -30.8924 | 384.6888 | -2750 | -200 | -2565.3112 | 64.13% | 58.53% | 95% | 0% | 1619 | -27
[5 empty] | 2019-07-16 | 6 | 4706 | 1575 | -26 | 0 | 0 | 1601 | 387.3866 | 387.3866 | 387.3866 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -29.7483 | 357.6384 | -2750 | -200 | -2592.3616 | 64.81% | 58.53% | 95% | 0% | 1601 | -26
[5 empty] | 2019-07-16 | 7 | 4706.5 | 1562 | -26 | 0 | 0 | 1588 | 367.0239 | 367.0239 | 367.0239 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -29.7483 | 337.2756 | -2750 | -200 | -2612.7244 | 65.32% | 58.53% | 95% | 0% | 1588 | -26
[5 empty] | 2019-07-16 | 8 | 4707 | 1557 | -25 | 0 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -28.6041 | 329.0216 | -2750 | -200 | -2620.9784 | 65.52% | 58.53% | 95% | 0% | 1582 | -25
[5 empty] | 2019-07-16 | 9 | 4707.5 | 1556 | -25 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 1283.3471 | 780 | 200 | 2263.3471 | 56.58% | 95% | 0% | -28.6041 | 327.4552 | -2750 | -200 | -2622.5448 | 65.56% | 58.53% | 95% | 0% | 1581 | -25
[5 empty] | 2019-07-16 | 10 | 4708 | 1545 | -25 | 0 | 0 | 1570 | 338.8293 | 338.8293 | 338.8293 | 1281.7807 | 780 | 200 | 2261.7807 | 56.54% | 95% | 0% | -28.6041 | 310.2252 | -2750 | -200 | -2639.7748 | 65.99% | 58.52% | 95% | 0% | 1570 | -25
[5 empty] | 2019-07-16 | 11 | 4708.5 | 1576 | -27 | 0 | 0 | 1603 | 390.5194 | 390.5194 | 390.5194 | 1281.7807 | 780 | 200 | 2261.7807 | 56.54% | 95% | 0% | -30.8924 | 359.6269 | -2750 | -200 | -2590.3731 | 64.76% | 58.52% | 95% | 0% | 1603 | -27
[5 empty] | 2019-07-16 | 12 | 4709 | 1624 | -41 | 0 | 0 | 1665 | 487.634 | 487.634 | 487.634 | 1281.7807 | 780 | 200 | 2261.7807 | 56.54% | 95% | 0% | -46.9108 | 440.7232 | -2750 | -200 | -2509.2768 | 62.73% | 58.52% | 95% | 0% | 1665 | -41
[5 empty] | 2019-07-16 | 13 | 4709.5 | 1764 | -72 | 1 | 0 | 1836 | 755.4823 | 755.4823 | 755.4823 | 1281.7807 | 780 | 200 | 2261.7807 | 56.54% | 95% | 0% | -82.3799 | 673.1024 | -3550 | -400 | -3276.8976 | 81.92% | 58.52% | 95% | 0% | 1836 | -72
[5 empty] | 2019-07-16 | 14 | 4710 | 1894 | -103 | 1 | 0 | 1997 | 1007.6669 | 1007.6669 | 1007.6669 | 1281.7807 | 780 | 200 | 2261.7807 | 56.54% | 95% | 0% | -117.849 | 889.818 | -3550 | -400 | -3060.182 | 76.5% | 58.51% | 95% | 0% | 1997 | -103
[5 empty] | 2019-07-16 | 15 | 4710.5 | 2037 | -142 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 1281.7807 | 780 | 200 | 2261.7807 | 56.54% | 95% | 0% | -162.4714 | 1130.2739 | -3550 | -400 | -2819.7261 | 70.49% | 58.51% | 95% | 0% | 2179 | -142
[5 empty] | 2019-07-16 | 16 | 4711 | 2055 | -195 | 1 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 1281.7807 | 780 | 200 | 2261.7807 | 56.54% | 95% | 0% | -223.1121 | 1180.845 | -3550 | -400 | -2769.155 | 69.23% | 58.49% | 95% | 0% | 2250 | -195
[5 empty] | 2019-07-16 | 17 | 4711.5 | 2042 | -251 | 1 | 0 | 2293 | 1471.3108 | 1471.3108 | 1471.3108 | 1281.7807 | 780 | 200 | 2261.7807 | 56.54% | 95% | 0% | -287.1854 | 1184.1254 | -3550 | -400 | -2765.8746 | 69.15% | 58.49% | 95% | 0% | 2293 | -251
[5 empty] | 2019-07-16 | 18 | 4712 | 1974 | -318 | 1 | 0 | 2292 | 1469.7444 | 1469.7444 | 1469.7444 | 1281.7807 | 780 | 200 | 2261.7807 | 56.54% | 95% | 0% | -363.8444 | 1105.9 | -3550 | -400 | -2844.1 | 71.1% | 58.48% | 95% | 0% | 2292 | -318
[5 empty] | 2019-07-16 | 19 | 4712.5 | 1907 | -372 | 1 | 0 | 2279 | 1449.3817 | 1449.3817 | 1449.3817 | 1281.7807 | 780 | 200 | 2261.7807 | 56.54% | 95% | 0% | -425.6293 | 1023.7524 | -3550 | -400 | -2926.2476 | 73.16% | 58.48% | 95% | 0% | 2279 | -372
[5 empty] | 2019-07-16 | 20 | 4713 | 1825 | -432 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 1281.7807 | 780 | 200 | 2261.7807 | 56.54% | 95% | 0% | -494.2792 | 920.6425 | -3550 | -400 | -3029.3575 | 75.73% | 58.47% | 95% | 0% | 2257 | -432
[5 empty] | 2019-07-16 | 21 | 4713.5 | 1748 | -486 | 1 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 1281.7807 | 780 | 200 | 2261.7807 | 56.54% | 95% | 0% | -556.0641 | 822.8312 | -3550 | -400 | -3127.1688 | 78.18% | 58.47% | 95% | 0% | 2234 | -486
[5 empty] | 2019-07-16 | 22 | 4714 | 1699 | -524 | 1 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 1280.2143 | 780 | 200 | 2260.2143 | 56.51% | 95% | 0% | -599.5423 | 762.123 | -3550 | -400 | -3187.877 | 79.7% | 58.47% | 95% | 0% | 2223 | -524
[5 empty] | 2019-07-16 | 23 | 4714.5 | 1681 | -540 | 1 | 0 | 2221 | 1358.5326 | 1358.5326 | 1358.5326 | 1280.2143 | 780 | 200 | 2260.2143 | 56.51% | 95% | 0% | -617.849 | 740.6836 | -3550 | -400 | -3209.3164 | 80.23% | 58.47% | 95% | 0% | 2221 | -540
[5 empty] | 2019-07-16 | 24 | 4715 | 1691 | -561 | 1 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 1280.2143 | 780 | 200 | 2260.2143 | 56.51% | 95% | 0% | -641.8764 | 765.2134 | -3550 | -400 | -3184.7866 | 79.62% | 58.47% | 95% | 0% | 2252 | -561
[5 empty] | 2019-07-16 | 25 | 4715.5 | 1624 | -601 | 1 | 0 | 2225 | 1364.798 | 1364.798 | 1364.798 | 1280.2143 | 780 | 200 | 2260.2143 | 56.51% | 95% | 0% | -687.643 | 677.155 | -3550 | -400 | -3272.845 | 81.82% | 58.47% | 95% | 0% | 2225 | -601
[5 empty] | 2019-07-16 | 26 | 4716 | 1595 | -613 | 1 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 1280.2143 | 780 | 200 | 2260.2143 | 56.51% | 95% | 0% | -701.373 | 636.7968 | -3550 | -400 | -3313.2032 | 82.83% | 58.47% | 95% | 0% | 2208 | -613
[5 empty] | 2019-07-16 | 27 | 4716.5 | 1576 | -622 | 1 | 0 | 2198 | 1322.5062 | 1322.5062 | 1322.5062 | 1280.2143 | 780 | 200 | 2260.2143 | 56.51% | 95% | 0% | -711.6705 | 610.8357 | -3550 | -400 | -3339.1643 | 83.48% | 58.46% | 95% | 0% | 2198 | -622
[5 empty] | 2019-07-16 | 28 | 4717 | 1581 | -597 | 1 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 1280.2143 | 780 | 200 | 2260.2143 | 56.51% | 95% | 0% | -683.0664 | 608.1125 | -3550 | -400 | -3341.8875 | 83.55% | 58.46% | 95% | 0% | 2178 | -597
[5 empty] | 2019-07-16 | 29 | 4717.5 | 1598 | -585 | 1 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 1280.2143 | 780 | 200 | 2260.2143 | 56.51% | 95% | 0% | -669.3364 | 629.6743 | -3550 | -400 | -3320.3257 | 83.01% | 58.46% | 95% | 0% | 2183 | -585
[5 empty] | 2019-07-16 | 30 | 4718 | 1629 | -565 | 1 | 0 | 2194 | 1316.2407 | 1316.2407 | 1316.2407 | 1280.2143 | 780 | 200 | 2260.2143 | 56.51% | 95% | 0% | -646.4531 | 669.7876 | -3550 | -400 | -3280.2124 | 82.01% | 58.46% | 95% | 0% | 2194 | -565
[5 empty] | 2019-07-16 | 31 | 4718.5 | 1688 | -507 | 1 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 1280.2143 | 780 | 200 | 2260.2143 | 56.51% | 95% | 0% | -580.0915 | 737.7156 | -3550 | -400 | -3212.2844 | 80.31% | 58.45% | 95% | 0% | 2195 | -507
[5 empty] | 2019-07-16 | 32 | 4719 | 1775 | -470 | 1 | 0 | 2245 | 1396.1253 | 1396.1253 | 1396.1253 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -537.7574 | 858.3679 | -3550 | -400 | -3091.6321 | 77.29% | 58.45% | 95% | 0% | 2245 | -470
[5 empty] | 2019-07-16 | 33 | 4719.5 | 1869 | -418 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -478.2609 | 983.6517 | -3550 | -400 | -2966.3483 | 74.16% | 58.45% | 95% | 0% | 2287 | -418
[5 empty] | 2019-07-16 | 34 | 4720 | 1964 | -367 | 1 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -419.9085 | 1110.9242 | -3550 | -400 | -2839.0758 | 70.98% | 58.45% | 95% | 0% | 2331 | -367
[5 empty] | 2019-07-16 | 35 | 4720.5 | 2067 | -322 | 1 | 0 | 2389 | 1621.6818 | 1621.6818 | 1621.6818 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -368.4211 | 1253.2607 | -3550 | -400 | -2696.7393 | 67.42% | 58.45% | 95% | 0% | 2389 | -322
[5 empty] | 2019-07-16 | 36 | 4721 | 2152 | -256 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -292.9062 | 1358.5365 | -3550 | -400 | -2591.4635 | 64.79% | 58.44% | 95% | 0% | 2408 | -256
[5 empty] | 2019-07-16 | 37 | 4721.5 | 2211 | -200 | 1 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -228.833 | 1427.3088 | -3550 | -400 | -2522.6912 | 63.07% | 58.44% | 95% | 0% | 2411 | -200
[5 empty] | 2019-07-16 | 38 | 4722 | 2264 | -162 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -185.3547 | 1494.2826 | -3550 | -400 | -2455.7174 | 61.39% | 58.43% | 95% | 0% | 2426 | -162
[5 empty] | 2019-07-16 | 39 | 4722.5 | 2290 | -126 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -144.1648 | 1519.8089 | -3550 | -400 | -2430.1911 | 60.75% | 58.42% | 95% | 0% | 2416 | -126
[5 empty] | 2019-07-16 | 40 | 4723 | 2309 | -91 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -104.119 | 1534.7928 | -3550 | -400 | -2415.2072 | 60.38% | 58.42% | 95% | 0% | 2400 | -91
[5 empty] | 2019-07-16 | 41 | 4723.5 | 2339 | -62 | 1 | 0 | 2401 | 1640.4782 | 1640.4782 | 1640.4782 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -70.9382 | 1569.5399 | -3550 | -400 | -2380.4601 | 59.51% | 58.42% | 95% | 0% | 2401 | -62
[5 empty] | 2019-07-16 | 42 | 4724 | 2331 | -42 | 1 | 0 | 2373 | 1596.62 | 1596.62 | 1596.62 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -48.0549 | 1548.565 | -3550 | -400 | -2401.435 | 60.04% | 58.41% | 95% | 0% | 2373 | -42
[5 empty] | 2019-07-16 | 43 | 4724.5 | 2299 | -34 | 1 | 0 | 2333 | 1533.9654 | 1533.9654 | 1533.9654 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -38.9016 | 1495.0638 | -3550 | -400 | -2454.9362 | 61.37% | 58.41% | 95% | 0% | 2333 | -34
[5 empty] | 2019-07-16 | 44 | 4725 | 2273 | -33 | 1 | 0 | 2306 | 1491.6735 | 1491.6735 | 1491.6735 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -37.7574 | 1453.9161 | -3550 | -400 | -2496.0839 | 62.4% | 58.41% | 95% | 0% | 2306 | -33
[5 empty] | 2019-07-16 | 45 | 4725.5 | 2225 | -33 | 1 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -37.7574 | 1378.7306 | -3550 | -400 | -2571.2694 | 64.28% | 58.41% | 95% | 0% | 2258 | -33
[5 empty] | 2019-07-16 | 46 | 4726 | 2116 | -33 | 0 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -37.7574 | 1207.9969 | -2750 | -200 | -1742.0031 | 43.55% | 58.41% | 95% | 0% | 2149 | -33
[5 empty] | 2019-07-16 | 47 | 4726.5 | 1978 | -33 | 0 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -37.7574 | 991.8386 | -2750 | -200 | -1958.1614 | 48.95% | 58.4% | 95% | 0% | 2011 | -33
[5 empty] | 2019-07-16 | 48 | 4727 | 1855 | -34 | 0 | 0 | 1889 | 838.4996 | 838.4996 | 838.4996 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -38.9016 | 799.598 | -2750 | -200 | -2150.402 | 53.76% | 58.4% | 95% | 0% | 1889 | -34
[5 empty] | 2019-07-17 | 1 | 4727.5 | 1749 | -37 | 0 | 0 | 1786 | 677.1641 | 677.1641 | 677.1641 | 1278.648 | 780 | 200 | 2258.648 | 56.47% | 95% | 0% | -42.3341 | 634.83 | -2750 | -200 | -2315.17 | 57.88% | 58.4% | 95% | 0% | 1786 | -37
[5 empty] | 2019-07-17 | 2 | 4728 | 1695 | -39 | 0 | 0 | 1734 | 595.7131 | 595.7131 | 595.7131 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -44.6224 | 551.0907 | -2750 | -200 | -2398.9093 | 59.97% | 58.4% | 95% | 0% | 1734 | -39
[5 empty] | 2019-07-17 | 3 | 4728.5 | 1643 | -39 | 0 | 0 | 1682 | 514.2622 | 514.2622 | 514.2622 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -44.6224 | 469.6397 | -2750 | -200 | -2480.3603 | 62.01% | 58.4% | 95% | 0% | 1682 | -39
[5 empty] | 2019-07-17 | 4 | 4729 | 1625 | -39 | 1 | 0 | 1664 | 486.0676 | 486.0676 | 486.0676 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -44.6224 | 441.4452 | -3550 | -400 | -3508.5548 | 87.71% | 58.4% | 95% | 0% | 1664 | -39
[5 empty] | 2019-07-17 | 5 | 4729.5 | 1590 | -40 | 1 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -45.7666 | 387.0446 | -3550 | -400 | -3562.9554 | 89.07% | 58.39% | 95% | 0% | 1630 | -40
[5 empty] | 2019-07-17 | 6 | 4730 | 1561 | -41 | 1 | 0 | 1602 | 388.953 | 388.953 | 388.953 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -46.9108 | 342.0423 | -3550 | -400 | -3607.9577 | 90.2% | 58.39% | 95% | 0% | 1602 | -41
[5 empty] | 2019-07-17 | 7 | 4730.5 | 1549 | -41 | 1 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -46.9108 | 323.2459 | -3550 | -400 | -3626.7541 | 90.67% | 58.39% | 95% | 0% | 1590 | -41
[5 empty] | 2019-07-17 | 8 | 4731 | 1543 | -41 | 1 | 0 | 1584 | 360.7585 | 360.7585 | 360.7585 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -46.9108 | 313.8477 | -3550 | -400 | -3636.1523 | 90.9% | 58.39% | 95% | 0% | 1584 | -41
[5 empty] | 2019-07-17 | 9 | 4731.5 | 1542 | -42 | 1 | 0 | 1584 | 360.7585 | 360.7585 | 360.7585 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -48.0549 | 312.7035 | -3550 | -400 | -3637.2965 | 90.93% | 58.39% | 95% | 0% | 1584 | -42
[5 empty] | 2019-07-17 | 10 | 4732 | 1541 | -44 | 1 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -50.3432 | 311.9816 | -3550 | -400 | -3638.0184 | 90.95% | 58.38% | 95% | 0% | 1585 | -44
[5 empty] | 2019-07-17 | 11 | 4732.5 | 1562 | -46 | 1 | 0 | 1608 | 398.3512 | 398.3512 | 398.3512 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -52.6316 | 345.7196 | -3550 | -400 | -3604.2804 | 90.11% | 58.38% | 95% | 0% | 1608 | -46
[5 empty] | 2019-07-17 | 12 | 4733 | 1616 | -60 | 1 | 0 | 1676 | 504.864 | 504.864 | 504.864 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -68.6499 | 436.2141 | -3550 | -400 | -3513.7859 | 87.84% | 58.38% | 95% | 0% | 1676 | -60
[5 empty] | 2019-07-17 | 13 | 4733.5 | 1753 | -86 | 1 | 0 | 1839 | 760.1814 | 760.1814 | 760.1814 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -98.3982 | 661.7832 | -3550 | -400 | -3288.2168 | 82.21% | 58.38% | 95% | 0% | 1839 | -86
[5 empty] | 2019-07-17 | 14 | 4734 | 1881 | -119 | 1 | 0 | 2000 | 1012.366 | 1012.366 | 1012.366 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -136.1556 | 876.2104 | -3550 | -400 | -3073.7896 | 76.84% | 58.38% | 95% | 0% | 2000 | -119
[5 empty] | 2019-07-17 | 15 | 4734.5 | 2012 | -173 | 1 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -197.9405 | 1104.2029 | -3550 | -400 | -2845.7971 | 71.14% | 58.38% | 95% | 0% | 2185 | -173
[5 empty] | 2019-07-17 | 16 | 4735 | 2034 | -221 | 1 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -252.8604 | 1158.9285 | -3550 | -400 | -2791.0715 | 69.78% | 58.37% | 95% | 0% | 2255 | -221
[5 empty] | 2019-07-17 | 17 | 4735.5 | 1993 | -288 | 1 | 0 | 2281 | 1452.5144 | 1452.5144 | 1452.5144 | 1277.0816 | 780 | 200 | 2257.0816 | 56.43% | 95% | 0% | -329.5195 | 1122.995 | -3550 | -400 | -2827.005 | 70.68% | 58.37% | 95% | 0% | 2281 | -288
[5 empty] | 2019-07-17 | 18 | 4736 | 1948 | -346 | 1 | 0 | 2294 | 1472.8772 | 1472.8772 | 1472.8772 | 1275.5153 | 780 | 200 | 2255.5153 | 56.39% | 95% | 0% | -395.881 | 1076.9962 | -3550 | -400 | -2873.0038 | 71.83% | 58.37% | 95% | 0% | 2294 | -346
[5 empty] | 2019-07-17 | 19 | 4736.5 | 1940 | -391 | 1 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 1275.5153 | 780 | 200 | 2255.5153 | 56.39% | 95% | 0% | -447.3684 | 1083.4642 | -3550 | -400 | -2866.5358 | 71.66% | 58.37% | 95% | 0% | 2331 | -391
[5 empty] | 2019-07-17 | 20 | 4737 | 1859 | -442 | 1 | 0 | 2301 | 1483.8417 | 1483.8417 | 1483.8417 | 1275.5153 | 780 | 200 | 2255.5153 | 56.39% | 95% | 0% | -505.7208 | 978.1209 | -3550 | -400 | -2971.8791 | 74.3% | 58.36% | 95% | 0% | 2301 | -442
[5 empty] | 2019-07-17 | 21 | 4737.5 | 1799 | -484 | 1 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 1275.5153 | 780 | 200 | 2255.5153 | 56.39% | 95% | 0% | -553.7757 | 901.8714 | -3550 | -400 | -3048.1286 | 76.2% | 58.36% | 95% | 0% | 2283 | -484
[5 empty] | 2019-07-17 | 22 | 4738 | 1759 | -522 | 1 | 0 | 2281 | 1452.5144 | 1452.5144 | 1452.5144 | 1275.5153 | 780 | 200 | 2255.5153 | 56.39% | 95% | 0% | -597.254 | 855.2604 | -3550 | -400 | -3094.7396 | 77.37% | 58.36% | 95% | 0% | 2281 | -522
[5 empty] | 2019-07-17 | 23 | 4738.5 | 1705 | -563 | 1 | 0 | 2268 | 1432.1517 | 1432.1517 | 1432.1517 | 1275.5153 | 780 | 200 | 2255.5153 | 56.39% | 95% | 0% | -644.1648 | 787.9869 | -3550 | -400 | -3162.0131 | 79.05% | 58.36% | 95% | 0% | 2268 | -563
[5 empty] | 2019-07-17 | 24 | 4739 | 1676 | -582 | 1 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 1275.5153 | 780 | 200 | 2255.5153 | 56.39% | 95% | 0% | -665.9039 | 750.5842 | -3550 | -400 | -3199.4158 | 79.99% | 58.36% | 95% | 0% | 2258 | -582
[5 empty] | 2019-07-17 | 25 | 4739.5 | 1722 | -555 | 1 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 1275.5153 | 780 | 200 | 2255.5153 | 56.39% | 95% | 0% | -635.0114 | 811.2375 | -3550 | -400 | -3138.7625 | 78.47% | 58.36% | 95% | 0% | 2277 | -555
[5 empty] | 2019-07-17 | 26 | 4740 | 1702 | -562 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 1275.5153 | 780 | 200 | 2255.5153 | 56.39% | 95% | 0% | -643.0206 | 782.8656 | -3550 | -400 | -3167.1344 | 79.18% | 58.35% | 95% | 0% | 2264 | -562
[5 empty] | 2019-07-17 | 27 | 4740.5 | 1660 | -563 | 1 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 1275.5153 | 780 | 200 | 2255.5153 | 56.39% | 95% | 0% | -644.1648 | 717.5005 | -3550 | -400 | -3232.4995 | 80.81% | 58.35% | 95% | 0% | 2223 | -563
[5 empty] | 2019-07-17 | 28 | 4741 | 1668 | -542 | 1 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 1275.5153 | 780 | 200 | 2255.5153 | 56.39% | 95% | 0% | -620.1373 | 721.1653 | -3550 | -400 | -3228.8347 | 80.72% | 58.35% | 95% | 0% | 2210 | -542
[5 empty] | 2019-07-17 | 29 | 4741.5 | 1692 | -512 | 1 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 1273.9489 | 780 | 200 | 2253.9489 | 56.35% | 95% | 0% | -585.8124 | 746.092 | -3550 | -400 | -3203.908 | 80.1% | 58.35% | 95% | 0% | 2204 | -512
[5 empty] | 2019-07-17 | 30 | 4742 | 1712 | -497 | 1 | 0 | 2209 | 1339.7362 | 1339.7362 | 1339.7362 | 1273.9489 | 780 | 200 | 2253.9489 | 56.35% | 95% | 0% | -568.6499 | 771.0863 | -3550 | -400 | -3178.9137 | 79.47% | 58.35% | 95% | 0% | 2209 | -497
[5 empty] | 2019-07-17 | 31 | 4742.5 | 1771 | -457 | 1 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 1273.9489 | 780 | 200 | 2253.9489 | 56.35% | 95% | 0% | -522.8833 | 846.6138 | -3550 | -400 | -3103.3862 | 77.58% | 58.33% | 95% | 0% | 2228 | -457
[5 empty] | 2019-07-17 | 32 | 4743 | 1841 | -437 | 1 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 1273.9489 | 780 | 200 | 2253.9489 | 56.35% | 95% | 0% | -500 | 947.8153 | -3550 | -400 | -3002.1847 | 75.05% | 58.32% | 95% | 0% | 2278 | -437
[5 empty] | 2019-07-17 | 33 | 4743.5 | 1967 | -389 | 1 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 1273.9489 | 780 | 200 | 2253.9489 | 56.35% | 95% | 0% | -445.0801 | 1124.9117 | -3550 | -400 | -2825.0883 | 70.63% | 58.32% | 95% | 0% | 2356 | -389
[5 empty] | 2019-07-17 | 34 | 4744 | 2076 | -334 | 1 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 1273.9489 | 780 | 200 | 2253.9489 | 56.35% | 95% | 0% | -382.151 | 1272.4244 | -3550 | -400 | -2677.5756 | 66.94% | 58.32% | 95% | 0% | 2410 | -334
[5 empty] | 2019-07-17 | 35 | 4744.5 | 2179 | -277 | 1 | 0 | 2456 | 1726.6282 | 1726.6282 | 1726.6282 | 1273.9489 | 780 | 200 | 2253.9489 | 56.35% | 95% | 0% | -316.9336 | 1409.6946 | -3550 | -400 | -2540.3054 | 63.51% | 58.31% | 95% | 0% | 2456 | -277
[5 empty] | 2019-07-17 | 36 | 4745 | 2230 | -251 | 1 | 0 | 2481 | 1765.7873 | 1765.7873 | 1765.7873 | 1273.9489 | 780 | 200 | 2253.9489 | 56.35% | 95% | 0% | -287.1854 | 1478.6019 | -3550 | -400 | -2471.3981 | 61.78% | 58.31% | 95% | 0% | 2481 | -251
[5 empty] | 2019-07-17 | 37 | 4745.5 | 2240 | -230 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 1273.9489 | 780 | 200 | 2253.9489 | 56.35% | 95% | 0% | -263.1579 | 1485.3994 | -3550 | -400 | -2464.6006 | 61.62% | 58.3% | 95% | 0% | 2470 | -230
[5 empty] | 2019-07-17 | 38 | 4746 | 2270 | -203 | 1 | 0 | 2473 | 1753.2564 | 1753.2564 | 1753.2564 | 1273.9489 | 780 | 200 | 2253.9489 | 56.35% | 95% | 0% | -232.2654 | 1520.9909 | -3550 | -400 | -2429.0091 | 60.73% | 58.3% | 95% | 0% | 2473 | -203
[5 empty] | 2019-07-17 | 39 | 4746.5 | 2269 | -178 | 1 | 0 | 2447 | 1712.5309 | 1712.5309 | 1712.5309 | 1273.9489 | 780 | 200 | 2253.9489 | 56.35% | 95% | 0% | -203.6613 | 1508.8696 | -3550 | -400 | -2441.1304 | 61.03% | 58.3% | 95% | 0% | 2447 | -178
[5 empty] | 2019-07-17 | 40 | 4747 | 2287 | -143 | 1 | 0 | 2430 | 1685.9027 | 1685.9027 | 1685.9027 | 1272.3825 | 780 | 200 | 2252.3825 | 56.31% | 95% | 0% | -163.6156 | 1522.2872 | -3550 | -400 | -2427.7128 | 60.69% | 58.3% | 95% | 0% | 2430 | -143
[5 empty] | 2019-07-17 | 41 | 4747.5 | 2267 | -123 | 1 | 0 | 2390 | 1623.2481 | 1623.2481 | 1623.2481 | 1272.3825 | 780 | 200 | 2252.3825 | 56.31% | 95% | 0% | -140.7323 | 1482.5159 | -3550 | -400 | -2467.4841 | 61.69% | 58.3% | 95% | 0% | 2390 | -123
[5 empty] | 2019-07-17 | 42 | 4748 | 2244 | -106 | 1 | 0 | 2350 | 1560.5936 | 1560.5936 | 1560.5936 | 1272.3825 | 780 | 200 | 2252.3825 | 56.31% | 95% | 0% | -121.2815 | 1439.3121 | -3550 | -400 | -2510.6879 | 62.77% | 58.29% | 95% | 0% | 2350 | -106
[5 empty] | 2019-07-17 | 43 | 4748.5 | 2214 | -99 | 1 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 1272.3825 | 780 | 200 | 2252.3825 | 56.31% | 95% | 0% | -113.2723 | 1389.3658 | -3550 | -400 | -2560.6342 | 64.02% | 58.29% | 95% | 0% | 2313 | -99
[5 empty] | 2019-07-17 | 44 | 4749 | 2176 | -95 | 1 | 0 | 2271 | 1436.8508 | 1436.8508 | 1436.8508 | 1272.3825 | 780 | 200 | 2252.3825 | 56.31% | 95% | 0% | -108.6957 | 1328.1551 | -3550 | -400 | -2621.8449 | 65.55% | 58.29% | 95% | 0% | 2271 | -95
[5 empty] | 2019-07-17 | 45 | 4749.5 | 2083 | -93 | 1 | 0 | 2176 | 1288.0462 | 1288.0462 | 1288.0462 | 1272.3825 | 780 | 200 | 2252.3825 | 56.31% | 95% | 0% | -106.4073 | 1181.6388 | -3550 | -400 | -2768.3612 | 69.21% | 58.29% | 95% | 0% | 2176 | -93
[5 empty] | 2019-07-17 | 46 | 4750 | 1953 | -90 | 0 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 1272.3825 | 780 | 200 | 2252.3825 | 56.31% | 95% | 0% | -102.9748 | 976.7449 | -2750 | -200 | -1973.2551 | 49.33% | 58.29% | 95% | 0% | 2043 | -90
[5 empty] | 2019-07-17 | 47 | 4750.5 | 1802 | -88 | 0 | 0 | 1890 | 840.066 | 840.066 | 840.066 | 1272.3825 | 780 | 200 | 2252.3825 | 56.31% | 95% | 0% | -100.6865 | 739.3795 | -2750 | -200 | -2210.6205 | 55.27% | 58.28% | 95% | 0% | 1890 | -88
[5 empty] | 2019-07-17 | 48 | 4751 | 1694 | -86 | 0 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 1272.3825 | 780 | 200 | 2252.3825 | 56.31% | 95% | 0% | -98.3982 | 569.3677 | -2750 | -200 | -2380.6323 | 59.52% | 58.28% | 95% | 0% | 1780 | -86
[5 empty] | 2019-07-18 | 1 | 4751.5 | 1609 | -82 | 0 | 0 | 1691 | 528.3594 | 528.3594 | 528.3594 | 1272.3825 | 780 | 200 | 2252.3825 | 56.31% | 95% | 0% | -93.8215 | 434.5379 | -2750 | -200 | -2515.4621 | 62.89% | 58.28% | 95% | 0% | 1691 | -82
[5 empty] | 2019-07-18 | 2 | 4752 | 1558 | -78 | 0 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 1270.8162 | 780 | 200 | 2250.8162 | 56.27% | 95% | 0% | -89.2449 | 352.9645 | -2750 | -200 | -2597.0355 | 64.93% | 58.27% | 95% | 0% | 1636 | -78
[5 empty] | 2019-07-18 | 3 | 4752.5 | 1516 | -78 | 0 | 0 | 1594 | 376.4221 | 376.4221 | 376.4221 | 1270.8162 | 780 | 200 | 2250.8162 | 56.27% | 95% | 0% | -89.2449 | 287.1772 | -2750 | -200 | -2662.8228 | 66.57% | 58.27% | 95% | 0% | 1594 | -78
[5 empty] | 2019-07-18 | 4 | 4753 | 1492 | -78 | 0 | 0 | 1570 | 338.8293 | 338.8293 | 338.8293 | 1270.8162 | 780 | 200 | 2250.8162 | 56.27% | 95% | 0% | -89.2449 | 249.5845 | -2750 | -200 | -2700.4155 | 67.51% | 58.27% | 95% | 0% | 1570 | -78
[5 empty] | 2019-07-18 | 5 | 4753.5 | 1466 | -77 | 0 | 0 | 1543 | 296.5375 | 296.5375 | 296.5375 | 1270.8162 | 780 | 200 | 2250.8162 | 56.27% | 95% | 0% | -88.1007 | 208.4368 | -2750 | -200 | -2741.5632 | 68.54% | 58.27% | 95% | 0% | 1543 | -77
[5 empty] | 2019-07-18 | 6 | 4754 | 1444 | -77 | 0 | 0 | 1521 | 262.0775 | 262.0775 | 262.0775 | 1270.8162 | 780 | 200 | 2250.8162 | 56.27% | 95% | 0% | -88.1007 | 173.9768 | -2750 | -200 | -2776.0232 | 69.4% | 58.27% | 95% | 0% | 1521 | -77
[5 empty] | 2019-07-18 | 7 | 4754.5 | 1440 | -75 | 0 | 0 | 1515 | 252.6793 | 252.6793 | 252.6793 | 1270.8162 | 780 | 200 | 2250.8162 | 56.27% | 95% | 0% | -85.8124 | 166.867 | -2750 | -200 | -2783.133 | 69.58% | 58.26% | 95% | 0% | 1515 | -75
[5 empty] | 2019-07-18 | 8 | 4755 | 1444 | -74 | 0 | 0 | 1518 | 257.3784 | 257.3784 | 257.3784 | 1270.8162 | 780 | 200 | 2250.8162 | 56.27% | 95% | 0% | -84.6682 | 172.7102 | -2750 | -200 | -2777.2898 | 69.43% | 58.26% | 95% | 0% | 1518 | -74
[5 empty] | 2019-07-18 | 9 | 4755.5 | 1458 | -73 | 0 | 0 | 1531 | 277.7411 | 277.7411 | 277.7411 | 1270.8162 | 780 | 200 | 2250.8162 | 56.27% | 95% | 0% | -83.524 | 194.2171 | -2750 | -200 | -2755.7829 | 68.89% | 58.25% | 95% | 0% | 1531 | -73
[5 empty] | 2019-07-18 | 10 | 4756 | 1455 | -72 | 0 | 0 | 1527 | 271.4757 | 271.4757 | 271.4757 | 1270.8162 | 780 | 200 | 2250.8162 | 56.27% | 95% | 0% | -82.3799 | 189.0958 | -2750 | -200 | -2760.9042 | 69.02% | 58.25% | 95% | 0% | 1527 | -72
[5 empty] | 2019-07-18 | 11 | 4756.5 | 1487 | -73 | 1 | 0 | 1560 | 323.1657 | 323.1657 | 323.1657 | 1270.8162 | 780 | 200 | 2250.8162 | 56.27% | 95% | 0% | -83.524 | 239.6417 | -3550 | -400 | -3710.3583 | 92.76% | 58.24% | 95% | 0% | 1560 | -73
[5 empty] | 2019-07-18 | 12 | 4757 | 1559 | -77 | 1 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 1270.8162 | 780 | 200 | 2250.8162 | 56.27% | 95% | 0% | -88.1007 | 354.1087 | -3550 | -400 | -3595.8913 | 89.9% | 58.24% | 95% | 0% | 1636 | -77
[5 empty] | 2019-07-18 | 13 | 4757.5 | 1724 | -90 | 1 | 0 | 1814 | 721.0223 | 721.0223 | 721.0223 | 1270.8162 | 780 | 200 | 2250.8162 | 56.27% | 95% | 0% | -102.9748 | 618.0474 | -3550 | -400 | -3331.9526 | 83.3% | 58.24% | 95% | 0% | 1814 | -90
[5 empty] | 2019-07-18 | 14 | 4758 | 1857 | -110 | 1 | 0 | 1967 | 960.676 | 960.676 | 960.676 | 1269.2498 | 780 | 200 | 2249.2498 | 56.23% | 95% | 0% | -125.8581 | 834.8179 | -3550 | -400 | -3115.1821 | 77.88% | 58.24% | 95% | 0% | 1967 | -110
[5 empty] | 2019-07-18 | 15 | 4758.5 | 2043 | -139 | 1 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 1269.2498 | 780 | 200 | 2249.2498 | 56.23% | 95% | 0% | -159.0389 | 1138.4055 | -3550 | -400 | -2811.5945 | 70.29% | 58.23% | 95% | 0% | 2182 | -139
[5 empty] | 2019-07-18 | 16 | 4759 | 2100 | -179 | 1 | 0 | 2279 | 1449.3817 | 1449.3817 | 1449.3817 | 1269.2498 | 780 | 200 | 2249.2498 | 56.23% | 95% | 0% | -204.8055 | 1244.5762 | -3550 | -400 | -2705.4238 | 67.64% | 58.23% | 95% | 0% | 2279 | -179
[5 empty] | 2019-07-18 | 17 | 4759.5 | 2119 | -215 | 1 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 1269.2498 | 780 | 200 | 2249.2498 | 56.23% | 95% | 0% | -245.9954 | 1289.5363 | -3550 | -400 | -2660.4637 | 66.51% | 58.23% | 95% | 0% | 2334 | -215
[5 empty] | 2019-07-18 | 18 | 4760 | 2090 | -249 | 1 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 1269.2498 | 780 | 200 | 2249.2498 | 56.23% | 95% | 0% | -284.897 | 1258.4665 | -3550 | -400 | -2691.5335 | 67.29% | 58.23% | 95% | 0% | 2339 | -249
[5 empty] | 2019-07-18 | 19 | 4760.5 | 2076 | -273 | 1 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 1269.2498 | 780 | 200 | 2249.2498 | 56.23% | 95% | 0% | -312.357 | 1246.6702 | -3550 | -400 | -2703.3298 | 67.58% | 58.22% | 95% | 0% | 2349 | -273
[5 empty] | 2019-07-18 | 20 | 4761 | 2028 | -310 | 1 | 0 | 2338 | 1541.7972 | 1541.7972 | 1541.7972 | 1269.2498 | 780 | 200 | 2249.2498 | 56.23% | 95% | 0% | -354.6911 | 1187.1061 | -3550 | -400 | -2762.8939 | 69.07% | 58.22% | 95% | 0% | 2338 | -310
[5 empty] | 2019-07-18 | 21 | 4761.5 | 1975 | -347 | 1 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 1269.2498 | 780 | 200 | 2249.2498 | 56.23% | 95% | 0% | -397.0252 | 1119.7102 | -3550 | -400 | -2830.2898 | 70.76% | 58.22% | 95% | 0% | 2322 | -347
[5 empty] | 2019-07-18 | 22 | 4762 | 1902 | -412 | 1 | 0 | 2314 | 1504.2045 | 1504.2045 | 1504.2045 | 1269.2498 | 780 | 200 | 2249.2498 | 56.23% | 95% | 0% | -471.3959 | 1032.8086 | -3550 | -400 | -2917.1914 | 72.93% | 58.22% | 95% | 0% | 2314 | -412
[5 empty] | 2019-07-18 | 23 | 4762.5 | 1856 | -433 | 1 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 1269.2498 | 780 | 200 | 2249.2498 | 56.23% | 95% | 0% | -495.4233 | 969.622 | -3550 | -400 | -2980.378 | 74.51% | 58.21% | 95% | 0% | 2289 | -433
[5 empty] | 2019-07-18 | 24 | 4763 | 1790 | -473 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 1269.2498 | 780 | 200 | 2249.2498 | 56.23% | 95% | 0% | -541.1899 | 883.1299 | -3550 | -400 | -3066.8701 | 76.67% | 58.21% | 95% | 0% | 2263 | -473
[5 empty] | 2019-07-18 | 25 | 4763.5 | 1730 | -520 | 1 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 1269.2498 | 780 | 200 | 2249.2498 | 56.23% | 95% | 0% | -594.9657 | 808.9915 | -3550 | -400 | -3141.0085 | 78.53% | 58.21% | 95% | 0% | 2250 | -520
[5 empty] | 2019-07-18 | 26 | 4764 | 1733 | -491 | 1 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 1267.6834 | 780 | 200 | 2247.6834 | 56.19% | 95% | 0% | -561.7849 | 801.4468 | -3550 | -400 | -3148.5532 | 78.71% | 58.21% | 95% | 0% | 2224 | -491
[5 empty] | 2019-07-18 | 27 | 4764.5 | 1687 | -514 | 1 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 1267.6834 | 780 | 200 | 2247.6834 | 56.19% | 95% | 0% | -588.1007 | 739.1046 | -3550 | -400 | -3210.8954 | 80.27% | 58.2% | 95% | 0% | 2201 | -514
[5 empty] | 2019-07-18 | 28 | 4765 | 1610 | -552 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 1267.6834 | 780 | 200 | 2247.6834 | 56.19% | 95% | 0% | -631.5789 | 634.5381 | -3550 | -400 | -3315.4619 | 82.89% | 58.2% | 95% | 0% | 2162 | -552
[5 empty] | 2019-07-18 | 29 | 4765.5 | 1555 | -579 | 1 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 1267.6834 | 780 | 200 | 2247.6834 | 56.19% | 95% | 0% | -662.4714 | 559.7875 | -3550 | -400 | -3390.2125 | 84.76% | 58.2% | 95% | 0% | 2134 | -579
[5 empty] | 2019-07-18 | 30 | 4766 | 1560 | -560 | 1 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1267.6834 | 780 | 200 | 2247.6834 | 56.19% | 95% | 0% | -640.7323 | 559.5975 | -3550 | -400 | -3390.4025 | 84.76% | 58.2% | 95% | 0% | 2120 | -560
[5 empty] | 2019-07-18 | 31 | 4766.5 | 1559 | -531 | 1 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 1267.6834 | 780 | 200 | 2247.6834 | 56.19% | 95% | 0% | -607.5515 | 545.7873 | -3550 | -400 | -3404.2127 | 85.11% | 58.19% | 95% | 0% | 2090 | -531
[5 empty] | 2019-07-18 | 32 | 4767 | 1610 | -522 | 1 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 1267.6834 | 780 | 200 | 2247.6834 | 56.19% | 95% | 0% | -597.254 | 621.8721 | -3550 | -400 | -3328.1279 | 83.2% | 58.19% | 95% | 0% | 2132 | -522
[5 empty] | 2019-07-18 | 33 | 4767.5 | 1714 | -459 | 1 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 1267.6834 | 780 | 200 | 2247.6834 | 56.19% | 95% | 0% | -525.1716 | 758.1754 | -3550 | -400 | -3191.8246 | 79.8% | 58.19% | 95% | 0% | 2173 | -459
[5 empty] | 2019-07-18 | 34 | 4768 | 1783 | -438 | 1 | 0 | 2221 | 1358.5326 | 1358.5326 | 1358.5326 | 1267.6834 | 780 | 200 | 2247.6834 | 56.19% | 95% | 0% | -501.1442 | 857.3884 | -3550 | -400 | -3092.6116 | 77.32% | 58.19% | 95% | 0% | 2221 | -438
[5 empty] | 2019-07-18 | 35 | 4768.5 | 1860 | -403 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 1267.6834 | 780 | 200 | 2247.6834 | 56.19% | 95% | 0% | -461.0984 | 963.2215 | -3550 | -400 | -2986.7785 | 74.67% | 58.19% | 95% | 0% | 2263 | -403
[5 empty] | 2019-07-18 | 36 | 4769 | 1943 | -361 | 1 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -413.0435 | 1075.4973 | -3550 | -400 | -2874.5027 | 71.86% | 58.18% | 95% | 0% | 2304 | -361
[5 empty] | 2019-07-18 | 37 | 4769.5 | 2017 | -298 | 1 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -340.9611 | 1164.8097 | -3550 | -400 | -2785.1903 | 69.63% | 58.17% | 95% | 0% | 2315 | -298
[5 empty] | 2019-07-18 | 38 | 4770 | 2070 | -251 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -287.1854 | 1227.9836 | -3550 | -400 | -2722.0164 | 68.05% | 58.17% | 95% | 0% | 2321 | -251
[5 empty] | 2019-07-18 | 39 | 4770.5 | 2140 | -197 | 1 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -225.4005 | 1314.8304 | -3550 | -400 | -2635.1696 | 65.88% | 58.17% | 95% | 0% | 2337 | -197
[5 empty] | 2019-07-18 | 40 | 4771 | 2195 | -155 | 1 | 0 | 2350 | 1560.5936 | 1560.5936 | 1560.5936 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -177.3455 | 1383.248 | -3550 | -400 | -2566.752 | 64.17% | 58.16% | 95% | 0% | 2350 | -155
[5 empty] | 2019-07-18 | 41 | 4771.5 | 2203 | -116 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -132.7231 | 1379.3132 | -3550 | -400 | -2570.6868 | 64.27% | 58.16% | 95% | 0% | 2319 | -116
[5 empty] | 2019-07-18 | 42 | 4772 | 2197 | -87 | 1 | 0 | 2284 | 1457.2135 | 1457.2135 | 1457.2135 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -99.5423 | 1357.6712 | -3550 | -400 | -2592.3288 | 64.81% | 58.16% | 95% | 0% | 2284 | -87
[5 empty] | 2019-07-18 | 43 | 4772.5 | 2192 | -76 | 1 | 0 | 2268 | 1432.1517 | 1432.1517 | 1432.1517 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -86.9565 | 1345.1952 | -3550 | -400 | -2604.8048 | 65.12% | 58.16% | 95% | 0% | 2268 | -76
[5 empty] | 2019-07-18 | 44 | 4773 | 2167 | -73 | 1 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -83.524 | 1304.7695 | -3550 | -400 | -2645.2305 | 66.13% | 58.15% | 95% | 0% | 2240 | -73
[5 empty] | 2019-07-18 | 45 | 4773.5 | 2088 | -73 | 0 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -83.524 | 1181.0267 | -2750 | -200 | -1768.9733 | 44.22% | 58.14% | 95% | 0% | 2161 | -73
[5 empty] | 2019-07-18 | 46 | 4774 | 1986 | -73 | 0 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -83.524 | 1021.2575 | -2750 | -200 | -1928.7425 | 48.22% | 58.14% | 95% | 0% | 2059 | -73
[5 empty] | 2019-07-18 | 47 | 4774.5 | 1855 | -73 | 0 | 0 | 1928 | 899.5878 | 899.5878 | 899.5878 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -83.524 | 816.0638 | -2750 | -200 | -2133.9362 | 53.35% | 58.14% | 95% | 0% | 1928 | -73
[5 empty] | 2019-07-18 | 48 | 4775 | 1740 | -73 | 0 | 0 | 1813 | 719.4559 | 719.4559 | 719.4559 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -83.524 | 635.9319 | -2750 | -200 | -2314.0681 | 57.85% | 58.14% | 95% | 0% | 1813 | -73
[5 empty] | 2019-07-19 | 1 | 4775.5 | 1645 | -71 | 0 | 0 | 1716 | 567.5185 | 567.5185 | 567.5185 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -81.2357 | 486.2829 | -2750 | -200 | -2463.7171 | 61.59% | 58.14% | 95% | 0% | 1716 | -71
[5 empty] | 2019-07-19 | 2 | 4776 | 1597 | -68 | 0 | 0 | 1665 | 487.634 | 487.634 | 487.634 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -77.8032 | 409.8308 | -2750 | -200 | -2540.1692 | 63.5% | 58.13% | 95% | 0% | 1665 | -68
[5 empty] | 2019-07-19 | 3 | 4776.5 | 1546 | -68 | 0 | 0 | 1614 | 407.7494 | 407.7494 | 407.7494 | 1266.1171 | 780 | 200 | 2246.1171 | 56.15% | 95% | 0% | -77.8032 | 329.9462 | -2750 | -200 | -2620.0538 | 65.5% | 58.13% | 95% | 0% | 1614 | -68
[5 empty] | 2019-07-19 | 4 | 4777 | 1527 | -68 | 0 | 0 | 1595 | 377.9885 | 377.9885 | 377.9885 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -77.8032 | 300.1853 | -2750 | -200 | -2649.8147 | 66.25% | 58.13% | 95% | 0% | 1595 | -68
[5 empty] | 2019-07-19 | 5 | 4777.5 | 1498 | -67 | 0 | 0 | 1565 | 330.9975 | 330.9975 | 330.9975 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -76.659 | 254.3385 | -2750 | -200 | -2695.6615 | 67.39% | 58.12% | 95% | 0% | 1565 | -67
[5 empty] | 2019-07-19 | 6 | 4778 | 1482 | -66 | 0 | 0 | 1548 | 304.3693 | 304.3693 | 304.3693 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -75.5149 | 228.8545 | -2750 | -200 | -2721.1455 | 68.03% | 58.12% | 95% | 0% | 1548 | -66
[5 empty] | 2019-07-19 | 7 | 4778.5 | 1464 | -64 | 0 | 0 | 1528 | 273.042 | 273.042 | 273.042 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -73.2265 | 199.8155 | -2750 | -200 | -2750.1845 | 68.75% | 58.11% | 95% | 0% | 1528 | -64
[5 empty] | 2019-07-19 | 8 | 4779 | 1453 | -63 | 0 | 0 | 1516 | 254.2457 | 254.2457 | 254.2457 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -72.0824 | 182.1633 | -2750 | -200 | -2767.8367 | 69.2% | 58.11% | 95% | 0% | 1516 | -63
[5 empty] | 2019-07-19 | 9 | 4779.5 | 1464 | -60 | 0 | 0 | 1524 | 266.7766 | 266.7766 | 266.7766 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -68.6499 | 198.1267 | -2750 | -200 | -2751.8733 | 68.8% | 58.11% | 95% | 0% | 1524 | -60
[5 empty] | 2019-07-19 | 10 | 4780 | 1467 | -57 | 0 | 0 | 1524 | 266.7766 | 266.7766 | 266.7766 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -65.2174 | 201.5592 | -2750 | -200 | -2748.4408 | 68.71% | 58.11% | 95% | 0% | 1524 | -57
[5 empty] | 2019-07-19 | 11 | 4780.5 | 1479 | -59 | 1 | 0 | 1538 | 288.7057 | 288.7057 | 288.7057 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -67.5057 | 221.2 | -3550 | -400 | -3728.8 | 93.22% | 58.1% | 95% | 0% | 1538 | -59
[5 empty] | 2019-07-19 | 12 | 4781 | 1538 | -71 | 1 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -81.2357 | 318.6819 | -3550 | -400 | -3631.3181 | 90.78% | 58.1% | 95% | 0% | 1609 | -71
[5 empty] | 2019-07-19 | 13 | 4781.5 | 1699 | -86 | 1 | 0 | 1785 | 675.5977 | 675.5977 | 675.5977 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -98.3982 | 577.1995 | -3550 | -400 | -3372.8005 | 84.32% | 58.1% | 95% | 0% | 1785 | -86
[5 empty] | 2019-07-19 | 14 | 4782 | 1853 | -107 | 1 | 0 | 1960 | 949.7115 | 949.7115 | 949.7115 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -122.4256 | 827.2858 | -3550 | -400 | -3122.7142 | 78.07% | 58.1% | 95% | 0% | 1960 | -107
[5 empty] | 2019-07-19 | 15 | 4782.5 | 2057 | -116 | 1 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -132.7231 | 1150.624 | -3550 | -400 | -2799.376 | 69.98% | 58.09% | 95% | 0% | 2173 | -116
[5 empty] | 2019-07-19 | 16 | 4783 | 2172 | -131 | 1 | 0 | 2303 | 1486.9744 | 1486.9744 | 1486.9744 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -149.8856 | 1337.0889 | -3550 | -400 | -2612.9111 | 65.32% | 58.09% | 95% | 0% | 2303 | -131
[5 empty] | 2019-07-19 | 17 | 4783.5 | 2227 | -159 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 1264.5507 | 780 | 200 | 2244.5507 | 56.11% | 95% | 0% | -181.9222 | 1435.0605 | -3550 | -400 | -2514.9395 | 62.87% | 58.09% | 95% | 0% | 2386 | -159
[5 empty] | 2019-07-19 | 18 | 4784 | 2204 | -181 | 1 | 0 | 2385 | 1615.4163 | 1615.4163 | 1615.4163 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -207.0938 | 1408.3225 | -3550 | -400 | -2541.6775 | 63.54% | 58.09% | 95% | 0% | 2385 | -181
[5 empty] | 2019-07-19 | 19 | 4784.5 | 2198 | -223 | 1 | 0 | 2421 | 1671.8054 | 1671.8054 | 1671.8054 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -255.1487 | 1416.6567 | -3550 | -400 | -2533.3433 | 63.33% | 58.08% | 95% | 0% | 2421 | -223
[5 empty] | 2019-07-19 | 20 | 4785 | 2190 | -248 | 1 | 0 | 2438 | 1698.4336 | 1698.4336 | 1698.4336 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -283.7529 | 1414.6808 | -3550 | -400 | -2535.3192 | 63.38% | 58.08% | 95% | 0% | 2438 | -248
[5 empty] | 2019-07-19 | 21 | 4785.5 | 2194 | -246 | 1 | 0 | 2440 | 1701.5664 | 1701.5664 | 1701.5664 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -281.4645 | 1420.1018 | -3550 | -400 | -2529.8982 | 63.25% | 58.08% | 95% | 0% | 2440 | -246
[5 empty] | 2019-07-19 | 22 | 4786 | 2168 | -263 | 1 | 0 | 2431 | 1687.4691 | 1687.4691 | 1687.4691 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -300.9153 | 1386.5538 | -3550 | -400 | -2563.4462 | 64.09% | 58.07% | 95% | 0% | 2431 | -263
[5 empty] | 2019-07-19 | 23 | 4786.5 | 2150 | -283 | 1 | 0 | 2433 | 1690.6018 | 1690.6018 | 1690.6018 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -323.7986 | 1366.8032 | -3550 | -400 | -2583.1968 | 64.58% | 58.07% | 95% | 0% | 2433 | -283
[5 empty] | 2019-07-19 | 24 | 4787 | 2173 | -289 | 1 | 0 | 2462 | 1736.0264 | 1736.0264 | 1736.0264 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -330.6636 | 1405.3628 | -3550 | -400 | -2544.6372 | 63.62% | 58.07% | 95% | 0% | 2462 | -289
[5 empty] | 2019-07-19 | 25 | 4787.5 | 2171 | -303 | 1 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -346.6819 | 1408.1408 | -3550 | -400 | -2541.8592 | 63.55% | 58.06% | 95% | 0% | 2474 | -303
[5 empty] | 2019-07-19 | 26 | 4788 | 2124 | -312 | 1 | 0 | 2436 | 1695.3009 | 1695.3009 | 1695.3009 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -356.9794 | 1338.3215 | -3550 | -400 | -2611.6785 | 65.29% | 58.05% | 95% | 0% | 2436 | -312
[5 empty] | 2019-07-19 | 27 | 4788.5 | 2083 | -308 | 1 | 0 | 2391 | 1624.8145 | 1624.8145 | 1624.8145 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -352.4027 | 1272.4118 | -3550 | -400 | -2677.5882 | 66.94% | 58.05% | 95% | 0% | 2391 | -308
[5 empty] | 2019-07-19 | 28 | 4789 | 2009 | -338 | 1 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -386.7277 | 1169.1668 | -3550 | -400 | -2780.8332 | 69.52% | 58.05% | 95% | 0% | 2347 | -338
[5 empty] | 2019-07-19 | 29 | 4789.5 | 2019 | -319 | 1 | 0 | 2338 | 1541.7972 | 1541.7972 | 1541.7972 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -364.9886 | 1176.8086 | -3550 | -400 | -2773.1914 | 69.33% | 58.04% | 95% | 0% | 2338 | -319
[5 empty] | 2019-07-19 | 30 | 4790 | 2031 | -308 | 1 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -352.4027 | 1190.9608 | -3550 | -400 | -2759.0392 | 68.98% | 58.03% | 95% | 0% | 2339 | -308
[5 empty] | 2019-07-19 | 31 | 4790.5 | 2074 | -244 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -279.1762 | 1231.2937 | -3550 | -400 | -2718.7063 | 67.97% | 58.03% | 95% | 0% | 2318 | -244
[5 empty] | 2019-07-19 | 32 | 4791 | 2103 | -218 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -249.4279 | 1265.7411 | -3550 | -400 | -2684.2589 | 67.11% | 58.03% | 95% | 0% | 2321 | -218
[5 empty] | 2019-07-19 | 33 | 4791.5 | 2148 | -206 | 1 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -235.6979 | 1331.1611 | -3550 | -400 | -2618.8389 | 65.47% | 58.03% | 95% | 0% | 2354 | -206
[5 empty] | 2019-07-19 | 34 | 4792 | 2204 | -185 | 1 | 0 | 2389 | 1621.6818 | 1621.6818 | 1621.6818 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -211.6705 | 1410.0113 | -3550 | -400 | -2539.9887 | 63.5% | 58.03% | 95% | 0% | 2389 | -185
[5 empty] | 2019-07-19 | 35 | 4792.5 | 2262 | -164 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -187.643 | 1491.9942 | -3550 | -400 | -2458.0058 | 61.45% | 58.03% | 95% | 0% | 2426 | -164
[5 empty] | 2019-07-19 | 36 | 4793 | 2281 | -156 | 1 | 0 | 2437 | 1696.8673 | 1696.8673 | 1696.8673 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -178.4897 | 1518.3776 | -3550 | -400 | -2431.6224 | 60.79% | 58.02% | 95% | 0% | 2437 | -156
[5 empty] | 2019-07-19 | 37 | 4793.5 | 2276 | -145 | 1 | 0 | 2421 | 1671.8054 | 1671.8054 | 1671.8054 | 1262.9843 | 780 | 200 | 2242.9843 | 56.07% | 95% | 0% | -165.9039 | 1505.9016 | -3550 | -400 | -2444.0984 | 61.1% | 58.02% | 95% | 0% | 2421 | -145
[5 empty] | 2019-07-19 | 38 | 4794 | 2272 | -133 | 1 | 0 | 2405 | 1646.7436 | 1646.7436 | 1646.7436 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -152.1739 | 1494.5697 | -3550 | -400 | -2455.4303 | 61.39% | 58.02% | 95% | 0% | 2405 | -133
[5 empty] | 2019-07-19 | 39 | 4794.5 | 2233 | -122 | 1 | 0 | 2355 | 1568.4254 | 1568.4254 | 1568.4254 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -139.5881 | 1428.8373 | -3550 | -400 | -2521.1627 | 63.03% | 58.01% | 95% | 0% | 2355 | -122
[5 empty] | 2019-07-19 | 40 | 4795 | 2204 | -114 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -130.4348 | 1380.0351 | -3550 | -400 | -2569.9649 | 64.25% | 58.01% | 95% | 0% | 2318 | -114
[5 empty] | 2019-07-19 | 41 | 4795.5 | 2149 | -106 | 1 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -121.2815 | 1290.5075 | -3550 | -400 | -2659.4925 | 66.49% | 58.01% | 95% | 0% | 2255 | -106
[5 empty] | 2019-07-19 | 42 | 4796 | 2116 | -102 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -116.7048 | 1237.1287 | -3550 | -400 | -2712.8713 | 67.82% | 58.01% | 95% | 0% | 2218 | -102
[5 empty] | 2019-07-19 | 43 | 4796.5 | 2070 | -101 | 1 | 0 | 2171 | 1280.2143 | 1280.2143 | 1280.2143 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -115.5606 | 1164.6537 | -3550 | -400 | -2785.3463 | 69.63% | 58.01% | 95% | 0% | 2171 | -101
[5 empty] | 2019-07-19 | 44 | 4797 | 2034 | -101 | 1 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -115.5606 | 1108.2646 | -3550 | -400 | -2841.7354 | 71.04% | 58.01% | 95% | 0% | 2135 | -101
[5 empty] | 2019-07-19 | 45 | 4797.5 | 1967 | -100 | 0 | 0 | 2067 | 1117.3124 | 1117.3124 | 1117.3124 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -114.4165 | 1002.896 | -2750 | -200 | -1947.104 | 48.68% | 58% | 95% | 0% | 2067 | -100
[5 empty] | 2019-07-19 | 46 | 4798 | 1849 | -99 | 0 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -113.2723 | 817.6428 | -2750 | -200 | -2132.3572 | 53.31% | 58% | 95% | 0% | 1948 | -99
[5 empty] | 2019-07-19 | 47 | 4798.5 | 1749 | -98 | 1 | 0 | 1847 | 772.7123 | 772.7123 | 772.7123 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -112.1281 | 660.5841 | -3550 | -400 | -3289.4159 | 82.24% | 58% | 95% | 0% | 1847 | -98
[5 empty] | 2019-07-19 | 48 | 4799 | 1635 | -98 | 1 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -112.1281 | 482.0186 | -3550 | -400 | -3467.9814 | 86.7% | 58% | 95% | 0% | 1733 | -98
[5 empty] | 2019-07-20 | 1 | 4799.5 | 1558 | -98 | 1 | 0 | 1656 | 473.5367 | 473.5367 | 473.5367 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -112.1281 | 361.4085 | -3550 | -400 | -3588.5915 | 89.71% | 57.99% | 95% | 0% | 1656 | -98
[5 empty] | 2019-07-20 | 2 | 4800 | 1489 | -97 | 1 | 0 | 1586 | 363.8912 | 363.8912 | 363.8912 | 1261.418 | 780 | 200 | 2241.418 | 56.04% | 95% | 0% | -110.984 | 252.9072 | -3550 | -400 | -3697.0928 | 92.43% | 57.99% | 95% | 0% | 1586 | -97
[5 empty] | 2019-07-20 | 3 | 4800.5 | 1439 | -97 | 1 | 0 | 1536 | 285.573 | 285.573 | 285.573 | 1259.8516 | 780 | 200 | 2239.8516 | 56% | 95% | 0% | -110.984 | 174.589 | -3550 | -400 | -3775.411 | 94.39% | 57.99% | 95% | 0% | 1536 | -97
[5 empty] | 2019-07-20 | 4 | 4801 | 1409 | -96 | 1 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 1259.8516 | 780 | 200 | 2239.8516 | 56% | 95% | 0% | -109.8398 | 127.1758 | -3550 | -400 | -3822.8242 | 95.57% | 57.99% | 95% | 0% | 1505 | -96
[5 empty] | 2019-07-20 | 5 | 4801.5 | 1373 | -95 | 1 | 0 | 1468 | 179.0602 | 179.0602 | 179.0602 | 1259.8516 | 780 | 200 | 2239.8516 | 56% | 95% | 0% | -108.6957 | 70.3645 | -3550 | -400 | -3879.6355 | 96.99% | 57.99% | 95% | 0% | 1468 | -95
[5 empty] | 2019-07-20 | 6 | 4802 | 1351 | -95 | 1 | 0 | 1446 | 144.6002 | 144.6002 | 144.6002 | 1259.8516 | 780 | 200 | 2239.8516 | 56% | 95% | 0% | -108.6957 | 35.9045 | -3550 | -400 | -3914.0955 | 97.85% | 57.99% | 95% | 0% | 1446 | -95
[5 empty] | 2019-07-20 | 7 | 4802.5 | 1329 | -93 | 1 | 0 | 1422 | 107.0074 | 107.0074 | 107.0074 | 1259.8516 | 780 | 200 | 2239.8516 | 56% | 95% | 0% | -106.4073 | 0.6001 | -3550 | -400 | -3949.3999 | 98.73% | 57.99% | 95% | 0% | 1422 | -93
[5 empty] | 2019-07-20 | 8 | 4803 | 1314 | -92 | 1 | 0 | 1406 | 81.9456 | 81.9456 | 81.9456 | 1259.8516 | 780 | 200 | 2239.8516 | 56% | 95% | 0% | -105.2632 | -23.3176 | -3550 | -400 | -3973.3176 | 99.33% | 57.98% | 95% | 0% | 1406 | -92
[5 empty] | 2019-07-20 | 9 | 4803.5 | 1304 | -91 | 1 | 0 | 1395 | 64.7156 | 64.7156 | 64.7156 | 1259.8516 | 780 | 200 | 2239.8516 | 56% | 95% | 0% | -104.119 | -39.4034 | -3550 | -400 | -3989.4034 | 99.74% | 57.98% | 95% | 0% | 1395 | -91
[5 empty] | 2019-07-20 | 10 | 4804 | 1296 | -90 | 1 | 0 | 1386 | 50.6183 | 50.6183 | 50.6183 | 1259.8516 | 780 | 200 | 2239.8516 | 56% | 95% | 0% | -102.9748 | -52.3565 | -3550 | -400 | -4002.3565 | 100.1% | 57.98% | 95% | 0% | 1386 | -90
[5 empty] | 2019-07-20 | 11 | 4804.5 | 1295 | -89 | 1 | 0 | 1384 | 47.4856 | 47.4856 | 47.4856 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -101.8307 | -54.3451 | -3550 | -400 | -4004.3451 | 100.1% | 57.97% | 95% | 0% | 1384 | -89
[5 empty] | 2019-07-20 | 12 | 4805 | 1313 | -93 | 1 | 0 | 1406 | 81.9456 | 81.9456 | 81.9456 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -106.4073 | -24.4617 | -3550 | -400 | -3974.4617 | 99.36% | 57.97% | 95% | 0% | 1406 | -93
[5 empty] | 2019-07-20 | 13 | 4805.5 | 1371 | -109 | 1 | 0 | 1480 | 197.8566 | 197.8566 | 197.8566 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -124.714 | 73.1426 | -3550 | -400 | -3876.8574 | 96.92% | 57.97% | 95% | 0% | 1480 | -109
[5 empty] | 2019-07-20 | 14 | 4806 | 1411 | -131 | 1 | 0 | 1542 | 294.9711 | 294.9711 | 294.9711 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -149.8856 | 145.0856 | -3550 | -400 | -3804.9144 | 95.12% | 57.97% | 95% | 0% | 1542 | -131
[5 empty] | 2019-07-20 | 15 | 4806.5 | 1469 | -161 | 1 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -184.2105 | 248.6007 | -3550 | -400 | -3701.3993 | 92.53% | 57.97% | 95% | 0% | 1630 | -161
[5 empty] | 2019-07-20 | 16 | 4807 | 1518 | -210 | 1 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -240.2746 | 346.0403 | -3550 | -400 | -3603.9597 | 90.1% | 57.97% | 95% | 0% | 1728 | -210
[5 empty] | 2019-07-20 | 17 | 4807.5 | 1579 | -236 | 1 | 0 | 1815 | 722.5886 | 722.5886 | 722.5886 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -270.0229 | 452.5657 | -3550 | -400 | -3497.4343 | 87.44% | 57.96% | 95% | 0% | 1815 | -236
[5 empty] | 2019-07-20 | 18 | 4808 | 1552 | -308 | 1 | 0 | 1860 | 793.075 | 793.075 | 793.075 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -352.4027 | 440.6723 | -3550 | -400 | -3509.3277 | 87.73% | 57.96% | 95% | 0% | 1860 | -308
[5 empty] | 2019-07-20 | 19 | 4808.5 | 1565 | -330 | 1 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -377.5744 | 470.3234 | -3550 | -400 | -3479.6766 | 86.99% | 57.96% | 95% | 0% | 1895 | -330
[5 empty] | 2019-07-20 | 20 | 4809 | 1532 | -359 | 1 | 0 | 1891 | 841.6323 | 841.6323 | 841.6323 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -410.7551 | 430.8772 | -3550 | -400 | -3519.1228 | 87.98% | 57.96% | 95% | 0% | 1891 | -359
[5 empty] | 2019-07-20 | 21 | 4809.5 | 1468 | -427 | 1 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -488.5584 | 359.3394 | -3550 | -400 | -3590.6606 | 89.77% | 57.95% | 95% | 0% | 1895 | -427
[5 empty] | 2019-07-20 | 22 | 4810 | 1399 | -504 | 1 | 0 | 1903 | 860.4287 | 860.4287 | 860.4287 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -576.659 | 283.7697 | -3550 | -400 | -3666.2303 | 91.66% | 57.95% | 95% | 0% | 1903 | -504
[5 empty] | 2019-07-20 | 23 | 4810.5 | 1371 | -515 | 1 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -589.2449 | 244.5556 | -3550 | -400 | -3705.4444 | 92.64% | 57.95% | 95% | 0% | 1886 | -515
[5 empty] | 2019-07-20 | 24 | 4811 | 1304 | -551 | 1 | 0 | 1855 | 785.2432 | 785.2432 | 785.2432 | 1258.2852 | 780 | 200 | 2238.2852 | 55.96% | 95% | 0% | -630.4348 | 154.8084 | -3550 | -400 | -3795.1916 | 94.88% | 57.95% | 95% | 0% | 1855 | -551
[5 empty] | 2019-07-20 | 25 | 4811.5 | 1281 | -555 | 1 | 0 | 1836 | 755.4823 | 755.4823 | 755.4823 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -635.0114 | 120.4708 | -3550 | -400 | -3829.5292 | 95.74% | 57.95% | 95% | 0% | 1836 | -555
[5 empty] | 2019-07-20 | 26 | 4812 | 1229 | -578 | 1 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -661.3272 | 48.7305 | -3550 | -400 | -3901.2695 | 97.53% | 57.95% | 95% | 0% | 1807 | -578
[5 empty] | 2019-07-20 | 27 | 4812.5 | 1149 | -610 | 0 | 0 | 1759 | 634.8722 | 634.8722 | 634.8722 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -697.9405 | -63.0683 | -2750 | -200 | -3013.0683 | 75.33% | 57.95% | 95% | 0% | 1759 | -610
[5 empty] | 2019-07-20 | 28 | 4813 | 1081 | -615 | 1 | 0 | 1696 | 536.1913 | 536.1913 | 536.1913 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -703.6613 | -167.4701 | -3550 | -400 | -4117.4701 | 102.9% | 57.94% | 95% | 0% | 1696 | -615
[5 empty] | 2019-07-20 | 29 | 4813.5 | 1037 | -631 | 1 | 0 | 1668 | 492.3331 | 492.3331 | 492.3331 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -721.968 | -229.6349 | -3550 | -400 | -4179.6349 | 104.5% | 57.94% | 95% | 0% | 1668 | -631
[5 empty] | 2019-07-20 | 30 | 4814 | 1026 | -607 | 1 | 0 | 1633 | 437.5103 | 437.5103 | 437.5103 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -694.508 | -256.9977 | -3550 | -400 | -4206.9977 | 105.2% | 57.94% | 95% | 0% | 1633 | -607
[5 empty] | 2019-07-20 | 31 | 4814.5 | 1024 | -601 | 1 | 0 | 1625 | 424.9794 | 424.9794 | 424.9794 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -687.643 | -262.6636 | -3550 | -400 | -4212.6636 | 105.3% | 57.93% | 95% | 0% | 1625 | -601
[5 empty] | 2019-07-20 | 32 | 4815 | 1064 | -578 | 1 | 0 | 1642 | 451.6076 | 451.6076 | 451.6076 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -661.3272 | -209.7196 | -3550 | -400 | -4159.7196 | 104% | 57.92% | 95% | 0% | 1642 | -578
[5 empty] | 2019-07-20 | 33 | 4815.5 | 1137 | -541 | 1 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -618.9931 | -110.9964 | -3550 | -400 | -4060.9964 | 101.5% | 57.91% | 95% | 0% | 1678 | -541
[5 empty] | 2019-07-20 | 34 | 4816 | 1275 | -464 | 1 | 0 | 1739 | 603.5449 | 603.5449 | 603.5449 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -530.8924 | 72.6525 | -3550 | -400 | -3877.3475 | 96.93% | 57.91% | 95% | 0% | 1739 | -464
[5 empty] | 2019-07-20 | 35 | 4816.5 | 1381 | -430 | 1 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -491.9908 | 224.3323 | -3550 | -400 | -3725.6677 | 93.14% | 57.91% | 95% | 0% | 1811 | -430
[5 empty] | 2019-07-20 | 36 | 4817 | 1453 | -413 | 1 | 0 | 1866 | 802.4732 | 802.4732 | 802.4732 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -472.54 | 329.9332 | -3550 | -400 | -3620.0668 | 90.5% | 57.91% | 95% | 0% | 1866 | -413
[5 empty] | 2019-07-20 | 37 | 4817.5 | 1534 | -360 | 1 | 0 | 1894 | 846.3314 | 846.3314 | 846.3314 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -411.8993 | 434.4321 | -3550 | -400 | -3515.5679 | 87.89% | 57.91% | 95% | 0% | 1894 | -360
[5 empty] | 2019-07-20 | 38 | 4818 | 1644 | -291 | 1 | 0 | 1935 | 910.5523 | 910.5523 | 910.5523 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -332.9519 | 577.6004 | -3550 | -400 | -3372.3996 | 84.31% | 57.91% | 95% | 0% | 1935 | -291
[5 empty] | 2019-07-20 | 39 | 4818.5 | 1736 | -231 | 1 | 0 | 1967 | 960.676 | 960.676 | 960.676 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -264.3021 | 696.374 | -3550 | -400 | -3253.626 | 81.34% | 57.9% | 95% | 0% | 1967 | -231
[5 empty] | 2019-07-20 | 40 | 4819 | 1789 | -178 | 1 | 0 | 1967 | 960.676 | 960.676 | 960.676 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -203.6613 | 757.0147 | -3550 | -400 | -3192.9853 | 79.82% | 57.89% | 95% | 0% | 1967 | -178
[5 empty] | 2019-07-20 | 41 | 4819.5 | 1820 | -133 | 1 | 0 | 1953 | 938.7469 | 938.7469 | 938.7469 | 1256.7189 | 780 | 200 | 2236.7189 | 55.92% | 95% | 0% | -152.1739 | 786.573 | -3550 | -400 | -3163.427 | 79.09% | 57.89% | 95% | 0% | 1953 | -133
[5 empty] | 2019-07-20 | 42 | 4820 | 1829 | -104 | 1 | 0 | 1933 | 907.4196 | 907.4196 | 907.4196 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -118.9931 | 788.4265 | -3550 | -400 | -3161.5735 | 79.04% | 57.89% | 95% | 0% | 1933 | -104
[5 empty] | 2019-07-20 | 43 | 4820.5 | 1844 | -92 | 1 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -105.2632 | 806.8556 | -3550 | -400 | -3143.1444 | 78.58% | 57.89% | 95% | 0% | 1936 | -92
[5 empty] | 2019-07-20 | 44 | 4821 | 1851 | -86 | 1 | 0 | 1937 | 913.6851 | 913.6851 | 913.6851 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -98.3982 | 815.2869 | -3550 | -400 | -3134.7131 | 78.37% | 57.89% | 95% | 0% | 1937 | -86
[5 empty] | 2019-07-20 | 45 | 4821.5 | 1823 | -84 | 1 | 0 | 1907 | 866.6941 | 866.6941 | 866.6941 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -96.1098 | 770.5843 | -3550 | -400 | -3179.4157 | 79.49% | 57.88% | 95% | 0% | 1907 | -84
[5 empty] | 2019-07-20 | 46 | 4822 | 1756 | -82 | 0 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -93.8215 | 664.7935 | -2750 | -200 | -2285.2065 | 57.13% | 57.88% | 95% | 0% | 1838 | -82
[5 empty] | 2019-07-20 | 47 | 4822.5 | 1674 | -81 | 0 | 0 | 1755 | 628.6068 | 628.6068 | 628.6068 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -92.6773 | 535.9294 | -2750 | -200 | -2414.0706 | 60.35% | 57.88% | 95% | 0% | 1755 | -81
[5 empty] | 2019-07-20 | 48 | 4823 | 1590 | -81 | 0 | 0 | 1671 | 497.0322 | 497.0322 | 497.0322 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -92.6773 | 404.3548 | -2750 | -200 | -2545.6452 | 63.64% | 57.88% | 95% | 0% | 1671 | -81
[5 empty] | 2019-07-21 | 1 | 4823.5 | 1528 | -76 | 0 | 0 | 1604 | 392.0857 | 392.0857 | 392.0857 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -86.9565 | 305.1292 | -2750 | -200 | -2644.8708 | 66.12% | 57.86% | 95% | 0% | 1604 | -76
[5 empty] | 2019-07-21 | 2 | 4824 | 1477 | -72 | 0 | 0 | 1549 | 305.9357 | 305.9357 | 305.9357 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -82.3799 | 223.5558 | -2750 | -200 | -2726.4442 | 68.16% | 57.86% | 95% | 0% | 1549 | -72
[5 empty] | 2019-07-21 | 3 | 4824.5 | 1438 | -72 | 0 | 0 | 1510 | 244.8475 | 244.8475 | 244.8475 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -82.3799 | 162.4676 | -2750 | -200 | -2787.5324 | 69.69% | 57.86% | 95% | 0% | 1510 | -72
[5 empty] | 2019-07-21 | 4 | 4825 | 1420 | -73 | 0 | 0 | 1493 | 218.2193 | 218.2193 | 218.2193 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -83.524 | 134.6953 | -2750 | -200 | -2815.3047 | 70.38% | 57.86% | 95% | 0% | 1493 | -73
[5 empty] | 2019-07-21 | 5 | 4825.5 | 1384 | -72 | 0 | 0 | 1456 | 160.2638 | 160.2638 | 160.2638 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -82.3799 | 77.8839 | -2750 | -200 | -2872.1161 | 71.8% | 57.85% | 95% | 0% | 1456 | -72
[5 empty] | 2019-07-21 | 6 | 4826 | 1355 | -72 | 0 | 0 | 1427 | 114.8392 | 114.8392 | 114.8392 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -82.3799 | 32.4594 | -2750 | -200 | -2917.5406 | 72.94% | 57.85% | 95% | 0% | 1427 | -72
[5 empty] | 2019-07-21 | 7 | 4826.5 | 1331 | -72 | 0 | 0 | 1403 | 77.2465 | 77.2465 | 77.2465 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -82.3799 | -5.1334 | -2750 | -200 | -2955.1334 | 73.88% | 57.85% | 95% | 0% | 1403 | -72
[5 empty] | 2019-07-21 | 8 | 4827 | 1320 | -72 | 0 | 0 | 1392 | 60.0165 | 60.0165 | 60.0165 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -82.3799 | -22.3634 | -2750 | -200 | -2972.3634 | 74.31% | 57.85% | 95% | 0% | 1392 | -72
[5 empty] | 2019-07-21 | 9 | 4827.5 | 1311 | -71 | 0 | 0 | 1382 | 44.3528 | 44.3528 | 44.3528 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -81.2357 | -36.8829 | -2750 | -200 | -2986.8829 | 74.67% | 57.84% | 95% | 0% | 1382 | -71
[5 empty] | 2019-07-21 | 10 | 4828 | 1302 | -70 | 1 | 0 | 1372 | 28.6892 | 28.6892 | 28.6892 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -80.0915 | -51.4023 | -3550 | -400 | -4001.4023 | 100% | 57.84% | 95% | 0% | 1372 | -70
[5 empty] | 2019-07-21 | 11 | 4828.5 | 1285 | -69 | 1 | 0 | 1354 | 0.49464 | 0.49464 | 0.49464 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -78.9474 | -78.4527 | -3550 | -400 | -4028.4527 | 100.7% | 57.84% | 95% | 0% | 1354 | -69
[5 empty] | 2019-07-21 | 12 | 4829 | 1274 | -77 | 1 | 0 | 1351 | -4.2045 | -4.2045 | -4.2045 | 1255.1525 | 780 | 200 | 2235.1525 | 55.88% | 95% | 0% | -88.1007 | -92.3051 | -3550 | -400 | -4042.3051 | 101.1% | 57.84% | 95% | 0% | 1351 | -77
[5 empty] | 2019-07-21 | 13 | 4829.5 | 1297 | -97 | 1 | 0 | 1394 | 63.1492 | 63.1492 | 63.1492 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -110.984 | -47.8348 | -3550 | -400 | -3997.8348 | 99.95% | 57.83% | 95% | 0% | 1394 | -97
[5 empty] | 2019-07-21 | 14 | 4830 | 1299 | -127 | 1 | 0 | 1426 | 113.2729 | 113.2729 | 113.2729 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -145.3089 | -32.036 | -3550 | -400 | -3982.036 | 99.55% | 57.83% | 95% | 0% | 1426 | -127
[5 empty] | 2019-07-21 | 15 | 4830.5 | 1313 | -176 | 1 | 0 | 1489 | 211.9538 | 211.9538 | 211.9538 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -201.373 | 10.5808 | -3550 | -400 | -3939.4192 | 98.49% | 57.83% | 95% | 0% | 1489 | -176
[5 empty] | 2019-07-21 | 16 | 4831 | 1314 | -222 | 1 | 0 | 1536 | 285.573 | 285.573 | 285.573 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -254.0046 | 31.5684 | -3550 | -400 | -3918.4316 | 97.96% | 57.82% | 95% | 0% | 1536 | -222
[5 empty] | 2019-07-21 | 17 | 4831.5 | 1341 | -263 | 1 | 0 | 1604 | 392.0857 | 392.0857 | 392.0857 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -300.9153 | 91.1704 | -3550 | -400 | -3858.8296 | 96.47% | 57.82% | 95% | 0% | 1604 | -263
[5 empty] | 2019-07-21 | 18 | 4832 | 1337 | -313 | 1 | 0 | 1650 | 464.1385 | 464.1385 | 464.1385 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -358.1236 | 106.0149 | -3550 | -400 | -3843.9851 | 96.1% | 57.81% | 95% | 0% | 1650 | -313
[5 empty] | 2019-07-21 | 19 | 4832.5 | 1302 | -382 | 1 | 0 | 1684 | 517.3949 | 517.3949 | 517.3949 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -437.0709 | 80.324 | -3550 | -400 | -3869.676 | 96.74% | 57.81% | 95% | 0% | 1684 | -382
[5 empty] | 2019-07-21 | 20 | 4833 | 1298 | -419 | 1 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -479.405 | 89.6799 | -3550 | -400 | -3860.3201 | 96.51% | 57.81% | 95% | 0% | 1717 | -419
[5 empty] | 2019-07-21 | 21 | 4833.5 | 1293 | -463 | 1 | 0 | 1756 | 630.1731 | 630.1731 | 630.1731 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -529.7483 | 100.4248 | -3550 | -400 | -3849.5752 | 96.24% | 57.81% | 95% | 0% | 1756 | -463
[5 empty] | 2019-07-21 | 22 | 4834 | 1288 | -478 | 1 | 0 | 1766 | 645.8368 | 645.8368 | 645.8368 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -546.9108 | 98.926 | -3550 | -400 | -3851.074 | 96.28% | 57.8% | 95% | 0% | 1766 | -478
[5 empty] | 2019-07-21 | 23 | 4834.5 | 1317 | -477 | 1 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -545.7666 | 143.9284 | -3550 | -400 | -3806.0716 | 95.15% | 57.8% | 95% | 0% | 1794 | -477
[5 empty] | 2019-07-21 | 24 | 4835 | 1316 | -482 | 1 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -551.4874 | 144.473 | -3550 | -400 | -3805.527 | 95.14% | 57.79% | 95% | 0% | 1798 | -482
[5 empty] | 2019-07-21 | 25 | 4835.5 | 1312 | -488 | 1 | 0 | 1800 | 699.0932 | 699.0932 | 699.0932 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -558.3524 | 140.7408 | -3550 | -400 | -3809.2592 | 95.23% | 57.78% | 95% | 0% | 1800 | -488
[5 empty] | 2019-07-21 | 26 | 4836 | 1286 | -502 | 1 | 0 | 1788 | 680.2968 | 680.2968 | 680.2968 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -574.3707 | 105.9261 | -3550 | -400 | -3844.0739 | 96.1% | 57.78% | 95% | 0% | 1788 | -502
[5 empty] | 2019-07-21 | 27 | 4836.5 | 1275 | -502 | 1 | 0 | 1777 | 663.0668 | 663.0668 | 663.0668 | 1253.5862 | 780 | 200 | 2233.5862 | 55.84% | 95% | 0% | -574.3707 | 88.6961 | -3550 | -400 | -3861.3039 | 96.53% | 57.78% | 95% | 0% | 1777 | -502
[5 empty] | 2019-07-21 | 28 | 4837 | 1211 | -521 | 1 | 0 | 1732 | 592.5804 | 592.5804 | 592.5804 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -596.1098 | -3.5295 | -3550 | -400 | -3953.5295 | 98.84% | 57.78% | 95% | 0% | 1732 | -521
[5 empty] | 2019-07-21 | 29 | 4837.5 | 1196 | -524 | 1 | 0 | 1720 | 573.784 | 573.784 | 573.784 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -599.5423 | -25.7583 | -3550 | -400 | -3975.7583 | 99.39% | 57.78% | 95% | 0% | 1720 | -524
[5 empty] | 2019-07-21 | 30 | 4838 | 1224 | -485 | 1 | 0 | 1709 | 556.554 | 556.554 | 556.554 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -554.9199 | 1.6341 | -3550 | -400 | -3948.3659 | 98.71% | 57.77% | 95% | 0% | 1709 | -485
[5 empty] | 2019-07-21 | 31 | 4838.5 | 1222 | -490 | 1 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -560.6407 | 0.61236 | -3550 | -400 | -3949.3876 | 98.73% | 57.77% | 95% | 0% | 1712 | -490
[5 empty] | 2019-07-21 | 32 | 4839 | 1303 | -435 | 1 | 0 | 1738 | 601.9786 | 601.9786 | 601.9786 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -497.7117 | 104.2669 | -3550 | -400 | -3845.7331 | 96.14% | 57.77% | 95% | 0% | 1738 | -435
[5 empty] | 2019-07-21 | 33 | 4839.5 | 1378 | -409 | 1 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -467.9634 | 210.767 | -3550 | -400 | -3739.233 | 93.48% | 57.77% | 95% | 0% | 1787 | -409
[5 empty] | 2019-07-21 | 34 | 4840 | 1450 | -390 | 1 | 0 | 1840 | 761.7477 | 761.7477 | 761.7477 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -446.2243 | 315.5235 | -3550 | -400 | -3634.4765 | 90.86% | 57.76% | 95% | 0% | 1840 | -390
[5 empty] | 2019-07-21 | 35 | 4840.5 | 1531 | -372 | 1 | 0 | 1903 | 860.4287 | 860.4287 | 860.4287 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -425.6293 | 434.7994 | -3550 | -400 | -3515.2006 | 87.88% | 57.76% | 95% | 0% | 1903 | -372
[5 empty] | 2019-07-21 | 36 | 4841 | 1615 | -334 | 1 | 0 | 1949 | 932.4815 | 932.4815 | 932.4815 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -382.151 | 550.3304 | -3550 | -400 | -3399.6696 | 84.99% | 57.75% | 95% | 0% | 1949 | -334
[5 empty] | 2019-07-21 | 37 | 4841.5 | 1671 | -298 | 1 | 0 | 1969 | 963.8087 | 963.8087 | 963.8087 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -340.9611 | 622.8476 | -3550 | -400 | -3327.1524 | 83.18% | 57.75% | 95% | 0% | 1969 | -298
[5 empty] | 2019-07-21 | 38 | 4842 | 1733 | -259 | 1 | 0 | 1992 | 999.8351 | 999.8351 | 999.8351 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -296.3387 | 703.4964 | -3550 | -400 | -3246.5036 | 81.16% | 57.75% | 95% | 0% | 1992 | -259
[5 empty] | 2019-07-21 | 39 | 4842.5 | 1770 | -225 | 1 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -257.4371 | 747.0971 | -3550 | -400 | -3202.9029 | 80.07% | 57.74% | 95% | 0% | 1995 | -225
[5 empty] | 2019-07-21 | 40 | 4843 | 1804 | -190 | 1 | 0 | 1994 | 1002.9678 | 1002.9678 | 1002.9678 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -217.3913 | 785.5765 | -3550 | -400 | -3164.4235 | 79.11% | 57.74% | 95% | 0% | 1994 | -190
[5 empty] | 2019-07-21 | 41 | 4843.5 | 1826 | -169 | 1 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 1252.0198 | 780 | 200 | 2232.0198 | 55.8% | 95% | 0% | -193.3638 | 811.1704 | -3550 | -400 | -3138.8296 | 78.47% | 57.74% | 95% | 0% | 1995 | -169
[5 empty] | 2019-07-21 | 42 | 4844 | 1825 | -155 | 1 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 1250.4534 | 780 | 200 | 2230.4534 | 55.76% | 95% | 0% | -177.3455 | 803.6932 | -3550 | -400 | -3146.3068 | 78.66% | 57.72% | 95% | 0% | 1980 | -155
[5 empty] | 2019-07-21 | 43 | 4844.5 | 1815 | -154 | 1 | 0 | 1969 | 963.8087 | 963.8087 | 963.8087 | 1250.4534 | 780 | 200 | 2230.4534 | 55.76% | 95% | 0% | -176.2014 | 787.6074 | -3550 | -400 | -3162.3926 | 79.06% | 57.71% | 95% | 0% | 1969 | -154
[5 empty] | 2019-07-21 | 44 | 4845 | 1791 | -157 | 0 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 1250.4534 | 780 | 200 | 2230.4534 | 55.76% | 95% | 0% | -179.6339 | 751.2812 | -2750 | -200 | -2198.7188 | 54.97% | 57.71% | 95% | 0% | 1948 | -157
[5 empty] | 2019-07-21 | 45 | 4845.5 | 1722 | -158 | 0 | 0 | 1880 | 824.4023 | 824.4023 | 824.4023 | 1250.4534 | 780 | 200 | 2230.4534 | 55.76% | 95% | 0% | -180.778 | 643.6243 | -2750 | -200 | -2306.3757 | 57.66% | 57.7% | 95% | 0% | 1880 | -158
[5 empty] | 2019-07-21 | 46 | 4846 | 1617 | -159 | 0 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 1250.4534 | 780 | 200 | 2230.4534 | 55.76% | 95% | 0% | -181.9222 | 479.5782 | -2750 | -200 | -2470.4218 | 61.76% | 57.7% | 95% | 0% | 1776 | -159
[5 empty] | 2019-07-21 | 47 | 4846.5 | 1502 | -160 | 0 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 1250.4534 | 780 | 200 | 2230.4534 | 55.76% | 95% | 0% | -183.0664 | 299.8685 | -2750 | -200 | -2650.1315 | 66.25% | 57.7% | 95% | 0% | 1662 | -160
[5 empty] | 2019-07-21 | 48 | 4847 | 1371 | -161 | 0 | 0 | 1532 | 279.3075 | 279.3075 | 279.3075 | 1250.4534 | 780 | 200 | 2230.4534 | 55.76% | 95% | 0% | -184.2105 | 95.097 | -2750 | -200 | -2854.903 | 71.37% | 57.7% | 95% | 0% | 1532 | -161
[5 empty] | 2019-07-22 | 1 | 4847.5 | 1278 | -162 | 0 | 0 | 1440 | 135.202 | 135.202 | 135.202 | 1250.4534 | 780 | 200 | 2230.4534 | 55.76% | 95% | 0% | -185.3547 | -50.1527 | -2750 | -200 | -3000.1527 | 75% | 57.69% | 95% | 0% | 1440 | -162
[5 empty] | 2019-07-22 | 2 | 4848 | 1217 | -163 | 0 | 0 | 1380 | 41.2201 | 41.2201 | 41.2201 | 1250.4534 | 780 | 200 | 2230.4534 | 55.76% | 95% | 0% | -186.4989 | -145.2787 | -2750 | -200 | -3095.2787 | 77.38% | 57.69% | 95% | 0% | 1380 | -163
[5 empty] | 2019-07-22 | 3 | 4848.5 | 1188 | -164 | 0 | 0 | 1352 | -2.6381 | -2.6381 | -2.6381 | 1250.4534 | 780 | 200 | 2230.4534 | 55.76% | 95% | 0% | -187.643 | -190.2811 | -2750 | -200 | -3140.2811 | 78.51% | 57.68% | 95% | 0% | 1352 | -164
[5 empty] | 2019-07-22 | 4 | 4849 | 1167 | -165 | 0 | 0 | 1332 | -33.9654 | -33.9654 | -33.9654 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -188.7872 | -222.7526 | -2750 | -200 | -3172.7526 | 79.32% | 57.68% | 95% | 0% | 1332 | -165
[5 empty] | 2019-07-22 | 5 | 4849.5 | 1137 | -167 | 0 | 0 | 1304 | -77.8236 | -77.8236 | -77.8236 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -191.0755 | -268.8991 | -2750 | -200 | -3218.8991 | 80.47% | 57.67% | 95% | 0% | 1304 | -167
[5 empty] | 2019-07-22 | 6 | 4850 | 1107 | -168 | 1 | 0 | 1275 | -123.2481 | -123.2481 | -123.2481 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -192.2197 | -315.4678 | -3550 | -400 | -4265.4678 | 106.6% | 57.67% | 95% | 0% | 1275 | -168
[5 empty] | 2019-07-22 | 7 | 4850.5 | 1096 | -171 | 1 | 0 | 1267 | -135.7791 | -135.7791 | -135.7791 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -195.6522 | -331.4312 | -3550 | -400 | -4281.4312 | 107% | 57.66% | 95% | 0% | 1267 | -171
[5 empty] | 2019-07-22 | 8 | 4851 | 1100 | -173 | 1 | 0 | 1273 | -126.3809 | -126.3809 | -126.3809 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -197.9405 | -324.3214 | -3550 | -400 | -4274.3214 | 106.9% | 57.66% | 95% | 0% | 1273 | -173
[5 empty] | 2019-07-22 | 9 | 4851.5 | 1113 | -172 | 1 | 0 | 1285 | -107.5845 | -107.5845 | -107.5845 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -196.7963 | -304.3808 | -3550 | -400 | -4254.3808 | 106.4% | 57.66% | 95% | 0% | 1285 | -172
[5 empty] | 2019-07-22 | 10 | 4852 | 1116 | -171 | 1 | 0 | 1287 | -104.4518 | -104.4518 | -104.4518 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -195.6522 | -300.1039 | -3550 | -400 | -4250.1039 | 106.3% | 57.66% | 95% | 0% | 1287 | -171
[5 empty] | 2019-07-22 | 11 | 4852.5 | 1165 | -171 | 1 | 0 | 1336 | -27.6999 | -27.6999 | -27.6999 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -195.6522 | -223.3521 | -3550 | -400 | -4173.3521 | 104.3% | 57.65% | 95% | 0% | 1336 | -171
[5 empty] | 2019-07-22 | 12 | 4853 | 1211 | -175 | 1 | 0 | 1386 | 50.6183 | 50.6183 | 50.6183 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -200.2288 | -149.6105 | -3550 | -400 | -4099.6105 | 102.5% | 57.65% | 95% | 0% | 1386 | -175
[5 empty] | 2019-07-22 | 13 | 4853.5 | 1372 | -186 | 1 | 0 | 1558 | 320.033 | 320.033 | 320.033 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -212.8146 | 107.2183 | -3550 | -400 | -3842.7817 | 96.07% | 57.65% | 95% | 0% | 1558 | -186
[5 empty] | 2019-07-22 | 14 | 4854 | 1490 | -208 | 1 | 0 | 1698 | 539.324 | 539.324 | 539.324 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -237.9863 | 301.3377 | -3550 | -400 | -3648.6623 | 91.22% | 57.65% | 95% | 0% | 1698 | -208
[5 empty] | 2019-07-22 | 15 | 4854.5 | 1652 | -237 | 1 | 0 | 1889 | 838.4996 | 838.4996 | 838.4996 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -271.167 | 567.3325 | -3550 | -400 | -3382.6675 | 84.57% | 57.64% | 95% | 0% | 1889 | -237
[5 empty] | 2019-07-22 | 16 | 4855 | 1741 | -274 | 1 | 0 | 2015 | 1035.8615 | 1035.8615 | 1035.8615 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -313.5011 | 722.3604 | -3550 | -400 | -3227.6396 | 80.69% | 57.64% | 95% | 0% | 2015 | -274
[5 empty] | 2019-07-22 | 17 | 4855.5 | 1790 | -331 | 1 | 0 | 2121 | 1201.8961 | 1201.8961 | 1201.8961 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -378.7185 | 823.1776 | -3550 | -400 | -3126.8224 | 78.17% | 57.63% | 95% | 0% | 2121 | -331
[5 empty] | 2019-07-22 | 18 | 4856 | 1773 | -382 | 1 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -437.0709 | 818.0816 | -3550 | -400 | -3131.9184 | 78.3% | 57.63% | 95% | 0% | 2155 | -382
[5 empty] | 2019-07-22 | 19 | 4856.5 | 1732 | -441 | 1 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 1248.8871 | 780 | 200 | 2228.8871 | 55.72% | 95% | 0% | -504.5767 | 778.7704 | -3550 | -400 | -3171.2296 | 79.28% | 57.63% | 95% | 0% | 2173 | -441
[5 empty] | 2019-07-22 | 20 | 4857 | 1683 | -480 | 1 | 0 | 2163 | 1267.6834 | 1267.6834 | 1267.6834 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -549.1991 | 718.4843 | -3550 | -400 | -3231.5157 | 80.79% | 57.63% | 95% | 0% | 2163 | -480
[5 empty] | 2019-07-22 | 21 | 4857.5 | 1629 | -499 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -570.9382 | 641.9225 | -3550 | -400 | -3308.0775 | 82.7% | 57.62% | 95% | 0% | 2128 | -499
[5 empty] | 2019-07-22 | 22 | 4858 | 1574 | -538 | 1 | 0 | 2112 | 1187.7988 | 1187.7988 | 1187.7988 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -615.5606 | 572.2382 | -3550 | -400 | -3377.7618 | 84.44% | 57.62% | 95% | 0% | 2112 | -538
[5 empty] | 2019-07-22 | 23 | 4858.5 | 1546 | -570 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -652.1739 | 541.8904 | -3550 | -400 | -3408.1096 | 85.2% | 57.62% | 95% | 0% | 2116 | -570
[5 empty] | 2019-07-22 | 24 | 4859 | 1523 | -602 | 1 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -688.7872 | 519.3744 | -3550 | -400 | -3430.6256 | 85.77% | 57.62% | 95% | 0% | 2125 | -602
[5 empty] | 2019-07-22 | 25 | 4859.5 | 1505 | -623 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -712.8146 | 500.046 | -3550 | -400 | -3449.954 | 86.25% | 57.62% | 95% | 0% | 2128 | -623
[5 empty] | 2019-07-22 | 26 | 4860 | 1457 | -639 | 1 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -731.1213 | 431.6157 | -3550 | -400 | -3518.3843 | 87.96% | 57.62% | 95% | 0% | 2096 | -639
[5 empty] | 2019-07-22 | 27 | 4860.5 | 1397 | -676 | 1 | 0 | 2073 | 1126.7106 | 1126.7106 | 1126.7106 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -773.4554 | 353.2553 | -3550 | -400 | -3596.7447 | 89.92% | 57.62% | 95% | 0% | 2073 | -676
[5 empty] | 2019-07-22 | 28 | 4861 | 1402 | -667 | 1 | 0 | 2069 | 1120.4452 | 1120.4452 | 1120.4452 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -763.1579 | 357.2873 | -3550 | -400 | -3592.7127 | 89.82% | 57.61% | 95% | 0% | 2069 | -667
[5 empty] | 2019-07-22 | 29 | 4861.5 | 1355 | -695 | 1 | 0 | 2050 | 1090.6843 | 1090.6843 | 1090.6843 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -795.1945 | 295.4897 | -3550 | -400 | -3654.5103 | 91.36% | 57.61% | 95% | 0% | 2050 | -695
[5 empty] | 2019-07-22 | 30 | 4862 | 1370 | -682 | 1 | 0 | 2052 | 1093.817 | 1093.817 | 1093.817 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -780.3204 | 313.4966 | -3550 | -400 | -3636.5034 | 90.91% | 57.61% | 95% | 0% | 2052 | -682
[5 empty] | 2019-07-22 | 31 | 4862.5 | 1391 | -667 | 1 | 0 | 2058 | 1103.2152 | 1103.2152 | 1103.2152 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -763.1579 | 340.0573 | -3550 | -400 | -3609.9427 | 90.25% | 57.61% | 95% | 0% | 2058 | -667
[5 empty] | 2019-07-22 | 32 | 4863 | 1457 | -640 | 1 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 1247.3207 | 780 | 200 | 2227.3207 | 55.68% | 95% | 0% | -732.2654 | 432.0379 | -3550 | -400 | -3517.9621 | 87.95% | 57.61% | 95% | 0% | 2097 | -640
[5 empty] | 2019-07-22 | 33 | 4863.5 | 1555 | -572 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -654.4622 | 556.8321 | -3550 | -400 | -3393.1679 | 84.83% | 57.6% | 95% | 0% | 2127 | -572
[5 empty] | 2019-07-22 | 34 | 4864 | 1671 | -514 | 1 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -588.1007 | 714.0428 | -3550 | -400 | -3235.9572 | 80.9% | 57.6% | 95% | 0% | 2185 | -514
[5 empty] | 2019-07-22 | 35 | 4864.5 | 1818 | -451 | 1 | 0 | 2269 | 1433.7181 | 1433.7181 | 1433.7181 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -516.0183 | 917.6997 | -3550 | -400 | -3032.3003 | 75.81% | 57.6% | 95% | 0% | 2269 | -451
[5 empty] | 2019-07-22 | 36 | 4865 | 1913 | -394 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -450.8009 | 1042.439 | -3550 | -400 | -2907.561 | 72.69% | 57.6% | 95% | 0% | 2307 | -394
[5 empty] | 2019-07-22 | 37 | 4865.5 | 1988 | -336 | 1 | 0 | 2324 | 1519.8681 | 1519.8681 | 1519.8681 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -384.4394 | 1135.4287 | -3550 | -400 | -2814.5713 | 70.36% | 57.6% | 95% | 0% | 2324 | -336
[5 empty] | 2019-07-22 | 38 | 4866 | 2057 | -279 | 1 | 0 | 2336 | 1538.6645 | 1538.6645 | 1538.6645 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -319.222 | 1219.4425 | -3550 | -400 | -2730.5575 | 68.26% | 57.6% | 95% | 0% | 2336 | -279
[5 empty] | 2019-07-22 | 39 | 4866.5 | 2125 | -229 | 1 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -262.0137 | 1304.8453 | -3550 | -400 | -2645.1547 | 66.13% | 57.59% | 95% | 0% | 2354 | -229
[5 empty] | 2019-07-22 | 40 | 4867 | 2166 | -185 | 1 | 0 | 2351 | 1562.1599 | 1562.1599 | 1562.1599 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -211.6705 | 1350.4895 | -3550 | -400 | -2599.5105 | 64.99% | 57.59% | 95% | 0% | 2351 | -185
[5 empty] | 2019-07-22 | 41 | 4867.5 | 2201 | -150 | 1 | 0 | 2351 | 1562.1599 | 1562.1599 | 1562.1599 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -171.6247 | 1390.5352 | -3550 | -400 | -2559.4648 | 63.99% | 57.59% | 95% | 0% | 2351 | -150
[5 empty] | 2019-07-22 | 42 | 4868 | 2196 | -127 | 1 | 0 | 2323 | 1518.3017 | 1518.3017 | 1518.3017 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -145.3089 | 1372.9928 | -3550 | -400 | -2577.0072 | 64.43% | 57.58% | 95% | 0% | 2323 | -127
[5 empty] | 2019-07-22 | 43 | 4868.5 | 2165 | -118 | 1 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -135.0114 | 1320.6357 | -3550 | -400 | -2629.3643 | 65.73% | 57.58% | 95% | 0% | 2283 | -118
[5 empty] | 2019-07-22 | 44 | 4869 | 2139 | -115 | 1 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -131.5789 | 1278.6436 | -3550 | -400 | -2671.3564 | 66.78% | 57.58% | 95% | 0% | 2254 | -115
[5 empty] | 2019-07-22 | 45 | 4869.5 | 2096 | -112 | 0 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -128.1465 | 1210.0234 | -2750 | -200 | -1739.9766 | 43.5% | 57.57% | 95% | 0% | 2208 | -112
[5 empty] | 2019-07-22 | 46 | 4870 | 1975 | -108 | 0 | 0 | 2083 | 1142.3743 | 1142.3743 | 1142.3743 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -123.5698 | 1018.8045 | -2750 | -200 | -1931.1955 | 48.28% | 57.57% | 95% | 0% | 2083 | -108
[5 empty] | 2019-07-22 | 47 | 4870.5 | 1833 | -106 | 0 | 0 | 1939 | 916.8178 | 916.8178 | 916.8178 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -121.2815 | 795.5363 | -2750 | -200 | -2154.4637 | 53.86% | 57.57% | 95% | 0% | 1939 | -106
[5 empty] | 2019-07-22 | 48 | 4871 | 1725 | -104 | 0 | 0 | 1829 | 744.5177 | 744.5177 | 744.5177 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -118.9931 | 625.5246 | -2750 | -200 | -2324.4754 | 58.11% | 57.56% | 95% | 0% | 1829 | -104
[5 empty] | 2019-07-23 | 1 | 4871.5 | 1661 | -99 | 0 | 0 | 1760 | 636.4386 | 636.4386 | 636.4386 | 1245.7543 | 780 | 200 | 2225.7543 | 55.64% | 95% | 0% | -113.2723 | 523.1663 | -2750 | -200 | -2426.8337 | 60.67% | 57.56% | 95% | 0% | 1760 | -99
[5 empty] | 2019-07-23 | 2 | 4872 | 1605 | -95 | 0 | 0 | 1700 | 542.4567 | 542.4567 | 542.4567 | 1244.188 | 780 | 200 | 2224.188 | 55.6% | 95% | 0% | -108.6957 | 433.7611 | -2750 | -200 | -2516.2389 | 62.91% | 57.56% | 95% | 0% | 1700 | -95
[5 empty] | 2019-07-23 | 3 | 4872.5 | 1564 | -91 | 0 | 0 | 1655 | 471.9703 | 471.9703 | 471.9703 | 1244.188 | 780 | 200 | 2224.188 | 55.6% | 95% | 0% | -104.119 | 367.8513 | -2750 | -200 | -2582.1487 | 64.55% | 57.55% | 95% | 0% | 1655 | -91
[5 empty] | 2019-07-23 | 4 | 4873 | 1552 | -88 | 0 | 0 | 1640 | 448.4749 | 448.4749 | 448.4749 | 1244.188 | 780 | 200 | 2224.188 | 55.6% | 95% | 0% | -100.6865 | 347.7884 | -2750 | -200 | -2602.2116 | 65.06% | 57.55% | 95% | 0% | 1640 | -88
[5 empty] | 2019-07-23 | 5 | 4873.5 | 1531 | -85 | 0 | 0 | 1616 | 410.8821 | 410.8821 | 410.8821 | 1244.188 | 780 | 200 | 2224.188 | 55.6% | 95% | 0% | -97.254 | 313.6281 | -2750 | -200 | -2636.3719 | 65.91% | 57.55% | 95% | 0% | 1616 | -85
[5 empty] | 2019-07-23 | 6 | 4874 | 1504 | -82 | 0 | 0 | 1586 | 363.8912 | 363.8912 | 363.8912 | 1244.188 | 780 | 200 | 2224.188 | 55.6% | 95% | 0% | -93.8215 | 270.0697 | -2750 | -200 | -2679.9303 | 67% | 57.54% | 95% | 0% | 1586 | -82
[5 empty] | 2019-07-23 | 7 | 4874.5 | 1490 | -79 | 0 | 0 | 1569 | 337.263 | 337.263 | 337.263 | 1244.188 | 780 | 200 | 2224.188 | 55.6% | 95% | 0% | -90.389 | 246.874 | -2750 | -200 | -2703.126 | 67.58% | 57.54% | 95% | 0% | 1569 | -79
[5 empty] | 2019-07-23 | 8 | 4875 | 1480 | -76 | 0 | 0 | 1556 | 316.9002 | 316.9002 | 316.9002 | 1244.188 | 780 | 200 | 2224.188 | 55.6% | 95% | 0% | -86.9565 | 229.9437 | -2750 | -200 | -2720.0563 | 68% | 57.53% | 95% | 0% | 1556 | -76
[5 empty] | 2019-07-23 | 9 | 4875.5 | 1480 | -75 | 0 | 0 | 1555 | 315.3339 | 315.3339 | 315.3339 | 1244.188 | 780 | 200 | 2224.188 | 55.6% | 95% | 0% | -85.8124 | 229.5215 | -2750 | -200 | -2720.4785 | 68.01% | 57.53% | 95% | 0% | 1555 | -75
[5 empty] | 2019-07-23 | 10 | 4876 | 1480 | -74 | 0 | 0 | 1554 | 313.7675 | 313.7675 | 313.7675 | 1244.188 | 780 | 200 | 2224.188 | 55.6% | 95% | 0% | -84.6682 | 229.0993 | -2750 | -200 | -2720.9007 | 68.02% | 57.53% | 95% | 0% | 1554 | -74
[5 empty] | 2019-07-23 | 11 | 4876.5 | 1506 | -74 | 1 | 0 | 1580 | 354.493 | 354.493 | 354.493 | 1244.188 | 780 | 200 | 2224.188 | 55.6% | 95% | 0% | -84.6682 | 269.8248 | -3550 | -400 | -3680.1752 | 92% | 57.53% | 95% | 0% | 1580 | -74
[5 empty] | 2019-07-23 | 12 | 4877 | 1565 | -83 | 1 | 0 | 1648 | 461.0058 | 461.0058 | 461.0058 | 1242.6216 | 780 | 200 | 2222.6216 | 55.57% | 95% | 0% | -94.9657 | 366.0401 | -3550 | -400 | -3583.9599 | 89.6% | 57.52% | 95% | 0% | 1648 | -83
[5 empty] | 2019-07-23 | 13 | 4877.5 | 1691 | -108 | 1 | 0 | 1799 | 697.5268 | 697.5268 | 697.5268 | 1242.6216 | 780 | 200 | 2222.6216 | 55.57% | 95% | 0% | -123.5698 | 573.957 | -3550 | -400 | -3376.043 | 84.4% | 57.52% | 95% | 0% | 1799 | -108
[5 empty] | 2019-07-23 | 14 | 4878 | 1794 | -142 | 1 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 1242.6216 | 780 | 200 | 2222.6216 | 55.57% | 95% | 0% | -162.4714 | 749.6473 | -3550 | -400 | -3200.3527 | 80.01% | 57.52% | 95% | 0% | 1936 | -142
[5 empty] | 2019-07-23 | 15 | 4878.5 | 1912 | -182 | 1 | 0 | 2094 | 1159.6043 | 1159.6043 | 1159.6043 | 1242.6216 | 780 | 200 | 2222.6216 | 55.57% | 95% | 0% | -208.238 | 951.3663 | -3550 | -400 | -2998.6337 | 74.97% | 57.52% | 95% | 0% | 2094 | -182
[5 empty] | 2019-07-23 | 16 | 4879 | 1951 | -234 | 1 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 1242.6216 | 780 | 200 | 2222.6216 | 55.57% | 95% | 0% | -267.7346 | 1034.4089 | -3550 | -400 | -2915.5911 | 72.89% | 57.52% | 95% | 0% | 2185 | -234
[5 empty] | 2019-07-23 | 17 | 4879.5 | 1982 | -304 | 1 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 1242.6216 | 780 | 200 | 2222.6216 | 55.57% | 95% | 0% | -347.8261 | 1112.5202 | -3550 | -400 | -2837.4798 | 70.94% | 57.52% | 95% | 0% | 2286 | -304
[5 empty] | 2019-07-23 | 18 | 4880 | 1933 | -388 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 1242.6216 | 780 | 200 | 2222.6216 | 55.57% | 95% | 0% | -443.9359 | 1071.2331 | -3550 | -400 | -2878.7669 | 71.97% | 57.52% | 95% | 0% | 2321 | -388
[5 empty] | 2019-07-23 | 19 | 4880.5 | 1843 | -464 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1241.0552 | 780 | 200 | 2221.0552 | 55.53% | 95% | 0% | -530.8924 | 962.3475 | -3550 | -400 | -2987.6525 | 74.69% | 57.51% | 95% | 0% | 2307 | -464
[5 empty] | 2019-07-23 | 20 | 4881 | 1744 | -533 | 1 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 1241.0552 | 780 | 200 | 2221.0552 | 55.53% | 95% | 0% | -609.8398 | 836.4092 | -3550 | -400 | -3113.5908 | 77.84% | 57.51% | 95% | 0% | 2277 | -533
[5 empty] | 2019-07-23 | 21 | 4881.5 | 1645 | -594 | 1 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 1241.0552 | 780 | 200 | 2221.0552 | 55.53% | 95% | 0% | -679.6339 | 707.0933 | -3550 | -400 | -3242.9067 | 81.07% | 57.5% | 95% | 0% | 2239 | -594
[5 empty] | 2019-07-23 | 22 | 4882 | 1563 | -645 | 1 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 1241.0552 | 780 | 200 | 2221.0552 | 55.53% | 95% | 0% | -737.9863 | 600.1836 | -3550 | -400 | -3349.8164 | 83.75% | 57.49% | 95% | 0% | 2208 | -645
[5 empty] | 2019-07-23 | 23 | 4882.5 | 1487 | -692 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 1241.0552 | 780 | 200 | 2221.0552 | 55.53% | 95% | 0% | -791.762 | 500.9832 | -3550 | -400 | -3449.0168 | 86.23% | 57.49% | 95% | 0% | 2179 | -692
[5 empty] | 2019-07-23 | 24 | 4883 | 1425 | -729 | 1 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 1241.0552 | 780 | 200 | 2221.0552 | 55.53% | 95% | 0% | -834.0961 | 419.49 | -3550 | -400 | -3530.51 | 88.26% | 57.49% | 95% | 0% | 2154 | -729
[5 empty] | 2019-07-23 | 25 | 4883.5 | 1399 | -761 | 1 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1241.0552 | 780 | 200 | 2221.0552 | 55.53% | 95% | 0% | -870.7094 | 392.275 | -3550 | -400 | -3557.725 | 88.94% | 57.49% | 95% | 0% | 2160 | -761
[5 empty] | 2019-07-23 | 26 | 4884 | 1367 | -782 | 1 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 1241.0552 | 780 | 200 | 2221.0552 | 55.53% | 95% | 0% | -894.7368 | 351.0175 | -3550 | -400 | -3598.9825 | 89.97% | 57.49% | 95% | 0% | 2149 | -782
[5 empty] | 2019-07-23 | 27 | 4884.5 | 1344 | -784 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1241.0552 | 780 | 200 | 2221.0552 | 55.53% | 95% | 0% | -897.0252 | 315.8355 | -3550 | -400 | -3634.1645 | 90.85% | 57.49% | 95% | 0% | 2128 | -784
[5 empty] | 2019-07-23 | 28 | 4885 | 1357 | -771 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1241.0552 | 780 | 200 | 2221.0552 | 55.53% | 95% | 0% | -882.151 | 330.7096 | -3550 | -400 | -3619.2904 | 90.48% | 57.48% | 95% | 0% | 2128 | -771
[5 empty] | 2019-07-23 | 29 | 4885.5 | 1369 | -754 | 1 | 0 | 2123 | 1205.0289 | 1205.0289 | 1205.0289 | 1241.0552 | 780 | 200 | 2221.0552 | 55.53% | 95% | 0% | -862.7002 | 342.3286 | -3550 | -400 | -3607.6714 | 90.19% | 57.48% | 95% | 0% | 2123 | -754
[5 empty] | 2019-07-23 | 30 | 4886 | 1381 | -728 | 1 | 0 | 2109 | 1183.0998 | 1183.0998 | 1183.0998 | 1241.0552 | 780 | 200 | 2221.0552 | 55.53% | 95% | 0% | -832.9519 | 350.1478 | -3550 | -400 | -3599.8522 | 90% | 57.47% | 95% | 0% | 2109 | -728
[5 empty] | 2019-07-23 | 31 | 4886.5 | 1449 | -677 | 1 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -774.5995 | 435.1284 | -3550 | -400 | -3514.8716 | 87.87% | 57.47% | 95% | 0% | 2126 | -677
[5 empty] | 2019-07-23 | 32 | 4887 | 1572 | -623 | 1 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -712.8146 | 604.9924 | -3550 | -400 | -3345.0076 | 83.63% | 57.47% | 95% | 0% | 2195 | -623
[5 empty] | 2019-07-23 | 33 | 4887.5 | 1707 | -562 | 1 | 0 | 2269 | 1433.7181 | 1433.7181 | 1433.7181 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -643.0206 | 790.6975 | -3550 | -400 | -3159.3025 | 78.98% | 57.47% | 95% | 0% | 2269 | -562
[5 empty] | 2019-07-23 | 34 | 4888 | 1827 | -483 | 1 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -552.6316 | 945.3074 | -3550 | -400 | -3004.6926 | 75.12% | 57.47% | 95% | 0% | 2310 | -483
[5 empty] | 2019-07-23 | 35 | 4888.5 | 1945 | -410 | 1 | 0 | 2355 | 1568.4254 | 1568.4254 | 1568.4254 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -469.1076 | 1099.3178 | -3550 | -400 | -2850.6822 | 71.27% | 57.46% | 95% | 0% | 2355 | -410
[5 empty] | 2019-07-23 | 36 | 4889 | 2058 | -341 | 1 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -390.1602 | 1247.1852 | -3550 | -400 | -2702.8148 | 67.57% | 57.46% | 95% | 0% | 2399 | -341
[5 empty] | 2019-07-23 | 37 | 4889.5 | 2157 | -273 | 1 | 0 | 2430 | 1685.9027 | 1685.9027 | 1685.9027 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -312.357 | 1373.5457 | -3550 | -400 | -2576.4543 | 64.41% | 57.46% | 95% | 0% | 2430 | -273
[5 empty] | 2019-07-23 | 38 | 4890 | 2254 | -215 | 1 | 0 | 2469 | 1746.9909 | 1746.9909 | 1746.9909 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -245.9954 | 1500.9955 | -3550 | -400 | -2449.0045 | 61.23% | 57.45% | 95% | 0% | 2469 | -215
[5 empty] | 2019-07-23 | 39 | 4890.5 | 2316 | -174 | 1 | 0 | 2490 | 1779.8846 | 1779.8846 | 1779.8846 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -199.0847 | 1580.7999 | -3550 | -400 | -2369.2001 | 59.23% | 57.45% | 95% | 0% | 2490 | -174
[5 empty] | 2019-07-23 | 40 | 4891 | 2345 | -140 | 1 | 0 | 2485 | 1772.0528 | 1772.0528 | 1772.0528 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -160.1831 | 1611.8697 | -3550 | -400 | -2338.1303 | 58.45% | 57.45% | 95% | 0% | 2485 | -140
[5 empty] | 2019-07-23 | 41 | 4891.5 | 2317 | -115 | 1 | 0 | 2432 | 1689.0354 | 1689.0354 | 1689.0354 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -131.5789 | 1557.4565 | -3550 | -400 | -2392.5435 | 59.81% | 57.45% | 95% | 0% | 2432 | -115
[5 empty] | 2019-07-23 | 42 | 4892 | 2314 | -99 | 1 | 0 | 2413 | 1659.2745 | 1659.2745 | 1659.2745 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -113.2723 | 1546.0022 | -3550 | -400 | -2403.9978 | 60.1% | 57.44% | 95% | 0% | 2413 | -99
[5 empty] | 2019-07-23 | 43 | 4892.5 | 2296 | -97 | 1 | 0 | 2393 | 1627.9472 | 1627.9472 | 1627.9472 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -110.984 | 1516.9633 | -3550 | -400 | -2433.0367 | 60.83% | 57.43% | 95% | 0% | 2393 | -97
[5 empty] | 2019-07-23 | 44 | 4893 | 2278 | -100 | 0 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 1239.4889 | 780 | 200 | 2219.4889 | 55.49% | 95% | 0% | -114.4165 | 1490.0353 | -2750 | -200 | -1459.9647 | 36.5% | 57.42% | 95% | 0% | 2378 | -100
[5 empty] | 2019-07-23 | 45 | 4893.5 | 2206 | -103 | 0 | 0 | 2309 | 1496.3726 | 1496.3726 | 1496.3726 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -117.849 | 1378.5237 | -2750 | -200 | -1571.4763 | 39.29% | 57.42% | 95% | 0% | 2309 | -103
[5 empty] | 2019-07-23 | 46 | 4894 | 2080 | -106 | 0 | 0 | 2186 | 1303.7098 | 1303.7098 | 1303.7098 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -121.2815 | 1182.4283 | -2750 | -200 | -1767.5717 | 44.19% | 57.42% | 95% | 0% | 2186 | -106
[5 empty] | 2019-07-23 | 47 | 4894.5 | 1926 | -108 | 0 | 0 | 2034 | 1065.6224 | 1065.6224 | 1065.6224 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -123.5698 | 942.0526 | -2750 | -200 | -2007.9474 | 50.2% | 57.41% | 95% | 0% | 2034 | -108
[5 empty] | 2019-07-23 | 48 | 4895 | 1804 | -109 | 0 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -124.714 | 751.3784 | -2750 | -200 | -2198.6216 | 54.97% | 57.41% | 95% | 0% | 1913 | -109
[5 empty] | 2019-07-24 | 1 | 4895.5 | 1711 | -107 | 0 | 0 | 1818 | 727.2877 | 727.2877 | 727.2877 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -122.4256 | 604.8621 | -2750 | -200 | -2345.1379 | 58.63% | 57.4% | 95% | 0% | 1818 | -107
[5 empty] | 2019-07-24 | 2 | 4896 | 1646 | -105 | 0 | 0 | 1751 | 622.3413 | 622.3413 | 622.3413 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -120.1373 | 502.204 | -2750 | -200 | -2447.796 | 61.19% | 57.39% | 95% | 0% | 1751 | -105
[5 empty] | 2019-07-24 | 3 | 4896.5 | 1605 | -107 | 0 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -122.4256 | 438.8275 | -2750 | -200 | -2511.1725 | 62.78% | 57.39% | 95% | 0% | 1712 | -107
[5 empty] | 2019-07-24 | 4 | 4897 | 1573 | -110 | 0 | 0 | 1683 | 515.8285 | 515.8285 | 515.8285 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -125.8581 | 389.9704 | -2750 | -200 | -2560.0296 | 64% | 57.39% | 95% | 0% | 1683 | -110
[5 empty] | 2019-07-24 | 5 | 4897.5 | 1547 | -109 | 0 | 0 | 1656 | 473.5367 | 473.5367 | 473.5367 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -124.714 | 348.8227 | -2750 | -200 | -2601.1773 | 65.03% | 57.39% | 95% | 0% | 1656 | -109
[5 empty] | 2019-07-24 | 6 | 4898 | 1523 | -108 | 1 | 0 | 1631 | 434.3776 | 434.3776 | 434.3776 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -123.5698 | 310.8078 | -3550 | -400 | -3639.1922 | 90.98% | 57.38% | 95% | 0% | 1631 | -108
[5 empty] | 2019-07-24 | 7 | 4898.5 | 1522 | -106 | 1 | 0 | 1628 | 429.6785 | 429.6785 | 429.6785 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -121.2815 | 308.397 | -3550 | -400 | -3641.603 | 91.04% | 57.38% | 95% | 0% | 1628 | -106
[5 empty] | 2019-07-24 | 8 | 4899 | 1537 | -103 | 1 | 0 | 1640 | 448.4749 | 448.4749 | 448.4749 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -117.849 | 330.6259 | -3550 | -400 | -3619.3741 | 90.48% | 57.37% | 95% | 0% | 1640 | -103
[5 empty] | 2019-07-24 | 9 | 4899.5 | 1518 | -98 | 1 | 0 | 1616 | 410.8821 | 410.8821 | 410.8821 | 1237.9225 | 780 | 200 | 2217.9225 | 55.45% | 95% | 0% | -112.1281 | 298.754 | -3550 | -400 | -3651.246 | 91.28% | 57.37% | 95% | 0% | 1616 | -98
[5 empty] | 2019-07-24 | 10 | 4900 | 1504 | -93 | 1 | 0 | 1597 | 381.1212 | 381.1212 | 381.1212 | 1236.3561 | 780 | 200 | 2216.3561 | 55.41% | 95% | 0% | -106.4073 | 274.7139 | -3550 | -400 | -3675.2861 | 91.88% | 57.37% | 95% | 0% | 1597 | -93
[5 empty] | 2019-07-24 | 11 | 4900.5 | 1523 | -90 | 1 | 0 | 1613 | 406.183 | 406.183 | 406.183 | 1236.3561 | 780 | 200 | 2216.3561 | 55.41% | 95% | 0% | -102.9748 | 303.2082 | -3550 | -400 | -3646.7918 | 91.17% | 57.37% | 95% | 0% | 1613 | -90
[5 empty] | 2019-07-24 | 12 | 4901 | 1595 | -90 | 1 | 0 | 1685 | 518.9613 | 518.9613 | 518.9613 | 1236.3561 | 780 | 200 | 2216.3561 | 55.41% | 95% | 0% | -102.9748 | 415.9864 | -3550 | -400 | -3534.0136 | 88.35% | 57.37% | 95% | 0% | 1685 | -90
[5 empty] | 2019-07-24 | 13 | 4901.5 | 1746 | -107 | 1 | 0 | 1853 | 782.1105 | 782.1105 | 782.1105 | 1236.3561 | 780 | 200 | 2216.3561 | 55.41% | 95% | 0% | -122.4256 | 659.6848 | -3550 | -400 | -3290.3152 | 82.26% | 57.36% | 95% | 0% | 1853 | -107
[5 empty] | 2019-07-24 | 14 | 4902 | 1872 | -135 | 1 | 0 | 2007 | 1023.3306 | 1023.3306 | 1023.3306 | 1236.3561 | 780 | 200 | 2216.3561 | 55.41% | 95% | 0% | -154.4622 | 868.8683 | -3550 | -400 | -3081.1317 | 77.03% | 57.35% | 95% | 0% | 2007 | -135
[5 empty] | 2019-07-24 | 15 | 4902.5 | 2016 | -174 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1236.3561 | 780 | 200 | 2216.3561 | 55.41% | 95% | 0% | -199.0847 | 1110.8906 | -3550 | -400 | -2839.1094 | 70.98% | 57.35% | 95% | 0% | 2190 | -174
[5 empty] | 2019-07-24 | 16 | 4903 | 2053 | -221 | 1 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 1236.3561 | 780 | 200 | 2216.3561 | 55.41% | 95% | 0% | -252.8604 | 1188.6895 | -3550 | -400 | -2761.3105 | 69.03% | 57.35% | 95% | 0% | 2274 | -221
[5 empty] | 2019-07-24 | 17 | 4903.5 | 2054 | -279 | 1 | 0 | 2333 | 1533.9654 | 1533.9654 | 1533.9654 | 1236.3561 | 780 | 200 | 2216.3561 | 55.41% | 95% | 0% | -319.222 | 1214.7434 | -3550 | -400 | -2735.2566 | 68.38% | 57.34% | 95% | 0% | 2333 | -279
[5 empty] | 2019-07-24 | 18 | 4904 | 1996 | -342 | 1 | 0 | 2338 | 1541.7972 | 1541.7972 | 1541.7972 | 1236.3561 | 780 | 200 | 2216.3561 | 55.41% | 95% | 0% | -391.3043 | 1150.4928 | -3550 | -400 | -2799.5072 | 69.99% | 57.34% | 95% | 0% | 2338 | -342
[5 empty] | 2019-07-24 | 19 | 4904.5 | 1919 | -407 | 1 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 1236.3561 | 780 | 200 | 2216.3561 | 55.41% | 95% | 0% | -465.6751 | 1057.3258 | -3550 | -400 | -2892.6742 | 72.32% | 57.34% | 95% | 0% | 2326 | -407
[5 empty] | 2019-07-24 | 20 | 4905 | 1824 | -470 | 1 | 0 | 2294 | 1472.8772 | 1472.8772 | 1472.8772 | 1234.7898 | 780 | 200 | 2214.7898 | 55.37% | 95% | 0% | -537.7574 | 935.1197 | -3550 | -400 | -3014.8803 | 75.37% | 57.34% | 95% | 0% | 2294 | -470
[5 empty] | 2019-07-24 | 21 | 4905.5 | 1739 | -535 | 1 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 1234.7898 | 780 | 200 | 2214.7898 | 55.37% | 95% | 0% | -612.1281 | 829.4217 | -3550 | -400 | -3120.5783 | 78.01% | 57.34% | 95% | 0% | 2274 | -535
[5 empty] | 2019-07-24 | 22 | 4906 | 1677 | -585 | 1 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 1234.7898 | 780 | 200 | 2214.7898 | 55.37% | 95% | 0% | -669.3364 | 753.4171 | -3550 | -400 | -3196.5829 | 79.91% | 57.34% | 95% | 0% | 2262 | -585
[5 empty] | 2019-07-24 | 23 | 4906.5 | 1592 | -669 | 1 | 0 | 2261 | 1421.1871 | 1421.1871 | 1421.1871 | 1234.7898 | 780 | 200 | 2214.7898 | 55.37% | 95% | 0% | -765.4462 | 655.7409 | -3550 | -400 | -3294.2591 | 82.36% | 57.34% | 95% | 0% | 2261 | -669
[5 empty] | 2019-07-24 | 24 | 4907 | 1573 | -695 | 1 | 0 | 2268 | 1432.1517 | 1432.1517 | 1432.1517 | 1234.7898 | 780 | 200 | 2214.7898 | 55.37% | 95% | 0% | -795.1945 | 636.9572 | -3550 | -400 | -3313.0428 | 82.83% | 57.33% | 95% | 0% | 2268 | -695
[5 empty] | 2019-07-24 | 25 | 4907.5 | 1548 | -715 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 1234.7898 | 780 | 200 | 2214.7898 | 55.37% | 95% | 0% | -818.0778 | 606.2421 | -3550 | -400 | -3343.7579 | 83.59% | 57.33% | 95% | 0% | 2263 | -715
[5 empty] | 2019-07-24 | 26 | 4908 | 1496 | -738 | 1 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 1234.7898 | 780 | 200 | 2214.7898 | 55.37% | 95% | 0% | -844.3936 | 534.5017 | -3550 | -400 | -3415.4983 | 85.39% | 57.33% | 95% | 0% | 2234 | -738
[5 empty] | 2019-07-24 | 27 | 4908.5 | 1496 | -743 | 1 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 1234.7898 | 780 | 200 | 2214.7898 | 55.37% | 95% | 0% | -850.1144 | 536.6127 | -3550 | -400 | -3413.3873 | 85.33% | 57.33% | 95% | 0% | 2239 | -743
[5 empty] | 2019-07-24 | 28 | 4909 | 1511 | -714 | 1 | 0 | 2225 | 1364.798 | 1364.798 | 1364.798 | 1234.7898 | 780 | 200 | 2214.7898 | 55.37% | 95% | 0% | -816.9336 | 547.8644 | -3550 | -400 | -3402.1356 | 85.05% | 57.33% | 95% | 0% | 2225 | -714
[5 empty] | 2019-07-24 | 29 | 4909.5 | 1547 | -674 | 1 | 0 | 2221 | 1358.5326 | 1358.5326 | 1358.5326 | 1234.7898 | 780 | 200 | 2214.7898 | 55.37% | 95% | 0% | -771.167 | 587.3655 | -3550 | -400 | -3362.6345 | 84.07% | 57.33% | 95% | 0% | 2221 | -674
[5 empty] | 2019-07-24 | 30 | 4910 | 1574 | -656 | 1 | 0 | 2230 | 1372.6298 | 1372.6298 | 1372.6298 | 1234.7898 | 780 | 200 | 2214.7898 | 55.37% | 95% | 0% | -750.5721 | 622.0578 | -3550 | -400 | -3327.9422 | 83.2% | 57.32% | 95% | 0% | 2230 | -656
[5 empty] | 2019-07-24 | 31 | 4910.5 | 1612 | -615 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -703.6613 | 664.2694 | -3550 | -400 | -3285.7306 | 82.14% | 57.32% | 95% | 0% | 2227 | -615
[5 empty] | 2019-07-24 | 32 | 4911 | 1685 | -569 | 1 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -651.0297 | 759.1928 | -3550 | -400 | -3190.8072 | 79.77% | 57.32% | 95% | 0% | 2254 | -569
[5 empty] | 2019-07-24 | 33 | 4911.5 | 1803 | -518 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -592.6773 | 922.4917 | -3550 | -400 | -3027.5083 | 75.69% | 57.32% | 95% | 0% | 2321 | -518
[5 empty] | 2019-07-24 | 34 | 4912 | 1943 | -443 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -506.865 | 1110.1177 | -3550 | -400 | -2839.8823 | 71% | 57.31% | 95% | 0% | 2386 | -443
[5 empty] | 2019-07-24 | 35 | 4912.5 | 2054 | -387 | 1 | 0 | 2441 | 1703.1327 | 1703.1327 | 1703.1327 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -442.7918 | 1260.341 | -3550 | -400 | -2689.659 | 67.24% | 57.31% | 95% | 0% | 2441 | -387
[5 empty] | 2019-07-24 | 36 | 4913 | 2144 | -326 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -372.9977 | 1375.5596 | -3550 | -400 | -2574.4404 | 64.36% | 57.31% | 95% | 0% | 2470 | -326
[5 empty] | 2019-07-24 | 37 | 4913.5 | 2210 | -264 | 1 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -302.0595 | 1452.7633 | -3550 | -400 | -2497.2367 | 62.43% | 57.31% | 95% | 0% | 2474 | -264
[5 empty] | 2019-07-24 | 38 | 4914 | 2288 | -200 | 1 | 0 | 2488 | 1776.7519 | 1776.7519 | 1776.7519 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -228.833 | 1547.9189 | -3550 | -400 | -2402.0811 | 60.05% | 57.3% | 95% | 0% | 2488 | -200
[5 empty] | 2019-07-24 | 39 | 4914.5 | 2315 | -149 | 1 | 0 | 2464 | 1739.1591 | 1739.1591 | 1739.1591 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -170.4805 | 1568.6786 | -3550 | -400 | -2381.3214 | 59.53% | 57.3% | 95% | 0% | 2464 | -149
[5 empty] | 2019-07-24 | 40 | 4915 | 2351 | -111 | 1 | 0 | 2462 | 1736.0264 | 1736.0264 | 1736.0264 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -127.0023 | 1609.0241 | -3550 | -400 | -2340.9759 | 58.52% | 57.3% | 95% | 0% | 2462 | -111
[5 empty] | 2019-07-24 | 41 | 4915.5 | 2374 | -79 | 1 | 0 | 2453 | 1721.9291 | 1721.9291 | 1721.9291 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -90.389 | 1631.5401 | -3550 | -400 | -2318.4599 | 57.96% | 57.29% | 95% | 0% | 2453 | -79
[5 empty] | 2019-07-24 | 42 | 4916 | 2361 | -60 | 1 | 0 | 2421 | 1671.8054 | 1671.8054 | 1671.8054 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -68.6499 | 1603.1556 | -3550 | -400 | -2346.8444 | 58.67% | 57.29% | 95% | 0% | 2421 | -60
[5 empty] | 2019-07-24 | 43 | 4916.5 | 2376 | -55 | 1 | 0 | 2431 | 1687.4691 | 1687.4691 | 1687.4691 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -62.9291 | 1624.54 | -3550 | -400 | -2325.46 | 58.14% | 57.29% | 95% | 0% | 2431 | -55
[5 empty] | 2019-07-24 | 44 | 4917 | 2362 | -55 | 1 | 0 | 2417 | 1665.54 | 1665.54 | 1665.54 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -62.9291 | 1602.6109 | -3550 | -400 | -2347.3891 | 58.68% | 57.29% | 95% | 0% | 2417 | -55
[5 empty] | 2019-07-24 | 45 | 4917.5 | 2260 | -57 | 0 | 0 | 2317 | 1508.9035 | 1508.9035 | 1508.9035 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -65.2174 | 1443.6862 | -2750 | -200 | -1506.3138 | 37.66% | 57.28% | 95% | 0% | 2317 | -57
[5 empty] | 2019-07-24 | 46 | 4918 | 2153 | -58 | 0 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -66.3616 | 1276.5074 | -2750 | -200 | -1673.4926 | 41.84% | 57.28% | 95% | 0% | 2211 | -58
[5 empty] | 2019-07-24 | 47 | 4918.5 | 2043 | -59 | 0 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -67.5057 | 1104.6295 | -2750 | -200 | -1845.3705 | 46.13% | 57.28% | 95% | 0% | 2102 | -59
[5 empty] | 2019-07-24 | 48 | 4919 | 1923 | -60 | 0 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -68.6499 | 917.088 | -2750 | -200 | -2032.912 | 50.82% | 57.27% | 95% | 0% | 1983 | -60
[5 empty] | 2019-07-25 | 1 | 4919.5 | 1819 | -62 | 0 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -70.9382 | 755.0305 | -2750 | -200 | -2194.9695 | 54.87% | 57.26% | 95% | 0% | 1881 | -62
[5 empty] | 2019-07-25 | 2 | 4920 | 1755 | -65 | 1 | 0 | 1820 | 730.4204 | 730.4204 | 730.4204 | 1233.2234 | 780 | 200 | 2213.2234 | 55.33% | 95% | 0% | -74.3707 | 656.0497 | -3550 | -400 | -3293.9503 | 82.35% | 57.26% | 95% | 0% | 1820 | -65
[5 empty] | 2019-07-25 | 3 | 4920.5 | 1697 | -66 | 1 | 0 | 1763 | 641.1377 | 641.1377 | 641.1377 | 1231.657 | 780 | 200 | 2211.657 | 55.29% | 95% | 0% | -75.5149 | 565.6228 | -3550 | -400 | -3384.3772 | 84.61% | 57.26% | 95% | 0% | 1763 | -66
[5 empty] | 2019-07-25 | 4 | 4921 | 1665 | -67 | 1 | 0 | 1732 | 592.5804 | 592.5804 | 592.5804 | 1231.657 | 780 | 200 | 2211.657 | 55.29% | 95% | 0% | -76.659 | 515.9213 | -3550 | -400 | -3434.0787 | 85.85% | 57.25% | 95% | 0% | 1732 | -67
[5 empty] | 2019-07-25 | 5 | 4921.5 | 1631 | -68 | 1 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 1231.657 | 780 | 200 | 2211.657 | 55.29% | 95% | 0% | -77.8032 | 463.0872 | -3550 | -400 | -3486.9128 | 87.17% | 57.25% | 95% | 0% | 1699 | -68
[5 empty] | 2019-07-25 | 6 | 4922 | 1606 | -68 | 1 | 0 | 1674 | 501.7312 | 501.7312 | 501.7312 | 1231.657 | 780 | 200 | 2211.657 | 55.29% | 95% | 0% | -77.8032 | 423.928 | -3550 | -400 | -3526.072 | 88.15% | 57.25% | 95% | 0% | 1674 | -68
[5 empty] | 2019-07-25 | 7 | 4922.5 | 1573 | -71 | 1 | 0 | 1644 | 454.7403 | 454.7403 | 454.7403 | 1231.657 | 780 | 200 | 2211.657 | 55.29% | 95% | 0% | -81.2357 | 373.5046 | -3550 | -400 | -3576.4954 | 89.41% | 57.24% | 95% | 0% | 1644 | -71
[5 empty] | 2019-07-25 | 8 | 4923 | 1561 | -74 | 1 | 0 | 1635 | 440.643 | 440.643 | 440.643 | 1231.657 | 780 | 200 | 2211.657 | 55.29% | 95% | 0% | -84.6682 | 355.9748 | -3550 | -400 | -3594.0252 | 89.85% | 57.24% | 95% | 0% | 1635 | -74
[5 empty] | 2019-07-25 | 9 | 4923.5 | 1546 | -79 | 1 | 0 | 1625 | 424.9794 | 424.9794 | 424.9794 | 1231.657 | 780 | 200 | 2211.657 | 55.29% | 95% | 0% | -90.389 | 334.5904 | -3550 | -400 | -3615.4096 | 90.39% | 57.23% | 95% | 0% | 1625 | -79
[5 empty] | 2019-07-25 | 10 | 4924 | 1557 | -84 | 1 | 0 | 1641 | 450.0412 | 450.0412 | 450.0412 | 1231.657 | 780 | 200 | 2211.657 | 55.29% | 95% | 0% | -96.1098 | 353.9314 | -3550 | -400 | -3596.0686 | 89.9% | 57.23% | 95% | 0% | 1641 | -84
[5 empty] | 2019-07-25 | 11 | 4924.5 | 1566 | -86 | 1 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 1231.657 | 780 | 200 | 2211.657 | 55.29% | 95% | 0% | -98.3982 | 368.8731 | -3550 | -400 | -3581.1269 | 89.53% | 57.23% | 95% | 0% | 1652 | -86
[5 empty] | 2019-07-25 | 12 | 4925 | 1602 | -97 | 1 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 1231.657 | 780 | 200 | 2211.657 | 55.29% | 95% | 0% | -110.984 | 429.9064 | -3550 | -400 | -3520.0936 | 88% | 57.23% | 95% | 0% | 1699 | -97
[5 empty] | 2019-07-25 | 13 | 4925.5 | 1728 | -124 | 1 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 1231.657 | 780 | 200 | 2211.657 | 55.29% | 95% | 0% | -141.8764 | 638.6677 | -3550 | -400 | -3311.3323 | 82.78% | 57.23% | 95% | 0% | 1852 | -124
[5 empty] | 2019-07-25 | 14 | 4926 | 1839 | -163 | 1 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 1231.657 | 780 | 200 | 2211.657 | 55.29% | 95% | 0% | -186.4989 | 828.9999 | -3550 | -400 | -3121.0001 | 78.03% | 57.22% | 95% | 0% | 2002 | -163
[5 empty] | 2019-07-25 | 15 | 4926.5 | 1956 | -211 | 1 | 0 | 2167 | 1273.9489 | 1273.9489 | 1273.9489 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -241.4188 | 1032.5301 | -3550 | -400 | -2917.4699 | 72.94% | 57.22% | 95% | 0% | 2167 | -211
[5 empty] | 2019-07-25 | 16 | 4927 | 2007 | -264 | 1 | 0 | 2271 | 1436.8508 | 1436.8508 | 1436.8508 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -302.0595 | 1134.7913 | -3550 | -400 | -2815.2087 | 70.38% | 57.22% | 95% | 0% | 2271 | -264
[5 empty] | 2019-07-25 | 17 | 4927.5 | 2025 | -328 | 1 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -375.286 | 1190.0066 | -3550 | -400 | -2759.9934 | 69% | 57.21% | 95% | 0% | 2353 | -328
[5 empty] | 2019-07-25 | 18 | 4928 | 1988 | -394 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -450.8009 | 1159.9163 | -3550 | -400 | -2790.0837 | 69.75% | 57.21% | 95% | 0% | 2382 | -394
[5 empty] | 2019-07-25 | 19 | 4928.5 | 1914 | -470 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -537.7574 | 1076.0925 | -3550 | -400 | -2873.9075 | 71.85% | 57.21% | 95% | 0% | 2384 | -470
[5 empty] | 2019-07-25 | 20 | 4929 | 1814 | -535 | 1 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -612.1281 | 946.8991 | -3550 | -400 | -3003.1009 | 75.08% | 57.21% | 95% | 0% | 2349 | -535
[5 empty] | 2019-07-25 | 21 | 4929.5 | 1707 | -597 | 1 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -683.0664 | 805.4744 | -3550 | -400 | -3144.5256 | 78.61% | 57.2% | 95% | 0% | 2304 | -597
[5 empty] | 2019-07-25 | 22 | 4930 | 1662 | -648 | 1 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -741.4188 | 756.5202 | -3550 | -400 | -3193.4798 | 79.84% | 57.2% | 95% | 0% | 2310 | -648
[5 empty] | 2019-07-25 | 23 | 4930.5 | 1633 | -688 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -787.1854 | 727.9836 | -3550 | -400 | -3222.0164 | 80.55% | 57.2% | 95% | 0% | 2321 | -688
[5 empty] | 2019-07-25 | 24 | 4931 | 1599 | -717 | 1 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -820.3661 | 686.971 | -3550 | -400 | -3263.029 | 81.58% | 57.2% | 95% | 0% | 2316 | -717
[5 empty] | 2019-07-25 | 25 | 4931.5 | 1564 | -743 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -850.1144 | 643.1255 | -3550 | -400 | -3306.8745 | 82.67% | 57.2% | 95% | 0% | 2307 | -743
[5 empty] | 2019-07-25 | 26 | 4932 | 1560 | -748 | 1 | 0 | 2308 | 1494.8063 | 1494.8063 | 1494.8063 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -855.8352 | 638.971 | -3550 | -400 | -3311.029 | 82.78% | 57.19% | 95% | 0% | 2308 | -748
[5 empty] | 2019-07-25 | 27 | 4932.5 | 1558 | -746 | 1 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -853.5469 | 634.9939 | -3550 | -400 | -3315.0061 | 82.88% | 57.18% | 95% | 0% | 2304 | -746
[5 empty] | 2019-07-25 | 28 | 4933 | 1573 | -726 | 1 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -830.6636 | 650.0454 | -3550 | -400 | -3299.9546 | 82.5% | 57.18% | 95% | 0% | 2299 | -726
[5 empty] | 2019-07-25 | 29 | 4933.5 | 1606 | -690 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -789.4737 | 686.5362 | -3550 | -400 | -3263.4638 | 81.59% | 57.18% | 95% | 0% | 2296 | -690
[5 empty] | 2019-07-25 | 30 | 4934 | 1686 | -609 | 1 | 0 | 2295 | 1474.4435 | 1474.4435 | 1474.4435 | 1230.0907 | 780 | 200 | 2210.0907 | 55.25% | 95% | 0% | -696.7963 | 777.6472 | -3550 | -400 | -3172.3528 | 79.31% | 57.17% | 95% | 0% | 2295 | -609
[5 empty] | 2019-07-25 | 31 | 4934.5 | 1695 | -610 | 1 | 0 | 2305 | 1490.1072 | 1490.1072 | 1490.1072 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -697.9405 | 792.1667 | -3550 | -400 | -3157.8333 | 78.95% | 57.17% | 95% | 0% | 2305 | -610
[5 empty] | 2019-07-25 | 32 | 4935 | 1760 | -569 | 1 | 0 | 2329 | 1527.6999 | 1527.6999 | 1527.6999 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -651.0297 | 876.6702 | -3550 | -400 | -3073.3298 | 76.83% | 57.16% | 95% | 0% | 2329 | -569
[5 empty] | 2019-07-25 | 33 | 4935.5 | 1871 | -483 | 1 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -552.6316 | 1014.2274 | -3550 | -400 | -2935.7726 | 73.39% | 57.16% | 95% | 0% | 2354 | -483
[5 empty] | 2019-07-25 | 34 | 4936 | 1991 | -411 | 1 | 0 | 2402 | 1642.0445 | 1642.0445 | 1642.0445 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -470.2517 | 1171.7928 | -3550 | -400 | -2778.2072 | 69.46% | 57.16% | 95% | 0% | 2402 | -411
[5 empty] | 2019-07-25 | 35 | 4936.5 | 2083 | -360 | 1 | 0 | 2443 | 1706.2655 | 1706.2655 | 1706.2655 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -411.8993 | 1294.3661 | -3550 | -400 | -2655.6339 | 66.39% | 57.15% | 95% | 0% | 2443 | -360
[5 empty] | 2019-07-25 | 36 | 4937 | 2172 | -298 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -340.9611 | 1407.5962 | -3550 | -400 | -2542.4038 | 63.56% | 57.15% | 95% | 0% | 2470 | -298
[5 empty] | 2019-07-25 | 37 | 4937.5 | 2230 | -254 | 1 | 0 | 2484 | 1770.4864 | 1770.4864 | 1770.4864 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -290.6178 | 1479.8685 | -3550 | -400 | -2470.1315 | 61.75% | 57.14% | 95% | 0% | 2484 | -254
[5 empty] | 2019-07-25 | 38 | 4938 | 2285 | -214 | 1 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -244.8513 | 1549.1306 | -3550 | -400 | -2400.8694 | 60.02% | 57.14% | 95% | 0% | 2499 | -214
[5 empty] | 2019-07-25 | 39 | 4938.5 | 2313 | -175 | 1 | 0 | 2488 | 1776.7519 | 1776.7519 | 1776.7519 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -200.2288 | 1576.523 | -3550 | -400 | -2373.477 | 59.34% | 57.14% | 95% | 0% | 2488 | -175
[5 empty] | 2019-07-25 | 40 | 4939 | 2304 | -155 | 1 | 0 | 2459 | 1731.3273 | 1731.3273 | 1731.3273 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -177.3455 | 1553.9817 | -3550 | -400 | -2396.0183 | 59.9% | 57.13% | 95% | 0% | 2459 | -155
[5 empty] | 2019-07-25 | 41 | 4939.5 | 2339 | -123 | 1 | 0 | 2462 | 1736.0264 | 1736.0264 | 1736.0264 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -140.7323 | 1595.2941 | -3550 | -400 | -2354.7059 | 58.87% | 57.13% | 95% | 0% | 2462 | -123
[5 empty] | 2019-07-25 | 42 | 4940 | 2341 | -106 | 1 | 0 | 2447 | 1712.5309 | 1712.5309 | 1712.5309 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -121.2815 | 1591.2495 | -3550 | -400 | -2358.7505 | 58.97% | 57.13% | 95% | 0% | 2447 | -106
[5 empty] | 2019-07-25 | 43 | 4940.5 | 2311 | -101 | 1 | 0 | 2412 | 1657.7082 | 1657.7082 | 1657.7082 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -115.5606 | 1542.1475 | -3550 | -400 | -2407.8525 | 60.2% | 57.12% | 95% | 0% | 2412 | -101
[5 empty] | 2019-07-25 | 44 | 4941 | 2311 | -100 | 1 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -114.4165 | 1541.7253 | -3550 | -400 | -2408.2747 | 60.21% | 57.12% | 95% | 0% | 2411 | -100
[5 empty] | 2019-07-25 | 45 | 4941.5 | 2212 | -98 | 0 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -112.1281 | 1385.8108 | -2750 | -200 | -1564.1892 | 39.1% | 57.12% | 95% | 0% | 2310 | -98
[5 empty] | 2019-07-25 | 46 | 4942 | 2111 | -96 | 0 | 0 | 2207 | 1336.6035 | 1336.6035 | 1336.6035 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -109.8398 | 1226.7636 | -2750 | -200 | -1723.2364 | 43.08% | 57.12% | 95% | 0% | 2207 | -96
[5 empty] | 2019-07-25 | 47 | 4942.5 | 1996 | -93 | 0 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -106.4073 | 1045.3651 | -2750 | -200 | -1904.6349 | 47.62% | 57.12% | 95% | 0% | 2089 | -93
[5 empty] | 2019-07-25 | 48 | 4943 | 1875 | -90 | 0 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -102.9748 | 854.5685 | -2750 | -200 | -2095.4315 | 52.39% | 57.11% | 95% | 0% | 1965 | -90
[5 empty] | 2019-07-26 | 1 | 4943.5 | 1778 | -88 | 0 | 0 | 1866 | 802.4732 | 802.4732 | 802.4732 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -100.6865 | 701.7867 | -2750 | -200 | -2248.2133 | 56.21% | 57.11% | 95% | 0% | 1866 | -88
[5 empty] | 2019-07-26 | 2 | 4944 | 1719 | -86 | 0 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -98.3982 | 608.5268 | -2750 | -200 | -2341.4732 | 58.54% | 57.1% | 95% | 0% | 1805 | -86
[5 empty] | 2019-07-26 | 3 | 4944.5 | 1686 | -84 | 0 | 0 | 1770 | 652.1022 | 652.1022 | 652.1022 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -96.1098 | 555.9924 | -2750 | -200 | -2394.0076 | 59.85% | 57.1% | 95% | 0% | 1770 | -84
[5 empty] | 2019-07-26 | 4 | 4945 | 1648 | -81 | 0 | 0 | 1729 | 587.8813 | 587.8813 | 587.8813 | 1228.5243 | 780 | 200 | 2208.5243 | 55.21% | 95% | 0% | -92.6773 | 495.2039 | -2750 | -200 | -2454.7961 | 61.37% | 57.1% | 95% | 0% | 1729 | -81
[5 empty] | 2019-07-26 | 5 | 4945.5 | 1610 | -79 | 0 | 0 | 1689 | 525.2267 | 525.2267 | 525.2267 | 1226.958 | 780 | 200 | 2206.958 | 55.17% | 95% | 0% | -90.389 | 434.8377 | -2750 | -200 | -2515.1623 | 62.88% | 57.1% | 95% | 0% | 1689 | -79
[5 empty] | 2019-07-26 | 6 | 4946 | 1586 | -77 | 0 | 0 | 1663 | 484.5012 | 484.5012 | 484.5012 | 1226.958 | 780 | 200 | 2206.958 | 55.17% | 95% | 0% | -88.1007 | 396.4006 | -2750 | -200 | -2553.5994 | 63.84% | 57.09% | 95% | 0% | 1663 | -77
[5 empty] | 2019-07-26 | 7 | 4946.5 | 1593 | -74 | 0 | 0 | 1667 | 490.7667 | 490.7667 | 490.7667 | 1226.958 | 780 | 200 | 2206.958 | 55.17% | 95% | 0% | -84.6682 | 406.0985 | -2750 | -200 | -2543.9015 | 63.6% | 57.09% | 95% | 0% | 1667 | -74
[5 empty] | 2019-07-26 | 8 | 4947 | 1589 | -72 | 0 | 0 | 1661 | 481.3685 | 481.3685 | 481.3685 | 1226.958 | 780 | 200 | 2206.958 | 55.17% | 95% | 0% | -82.3799 | 398.9886 | -2750 | -200 | -2551.0114 | 63.78% | 57.08% | 95% | 0% | 1661 | -72
[5 empty] | 2019-07-26 | 9 | 4947.5 | 1594 | -75 | 0 | 0 | 1669 | 493.8994 | 493.8994 | 493.8994 | 1226.958 | 780 | 200 | 2206.958 | 55.17% | 95% | 0% | -85.8124 | 408.0871 | -2750 | -200 | -2541.9129 | 63.55% | 57.07% | 95% | 0% | 1669 | -75
[5 empty] | 2019-07-26 | 10 | 4948 | 1612 | -78 | 0 | 0 | 1690 | 526.7931 | 526.7931 | 526.7931 | 1226.958 | 780 | 200 | 2206.958 | 55.17% | 95% | 0% | -89.2449 | 437.5482 | -2750 | -200 | -2512.4518 | 62.81% | 57.07% | 95% | 0% | 1690 | -78
[5 empty] | 2019-07-26 | 11 | 4948.5 | 1626 | -76 | 0 | 0 | 1702 | 545.5894 | 545.5894 | 545.5894 | 1226.958 | 780 | 200 | 2206.958 | 55.17% | 95% | 0% | -86.9565 | 458.6329 | -2750 | -200 | -2491.3671 | 62.28% | 57.06% | 95% | 0% | 1702 | -76
[5 empty] | 2019-07-26 | 12 | 4949 | 1667 | -77 | 0 | 0 | 1744 | 611.3768 | 611.3768 | 611.3768 | 1226.958 | 780 | 200 | 2206.958 | 55.17% | 95% | 0% | -88.1007 | 523.2761 | -2750 | -200 | -2426.7239 | 60.67% | 57.06% | 95% | 0% | 1744 | -77
[5 empty] | 2019-07-26 | 13 | 4949.5 | 1788 | -92 | 1 | 0 | 1880 | 824.4023 | 824.4023 | 824.4023 | 1225.3916 | 780 | 200 | 2205.3916 | 55.13% | 95% | 0% | -105.2632 | 719.1392 | -3550 | -400 | -3230.8608 | 80.77% | 57.06% | 95% | 0% | 1880 | -92
[5 empty] | 2019-07-26 | 14 | 4950 | 1906 | -113 | 1 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 1225.3916 | 780 | 200 | 2205.3916 | 55.13% | 95% | 0% | -129.2906 | 912.8363 | -3550 | -400 | -3037.1637 | 75.93% | 57.04% | 95% | 0% | 2019 | -113
[5 empty] | 2019-07-26 | 15 | 4950.5 | 2051 | -140 | 1 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 1225.3916 | 780 | 200 | 2205.3916 | 55.13% | 95% | 0% | -160.1831 | 1151.3586 | -3550 | -400 | -2798.6414 | 69.97% | 57.04% | 95% | 0% | 2191 | -140
[5 empty] | 2019-07-26 | 16 | 4951 | 2118 | -169 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1225.3916 | 780 | 200 | 2205.3916 | 55.13% | 95% | 0% | -193.3638 | 1268.5488 | -3550 | -400 | -2681.4512 | 67.04% | 57.04% | 95% | 0% | 2287 | -169
[5 empty] | 2019-07-26 | 17 | 4951.5 | 2158 | -211 | 1 | 0 | 2369 | 1590.3545 | 1590.3545 | 1590.3545 | 1225.3916 | 780 | 200 | 2205.3916 | 55.13% | 95% | 0% | -241.4188 | 1348.9357 | -3550 | -400 | -2601.0643 | 65.03% | 57.04% | 95% | 0% | 2369 | -211
[5 empty] | 2019-07-26 | 18 | 4952 | 2122 | -284 | 1 | 0 | 2406 | 1648.31 | 1648.31 | 1648.31 | 1225.3916 | 780 | 200 | 2205.3916 | 55.13% | 95% | 0% | -324.9428 | 1323.3672 | -3550 | -400 | -2626.6328 | 65.67% | 57.03% | 95% | 0% | 2406 | -284
[5 empty] | 2019-07-26 | 19 | 4952.5 | 2115 | -322 | 1 | 0 | 2437 | 1696.8673 | 1696.8673 | 1696.8673 | 1225.3916 | 780 | 200 | 2205.3916 | 55.13% | 95% | 0% | -368.4211 | 1328.4462 | -3550 | -400 | -2621.5538 | 65.54% | 57.02% | 95% | 0% | 2437 | -322
[5 empty] | 2019-07-26 | 20 | 4953 | 2088 | -338 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1225.3916 | 780 | 200 | 2205.3916 | 55.13% | 95% | 0% | -386.7277 | 1292.9096 | -3550 | -400 | -2657.0904 | 66.43% | 57.02% | 95% | 0% | 2426 | -338
[5 empty] | 2019-07-26 | 21 | 4953.5 | 2068 | -355 | 1 | 0 | 2423 | 1674.9382 | 1674.9382 | 1674.9382 | 1225.3916 | 780 | 200 | 2205.3916 | 55.13% | 95% | 0% | -406.1785 | 1268.7597 | -3550 | -400 | -2681.2403 | 67.03% | 57.02% | 95% | 0% | 2423 | -355
[5 empty] | 2019-07-26 | 22 | 4954 | 2021 | -378 | 1 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 1225.3916 | 780 | 200 | 2205.3916 | 55.13% | 95% | 0% | -432.4943 | 1204.8511 | -3550 | -400 | -2745.1489 | 68.63% | 57.02% | 95% | 0% | 2399 | -378
[5 empty] | 2019-07-26 | 23 | 4954.5 | 1948 | -414 | 1 | 0 | 2362 | 1579.3899 | 1579.3899 | 1579.3899 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -473.6842 | 1105.7057 | -3550 | -400 | -2844.2943 | 71.11% | 57.01% | 95% | 0% | 2362 | -414
[5 empty] | 2019-07-26 | 24 | 4955 | 1964 | -401 | 1 | 0 | 2365 | 1584.089 | 1584.089 | 1584.089 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -458.8101 | 1125.279 | -3550 | -400 | -2824.721 | 70.62% | 57.01% | 95% | 0% | 2365 | -401
[5 empty] | 2019-07-26 | 25 | 4955.5 | 2000 | -416 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -475.9725 | 1188.0011 | -3550 | -400 | -2761.9989 | 69.05% | 57.01% | 95% | 0% | 2416 | -416
[5 empty] | 2019-07-26 | 26 | 4956 | 2006 | -396 | 1 | 0 | 2402 | 1642.0445 | 1642.0445 | 1642.0445 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -453.0892 | 1188.9553 | -3550 | -400 | -2761.0447 | 69.03% | 57% | 95% | 0% | 2402 | -396
[5 empty] | 2019-07-26 | 27 | 4956.5 | 1954 | -427 | 1 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -488.5584 | 1120.5925 | -3550 | -400 | -2829.4075 | 70.74% | 56.99% | 95% | 0% | 2381 | -427
[5 empty] | 2019-07-26 | 28 | 4957 | 1917 | -439 | 1 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -502.2883 | 1067.7034 | -3550 | -400 | -2882.2966 | 72.06% | 56.99% | 95% | 0% | 2356 | -439
[5 empty] | 2019-07-26 | 29 | 4957.5 | 1906 | -426 | 1 | 0 | 2332 | 1532.399 | 1532.399 | 1532.399 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -487.4142 | 1044.9848 | -3550 | -400 | -2905.0152 | 72.63% | 56.99% | 95% | 0% | 2332 | -426
[5 empty] | 2019-07-26 | 30 | 4958 | 1884 | -431 | 1 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -493.135 | 1012.6358 | -3550 | -400 | -2937.3642 | 73.43% | 56.99% | 95% | 0% | 2315 | -431
[5 empty] | 2019-07-26 | 31 | 4958.5 | 1913 | -397 | 1 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -454.2334 | 1043.7056 | -3550 | -400 | -2906.2944 | 72.66% | 56.99% | 95% | 0% | 2310 | -397
[5 empty] | 2019-07-26 | 32 | 4959 | 1917 | -411 | 1 | 0 | 2328 | 1526.1336 | 1526.1336 | 1526.1336 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -470.2517 | 1055.8818 | -3550 | -400 | -2894.1182 | 72.35% | 56.99% | 95% | 0% | 2328 | -411
[5 empty] | 2019-07-26 | 33 | 4959.5 | 1995 | -348 | 1 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -398.1693 | 1151.4597 | -3550 | -400 | -2798.5403 | 69.96% | 56.98% | 95% | 0% | 2343 | -348
[5 empty] | 2019-07-26 | 34 | 4960 | 2083 | -303 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -346.6819 | 1270.3008 | -3550 | -400 | -2679.6992 | 66.99% | 56.98% | 95% | 0% | 2386 | -303
[5 empty] | 2019-07-26 | 35 | 4960.5 | 2168 | -257 | 1 | 0 | 2425 | 1678.0709 | 1678.0709 | 1678.0709 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -294.0503 | 1384.0206 | -3550 | -400 | -2565.9794 | 64.15% | 56.97% | 95% | 0% | 2425 | -257
[5 empty] | 2019-07-26 | 36 | 4961 | 2226 | -209 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -239.1304 | 1454.6041 | -3550 | -400 | -2495.3959 | 62.38% | 56.97% | 95% | 0% | 2435 | -209
[5 empty] | 2019-07-26 | 37 | 4961.5 | 2268 | -167 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1223.8252 | 780 | 200 | 2203.8252 | 55.1% | 95% | 0% | -191.0755 | 1502.659 | -3550 | -400 | -2447.341 | 61.18% | 56.96% | 95% | 0% | 2435 | -167
[5 empty] | 2019-07-26 | 38 | 4962 | 2318 | -136 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -155.6064 | 1567.8891 | -3550 | -400 | -2382.1109 | 59.55% | 56.96% | 95% | 0% | 2454 | -136
[5 empty] | 2019-07-26 | 39 | 4962.5 | 2313 | -108 | 1 | 0 | 2421 | 1671.8054 | 1671.8054 | 1671.8054 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -123.5698 | 1548.2356 | -3550 | -400 | -2401.7644 | 60.04% | 56.96% | 95% | 0% | 2421 | -108
[5 empty] | 2019-07-26 | 40 | 4963 | 2320 | -80 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -91.5332 | 1547.3786 | -3550 | -400 | -2402.6214 | 60.07% | 56.96% | 95% | 0% | 2400 | -80
[5 empty] | 2019-07-26 | 41 | 4963.5 | 2322 | -62 | 1 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -70.9382 | 1542.9117 | -3550 | -400 | -2407.0883 | 60.18% | 56.95% | 95% | 0% | 2384 | -62
[5 empty] | 2019-07-26 | 42 | 4964 | 2304 | -52 | 1 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -59.4966 | 1510.4952 | -3550 | -400 | -2439.5048 | 60.99% | 56.95% | 95% | 0% | 2356 | -52
[5 empty] | 2019-07-26 | 43 | 4964.5 | 2282 | -49 | 1 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -56.0641 | 1474.7686 | -3550 | -400 | -2475.2314 | 61.88% | 56.93% | 95% | 0% | 2331 | -49
[5 empty] | 2019-07-26 | 44 | 4965 | 2247 | -48 | 1 | 0 | 2295 | 1474.4435 | 1474.4435 | 1474.4435 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -54.9199 | 1419.5236 | -3550 | -400 | -2530.4764 | 63.26% | 56.93% | 95% | 0% | 2295 | -48
[5 empty] | 2019-07-26 | 45 | 4965.5 | 2178 | -47 | 0 | 0 | 2225 | 1364.798 | 1364.798 | 1364.798 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -53.7757 | 1311.0223 | -2750 | -200 | -1638.9777 | 40.97% | 56.93% | 95% | 0% | 2225 | -47
[5 empty] | 2019-07-26 | 46 | 4966 | 2074 | -45 | 0 | 0 | 2119 | 1198.7634 | 1198.7634 | 1198.7634 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -51.4874 | 1147.276 | -2750 | -200 | -1802.724 | 45.07% | 56.93% | 95% | 0% | 2119 | -45
[5 empty] | 2019-07-26 | 47 | 4966.5 | 1966 | -45 | 0 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -51.4874 | 978.1086 | -2750 | -200 | -1971.8914 | 49.3% | 56.92% | 95% | 0% | 2011 | -45
[5 empty] | 2019-07-26 | 48 | 4967 | 1878 | -45 | 0 | 0 | 1923 | 891.756 | 891.756 | 891.756 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -51.4874 | 840.2686 | -2750 | -200 | -2109.7314 | 52.74% | 56.92% | 95% | 0% | 1923 | -45
[5 empty] | 2019-07-27 | 1 | 4967.5 | 1773 | -43 | 0 | 0 | 1816 | 724.155 | 724.155 | 724.155 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -49.1991 | 674.9559 | -2750 | -200 | -2275.0441 | 56.88% | 56.92% | 95% | 0% | 1816 | -43
[5 empty] | 2019-07-27 | 2 | 4968 | 1703 | -42 | 0 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 1222.2589 | 780 | 200 | 2202.2589 | 55.06% | 95% | 0% | -48.0549 | 564.8882 | -2750 | -200 | -2385.1118 | 59.63% | 56.92% | 95% | 0% | 1745 | -42
[5 empty] | 2019-07-27 | 3 | 4968.5 | 1648 | -42 | 0 | 0 | 1690 | 526.7931 | 526.7931 | 526.7931 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -48.0549 | 478.7382 | -2750 | -200 | -2471.2618 | 61.78% | 56.91% | 95% | 0% | 1690 | -42
[5 empty] | 2019-07-27 | 4 | 4969 | 1611 | -43 | 0 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -49.1991 | 421.2049 | -2750 | -200 | -2528.7951 | 63.22% | 56.91% | 95% | 0% | 1654 | -43
[5 empty] | 2019-07-27 | 5 | 4969.5 | 1574 | -42 | 0 | 0 | 1616 | 410.8821 | 410.8821 | 410.8821 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -48.0549 | 362.8272 | -2750 | -200 | -2587.1728 | 64.68% | 56.91% | 95% | 0% | 1616 | -42
[5 empty] | 2019-07-27 | 6 | 4970 | 1552 | -41 | 0 | 0 | 1593 | 374.8557 | 374.8557 | 374.8557 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -46.9108 | 327.945 | -2750 | -200 | -2622.055 | 65.55% | 56.9% | 95% | 0% | 1593 | -41
[5 empty] | 2019-07-27 | 7 | 4970.5 | 1535 | -40 | 0 | 0 | 1575 | 346.6612 | 346.6612 | 346.6612 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -45.7666 | 300.8946 | -2750 | -200 | -2649.1054 | 66.23% | 56.89% | 95% | 0% | 1575 | -40
[5 empty] | 2019-07-27 | 8 | 4971 | 1527 | -39 | 0 | 0 | 1566 | 332.5639 | 332.5639 | 332.5639 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -44.6224 | 287.9415 | -2750 | -200 | -2662.0585 | 66.55% | 56.89% | 95% | 0% | 1566 | -39
[5 empty] | 2019-07-27 | 9 | 4971.5 | 1516 | -40 | 0 | 0 | 1556 | 316.9002 | 316.9002 | 316.9002 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -45.7666 | 271.1337 | -2750 | -200 | -2678.8663 | 66.97% | 56.89% | 95% | 0% | 1556 | -40
[5 empty] | 2019-07-27 | 10 | 4972 | 1514 | -42 | 0 | 0 | 1556 | 316.9002 | 316.9002 | 316.9002 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -48.0549 | 268.8453 | -2750 | -200 | -2681.1547 | 67.03% | 56.89% | 95% | 0% | 1556 | -42
[5 empty] | 2019-07-27 | 11 | 4972.5 | 1520 | -43 | 0 | 0 | 1563 | 327.8648 | 327.8648 | 327.8648 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -49.1991 | 278.6657 | -2750 | -200 | -2671.3343 | 66.78% | 56.89% | 95% | 0% | 1563 | -43
[5 empty] | 2019-07-27 | 12 | 4973 | 1518 | -46 | 0 | 0 | 1564 | 329.4312 | 329.4312 | 329.4312 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -52.6316 | 276.7996 | -2750 | -200 | -2673.2004 | 66.83% | 56.88% | 95% | 0% | 1564 | -46
[5 empty] | 2019-07-27 | 13 | 4973.5 | 1582 | -53 | 0 | 0 | 1635 | 440.643 | 440.643 | 440.643 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -60.6407 | 380.0023 | -2750 | -200 | -2569.9977 | 64.25% | 56.87% | 95% | 0% | 1635 | -53
[5 empty] | 2019-07-27 | 14 | 4974 | 1634 | -65 | 0 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -74.3707 | 466.5196 | -2750 | -200 | -2483.4804 | 62.09% | 56.87% | 95% | 0% | 1699 | -65
[5 empty] | 2019-07-27 | 15 | 4974.5 | 1706 | -83 | 0 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -94.9657 | 586.8975 | -2750 | -200 | -2363.1025 | 59.08% | 56.87% | 95% | 0% | 1789 | -83
[5 empty] | 2019-07-27 | 16 | 4975 | 1772 | -101 | 1 | 0 | 1873 | 813.4378 | 813.4378 | 813.4378 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -115.5606 | 697.8771 | -3550 | -400 | -3252.1229 | 81.3% | 56.87% | 95% | 0% | 1873 | -101
[5 empty] | 2019-07-27 | 17 | 4975.5 | 1857 | -122 | 1 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -139.5881 | 839.8843 | -3550 | -400 | -3110.1157 | 77.75% | 56.87% | 95% | 0% | 1979 | -122
[5 empty] | 2019-07-27 | 18 | 4976 | 1919 | -132 | 1 | 0 | 2051 | 1092.2506 | 1092.2506 | 1092.2506 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -151.0297 | 941.2209 | -3550 | -400 | -3008.7791 | 75.22% | 56.86% | 95% | 0% | 2051 | -132
[5 empty] | 2019-07-27 | 19 | 4976.5 | 1954 | -150 | 1 | 0 | 2104 | 1175.2679 | 1175.2679 | 1175.2679 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -171.6247 | 1003.6432 | -3550 | -400 | -2946.3568 | 73.66% | 56.86% | 95% | 0% | 2104 | -150
[5 empty] | 2019-07-27 | 20 | 4977 | 1953 | -175 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1220.6925 | 780 | 200 | 2200.6925 | 55.02% | 95% | 0% | -200.2288 | 1012.6318 | -3550 | -400 | -2937.3682 | 73.43% | 56.86% | 95% | 0% | 2128 | -175
[5 empty] | 2019-07-27 | 21 | 4977.5 | 1935 | -217 | 1 | 0 | 2152 | 1250.4534 | 1250.4534 | 1250.4534 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -248.2838 | 1002.1697 | -3550 | -400 | -2947.8303 | 73.7% | 56.86% | 95% | 0% | 2152 | -217
[5 empty] | 2019-07-27 | 22 | 4978 | 1893 | -254 | 1 | 0 | 2147 | 1242.6216 | 1242.6216 | 1242.6216 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -290.6178 | 952.0038 | -3550 | -400 | -2997.9962 | 74.95% | 56.85% | 95% | 0% | 2147 | -254
[5 empty] | 2019-07-27 | 23 | 4978.5 | 1848 | -267 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -305.492 | 887.0059 | -3550 | -400 | -3062.9941 | 76.57% | 56.85% | 95% | 0% | 2115 | -267
[5 empty] | 2019-07-27 | 24 | 4979 | 1794 | -290 | 1 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -331.8078 | 812.1329 | -3550 | -400 | -3137.8671 | 78.45% | 56.85% | 95% | 0% | 2084 | -290
[5 empty] | 2019-07-27 | 25 | 4979.5 | 1735 | -321 | 1 | 0 | 2056 | 1100.0824 | 1100.0824 | 1100.0824 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -367.2769 | 732.8056 | -3550 | -400 | -3217.1944 | 80.43% | 56.85% | 95% | 0% | 2056 | -321
[5 empty] | 2019-07-27 | 26 | 4980 | 1725 | -320 | 1 | 0 | 2045 | 1082.8524 | 1082.8524 | 1082.8524 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -366.1327 | 716.7197 | -3550 | -400 | -3233.2803 | 80.83% | 56.84% | 95% | 0% | 2045 | -320
[5 empty] | 2019-07-27 | 27 | 4980.5 | 1713 | -313 | 1 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -358.1236 | 694.9679 | -3550 | -400 | -3255.0321 | 81.38% | 56.84% | 95% | 0% | 2026 | -313
[5 empty] | 2019-07-27 | 28 | 4981 | 1672 | -313 | 1 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -358.1236 | 630.747 | -3550 | -400 | -3319.253 | 82.98% | 56.84% | 95% | 0% | 1985 | -313
[5 empty] | 2019-07-27 | 29 | 4981.5 | 1640 | -315 | 1 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -360.4119 | 581.4677 | -3550 | -400 | -3368.5323 | 84.21% | 56.83% | 95% | 0% | 1955 | -315
[5 empty] | 2019-07-27 | 30 | 4982 | 1631 | -317 | 1 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -362.7002 | 568.2149 | -3550 | -400 | -3381.7851 | 84.54% | 56.83% | 95% | 0% | 1948 | -317
[5 empty] | 2019-07-27 | 31 | 4982.5 | 1660 | -294 | 1 | 0 | 1954 | 940.3133 | 940.3133 | 940.3133 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -336.3844 | 603.9288 | -3550 | -400 | -3346.0712 | 83.65% | 56.83% | 95% | 0% | 1954 | -294
[5 empty] | 2019-07-27 | 32 | 4983 | 1674 | -287 | 1 | 0 | 1961 | 951.2778 | 951.2778 | 951.2778 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -328.3753 | 622.9025 | -3550 | -400 | -3327.0975 | 83.18% | 56.82% | 95% | 0% | 1961 | -287
[5 empty] | 2019-07-27 | 33 | 4983.5 | 1725 | -274 | 1 | 0 | 1999 | 1010.7997 | 1010.7997 | 1010.7997 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -313.5011 | 697.2985 | -3550 | -400 | -3252.7015 | 81.32% | 56.82% | 95% | 0% | 1999 | -274
[5 empty] | 2019-07-27 | 34 | 4984 | 1803 | -242 | 1 | 0 | 2045 | 1082.8524 | 1082.8524 | 1082.8524 | 1219.1261 | 780 | 200 | 2199.1261 | 54.98% | 95% | 0% | -276.8879 | 805.9646 | -3550 | -400 | -3144.0354 | 78.6% | 56.82% | 95% | 0% | 2045 | -242
[5 empty] | 2019-07-27 | 35 | 4984.5 | 1889 | -212 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -242.5629 | 928.0059 | -3550 | -400 | -3021.9941 | 75.55% | 56.81% | 95% | 0% | 2101 | -212
[5 empty] | 2019-07-27 | 36 | 4985 | 1931 | -192 | 1 | 0 | 2123 | 1205.0289 | 1205.0289 | 1205.0289 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -219.6796 | 985.3492 | -3550 | -400 | -2964.6508 | 74.12% | 56.81% | 95% | 0% | 2123 | -192
[5 empty] | 2019-07-27 | 37 | 4985.5 | 1966 | -167 | 1 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -191.0755 | 1029.617 | -3550 | -400 | -2920.383 | 73.01% | 56.81% | 95% | 0% | 2133 | -167
[5 empty] | 2019-07-27 | 38 | 4986 | 2005 | -140 | 1 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -160.1831 | 1079.3058 | -3550 | -400 | -2870.6942 | 71.77% | 56.81% | 95% | 0% | 2145 | -140
[5 empty] | 2019-07-27 | 39 | 4986.5 | 2021 | -120 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -137.2998 | 1095.9236 | -3550 | -400 | -2854.0764 | 71.35% | 56.8% | 95% | 0% | 2141 | -120
[5 empty] | 2019-07-27 | 40 | 4987 | 2022 | -105 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -120.1373 | 1091.157 | -3550 | -400 | -2858.843 | 71.47% | 56.8% | 95% | 0% | 2127 | -105
[5 empty] | 2019-07-27 | 41 | 4987.5 | 2018 | -92 | 1 | 0 | 2110 | 1184.6661 | 1184.6661 | 1184.6661 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -105.2632 | 1079.403 | -3550 | -400 | -2870.597 | 71.76% | 56.79% | 95% | 0% | 2110 | -92
[5 empty] | 2019-07-27 | 42 | 4988 | 1989 | -83 | 1 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -94.9657 | 1030.1786 | -3550 | -400 | -2919.8214 | 73% | 56.79% | 95% | 0% | 2072 | -83
[5 empty] | 2019-07-27 | 43 | 4988.5 | 1994 | -81 | 1 | 0 | 2075 | 1129.8434 | 1129.8434 | 1129.8434 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -92.6773 | 1037.166 | -3550 | -400 | -2912.834 | 72.82% | 56.78% | 95% | 0% | 2075 | -81
[5 empty] | 2019-07-27 | 44 | 4989 | 1970 | -81 | 1 | 0 | 2051 | 1092.2506 | 1092.2506 | 1092.2506 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -92.6773 | 999.5733 | -3550 | -400 | -2950.4267 | 73.76% | 56.78% | 95% | 0% | 2051 | -81
[5 empty] | 2019-07-27 | 45 | 4989.5 | 1907 | -82 | 0 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -93.8215 | 901.3145 | -2750 | -200 | -2048.6855 | 51.22% | 56.77% | 95% | 0% | 1989 | -82
[5 empty] | 2019-07-27 | 46 | 4990 | 1830 | -83 | 0 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -94.9657 | 781.1267 | -2750 | -200 | -2168.8733 | 54.22% | 56.77% | 95% | 0% | 1913 | -83
[5 empty] | 2019-07-27 | 47 | 4990.5 | 1720 | -84 | 0 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 1217.5598 | 780 | 200 | 2197.5598 | 54.94% | 95% | 0% | -96.1098 | 609.2488 | -2750 | -200 | -2340.7512 | 58.52% | 56.77% | 95% | 0% | 1804 | -84
[5 empty] | 2019-07-27 | 48 | 4991 | 1651 | -85 | 0 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -97.254 | 501.5918 | -2750 | -200 | -2448.4082 | 61.21% | 56.76% | 95% | 0% | 1736 | -85
[5 empty] | 2019-07-28 | 1 | 4991.5 | 1578 | -84 | 0 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -96.1098 | 386.825 | -2750 | -200 | -2563.175 | 64.08% | 56.76% | 95% | 0% | 1662 | -84
[5 empty] | 2019-07-28 | 2 | 4992 | 1478 | -83 | 0 | 0 | 1561 | 324.7321 | 324.7321 | 324.7321 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -94.9657 | 229.7664 | -2750 | -200 | -2720.2336 | 68.01% | 56.76% | 95% | 0% | 1561 | -83
[5 empty] | 2019-07-28 | 3 | 4992.5 | 1435 | -85 | 0 | 0 | 1520 | 260.5111 | 260.5111 | 260.5111 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -97.254 | 163.2571 | -2750 | -200 | -2786.7429 | 69.67% | 56.75% | 95% | 0% | 1520 | -85
[5 empty] | 2019-07-28 | 4 | 4993 | 1409 | -86 | 1 | 0 | 1495 | 221.352 | 221.352 | 221.352 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -98.3982 | 122.9539 | -3550 | -400 | -3827.0461 | 95.68% | 56.75% | 95% | 0% | 1495 | -86
[5 empty] | 2019-07-28 | 5 | 4993.5 | 1373 | -88 | 1 | 0 | 1461 | 168.0956 | 168.0956 | 168.0956 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -100.6865 | 67.4091 | -3550 | -400 | -3882.5909 | 97.06% | 56.74% | 95% | 0% | 1461 | -88
[5 empty] | 2019-07-28 | 6 | 4994 | 1343 | -89 | 1 | 0 | 1432 | 122.6711 | 122.6711 | 122.6711 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -101.8307 | 20.8404 | -3550 | -400 | -3929.1596 | 98.23% | 56.73% | 95% | 0% | 1432 | -89
[5 empty] | 2019-07-28 | 7 | 4994.5 | 1321 | -90 | 1 | 0 | 1411 | 89.7774 | 89.7774 | 89.7774 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -102.9748 | -13.1974 | -3550 | -400 | -3963.1974 | 99.08% | 56.73% | 95% | 0% | 1411 | -90
[5 empty] | 2019-07-28 | 8 | 4995 | 1310 | -90 | 1 | 0 | 1400 | 72.5474 | 72.5474 | 72.5474 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -102.9748 | -30.4274 | -3550 | -400 | -3980.4274 | 99.51% | 56.72% | 95% | 0% | 1400 | -90
[5 empty] | 2019-07-28 | 9 | 4995.5 | 1300 | -90 | 1 | 0 | 1390 | 56.8838 | 56.8838 | 56.8838 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -102.9748 | -46.0911 | -3550 | -400 | -3996.0911 | 99.9% | 56.71% | 95% | 0% | 1390 | -90
[5 empty] | 2019-07-28 | 10 | 4996 | 1291 | -89 | 1 | 0 | 1380 | 41.2201 | 41.2201 | 41.2201 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -101.8307 | -60.6105 | -3550 | -400 | -4010.6105 | 100.3% | 56.7% | 95% | 0% | 1380 | -89
[5 empty] | 2019-07-28 | 11 | 4996.5 | 1282 | -89 | 1 | 0 | 1371 | 27.1228 | 27.1228 | 27.1228 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -101.8307 | -74.7078 | -3550 | -400 | -4024.7078 | 100.6% | 56.69% | 95% | 0% | 1371 | -89
[5 empty] | 2019-07-28 | 12 | 4997 | 1277 | -90 | 1 | 0 | 1367 | 20.8574 | 20.8574 | 20.8574 | 1215.9934 | 780 | 200 | 2195.9934 | 54.9% | 95% | 0% | -102.9748 | -82.1174 | -3550 | -400 | -4032.1174 | 100.8% | 56.69% | 95% | 0% | 1367 | -90
[5 empty] | 2019-07-28 | 13 | 4997.5 | 1316 | -98 | 1 | 0 | 1414 | 94.4765 | 94.4765 | 94.4765 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -112.1281 | -17.6516 | -3550 | -400 | -3967.6516 | 99.19% | 56.69% | 95% | 0% | 1414 | -98
[5 empty] | 2019-07-28 | 14 | 4998 | 1341 | -113 | 1 | 0 | 1454 | 157.1311 | 157.1311 | 157.1311 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -129.2906 | 27.8405 | -3550 | -400 | -3922.1595 | 98.05% | 56.69% | 95% | 0% | 1454 | -113
[5 empty] | 2019-07-28 | 15 | 4998.5 | 1385 | -133 | 1 | 0 | 1518 | 257.3784 | 257.3784 | 257.3784 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -152.1739 | 105.2045 | -3550 | -400 | -3844.7955 | 96.12% | 56.68% | 95% | 0% | 1518 | -133
[5 empty] | 2019-07-28 | 16 | 4999 | 1407 | -163 | 1 | 0 | 1570 | 338.8293 | 338.8293 | 338.8293 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -186.4989 | 152.3305 | -3550 | -400 | -3797.6695 | 94.94% | 56.68% | 95% | 0% | 1570 | -163
[5 empty] | 2019-07-28 | 17 | 4999.5 | 1443 | -201 | 1 | 0 | 1644 | 454.7403 | 454.7403 | 454.7403 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -229.9771 | 224.7632 | -3550 | -400 | -3725.2368 | 93.13% | 56.68% | 95% | 0% | 1644 | -201
[5 empty] | 2019-07-28 | 18 | 5000 | 1457 | -234 | 1 | 0 | 1691 | 528.3594 | 528.3594 | 528.3594 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -267.7346 | 260.6249 | -3550 | -400 | -3689.3751 | 92.23% | 56.68% | 95% | 0% | 1691 | -234
[5 empty] | 2019-07-28 | 19 | 5000.5 | 1505 | -265 | 1 | 0 | 1770 | 652.1022 | 652.1022 | 652.1022 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -303.2037 | 348.8986 | -3550 | -400 | -3601.1014 | 90.03% | 56.68% | 95% | 0% | 1770 | -265
[5 empty] | 2019-07-28 | 20 | 5001 | 1516 | -299 | 1 | 0 | 1815 | 722.5886 | 722.5886 | 722.5886 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -342.1053 | 380.4834 | -3550 | -400 | -3569.5166 | 89.24% | 56.67% | 95% | 0% | 1815 | -299
[5 empty] | 2019-07-28 | 21 | 5001.5 | 1535 | -335 | 1 | 0 | 1870 | 808.7387 | 808.7387 | 808.7387 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -383.2952 | 425.4435 | -3550 | -400 | -3524.5565 | 88.11% | 56.67% | 95% | 0% | 1870 | -335
[5 empty] | 2019-07-28 | 22 | 5002 | 1555 | -350 | 1 | 0 | 1905 | 863.5614 | 863.5614 | 863.5614 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -400.4577 | 463.1038 | -3550 | -400 | -3486.8962 | 87.17% | 56.67% | 95% | 0% | 1905 | -350
[5 empty] | 2019-07-28 | 23 | 5002.5 | 1562 | -364 | 1 | 0 | 1926 | 896.4551 | 896.4551 | 896.4551 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -416.476 | 479.9791 | -3550 | -400 | -3470.0209 | 86.75% | 56.66% | 95% | 0% | 1926 | -364
[5 empty] | 2019-07-28 | 24 | 5003 | 1560 | -372 | 1 | 0 | 1932 | 905.8533 | 905.8533 | 905.8533 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -425.6293 | 480.224 | -3550 | -400 | -3469.776 | 86.74% | 56.66% | 95% | 0% | 1932 | -372
[5 empty] | 2019-07-28 | 25 | 5003.5 | 1566 | -385 | 1 | 0 | 1951 | 935.6142 | 935.6142 | 935.6142 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -440.5034 | 495.1107 | -3550 | -400 | -3454.8893 | 86.37% | 56.66% | 95% | 0% | 1951 | -385
[5 empty] | 2019-07-28 | 26 | 5004 | 1529 | -401 | 1 | 0 | 1930 | 902.7205 | 902.7205 | 902.7205 | 1214.427 | 780 | 200 | 2194.427 | 54.86% | 95% | 0% | -458.8101 | 443.9105 | -3550 | -400 | -3506.0895 | 87.65% | 56.66% | 95% | 0% | 1930 | -401
[5 empty] | 2019-07-28 | 27 | 5004.5 | 1502 | -404 | 1 | 0 | 1906 | 865.1278 | 865.1278 | 865.1278 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -462.2426 | 402.8852 | -3550 | -400 | -3547.1148 | 88.68% | 56.65% | 95% | 0% | 1906 | -404
[5 empty] | 2019-07-28 | 28 | 5005 | 1496 | -403 | 1 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -461.0984 | 393.0648 | -3550 | -400 | -3556.9352 | 88.92% | 56.65% | 95% | 0% | 1899 | -403
[5 empty] | 2019-07-28 | 29 | 5005.5 | 1487 | -398 | 1 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -455.3776 | 376.8566 | -3550 | -400 | -3573.1434 | 89.33% | 56.65% | 95% | 0% | 1885 | -398
[5 empty] | 2019-07-28 | 30 | 5006 | 1487 | -386 | 1 | 0 | 1873 | 813.4378 | 813.4378 | 813.4378 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -441.6476 | 371.7902 | -3550 | -400 | -3578.2098 | 89.46% | 56.64% | 95% | 0% | 1873 | -386
[5 empty] | 2019-07-28 | 31 | 5006.5 | 1510 | -367 | 1 | 0 | 1877 | 819.7032 | 819.7032 | 819.7032 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -419.9085 | 399.7947 | -3550 | -400 | -3550.2053 | 88.76% | 56.64% | 95% | 0% | 1877 | -367
[5 empty] | 2019-07-28 | 32 | 5007 | 1544 | -349 | 1 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -399.3135 | 445.4515 | -3550 | -400 | -3504.5485 | 87.61% | 56.64% | 95% | 0% | 1893 | -349
[5 empty] | 2019-07-28 | 33 | 5007.5 | 1606 | -330 | 1 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -377.5744 | 534.5443 | -3550 | -400 | -3415.4557 | 85.39% | 56.63% | 95% | 0% | 1936 | -330
[5 empty] | 2019-07-28 | 34 | 5008 | 1677 | -311 | 1 | 0 | 1988 | 993.5697 | 993.5697 | 993.5697 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -355.8352 | 637.7344 | -3550 | -400 | -3312.2656 | 82.81% | 56.62% | 95% | 0% | 1988 | -311
[5 empty] | 2019-07-28 | 35 | 5008.5 | 1744 | -293 | 1 | 0 | 2037 | 1070.3215 | 1070.3215 | 1070.3215 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -335.2403 | 735.0812 | -3550 | -400 | -3214.9188 | 80.37% | 56.62% | 95% | 0% | 2037 | -293
[5 empty] | 2019-07-28 | 36 | 5009 | 1808 | -262 | 1 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -299.7712 | 822.2404 | -3550 | -400 | -3127.7596 | 78.19% | 56.62% | 95% | 0% | 2070 | -262
[5 empty] | 2019-07-28 | 37 | 5009.5 | 1862 | -219 | 1 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -250.5721 | 888.6695 | -3550 | -400 | -3061.3305 | 76.53% | 56.61% | 95% | 0% | 2081 | -219
[5 empty] | 2019-07-28 | 38 | 5010 | 1923 | -182 | 1 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -208.238 | 968.5963 | -3550 | -400 | -2981.4037 | 74.54% | 56.61% | 95% | 0% | 2105 | -182
[5 empty] | 2019-07-28 | 39 | 5010.5 | 1976 | -143 | 1 | 0 | 2119 | 1198.7634 | 1198.7634 | 1198.7634 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -163.6156 | 1035.1478 | -3550 | -400 | -2914.8522 | 72.87% | 56.61% | 95% | 0% | 2119 | -143
[5 empty] | 2019-07-28 | 40 | 5011 | 2007 | -107 | 1 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -122.4256 | 1068.5059 | -3550 | -400 | -2881.4941 | 72.04% | 56.61% | 95% | 0% | 2114 | -107
[5 empty] | 2019-07-28 | 41 | 5011.5 | 2044 | -84 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -96.1098 | 1116.7508 | -3550 | -400 | -2833.2492 | 70.83% | 56.6% | 95% | 0% | 2128 | -84
[5 empty] | 2019-07-28 | 42 | 5012 | 2054 | -69 | 1 | 0 | 2123 | 1205.0289 | 1205.0289 | 1205.0289 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -78.9474 | 1126.0815 | -3550 | -400 | -2823.9185 | 70.6% | 56.6% | 95% | 0% | 2123 | -69
[5 empty] | 2019-07-28 | 43 | 5012.5 | 2062 | -65 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 1212.8607 | 780 | 200 | 2192.8607 | 54.82% | 95% | 0% | -74.3707 | 1136.9236 | -3550 | -400 | -2813.0764 | 70.33% | 56.6% | 95% | 0% | 2127 | -65
[5 empty] | 2019-07-28 | 44 | 5013 | 2015 | -62 | 1 | 0 | 2077 | 1132.9761 | 1132.9761 | 1132.9761 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -70.9382 | 1062.0379 | -3550 | -400 | -2887.9621 | 72.2% | 56.59% | 95% | 0% | 2077 | -62
[5 empty] | 2019-07-28 | 45 | 5013.5 | 1962 | -60 | 0 | 0 | 2022 | 1046.8261 | 1046.8261 | 1046.8261 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -68.6499 | 978.1762 | -2750 | -200 | -1971.8238 | 49.3% | 56.59% | 95% | 0% | 2022 | -60
[5 empty] | 2019-07-28 | 46 | 5014 | 1868 | -58 | 0 | 0 | 1926 | 896.4551 | 896.4551 | 896.4551 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -66.3616 | 830.0935 | -2750 | -200 | -2119.9065 | 53% | 56.59% | 95% | 0% | 1926 | -58
[5 empty] | 2019-07-28 | 47 | 5014.5 | 1750 | -58 | 0 | 0 | 1808 | 711.6241 | 711.6241 | 711.6241 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -66.3616 | 645.2625 | -2750 | -200 | -2304.7375 | 57.62% | 56.59% | 95% | 0% | 1808 | -58
[5 empty] | 2019-07-28 | 48 | 5015 | 1653 | -57 | 0 | 0 | 1710 | 558.1204 | 558.1204 | 558.1204 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -65.2174 | 492.903 | -2750 | -200 | -2457.097 | 61.43% | 56.59% | 95% | 0% | 1710 | -57
[5 empty] | 2019-07-29 | 1 | 5015.5 | 1579 | -52 | 0 | 0 | 1631 | 434.3776 | 434.3776 | 434.3776 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -59.4966 | 374.881 | -2750 | -200 | -2575.119 | 64.38% | 56.59% | 95% | 0% | 1631 | -52
[5 empty] | 2019-07-29 | 2 | 5016 | 1530 | -47 | 0 | 0 | 1577 | 349.7939 | 349.7939 | 349.7939 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -53.7757 | 296.0182 | -2750 | -200 | -2653.9818 | 66.35% | 56.58% | 95% | 0% | 1577 | -47
[5 empty] | 2019-07-29 | 3 | 5016.5 | 1492 | -46 | 0 | 0 | 1538 | 288.7057 | 288.7057 | 288.7057 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -52.6316 | 236.0741 | -2750 | -200 | -2713.9259 | 67.85% | 56.57% | 95% | 0% | 1538 | -46
[5 empty] | 2019-07-29 | 4 | 5017 | 1479 | -45 | 0 | 0 | 1524 | 266.7766 | 266.7766 | 266.7766 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -51.4874 | 215.2892 | -2750 | -200 | -2734.7108 | 68.37% | 56.56% | 95% | 0% | 1524 | -45
[5 empty] | 2019-07-29 | 5 | 5017.5 | 1455 | -44 | 0 | 0 | 1499 | 227.6175 | 227.6175 | 227.6175 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -50.3432 | 177.2742 | -2750 | -200 | -2772.7258 | 69.32% | 56.54% | 95% | 0% | 1499 | -44
[5 empty] | 2019-07-29 | 6 | 5018 | 1429 | -43 | 0 | 0 | 1472 | 185.3256 | 185.3256 | 185.3256 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -49.1991 | 136.1266 | -2750 | -200 | -2813.8734 | 70.35% | 56.54% | 95% | 0% | 1472 | -43
[5 empty] | 2019-07-29 | 7 | 5018.5 | 1421 | -42 | 0 | 0 | 1463 | 171.2284 | 171.2284 | 171.2284 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -48.0549 | 123.1734 | -2750 | -200 | -2826.8266 | 70.67% | 56.54% | 95% | 0% | 1463 | -42
[5 empty] | 2019-07-29 | 8 | 5019 | 1416 | -42 | 0 | 0 | 1458 | 163.3965 | 163.3965 | 163.3965 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -48.0549 | 115.3416 | -2750 | -200 | -2834.6584 | 70.87% | 56.54% | 95% | 0% | 1458 | -42
[5 empty] | 2019-07-29 | 9 | 5019.5 | 1431 | -40 | 0 | 0 | 1471 | 183.7593 | 183.7593 | 183.7593 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -45.7666 | 137.9927 | -2750 | -200 | -2812.0073 | 70.3% | 56.54% | 95% | 0% | 1471 | -40
[5 empty] | 2019-07-29 | 10 | 5020 | 1440 | -38 | 0 | 0 | 1478 | 194.7238 | 194.7238 | 194.7238 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -43.4783 | 151.2456 | -2750 | -200 | -2798.7544 | 69.97% | 56.53% | 95% | 0% | 1478 | -38
[5 empty] | 2019-07-29 | 11 | 5020.5 | 1478 | -38 | 0 | 0 | 1516 | 254.2457 | 254.2457 | 254.2457 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -43.4783 | 210.7674 | -2750 | -200 | -2739.2326 | 68.48% | 56.53% | 95% | 0% | 1516 | -38
[5 empty] | 2019-07-29 | 12 | 5021 | 1524 | -41 | 1 | 0 | 1565 | 330.9975 | 330.9975 | 330.9975 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -46.9108 | 284.0868 | -3550 | -400 | -3665.9132 | 91.65% | 56.53% | 95% | 0% | 1565 | -41
[5 empty] | 2019-07-29 | 13 | 5021.5 | 1672 | -56 | 1 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -64.0732 | 522.2417 | -3550 | -400 | -3427.7583 | 85.69% | 56.53% | 95% | 0% | 1728 | -56
[5 empty] | 2019-07-29 | 14 | 5022 | 1775 | -83 | 1 | 0 | 1858 | 789.9423 | 789.9423 | 789.9423 | 1211.2943 | 780 | 200 | 2191.2943 | 54.78% | 95% | 0% | -94.9657 | 694.9766 | -3550 | -400 | -3255.0234 | 81.38% | 56.52% | 95% | 0% | 1858 | -83
[5 empty] | 2019-07-29 | 15 | 5022.5 | 1877 | -131 | 1 | 0 | 2008 | 1024.8969 | 1024.8969 | 1024.8969 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -149.8856 | 875.0114 | -3550 | -400 | -3074.9886 | 76.87% | 56.52% | 95% | 0% | 2008 | -131
[5 empty] | 2019-07-29 | 16 | 5023 | 1926 | -189 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -216.2471 | 976.2508 | -3550 | -400 | -2973.7492 | 74.34% | 56.51% | 95% | 0% | 2115 | -189
[5 empty] | 2019-07-29 | 17 | 5023.5 | 1951 | -247 | 1 | 0 | 2198 | 1322.5062 | 1322.5062 | 1322.5062 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -282.6087 | 1039.8975 | -3550 | -400 | -2910.1025 | 72.75% | 56.51% | 95% | 0% | 2198 | -247
[5 empty] | 2019-07-29 | 18 | 5024 | 1907 | -311 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -355.8352 | 997.9982 | -3550 | -400 | -2952.0018 | 73.8% | 56.5% | 95% | 0% | 2218 | -311
[5 empty] | 2019-07-29 | 19 | 5024.5 | 1839 | -374 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -427.9176 | 918.084 | -3550 | -400 | -3031.916 | 75.8% | 56.5% | 95% | 0% | 2213 | -374
[5 empty] | 2019-07-29 | 20 | 5025 | 1743 | -438 | 1 | 0 | 2181 | 1295.878 | 1295.878 | 1295.878 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -501.1442 | 794.7338 | -3550 | -400 | -3155.2662 | 78.88% | 56.5% | 95% | 0% | 2181 | -438
[5 empty] | 2019-07-29 | 21 | 5025.5 | 1648 | -494 | 1 | 0 | 2142 | 1234.7898 | 1234.7898 | 1234.7898 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -565.2174 | 669.5724 | -3550 | -400 | -3280.4276 | 82.01% | 56.5% | 95% | 0% | 2142 | -494
[5 empty] | 2019-07-29 | 22 | 5026 | 1573 | -541 | 1 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -618.9931 | 571.9384 | -3550 | -400 | -3378.0616 | 84.45% | 56.49% | 95% | 0% | 2114 | -541
[5 empty] | 2019-07-29 | 23 | 5026.5 | 1557 | -564 | 1 | 0 | 2121 | 1201.8961 | 1201.8961 | 1201.8961 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -645.3089 | 556.5872 | -3550 | -400 | -3393.4128 | 84.84% | 56.49% | 95% | 0% | 2121 | -564
[5 empty] | 2019-07-29 | 24 | 5027 | 1525 | -589 | 1 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -673.913 | 517.0185 | -3550 | -400 | -3432.9815 | 85.82% | 56.49% | 95% | 0% | 2114 | -589
[5 empty] | 2019-07-29 | 25 | 5027.5 | 1512 | -612 | 1 | 0 | 2124 | 1206.5952 | 1206.5952 | 1206.5952 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -700.2288 | 506.3664 | -3550 | -400 | -3443.6336 | 86.09% | 56.49% | 95% | 0% | 2124 | -612
[5 empty] | 2019-07-29 | 26 | 5028 | 1494 | -610 | 1 | 0 | 2104 | 1175.2679 | 1175.2679 | 1175.2679 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -697.9405 | 477.3274 | -3550 | -400 | -3472.6726 | 86.82% | 56.48% | 95% | 0% | 2104 | -610
[5 empty] | 2019-07-29 | 27 | 5028.5 | 1507 | -594 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 1209.7279 | 780 | 200 | 2189.7279 | 54.74% | 95% | 0% | -679.6339 | 490.935 | -3550 | -400 | -3459.065 | 86.48% | 56.48% | 95% | 0% | 2101 | -594
[5 empty] | 2019-07-29 | 28 | 5029 | 1510 | -569 | 1 | 0 | 2079 | 1136.1088 | 1136.1088 | 1136.1088 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -651.0297 | 485.0791 | -3550 | -400 | -3464.9209 | 86.62% | 56.47% | 95% | 0% | 2079 | -569
[5 empty] | 2019-07-29 | 29 | 5029.5 | 1515 | -568 | 1 | 0 | 2083 | 1142.3743 | 1142.3743 | 1142.3743 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -649.8856 | 492.4887 | -3550 | -400 | -3457.5113 | 86.44% | 56.47% | 95% | 0% | 2083 | -568
[5 empty] | 2019-07-29 | 30 | 5030 | 1526 | -556 | 1 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -636.1556 | 504.6523 | -3550 | -400 | -3445.3477 | 86.13% | 56.46% | 95% | 0% | 2082 | -556
[5 empty] | 2019-07-29 | 31 | 5030.5 | 1579 | -534 | 1 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -610.984 | 578.3812 | -3550 | -400 | -3371.6188 | 84.29% | 56.46% | 95% | 0% | 2113 | -534
[5 empty] | 2019-07-29 | 32 | 5031 | 1646 | -492 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -562.9291 | 665.5953 | -3550 | -400 | -3284.4047 | 82.11% | 56.46% | 95% | 0% | 2138 | -492
[5 empty] | 2019-07-29 | 33 | 5031.5 | 1709 | -453 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -518.3066 | 747.8104 | -3550 | -400 | -3202.1896 | 80.05% | 56.46% | 95% | 0% | 2162 | -453
[5 empty] | 2019-07-29 | 34 | 5032 | 1856 | -381 | 1 | 0 | 2237 | 1383.5944 | 1383.5944 | 1383.5944 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -435.9268 | 947.6676 | -3550 | -400 | -3002.3324 | 75.06% | 56.46% | 95% | 0% | 2237 | -381
[5 empty] | 2019-07-29 | 35 | 5032.5 | 1991 | -314 | 1 | 0 | 2305 | 1490.1072 | 1490.1072 | 1490.1072 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -359.2677 | 1130.8394 | -3550 | -400 | -2819.1606 | 70.48% | 56.45% | 95% | 0% | 2305 | -314
[5 empty] | 2019-07-29 | 36 | 5033 | 2093 | -258 | 1 | 0 | 2351 | 1562.1599 | 1562.1599 | 1562.1599 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -295.1945 | 1266.9654 | -3550 | -400 | -2683.0346 | 67.08% | 56.44% | 95% | 0% | 2351 | -258
[5 empty] | 2019-07-29 | 37 | 5033.5 | 2170 | -207 | 1 | 0 | 2377 | 1602.8854 | 1602.8854 | 1602.8854 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -236.8421 | 1366.0433 | -3550 | -400 | -2583.9567 | 64.6% | 56.44% | 95% | 0% | 2377 | -207
[5 empty] | 2019-07-29 | 38 | 5034 | 2250 | -163 | 1 | 0 | 2413 | 1659.2745 | 1659.2745 | 1659.2745 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -186.4989 | 1472.7757 | -3550 | -400 | -2477.2243 | 61.93% | 56.44% | 95% | 0% | 2413 | -163
[5 empty] | 2019-07-29 | 39 | 5034.5 | 2281 | -124 | 1 | 0 | 2405 | 1646.7436 | 1646.7436 | 1646.7436 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -141.8764 | 1504.8672 | -3550 | -400 | -2445.1328 | 61.13% | 56.44% | 95% | 0% | 2405 | -124
[5 empty] | 2019-07-29 | 40 | 5035 | 2305 | -94 | 1 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -107.5515 | 1529.7939 | -3550 | -400 | -2420.2061 | 60.51% | 56.43% | 95% | 0% | 2399 | -94
[5 empty] | 2019-07-29 | 41 | 5035.5 | 2309 | -68 | 1 | 0 | 2377 | 1602.8854 | 1602.8854 | 1602.8854 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -77.8032 | 1525.0822 | -3550 | -400 | -2424.9178 | 60.62% | 56.43% | 95% | 0% | 2377 | -68
[5 empty] | 2019-07-29 | 42 | 5036 | 2278 | -58 | 1 | 0 | 2336 | 1538.6645 | 1538.6645 | 1538.6645 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -66.3616 | 1472.3029 | -3550 | -400 | -2477.6971 | 61.94% | 56.43% | 95% | 0% | 2336 | -58
[5 empty] | 2019-07-29 | 43 | 5036.5 | 2274 | -60 | 1 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -68.6499 | 1466.8819 | -3550 | -400 | -2483.1181 | 62.08% | 56.42% | 95% | 0% | 2334 | -60
[5 empty] | 2019-07-29 | 44 | 5037 | 2215 | -63 | 1 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -72.0824 | 1375.733 | -3550 | -400 | -2574.267 | 64.36% | 56.42% | 95% | 0% | 2278 | -63
[5 empty] | 2019-07-29 | 45 | 5037.5 | 2117 | -65 | 0 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 1208.1616 | 780 | 200 | 2188.1616 | 54.7% | 95% | 0% | -74.3707 | 1223.0736 | -2750 | -200 | -1726.9264 | 43.17% | 56.42% | 95% | 0% | 2182 | -65
[5 empty] | 2019-07-29 | 46 | 5038 | 1973 | -66 | 0 | 0 | 2039 | 1073.4542 | 1073.4542 | 1073.4542 | 1206.5952 | 780 | 200 | 2186.5952 | 54.66% | 95% | 0% | -75.5149 | 997.9394 | -2750 | -200 | -1952.0606 | 48.8% | 56.42% | 95% | 0% | 2039 | -66
[5 empty] | 2019-07-29 | 47 | 5038.5 | 1824 | -68 | 0 | 0 | 1892 | 843.1987 | 843.1987 | 843.1987 | 1206.5952 | 780 | 200 | 2186.5952 | 54.66% | 95% | 0% | -77.8032 | 765.3955 | -2750 | -200 | -2184.6045 | 54.62% | 56.41% | 95% | 0% | 1892 | -68
[5 empty] | 2019-07-29 | 48 | 5039 | 1700 | -69 | 1 | 0 | 1769 | 650.5359 | 650.5359 | 650.5359 | 1206.5952 | 780 | 200 | 2186.5952 | 54.66% | 95% | 0% | -78.9474 | 571.5885 | -3550 | -400 | -3378.4115 | 84.46% | 56.41% | 95% | 0% | 1769 | -69
[5 empty] | 2019-07-30 | 1 | 5039.5 | 1605 | -69 | 1 | 0 | 1674 | 501.7312 | 501.7312 | 501.7312 | 1206.5952 | 780 | 200 | 2186.5952 | 54.66% | 95% | 0% | -78.9474 | 422.7839 | -3550 | -400 | -3527.2161 | 88.18% | 56.41% | 95% | 0% | 1674 | -69
[5 empty] | 2019-07-30 | 2 | 5040 | 1554 | -69 | 1 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 1206.5952 | 780 | 200 | 2186.5952 | 54.66% | 95% | 0% | -78.9474 | 342.8993 | -3550 | -400 | -3607.1007 | 90.18% | 56.41% | 95% | 0% | 1623 | -69
[5 empty] | 2019-07-30 | 3 | 5040.5 | 1514 | -68 | 1 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 1206.5952 | 780 | 200 | 2186.5952 | 54.66% | 95% | 0% | -77.8032 | 279.8225 | -3550 | -400 | -3670.1775 | 91.75% | 56.41% | 95% | 0% | 1582 | -68
[5 empty] | 2019-07-30 | 4 | 5041 | 1485 | -67 | 1 | 0 | 1552 | 310.6348 | 310.6348 | 310.6348 | 1206.5952 | 780 | 200 | 2186.5952 | 54.66% | 95% | 0% | -76.659 | 233.9758 | -3550 | -400 | -3716.0242 | 92.9% | 56.41% | 95% | 0% | 1552 | -67
[5 empty] | 2019-07-30 | 5 | 5041.5 | 1458 | -67 | 1 | 0 | 1525 | 268.343 | 268.343 | 268.343 | 1206.5952 | 780 | 200 | 2186.5952 | 54.66% | 95% | 0% | -76.659 | 191.6839 | -3550 | -400 | -3758.3161 | 93.96% | 56.4% | 95% | 0% | 1525 | -67
[5 empty] | 2019-07-30 | 6 | 5042 | 1435 | -67 | 1 | 0 | 1502 | 232.3166 | 232.3166 | 232.3166 | 1206.5952 | 780 | 200 | 2186.5952 | 54.66% | 95% | 0% | -76.659 | 155.6575 | -3550 | -400 | -3794.3425 | 94.86% | 56.4% | 95% | 0% | 1502 | -67
[5 empty] | 2019-07-30 | 7 | 5042.5 | 1422 | -66 | 1 | 0 | 1488 | 210.3875 | 210.3875 | 210.3875 | 1206.5952 | 780 | 200 | 2186.5952 | 54.66% | 95% | 0% | -75.5149 | 134.8726 | -3550 | -400 | -3815.1274 | 95.38% | 56.4% | 95% | 0% | 1488 | -66
[5 empty] | 2019-07-30 | 8 | 5043 | 1429 | -64 | 1 | 0 | 1493 | 218.2193 | 218.2193 | 218.2193 | 1206.5952 | 780 | 200 | 2186.5952 | 54.66% | 95% | 0% | -73.2265 | 144.9927 | -3550 | -400 | -3805.0073 | 95.13% | 56.4% | 95% | 0% | 1493 | -64
[5 empty] | 2019-07-30 | 9 | 5043.5 | 1431 | -63 | 1 | 0 | 1494 | 219.7857 | 219.7857 | 219.7857 | 1206.5952 | 780 | 200 | 2186.5952 | 54.66% | 95% | 0% | -72.0824 | 147.7033 | -3550 | -400 | -3802.2967 | 95.06% | 56.4% | 95% | 0% | 1494 | -63
[5 empty] | 2019-07-30 | 10 | 5044 | 1450 | -62 | 1 | 0 | 1512 | 247.9802 | 247.9802 | 247.9802 | 1205.0289 | 780 | 200 | 2185.0289 | 54.63% | 95% | 0% | -70.9382 | 177.042 | -3550 | -400 | -3772.958 | 94.32% | 56.4% | 95% | 0% | 1512 | -62
[5 empty] | 2019-07-30 | 11 | 5044.5 | 1464 | -63 | 1 | 0 | 1527 | 271.4757 | 271.4757 | 271.4757 | 1205.0289 | 780 | 200 | 2185.0289 | 54.63% | 95% | 0% | -72.0824 | 199.3933 | -3550 | -400 | -3750.6067 | 93.77% | 56.39% | 95% | 0% | 1527 | -63
[5 empty] | 2019-07-30 | 12 | 5045 | 1519 | -67 | 1 | 0 | 1586 | 363.8912 | 363.8912 | 363.8912 | 1205.0289 | 780 | 200 | 2185.0289 | 54.63% | 95% | 0% | -76.659 | 287.2321 | -3550 | -400 | -3662.7679 | 91.57% | 56.39% | 95% | 0% | 1586 | -67
[5 empty] | 2019-07-30 | 13 | 5045.5 | 1665 | -86 | 1 | 0 | 1751 | 622.3413 | 622.3413 | 622.3413 | 1205.0289 | 780 | 200 | 2185.0289 | 54.63% | 95% | 0% | -98.3982 | 523.9431 | -3550 | -400 | -3426.0569 | 85.65% | 56.39% | 95% | 0% | 1751 | -86
[5 empty] | 2019-07-30 | 14 | 5046 | 1768 | -117 | 1 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 1205.0289 | 780 | 200 | 2185.0289 | 54.63% | 95% | 0% | -133.8673 | 698.3669 | -3550 | -400 | -3251.6331 | 81.29% | 56.39% | 95% | 0% | 1885 | -117
[5 empty] | 2019-07-30 | 15 | 5046.5 | 1885 | -156 | 1 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 1205.0289 | 780 | 200 | 2185.0289 | 54.63% | 95% | 0% | -178.4897 | 898.0973 | -3550 | -400 | -3051.9027 | 76.3% | 56.39% | 95% | 0% | 2041 | -156
[5 empty] | 2019-07-30 | 16 | 5047 | 1951 | -194 | 1 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 1205.0289 | 780 | 200 | 2185.0289 | 54.63% | 95% | 0% | -221.968 | 1017.5209 | -3550 | -400 | -2932.4791 | 73.31% | 56.38% | 95% | 0% | 2145 | -194
[5 empty] | 2019-07-30 | 17 | 5047.5 | 1993 | -239 | 1 | 0 | 2232 | 1375.7626 | 1375.7626 | 1375.7626 | 1205.0289 | 780 | 200 | 2185.0289 | 54.63% | 95% | 0% | -273.4554 | 1102.3072 | -3550 | -400 | -2847.6928 | 71.19% | 56.38% | 95% | 0% | 2232 | -239
[5 empty] | 2019-07-30 | 18 | 5048 | 1988 | -284 | 1 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 1205.0289 | 780 | 200 | 2185.0289 | 54.63% | 95% | 0% | -324.9428 | 1113.4744 | -3550 | -400 | -2836.5256 | 70.91% | 56.37% | 95% | 0% | 2272 | -284
[5 empty] | 2019-07-30 | 19 | 5048.5 | 1964 | -332 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1205.0289 | 780 | 200 | 2185.0289 | 54.63% | 95% | 0% | -379.8627 | 1096.1472 | -3550 | -400 | -2853.8528 | 71.35% | 56.36% | 95% | 0% | 2296 | -332
[5 empty] | 2019-07-30 | 20 | 5049 | 1935 | -362 | 1 | 0 | 2297 | 1477.5763 | 1477.5763 | 1477.5763 | 1203.4625 | 780 | 200 | 2183.4625 | 54.59% | 95% | 0% | -414.1876 | 1063.3886 | -3550 | -400 | -2886.6114 | 72.17% | 56.35% | 95% | 0% | 2297 | -362
[5 empty] | 2019-07-30 | 21 | 5049.5 | 1917 | -371 | 1 | 0 | 2288 | 1463.479 | 1463.479 | 1463.479 | 1203.4625 | 780 | 200 | 2183.4625 | 54.59% | 95% | 0% | -424.4851 | 1038.9939 | -3550 | -400 | -2911.0061 | 72.78% | 56.35% | 95% | 0% | 2288 | -371
[5 empty] | 2019-07-30 | 22 | 5050 | 1911 | -352 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 1203.4625 | 780 | 200 | 2183.4625 | 54.59% | 95% | 0% | -402.746 | 1021.5739 | -3550 | -400 | -2928.4261 | 73.21% | 56.34% | 95% | 0% | 2263 | -352
[5 empty] | 2019-07-30 | 23 | 5050.5 | 1891 | -386 | 1 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 1203.4625 | 780 | 200 | 2183.4625 | 54.59% | 95% | 0% | -441.6476 | 1004.6014 | -3550 | -400 | -2945.3986 | 73.63% | 56.34% | 95% | 0% | 2277 | -386
[5 empty] | 2019-07-30 | 24 | 5051 | 1906 | -388 | 1 | 0 | 2294 | 1472.8772 | 1472.8772 | 1472.8772 | 1203.4625 | 780 | 200 | 2183.4625 | 54.59% | 95% | 0% | -443.9359 | 1028.9412 | -3550 | -400 | -2921.0588 | 73.03% | 56.34% | 95% | 0% | 2294 | -388
[5 empty] | 2019-07-30 | 25 | 5051.5 | 1948 | -379 | 1 | 0 | 2327 | 1524.5672 | 1524.5672 | 1524.5672 | 1203.4625 | 780 | 200 | 2183.4625 | 54.59% | 95% | 0% | -433.6384 | 1090.9287 | -3550 | -400 | -2859.0713 | 71.48% | 56.34% | 95% | 0% | 2327 | -379
[5 empty] | 2019-07-30 | 26 | 5052 | 1925 | -384 | 1 | 0 | 2309 | 1496.3726 | 1496.3726 | 1496.3726 | 1203.4625 | 780 | 200 | 2183.4625 | 54.59% | 95% | 0% | -439.3593 | 1057.0134 | -3550 | -400 | -2892.9866 | 72.32% | 56.33% | 95% | 0% | 2309 | -384
[5 empty] | 2019-07-30 | 27 | 5052.5 | 1855 | -437 | 1 | 0 | 2292 | 1469.7444 | 1469.7444 | 1469.7444 | 1203.4625 | 780 | 200 | 2183.4625 | 54.59% | 95% | 0% | -500 | 969.7444 | -3550 | -400 | -2980.2556 | 74.51% | 56.33% | 95% | 0% | 2292 | -437
[5 empty] | 2019-07-30 | 28 | 5053 | 1895 | -385 | 1 | 0 | 2280 | 1450.9481 | 1450.9481 | 1450.9481 | 1203.4625 | 780 | 200 | 2183.4625 | 54.59% | 95% | 0% | -440.5034 | 1010.4446 | -3550 | -400 | -2939.5554 | 73.49% | 56.32% | 95% | 0% | 2280 | -385
[5 empty] | 2019-07-30 | 29 | 5053.5 | 1894 | -372 | 1 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 1203.4625 | 780 | 200 | 2183.4625 | 54.59% | 95% | 0% | -425.6293 | 1003.3897 | -3550 | -400 | -2946.6103 | 73.67% | 56.32% | 95% | 0% | 2266 | -372
[5 empty] | 2019-07-30 | 30 | 5054 | 1865 | -379 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1201.8961 | 780 | 200 | 2181.8961 | 54.55% | 95% | 0% | -433.6384 | 960.9205 | -3550 | -400 | -2989.0795 | 74.73% | 56.31% | 95% | 0% | 2244 | -379
[5 empty] | 2019-07-30 | 31 | 5054.5 | 1839 | -398 | 1 | 0 | 2237 | 1383.5944 | 1383.5944 | 1383.5944 | 1201.8961 | 780 | 200 | 2181.8961 | 54.55% | 95% | 0% | -455.3776 | 928.2168 | -3550 | -400 | -3021.7832 | 75.54% | 56.31% | 95% | 0% | 2237 | -398
[5 empty] | 2019-07-30 | 32 | 5055 | 1848 | -396 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1201.8961 | 780 | 200 | 2181.8961 | 54.55% | 95% | 0% | -453.0892 | 941.4697 | -3550 | -400 | -3008.5303 | 75.21% | 56.31% | 95% | 0% | 2244 | -396
[5 empty] | 2019-07-30 | 33 | 5055.5 | 1931 | -333 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 1201.8961 | 780 | 200 | 2181.8961 | 54.55% | 95% | 0% | -381.0069 | 1044.8794 | -3550 | -400 | -2905.1206 | 72.63% | 56.31% | 95% | 0% | 2264 | -333
[5 empty] | 2019-07-30 | 34 | 5056 | 2014 | -306 | 1 | 0 | 2320 | 1513.6026 | 1513.6026 | 1513.6026 | 1201.8961 | 780 | 200 | 2181.8961 | 54.55% | 95% | 0% | -350.1144 | 1163.4882 | -3550 | -400 | -2786.5118 | 69.66% | 56.31% | 95% | 0% | 2320 | -306
[5 empty] | 2019-07-30 | 35 | 5056.5 | 2101 | -264 | 1 | 0 | 2365 | 1584.089 | 1584.089 | 1584.089 | 1201.8961 | 780 | 200 | 2181.8961 | 54.55% | 95% | 0% | -302.0595 | 1282.0295 | -3550 | -400 | -2667.9705 | 66.7% | 56.3% | 95% | 0% | 2365 | -264
[5 empty] | 2019-07-30 | 36 | 5057 | 2173 | -227 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 1201.8961 | 780 | 200 | 2181.8961 | 54.55% | 95% | 0% | -259.7254 | 1379.1864 | -3550 | -400 | -2570.8136 | 64.27% | 56.29% | 95% | 0% | 2400 | -227
[5 empty] | 2019-07-30 | 37 | 5057.5 | 2171 | -220 | 1 | 0 | 2391 | 1624.8145 | 1624.8145 | 1624.8145 | 1201.8961 | 780 | 200 | 2181.8961 | 54.55% | 95% | 0% | -251.7162 | 1373.0983 | -3550 | -400 | -2576.9017 | 64.42% | 56.28% | 95% | 0% | 2391 | -220
[5 empty] | 2019-07-30 | 38 | 5058 | 2171 | -201 | 1 | 0 | 2372 | 1595.0536 | 1595.0536 | 1595.0536 | 1201.8961 | 780 | 200 | 2181.8961 | 54.55% | 95% | 0% | -229.9771 | 1365.0765 | -3550 | -400 | -2584.9235 | 64.62% | 56.27% | 95% | 0% | 2372 | -201
[5 empty] | 2019-07-30 | 39 | 5058.5 | 2175 | -163 | 1 | 0 | 2338 | 1541.7972 | 1541.7972 | 1541.7972 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -186.4989 | 1355.2983 | -3550 | -400 | -2594.7017 | 64.87% | 56.27% | 95% | 0% | 2338 | -163
[5 empty] | 2019-07-30 | 40 | 5059 | 2172 | -144 | 1 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -164.7597 | 1342.5775 | -3550 | -400 | -2607.4225 | 65.19% | 56.26% | 95% | 0% | 2316 | -144
[5 empty] | 2019-07-30 | 41 | 5059.5 | 2140 | -126 | 1 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -144.1648 | 1284.8542 | -3550 | -400 | -2665.1458 | 66.63% | 56.26% | 95% | 0% | 2266 | -126
[5 empty] | 2019-07-30 | 42 | 5060 | 2120 | -117 | 1 | 0 | 2237 | 1383.5944 | 1383.5944 | 1383.5944 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -133.8673 | 1249.7271 | -3550 | -400 | -2700.2729 | 67.51% | 56.24% | 95% | 0% | 2237 | -117
[5 empty] | 2019-07-30 | 43 | 5060.5 | 2107 | -115 | 1 | 0 | 2222 | 1360.0989 | 1360.0989 | 1360.0989 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -131.5789 | 1228.52 | -3550 | -400 | -2721.48 | 68.04% | 56.24% | 95% | 0% | 2222 | -115
[5 empty] | 2019-07-30 | 44 | 5061 | 2038 | -113 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -129.2906 | 1119.5964 | -3550 | -400 | -2830.4036 | 70.76% | 56.24% | 95% | 0% | 2151 | -113
[5 empty] | 2019-07-30 | 45 | 5061.5 | 1926 | -112 | 0 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -128.1465 | 943.7414 | -2750 | -200 | -2006.2586 | 50.16% | 56.24% | 95% | 0% | 2038 | -112
[5 empty] | 2019-07-30 | 46 | 5062 | 1816 | -111 | 0 | 0 | 1927 | 898.0214 | 898.0214 | 898.0214 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -127.0023 | 771.0191 | -2750 | -200 | -2178.9809 | 54.47% | 56.24% | 95% | 0% | 1927 | -111
[5 empty] | 2019-07-30 | 47 | 5062.5 | 1692 | -109 | 0 | 0 | 1801 | 700.6595 | 700.6595 | 700.6595 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -124.714 | 575.9456 | -2750 | -200 | -2374.0544 | 59.35% | 56.22% | 95% | 0% | 1801 | -109
[5 empty] | 2019-07-30 | 48 | 5063 | 1574 | -108 | 0 | 0 | 1682 | 514.2622 | 514.2622 | 514.2622 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -123.5698 | 390.6924 | -2750 | -200 | -2559.3076 | 63.98% | 56.22% | 95% | 0% | 1682 | -108
[5 empty] | 2019-07-31 | 1 | 5063.5 | 1496 | -106 | 0 | 0 | 1602 | 388.953 | 388.953 | 388.953 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -121.2815 | 267.6715 | -2750 | -200 | -2682.3285 | 67.06% | 56.22% | 95% | 0% | 1602 | -106
[5 empty] | 2019-07-31 | 2 | 5064 | 1447 | -105 | 1 | 0 | 1552 | 310.6348 | 310.6348 | 310.6348 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -120.1373 | 190.4975 | -3550 | -400 | -3759.5025 | 93.99% | 56.22% | 95% | 0% | 1552 | -105
[5 empty] | 2019-07-31 | 3 | 5064.5 | 1406 | -104 | 1 | 0 | 1510 | 244.8475 | 244.8475 | 244.8475 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -118.9931 | 125.8544 | -3550 | -400 | -3824.1456 | 95.6% | 56.22% | 95% | 0% | 1510 | -104
[5 empty] | 2019-07-31 | 4 | 5065 | 1387 | -103 | 1 | 0 | 1490 | 213.5202 | 213.5202 | 213.5202 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -117.849 | 95.6712 | -3550 | -400 | -3854.3288 | 96.36% | 56.22% | 95% | 0% | 1490 | -103
[5 empty] | 2019-07-31 | 5 | 5065.5 | 1360 | -104 | 1 | 0 | 1464 | 172.7947 | 172.7947 | 172.7947 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -118.9931 | 53.8016 | -3550 | -400 | -3896.1984 | 97.4% | 56.21% | 95% | 0% | 1464 | -104
[5 empty] | 2019-07-31 | 6 | 5066 | 1340 | -104 | 1 | 0 | 1444 | 141.4674 | 141.4674 | 141.4674 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -118.9931 | 22.4743 | -3550 | -400 | -3927.5257 | 98.19% | 56.2% | 95% | 0% | 1444 | -104
[5 empty] | 2019-07-31 | 7 | 5066.5 | 1330 | -103 | 1 | 0 | 1433 | 124.2374 | 124.2374 | 124.2374 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -117.849 | 6.3885 | -3550 | -400 | -3943.6115 | 98.59% | 56.19% | 95% | 0% | 1433 | -103
[5 empty] | 2019-07-31 | 8 | 5067 | 1331 | -102 | 1 | 0 | 1433 | 124.2374 | 124.2374 | 124.2374 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -116.7048 | 7.5326 | -3550 | -400 | -3942.4674 | 98.56% | 56.19% | 95% | 0% | 1433 | -102
[5 empty] | 2019-07-31 | 9 | 5067.5 | 1329 | -102 | 1 | 0 | 1431 | 121.1047 | 121.1047 | 121.1047 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -116.7048 | 4.3999 | -3550 | -400 | -3945.6001 | 98.64% | 56.19% | 95% | 0% | 1431 | -102
[5 empty] | 2019-07-31 | 10 | 5068 | 1342 | -102 | 1 | 0 | 1444 | 141.4674 | 141.4674 | 141.4674 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -116.7048 | 24.7626 | -3550 | -400 | -3925.2374 | 98.13% | 56.19% | 95% | 0% | 1444 | -102
[5 empty] | 2019-07-31 | 11 | 5068.5 | 1380 | -102 | 1 | 0 | 1482 | 200.9893 | 200.9893 | 200.9893 | 1200.3298 | 780 | 200 | 2180.3298 | 54.51% | 95% | 0% | -116.7048 | 84.2845 | -3550 | -400 | -3865.7155 | 96.64% | 56.19% | 95% | 0% | 1482 | -102
[5 empty] | 2019-07-31 | 12 | 5069 | 1426 | -103 | 1 | 0 | 1529 | 274.6084 | 274.6084 | 274.6084 | 1198.7634 | 780 | 200 | 2178.7634 | 54.47% | 95% | 0% | -117.849 | 156.7594 | -3550 | -400 | -3793.2406 | 94.83% | 56.19% | 95% | 0% | 1529 | -103
[5 empty] | 2019-07-31 | 13 | 5069.5 | 1557 | -111 | 1 | 0 | 1668 | 492.3331 | 492.3331 | 492.3331 | 1198.7634 | 780 | 200 | 2178.7634 | 54.47% | 95% | 0% | -127.0023 | 365.3308 | -3550 | -400 | -3584.6692 | 89.62% | 56.18% | 95% | 0% | 1668 | -111
[5 empty] | 2019-07-31 | 14 | 5070 | 1676 | -129 | 1 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 1198.7634 | 780 | 200 | 2178.7634 | 54.47% | 95% | 0% | -147.5973 | 559.3277 | -3550 | -400 | -3390.6723 | 84.77% | 56.18% | 95% | 0% | 1805 | -129
[5 empty] | 2019-07-31 | 15 | 5070.5 | 1835 | -155 | 1 | 0 | 1990 | 996.7024 | 996.7024 | 996.7024 | 1198.7634 | 780 | 200 | 2178.7634 | 54.47% | 95% | 0% | -177.3455 | 819.3569 | -3550 | -400 | -3130.6431 | 78.27% | 56.18% | 95% | 0% | 1990 | -155
[5 empty] | 2019-07-31 | 16 | 5071 | 1915 | -182 | 1 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 1198.7634 | 780 | 200 | 2178.7634 | 54.47% | 95% | 0% | -208.238 | 956.0654 | -3550 | -400 | -2993.9346 | 74.85% | 56.18% | 95% | 0% | 2097 | -182
[5 empty] | 2019-07-31 | 17 | 5071.5 | 1964 | -219 | 1 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 1198.7634 | 780 | 200 | 2178.7634 | 54.47% | 95% | 0% | -250.5721 | 1048.4386 | -3550 | -400 | -2901.5614 | 72.54% | 56.17% | 95% | 0% | 2183 | -219
[5 empty] | 2019-07-31 | 18 | 5072 | 1957 | -267 | 1 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 1198.7634 | 780 | 200 | 2178.7634 | 54.47% | 95% | 0% | -305.492 | 1057.7397 | -3550 | -400 | -2892.2603 | 72.31% | 56.17% | 95% | 0% | 2224 | -267
[5 empty] | 2019-07-31 | 19 | 5072.5 | 1949 | -293 | 1 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 1198.7634 | 780 | 200 | 2178.7634 | 54.47% | 95% | 0% | -335.2403 | 1056.1859 | -3550 | -400 | -2893.8141 | 72.35% | 56.16% | 95% | 0% | 2242 | -293
[5 empty] | 2019-07-31 | 20 | 5073 | 1895 | -346 | 1 | 0 | 2241 | 1389.8599 | 1389.8599 | 1389.8599 | 1198.7634 | 780 | 200 | 2178.7634 | 54.47% | 95% | 0% | -395.881 | 993.9788 | -3550 | -400 | -2956.0212 | 73.9% | 56.16% | 95% | 0% | 2241 | -346
[5 empty] | 2019-07-31 | 21 | 5073.5 | 1866 | -360 | 1 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 1198.7634 | 780 | 200 | 2178.7634 | 54.47% | 95% | 0% | -411.8993 | 954.4651 | -3550 | -400 | -2995.5349 | 74.89% | 56.15% | 95% | 0% | 2226 | -360
[5 empty] | 2019-07-31 | 22 | 5074 | 1835 | -383 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 1197.197 | 780 | 200 | 2177.197 | 54.43% | 95% | 0% | -438.2151 | 915.6184 | -3550 | -400 | -3034.3816 | 75.86% | 56.15% | 95% | 0% | 2218 | -383
[5 empty] | 2019-07-31 | 23 | 5074.5 | 1776 | -431 | 1 | 0 | 2207 | 1336.6035 | 1336.6035 | 1336.6035 | 1197.197 | 780 | 200 | 2177.197 | 54.43% | 95% | 0% | -493.135 | 843.4685 | -3550 | -400 | -3106.5315 | 77.66% | 56.14% | 95% | 0% | 2207 | -431
[5 empty] | 2019-07-31 | 24 | 5075 | 1758 | -452 | 1 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 1197.197 | 780 | 200 | 2177.197 | 54.43% | 95% | 0% | -517.1625 | 824.1401 | -3550 | -400 | -3125.8599 | 78.15% | 56.13% | 95% | 0% | 2210 | -452
[5 empty] | 2019-07-31 | 25 | 5075.5 | 1749 | -455 | 1 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 1197.197 | 780 | 200 | 2177.197 | 54.43% | 95% | 0% | -520.595 | 811.3094 | -3550 | -400 | -3138.6906 | 78.47% | 56.13% | 95% | 0% | 2204 | -455
[5 empty] | 2019-07-31 | 26 | 5076 | 1712 | -481 | 1 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 1197.197 | 780 | 200 | 2177.197 | 54.43% | 95% | 0% | -550.3432 | 764.3311 | -3550 | -400 | -3185.6689 | 79.64% | 56.13% | 95% | 0% | 2193 | -481
[5 empty] | 2019-07-31 | 27 | 5076.5 | 1703 | -477 | 1 | 0 | 2180 | 1294.3116 | 1294.3116 | 1294.3116 | 1197.197 | 780 | 200 | 2177.197 | 54.43% | 95% | 0% | -545.7666 | 748.545 | -3550 | -400 | -3201.455 | 80.04% | 56.13% | 95% | 0% | 2180 | -477
[5 empty] | 2019-07-31 | 28 | 5077 | 1686 | -465 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1197.197 | 780 | 200 | 2177.197 | 54.43% | 95% | 0% | -532.0366 | 716.8504 | -3550 | -400 | -3233.1496 | 80.83% | 56.13% | 95% | 0% | 2151 | -465
[5 empty] | 2019-07-31 | 29 | 5077.5 | 1671 | -461 | 1 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 1197.197 | 780 | 200 | 2177.197 | 54.43% | 95% | 0% | -527.46 | 691.6662 | -3550 | -400 | -3258.3338 | 81.46% | 56.12% | 95% | 0% | 2132 | -461
[5 empty] | 2019-07-31 | 30 | 5078 | 1665 | -459 | 1 | 0 | 2124 | 1206.5952 | 1206.5952 | 1206.5952 | 1195.6307 | 780 | 200 | 2175.6307 | 54.39% | 95% | 0% | -525.1716 | 681.4236 | -3550 | -400 | -3268.5764 | 81.71% | 56.12% | 95% | 0% | 2124 | -459
[5 empty] | 2019-07-31 | 31 | 5078.5 | 1707 | -434 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1195.6307 | 780 | 200 | 2175.6307 | 54.39% | 95% | 0% | -496.5675 | 736.6559 | -3550 | -400 | -3213.3441 | 80.33% | 56.12% | 95% | 0% | 2141 | -434
[5 empty] | 2019-07-31 | 32 | 5079 | 1748 | -412 | 1 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1195.6307 | 780 | 200 | 2175.6307 | 54.39% | 95% | 0% | -471.3959 | 791.5885 | -3550 | -400 | -3158.4115 | 78.96% | 56.12% | 95% | 0% | 2160 | -412
[5 empty] | 2019-07-31 | 33 | 5079.5 | 1790 | -407 | 1 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 1195.6307 | 780 | 200 | 2175.6307 | 54.39% | 95% | 0% | -465.6751 | 855.2648 | -3550 | -400 | -3094.7352 | 77.37% | 56.12% | 95% | 0% | 2197 | -407
[5 empty] | 2019-07-31 | 34 | 5080 | 1894 | -366 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 1195.6307 | 780 | 200 | 2175.6307 | 54.39% | 95% | 0% | -418.7643 | 1000.8565 | -3550 | -400 | -2949.1435 | 73.73% | 56.11% | 95% | 0% | 2260 | -366
[5 empty] | 2019-07-31 | 35 | 5080.5 | 1979 | -339 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 1195.6307 | 780 | 200 | 2175.6307 | 54.39% | 95% | 0% | -387.8719 | 1122.5981 | -3550 | -400 | -2827.4019 | 70.69% | 56.11% | 95% | 0% | 2318 | -339
[5 empty] | 2019-07-31 | 36 | 5081 | 2074 | -273 | 1 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 1195.6307 | 780 | 200 | 2175.6307 | 54.39% | 95% | 0% | -312.357 | 1243.5375 | -3550 | -400 | -2706.4625 | 67.66% | 56.11% | 95% | 0% | 2347 | -273
[5 empty] | 2019-07-31 | 37 | 5081.5 | 2115 | -239 | 1 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 1195.6307 | 780 | 200 | 2175.6307 | 54.39% | 95% | 0% | -273.4554 | 1293.4036 | -3550 | -400 | -2656.5964 | 66.41% | 56.11% | 95% | 0% | 2354 | -239
[5 empty] | 2019-07-31 | 38 | 5082 | 2158 | -195 | 1 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 1195.6307 | 780 | 200 | 2175.6307 | 54.39% | 95% | 0% | -223.1121 | 1342.1805 | -3550 | -400 | -2607.8195 | 65.2% | 56.1% | 95% | 0% | 2353 | -195
[5 empty] | 2019-07-31 | 39 | 5082.5 | 2207 | -149 | 1 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 1195.6307 | 780 | 200 | 2175.6307 | 54.39% | 95% | 0% | -170.4805 | 1399.5112 | -3550 | -400 | -2550.4888 | 63.76% | 56.1% | 95% | 0% | 2356 | -149
[5 empty] | 2019-07-31 | 40 | 5083 | 2235 | -116 | 1 | 0 | 2351 | 1562.1599 | 1562.1599 | 1562.1599 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -132.7231 | 1429.4368 | -3550 | -400 | -2520.5632 | 63.01% | 56.1% | 95% | 0% | 2351 | -116
[5 empty] | 2019-07-31 | 41 | 5083.5 | 2232 | -90 | 1 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -102.9748 | 1413.7605 | -3550 | -400 | -2536.2395 | 63.41% | 56.09% | 95% | 0% | 2322 | -90
[5 empty] | 2019-07-31 | 42 | 5084 | 2224 | -76 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -86.9565 | 1395.3188 | -3550 | -400 | -2554.6812 | 63.87% | 56.09% | 95% | 0% | 2300 | -76
[5 empty] | 2019-07-31 | 43 | 5084.5 | 2233 | -71 | 1 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -81.2357 | 1407.3051 | -3550 | -400 | -2542.6949 | 63.57% | 56.08% | 95% | 0% | 2304 | -71
[5 empty] | 2019-07-31 | 44 | 5085 | 2170 | -69 | 1 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -78.9474 | 1307.7798 | -3550 | -400 | -2642.2202 | 66.06% | 56.08% | 95% | 0% | 2239 | -69
[5 empty] | 2019-07-31 | 45 | 5085.5 | 2069 | -67 | 0 | 0 | 2136 | 1225.3916 | 1225.3916 | 1225.3916 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -76.659 | 1148.7326 | -2750 | -200 | -1801.2674 | 45.03% | 56.08% | 95% | 0% | 2136 | -67
[5 empty] | 2019-07-31 | 46 | 5086 | 1939 | -66 | 0 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -75.5149 | 944.683 | -2750 | -200 | -2005.317 | 50.13% | 56.08% | 95% | 0% | 2005 | -66
[5 empty] | 2019-07-31 | 47 | 5086.5 | 1824 | -65 | 0 | 0 | 1889 | 838.4996 | 838.4996 | 838.4996 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -74.3707 | 764.1289 | -2750 | -200 | -2185.8711 | 54.65% | 56.08% | 95% | 0% | 1889 | -65
[5 empty] | 2019-07-31 | 48 | 5087 | 1723 | -63 | 0 | 0 | 1786 | 677.1641 | 677.1641 | 677.1641 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -72.0824 | 605.0817 | -2750 | -200 | -2344.9183 | 58.62% | 56.07% | 95% | 0% | 1786 | -63
[5 empty] | 2019-08-01 | 1 | 5087.5 | 1618 | -59 | 0 | 0 | 1677 | 506.4303 | 506.4303 | 506.4303 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -67.5057 | 438.9246 | -2750 | -200 | -2511.0754 | 62.78% | 56.07% | 95% | 0% | 1677 | -59
[5 empty] | 2019-08-01 | 2 | 5088 | 1563 | -56 | 0 | 0 | 1619 | 415.5812 | 415.5812 | 415.5812 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -64.0732 | 351.508 | -2750 | -200 | -2598.492 | 64.96% | 56.07% | 95% | 0% | 1619 | -56
[5 empty] | 2019-08-01 | 3 | 5088.5 | 1529 | -55 | 0 | 0 | 1584 | 360.7585 | 360.7585 | 360.7585 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -62.9291 | 297.8294 | -2750 | -200 | -2652.1706 | 66.3% | 56.07% | 95% | 0% | 1584 | -55
[5 empty] | 2019-08-01 | 4 | 5089 | 1515 | -55 | 0 | 0 | 1570 | 338.8293 | 338.8293 | 338.8293 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -62.9291 | 275.9003 | -2750 | -200 | -2674.0997 | 66.85% | 56.07% | 95% | 0% | 1570 | -55
[5 empty] | 2019-08-01 | 5 | 5089.5 | 1490 | -54 | 0 | 0 | 1544 | 298.1039 | 298.1039 | 298.1039 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -61.7849 | 236.319 | -2750 | -200 | -2713.681 | 67.84% | 56.06% | 95% | 0% | 1544 | -54
[5 empty] | 2019-08-01 | 6 | 5090 | 1468 | -53 | 0 | 0 | 1521 | 262.0775 | 262.0775 | 262.0775 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -60.6407 | 201.4368 | -2750 | -200 | -2748.5632 | 68.71% | 56.06% | 95% | 0% | 1521 | -53
[5 empty] | 2019-08-01 | 7 | 5090.5 | 1457 | -52 | 0 | 0 | 1509 | 243.2811 | 243.2811 | 243.2811 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -59.4966 | 183.7846 | -2750 | -200 | -2766.2154 | 69.16% | 56.05% | 95% | 0% | 1509 | -52
[5 empty] | 2019-08-01 | 8 | 5091 | 1460 | -51 | 0 | 0 | 1511 | 246.4138 | 246.4138 | 246.4138 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -58.3524 | 188.0614 | -2750 | -200 | -2761.9386 | 69.05% | 56.05% | 95% | 0% | 1511 | -51
[5 empty] | 2019-08-01 | 9 | 5091.5 | 1465 | -50 | 0 | 0 | 1515 | 252.6793 | 252.6793 | 252.6793 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -57.2082 | 195.4711 | -2750 | -200 | -2754.5289 | 68.86% | 56.04% | 95% | 0% | 1515 | -50
[5 empty] | 2019-08-01 | 10 | 5092 | 1478 | -48 | 0 | 0 | 1526 | 269.9093 | 269.9093 | 269.9093 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -54.9199 | 214.9894 | -2750 | -200 | -2735.0106 | 68.38% | 56.04% | 95% | 0% | 1526 | -48
[5 empty] | 2019-08-01 | 11 | 5092.5 | 1506 | -47 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -53.7757 | 258.4254 | -2750 | -200 | -2691.5746 | 67.29% | 56.04% | 95% | 0% | 1553 | -47
[5 empty] | 2019-08-01 | 12 | 5093 | 1553 | -49 | 0 | 0 | 1602 | 388.953 | 388.953 | 388.953 | 1194.0643 | 780 | 200 | 2174.0643 | 54.35% | 95% | 0% | -56.0641 | 332.8889 | -2750 | -200 | -2617.1111 | 65.43% | 56.04% | 95% | 0% | 1602 | -49
[5 empty] | 2019-08-01 | 13 | 5093.5 | 1692 | -62 | 0 | 0 | 1754 | 627.0404 | 627.0404 | 627.0404 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -70.9382 | 556.1022 | -2750 | -200 | -2393.8978 | 59.85% | 56.03% | 95% | 0% | 1754 | -62
[5 empty] | 2019-08-01 | 14 | 5094 | 1797 | -86 | 1 | 0 | 1883 | 829.1014 | 829.1014 | 829.1014 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -98.3982 | 730.7032 | -3550 | -400 | -3219.2968 | 80.48% | 56.03% | 95% | 0% | 1883 | -86
[5 empty] | 2019-08-01 | 15 | 5094.5 | 1916 | -123 | 1 | 0 | 2039 | 1073.4542 | 1073.4542 | 1073.4542 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -140.7323 | 932.722 | -3550 | -400 | -3017.278 | 75.43% | 56.02% | 95% | 0% | 2039 | -123
[5 empty] | 2019-08-01 | 16 | 5095 | 1960 | -165 | 1 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -188.7872 | 1019.3744 | -3550 | -400 | -2930.6256 | 73.27% | 56.02% | 95% | 0% | 2125 | -165
[5 empty] | 2019-08-01 | 17 | 5095.5 | 1996 | -197 | 1 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -225.4005 | 1089.2739 | -3550 | -400 | -2860.7261 | 71.52% | 56.01% | 95% | 0% | 2193 | -197
[5 empty] | 2019-08-01 | 18 | 5096 | 1965 | -247 | 1 | 0 | 2212 | 1344.4353 | 1344.4353 | 1344.4353 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -282.6087 | 1061.8266 | -3550 | -400 | -2888.1734 | 72.2% | 56.01% | 95% | 0% | 2212 | -247
[5 empty] | 2019-08-01 | 19 | 5096.5 | 1979 | -288 | 1 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -329.5195 | 1101.0659 | -3550 | -400 | -2848.9341 | 71.22% | 56% | 95% | 0% | 2267 | -288
[5 empty] | 2019-08-01 | 20 | 5097 | 1942 | -330 | 1 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -377.5744 | 1060.8428 | -3550 | -400 | -2889.1572 | 72.23% | 56% | 95% | 0% | 2272 | -330
[5 empty] | 2019-08-01 | 21 | 5097.5 | 1891 | -368 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -421.0526 | 997.0018 | -3550 | -400 | -2952.9982 | 73.82% | 56% | 95% | 0% | 2259 | -368
[5 empty] | 2019-08-01 | 22 | 5098 | 1859 | -390 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -446.2243 | 956.1665 | -3550 | -400 | -2993.8335 | 74.85% | 56% | 95% | 0% | 2249 | -390
[5 empty] | 2019-08-01 | 23 | 5098.5 | 1846 | -409 | 1 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -467.9634 | 943.8256 | -3550 | -400 | -3006.1744 | 75.15% | 56% | 95% | 0% | 2255 | -409
[5 empty] | 2019-08-01 | 24 | 5099 | 1863 | -381 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -435.9268 | 958.6322 | -3550 | -400 | -2991.3678 | 74.78% | 55.99% | 95% | 0% | 2244 | -381
[5 empty] | 2019-08-01 | 25 | 5099.5 | 1811 | -415 | 1 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -474.8284 | 891.536 | -3550 | -400 | -3058.464 | 76.46% | 55.99% | 95% | 0% | 2226 | -415
[5 empty] | 2019-08-01 | 26 | 5100 | 1774 | -441 | 1 | 0 | 2215 | 1349.1344 | 1349.1344 | 1349.1344 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -504.5767 | 844.5577 | -3550 | -400 | -3105.4423 | 77.64% | 55.99% | 95% | 0% | 2215 | -441
[5 empty] | 2019-08-01 | 27 | 5100.5 | 1772 | -439 | 1 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -502.2883 | 840.5806 | -3550 | -400 | -3109.4194 | 77.74% | 55.99% | 95% | 0% | 2211 | -439
[5 empty] | 2019-08-01 | 28 | 5101 | 1734 | -467 | 1 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -534.3249 | 792.8803 | -3550 | -400 | -3157.1197 | 78.93% | 55.99% | 95% | 0% | 2201 | -467
[5 empty] | 2019-08-01 | 29 | 5101.5 | 1713 | -456 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -521.7391 | 755.3425 | -3550 | -400 | -3194.6575 | 79.87% | 55.99% | 95% | 0% | 2169 | -456
[5 empty] | 2019-08-01 | 30 | 5102 | 1741 | -424 | 1 | 0 | 2165 | 1270.8162 | 1270.8162 | 1270.8162 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -485.1259 | 785.6903 | -3550 | -400 | -3164.3097 | 79.11% | 55.98% | 95% | 0% | 2165 | -424
[5 empty] | 2019-08-01 | 31 | 5102.5 | 1735 | -431 | 1 | 0 | 2166 | 1272.3825 | 1272.3825 | 1272.3825 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -493.135 | 779.2475 | -3550 | -400 | -3170.7525 | 79.27% | 55.98% | 95% | 0% | 2166 | -431
[5 empty] | 2019-08-01 | 32 | 5103 | 1751 | -431 | 1 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 1192.4979 | 780 | 200 | 2172.4979 | 54.31% | 95% | 0% | -493.135 | 804.3093 | -3550 | -400 | -3145.6907 | 78.64% | 55.98% | 95% | 0% | 2182 | -431
[5 empty] | 2019-08-01 | 33 | 5103.5 | 1787 | -417 | 1 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -477.1167 | 854.7877 | -3550 | -400 | -3095.2123 | 77.38% | 55.97% | 95% | 0% | 2204 | -417
[5 empty] | 2019-08-01 | 34 | 5104 | 1887 | -372 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -425.6293 | 992.4251 | -3550 | -400 | -2957.5749 | 73.94% | 55.97% | 95% | 0% | 2259 | -372
[5 empty] | 2019-08-01 | 35 | 5104.5 | 1973 | -341 | 1 | 0 | 2314 | 1504.2045 | 1504.2045 | 1504.2045 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -390.1602 | 1114.0443 | -3550 | -400 | -2835.9557 | 70.9% | 55.97% | 95% | 0% | 2314 | -341
[5 empty] | 2019-08-01 | 36 | 5105 | 2092 | -252 | 1 | 0 | 2344 | 1551.1954 | 1551.1954 | 1551.1954 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -288.3295 | 1262.8659 | -3550 | -400 | -2687.1341 | 67.18% | 55.97% | 95% | 0% | 2344 | -252
[5 empty] | 2019-08-01 | 37 | 5105.5 | 2161 | -202 | 1 | 0 | 2363 | 1580.9563 | 1580.9563 | 1580.9563 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -231.1213 | 1349.835 | -3550 | -400 | -2600.165 | 65% | 55.97% | 95% | 0% | 2363 | -202
[5 empty] | 2019-08-01 | 38 | 5106 | 2228 | -158 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -180.778 | 1436.2047 | -3550 | -400 | -2513.7953 | 62.84% | 55.96% | 95% | 0% | 2386 | -158
[5 empty] | 2019-08-01 | 39 | 5106.5 | 2255 | -109 | 1 | 0 | 2364 | 1582.5227 | 1582.5227 | 1582.5227 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -124.714 | 1457.8087 | -3550 | -400 | -2492.1913 | 62.3% | 55.95% | 95% | 0% | 2364 | -109
[5 empty] | 2019-08-01 | 40 | 5107 | 2275 | -76 | 1 | 0 | 2351 | 1562.1599 | 1562.1599 | 1562.1599 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -86.9565 | 1475.2034 | -3550 | -400 | -2474.7966 | 61.87% | 55.95% | 95% | 0% | 2351 | -76
[5 empty] | 2019-08-01 | 41 | 5107.5 | 2308 | -54 | 1 | 0 | 2362 | 1579.3899 | 1579.3899 | 1579.3899 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -61.7849 | 1517.605 | -3550 | -400 | -2432.395 | 60.81% | 55.95% | 95% | 0% | 2362 | -54
[5 empty] | 2019-08-01 | 42 | 5108 | 2312 | -43 | 1 | 0 | 2355 | 1568.4254 | 1568.4254 | 1568.4254 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -49.1991 | 1519.2263 | -3550 | -400 | -2430.7737 | 60.77% | 55.95% | 95% | 0% | 2355 | -43
[5 empty] | 2019-08-01 | 43 | 5108.5 | 2300 | -41 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -46.9108 | 1499.5855 | -3550 | -400 | -2450.4145 | 61.26% | 55.95% | 95% | 0% | 2341 | -41
[5 empty] | 2019-08-01 | 44 | 5109 | 2256 | -40 | 0 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -45.7666 | 1430.2433 | -2750 | -200 | -1519.7567 | 37.99% | 55.95% | 95% | 0% | 2296 | -40
[5 empty] | 2019-08-01 | 45 | 5109.5 | 2139 | -40 | 0 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 1190.9316 | 780 | 200 | 2170.9316 | 54.27% | 95% | 0% | -45.7666 | 1246.9787 | -2750 | -200 | -1703.0213 | 42.58% | 55.93% | 95% | 0% | 2179 | -40
[5 empty] | 2019-08-01 | 46 | 5110 | 2003 | -40 | 0 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -45.7666 | 1033.9531 | -2750 | -200 | -1916.0469 | 47.9% | 55.93% | 95% | 0% | 2043 | -40
[5 empty] | 2019-08-01 | 47 | 5110.5 | 1878 | -40 | 0 | 0 | 1918 | 883.9242 | 883.9242 | 883.9242 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -45.7666 | 838.1576 | -2750 | -200 | -2111.8424 | 52.8% | 55.93% | 95% | 0% | 1918 | -40
[5 empty] | 2019-08-01 | 48 | 5111 | 1767 | -40 | 0 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -45.7666 | 664.2911 | -2750 | -200 | -2285.7089 | 57.14% | 55.92% | 95% | 0% | 1807 | -40
[5 empty] | 2019-08-02 | 1 | 5111.5 | 1674 | -43 | 0 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -49.1991 | 519.8858 | -2750 | -200 | -2430.1142 | 60.75% | 55.91% | 95% | 0% | 1717 | -43
[5 empty] | 2019-08-02 | 2 | 5112 | 1611 | -46 | 0 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -52.6316 | 422.4715 | -2750 | -200 | -2527.5285 | 63.19% | 55.9% | 95% | 0% | 1657 | -46
[5 empty] | 2019-08-02 | 3 | 5112.5 | 1569 | -44 | 0 | 0 | 1613 | 406.183 | 406.183 | 406.183 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -50.3432 | 355.8398 | -2750 | -200 | -2594.1602 | 64.85% | 55.9% | 95% | 0% | 1613 | -44
[5 empty] | 2019-08-02 | 4 | 5113 | 1550 | -42 | 0 | 0 | 1592 | 373.2894 | 373.2894 | 373.2894 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -48.0549 | 325.2344 | -2750 | -200 | -2624.7656 | 65.62% | 55.9% | 95% | 0% | 1592 | -42
[5 empty] | 2019-08-02 | 5 | 5113.5 | 1529 | -41 | 0 | 0 | 1570 | 338.8293 | 338.8293 | 338.8293 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -46.9108 | 291.9186 | -2750 | -200 | -2658.0814 | 66.45% | 55.9% | 95% | 0% | 1570 | -41
[5 empty] | 2019-08-02 | 6 | 5114 | 1494 | -40 | 0 | 0 | 1534 | 282.4402 | 282.4402 | 282.4402 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -45.7666 | 236.6736 | -2750 | -200 | -2713.3264 | 67.83% | 55.89% | 95% | 0% | 1534 | -40
[5 empty] | 2019-08-02 | 7 | 5114.5 | 1484 | -39 | 0 | 0 | 1523 | 265.2102 | 265.2102 | 265.2102 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -44.6224 | 220.5878 | -2750 | -200 | -2729.4122 | 68.24% | 55.89% | 95% | 0% | 1523 | -39
[5 empty] | 2019-08-02 | 8 | 5115 | 1485 | -38 | 0 | 0 | 1523 | 265.2102 | 265.2102 | 265.2102 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -43.4783 | 221.732 | -2750 | -200 | -2728.268 | 68.21% | 55.89% | 95% | 0% | 1523 | -38
[5 empty] | 2019-08-02 | 9 | 5115.5 | 1488 | -38 | 1 | 0 | 1526 | 269.9093 | 269.9093 | 269.9093 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -43.4783 | 226.4311 | -3550 | -400 | -3723.5689 | 93.09% | 55.89% | 95% | 0% | 1526 | -38
[5 empty] | 2019-08-02 | 10 | 5116 | 1500 | -39 | 1 | 0 | 1539 | 290.2721 | 290.2721 | 290.2721 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -44.6224 | 245.6496 | -3550 | -400 | -3704.3504 | 92.61% | 55.87% | 95% | 0% | 1539 | -39
[5 empty] | 2019-08-02 | 11 | 5116.5 | 1528 | -38 | 1 | 0 | 1566 | 332.5639 | 332.5639 | 332.5639 | 1189.3652 | 780 | 200 | 2169.3652 | 54.23% | 95% | 0% | -43.4783 | 289.0856 | -3550 | -400 | -3660.9144 | 91.52% | 55.86% | 95% | 0% | 1566 | -38
[5 empty] | 2019-08-02 | 12 | 5117 | 1568 | -40 | 1 | 0 | 1608 | 398.3512 | 398.3512 | 398.3512 | 1187.7988 | 780 | 200 | 2167.7988 | 54.19% | 95% | 0% | -45.7666 | 352.5846 | -3550 | -400 | -3597.4154 | 89.94% | 55.86% | 95% | 0% | 1608 | -40
[5 empty] | 2019-08-02 | 13 | 5117.5 | 1691 | -54 | 1 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 1187.7988 | 780 | 200 | 2167.7988 | 54.19% | 95% | 0% | -61.7849 | 551.1582 | -3550 | -400 | -3398.8418 | 84.97% | 55.86% | 95% | 0% | 1745 | -54
[5 empty] | 2019-08-02 | 14 | 5118 | 1792 | -86 | 1 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 1187.7988 | 780 | 200 | 2167.7988 | 54.19% | 95% | 0% | -98.3982 | 722.8714 | -3550 | -400 | -3227.1286 | 80.68% | 55.86% | 95% | 0% | 1878 | -86
[5 empty] | 2019-08-02 | 15 | 5118.5 | 1907 | -120 | 1 | 0 | 2027 | 1054.6579 | 1054.6579 | 1054.6579 | 1187.7988 | 780 | 200 | 2167.7988 | 54.19% | 95% | 0% | -137.2998 | 917.3581 | -3550 | -400 | -3032.6419 | 75.82% | 55.86% | 95% | 0% | 2027 | -120
[5 empty] | 2019-08-02 | 16 | 5119 | 1950 | -157 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1187.7988 | 780 | 200 | 2167.7988 | 54.19% | 95% | 0% | -179.6339 | 1000.3332 | -3550 | -400 | -2949.6668 | 73.74% | 55.85% | 95% | 0% | 2107 | -157
[5 empty] | 2019-08-02 | 17 | 5119.5 | 2003 | -208 | 1 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 1187.7988 | 780 | 200 | 2167.7988 | 54.19% | 95% | 0% | -237.9863 | 1104.8827 | -3550 | -400 | -2845.1173 | 71.13% | 55.85% | 95% | 0% | 2211 | -208
[5 empty] | 2019-08-02 | 18 | 5120 | 1980 | -267 | 1 | 0 | 2247 | 1399.258 | 1399.258 | 1399.258 | 1187.7988 | 780 | 200 | 2167.7988 | 54.19% | 95% | 0% | -305.492 | 1093.766 | -3550 | -400 | -2856.234 | 71.41% | 55.84% | 95% | 0% | 2247 | -267
[5 empty] | 2019-08-02 | 19 | 5120.5 | 1935 | -316 | 1 | 0 | 2251 | 1405.5235 | 1405.5235 | 1405.5235 | 1187.7988 | 780 | 200 | 2167.7988 | 54.19% | 95% | 0% | -361.5561 | 1043.9674 | -3550 | -400 | -2906.0326 | 72.65% | 55.84% | 95% | 0% | 2251 | -316
[5 empty] | 2019-08-02 | 20 | 5121 | 1879 | -363 | 1 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 1187.7988 | 780 | 200 | 2167.7988 | 54.19% | 95% | 0% | -415.3318 | 976.0944 | -3550 | -400 | -2973.9056 | 74.35% | 55.83% | 95% | 0% | 2242 | -363
[5 empty] | 2019-08-02 | 21 | 5121.5 | 1828 | -405 | 1 | 0 | 2233 | 1377.3289 | 1377.3289 | 1377.3289 | 1187.7988 | 780 | 200 | 2167.7988 | 54.19% | 95% | 0% | -463.3867 | 913.9422 | -3550 | -400 | -3036.0578 | 75.9% | 55.83% | 95% | 0% | 2233 | -405
[5 empty] | 2019-08-02 | 22 | 5122 | 1812 | -412 | 1 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 1187.7988 | 780 | 200 | 2167.7988 | 54.19% | 95% | 0% | -471.3959 | 891.8358 | -3550 | -400 | -3058.1642 | 76.45% | 55.83% | 95% | 0% | 2224 | -412
[5 empty] | 2019-08-02 | 23 | 5122.5 | 1776 | -437 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -500 | 846.0016 | -3550 | -400 | -3103.9984 | 77.6% | 55.83% | 95% | 0% | 2213 | -437
[5 empty] | 2019-08-02 | 24 | 5123 | 1736 | -463 | 1 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -529.7483 | 794.3243 | -3550 | -400 | -3155.6757 | 78.89% | 55.83% | 95% | 0% | 2199 | -463
[5 empty] | 2019-08-02 | 25 | 5123.5 | 1726 | -483 | 1 | 0 | 2209 | 1339.7362 | 1339.7362 | 1339.7362 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -552.6316 | 787.1046 | -3550 | -400 | -3162.8954 | 79.07% | 55.83% | 95% | 0% | 2209 | -483
[5 empty] | 2019-08-02 | 26 | 5124 | 1711 | -488 | 1 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -558.3524 | 765.7201 | -3550 | -400 | -3184.2799 | 79.61% | 55.82% | 95% | 0% | 2199 | -488
[5 empty] | 2019-08-02 | 27 | 5124.5 | 1717 | -468 | 1 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -535.4691 | 766.6743 | -3550 | -400 | -3183.3257 | 79.58% | 55.82% | 95% | 0% | 2185 | -468
[5 empty] | 2019-08-02 | 28 | 5125 | 1671 | -494 | 1 | 0 | 2165 | 1270.8162 | 1270.8162 | 1270.8162 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -565.2174 | 705.5988 | -3550 | -400 | -3244.4012 | 81.11% | 55.82% | 95% | 0% | 2165 | -494
[5 empty] | 2019-08-02 | 29 | 5125.5 | 1634 | -490 | 1 | 0 | 2124 | 1206.5952 | 1206.5952 | 1206.5952 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -560.6407 | 645.9545 | -3550 | -400 | -3304.0455 | 82.6% | 55.82% | 95% | 0% | 2124 | -490
[5 empty] | 2019-08-02 | 30 | 5126 | 1660 | -451 | 1 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -516.0183 | 670.2142 | -3550 | -400 | -3279.7858 | 81.99% | 55.82% | 95% | 0% | 2111 | -451
[5 empty] | 2019-08-02 | 31 | 5126.5 | 1664 | -425 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -486.27 | 665.5024 | -3550 | -400 | -3284.4976 | 82.11% | 55.82% | 95% | 0% | 2089 | -425
[5 empty] | 2019-08-02 | 32 | 5127 | 1683 | -413 | 1 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -472.54 | 690.197 | -3550 | -400 | -3259.803 | 81.5% | 55.81% | 95% | 0% | 2096 | -413
[5 empty] | 2019-08-02 | 33 | 5127.5 | 1760 | -370 | 1 | 0 | 2130 | 1215.9934 | 1215.9934 | 1215.9934 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -423.341 | 792.6524 | -3550 | -400 | -3157.3476 | 78.93% | 55.81% | 95% | 0% | 2130 | -370
[5 empty] | 2019-08-02 | 34 | 5128 | 1860 | -331 | 1 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -378.7185 | 932.8231 | -3550 | -400 | -3017.1769 | 75.43% | 55.81% | 95% | 0% | 2191 | -331
[5 empty] | 2019-08-02 | 35 | 5128.5 | 1938 | -286 | 1 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 1186.2325 | 780 | 200 | 2166.2325 | 54.16% | 95% | 0% | -327.2311 | 1036.0005 | -3550 | -400 | -2913.9995 | 72.85% | 55.81% | 95% | 0% | 2224 | -286
[5 empty] | 2019-08-02 | 36 | 5129 | 2009 | -240 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1184.6661 | 780 | 200 | 2164.6661 | 54.12% | 95% | 0% | -274.5995 | 1127.7912 | -3550 | -400 | -2822.2088 | 70.56% | 55.81% | 95% | 0% | 2249 | -240
[5 empty] | 2019-08-02 | 37 | 5129.5 | 2066 | -196 | 1 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 1184.6661 | 780 | 200 | 2164.6661 | 54.12% | 95% | 0% | -224.2563 | 1198.4972 | -3550 | -400 | -2751.5028 | 68.79% | 55.8% | 95% | 0% | 2262 | -196
[5 empty] | 2019-08-02 | 38 | 5130 | 2140 | -153 | 1 | 0 | 2293 | 1471.3108 | 1471.3108 | 1471.3108 | 1184.6661 | 780 | 200 | 2164.6661 | 54.12% | 95% | 0% | -175.0572 | 1296.2536 | -3550 | -400 | -2653.7464 | 66.34% | 55.79% | 95% | 0% | 2293 | -153
[5 empty] | 2019-08-02 | 39 | 5130.5 | 2179 | -108 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1184.6661 | 780 | 200 | 2164.6661 | 54.12% | 95% | 0% | -123.5698 | 1338.3428 | -3550 | -400 | -2611.6572 | 65.29% | 55.78% | 95% | 0% | 2287 | -108
[5 empty] | 2019-08-02 | 40 | 5131 | 2224 | -68 | 1 | 0 | 2292 | 1469.7444 | 1469.7444 | 1469.7444 | 1184.6661 | 780 | 200 | 2164.6661 | 54.12% | 95% | 0% | -77.8032 | 1391.9412 | -3550 | -400 | -2558.0588 | 63.95% | 55.77% | 95% | 0% | 2292 | -68
[5 empty] | 2019-08-02 | 41 | 5131.5 | 2243 | -41 | 1 | 0 | 2284 | 1457.2135 | 1457.2135 | 1457.2135 | 1184.6661 | 780 | 200 | 2164.6661 | 54.12% | 95% | 0% | -46.9108 | 1410.3028 | -3550 | -400 | -2539.6972 | 63.49% | 55.77% | 95% | 0% | 2284 | -41
[5 empty] | 2019-08-02 | 42 | 5132 | 2233 | -29 | 1 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -33.1808 | 1389.5727 | -3550 | -400 | -2560.4273 | 64.01% | 55.77% | 95% | 0% | 2262 | -29
[5 empty] | 2019-08-02 | 43 | 5132.5 | 2248 | -27 | 1 | 0 | 2275 | 1443.1162 | 1443.1162 | 1443.1162 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -30.8924 | 1412.2238 | -3550 | -400 | -2537.7762 | 63.44% | 55.77% | 95% | 0% | 2275 | -27
[5 empty] | 2019-08-02 | 44 | 5133 | 2201 | -27 | 0 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -30.8924 | 1338.6047 | -2750 | -200 | -1611.3953 | 40.28% | 55.76% | 95% | 0% | 2228 | -27
[5 empty] | 2019-08-02 | 45 | 5133.5 | 2107 | -26 | 0 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -29.7483 | 1190.9442 | -2750 | -200 | -1759.0558 | 43.98% | 55.76% | 95% | 0% | 2133 | -26
[5 empty] | 2019-08-02 | 46 | 5134 | 2005 | -26 | 0 | 0 | 2031 | 1060.9233 | 1060.9233 | 1060.9233 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -29.7483 | 1031.175 | -2750 | -200 | -1918.825 | 47.97% | 55.76% | 95% | 0% | 2031 | -26
[5 empty] | 2019-08-02 | 47 | 5134.5 | 1899 | -26 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -29.7483 | 865.1404 | -2750 | -200 | -2084.8596 | 52.12% | 55.75% | 95% | 0% | 1925 | -26
[5 empty] | 2019-08-02 | 48 | 5135 | 1792 | -26 | 0 | 0 | 1818 | 727.2877 | 727.2877 | 727.2877 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -29.7483 | 697.5394 | -2750 | -200 | -2252.4606 | 56.31% | 55.75% | 95% | 0% | 1818 | -26
[5 empty] | 2019-08-03 | 1 | 5135.5 | 1702 | -27 | 0 | 0 | 1729 | 587.8813 | 587.8813 | 587.8813 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -30.8924 | 556.9888 | -2750 | -200 | -2393.0112 | 59.83% | 55.75% | 95% | 0% | 1729 | -27
[5 empty] | 2019-08-03 | 2 | 5136 | 1641 | -28 | 0 | 0 | 1669 | 493.8994 | 493.8994 | 493.8994 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -32.0366 | 461.8628 | -2750 | -200 | -2488.1372 | 62.2% | 55.74% | 95% | 0% | 1669 | -28
[5 empty] | 2019-08-03 | 3 | 5136.5 | 1589 | -28 | 0 | 0 | 1617 | 412.4485 | 412.4485 | 412.4485 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -32.0366 | 380.4119 | -2750 | -200 | -2569.5881 | 64.24% | 55.74% | 95% | 0% | 1617 | -28
[5 empty] | 2019-08-03 | 4 | 5137 | 1563 | -27 | 0 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -30.8924 | 339.2642 | -2750 | -200 | -2610.7358 | 65.27% | 55.74% | 95% | 0% | 1590 | -27
[5 empty] | 2019-08-03 | 5 | 5137.5 | 1527 | -28 | 0 | 0 | 1555 | 315.3339 | 315.3339 | 315.3339 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -32.0366 | 283.2973 | -2750 | -200 | -2666.7027 | 66.67% | 55.73% | 95% | 0% | 1555 | -28
[5 empty] | 2019-08-03 | 6 | 5138 | 1499 | -28 | 0 | 0 | 1527 | 271.4757 | 271.4757 | 271.4757 | 1183.0998 | 780 | 200 | 2163.0998 | 54.08% | 95% | 0% | -32.0366 | 239.4391 | -2750 | -200 | -2710.5609 | 67.76% | 55.73% | 95% | 0% | 1527 | -28
[5 empty] | 2019-08-03 | 7 | 5138.5 | 1470 | -27 | 0 | 0 | 1497 | 224.4847 | 224.4847 | 224.4847 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -30.8924 | 193.5923 | -2750 | -200 | -2756.4077 | 68.91% | 55.73% | 95% | 0% | 1497 | -27
[5 empty] | 2019-08-03 | 8 | 5139 | 1467 | -27 | 0 | 0 | 1494 | 219.7857 | 219.7857 | 219.7857 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -30.8924 | 188.8932 | -2750 | -200 | -2761.1068 | 69.03% | 55.73% | 95% | 0% | 1494 | -27
[5 empty] | 2019-08-03 | 9 | 5139.5 | 1460 | -27 | 0 | 0 | 1487 | 208.8211 | 208.8211 | 208.8211 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -30.8924 | 177.9287 | -2750 | -200 | -2772.0713 | 69.3% | 55.73% | 95% | 0% | 1487 | -27
[5 empty] | 2019-08-03 | 10 | 5140 | 1451 | -28 | 1 | 0 | 1479 | 196.2902 | 196.2902 | 196.2902 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -32.0366 | 164.2536 | -3550 | -400 | -3785.7464 | 94.64% | 55.73% | 95% | 0% | 1479 | -28
[5 empty] | 2019-08-03 | 11 | 5140.5 | 1455 | -28 | 1 | 0 | 1483 | 202.5556 | 202.5556 | 202.5556 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -32.0366 | 170.519 | -3550 | -400 | -3779.481 | 94.49% | 55.72% | 95% | 0% | 1483 | -28
[5 empty] | 2019-08-03 | 12 | 5141 | 1462 | -31 | 1 | 0 | 1493 | 218.2193 | 218.2193 | 218.2193 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -35.4691 | 182.7502 | -3550 | -400 | -3767.2498 | 94.18% | 55.72% | 95% | 0% | 1493 | -31
[5 empty] | 2019-08-03 | 13 | 5141.5 | 1512 | -48 | 1 | 0 | 1560 | 323.1657 | 323.1657 | 323.1657 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -54.9199 | 268.2458 | -3550 | -400 | -3681.7542 | 92.04% | 55.71% | 95% | 0% | 1560 | -48
[5 empty] | 2019-08-03 | 14 | 5142 | 1537 | -76 | 1 | 0 | 1613 | 406.183 | 406.183 | 406.183 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -86.9565 | 319.2265 | -3550 | -400 | -3630.7735 | 90.77% | 55.7% | 95% | 0% | 1613 | -76
[5 empty] | 2019-08-03 | 15 | 5142.5 | 1599 | -110 | 1 | 0 | 1709 | 556.554 | 556.554 | 556.554 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -125.8581 | 430.6959 | -3550 | -400 | -3519.3041 | 87.98% | 55.7% | 95% | 0% | 1709 | -110
[5 empty] | 2019-08-03 | 16 | 5143 | 1637 | -148 | 1 | 0 | 1785 | 675.5977 | 675.5977 | 675.5977 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -169.3364 | 506.2613 | -3550 | -400 | -3443.7387 | 86.09% | 55.7% | 95% | 0% | 1785 | -148
[5 empty] | 2019-08-03 | 17 | 5143.5 | 1684 | -196 | 1 | 0 | 1880 | 824.4023 | 824.4023 | 824.4023 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -224.2563 | 600.146 | -3550 | -400 | -3349.854 | 83.75% | 55.69% | 95% | 0% | 1880 | -196
[5 empty] | 2019-08-03 | 18 | 5144 | 1697 | -249 | 1 | 0 | 1946 | 927.7824 | 927.7824 | 927.7824 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -284.897 | 642.8853 | -3550 | -400 | -3307.1147 | 82.68% | 55.69% | 95% | 0% | 1946 | -249
[5 empty] | 2019-08-03 | 19 | 5144.5 | 1689 | -285 | 1 | 0 | 1974 | 971.6406 | 971.6406 | 971.6406 | 1181.5334 | 780 | 200 | 2161.5334 | 54.04% | 95% | 0% | -326.087 | 645.5536 | -3550 | -400 | -3304.4464 | 82.61% | 55.69% | 95% | 0% | 1974 | -285
[5 empty] | 2019-08-03 | 20 | 5145 | 1644 | -331 | 1 | 0 | 1975 | 973.2069 | 973.2069 | 973.2069 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -378.7185 | 594.4884 | -3550 | -400 | -3355.5116 | 83.89% | 55.69% | 95% | 0% | 1975 | -331
[5 empty] | 2019-08-03 | 21 | 5145.5 | 1612 | -371 | 1 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -424.4851 | 561.2527 | -3550 | -400 | -3388.7473 | 84.72% | 55.69% | 95% | 0% | 1983 | -371
[5 empty] | 2019-08-03 | 22 | 5146 | 1562 | -410 | 1 | 0 | 1972 | 968.5078 | 968.5078 | 968.5078 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -469.1076 | 499.4003 | -3550 | -400 | -3450.5997 | 86.26% | 55.69% | 95% | 0% | 1972 | -410
[5 empty] | 2019-08-03 | 23 | 5146.5 | 1493 | -469 | 1 | 0 | 1962 | 952.8442 | 952.8442 | 952.8442 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -536.6133 | 416.2309 | -3550 | -400 | -3533.7691 | 88.34% | 55.68% | 95% | 0% | 1962 | -469
[5 empty] | 2019-08-03 | 24 | 5147 | 1463 | -479 | 1 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -548.0549 | 373.462 | -3550 | -400 | -3576.538 | 89.41% | 55.68% | 95% | 0% | 1942 | -479
[5 empty] | 2019-08-03 | 25 | 5147.5 | 1420 | -506 | 1 | 0 | 1926 | 896.4551 | 896.4551 | 896.4551 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -578.9474 | 317.5077 | -3550 | -400 | -3632.4923 | 90.81% | 55.68% | 95% | 0% | 1926 | -506
[5 empty] | 2019-08-03 | 26 | 5148 | 1404 | -509 | 1 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -582.3799 | 293.7125 | -3550 | -400 | -3656.2875 | 91.41% | 55.67% | 95% | 0% | 1913 | -509
[5 empty] | 2019-08-03 | 27 | 5148.5 | 1400 | -496 | 1 | 0 | 1896 | 849.4641 | 849.4641 | 849.4641 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -567.5057 | 281.9584 | -3550 | -400 | -3668.0416 | 91.7% | 55.66% | 95% | 0% | 1896 | -496
[5 empty] | 2019-08-03 | 28 | 5149 | 1410 | -461 | 1 | 0 | 1871 | 810.305 | 810.305 | 810.305 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -527.46 | 282.8451 | -3550 | -400 | -3667.1549 | 91.68% | 55.66% | 95% | 0% | 1871 | -461
[5 empty] | 2019-08-03 | 29 | 5149.5 | 1390 | -459 | 1 | 0 | 1849 | 775.845 | 775.845 | 775.845 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -525.1716 | 250.6734 | -3550 | -400 | -3699.3266 | 92.48% | 55.66% | 95% | 0% | 1849 | -459
[5 empty] | 2019-08-03 | 30 | 5150 | 1432 | -405 | 1 | 0 | 1837 | 757.0486 | 757.0486 | 757.0486 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -463.3867 | 293.6619 | -3550 | -400 | -3656.3381 | 91.41% | 55.66% | 95% | 0% | 1837 | -405
[5 empty] | 2019-08-03 | 31 | 5150.5 | 1489 | -373 | 1 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -426.7735 | 369.4343 | -3550 | -400 | -3580.5657 | 89.51% | 55.65% | 95% | 0% | 1862 | -373
[5 empty] | 2019-08-03 | 32 | 5151 | 1542 | -345 | 1 | 0 | 1887 | 835.3669 | 835.3669 | 835.3669 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -394.7368 | 440.63 | -3550 | -400 | -3509.37 | 87.73% | 55.65% | 95% | 0% | 1887 | -345
[5 empty] | 2019-08-03 | 33 | 5151.5 | 1627 | -298 | 1 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -340.9611 | 553.9276 | -3550 | -400 | -3396.0724 | 84.9% | 55.64% | 95% | 0% | 1925 | -298
[5 empty] | 2019-08-03 | 34 | 5152 | 1704 | -273 | 1 | 0 | 1977 | 976.3397 | 976.3397 | 976.3397 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -312.357 | 663.9827 | -3550 | -400 | -3286.0173 | 82.15% | 55.64% | 95% | 0% | 1977 | -273
[5 empty] | 2019-08-03 | 35 | 5152.5 | 1799 | -236 | 1 | 0 | 2035 | 1067.1888 | 1067.1888 | 1067.1888 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -270.0229 | 797.1659 | -3550 | -400 | -3152.8341 | 78.82% | 55.64% | 95% | 0% | 2035 | -236
[5 empty] | 2019-08-03 | 36 | 5153 | 1870 | -207 | 1 | 0 | 2077 | 1132.9761 | 1132.9761 | 1132.9761 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -236.8421 | 896.134 | -3550 | -400 | -3053.866 | 76.35% | 55.63% | 95% | 0% | 2077 | -207
[5 empty] | 2019-08-03 | 37 | 5153.5 | 1912 | -184 | 1 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -210.5263 | 952.2107 | -3550 | -400 | -2997.7893 | 74.94% | 55.62% | 95% | 0% | 2096 | -184
[5 empty] | 2019-08-03 | 38 | 5154 | 1961 | -148 | 1 | 0 | 2109 | 1183.0998 | 1183.0998 | 1183.0998 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -169.3364 | 1013.7634 | -3550 | -400 | -2936.2366 | 73.41% | 55.61% | 95% | 0% | 2109 | -148
[5 empty] | 2019-08-03 | 39 | 5154.5 | 2006 | -105 | 1 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -120.1373 | 1066.0952 | -3550 | -400 | -2883.9048 | 72.1% | 55.61% | 95% | 0% | 2111 | -105
[5 empty] | 2019-08-03 | 40 | 5155 | 2026 | -76 | 1 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -86.9565 | 1085.1787 | -3550 | -400 | -2864.8213 | 71.62% | 55.6% | 95% | 0% | 2102 | -76
[5 empty] | 2019-08-03 | 41 | 5155.5 | 2036 | -53 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1179.967 | 780 | 200 | 2159.967 | 54% | 95% | 0% | -60.6407 | 1091.1317 | -3550 | -400 | -2858.8683 | 71.47% | 55.6% | 95% | 0% | 2089 | -53
[5 empty] | 2019-08-03 | 42 | 5156 | 2026 | -44 | 1 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -50.3432 | 1071.6683 | -3550 | -400 | -2878.3317 | 71.96% | 55.6% | 95% | 0% | 2070 | -44
[5 empty] | 2019-08-03 | 43 | 5156.5 | 2040 | -44 | 1 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -50.3432 | 1093.5974 | -3550 | -400 | -2856.4026 | 71.41% | 55.6% | 95% | 0% | 2084 | -44
[5 empty] | 2019-08-03 | 44 | 5157 | 2015 | -45 | 0 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -51.4874 | 1054.8605 | -2750 | -200 | -1895.1395 | 47.38% | 55.6% | 95% | 0% | 2060 | -45
[5 empty] | 2019-08-03 | 45 | 5157.5 | 1950 | -47 | 0 | 0 | 1997 | 1007.6669 | 1007.6669 | 1007.6669 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -53.7757 | 953.8912 | -2750 | -200 | -1996.1088 | 49.9% | 55.6% | 95% | 0% | 1997 | -47
[5 empty] | 2019-08-03 | 46 | 5158 | 1860 | -48 | 0 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -54.9199 | 813.3406 | -2750 | -200 | -2136.6594 | 53.42% | 55.59% | 95% | 0% | 1908 | -48
[5 empty] | 2019-08-03 | 47 | 5158.5 | 1752 | -50 | 0 | 0 | 1802 | 702.2259 | 702.2259 | 702.2259 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -57.2082 | 645.0176 | -2750 | -200 | -2304.9824 | 57.62% | 55.58% | 95% | 0% | 1802 | -50
[5 empty] | 2019-08-03 | 48 | 5159 | 1666 | -51 | 0 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -58.3524 | 510.7325 | -2750 | -200 | -2439.2675 | 60.98% | 55.58% | 95% | 0% | 1717 | -51
[5 empty] | 2019-08-04 | 1 | 5159.5 | 1597 | -50 | 0 | 0 | 1647 | 459.4394 | 459.4394 | 459.4394 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -57.2082 | 402.2312 | -2750 | -200 | -2547.7688 | 63.69% | 55.58% | 95% | 0% | 1647 | -50
[5 empty] | 2019-08-04 | 2 | 5160 | 1540 | -50 | 0 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -57.2082 | 312.9484 | -2750 | -200 | -2637.0516 | 65.93% | 55.58% | 95% | 0% | 1590 | -50
[5 empty] | 2019-08-04 | 3 | 5160.5 | 1500 | -50 | 0 | 0 | 1550 | 307.5021 | 307.5021 | 307.5021 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -57.2082 | 250.2938 | -2750 | -200 | -2699.7062 | 67.49% | 55.58% | 95% | 0% | 1550 | -50
[5 empty] | 2019-08-04 | 4 | 5161 | 1469 | -51 | 0 | 0 | 1520 | 260.5111 | 260.5111 | 260.5111 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -58.3524 | 202.1587 | -2750 | -200 | -2747.8413 | 68.7% | 55.58% | 95% | 0% | 1520 | -51
[5 empty] | 2019-08-04 | 5 | 5161.5 | 1440 | -50 | 0 | 0 | 1490 | 213.5202 | 213.5202 | 213.5202 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -57.2082 | 156.312 | -2750 | -200 | -2793.688 | 69.84% | 55.57% | 95% | 0% | 1490 | -50
[5 empty] | 2019-08-04 | 6 | 5162 | 1405 | -50 | 0 | 0 | 1455 | 158.6974 | 158.6974 | 158.6974 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -57.2082 | 101.4892 | -2750 | -200 | -2848.5108 | 71.21% | 55.57% | 95% | 0% | 1455 | -50
[5 empty] | 2019-08-04 | 7 | 5162.5 | 1387 | -50 | 0 | 0 | 1437 | 130.5029 | 130.5029 | 130.5029 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -57.2082 | 73.2946 | -2750 | -200 | -2876.7054 | 71.92% | 55.57% | 95% | 0% | 1437 | -50
[5 empty] | 2019-08-04 | 8 | 5163 | 1379 | -50 | 0 | 0 | 1429 | 117.972 | 117.972 | 117.972 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -57.2082 | 60.7637 | -2750 | -200 | -2889.2363 | 72.23% | 55.55% | 95% | 0% | 1429 | -50
[5 empty] | 2019-08-04 | 9 | 5163.5 | 1371 | -48 | 0 | 0 | 1419 | 102.3083 | 102.3083 | 102.3083 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -54.9199 | 47.3884 | -2750 | -200 | -2902.6116 | 72.57% | 55.55% | 95% | 0% | 1419 | -48
[5 empty] | 2019-08-04 | 10 | 5164 | 1368 | -46 | 0 | 0 | 1414 | 94.4765 | 94.4765 | 94.4765 | 1178.4007 | 780 | 200 | 2158.4007 | 53.96% | 95% | 0% | -52.6316 | 41.8449 | -2750 | -200 | -2908.1551 | 72.7% | 55.55% | 95% | 0% | 1414 | -46
[5 empty] | 2019-08-04 | 11 | 5164.5 | 1370 | -45 | 0 | 0 | 1415 | 96.0429 | 96.0429 | 96.0429 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -51.4874 | 44.5555 | -2750 | -200 | -2905.4445 | 72.64% | 55.55% | 95% | 0% | 1415 | -45
[5 empty] | 2019-08-04 | 12 | 5165 | 1352 | -47 | 0 | 0 | 1399 | 70.981 | 70.981 | 70.981 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -53.7757 | 17.2053 | -2750 | -200 | -2932.7947 | 73.32% | 55.55% | 95% | 0% | 1399 | -47
[5 empty] | 2019-08-04 | 13 | 5165.5 | 1369 | -65 | 1 | 0 | 1434 | 125.8038 | 125.8038 | 125.8038 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -74.3707 | 51.4331 | -3550 | -400 | -3898.5669 | 97.46% | 55.54% | 95% | 0% | 1434 | -65
[5 empty] | 2019-08-04 | 14 | 5166 | 1364 | -98 | 1 | 0 | 1462 | 169.662 | 169.662 | 169.662 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -112.1281 | 57.5338 | -3550 | -400 | -3892.4662 | 97.31% | 55.54% | 95% | 0% | 1462 | -98
[5 empty] | 2019-08-04 | 15 | 5166.5 | 1388 | -137 | 1 | 0 | 1525 | 268.343 | 268.343 | 268.343 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -156.7506 | 111.5924 | -3550 | -400 | -3838.4076 | 95.96% | 55.54% | 95% | 0% | 1525 | -137
[5 empty] | 2019-08-04 | 16 | 5167 | 1405 | -174 | 1 | 0 | 1579 | 352.9266 | 352.9266 | 352.9266 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -199.0847 | 153.842 | -3550 | -400 | -3796.158 | 94.9% | 55.54% | 95% | 0% | 1579 | -174
[5 empty] | 2019-08-04 | 17 | 5167.5 | 1437 | -222 | 1 | 0 | 1659 | 478.2358 | 478.2358 | 478.2358 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -254.0046 | 224.2312 | -3550 | -400 | -3725.7688 | 93.14% | 55.54% | 95% | 0% | 1659 | -222
[5 empty] | 2019-08-04 | 18 | 5168 | 1463 | -262 | 1 | 0 | 1725 | 581.6158 | 581.6158 | 581.6158 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -299.7712 | 281.8447 | -3550 | -400 | -3668.1553 | 91.7% | 55.54% | 95% | 0% | 1725 | -262
[5 empty] | 2019-08-04 | 19 | 5168.5 | 1481 | -309 | 1 | 0 | 1790 | 683.4295 | 683.4295 | 683.4295 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -353.5469 | 329.8826 | -3550 | -400 | -3620.1174 | 90.5% | 55.53% | 95% | 0% | 1790 | -309
[5 empty] | 2019-08-04 | 20 | 5169 | 1502 | -342 | 1 | 0 | 1844 | 768.0132 | 768.0132 | 768.0132 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -391.3043 | 376.7088 | -3550 | -400 | -3573.2912 | 89.33% | 55.53% | 95% | 0% | 1844 | -342
[5 empty] | 2019-08-04 | 21 | 5169.5 | 1492 | -381 | 1 | 0 | 1873 | 813.4378 | 813.4378 | 813.4378 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -435.9268 | 377.511 | -3550 | -400 | -3572.489 | 89.31% | 55.53% | 95% | 0% | 1873 | -381
[5 empty] | 2019-08-04 | 22 | 5170 | 1499 | -397 | 1 | 0 | 1896 | 849.4641 | 849.4641 | 849.4641 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -454.2334 | 395.2307 | -3550 | -400 | -3554.7693 | 88.87% | 55.53% | 95% | 0% | 1896 | -397
[5 empty] | 2019-08-04 | 23 | 5170.5 | 1489 | -413 | 1 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -472.54 | 386.3223 | -3550 | -400 | -3563.6777 | 89.09% | 55.52% | 95% | 0% | 1902 | -413
[5 empty] | 2019-08-04 | 24 | 5171 | 1478 | -427 | 1 | 0 | 1905 | 863.5614 | 863.5614 | 863.5614 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -488.5584 | 375.0031 | -3550 | -400 | -3574.9969 | 89.37% | 55.52% | 95% | 0% | 1905 | -427
[5 empty] | 2019-08-04 | 25 | 5171.5 | 1479 | -434 | 1 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -496.5675 | 379.5248 | -3550 | -400 | -3570.4752 | 89.26% | 55.52% | 95% | 0% | 1913 | -434
[5 empty] | 2019-08-04 | 26 | 5172 | 1466 | -432 | 1 | 0 | 1898 | 852.5969 | 852.5969 | 852.5969 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -494.2792 | 358.3177 | -3550 | -400 | -3591.6823 | 89.79% | 55.51% | 95% | 0% | 1898 | -432
[5 empty] | 2019-08-04 | 27 | 5172.5 | 1443 | -447 | 1 | 0 | 1890 | 840.066 | 840.066 | 840.066 | 1176.8343 | 780 | 200 | 2156.8343 | 53.92% | 95% | 0% | -511.4416 | 328.6243 | -3550 | -400 | -3621.3757 | 90.53% | 55.51% | 95% | 0% | 1890 | -447
[5 empty] | 2019-08-04 | 28 | 5173 | 1440 | -444 | 1 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -508.0092 | 322.6586 | -3550 | -400 | -3627.3414 | 90.68% | 55.5% | 95% | 0% | 1884 | -444
[5 empty] | 2019-08-04 | 29 | 5173.5 | 1471 | -409 | 1 | 0 | 1880 | 824.4023 | 824.4023 | 824.4023 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -467.9634 | 356.4389 | -3550 | -400 | -3593.5611 | 89.84% | 55.5% | 95% | 0% | 1880 | -409
[5 empty] | 2019-08-04 | 30 | 5174 | 1469 | -404 | 1 | 0 | 1873 | 813.4378 | 813.4378 | 813.4378 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -462.2426 | 351.1952 | -3550 | -400 | -3598.8048 | 89.97% | 55.5% | 95% | 0% | 1873 | -404
[5 empty] | 2019-08-04 | 31 | 5174.5 | 1522 | -364 | 1 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -416.476 | 417.3245 | -3550 | -400 | -3532.6755 | 88.32% | 55.5% | 95% | 0% | 1886 | -364
[5 empty] | 2019-08-04 | 32 | 5175 | 1591 | -338 | 1 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -386.7277 | 514.4265 | -3550 | -400 | -3435.5735 | 85.89% | 55.5% | 95% | 0% | 1929 | -338
[5 empty] | 2019-08-04 | 33 | 5175.5 | 1696 | -284 | 1 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -324.9428 | 656.096 | -3550 | -400 | -3293.904 | 82.35% | 55.5% | 95% | 0% | 1980 | -284
[5 empty] | 2019-08-04 | 34 | 5176 | 1763 | -263 | 1 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -300.9153 | 752.1762 | -3550 | -400 | -3197.8238 | 79.95% | 55.49% | 95% | 0% | 2026 | -263
[5 empty] | 2019-08-04 | 35 | 5176.5 | 1838 | -244 | 1 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -279.1762 | 861.6317 | -3550 | -400 | -3088.3683 | 77.21% | 55.49% | 95% | 0% | 2082 | -244
[5 empty] | 2019-08-04 | 36 | 5177 | 1898 | -207 | 1 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -236.8421 | 939.9922 | -3550 | -400 | -3010.0078 | 75.25% | 55.49% | 95% | 0% | 2105 | -207
[5 empty] | 2019-08-04 | 37 | 5177.5 | 1959 | -171 | 1 | 0 | 2130 | 1215.9934 | 1215.9934 | 1215.9934 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -195.6522 | 1020.3412 | -3550 | -400 | -2929.6588 | 73.24% | 55.48% | 95% | 0% | 2130 | -171
[5 empty] | 2019-08-04 | 38 | 5178 | 2010 | -137 | 1 | 0 | 2147 | 1242.6216 | 1242.6216 | 1242.6216 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -156.7506 | 1085.871 | -3550 | -400 | -2864.129 | 71.6% | 55.48% | 95% | 0% | 2147 | -137
[5 empty] | 2019-08-04 | 39 | 5178.5 | 2014 | -110 | 1 | 0 | 2124 | 1206.5952 | 1206.5952 | 1206.5952 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -125.8581 | 1080.7371 | -3550 | -400 | -2869.2629 | 71.73% | 55.48% | 95% | 0% | 2124 | -110
[5 empty] | 2019-08-04 | 40 | 5179 | 1995 | -91 | 1 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 1175.2679 | 780 | 200 | 2155.2679 | 53.88% | 95% | 0% | -104.119 | 1042.9544 | -3550 | -400 | -2907.0456 | 72.68% | 55.48% | 95% | 0% | 2086 | -91
[5 empty] | 2019-08-04 | 41 | 5179.5 | 2010 | -79 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -90.389 | 1061.3834 | -3550 | -400 | -2888.6166 | 72.22% | 55.48% | 95% | 0% | 2089 | -79
[5 empty] | 2019-08-04 | 42 | 5180 | 2030 | -72 | 1 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -82.3799 | 1089.7553 | -3550 | -400 | -2860.2447 | 71.51% | 55.47% | 95% | 0% | 2102 | -72
[5 empty] | 2019-08-04 | 43 | 5180.5 | 2054 | -73 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -83.524 | 1127.7703 | -3550 | -400 | -2822.2297 | 70.56% | 55.47% | 95% | 0% | 2127 | -73
[5 empty] | 2019-08-04 | 44 | 5181 | 2010 | -73 | 0 | 0 | 2083 | 1142.3743 | 1142.3743 | 1142.3743 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -83.524 | 1058.8503 | -2750 | -200 | -1891.1497 | 47.28% | 55.46% | 95% | 0% | 2083 | -73
[5 empty] | 2019-08-04 | 45 | 5181.5 | 1935 | -74 | 0 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -84.6682 | 941.7951 | -2750 | -200 | -2008.2049 | 50.21% | 55.46% | 95% | 0% | 2009 | -74
[5 empty] | 2019-08-04 | 46 | 5182 | 1822 | -75 | 0 | 0 | 1897 | 851.0305 | 851.0305 | 851.0305 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -85.8124 | 765.2181 | -2750 | -200 | -2184.7819 | 54.62% | 55.45% | 95% | 0% | 1897 | -75
[5 empty] | 2019-08-04 | 47 | 5182.5 | 1685 | -76 | 0 | 0 | 1761 | 638.0049 | 638.0049 | 638.0049 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -86.9565 | 551.0484 | -2750 | -200 | -2398.9516 | 59.97% | 55.45% | 95% | 0% | 1761 | -76
[5 empty] | 2019-08-04 | 48 | 5183 | 1584 | -77 | 0 | 0 | 1661 | 481.3685 | 481.3685 | 481.3685 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -88.1007 | 393.2678 | -2750 | -200 | -2556.7322 | 63.92% | 55.44% | 95% | 0% | 1661 | -77
[5 empty] | 2019-08-05 | 1 | 5183.5 | 1511 | -80 | 0 | 0 | 1591 | 371.723 | 371.723 | 371.723 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -91.5332 | 280.1898 | -2750 | -200 | -2669.8102 | 66.75% | 55.44% | 95% | 0% | 1591 | -80
[5 empty] | 2019-08-05 | 2 | 5184 | 1463 | -83 | 0 | 0 | 1546 | 301.2366 | 301.2366 | 301.2366 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -94.9657 | 206.2709 | -2750 | -200 | -2743.7291 | 68.59% | 55.44% | 95% | 0% | 1546 | -83
[5 empty] | 2019-08-05 | 3 | 5184.5 | 1431 | -82 | 0 | 0 | 1513 | 249.5466 | 249.5466 | 249.5466 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -93.8215 | 155.7251 | -2750 | -200 | -2794.2749 | 69.86% | 55.44% | 95% | 0% | 1513 | -82
[5 empty] | 2019-08-05 | 4 | 5185 | 1418 | -82 | 0 | 0 | 1500 | 229.1838 | 229.1838 | 229.1838 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -93.8215 | 135.3623 | -2750 | -200 | -2814.6377 | 70.37% | 55.44% | 95% | 0% | 1500 | -82
[5 empty] | 2019-08-05 | 5 | 5185.5 | 1394 | -81 | 0 | 0 | 1475 | 190.0247 | 190.0247 | 190.0247 | 1173.7016 | 780 | 200 | 2153.7016 | 53.84% | 95% | 0% | -92.6773 | 97.3474 | -2750 | -200 | -2852.6526 | 71.32% | 55.43% | 95% | 0% | 1475 | -81
[5 empty] | 2019-08-05 | 6 | 5186 | 1382 | -80 | 1 | 0 | 1462 | 169.662 | 169.662 | 169.662 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -91.5332 | 78.1288 | -3550 | -400 | -3871.8712 | 96.8% | 55.42% | 95% | 0% | 1462 | -80
[5 empty] | 2019-08-05 | 7 | 5186.5 | 1374 | -79 | 1 | 0 | 1453 | 155.5647 | 155.5647 | 155.5647 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -90.389 | 65.1757 | -3550 | -400 | -3884.8243 | 97.12% | 55.42% | 95% | 0% | 1453 | -79
[5 empty] | 2019-08-05 | 8 | 5187 | 1374 | -78 | 1 | 0 | 1452 | 153.9984 | 153.9984 | 153.9984 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -89.2449 | 64.7535 | -3550 | -400 | -3885.2465 | 97.13% | 55.42% | 95% | 0% | 1452 | -78
[5 empty] | 2019-08-05 | 9 | 5187.5 | 1383 | -77 | 1 | 0 | 1460 | 166.5293 | 166.5293 | 166.5293 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -88.1007 | 78.4286 | -3550 | -400 | -3871.5714 | 96.79% | 55.42% | 95% | 0% | 1460 | -77
[5 empty] | 2019-08-05 | 10 | 5188 | 1391 | -77 | 1 | 0 | 1468 | 179.0602 | 179.0602 | 179.0602 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -88.1007 | 90.9595 | -3550 | -400 | -3859.0405 | 96.48% | 55.41% | 95% | 0% | 1468 | -77
[5 empty] | 2019-08-05 | 11 | 5188.5 | 1451 | -76 | 1 | 0 | 1527 | 271.4757 | 271.4757 | 271.4757 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -86.9565 | 184.5192 | -3550 | -400 | -3765.4808 | 94.14% | 55.41% | 95% | 0% | 1527 | -76
[5 empty] | 2019-08-05 | 12 | 5189 | 1499 | -76 | 1 | 0 | 1575 | 346.6612 | 346.6612 | 346.6612 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -86.9565 | 259.7046 | -3550 | -400 | -3690.2954 | 92.26% | 55.4% | 95% | 0% | 1575 | -76
[5 empty] | 2019-08-05 | 13 | 5189.5 | 1641 | -84 | 1 | 0 | 1725 | 581.6158 | 581.6158 | 581.6158 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -96.1098 | 485.506 | -3550 | -400 | -3464.494 | 86.61% | 55.4% | 95% | 0% | 1725 | -84
[5 empty] | 2019-08-05 | 14 | 5190 | 1764 | -103 | 1 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -117.849 | 686.1906 | -3550 | -400 | -3263.8094 | 81.6% | 55.4% | 95% | 0% | 1867 | -103
[5 empty] | 2019-08-05 | 15 | 5190.5 | 1897 | -134 | 1 | 0 | 2031 | 1060.9233 | 1060.9233 | 1060.9233 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -153.3181 | 907.6053 | -3550 | -400 | -3042.3947 | 76.06% | 55.4% | 95% | 0% | 2031 | -134
[5 empty] | 2019-08-05 | 16 | 5191 | 1973 | -168 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -192.2197 | 1041.0037 | -3550 | -400 | -2908.9963 | 72.72% | 55.4% | 95% | 0% | 2141 | -168
[5 empty] | 2019-08-05 | 17 | 5191.5 | 2008 | -219 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -250.5721 | 1117.3587 | -3550 | -400 | -2832.6413 | 70.82% | 55.4% | 95% | 0% | 2227 | -219
[5 empty] | 2019-08-05 | 18 | 5192 | 1966 | -282 | 1 | 0 | 2248 | 1400.8244 | 1400.8244 | 1400.8244 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -322.6545 | 1078.1699 | -3550 | -400 | -2871.8301 | 71.8% | 55.39% | 95% | 0% | 2248 | -282
[5 empty] | 2019-08-05 | 19 | 5192.5 | 1937 | -327 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 1172.1352 | 780 | 200 | 2152.1352 | 53.8% | 95% | 0% | -374.1419 | 1051.7444 | -3550 | -400 | -2898.2556 | 72.46% | 55.39% | 95% | 0% | 2264 | -327
[5 empty] | 2019-08-05 | 20 | 5193 | 1857 | -378 | 1 | 0 | 2235 | 1380.4617 | 1380.4617 | 1380.4617 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -432.4943 | 947.9674 | -3550 | -400 | -3002.0326 | 75.05% | 55.39% | 95% | 0% | 2235 | -378
[5 empty] | 2019-08-05 | 21 | 5193.5 | 1745 | -437 | 1 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -500 | 797.4444 | -3550 | -400 | -3152.5556 | 78.81% | 55.39% | 95% | 0% | 2182 | -437
[5 empty] | 2019-08-05 | 22 | 5194 | 1635 | -515 | 1 | 0 | 2150 | 1247.3207 | 1247.3207 | 1247.3207 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -589.2449 | 658.0758 | -3550 | -400 | -3291.9242 | 82.3% | 55.39% | 95% | 0% | 2150 | -515
[5 empty] | 2019-08-05 | 23 | 5194.5 | 1554 | -578 | 1 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -661.3272 | 557.7989 | -3550 | -400 | -3392.2011 | 84.81% | 55.39% | 95% | 0% | 2132 | -578
[5 empty] | 2019-08-05 | 24 | 5195 | 1552 | -568 | 1 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -649.8856 | 550.4442 | -3550 | -400 | -3399.5558 | 84.99% | 55.38% | 95% | 0% | 2120 | -568
[5 empty] | 2019-08-05 | 25 | 5195.5 | 1530 | -586 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -670.4805 | 523.5838 | -3550 | -400 | -3426.4162 | 85.66% | 55.38% | 95% | 0% | 2116 | -586
[5 empty] | 2019-08-05 | 26 | 5196 | 1432 | -652 | 1 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -745.9954 | 397.9452 | -3550 | -400 | -3552.0548 | 88.8% | 55.38% | 95% | 0% | 2084 | -652
[5 empty] | 2019-08-05 | 27 | 5196.5 | 1412 | -643 | 1 | 0 | 2055 | 1098.5161 | 1098.5161 | 1098.5161 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -735.6979 | 362.8181 | -3550 | -400 | -3587.1819 | 89.68% | 55.37% | 95% | 0% | 2055 | -643
[5 empty] | 2019-08-05 | 28 | 5197 | 1386 | -647 | 1 | 0 | 2033 | 1064.0561 | 1064.0561 | 1064.0561 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -740.2746 | 323.7815 | -3550 | -400 | -3626.2185 | 90.66% | 55.37% | 95% | 0% | 2033 | -647
[5 empty] | 2019-08-05 | 29 | 5197.5 | 1412 | -615 | 1 | 0 | 2027 | 1054.6579 | 1054.6579 | 1054.6579 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -703.6613 | 350.9965 | -3550 | -400 | -3599.0035 | 89.98% | 55.36% | 95% | 0% | 2027 | -615
[5 empty] | 2019-08-05 | 30 | 5198 | 1386 | -642 | 1 | 0 | 2028 | 1056.2242 | 1056.2242 | 1056.2242 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -734.5538 | 321.6705 | -3550 | -400 | -3628.3295 | 90.71% | 55.35% | 95% | 0% | 2028 | -642
[5 empty] | 2019-08-05 | 31 | 5198.5 | 1424 | -597 | 1 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -683.0664 | 362.1933 | -3550 | -400 | -3587.8067 | 89.7% | 55.35% | 95% | 0% | 2021 | -597
[5 empty] | 2019-08-05 | 32 | 5199 | 1474 | -573 | 1 | 0 | 2047 | 1085.9852 | 1085.9852 | 1085.9852 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -655.6064 | 430.3788 | -3550 | -400 | -3519.6212 | 87.99% | 55.35% | 95% | 0% | 2047 | -573
[5 empty] | 2019-08-05 | 33 | 5199.5 | 1563 | -536 | 1 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -613.2723 | 554.1638 | -3550 | -400 | -3395.8362 | 84.9% | 55.35% | 95% | 0% | 2099 | -536
[5 empty] | 2019-08-05 | 34 | 5200 | 1689 | -478 | 1 | 0 | 2167 | 1273.9489 | 1273.9489 | 1273.9489 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -546.9108 | 727.0381 | -3550 | -400 | -3222.9619 | 80.57% | 55.34% | 95% | 0% | 2167 | -478
[5 empty] | 2019-08-05 | 35 | 5200.5 | 1826 | -411 | 1 | 0 | 2237 | 1383.5944 | 1383.5944 | 1383.5944 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -470.2517 | 913.3427 | -3550 | -400 | -3036.6573 | 75.92% | 55.34% | 95% | 0% | 2237 | -411
[5 empty] | 2019-08-05 | 36 | 5201 | 1922 | -361 | 1 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -413.0435 | 1042.6037 | -3550 | -400 | -2907.3963 | 72.68% | 55.34% | 95% | 0% | 2283 | -361
[5 empty] | 2019-08-05 | 37 | 5201.5 | 2033 | -288 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -329.5195 | 1185.6496 | -3550 | -400 | -2764.3504 | 69.11% | 55.33% | 95% | 0% | 2321 | -288
[5 empty] | 2019-08-05 | 38 | 5202 | 2135 | -213 | 1 | 0 | 2348 | 1557.4608 | 1557.4608 | 1557.4608 | 1170.5688 | 780 | 200 | 2150.5688 | 53.76% | 95% | 0% | -243.7071 | 1313.7537 | -3550 | -400 | -2636.2463 | 65.91% | 55.32% | 95% | 0% | 2348 | -213
[5 empty] | 2019-08-05 | 39 | 5202.5 | 2186 | -162 | 1 | 0 | 2348 | 1557.4608 | 1557.4608 | 1557.4608 | 1169.0025 | 780 | 200 | 2149.0025 | 53.73% | 95% | 0% | -185.3547 | 1372.1061 | -3550 | -400 | -2577.8939 | 64.45% | 55.32% | 95% | 0% | 2348 | -162
[5 empty] | 2019-08-05 | 40 | 5203 | 2202 | -130 | 1 | 0 | 2332 | 1532.399 | 1532.399 | 1532.399 | 1169.0025 | 780 | 200 | 2149.0025 | 53.73% | 95% | 0% | -148.7414 | 1383.6576 | -3550 | -400 | -2566.3424 | 64.16% | 55.32% | 95% | 0% | 2332 | -130
[5 empty] | 2019-08-05 | 41 | 5203.5 | 2202 | -105 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1169.0025 | 780 | 200 | 2149.0025 | 53.73% | 95% | 0% | -120.1373 | 1373.1026 | -3550 | -400 | -2576.8974 | 64.42% | 55.31% | 95% | 0% | 2307 | -105
[5 empty] | 2019-08-05 | 42 | 5204 | 2199 | -92 | 1 | 0 | 2291 | 1468.1781 | 1468.1781 | 1468.1781 | 1169.0025 | 780 | 200 | 2149.0025 | 53.73% | 95% | 0% | -105.2632 | 1362.9149 | -3550 | -400 | -2587.0851 | 64.68% | 55.3% | 95% | 0% | 2291 | -92
[5 empty] | 2019-08-05 | 43 | 5204.5 | 2219 | -90 | 1 | 0 | 2309 | 1496.3726 | 1496.3726 | 1496.3726 | 1169.0025 | 780 | 200 | 2149.0025 | 53.73% | 95% | 0% | -102.9748 | 1393.3978 | -3550 | -400 | -2556.6022 | 63.92% | 55.3% | 95% | 0% | 2309 | -90
[5 empty] | 2019-08-05 | 44 | 5205 | 2144 | -90 | 0 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 1169.0025 | 780 | 200 | 2149.0025 | 53.73% | 95% | 0% | -102.9748 | 1275.9205 | -2750 | -200 | -1674.0795 | 41.85% | 55.29% | 95% | 0% | 2234 | -90
[5 empty] | 2019-08-05 | 45 | 5205.5 | 2026 | -89 | 0 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 1169.0025 | 780 | 200 | 2149.0025 | 53.73% | 95% | 0% | -101.8307 | 1090.6673 | -2750 | -200 | -1859.3327 | 46.48% | 55.29% | 95% | 0% | 2115 | -89
[5 empty] | 2019-08-05 | 46 | 5206 | 1889 | -89 | 0 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 1169.0025 | 780 | 200 | 2149.0025 | 53.73% | 95% | 0% | -101.8307 | 876.0754 | -2750 | -200 | -2073.9246 | 51.85% | 55.29% | 95% | 0% | 1978 | -89
[5 empty] | 2019-08-05 | 47 | 5206.5 | 1752 | -89 | 0 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 1169.0025 | 780 | 200 | 2149.0025 | 53.73% | 95% | 0% | -101.8307 | 661.4834 | -2750 | -200 | -2288.5166 | 57.21% | 55.28% | 95% | 0% | 1841 | -89
[5 empty] | 2019-08-05 | 48 | 5207 | 1643 | -89 | 0 | 0 | 1732 | 592.5804 | 592.5804 | 592.5804 | 1169.0025 | 780 | 200 | 2149.0025 | 53.73% | 95% | 0% | -101.8307 | 490.7497 | -2750 | -200 | -2459.2503 | 61.48% | 55.28% | 95% | 0% | 1732 | -89
[5 empty] | 2019-08-06 | 1 | 5207.5 | 1556 | -89 | 0 | 0 | 1645 | 456.3067 | 456.3067 | 456.3067 | 1169.0025 | 780 | 200 | 2149.0025 | 53.73% | 95% | 0% | -101.8307 | 354.476 | -2750 | -200 | -2595.524 | 64.89% | 55.28% | 95% | 0% | 1645 | -89
[5 empty] | 2019-08-06 | 2 | 5208 | 1504 | -88 | 0 | 0 | 1592 | 373.2894 | 373.2894 | 373.2894 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -100.6865 | 272.6029 | -2750 | -200 | -2677.3971 | 66.93% | 55.28% | 95% | 0% | 1592 | -88
[5 empty] | 2019-08-06 | 3 | 5208.5 | 1465 | -88 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -100.6865 | 211.5147 | -2750 | -200 | -2738.4853 | 68.46% | 55.28% | 95% | 0% | 1553 | -88
[5 empty] | 2019-08-06 | 4 | 5209 | 1445 | -87 | 1 | 0 | 1532 | 279.3075 | 279.3075 | 279.3075 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -99.5423 | 179.7652 | -3550 | -400 | -3770.2348 | 94.26% | 55.28% | 95% | 0% | 1532 | -87
[5 empty] | 2019-08-06 | 5 | 5209.5 | 1418 | -87 | 1 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -99.5423 | 137.4733 | -3550 | -400 | -3812.5267 | 95.31% | 55.27% | 95% | 0% | 1505 | -87
[5 empty] | 2019-08-06 | 6 | 5210 | 1397 | -87 | 1 | 0 | 1484 | 204.122 | 204.122 | 204.122 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -99.5423 | 104.5797 | -3550 | -400 | -3845.4203 | 96.14% | 55.27% | 95% | 0% | 1484 | -87
[5 empty] | 2019-08-06 | 7 | 5210.5 | 1380 | -88 | 1 | 0 | 1468 | 179.0602 | 179.0602 | 179.0602 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -100.6865 | 78.3737 | -3550 | -400 | -3871.6263 | 96.79% | 55.27% | 95% | 0% | 1468 | -88
[5 empty] | 2019-08-06 | 8 | 5211 | 1377 | -88 | 1 | 0 | 1465 | 174.3611 | 174.3611 | 174.3611 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -100.6865 | 73.6746 | -3550 | -400 | -3876.3254 | 96.91% | 55.27% | 95% | 0% | 1465 | -88
[5 empty] | 2019-08-06 | 9 | 5211.5 | 1377 | -88 | 1 | 0 | 1465 | 174.3611 | 174.3611 | 174.3611 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -100.6865 | 73.6746 | -3550 | -400 | -3876.3254 | 96.91% | 55.25% | 95% | 0% | 1465 | -88
[5 empty] | 2019-08-06 | 10 | 5212 | 1397 | -87 | 1 | 0 | 1484 | 204.122 | 204.122 | 204.122 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -99.5423 | 104.5797 | -3550 | -400 | -3845.4203 | 96.14% | 55.25% | 95% | 0% | 1484 | -87
[5 empty] | 2019-08-06 | 11 | 5212.5 | 1431 | -87 | 1 | 0 | 1518 | 257.3784 | 257.3784 | 257.3784 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -99.5423 | 157.8361 | -3550 | -400 | -3792.1639 | 94.8% | 55.24% | 95% | 0% | 1518 | -87
[5 empty] | 2019-08-06 | 12 | 5213 | 1478 | -88 | 1 | 0 | 1566 | 332.5639 | 332.5639 | 332.5639 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -100.6865 | 231.8774 | -3550 | -400 | -3718.1226 | 92.95% | 55.24% | 95% | 0% | 1566 | -88
[5 empty] | 2019-08-06 | 13 | 5213.5 | 1610 | -102 | 1 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -116.7048 | 444.5483 | -3550 | -400 | -3505.4517 | 87.64% | 55.23% | 95% | 0% | 1712 | -102
[5 empty] | 2019-08-06 | 14 | 5214 | 1719 | -133 | 1 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -152.1739 | 628.3702 | -3550 | -400 | -3321.6298 | 83.04% | 55.23% | 95% | 0% | 1852 | -133
[5 empty] | 2019-08-06 | 15 | 5214.5 | 1833 | -176 | 1 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 1167.4361 | 780 | 200 | 2147.4361 | 53.69% | 95% | 0% | -201.373 | 825.0903 | -3550 | -400 | -3124.9097 | 78.12% | 55.23% | 95% | 0% | 2009 | -176
[5 empty] | 2019-08-06 | 16 | 5215 | 1883 | -219 | 1 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 1165.8697 | 780 | 200 | 2145.8697 | 53.65% | 95% | 0% | -250.5721 | 921.5631 | -3550 | -400 | -3028.4369 | 75.71% | 55.23% | 95% | 0% | 2102 | -219
[5 empty] | 2019-08-06 | 17 | 5215.5 | 1904 | -284 | 1 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 1165.8697 | 780 | 200 | 2145.8697 | 53.65% | 95% | 0% | -324.9428 | 981.8997 | -3550 | -400 | -2968.1003 | 74.2% | 55.23% | 95% | 0% | 2188 | -284
[5 empty] | 2019-08-06 | 18 | 5216 | 1891 | -327 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 1165.8697 | 780 | 200 | 2145.8697 | 53.65% | 95% | 0% | -374.1419 | 979.6916 | -3550 | -400 | -2970.3084 | 74.26% | 55.22% | 95% | 0% | 2218 | -327
[5 empty] | 2019-08-06 | 19 | 5216.5 | 1866 | -365 | 1 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 1165.8697 | 780 | 200 | 2145.8697 | 53.65% | 95% | 0% | -417.6201 | 956.5761 | -3550 | -400 | -2993.4239 | 74.84% | 55.22% | 95% | 0% | 2231 | -365
[5 empty] | 2019-08-06 | 20 | 5217 | 1829 | -389 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 1165.8697 | 780 | 200 | 2145.8697 | 53.65% | 95% | 0% | -445.0801 | 908.7534 | -3550 | -400 | -3041.2466 | 76.03% | 55.22% | 95% | 0% | 2218 | -389
[5 empty] | 2019-08-06 | 21 | 5217.5 | 1797 | -411 | 1 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 1165.8697 | 780 | 200 | 2145.8697 | 53.65% | 95% | 0% | -470.2517 | 867.9181 | -3550 | -400 | -3082.0819 | 77.05% | 55.22% | 95% | 0% | 2208 | -411
[5 empty] | 2019-08-06 | 22 | 5218 | 1754 | -439 | 1 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 1165.8697 | 780 | 200 | 2145.8697 | 53.65% | 95% | 0% | -502.2883 | 812.386 | -3550 | -400 | -3137.614 | 78.44% | 55.22% | 95% | 0% | 2193 | -439
[5 empty] | 2019-08-06 | 23 | 5218.5 | 1714 | -476 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1165.8697 | 780 | 200 | 2145.8697 | 53.65% | 95% | 0% | -544.6224 | 765.3528 | -3550 | -400 | -3184.6472 | 79.62% | 55.21% | 95% | 0% | 2190 | -476
[5 empty] | 2019-08-06 | 24 | 5219 | 1688 | -485 | 1 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 1165.8697 | 780 | 200 | 2145.8697 | 53.65% | 95% | 0% | -554.9199 | 728.4272 | -3550 | -400 | -3221.5728 | 80.54% | 55.21% | 95% | 0% | 2173 | -485
[5 empty] | 2019-08-06 | 25 | 5219.5 | 1681 | -486 | 1 | 0 | 2167 | 1273.9489 | 1273.9489 | 1273.9489 | 1165.8697 | 780 | 200 | 2145.8697 | 53.65% | 95% | 0% | -556.0641 | 717.8848 | -3550 | -400 | -3232.1152 | 80.8% | 55.21% | 95% | 0% | 2167 | -486
[5 empty] | 2019-08-06 | 26 | 5220 | 1621 | -516 | 1 | 0 | 2137 | 1226.958 | 1226.958 | 1226.958 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -590.389 | 636.5689 | -3550 | -400 | -3313.4311 | 82.84% | 55.21% | 95% | 0% | 2137 | -516
[5 empty] | 2019-08-06 | 27 | 5220.5 | 1549 | -559 | 1 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -639.5881 | 541.9453 | -3550 | -400 | -3408.0547 | 85.2% | 55.19% | 95% | 0% | 2108 | -559
[5 empty] | 2019-08-06 | 28 | 5221 | 1582 | -516 | 1 | 0 | 2098 | 1165.8697 | 1165.8697 | 1165.8697 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -590.389 | 575.4807 | -3550 | -400 | -3374.5193 | 84.36% | 55.19% | 95% | 0% | 2098 | -516
[5 empty] | 2019-08-06 | 29 | 5221.5 | 1595 | -512 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -585.8124 | 594.1547 | -3550 | -400 | -3355.8453 | 83.9% | 55.18% | 95% | 0% | 2107 | -512
[5 empty] | 2019-08-06 | 30 | 5222 | 1590 | -517 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -591.5332 | 588.4338 | -3550 | -400 | -3361.5662 | 84.04% | 55.18% | 95% | 0% | 2107 | -517
[5 empty] | 2019-08-06 | 31 | 5222.5 | 1601 | -497 | 1 | 0 | 2098 | 1165.8697 | 1165.8697 | 1165.8697 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -568.6499 | 597.2199 | -3550 | -400 | -3352.7801 | 83.82% | 55.18% | 95% | 0% | 2098 | -497
[5 empty] | 2019-08-06 | 32 | 5223 | 1645 | -471 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -538.9016 | 655.1627 | -3550 | -400 | -3294.8373 | 82.37% | 55.17% | 95% | 0% | 2116 | -471
[5 empty] | 2019-08-06 | 33 | 5223.5 | 1716 | -427 | 1 | 0 | 2143 | 1236.3561 | 1236.3561 | 1236.3561 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -488.5584 | 747.7978 | -3550 | -400 | -3202.2022 | 80.06% | 55.16% | 95% | 0% | 2143 | -427
[5 empty] | 2019-08-06 | 34 | 5224 | 1788 | -428 | 1 | 0 | 2216 | 1350.7007 | 1350.7007 | 1350.7007 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -489.7025 | 860.9982 | -3550 | -400 | -3089.0018 | 77.23% | 55.15% | 95% | 0% | 2216 | -428
[5 empty] | 2019-08-06 | 35 | 5224.5 | 1878 | -386 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -441.6476 | 984.2386 | -3550 | -400 | -2965.7614 | 74.14% | 55.15% | 95% | 0% | 2264 | -386
[5 empty] | 2019-08-06 | 36 | 5225 | 1960 | -329 | 1 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -376.4302 | 1088.6151 | -3550 | -400 | -2861.3849 | 71.53% | 55.15% | 95% | 0% | 2289 | -329
[5 empty] | 2019-08-06 | 37 | 5225.5 | 2057 | -268 | 1 | 0 | 2325 | 1521.4345 | 1521.4345 | 1521.4345 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -306.6362 | 1214.7983 | -3550 | -400 | -2735.2017 | 68.38% | 55.15% | 95% | 0% | 2325 | -268
[5 empty] | 2019-08-06 | 38 | 5226 | 2138 | -207 | 1 | 0 | 2345 | 1552.7617 | 1552.7617 | 1552.7617 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -236.8421 | 1315.9196 | -3550 | -400 | -2634.0804 | 65.85% | 55.14% | 95% | 0% | 2345 | -207
[5 empty] | 2019-08-06 | 39 | 5226.5 | 2184 | -160 | 1 | 0 | 2344 | 1551.1954 | 1551.1954 | 1551.1954 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -183.0664 | 1368.129 | -3550 | -400 | -2581.871 | 64.55% | 55.14% | 95% | 0% | 2344 | -160
[5 empty] | 2019-08-06 | 40 | 5227 | 2204 | -126 | 1 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -144.1648 | 1385.1015 | -3550 | -400 | -2564.8985 | 64.12% | 55.13% | 95% | 0% | 2330 | -126
[5 empty] | 2019-08-06 | 41 | 5227.5 | 2196 | -100 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1164.3034 | 780 | 200 | 2144.3034 | 53.61% | 95% | 0% | -114.4165 | 1361.5934 | -3550 | -400 | -2588.4066 | 64.71% | 55.13% | 95% | 0% | 2296 | -100
[5 empty] | 2019-08-06 | 42 | 5228 | 2197 | -89 | 1 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -101.8307 | 1358.5156 | -3550 | -400 | -2591.4844 | 64.79% | 55.12% | 95% | 0% | 2286 | -89
[5 empty] | 2019-08-06 | 43 | 5228.5 | 2203 | -88 | 1 | 0 | 2291 | 1468.1781 | 1468.1781 | 1468.1781 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -100.6865 | 1367.4916 | -3550 | -400 | -2582.5084 | 64.56% | 55.11% | 95% | 0% | 2291 | -88
[5 empty] | 2019-08-06 | 44 | 5229 | 2125 | -86 | 0 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -98.3982 | 1244.4708 | -2750 | -200 | -1705.5292 | 42.64% | 55.1% | 95% | 0% | 2211 | -86
[5 empty] | 2019-08-06 | 45 | 5229.5 | 1995 | -86 | 0 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -98.3982 | 1040.8434 | -2750 | -200 | -1909.1566 | 47.73% | 55.1% | 95% | 0% | 2081 | -86
[5 empty] | 2019-08-06 | 46 | 5230 | 1872 | -86 | 0 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -98.3982 | 848.1806 | -2750 | -200 | -2101.8194 | 52.55% | 55.1% | 95% | 0% | 1958 | -86
[5 empty] | 2019-08-06 | 47 | 5230.5 | 1738 | -87 | 0 | 0 | 1825 | 738.2523 | 738.2523 | 738.2523 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -99.5423 | 638.7099 | -2750 | -200 | -2311.2901 | 57.78% | 55.09% | 95% | 0% | 1825 | -87
[5 empty] | 2019-08-06 | 48 | 5231 | 1625 | -87 | 0 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -99.5423 | 461.7108 | -2750 | -200 | -2488.2892 | 62.21% | 55.09% | 95% | 0% | 1712 | -87
[5 empty] | 2019-08-07 | 1 | 5231.5 | 1531 | -88 | 0 | 0 | 1619 | 415.5812 | 415.5812 | 415.5812 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -100.6865 | 314.8947 | -2750 | -200 | -2635.1053 | 65.88% | 55.08% | 95% | 0% | 1619 | -88
[5 empty] | 2019-08-07 | 2 | 5232 | 1479 | -89 | 0 | 0 | 1568 | 335.6966 | 335.6966 | 335.6966 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -101.8307 | 233.866 | -2750 | -200 | -2716.134 | 67.9% | 55.08% | 95% | 0% | 1568 | -89
[5 empty] | 2019-08-07 | 3 | 5232.5 | 1444 | -90 | 0 | 0 | 1534 | 282.4402 | 282.4402 | 282.4402 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -102.9748 | 179.4654 | -2750 | -200 | -2770.5346 | 69.26% | 55.08% | 95% | 0% | 1534 | -90
[5 empty] | 2019-08-07 | 4 | 5233 | 1416 | -90 | 0 | 0 | 1506 | 238.582 | 238.582 | 238.582 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -102.9748 | 135.6072 | -2750 | -200 | -2814.3928 | 70.36% | 55.07% | 95% | 0% | 1506 | -90
[5 empty] | 2019-08-07 | 5 | 5233.5 | 1385 | -91 | 0 | 0 | 1476 | 191.5911 | 191.5911 | 191.5911 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -104.119 | 87.4721 | -2750 | -200 | -2862.5279 | 71.56% | 55.07% | 95% | 0% | 1476 | -91
[5 empty] | 2019-08-07 | 6 | 5234 | 1355 | -91 | 0 | 0 | 1446 | 144.6002 | 144.6002 | 144.6002 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -104.119 | 40.4812 | -2750 | -200 | -2909.5188 | 72.74% | 55.07% | 95% | 0% | 1446 | -91
[5 empty] | 2019-08-07 | 7 | 5234.5 | 1342 | -92 | 0 | 0 | 1434 | 125.8038 | 125.8038 | 125.8038 | 1162.737 | 780 | 200 | 2142.737 | 53.57% | 95% | 0% | -105.2632 | 20.5406 | -2750 | -200 | -2929.4594 | 73.24% | 55.06% | 95% | 0% | 1434 | -92
[5 empty] | 2019-08-07 | 8 | 5235 | 1343 | -92 | 0 | 0 | 1435 | 127.3702 | 127.3702 | 127.3702 | 1161.1707 | 780 | 200 | 2141.1707 | 53.53% | 95% | 0% | -105.2632 | 22.107 | -2750 | -200 | -2927.893 | 73.2% | 55.06% | 95% | 0% | 1435 | -92
[5 empty] | 2019-08-07 | 9 | 5235.5 | 1353 | -93 | 0 | 0 | 1446 | 144.6002 | 144.6002 | 144.6002 | 1161.1707 | 780 | 200 | 2141.1707 | 53.53% | 95% | 0% | -106.4073 | 38.1928 | -2750 | -200 | -2911.8072 | 72.8% | 55.05% | 95% | 0% | 1446 | -93
[5 empty] | 2019-08-07 | 10 | 5236 | 1360 | -93 | 0 | 0 | 1453 | 155.5647 | 155.5647 | 155.5647 | 1161.1707 | 780 | 200 | 2141.1707 | 53.53% | 95% | 0% | -106.4073 | 49.1574 | -2750 | -200 | -2900.8426 | 72.52% | 55.03% | 95% | 0% | 1453 | -93
[5 empty] | 2019-08-07 | 11 | 5236.5 | 1399 | -94 | 0 | 0 | 1493 | 218.2193 | 218.2193 | 218.2193 | 1161.1707 | 780 | 200 | 2141.1707 | 53.53% | 95% | 0% | -107.5515 | 110.6678 | -2750 | -200 | -2839.3322 | 70.98% | 55.03% | 95% | 0% | 1493 | -94
[5 empty] | 2019-08-07 | 12 | 5237 | 1441 | -96 | 0 | 0 | 1537 | 287.1393 | 287.1393 | 287.1393 | 1161.1707 | 780 | 200 | 2141.1707 | 53.53% | 95% | 0% | -109.8398 | 177.2995 | -2750 | -200 | -2772.7005 | 69.32% | 55.03% | 95% | 0% | 1537 | -96
[5 empty] | 2019-08-07 | 13 | 5237.5 | 1579 | -111 | 0 | 0 | 1690 | 526.7931 | 526.7931 | 526.7931 | 1161.1707 | 780 | 200 | 2141.1707 | 53.53% | 95% | 0% | -127.0023 | 399.7908 | -2750 | -200 | -2550.2092 | 63.76% | 55.02% | 95% | 0% | 1690 | -111
[5 empty] | 2019-08-07 | 14 | 5238 | 1683 | -142 | 0 | 0 | 1825 | 738.2523 | 738.2523 | 738.2523 | 1161.1707 | 780 | 200 | 2141.1707 | 53.53% | 95% | 0% | -162.4714 | 575.7809 | -2750 | -200 | -2374.2191 | 59.36% | 55.02% | 95% | 0% | 1825 | -142
[5 empty] | 2019-08-07 | 15 | 5238.5 | 1813 | -180 | 0 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 1161.1707 | 780 | 200 | 2141.1707 | 53.53% | 95% | 0% | -205.9497 | 795.4518 | -2750 | -200 | -2154.5482 | 53.86% | 55.02% | 95% | 0% | 1993 | -180
[5 empty] | 2019-08-07 | 16 | 5239 | 1864 | -226 | 1 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 1161.1707 | 780 | 200 | 2141.1707 | 53.53% | 95% | 0% | -258.5812 | 894.7576 | -3550 | -400 | -3055.2424 | 76.38% | 55.01% | 95% | 0% | 2090 | -226
[5 empty] | 2019-08-07 | 17 | 5239.5 | 1884 | -281 | 1 | 0 | 2165 | 1270.8162 | 1270.8162 | 1270.8162 | 1161.1707 | 780 | 200 | 2141.1707 | 53.53% | 95% | 0% | -321.5103 | 949.3059 | -3550 | -400 | -3000.6941 | 75.02% | 55.01% | 95% | 0% | 2165 | -281
[5 empty] | 2019-08-07 | 18 | 5240 | 1844 | -324 | 1 | 0 | 2168 | 1275.5153 | 1275.5153 | 1275.5153 | 1161.1707 | 780 | 200 | 2141.1707 | 53.53% | 95% | 0% | -370.7094 | 904.8059 | -3550 | -400 | -3045.1941 | 76.13% | 55% | 95% | 0% | 2168 | -324
[5 empty] | 2019-08-07 | 19 | 5240.5 | 1802 | -381 | 1 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 1161.1707 | 780 | 200 | 2141.1707 | 53.53% | 95% | 0% | -435.9268 | 863.0839 | -3550 | -400 | -3086.9161 | 77.17% | 55% | 95% | 0% | 2183 | -381
[5 empty] | 2019-08-07 | 20 | 5241 | 1694 | -458 | 1 | 0 | 2152 | 1250.4534 | 1250.4534 | 1250.4534 | 1159.6043 | 780 | 200 | 2139.6043 | 53.49% | 95% | 0% | -524.0275 | 726.426 | -3550 | -400 | -3223.574 | 80.59% | 55% | 95% | 0% | 2152 | -458
[5 empty] | 2019-08-07 | 21 | 5241.5 | 1648 | -471 | 1 | 0 | 2119 | 1198.7634 | 1198.7634 | 1198.7634 | 1159.6043 | 780 | 200 | 2139.6043 | 53.49% | 95% | 0% | -538.9016 | 659.8618 | -3550 | -400 | -3290.1382 | 82.25% | 55% | 95% | 0% | 2119 | -471
[5 empty] | 2019-08-07 | 22 | 5242 | 1575 | -524 | 1 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 1159.6043 | 780 | 200 | 2139.6043 | 53.49% | 95% | 0% | -599.5423 | 567.8938 | -3550 | -400 | -3382.1062 | 84.55% | 55% | 95% | 0% | 2099 | -524
[5 empty] | 2019-08-07 | 23 | 5242.5 | 1572 | -539 | 1 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 1159.6043 | 780 | 200 | 2139.6043 | 53.49% | 95% | 0% | -616.7048 | 569.5277 | -3550 | -400 | -3380.4723 | 84.51% | 54.99% | 95% | 0% | 2111 | -539
[5 empty] | 2019-08-07 | 24 | 5243 | 1553 | -548 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 1159.6043 | 780 | 200 | 2139.6043 | 53.49% | 95% | 0% | -627.0023 | 543.5665 | -3550 | -400 | -3406.4335 | 85.16% | 54.99% | 95% | 0% | 2101 | -548
[5 empty] | 2019-08-07 | 25 | 5243.5 | 1541 | -562 | 1 | 0 | 2103 | 1173.7016 | 1173.7016 | 1173.7016 | 1159.6043 | 780 | 200 | 2139.6043 | 53.49% | 95% | 0% | -643.0206 | 530.681 | -3550 | -400 | -3419.319 | 85.48% | 54.99% | 95% | 0% | 2103 | -562
[5 empty] | 2019-08-07 | 26 | 5244 | 1538 | -542 | 1 | 0 | 2080 | 1137.6752 | 1137.6752 | 1137.6752 | 1159.6043 | 780 | 200 | 2139.6043 | 53.49% | 95% | 0% | -620.1373 | 517.5379 | -3550 | -400 | -3432.4621 | 85.81% | 54.98% | 95% | 0% | 2080 | -542
[5 empty] | 2019-08-07 | 27 | 5244.5 | 1535 | -534 | 1 | 0 | 2069 | 1120.4452 | 1120.4452 | 1120.4452 | 1159.6043 | 780 | 200 | 2139.6043 | 53.49% | 95% | 0% | -610.984 | 509.4612 | -3550 | -400 | -3440.5388 | 86.01% | 54.98% | 95% | 0% | 2069 | -534
[5 empty] | 2019-08-07 | 28 | 5245 | 1487 | -551 | 1 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 1159.6043 | 780 | 200 | 2139.6043 | 53.49% | 95% | 0% | -630.4348 | 441.4531 | -3550 | -400 | -3508.5469 | 87.71% | 54.97% | 95% | 0% | 2038 | -551
[5 empty] | 2019-08-07 | 29 | 5245.5 | 1493 | -541 | 1 | 0 | 2034 | 1065.6224 | 1065.6224 | 1065.6224 | 1159.6043 | 780 | 200 | 2139.6043 | 53.49% | 95% | 0% | -618.9931 | 446.6293 | -3550 | -400 | -3503.3707 | 87.58% | 54.97% | 95% | 0% | 2034 | -541
[5 empty] | 2019-08-07 | 30 | 5246 | 1481 | -530 | 1 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 1159.6043 | 780 | 200 | 2139.6043 | 53.49% | 95% | 0% | -606.4073 | 423.1887 | -3550 | -400 | -3526.8113 | 88.17% | 54.97% | 95% | 0% | 2011 | -530
[5 empty] | 2019-08-07 | 31 | 5246.5 | 1477 | -549 | 1 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 1158.0379 | 780 | 200 | 2138.0379 | 53.45% | 95% | 0% | -628.1465 | 424.9451 | -3550 | -400 | -3525.0549 | 88.13% | 54.97% | 95% | 0% | 2026 | -549
[5 empty] | 2019-08-07 | 32 | 5247 | 1498 | -543 | 1 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 1158.0379 | 780 | 200 | 2138.0379 | 53.45% | 95% | 0% | -621.2815 | 455.3055 | -3550 | -400 | -3494.6945 | 87.37% | 54.97% | 95% | 0% | 2041 | -543
[5 empty] | 2019-08-07 | 33 | 5247.5 | 1581 | -494 | 1 | 0 | 2075 | 1129.8434 | 1129.8434 | 1129.8434 | 1158.0379 | 780 | 200 | 2138.0379 | 53.45% | 95% | 0% | -565.2174 | 564.626 | -3550 | -400 | -3385.374 | 84.63% | 54.97% | 95% | 0% | 2075 | -494
[5 empty] | 2019-08-07 | 34 | 5248 | 1685 | -442 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 1158.0379 | 780 | 200 | 2138.0379 | 53.45% | 95% | 0% | -505.7208 | 705.5735 | -3550 | -400 | -3244.4265 | 81.11% | 54.96% | 95% | 0% | 2127 | -442
[5 empty] | 2019-08-07 | 35 | 5248.5 | 1799 | -399 | 1 | 0 | 2198 | 1322.5062 | 1322.5062 | 1322.5062 | 1158.0379 | 780 | 200 | 2138.0379 | 53.45% | 95% | 0% | -456.5217 | 865.9844 | -3550 | -400 | -3084.0156 | 77.1% | 54.96% | 95% | 0% | 2198 | -399
[5 empty] | 2019-08-07 | 36 | 5249 | 1900 | -340 | 1 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 1156.4716 | 780 | 200 | 2136.4716 | 53.41% | 95% | 0% | -389.016 | 999.2775 | -3550 | -400 | -2950.7225 | 73.77% | 54.96% | 95% | 0% | 2240 | -340
[5 empty] | 2019-08-07 | 37 | 5249.5 | 1970 | -298 | 1 | 0 | 2268 | 1432.1517 | 1432.1517 | 1432.1517 | 1156.4716 | 780 | 200 | 2136.4716 | 53.41% | 95% | 0% | -340.9611 | 1091.1906 | -3550 | -400 | -2858.8094 | 71.47% | 54.96% | 95% | 0% | 2268 | -298
[5 empty] | 2019-08-07 | 38 | 5250 | 2058 | -240 | 1 | 0 | 2298 | 1479.1426 | 1479.1426 | 1479.1426 | 1156.4716 | 780 | 200 | 2136.4716 | 53.41% | 95% | 0% | -274.5995 | 1204.5431 | -3550 | -400 | -2745.4569 | 68.64% | 54.96% | 95% | 0% | 2298 | -240
[5 empty] | 2019-08-07 | 39 | 5250.5 | 2113 | -193 | 1 | 0 | 2306 | 1491.6735 | 1491.6735 | 1491.6735 | 1156.4716 | 780 | 200 | 2136.4716 | 53.41% | 95% | 0% | -220.8238 | 1270.8497 | -3550 | -400 | -2679.1503 | 66.98% | 54.95% | 95% | 0% | 2306 | -193
[5 empty] | 2019-08-07 | 40 | 5251 | 2159 | -144 | 1 | 0 | 2303 | 1486.9744 | 1486.9744 | 1486.9744 | 1156.4716 | 780 | 200 | 2136.4716 | 53.41% | 95% | 0% | -164.7597 | 1322.2147 | -3550 | -400 | -2627.7853 | 65.69% | 54.95% | 95% | 0% | 2303 | -144
[5 empty] | 2019-08-07 | 41 | 5251.5 | 2159 | -114 | 1 | 0 | 2273 | 1439.9835 | 1439.9835 | 1439.9835 | 1156.4716 | 780 | 200 | 2136.4716 | 53.41% | 95% | 0% | -130.4348 | 1309.5487 | -3550 | -400 | -2640.4513 | 66.01% | 54.95% | 95% | 0% | 2273 | -114
[5 empty] | 2019-08-07 | 42 | 5252 | 2139 | -101 | 1 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 1156.4716 | 780 | 200 | 2136.4716 | 53.41% | 95% | 0% | -115.5606 | 1272.7328 | -3550 | -400 | -2677.2672 | 66.93% | 54.94% | 95% | 0% | 2240 | -101
[5 empty] | 2019-08-07 | 43 | 5252.5 | 2161 | -99 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 1156.4716 | 780 | 200 | 2136.4716 | 53.41% | 95% | 0% | -113.2723 | 1306.3485 | -3550 | -400 | -2643.6515 | 66.09% | 54.93% | 95% | 0% | 2260 | -99
[5 empty] | 2019-08-07 | 44 | 5253 | 2101 | -97 | 1 | 0 | 2198 | 1322.5062 | 1322.5062 | 1322.5062 | 1156.4716 | 780 | 200 | 2136.4716 | 53.41% | 95% | 0% | -110.984 | 1211.5222 | -3550 | -400 | -2738.4778 | 68.46% | 54.93% | 95% | 0% | 2198 | -97
[5 empty] | 2019-08-07 | 45 | 5253.5 | 1991 | -95 | 0 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 1156.4716 | 780 | 200 | 2136.4716 | 53.41% | 95% | 0% | -108.6957 | 1038.3777 | -2750 | -200 | -1911.6223 | 47.79% | 54.93% | 95% | 0% | 2086 | -95
[5 empty] | 2019-08-07 | 46 | 5254 | 1871 | -93 | 0 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 1156.4716 | 780 | 200 | 2136.4716 | 53.41% | 95% | 0% | -106.4073 | 849.5696 | -2750 | -200 | -2100.4304 | 52.51% | 54.92% | 95% | 0% | 1964 | -93
[5 empty] | 2019-08-07 | 47 | 5254.5 | 1764 | -91 | 0 | 0 | 1855 | 785.2432 | 785.2432 | 785.2432 | 1154.9052 | 780 | 200 | 2134.9052 | 53.37% | 95% | 0% | -104.119 | 681.1242 | -2750 | -200 | -2268.8758 | 56.72% | 54.92% | 95% | 0% | 1855 | -91
[5 empty] | 2019-08-07 | 48 | 5255 | 1654 | -89 | 0 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 1154.9052 | 780 | 200 | 2134.9052 | 53.37% | 95% | 0% | -101.8307 | 507.9797 | -2750 | -200 | -2442.0203 | 61.05% | 54.92% | 95% | 0% | 1743 | -89
[5 empty] | 2019-08-08 | 1 | 5255.5 | 1568 | -86 | 0 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 1154.9052 | 780 | 200 | 2134.9052 | 53.37% | 95% | 0% | -98.3982 | 372.0058 | -2750 | -200 | -2577.9942 | 64.45% | 54.92% | 95% | 0% | 1654 | -86
[5 empty] | 2019-08-08 | 2 | 5256 | 1518 | -82 | 0 | 0 | 1600 | 385.8203 | 385.8203 | 385.8203 | 1154.9052 | 780 | 200 | 2134.9052 | 53.37% | 95% | 0% | -93.8215 | 291.9988 | -2750 | -200 | -2658.0012 | 66.45% | 54.91% | 95% | 0% | 1600 | -82
[5 empty] | 2019-08-08 | 3 | 5256.5 | 1479 | -81 | 0 | 0 | 1560 | 323.1657 | 323.1657 | 323.1657 | 1154.9052 | 780 | 200 | 2134.9052 | 53.37% | 95% | 0% | -92.6773 | 230.4884 | -2750 | -200 | -2719.5116 | 67.99% | 54.91% | 95% | 0% | 1560 | -81
[5 empty] | 2019-08-08 | 4 | 5257 | 1464 | -79 | 0 | 0 | 1543 | 296.5375 | 296.5375 | 296.5375 | 1154.9052 | 780 | 200 | 2134.9052 | 53.37% | 95% | 0% | -90.389 | 206.1485 | -2750 | -200 | -2743.8515 | 68.6% | 54.91% | 95% | 0% | 1543 | -79
[5 empty] | 2019-08-08 | 5 | 5257.5 | 1444 | -78 | 0 | 0 | 1522 | 263.6439 | 263.6439 | 263.6439 | 1154.9052 | 780 | 200 | 2134.9052 | 53.37% | 95% | 0% | -89.2449 | 174.399 | -2750 | -200 | -2775.601 | 69.39% | 54.91% | 95% | 0% | 1522 | -78
[5 empty] | 2019-08-08 | 6 | 5258 | 1422 | -76 | 0 | 0 | 1498 | 226.0511 | 226.0511 | 226.0511 | 1154.9052 | 780 | 200 | 2134.9052 | 53.37% | 95% | 0% | -86.9565 | 139.0946 | -2750 | -200 | -2810.9054 | 70.27% | 54.91% | 95% | 0% | 1498 | -76
[5 empty] | 2019-08-08 | 7 | 5258.5 | 1414 | -74 | 1 | 0 | 1488 | 210.3875 | 210.3875 | 210.3875 | 1154.9052 | 780 | 200 | 2134.9052 | 53.37% | 95% | 0% | -84.6682 | 125.7193 | -3550 | -400 | -3824.2807 | 95.61% | 54.9% | 95% | 0% | 1488 | -74
[5 empty] | 2019-08-08 | 8 | 5259 | 1413 | -72 | 1 | 0 | 1485 | 205.6884 | 205.6884 | 205.6884 | 1154.9052 | 780 | 200 | 2134.9052 | 53.37% | 95% | 0% | -82.3799 | 123.3085 | -3550 | -400 | -3826.6915 | 95.67% | 54.9% | 95% | 0% | 1485 | -72
[5 empty] | 2019-08-08 | 9 | 5259.5 | 1427 | -68 | 1 | 0 | 1495 | 221.352 | 221.352 | 221.352 | 1154.9052 | 780 | 200 | 2134.9052 | 53.37% | 95% | 0% | -77.8032 | 143.5488 | -3550 | -400 | -3806.4512 | 95.16% | 54.9% | 95% | 0% | 1495 | -68
[5 empty] | 2019-08-08 | 10 | 5260 | 1442 | -65 | 1 | 0 | 1507 | 240.1484 | 240.1484 | 240.1484 | 1154.9052 | 780 | 200 | 2134.9052 | 53.37% | 95% | 0% | -74.3707 | 165.7777 | -3550 | -400 | -3784.2223 | 94.61% | 54.9% | 95% | 0% | 1507 | -65
[5 empty] | 2019-08-08 | 11 | 5260.5 | 1486 | -63 | 1 | 0 | 1549 | 305.9357 | 305.9357 | 305.9357 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -72.0824 | 233.8533 | -3550 | -400 | -3716.1467 | 92.9% | 54.89% | 95% | 0% | 1549 | -63
[5 empty] | 2019-08-08 | 12 | 5261 | 1527 | -63 | 1 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -72.0824 | 298.0743 | -3550 | -400 | -3651.9257 | 91.3% | 54.89% | 95% | 0% | 1590 | -63
[5 empty] | 2019-08-08 | 13 | 5261.5 | 1671 | -79 | 1 | 0 | 1750 | 620.7749 | 620.7749 | 620.7749 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -90.389 | 530.3859 | -3550 | -400 | -3419.6141 | 85.49% | 54.89% | 95% | 0% | 1750 | -79
[5 empty] | 2019-08-08 | 14 | 5262 | 1794 | -102 | 1 | 0 | 1896 | 849.4641 | 849.4641 | 849.4641 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -116.7048 | 732.7593 | -3550 | -400 | -3217.2407 | 80.43% | 54.88% | 95% | 0% | 1896 | -102
[5 empty] | 2019-08-08 | 15 | 5262.5 | 1922 | -143 | 1 | 0 | 2065 | 1114.1797 | 1114.1797 | 1114.1797 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -163.6156 | 950.5642 | -3550 | -400 | -2999.4358 | 74.99% | 54.87% | 95% | 0% | 2065 | -143
[5 empty] | 2019-08-08 | 16 | 5263 | 1971 | -185 | 1 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -211.6705 | 1045.0484 | -3550 | -400 | -2904.9516 | 72.62% | 54.87% | 95% | 0% | 2156 | -185
[5 empty] | 2019-08-08 | 17 | 5263.5 | 1981 | -248 | 1 | 0 | 2229 | 1371.0635 | 1371.0635 | 1371.0635 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -283.7529 | 1087.3106 | -3550 | -400 | -2862.6894 | 71.57% | 54.87% | 95% | 0% | 2229 | -248
[5 empty] | 2019-08-08 | 18 | 5264 | 1938 | -309 | 1 | 0 | 2247 | 1399.258 | 1399.258 | 1399.258 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -353.5469 | 1045.7111 | -3550 | -400 | -2904.2889 | 72.61% | 54.86% | 95% | 0% | 2247 | -309
[5 empty] | 2019-08-08 | 19 | 5264.5 | 1883 | -368 | 1 | 0 | 2251 | 1405.5235 | 1405.5235 | 1405.5235 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -421.0526 | 984.4709 | -3550 | -400 | -2965.5291 | 74.14% | 54.86% | 95% | 0% | 2251 | -368
[5 empty] | 2019-08-08 | 20 | 5265 | 1791 | -414 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -473.6842 | 859.7865 | -3550 | -400 | -3090.2135 | 77.26% | 54.85% | 95% | 0% | 2205 | -414
[5 empty] | 2019-08-08 | 21 | 5265.5 | 1727 | -451 | 1 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -516.0183 | 775.1606 | -3550 | -400 | -3174.8394 | 79.37% | 54.85% | 95% | 0% | 2178 | -451
[5 empty] | 2019-08-08 | 22 | 5266 | 1704 | -482 | 1 | 0 | 2186 | 1303.7098 | 1303.7098 | 1303.7098 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -551.4874 | 752.2224 | -3550 | -400 | -3197.7776 | 79.94% | 54.85% | 95% | 0% | 2186 | -482
[5 empty] | 2019-08-08 | 23 | 5266.5 | 1688 | -510 | 1 | 0 | 2198 | 1322.5062 | 1322.5062 | 1322.5062 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -583.524 | 738.9822 | -3550 | -400 | -3211.0178 | 80.28% | 54.85% | 95% | 0% | 2198 | -510
[5 empty] | 2019-08-08 | 24 | 5267 | 1674 | -524 | 1 | 0 | 2198 | 1322.5062 | 1322.5062 | 1322.5062 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -599.5423 | 722.9638 | -3550 | -400 | -3227.0362 | 80.68% | 54.85% | 95% | 0% | 2198 | -524
[5 empty] | 2019-08-08 | 25 | 5267.5 | 1667 | -541 | 1 | 0 | 2208 | 1338.1698 | 1338.1698 | 1338.1698 | 1153.3388 | 780 | 200 | 2133.3388 | 53.33% | 95% | 0% | -618.9931 | 719.1767 | -3550 | -400 | -3230.8233 | 80.77% | 54.85% | 95% | 0% | 2208 | -541
[5 empty] | 2019-08-08 | 26 | 5268 | 1675 | -517 | 1 | 0 | 2192 | 1313.108 | 1313.108 | 1313.108 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -591.5332 | 721.5748 | -3550 | -400 | -3228.4252 | 80.71% | 54.84% | 95% | 0% | 2192 | -517
[5 empty] | 2019-08-08 | 27 | 5268.5 | 1658 | -521 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -596.1098 | 696.6354 | -3550 | -400 | -3253.3646 | 81.33% | 54.84% | 95% | 0% | 2179 | -521
[5 empty] | 2019-08-08 | 28 | 5269 | 1617 | -542 | 1 | 0 | 2159 | 1261.418 | 1261.418 | 1261.418 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -620.1373 | 641.2807 | -3550 | -400 | -3308.7193 | 82.72% | 54.84% | 95% | 0% | 2159 | -542
[5 empty] | 2019-08-08 | 29 | 5269.5 | 1666 | -507 | 1 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -580.0915 | 703.2555 | -3550 | -400 | -3246.7445 | 81.17% | 54.83% | 95% | 0% | 2173 | -507
[5 empty] | 2019-08-08 | 30 | 5270 | 1722 | -468 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -535.4691 | 774.5062 | -3550 | -400 | -3175.4938 | 79.39% | 54.82% | 95% | 0% | 2190 | -468
[5 empty] | 2019-08-08 | 31 | 5270.5 | 1764 | -442 | 1 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -505.7208 | 829.3163 | -3550 | -400 | -3120.6837 | 78.02% | 54.82% | 95% | 0% | 2206 | -442
[5 empty] | 2019-08-08 | 32 | 5271 | 1827 | -400 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -457.6659 | 910.2648 | -3550 | -400 | -3039.7352 | 75.99% | 54.82% | 95% | 0% | 2227 | -400
[5 empty] | 2019-08-08 | 33 | 5271.5 | 1896 | -372 | 1 | 0 | 2268 | 1432.1517 | 1432.1517 | 1432.1517 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -425.6293 | 1006.5224 | -3550 | -400 | -2943.4776 | 73.59% | 54.82% | 95% | 0% | 2268 | -372
[5 empty] | 2019-08-08 | 34 | 5272 | 2007 | -324 | 1 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -370.7094 | 1160.1233 | -3550 | -400 | -2789.8767 | 69.75% | 54.81% | 95% | 0% | 2331 | -324
[5 empty] | 2019-08-08 | 35 | 5272.5 | 2090 | -280 | 1 | 0 | 2370 | 1591.9209 | 1591.9209 | 1591.9209 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -320.3661 | 1271.5547 | -3550 | -400 | -2678.4453 | 66.96% | 54.81% | 95% | 0% | 2370 | -280
[5 empty] | 2019-08-08 | 36 | 5273 | 2133 | -243 | 1 | 0 | 2376 | 1601.319 | 1601.319 | 1601.319 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -278.032 | 1323.287 | -3550 | -400 | -2626.713 | 65.67% | 54.81% | 95% | 0% | 2376 | -243
[5 empty] | 2019-08-08 | 37 | 5273.5 | 2191 | -187 | 1 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -213.9588 | 1390.493 | -3550 | -400 | -2559.507 | 63.99% | 54.8% | 95% | 0% | 2378 | -187
[5 empty] | 2019-08-08 | 38 | 5274 | 2244 | -155 | 1 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -177.3455 | 1459.9999 | -3550 | -400 | -2490.0001 | 62.25% | 54.8% | 95% | 0% | 2399 | -155
[5 empty] | 2019-08-08 | 39 | 5274.5 | 2283 | -121 | 1 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -138.4439 | 1506.7333 | -3550 | -400 | -2443.2667 | 61.08% | 54.8% | 95% | 0% | 2404 | -121
[5 empty] | 2019-08-08 | 40 | 5275 | 2309 | -93 | 1 | 0 | 2402 | 1642.0445 | 1642.0445 | 1642.0445 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -106.4073 | 1535.6372 | -3550 | -400 | -2414.3628 | 60.36% | 54.8% | 95% | 0% | 2402 | -93
[5 empty] | 2019-08-08 | 41 | 5275.5 | 2286 | -85 | 1 | 0 | 2371 | 1593.4872 | 1593.4872 | 1593.4872 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -97.254 | 1496.2332 | -3550 | -400 | -2453.7668 | 61.34% | 54.8% | 95% | 0% | 2371 | -85
[5 empty] | 2019-08-08 | 42 | 5276 | 2281 | -88 | 1 | 0 | 2369 | 1590.3545 | 1590.3545 | 1590.3545 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -100.6865 | 1489.668 | -3550 | -400 | -2460.332 | 61.51% | 54.8% | 95% | 0% | 2369 | -88
[5 empty] | 2019-08-08 | 43 | 5276.5 | 2256 | -94 | 1 | 0 | 2350 | 1560.5936 | 1560.5936 | 1560.5936 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -107.5515 | 1453.0421 | -3550 | -400 | -2496.9579 | 62.42% | 54.79% | 95% | 0% | 2350 | -94
[5 empty] | 2019-08-08 | 44 | 5277 | 2162 | -101 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -115.5606 | 1308.7592 | -3550 | -400 | -2641.2408 | 66.03% | 54.79% | 95% | 0% | 2263 | -101
[5 empty] | 2019-08-08 | 45 | 5277.5 | 2003 | -106 | 0 | 0 | 2109 | 1183.0998 | 1183.0998 | 1183.0998 | 1151.7725 | 780 | 200 | 2131.7725 | 53.29% | 95% | 0% | -121.2815 | 1061.8183 | -2750 | -200 | -1888.1817 | 47.2% | 54.79% | 95% | 0% | 2109 | -106
[5 empty] | 2019-08-08 | 46 | 5278 | 1865 | -112 | 0 | 0 | 1977 | 976.3397 | 976.3397 | 976.3397 | 1150.2061 | 780 | 200 | 2130.2061 | 53.26% | 95% | 0% | -128.1465 | 848.1932 | -2750 | -200 | -2101.8068 | 52.55% | 54.78% | 95% | 0% | 1977 | -112
[5 empty] | 2019-08-08 | 47 | 5278.5 | 1724 | -117 | 0 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 1150.2061 | 780 | 200 | 2130.2061 | 53.26% | 95% | 0% | -133.8673 | 629.4468 | -2750 | -200 | -2320.5532 | 58.01% | 54.78% | 95% | 0% | 1841 | -117
[5 empty] | 2019-08-08 | 48 | 5279 | 1600 | -122 | 0 | 0 | 1722 | 576.9167 | 576.9167 | 576.9167 | 1150.2061 | 780 | 200 | 2130.2061 | 53.26% | 95% | 0% | -139.5881 | 437.3286 | -2750 | -200 | -2512.6714 | 62.82% | 54.77% | 95% | 0% | 1722 | -122
[5 empty] | 2019-08-09 | 1 | 5279.5 | 1499 | -126 | 0 | 0 | 1625 | 424.9794 | 424.9794 | 424.9794 | 1150.2061 | 780 | 200 | 2130.2061 | 53.26% | 95% | 0% | -144.1648 | 280.8146 | -2750 | -200 | -2669.1854 | 66.73% | 54.77% | 95% | 0% | 1625 | -126
[5 empty] | 2019-08-09 | 2 | 5280 | 1441 | -130 | 0 | 0 | 1571 | 340.3957 | 340.3957 | 340.3957 | 1150.2061 | 780 | 200 | 2130.2061 | 53.26% | 95% | 0% | -148.7414 | 191.6543 | -2750 | -200 | -2758.3457 | 68.96% | 54.77% | 95% | 0% | 1571 | -130
[5 empty] | 2019-08-09 | 3 | 5280.5 | 1383 | -134 | 0 | 0 | 1517 | 255.812 | 255.812 | 255.812 | 1150.2061 | 780 | 200 | 2130.2061 | 53.26% | 95% | 0% | -153.3181 | 102.494 | -2750 | -200 | -2847.506 | 71.19% | 54.76% | 95% | 0% | 1517 | -134
[5 empty] | 2019-08-09 | 4 | 5281 | 1361 | -137 | 0 | 0 | 1498 | 226.0511 | 226.0511 | 226.0511 | 1150.2061 | 780 | 200 | 2130.2061 | 53.26% | 95% | 0% | -156.7506 | 69.3005 | -2750 | -200 | -2880.6995 | 72.02% | 54.75% | 95% | 0% | 1498 | -137
[5 empty] | 2019-08-09 | 5 | 5281.5 | 1340 | -141 | 0 | 0 | 1481 | 199.4229 | 199.4229 | 199.4229 | 1150.2061 | 780 | 200 | 2130.2061 | 53.26% | 95% | 0% | -161.3272 | 38.0957 | -2750 | -200 | -2911.9043 | 72.8% | 54.75% | 95% | 0% | 1481 | -141
[5 empty] | 2019-08-09 | 6 | 5282 | 1315 | -144 | 0 | 0 | 1459 | 164.9629 | 164.9629 | 164.9629 | 1150.2061 | 780 | 200 | 2130.2061 | 53.26% | 95% | 0% | -164.7597 | 0.20318 | -2750 | -200 | -2949.7968 | 73.74% | 54.75% | 95% | 0% | 1459 | -144
[5 empty] | 2019-08-09 | 7 | 5282.5 | 1285 | -147 | 0 | 0 | 1432 | 122.6711 | 122.6711 | 122.6711 | 1150.2061 | 780 | 200 | 2130.2061 | 53.26% | 95% | 0% | -168.1922 | -45.5212 | -2750 | -200 | -2995.5212 | 74.89% | 54.74% | 95% | 0% | 1432 | -147
[5 empty] | 2019-08-09 | 8 | 5283 | 1271 | -151 | 0 | 0 | 1422 | 107.0074 | 107.0074 | 107.0074 | 1150.2061 | 780 | 200 | 2130.2061 | 53.26% | 95% | 0% | -172.7689 | -65.7615 | -2750 | -200 | -3015.7615 | 75.39% | 54.74% | 95% | 0% | 1422 | -151
[5 empty] | 2019-08-09 | 9 | 5283.5 | 1269 | -152 | 0 | 0 | 1421 | 105.4411 | 105.4411 | 105.4411 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -173.913 | -68.472 | -2750 | -200 | -3018.472 | 75.46% | 54.73% | 95% | 0% | 1421 | -152
[5 empty] | 2019-08-09 | 10 | 5284 | 1272 | -153 | 1 | 0 | 1425 | 111.7065 | 111.7065 | 111.7065 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -175.0572 | -63.3507 | -3550 | -400 | -4013.3507 | 100.3% | 54.73% | 95% | 0% | 1425 | -153
[5 empty] | 2019-08-09 | 11 | 5284.5 | 1304 | -155 | 1 | 0 | 1459 | 164.9629 | 164.9629 | 164.9629 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -177.3455 | -12.3826 | -3550 | -400 | -3962.3826 | 99.06% | 54.73% | 95% | 0% | 1459 | -155
[5 empty] | 2019-08-09 | 12 | 5285 | 1362 | -157 | 1 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -179.6339 | 79.3109 | -3550 | -400 | -3870.6891 | 96.77% | 54.72% | 95% | 0% | 1519 | -157
[5 empty] | 2019-08-09 | 13 | 5285.5 | 1507 | -161 | 1 | 0 | 1668 | 492.3331 | 492.3331 | 492.3331 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -184.2105 | 308.1225 | -3550 | -400 | -3641.8775 | 91.05% | 54.72% | 95% | 0% | 1668 | -161
[5 empty] | 2019-08-09 | 14 | 5286 | 1626 | -170 | 1 | 0 | 1796 | 692.8277 | 692.8277 | 692.8277 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -194.508 | 498.3197 | -3550 | -400 | -3451.6803 | 86.29% | 54.72% | 95% | 0% | 1796 | -170
[5 empty] | 2019-08-09 | 15 | 5286.5 | 1766 | -199 | 1 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -227.6888 | 729.8545 | -3550 | -400 | -3220.1455 | 80.5% | 54.71% | 95% | 0% | 1965 | -199
[5 empty] | 2019-08-09 | 16 | 5287 | 1855 | -223 | 1 | 0 | 2078 | 1134.5425 | 1134.5425 | 1134.5425 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -255.1487 | 879.3937 | -3550 | -400 | -3070.6063 | 76.77% | 54.7% | 95% | 0% | 2078 | -223
[5 empty] | 2019-08-09 | 17 | 5287.5 | 1928 | -253 | 1 | 0 | 2181 | 1295.878 | 1295.878 | 1295.878 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -289.4737 | 1006.4043 | -3550 | -400 | -2943.5957 | 73.59% | 54.7% | 95% | 0% | 2181 | -253
[5 empty] | 2019-08-09 | 18 | 5288 | 1920 | -297 | 1 | 0 | 2217 | 1352.2671 | 1352.2671 | 1352.2671 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -339.8169 | 1012.4502 | -3550 | -400 | -2937.5498 | 73.44% | 54.7% | 95% | 0% | 2217 | -297
[5 empty] | 2019-08-09 | 19 | 5288.5 | 1889 | -362 | 1 | 0 | 2251 | 1405.5235 | 1405.5235 | 1405.5235 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -414.1876 | 991.3359 | -3550 | -400 | -2958.6641 | 73.97% | 54.69% | 95% | 0% | 2251 | -362
[5 empty] | 2019-08-09 | 20 | 5289 | 1786 | -437 | 1 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -500 | 861.6653 | -3550 | -400 | -3088.3347 | 77.21% | 54.69% | 95% | 0% | 2223 | -437
[5 empty] | 2019-08-09 | 21 | 5289.5 | 1721 | -466 | 1 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -533.1808 | 772.0954 | -3550 | -400 | -3177.9046 | 79.45% | 54.69% | 95% | 0% | 2187 | -466
[5 empty] | 2019-08-09 | 22 | 5290 | 1633 | -527 | 1 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -602.9748 | 660.0095 | -3550 | -400 | -3289.9905 | 82.25% | 54.69% | 95% | 0% | 2160 | -527
[5 empty] | 2019-08-09 | 23 | 5290.5 | 1558 | -585 | 1 | 0 | 2143 | 1236.3561 | 1236.3561 | 1236.3561 | 1148.6397 | 780 | 200 | 2128.6397 | 53.22% | 95% | 0% | -669.3364 | 567.0198 | -3550 | -400 | -3382.9802 | 84.57% | 54.69% | 95% | 0% | 2143 | -585
[5 empty] | 2019-08-09 | 24 | 5291 | 1489 | -639 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -731.1213 | 481.7394 | -3550 | -400 | -3468.2606 | 86.71% | 54.69% | 95% | 0% | 2128 | -639
[5 empty] | 2019-08-09 | 25 | 5291.5 | 1504 | -632 | 1 | 0 | 2136 | 1225.3916 | 1225.3916 | 1225.3916 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -723.1121 | 502.2795 | -3550 | -400 | -3447.7205 | 86.19% | 54.68% | 95% | 0% | 2136 | -632
[5 empty] | 2019-08-09 | 26 | 5292 | 1515 | -598 | 1 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -684.2105 | 505.1547 | -3550 | -400 | -3444.8453 | 86.12% | 54.68% | 95% | 0% | 2113 | -598
[5 empty] | 2019-08-09 | 27 | 5292.5 | 1428 | -644 | 1 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -736.8421 | 388.3022 | -3550 | -400 | -3561.6978 | 89.04% | 54.68% | 95% | 0% | 2072 | -644
[5 empty] | 2019-08-09 | 28 | 5293 | 1483 | -589 | 1 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -673.913 | 451.2312 | -3550 | -400 | -3498.7688 | 87.47% | 54.68% | 95% | 0% | 2072 | -589
[5 empty] | 2019-08-09 | 29 | 5293.5 | 1471 | -590 | 1 | 0 | 2061 | 1107.9143 | 1107.9143 | 1107.9143 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -675.0572 | 432.8571 | -3550 | -400 | -3517.1429 | 87.93% | 54.68% | 95% | 0% | 2061 | -590
[5 empty] | 2019-08-09 | 30 | 5294 | 1512 | -551 | 1 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -630.4348 | 480.6122 | -3550 | -400 | -3469.3878 | 86.73% | 54.68% | 95% | 0% | 2063 | -551
[5 empty] | 2019-08-09 | 31 | 5294.5 | 1547 | -529 | 1 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -605.2632 | 526.1466 | -3550 | -400 | -3423.8534 | 85.6% | 54.67% | 95% | 0% | 2076 | -529
[5 empty] | 2019-08-09 | 32 | 5295 | 1589 | -512 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -585.8124 | 584.7565 | -3550 | -400 | -3365.2435 | 84.13% | 54.67% | 95% | 0% | 2101 | -512
[5 empty] | 2019-08-09 | 33 | 5295.5 | 1692 | -447 | 1 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -511.4416 | 718.649 | -3550 | -400 | -3231.351 | 80.78% | 54.67% | 95% | 0% | 2139 | -447
[5 empty] | 2019-08-09 | 34 | 5296 | 1802 | -373 | 1 | 0 | 2175 | 1286.4798 | 1286.4798 | 1286.4798 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -426.7735 | 859.7063 | -3550 | -400 | -3090.2937 | 77.26% | 54.66% | 95% | 0% | 2175 | -373
[5 empty] | 2019-08-09 | 35 | 5296.5 | 1830 | -332 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -379.8627 | 886.2544 | -3550 | -400 | -3063.7456 | 76.59% | 54.66% | 95% | 0% | 2162 | -332
[5 empty] | 2019-08-09 | 36 | 5297 | 1918 | -308 | 1 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -352.4027 | 1013.9616 | -3550 | -400 | -2936.0384 | 73.4% | 54.66% | 95% | 0% | 2226 | -308
[5 empty] | 2019-08-09 | 37 | 5297.5 | 1946 | -270 | 1 | 0 | 2216 | 1350.7007 | 1350.7007 | 1350.7007 | 1147.0734 | 780 | 200 | 2127.0734 | 53.18% | 95% | 0% | -308.9245 | 1041.7763 | -3550 | -400 | -2908.2237 | 72.71% | 54.65% | 95% | 0% | 2216 | -270
[5 empty] | 2019-08-09 | 38 | 5298 | 1992 | -218 | 1 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -249.4279 | 1091.8746 | -3550 | -400 | -2858.1254 | 71.45% | 54.65% | 95% | 0% | 2210 | -218
[5 empty] | 2019-08-09 | 39 | 5298.5 | 2030 | -183 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -209.3822 | 1136.6195 | -3550 | -400 | -2813.3805 | 70.33% | 54.65% | 95% | 0% | 2213 | -183
[5 empty] | 2019-08-09 | 40 | 5299 | 2017 | -163 | 1 | 0 | 2180 | 1294.3116 | 1294.3116 | 1294.3116 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -186.4989 | 1107.8128 | -3550 | -400 | -2842.1872 | 71.05% | 54.64% | 95% | 0% | 2180 | -163
[5 empty] | 2019-08-09 | 41 | 5299.5 | 1991 | -149 | 1 | 0 | 2140 | 1231.657 | 1231.657 | 1231.657 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -170.4805 | 1061.1765 | -3550 | -400 | -2888.8235 | 72.22% | 54.64% | 95% | 0% | 2140 | -149
[5 empty] | 2019-08-09 | 42 | 5300 | 2003 | -145 | 1 | 0 | 2148 | 1244.188 | 1244.188 | 1244.188 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -165.9039 | 1078.2841 | -3550 | -400 | -2871.7159 | 71.79% | 54.64% | 95% | 0% | 2148 | -145
[5 empty] | 2019-08-09 | 43 | 5300.5 | 2015 | -144 | 1 | 0 | 2159 | 1261.418 | 1261.418 | 1261.418 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -164.7597 | 1096.6582 | -3550 | -400 | -2853.3418 | 71.33% | 54.64% | 95% | 0% | 2159 | -144
[5 empty] | 2019-08-09 | 44 | 5301 | 1959 | -142 | 0 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -162.4714 | 1008.0974 | -2750 | -200 | -1941.9026 | 48.55% | 54.64% | 95% | 0% | 2101 | -142
[5 empty] | 2019-08-09 | 45 | 5301.5 | 1865 | -143 | 0 | 0 | 2008 | 1024.8969 | 1024.8969 | 1024.8969 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -163.6156 | 861.2814 | -2750 | -200 | -2088.7186 | 52.22% | 54.63% | 95% | 0% | 2008 | -143
[5 empty] | 2019-08-09 | 46 | 5302 | 1738 | -144 | 0 | 0 | 1882 | 827.535 | 827.535 | 827.535 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -164.7597 | 662.7753 | -2750 | -200 | -2287.2247 | 57.18% | 54.63% | 95% | 0% | 1882 | -144
[5 empty] | 2019-08-09 | 47 | 5302.5 | 1623 | -145 | 0 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -165.9039 | 483.0656 | -2750 | -200 | -2466.9344 | 61.67% | 54.63% | 95% | 0% | 1768 | -145
[5 empty] | 2019-08-09 | 48 | 5303 | 1524 | -147 | 0 | 0 | 1671 | 497.0322 | 497.0322 | 497.0322 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -168.1922 | 328.8399 | -2750 | -200 | -2621.1601 | 65.53% | 54.63% | 95% | 0% | 1671 | -147
[5 empty] | 2019-08-10 | 1 | 5303.5 | 1435 | -145 | 0 | 0 | 1580 | 354.493 | 354.493 | 354.493 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -165.9039 | 188.5891 | -2750 | -200 | -2761.4109 | 69.04% | 54.63% | 95% | 0% | 1580 | -145
[5 empty] | 2019-08-10 | 2 | 5304 | 1364 | -144 | 0 | 0 | 1508 | 241.7148 | 241.7148 | 241.7148 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -164.7597 | 76.955 | -2750 | -200 | -2873.045 | 71.83% | 54.62% | 95% | 0% | 1508 | -144
[5 empty] | 2019-08-10 | 3 | 5304.5 | 1326 | -143 | 0 | 0 | 1469 | 180.6265 | 180.6265 | 180.6265 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -163.6156 | 17.011 | -2750 | -200 | -2932.989 | 73.32% | 54.62% | 95% | 0% | 1469 | -143
[5 empty] | 2019-08-10 | 4 | 5305 | 1301 | -141 | 0 | 0 | 1442 | 138.3347 | 138.3347 | 138.3347 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -161.3272 | -22.9925 | -2750 | -200 | -2972.9925 | 74.32% | 54.62% | 95% | 0% | 1442 | -141
[5 empty] | 2019-08-10 | 5 | 5305.5 | 1264 | -142 | 0 | 0 | 1406 | 81.9456 | 81.9456 | 81.9456 | 1145.507 | 780 | 200 | 2125.507 | 53.14% | 95% | 0% | -162.4714 | -80.5258 | -2750 | -200 | -3030.5258 | 75.76% | 54.62% | 95% | 0% | 1406 | -142
[5 empty] | 2019-08-10 | 6 | 5306 | 1228 | -143 | 0 | 0 | 1371 | 27.1228 | 27.1228 | 27.1228 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -163.6156 | -136.4927 | -2750 | -200 | -3086.4927 | 77.16% | 54.62% | 95% | 0% | 1371 | -143
[5 empty] | 2019-08-10 | 7 | 5306.5 | 1216 | -140 | 0 | 0 | 1356 | 3.6274 | 3.6274 | 3.6274 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -160.1831 | -156.5557 | -2750 | -200 | -3106.5557 | 77.66% | 54.62% | 95% | 0% | 1356 | -140
[5 empty] | 2019-08-10 | 8 | 5307 | 1216 | -138 | 0 | 0 | 1354 | 0.49464 | 0.49464 | 0.49464 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -157.8947 | -157.4001 | -2750 | -200 | -3107.4001 | 77.69% | 54.62% | 95% | 0% | 1354 | -138
[5 empty] | 2019-08-10 | 9 | 5307.5 | 1207 | -137 | 0 | 0 | 1344 | -15.169 | -15.169 | -15.169 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -156.7506 | -171.9196 | -2750 | -200 | -3121.9196 | 78.05% | 54.61% | 95% | 0% | 1344 | -137
[5 empty] | 2019-08-10 | 10 | 5308 | 1208 | -136 | 0 | 0 | 1344 | -15.169 | -15.169 | -15.169 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -155.6064 | -170.7754 | -2750 | -200 | -3120.7754 | 78.02% | 54.61% | 95% | 0% | 1344 | -136
[5 empty] | 2019-08-10 | 11 | 5308.5 | 1224 | -137 | 0 | 0 | 1361 | 11.4592 | 11.4592 | 11.4592 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -156.7506 | -145.2914 | -2750 | -200 | -3095.2914 | 77.38% | 54.6% | 95% | 0% | 1361 | -137
[5 empty] | 2019-08-10 | 12 | 5309 | 1210 | -139 | 0 | 0 | 1349 | -7.3372 | -7.3372 | -7.3372 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -159.0389 | -166.3761 | -2750 | -200 | -3116.3761 | 77.91% | 54.6% | 95% | 0% | 1349 | -139
[5 empty] | 2019-08-10 | 13 | 5309.5 | 1273 | -144 | 0 | 0 | 1417 | 99.1756 | 99.1756 | 99.1756 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -164.7597 | -65.5841 | -2750 | -200 | -3015.5841 | 75.39% | 54.59% | 95% | 0% | 1417 | -144
[5 empty] | 2019-08-10 | 14 | 5310 | 1299 | -164 | 0 | 0 | 1463 | 171.2284 | 171.2284 | 171.2284 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -187.643 | -16.4147 | -2750 | -200 | -2966.4147 | 74.16% | 54.59% | 95% | 0% | 1463 | -164
[5 empty] | 2019-08-10 | 15 | 5310.5 | 1361 | -194 | 1 | 0 | 1555 | 315.3339 | 315.3339 | 315.3339 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -221.968 | 93.3659 | -3550 | -400 | -3856.6341 | 96.42% | 54.59% | 95% | 0% | 1555 | -194
[5 empty] | 2019-08-10 | 16 | 5311 | 1395 | -234 | 1 | 0 | 1629 | 431.2448 | 431.2448 | 431.2448 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -267.7346 | 163.5103 | -3550 | -400 | -3786.4897 | 94.66% | 54.58% | 95% | 0% | 1629 | -234
[5 empty] | 2019-08-10 | 17 | 5311.5 | 1455 | -265 | 1 | 0 | 1720 | 573.784 | 573.784 | 573.784 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -303.2037 | 270.5803 | -3550 | -400 | -3679.4197 | 91.99% | 54.58% | 95% | 0% | 1720 | -265
[5 empty] | 2019-08-10 | 18 | 5312 | 1484 | -307 | 1 | 0 | 1791 | 684.9959 | 684.9959 | 684.9959 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -351.2586 | 333.7373 | -3550 | -400 | -3616.2627 | 90.41% | 54.57% | 95% | 0% | 1791 | -307
[5 empty] | 2019-08-10 | 19 | 5312.5 | 1493 | -339 | 1 | 0 | 1832 | 749.2168 | 749.2168 | 749.2168 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -387.8719 | 361.345 | -3550 | -400 | -3588.655 | 89.72% | 54.56% | 95% | 0% | 1832 | -339
[5 empty] | 2019-08-10 | 20 | 5313 | 1480 | -380 | 1 | 0 | 1860 | 793.075 | 793.075 | 793.075 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -434.7826 | 358.2924 | -3550 | -400 | -3591.7076 | 89.79% | 54.56% | 95% | 0% | 1860 | -380
[5 empty] | 2019-08-10 | 21 | 5313.5 | 1502 | -377 | 1 | 0 | 1879 | 822.8359 | 822.8359 | 822.8359 | 1143.9406 | 780 | 200 | 2123.9406 | 53.1% | 95% | 0% | -431.3501 | 391.4858 | -3550 | -400 | -3558.5142 | 88.96% | 54.56% | 95% | 0% | 1879 | -377
[5 empty] | 2019-08-10 | 22 | 5314 | 1513 | -370 | 1 | 0 | 1883 | 829.1014 | 829.1014 | 829.1014 | 1142.3743 | 780 | 200 | 2122.3743 | 53.06% | 95% | 0% | -423.341 | 405.7604 | -3550 | -400 | -3544.2396 | 88.61% | 54.56% | 95% | 0% | 1883 | -370
[5 empty] | 2019-08-10 | 23 | 5314.5 | 1508 | -384 | 1 | 0 | 1892 | 843.1987 | 843.1987 | 843.1987 | 1142.3743 | 780 | 200 | 2122.3743 | 53.06% | 95% | 0% | -439.3593 | 403.8394 | -3550 | -400 | -3546.1606 | 88.65% | 54.56% | 95% | 0% | 1892 | -384
[5 empty] | 2019-08-10 | 24 | 5315 | 1491 | -387 | 1 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 1142.3743 | 780 | 200 | 2122.3743 | 53.06% | 95% | 0% | -442.7918 | 378.4778 | -3550 | -400 | -3571.5222 | 89.29% | 54.56% | 95% | 0% | 1878 | -387
[5 empty] | 2019-08-10 | 25 | 5315.5 | 1420 | -433 | 1 | 0 | 1853 | 782.1105 | 782.1105 | 782.1105 | 1142.3743 | 780 | 200 | 2122.3743 | 53.06% | 95% | 0% | -495.4233 | 286.6871 | -3550 | -400 | -3663.3129 | 91.58% | 54.53% | 95% | 0% | 1853 | -433
[5 empty] | 2019-08-10 | 26 | 5316 | 1341 | -464 | 1 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 1142.3743 | 780 | 200 | 2122.3743 | 53.06% | 95% | 0% | -530.8924 | 176.0325 | -3550 | -400 | -3773.9675 | 94.35% | 54.53% | 95% | 0% | 1805 | -464
[5 empty] | 2019-08-10 | 27 | 5316.5 | 1258 | -496 | 1 | 0 | 1754 | 627.0404 | 627.0404 | 627.0404 | 1142.3743 | 780 | 200 | 2122.3743 | 53.06% | 95% | 0% | -567.5057 | 59.5347 | -3550 | -400 | -3890.4653 | 97.26% | 54.52% | 95% | 0% | 1754 | -496
[5 empty] | 2019-08-10 | 28 | 5317 | 1192 | -510 | 1 | 0 | 1702 | 545.5894 | 545.5894 | 545.5894 | 1142.3743 | 780 | 200 | 2122.3743 | 53.06% | 95% | 0% | -583.524 | -37.9346 | -3550 | -400 | -3987.9346 | 99.7% | 54.52% | 95% | 0% | 1702 | -510
[5 empty] | 2019-08-10 | 29 | 5317.5 | 1141 | -537 | 1 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 1142.3743 | 780 | 200 | 2122.3743 | 53.06% | 95% | 0% | -614.4165 | -106.4198 | -3550 | -400 | -4056.4198 | 101.4% | 54.51% | 95% | 0% | 1678 | -537
[5 empty] | 2019-08-10 | 30 | 5318 | 1150 | -509 | 1 | 0 | 1659 | 478.2358 | 478.2358 | 478.2358 | 1142.3743 | 780 | 200 | 2122.3743 | 53.06% | 95% | 0% | -582.3799 | -104.1441 | -3550 | -400 | -4054.1441 | 101.4% | 54.51% | 95% | 0% | 1659 | -509
[5 empty] | 2019-08-10 | 31 | 5318.5 | 1136 | -500 | 1 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -572.0824 | -129.873 | -3550 | -400 | -4079.873 | 102% | 54.5% | 95% | 0% | 1636 | -500
[5 empty] | 2019-08-10 | 32 | 5319 | 1160 | -468 | 1 | 0 | 1628 | 429.6785 | 429.6785 | 429.6785 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -535.4691 | -105.7906 | -3550 | -400 | -4055.7906 | 101.4% | 54.5% | 95% | 0% | 1628 | -468
[5 empty] | 2019-08-10 | 33 | 5319.5 | 1231 | -454 | 1 | 0 | 1685 | 518.9613 | 518.9613 | 518.9613 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -519.4508 | -0.48955 | -3550 | -400 | -3950.4895 | 98.76% | 54.5% | 95% | 0% | 1685 | -454
[5 empty] | 2019-08-10 | 34 | 5320 | 1332 | -413 | 1 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -472.54 | 140.4031 | -3550 | -400 | -3809.5969 | 95.24% | 54.5% | 95% | 0% | 1745 | -413
[5 empty] | 2019-08-10 | 35 | 5320.5 | 1444 | -386 | 1 | 0 | 1830 | 746.0841 | 746.0841 | 746.0841 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -441.6476 | 304.4365 | -3550 | -400 | -3645.5635 | 91.14% | 54.49% | 95% | 0% | 1830 | -386
[5 empty] | 2019-08-10 | 36 | 5321 | 1521 | -351 | 1 | 0 | 1872 | 811.8714 | 811.8714 | 811.8714 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -401.6018 | 410.2696 | -3550 | -400 | -3539.7304 | 88.49% | 54.48% | 95% | 0% | 1872 | -351
[5 empty] | 2019-08-10 | 37 | 5321.5 | 1593 | -301 | 1 | 0 | 1894 | 846.3314 | 846.3314 | 846.3314 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -344.3936 | 501.9378 | -3550 | -400 | -3448.0622 | 86.2% | 54.48% | 95% | 0% | 1894 | -301
[5 empty] | 2019-08-10 | 38 | 5322 | 1643 | -259 | 1 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -296.3387 | 562.5237 | -3550 | -400 | -3387.4763 | 84.69% | 54.48% | 95% | 0% | 1902 | -259
[5 empty] | 2019-08-10 | 39 | 5322.5 | 1677 | -218 | 1 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -249.4279 | 598.4699 | -3550 | -400 | -3351.5301 | 83.79% | 54.48% | 95% | 0% | 1895 | -218
[5 empty] | 2019-08-10 | 40 | 5323 | 1699 | -184 | 1 | 0 | 1883 | 829.1014 | 829.1014 | 829.1014 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -210.5263 | 618.5751 | -3550 | -400 | -3331.4249 | 83.29% | 54.48% | 95% | 0% | 1883 | -184
[5 empty] | 2019-08-10 | 41 | 5323.5 | 1717 | -165 | 1 | 0 | 1882 | 827.535 | 827.535 | 827.535 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -188.7872 | 638.7479 | -3550 | -400 | -3311.2521 | 82.78% | 54.47% | 95% | 0% | 1882 | -165
[5 empty] | 2019-08-10 | 42 | 5324 | 1725 | -159 | 1 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -181.9222 | 648.7456 | -3550 | -400 | -3301.2544 | 82.53% | 54.47% | 95% | 0% | 1884 | -159
[5 empty] | 2019-08-10 | 43 | 5324.5 | 1731 | -159 | 1 | 0 | 1890 | 840.066 | 840.066 | 840.066 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -181.9222 | 658.1438 | -3550 | -400 | -3291.8562 | 82.3% | 54.47% | 95% | 0% | 1890 | -159
[5 empty] | 2019-08-10 | 44 | 5325 | 1676 | -159 | 0 | 0 | 1835 | 753.9159 | 753.9159 | 753.9159 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -181.9222 | 571.9937 | -2750 | -200 | -2378.0063 | 59.45% | 54.47% | 95% | 0% | 1835 | -159
[5 empty] | 2019-08-10 | 45 | 5325.5 | 1624 | -159 | 0 | 0 | 1783 | 672.465 | 672.465 | 672.465 | 1140.8079 | 780 | 200 | 2120.8079 | 53.02% | 95% | 0% | -181.9222 | 490.5428 | -2750 | -200 | -2459.4572 | 61.49% | 54.47% | 95% | 0% | 1783 | -159
[5 empty] | 2019-08-10 | 46 | 5326 | 1542 | -159 | 0 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -181.9222 | 362.1009 | -2750 | -200 | -2587.8991 | 64.7% | 54.47% | 95% | 0% | 1701 | -159
[5 empty] | 2019-08-10 | 47 | 5326.5 | 1427 | -158 | 0 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -180.778 | 181.5468 | -2750 | -200 | -2768.4532 | 69.21% | 54.47% | 95% | 0% | 1585 | -158
[5 empty] | 2019-08-10 | 48 | 5327 | 1348 | -157 | 0 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -179.6339 | 57.3818 | -2750 | -200 | -2892.6182 | 72.32% | 54.47% | 95% | 0% | 1505 | -157
[5 empty] | 2019-08-11 | 1 | 5327.5 | 1275 | -156 | 0 | 0 | 1431 | 121.1047 | 121.1047 | 121.1047 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -178.4897 | -57.385 | -2750 | -200 | -3007.385 | 75.18% | 54.47% | 95% | 0% | 1431 | -156
[5 empty] | 2019-08-11 | 2 | 5328 | 1218 | -156 | 0 | 0 | 1374 | 31.8219 | 31.8219 | 31.8219 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -178.4897 | -146.6678 | -2750 | -200 | -3096.6678 | 77.42% | 54.46% | 95% | 0% | 1374 | -156
[5 empty] | 2019-08-11 | 3 | 5328.5 | 1176 | -153 | 0 | 0 | 1329 | -38.6645 | -38.6645 | -38.6645 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -175.0572 | -213.7217 | -2750 | -200 | -3163.7217 | 79.09% | 54.46% | 95% | 0% | 1329 | -153
[5 empty] | 2019-08-11 | 4 | 5329 | 1154 | -151 | 0 | 0 | 1305 | -76.2572 | -76.2572 | -76.2572 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -172.7689 | -249.0261 | -2750 | -200 | -3199.0261 | 79.98% | 54.46% | 95% | 0% | 1305 | -151
[5 empty] | 2019-08-11 | 5 | 5329.5 | 1136 | -150 | 0 | 0 | 1286 | -106.0181 | -106.0181 | -106.0181 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -171.6247 | -277.6429 | -2750 | -200 | -3227.6429 | 80.69% | 54.45% | 95% | 0% | 1286 | -150
[5 empty] | 2019-08-11 | 6 | 5330 | 1112 | -149 | 0 | 0 | 1261 | -145.1772 | -145.1772 | -145.1772 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -170.4805 | -315.6578 | -2750 | -200 | -3265.6578 | 81.64% | 54.45% | 95% | 0% | 1261 | -149
[5 empty] | 2019-08-11 | 7 | 5330.5 | 1093 | -146 | 0 | 0 | 1239 | -179.6373 | -179.6373 | -179.6373 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -167.0481 | -346.6853 | -2750 | -200 | -3296.6853 | 82.42% | 54.45% | 95% | 0% | 1239 | -146
[5 empty] | 2019-08-11 | 8 | 5331 | 1085 | -144 | 0 | 0 | 1229 | -195.3009 | -195.3009 | -195.3009 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -164.7597 | -360.0606 | -2750 | -200 | -3310.0606 | 82.75% | 54.45% | 95% | 0% | 1229 | -144
[5 empty] | 2019-08-11 | 9 | 5331.5 | 1085 | -141 | 0 | 0 | 1226 | -200 | -200 | -200 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -161.3272 | -361.3272 | -2750 | -200 | -3311.3272 | 82.78% | 54.45% | 95% | 0% | 1226 | -141
[5 empty] | 2019-08-11 | 10 | 5332 | 1096 | -138 | 0 | 0 | 1234 | -187.4691 | -187.4691 | -187.4691 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -157.8947 | -345.3638 | -2750 | -200 | -3295.3638 | 82.38% | 54.44% | 95% | 0% | 1234 | -138
[5 empty] | 2019-08-11 | 11 | 5332.5 | 1115 | -135 | 0 | 0 | 1250 | -162.4073 | -162.4073 | -162.4073 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -154.4622 | -316.8695 | -2750 | -200 | -3266.8695 | 81.67% | 54.44% | 95% | 0% | 1250 | -135
[5 empty] | 2019-08-11 | 12 | 5333 | 1111 | -132 | 0 | 0 | 1243 | -173.3718 | -173.3718 | -173.3718 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -151.0297 | -324.4016 | -2750 | -200 | -3274.4016 | 81.86% | 54.44% | 95% | 0% | 1243 | -132
[5 empty] | 2019-08-11 | 13 | 5333.5 | 1150 | -141 | 0 | 0 | 1291 | -98.1863 | -98.1863 | -98.1863 | 1139.2415 | 780 | 200 | 2119.2415 | 52.98% | 95% | 0% | -161.3272 | -259.5135 | -2750 | -200 | -3209.5135 | 80.24% | 54.43% | 95% | 0% | 1291 | -141
[5 empty] | 2019-08-11 | 14 | 5334 | 1163 | -162 | 0 | 0 | 1325 | -44.9299 | -44.9299 | -44.9299 | 1137.6752 | 780 | 200 | 2117.6752 | 52.94% | 95% | 0% | -185.3547 | -230.2846 | -2750 | -200 | -3180.2846 | 79.51% | 54.43% | 95% | 0% | 1325 | -162
[5 empty] | 2019-08-11 | 15 | 5334.5 | 1190 | -198 | 0 | 0 | 1388 | 53.751 | 53.751 | 53.751 | 1137.6752 | 780 | 200 | 2117.6752 | 52.94% | 95% | 0% | -226.5446 | -172.7936 | -2750 | -200 | -3122.7936 | 78.07% | 54.43% | 95% | 0% | 1388 | -198
[5 empty] | 2019-08-11 | 16 | 5335 | 1192 | -244 | 1 | 0 | 1436 | 128.9365 | 128.9365 | 128.9365 | 1137.6752 | 780 | 200 | 2117.6752 | 52.94% | 95% | 0% | -279.1762 | -150.2397 | -3550 | -400 | -4100.2397 | 102.5% | 54.43% | 95% | 0% | 1436 | -244
[5 empty] | 2019-08-11 | 17 | 5335.5 | 1226 | -289 | 1 | 0 | 1515 | 252.6793 | 252.6793 | 252.6793 | 1137.6752 | 780 | 200 | 2117.6752 | 52.94% | 95% | 0% | -330.6636 | -77.9843 | -3550 | -400 | -4027.9843 | 100.7% | 54.43% | 95% | 0% | 1515 | -289
[5 empty] | 2019-08-11 | 18 | 5336 | 1233 | -331 | 1 | 0 | 1564 | 329.4312 | 329.4312 | 329.4312 | 1137.6752 | 780 | 200 | 2117.6752 | 52.94% | 95% | 0% | -378.7185 | -49.2874 | -3550 | -400 | -3999.2874 | 99.98% | 54.43% | 95% | 0% | 1564 | -331
[5 empty] | 2019-08-11 | 19 | 5336.5 | 1276 | -368 | 1 | 0 | 1644 | 454.7403 | 454.7403 | 454.7403 | 1137.6752 | 780 | 200 | 2117.6752 | 52.94% | 95% | 0% | -421.0526 | 33.6877 | -3550 | -400 | -3916.3123 | 97.91% | 54.42% | 95% | 0% | 1644 | -368
[5 empty] | 2019-08-11 | 20 | 5337 | 1300 | -399 | 1 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 1137.6752 | 780 | 200 | 2117.6752 | 52.94% | 95% | 0% | -456.5217 | 84.3686 | -3550 | -400 | -3865.6314 | 96.64% | 54.42% | 95% | 0% | 1699 | -399
[5 empty] | 2019-08-11 | 21 | 5337.5 | 1332 | -418 | 1 | 0 | 1750 | 620.7749 | 620.7749 | 620.7749 | 1137.6752 | 780 | 200 | 2117.6752 | 52.94% | 95% | 0% | -478.2609 | 142.5141 | -3550 | -400 | -3807.4859 | 95.19% | 54.42% | 95% | 0% | 1750 | -418
[5 empty] | 2019-08-11 | 22 | 5338 | 1317 | -451 | 1 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 1137.6752 | 780 | 200 | 2117.6752 | 52.94% | 95% | 0% | -516.0183 | 132.9512 | -3550 | -400 | -3817.0488 | 95.43% | 54.41% | 95% | 0% | 1768 | -451
[5 empty] | 2019-08-11 | 23 | 5338.5 | 1333 | -456 | 1 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 1137.6752 | 780 | 200 | 2117.6752 | 52.94% | 95% | 0% | -521.7391 | 160.124 | -3550 | -400 | -3789.876 | 94.75% | 54.41% | 95% | 0% | 1789 | -456
[5 empty] | 2019-08-11 | 24 | 5339 | 1279 | -515 | 1 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 1137.6752 | 780 | 200 | 2117.6752 | 52.94% | 95% | 0% | -589.2449 | 100.4501 | -3550 | -400 | -3849.5499 | 96.24% | 54.41% | 95% | 0% | 1794 | -515
[5 empty] | 2019-08-11 | 25 | 5339.5 | 1329 | -488 | 1 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 1137.6752 | 780 | 200 | 2117.6752 | 52.94% | 95% | 0% | -558.3524 | 167.3689 | -3550 | -400 | -3782.6311 | 94.57% | 54.4% | 95% | 0% | 1817 | -488
[5 empty] | 2019-08-11 | 26 | 5340 | 1318 | -494 | 1 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 1136.1088 | 780 | 200 | 2116.1088 | 52.9% | 95% | 0% | -565.2174 | 152.6721 | -3550 | -400 | -3797.3279 | 94.93% | 54.4% | 95% | 0% | 1812 | -494
[5 empty] | 2019-08-11 | 27 | 5340.5 | 1268 | -528 | 1 | 0 | 1796 | 692.8277 | 692.8277 | 692.8277 | 1136.1088 | 780 | 200 | 2116.1088 | 52.9% | 95% | 0% | -604.119 | 88.7087 | -3550 | -400 | -3861.2913 | 96.53% | 54.4% | 95% | 0% | 1796 | -528
[5 empty] | 2019-08-11 | 28 | 5341 | 1253 | -517 | 1 | 0 | 1770 | 652.1022 | 652.1022 | 652.1022 | 1136.1088 | 780 | 200 | 2116.1088 | 52.9% | 95% | 0% | -591.5332 | 60.569 | -3550 | -400 | -3889.431 | 97.24% | 54.39% | 95% | 0% | 1770 | -517
[5 empty] | 2019-08-11 | 29 | 5341.5 | 1265 | -489 | 1 | 0 | 1754 | 627.0404 | 627.0404 | 627.0404 | 1136.1088 | 780 | 200 | 2116.1088 | 52.9% | 95% | 0% | -559.4966 | 67.5438 | -3550 | -400 | -3882.4562 | 97.06% | 54.39% | 95% | 0% | 1754 | -489
[5 empty] | 2019-08-11 | 30 | 5342 | 1242 | -515 | 1 | 0 | 1757 | 631.7395 | 631.7395 | 631.7395 | 1136.1088 | 780 | 200 | 2116.1088 | 52.9% | 95% | 0% | -589.2449 | 42.4946 | -3550 | -400 | -3907.5054 | 97.69% | 54.39% | 95% | 0% | 1757 | -515
[5 empty] | 2019-08-11 | 31 | 5342.5 | 1317 | -474 | 1 | 0 | 1791 | 684.9959 | 684.9959 | 684.9959 | 1136.1088 | 780 | 200 | 2116.1088 | 52.9% | 95% | 0% | -542.3341 | 142.6618 | -3550 | -400 | -3807.3382 | 95.18% | 54.38% | 95% | 0% | 1791 | -474
[5 empty] | 2019-08-11 | 32 | 5343 | 1399 | -434 | 1 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 1136.1088 | 780 | 200 | 2116.1088 | 52.9% | 95% | 0% | -496.5675 | 254.2157 | -3550 | -400 | -3695.7843 | 92.39% | 54.38% | 95% | 0% | 1833 | -434
[5 empty] | 2019-08-11 | 33 | 5343.5 | 1520 | -373 | 1 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 1136.1088 | 780 | 200 | 2116.1088 | 52.9% | 95% | 0% | -426.7735 | 417.9916 | -3550 | -400 | -3532.0084 | 88.3% | 54.38% | 95% | 0% | 1893 | -373
[5 empty] | 2019-08-11 | 34 | 5344 | 1620 | -328 | 1 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -375.286 | 555.629 | -3550 | -400 | -3394.371 | 84.86% | 54.38% | 95% | 0% | 1948 | -328
[5 empty] | 2019-08-11 | 35 | 5344.5 | 1725 | -294 | 1 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -336.3844 | 705.7425 | -3550 | -400 | -3244.2575 | 81.11% | 54.38% | 95% | 0% | 2019 | -294
[5 empty] | 2019-08-11 | 36 | 5345 | 1797 | -260 | 1 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -297.4828 | 804.166 | -3550 | -400 | -3145.834 | 78.65% | 54.38% | 95% | 0% | 2057 | -260
[5 empty] | 2019-08-11 | 37 | 5345.5 | 1852 | -229 | 1 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -262.0137 | 877.2278 | -3550 | -400 | -3072.7722 | 76.82% | 54.37% | 95% | 0% | 2081 | -229
[5 empty] | 2019-08-11 | 38 | 5346 | 1901 | -188 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -215.103 | 936.6695 | -3550 | -400 | -3013.3305 | 75.33% | 54.37% | 95% | 0% | 2089 | -188
[5 empty] | 2019-08-11 | 39 | 5346.5 | 1926 | -154 | 1 | 0 | 2080 | 1137.6752 | 1137.6752 | 1137.6752 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -176.2014 | 961.4738 | -3550 | -400 | -2988.5262 | 74.71% | 54.36% | 95% | 0% | 2080 | -154
[5 empty] | 2019-08-11 | 40 | 5347 | 1938 | -128 | 1 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -146.4531 | 969.293 | -3550 | -400 | -2980.707 | 74.52% | 54.35% | 95% | 0% | 2066 | -128
[5 empty] | 2019-08-11 | 41 | 5347.5 | 1946 | -109 | 1 | 0 | 2055 | 1098.5161 | 1098.5161 | 1098.5161 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -124.714 | 973.8021 | -3550 | -400 | -2976.1979 | 74.4% | 54.35% | 95% | 0% | 2055 | -109
[5 empty] | 2019-08-11 | 42 | 5348 | 1962 | -100 | 1 | 0 | 2062 | 1109.4806 | 1109.4806 | 1109.4806 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -114.4165 | 995.0642 | -3550 | -400 | -2954.9358 | 73.87% | 54.34% | 95% | 0% | 2062 | -100
[5 empty] | 2019-08-11 | 43 | 5348.5 | 1974 | -96 | 1 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -109.8398 | 1012.1717 | -3550 | -400 | -2937.8283 | 73.45% | 54.34% | 95% | 0% | 2070 | -96
[5 empty] | 2019-08-11 | 44 | 5349 | 1917 | -92 | 0 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -105.2632 | 921.2002 | -2750 | -200 | -2028.7998 | 50.72% | 54.34% | 95% | 0% | 2009 | -92
[5 empty] | 2019-08-11 | 45 | 5349.5 | 1860 | -89 | 0 | 0 | 1949 | 932.4815 | 932.4815 | 932.4815 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -101.8307 | 830.6508 | -2750 | -200 | -2119.3492 | 52.98% | 54.33% | 95% | 0% | 1949 | -89
[5 empty] | 2019-08-11 | 46 | 5350 | 1760 | -87 | 0 | 0 | 1847 | 772.7123 | 772.7123 | 772.7123 | 1134.5425 | 780 | 200 | 2114.5425 | 52.86% | 95% | 0% | -99.5423 | 673.1699 | -2750 | -200 | -2276.8301 | 56.92% | 54.32% | 95% | 0% | 1847 | -87
[5 empty] | 2019-08-11 | 47 | 5350.5 | 1652 | -85 | 0 | 0 | 1737 | 600.4122 | 600.4122 | 600.4122 | 1132.9761 | 780 | 200 | 2112.9761 | 52.82% | 95% | 0% | -97.254 | 503.1582 | -2750 | -200 | -2446.8418 | 61.17% | 54.32% | 95% | 0% | 1737 | -85
[5 empty] | 2019-08-11 | 48 | 5351 | 1566 | -83 | 0 | 0 | 1649 | 462.5721 | 462.5721 | 462.5721 | 1132.9761 | 780 | 200 | 2112.9761 | 52.82% | 95% | 0% | -94.9657 | 367.6065 | -2750 | -200 | -2582.3935 | 64.56% | 54.32% | 95% | 0% | 1649 | -83
[5 empty] | 2019-08-12 | 1 | 5351.5 | 1487 | -79 | 0 | 0 | 1566 | 332.5639 | 332.5639 | 332.5639 | 1132.9761 | 780 | 200 | 2112.9761 | 52.82% | 95% | 0% | -90.389 | 242.1749 | -2750 | -200 | -2707.8251 | 67.7% | 54.31% | 95% | 0% | 1566 | -79
[5 empty] | 2019-08-12 | 2 | 5352 | 1439 | -74 | 0 | 0 | 1513 | 249.5466 | 249.5466 | 249.5466 | 1132.9761 | 780 | 200 | 2112.9761 | 52.82% | 95% | 0% | -84.6682 | 164.8784 | -2750 | -200 | -2785.1216 | 69.63% | 54.3% | 95% | 0% | 1513 | -74
[5 empty] | 2019-08-12 | 3 | 5352.5 | 1414 | -73 | 0 | 0 | 1487 | 208.8211 | 208.8211 | 208.8211 | 1132.9761 | 780 | 200 | 2112.9761 | 52.82% | 95% | 0% | -83.524 | 125.2971 | -2750 | -200 | -2824.7029 | 70.62% | 54.3% | 95% | 0% | 1487 | -73
[5 empty] | 2019-08-12 | 4 | 5353 | 1398 | -72 | 0 | 0 | 1470 | 182.1929 | 182.1929 | 182.1929 | 1132.9761 | 780 | 200 | 2112.9761 | 52.82% | 95% | 0% | -82.3799 | 99.813 | -2750 | -200 | -2850.187 | 71.25% | 54.3% | 95% | 0% | 1470 | -72
[5 empty] | 2019-08-12 | 5 | 5353.5 | 1384 | -71 | 0 | 0 | 1455 | 158.6974 | 158.6974 | 158.6974 | 1132.9761 | 780 | 200 | 2112.9761 | 52.82% | 95% | 0% | -81.2357 | 77.4617 | -2750 | -200 | -2872.5383 | 71.81% | 54.3% | 95% | 0% | 1455 | -71
[5 empty] | 2019-08-12 | 6 | 5354 | 1371 | -71 | 0 | 0 | 1442 | 138.3347 | 138.3347 | 138.3347 | 1132.9761 | 780 | 200 | 2112.9761 | 52.82% | 95% | 0% | -81.2357 | 57.099 | -2750 | -200 | -2892.901 | 72.32% | 54.29% | 95% | 0% | 1442 | -71
[5 empty] | 2019-08-12 | 7 | 5354.5 | 1363 | -70 | 0 | 0 | 1433 | 124.2374 | 124.2374 | 124.2374 | 1132.9761 | 780 | 200 | 2112.9761 | 52.82% | 95% | 0% | -80.0915 | 44.1459 | -2750 | -200 | -2905.8541 | 72.65% | 54.29% | 95% | 0% | 1433 | -70
[5 empty] | 2019-08-12 | 8 | 5355 | 1362 | -69 | 0 | 0 | 1431 | 121.1047 | 121.1047 | 121.1047 | 1132.9761 | 780 | 200 | 2112.9761 | 52.82% | 95% | 0% | -78.9474 | 42.1573 | -2750 | -200 | -2907.8427 | 72.7% | 54.29% | 95% | 0% | 1431 | -69
[5 empty] | 2019-08-12 | 9 | 5355.5 | 1372 | -67 | 0 | 0 | 1439 | 133.6356 | 133.6356 | 133.6356 | 1132.9761 | 780 | 200 | 2112.9761 | 52.82% | 95% | 0% | -76.659 | 56.9766 | -2750 | -200 | -2893.0234 | 72.33% | 54.29% | 95% | 0% | 1439 | -67
[5 empty] | 2019-08-12 | 10 | 5356 | 1397 | -65 | 0 | 0 | 1462 | 169.662 | 169.662 | 169.662 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -74.3707 | 95.2913 | -2750 | -200 | -2854.7087 | 71.37% | 54.28% | 95% | 0% | 1462 | -65
[5 empty] | 2019-08-12 | 11 | 5356.5 | 1460 | -64 | 0 | 0 | 1524 | 266.7766 | 266.7766 | 266.7766 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -73.2265 | 193.55 | -2750 | -200 | -2756.45 | 68.91% | 54.28% | 95% | 0% | 1524 | -64
[5 empty] | 2019-08-12 | 12 | 5357 | 1516 | -63 | 0 | 0 | 1579 | 352.9266 | 352.9266 | 352.9266 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -72.0824 | 280.8442 | -2750 | -200 | -2669.1558 | 66.73% | 54.28% | 95% | 0% | 1579 | -63
[5 empty] | 2019-08-12 | 13 | 5357.5 | 1675 | -67 | 0 | 0 | 1742 | 608.244 | 608.244 | 608.244 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -76.659 | 531.585 | -2750 | -200 | -2418.415 | 60.46% | 54.27% | 95% | 0% | 1742 | -67
[5 empty] | 2019-08-12 | 14 | 5358 | 1802 | -87 | 0 | 0 | 1889 | 838.4996 | 838.4996 | 838.4996 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -99.5423 | 738.9573 | -2750 | -200 | -2211.0427 | 55.28% | 54.26% | 95% | 0% | 1889 | -87
[5 empty] | 2019-08-12 | 15 | 5358.5 | 1949 | -112 | 0 | 0 | 2061 | 1107.9143 | 1107.9143 | 1107.9143 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -128.1465 | 979.7678 | -2750 | -200 | -1970.2322 | 49.26% | 54.26% | 95% | 0% | 2061 | -112
[5 empty] | 2019-08-12 | 16 | 5359 | 2035 | -148 | 1 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -169.3364 | 1129.6743 | -3550 | -400 | -2820.3257 | 70.51% | 54.25% | 95% | 0% | 2183 | -148
[5 empty] | 2019-08-12 | 17 | 5359.5 | 2091 | -184 | 1 | 0 | 2275 | 1443.1162 | 1443.1162 | 1443.1162 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -210.5263 | 1232.5899 | -3550 | -400 | -2717.4101 | 67.94% | 54.25% | 95% | 0% | 2275 | -184
[5 empty] | 2019-08-12 | 18 | 5360 | 2086 | -230 | 1 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -263.1579 | 1244.1793 | -3550 | -400 | -2705.8207 | 67.65% | 54.25% | 95% | 0% | 2316 | -230
[5 empty] | 2019-08-12 | 19 | 5360.5 | 2026 | -281 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -321.5103 | 1171.7296 | -3550 | -400 | -2778.2704 | 69.46% | 54.23% | 95% | 0% | 2307 | -281
[5 empty] | 2019-08-12 | 20 | 5361 | 1931 | -326 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -372.9977 | 1041.924 | -3550 | -400 | -2908.076 | 72.7% | 54.23% | 95% | 0% | 2257 | -326
[5 empty] | 2019-08-12 | 21 | 5361.5 | 1874 | -355 | 1 | 0 | 2229 | 1371.0635 | 1371.0635 | 1371.0635 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -406.1785 | 964.885 | -3550 | -400 | -2985.115 | 74.63% | 54.22% | 95% | 0% | 2229 | -355
[5 empty] | 2019-08-12 | 22 | 5362 | 1855 | -376 | 1 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -430.2059 | 943.9903 | -3550 | -400 | -3006.0097 | 75.15% | 54.22% | 95% | 0% | 2231 | -376
[5 empty] | 2019-08-12 | 23 | 5362.5 | 1820 | -395 | 1 | 0 | 2215 | 1349.1344 | 1349.1344 | 1349.1344 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -451.9451 | 897.1893 | -3550 | -400 | -3052.8107 | 76.32% | 54.22% | 95% | 0% | 2215 | -395
[5 empty] | 2019-08-12 | 24 | 5363 | 1816 | -406 | 1 | 0 | 2222 | 1360.0989 | 1360.0989 | 1360.0989 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -464.5309 | 895.568 | -3550 | -400 | -3054.432 | 76.36% | 54.22% | 95% | 0% | 2222 | -406
[5 empty] | 2019-08-12 | 25 | 5363.5 | 1827 | -419 | 1 | 0 | 2246 | 1397.6917 | 1397.6917 | 1397.6917 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -479.405 | 918.2866 | -3550 | -400 | -3031.7134 | 75.79% | 54.22% | 95% | 0% | 2246 | -419
[5 empty] | 2019-08-12 | 26 | 5364 | 1798 | -436 | 1 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 1131.4097 | 780 | 200 | 2111.4097 | 52.79% | 95% | 0% | -498.8558 | 880.0395 | -3550 | -400 | -3069.9605 | 76.75% | 54.21% | 95% | 0% | 2234 | -436
[5 empty] | 2019-08-12 | 27 | 5364.5 | 1749 | -471 | 1 | 0 | 2220 | 1356.9662 | 1356.9662 | 1356.9662 | 1129.8434 | 780 | 200 | 2109.8434 | 52.75% | 95% | 0% | -538.9016 | 818.0646 | -3550 | -400 | -3131.9354 | 78.3% | 54.21% | 95% | 0% | 2220 | -471
[5 empty] | 2019-08-12 | 28 | 5365 | 1707 | -487 | 1 | 0 | 2194 | 1316.2407 | 1316.2407 | 1316.2407 | 1129.8434 | 780 | 200 | 2109.8434 | 52.75% | 95% | 0% | -557.2082 | 759.0325 | -3550 | -400 | -3190.9675 | 79.77% | 54.21% | 95% | 0% | 2194 | -487
[5 empty] | 2019-08-12 | 29 | 5365.5 | 1711 | -460 | 1 | 0 | 2171 | 1280.2143 | 1280.2143 | 1280.2143 | 1129.8434 | 780 | 200 | 2109.8434 | 52.75% | 95% | 0% | -526.3158 | 753.8986 | -3550 | -400 | -3196.1014 | 79.9% | 54.21% | 95% | 0% | 2171 | -460
[5 empty] | 2019-08-12 | 30 | 5366 | 1691 | -468 | 1 | 0 | 2159 | 1261.418 | 1261.418 | 1261.418 | 1129.8434 | 780 | 200 | 2109.8434 | 52.75% | 95% | 0% | -535.4691 | 725.9489 | -3550 | -400 | -3224.0511 | 80.6% | 54.2% | 95% | 0% | 2159 | -468
[5 empty] | 2019-08-12 | 31 | 5366.5 | 1694 | -457 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1129.8434 | 780 | 200 | 2109.8434 | 52.75% | 95% | 0% | -522.8833 | 726.0038 | -3550 | -400 | -3223.9962 | 80.6% | 54.2% | 95% | 0% | 2151 | -457
[5 empty] | 2019-08-12 | 32 | 5367 | 1700 | -451 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1129.8434 | 780 | 200 | 2109.8434 | 52.75% | 95% | 0% | -516.0183 | 732.8688 | -3550 | -400 | -3217.1312 | 80.43% | 54.2% | 95% | 0% | 2151 | -451
[5 empty] | 2019-08-12 | 33 | 5367.5 | 1759 | -411 | 1 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 1129.8434 | 780 | 200 | 2109.8434 | 52.75% | 95% | 0% | -470.2517 | 808.3963 | -3550 | -400 | -3141.6037 | 78.54% | 54.2% | 95% | 0% | 2170 | -411
[5 empty] | 2019-08-12 | 34 | 5368 | 1877 | -369 | 1 | 0 | 2246 | 1397.6917 | 1397.6917 | 1397.6917 | 1129.8434 | 780 | 200 | 2109.8434 | 52.75% | 95% | 0% | -422.1968 | 975.4949 | -3550 | -400 | -2974.5051 | 74.36% | 54.19% | 95% | 0% | 2246 | -369
[5 empty] | 2019-08-12 | 35 | 5368.5 | 1995 | -330 | 1 | 0 | 2325 | 1521.4345 | 1521.4345 | 1521.4345 | 1129.8434 | 780 | 200 | 2109.8434 | 52.75% | 95% | 0% | -377.5744 | 1143.8601 | -3550 | -400 | -2806.1399 | 70.15% | 54.18% | 95% | 0% | 2325 | -330
[5 empty] | 2019-08-12 | 36 | 5369 | 2085 | -276 | 1 | 0 | 2361 | 1577.8236 | 1577.8236 | 1577.8236 | 1129.8434 | 780 | 200 | 2109.8434 | 52.75% | 95% | 0% | -315.7895 | 1262.0341 | -3550 | -400 | -2687.9659 | 67.2% | 54.18% | 95% | 0% | 2361 | -276
[5 empty] | 2019-08-12 | 37 | 5369.5 | 2139 | -220 | 1 | 0 | 2359 | 1574.6908 | 1574.6908 | 1574.6908 | 1129.8434 | 780 | 200 | 2109.8434 | 52.75% | 95% | 0% | -251.7162 | 1322.9746 | -3550 | -400 | -2627.0254 | 65.68% | 54.17% | 95% | 0% | 2359 | -220
[5 empty] | 2019-08-12 | 38 | 5370 | 2211 | -179 | 1 | 0 | 2390 | 1623.2481 | 1623.2481 | 1623.2481 | 1128.277 | 780 | 200 | 2108.277 | 52.71% | 95% | 0% | -204.8055 | 1418.4427 | -3550 | -400 | -2531.5573 | 63.29% | 54.17% | 95% | 0% | 2390 | -179
[5 empty] | 2019-08-12 | 39 | 5370.5 | 2243 | -128 | 1 | 0 | 2371 | 1593.4872 | 1593.4872 | 1593.4872 | 1128.277 | 780 | 200 | 2108.277 | 52.71% | 95% | 0% | -146.4531 | 1447.0341 | -3550 | -400 | -2502.9659 | 62.57% | 54.17% | 95% | 0% | 2371 | -128
[5 empty] | 2019-08-12 | 40 | 5371 | 2287 | -86 | 1 | 0 | 2373 | 1596.62 | 1596.62 | 1596.62 | 1128.277 | 780 | 200 | 2108.277 | 52.71% | 95% | 0% | -98.3982 | 1498.2218 | -3550 | -400 | -2451.7782 | 61.29% | 54.17% | 95% | 0% | 2373 | -86
[5 empty] | 2019-08-12 | 41 | 5371.5 | 2281 | -60 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 1128.277 | 780 | 200 | 2108.277 | 52.71% | 95% | 0% | -68.6499 | 1477.8464 | -3550 | -400 | -2472.1536 | 61.8% | 54.16% | 95% | 0% | 2341 | -60
[5 empty] | 2019-08-12 | 42 | 5372 | 2280 | -54 | 1 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 1128.277 | 780 | 200 | 2108.277 | 52.71% | 95% | 0% | -61.7849 | 1473.7468 | -3550 | -400 | -2476.2532 | 61.91% | 54.15% | 95% | 0% | 2334 | -54
[5 empty] | 2019-08-12 | 43 | 5372.5 | 2290 | -55 | 1 | 0 | 2345 | 1552.7617 | 1552.7617 | 1552.7617 | 1128.277 | 780 | 200 | 2108.277 | 52.71% | 95% | 0% | -62.9291 | 1489.8327 | -3550 | -400 | -2460.1673 | 61.5% | 54.15% | 95% | 0% | 2345 | -55
[5 empty] | 2019-08-12 | 44 | 5373 | 2209 | -55 | 0 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 1128.277 | 780 | 200 | 2108.277 | 52.71% | 95% | 0% | -62.9291 | 1362.9572 | -2750 | -200 | -1587.0428 | 39.68% | 54.15% | 95% | 0% | 2264 | -55
[5 empty] | 2019-08-12 | 45 | 5373.5 | 2092 | -56 | 0 | 0 | 2148 | 1244.188 | 1244.188 | 1244.188 | 1128.277 | 780 | 200 | 2108.277 | 52.71% | 95% | 0% | -64.0732 | 1180.1147 | -2750 | -200 | -1769.8853 | 44.25% | 54.15% | 95% | 0% | 2148 | -56
[5 empty] | 2019-08-12 | 46 | 5374 | 1971 | -57 | 0 | 0 | 2028 | 1056.2242 | 1056.2242 | 1056.2242 | 1128.277 | 780 | 200 | 2108.277 | 52.71% | 95% | 0% | -65.2174 | 991.0068 | -2750 | -200 | -1958.9932 | 48.97% | 54.15% | 95% | 0% | 2028 | -57
[5 empty] | 2019-08-12 | 47 | 5374.5 | 1830 | -58 | 0 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 1128.277 | 780 | 200 | 2108.277 | 52.71% | 95% | 0% | -66.3616 | 770.5717 | -2750 | -200 | -2179.4283 | 54.49% | 54.14% | 95% | 0% | 1888 | -58
[5 empty] | 2019-08-12 | 48 | 5375 | 1711 | -60 | 0 | 0 | 1771 | 653.6686 | 653.6686 | 653.6686 | 1128.277 | 780 | 200 | 2108.277 | 52.71% | 95% | 0% | -68.6499 | 585.0187 | -2750 | -200 | -2364.9813 | 59.12% | 54.14% | 95% | 0% | 1771 | -60
[5 empty] | 2019-08-13 | 1 | 5375.5 | 1624 | -59 | 1 | 0 | 1683 | 515.8285 | 515.8285 | 515.8285 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -67.5057 | 448.3228 | -3550 | -400 | -3501.6772 | 87.54% | 54.14% | 95% | 0% | 1683 | -59
[5 empty] | 2019-08-13 | 2 | 5376 | 1573 | -57 | 1 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -65.2174 | 367.5938 | -3550 | -400 | -3582.4062 | 89.56% | 54.14% | 95% | 0% | 1630 | -57
[5 empty] | 2019-08-13 | 3 | 5376.5 | 1535 | -58 | 1 | 0 | 1593 | 374.8557 | 374.8557 | 374.8557 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -66.3616 | 308.4942 | -3550 | -400 | -3641.5058 | 91.04% | 54.14% | 95% | 0% | 1593 | -58
[5 empty] | 2019-08-13 | 4 | 5377 | 1526 | -58 | 1 | 0 | 1584 | 360.7585 | 360.7585 | 360.7585 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -66.3616 | 294.3969 | -3550 | -400 | -3655.6031 | 91.39% | 54.13% | 95% | 0% | 1584 | -58
[5 empty] | 2019-08-13 | 5 | 5377.5 | 1503 | -59 | 1 | 0 | 1562 | 326.2984 | 326.2984 | 326.2984 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -67.5057 | 258.7927 | -3550 | -400 | -3691.2073 | 92.28% | 54.13% | 95% | 0% | 1562 | -59
[5 empty] | 2019-08-13 | 6 | 5378 | 1469 | -60 | 1 | 0 | 1529 | 274.6084 | 274.6084 | 274.6084 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -68.6499 | 205.9585 | -3550 | -400 | -3744.0415 | 93.6% | 54.13% | 95% | 0% | 1529 | -60
[5 empty] | 2019-08-13 | 7 | 5378.5 | 1462 | -61 | 1 | 0 | 1523 | 265.2102 | 265.2102 | 265.2102 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -69.7941 | 195.4162 | -3550 | -400 | -3754.5838 | 93.86% | 54.12% | 95% | 0% | 1523 | -61
[5 empty] | 2019-08-13 | 8 | 5379 | 1451 | -61 | 1 | 0 | 1512 | 247.9802 | 247.9802 | 247.9802 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -69.7941 | 178.1862 | -3550 | -400 | -3771.8138 | 94.3% | 54.11% | 95% | 0% | 1512 | -61
[5 empty] | 2019-08-13 | 9 | 5379.5 | 1459 | -60 | 1 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -68.6499 | 190.2949 | -3550 | -400 | -3759.7051 | 93.99% | 54.11% | 95% | 0% | 1519 | -60
[5 empty] | 2019-08-13 | 10 | 5380 | 1477 | -59 | 1 | 0 | 1536 | 285.573 | 285.573 | 285.573 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -67.5057 | 218.0672 | -3550 | -400 | -3731.9328 | 93.3% | 54.11% | 95% | 0% | 1536 | -59
[5 empty] | 2019-08-13 | 11 | 5380.5 | 1530 | -58 | 1 | 0 | 1588 | 367.0239 | 367.0239 | 367.0239 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -66.3616 | 300.6624 | -3550 | -400 | -3649.3376 | 91.23% | 54.1% | 95% | 0% | 1588 | -58
[5 empty] | 2019-08-13 | 12 | 5381 | 1578 | -58 | 1 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -66.3616 | 375.8478 | -3550 | -400 | -3574.1522 | 89.35% | 54.1% | 95% | 0% | 1636 | -58
[5 empty] | 2019-08-13 | 13 | 5381.5 | 1715 | -66 | 1 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -75.5149 | 593.8174 | -3550 | -400 | -3356.1826 | 83.9% | 54.1% | 95% | 0% | 1781 | -66
[5 empty] | 2019-08-13 | 14 | 5382 | 1821 | -94 | 1 | 0 | 1915 | 879.2251 | 879.2251 | 879.2251 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -107.5515 | 771.6736 | -3550 | -400 | -3178.3264 | 79.46% | 54.09% | 95% | 0% | 1915 | -94
[5 empty] | 2019-08-13 | 15 | 5382.5 | 1919 | -144 | 1 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 1126.7106 | 780 | 200 | 2106.7106 | 52.67% | 95% | 0% | -164.7597 | 946.2873 | -3550 | -400 | -3003.7127 | 75.09% | 54.08% | 95% | 0% | 2063 | -144
[5 empty] | 2019-08-13 | 16 | 5383 | 1960 | -195 | 1 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -223.1121 | 1032.0404 | -3550 | -400 | -2917.9596 | 72.95% | 54.08% | 95% | 0% | 2155 | -195
[5 empty] | 2019-08-13 | 17 | 5383.5 | 1969 | -258 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -295.1945 | 1072.7362 | -3550 | -400 | -2877.2638 | 71.93% | 54.08% | 95% | 0% | 2227 | -258
[5 empty] | 2019-08-13 | 18 | 5384 | 1894 | -335 | 1 | 0 | 2229 | 1371.0635 | 1371.0635 | 1371.0635 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -383.2952 | 987.7683 | -3550 | -400 | -2962.2317 | 74.06% | 54.08% | 95% | 0% | 2229 | -335
[5 empty] | 2019-08-13 | 19 | 5384.5 | 1815 | -400 | 1 | 0 | 2215 | 1349.1344 | 1349.1344 | 1349.1344 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -457.6659 | 891.4685 | -3550 | -400 | -3058.5315 | 76.46% | 54.08% | 95% | 0% | 2215 | -400
[5 empty] | 2019-08-13 | 20 | 5385 | 1723 | -470 | 1 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -537.7574 | 776.9169 | -3550 | -400 | -3173.0831 | 79.33% | 54.07% | 95% | 0% | 2193 | -470
[5 empty] | 2019-08-13 | 21 | 5385.5 | 1640 | -514 | 1 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -588.1007 | 665.4855 | -3550 | -400 | -3284.5145 | 82.11% | 54.06% | 95% | 0% | 2154 | -514
[5 empty] | 2019-08-13 | 22 | 5386 | 1604 | -549 | 1 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -628.1465 | 623.8733 | -3550 | -400 | -3326.1267 | 83.15% | 54.06% | 95% | 0% | 2153 | -549
[5 empty] | 2019-08-13 | 23 | 5386.5 | 1605 | -537 | 1 | 0 | 2142 | 1234.7898 | 1234.7898 | 1234.7898 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -614.4165 | 620.3733 | -3550 | -400 | -3329.6267 | 83.24% | 54.05% | 95% | 0% | 2142 | -537
[5 empty] | 2019-08-13 | 24 | 5387 | 1579 | -570 | 1 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -652.1739 | 593.5804 | -3550 | -400 | -3356.4196 | 83.91% | 54.05% | 95% | 0% | 2149 | -570
[5 empty] | 2019-08-13 | 25 | 5387.5 | 1551 | -595 | 1 | 0 | 2146 | 1241.0552 | 1241.0552 | 1241.0552 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -680.778 | 560.2772 | -3550 | -400 | -3389.7228 | 84.74% | 54.05% | 95% | 0% | 2146 | -595
[5 empty] | 2019-08-13 | 26 | 5388 | 1514 | -619 | 1 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -708.238 | 512.4545 | -3550 | -400 | -3437.5455 | 85.94% | 54.05% | 95% | 0% | 2133 | -619
[5 empty] | 2019-08-13 | 27 | 5388.5 | 1476 | -629 | 1 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -719.6796 | 457.1547 | -3550 | -400 | -3492.8453 | 87.32% | 54.05% | 95% | 0% | 2105 | -629
[5 empty] | 2019-08-13 | 28 | 5389 | 1442 | -647 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -740.2746 | 411.4979 | -3550 | -400 | -3538.5021 | 88.46% | 54.04% | 95% | 0% | 2089 | -647
[5 empty] | 2019-08-13 | 29 | 5389.5 | 1434 | -629 | 1 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -719.6796 | 391.3674 | -3550 | -400 | -3558.6326 | 88.97% | 54.04% | 95% | 0% | 2063 | -629
[5 empty] | 2019-08-13 | 30 | 5390 | 1458 | -598 | 1 | 0 | 2056 | 1100.0824 | 1100.0824 | 1100.0824 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -684.2105 | 415.8719 | -3550 | -400 | -3534.1281 | 88.35% | 54.04% | 95% | 0% | 2056 | -598
[5 empty] | 2019-08-13 | 31 | 5390.5 | 1508 | -558 | 1 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -638.4439 | 477.3021 | -3550 | -400 | -3472.6979 | 86.82% | 54.03% | 95% | 0% | 2066 | -558
[5 empty] | 2019-08-13 | 32 | 5391 | 1557 | -527 | 1 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -602.9748 | 540.9658 | -3550 | -400 | -3409.0342 | 85.23% | 54.03% | 95% | 0% | 2084 | -527
[5 empty] | 2019-08-13 | 33 | 5391.5 | 1646 | -469 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -536.6133 | 655.8847 | -3550 | -400 | -3294.1153 | 82.35% | 54.03% | 95% | 0% | 2115 | -469
[5 empty] | 2019-08-13 | 34 | 5392 | 1759 | -424 | 1 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 1125.1443 | 780 | 200 | 2105.1443 | 52.63% | 95% | 0% | -485.1259 | 813.8849 | -3550 | -400 | -3136.1151 | 78.4% | 54.03% | 95% | 0% | 2183 | -424
[5 empty] | 2019-08-13 | 35 | 5392.5 | 1911 | -346 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 1123.5779 | 780 | 200 | 2103.5779 | 52.59% | 95% | 0% | -395.881 | 1019.0407 | -3550 | -400 | -2930.9593 | 73.27% | 54.02% | 95% | 0% | 2257 | -346
[5 empty] | 2019-08-13 | 36 | 5393 | 2025 | -282 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1123.5779 | 780 | 200 | 2103.5779 | 52.59% | 95% | 0% | -322.6545 | 1170.5854 | -3550 | -400 | -2779.4146 | 69.49% | 54.02% | 95% | 0% | 2307 | -282
[5 empty] | 2019-08-13 | 37 | 5393.5 | 2109 | -227 | 1 | 0 | 2336 | 1538.6645 | 1538.6645 | 1538.6645 | 1123.5779 | 780 | 200 | 2103.5779 | 52.59% | 95% | 0% | -259.7254 | 1278.9391 | -3550 | -400 | -2671.0609 | 66.78% | 54.02% | 95% | 0% | 2336 | -227
[5 empty] | 2019-08-13 | 38 | 5394 | 2192 | -168 | 1 | 0 | 2360 | 1576.2572 | 1576.2572 | 1576.2572 | 1123.5779 | 780 | 200 | 2103.5779 | 52.59% | 95% | 0% | -192.2197 | 1384.0375 | -3550 | -400 | -2565.9625 | 64.15% | 54.02% | 95% | 0% | 2360 | -168
[5 empty] | 2019-08-13 | 39 | 5394.5 | 2260 | -115 | 1 | 0 | 2375 | 1599.7527 | 1599.7527 | 1599.7527 | 1123.5779 | 780 | 200 | 2103.5779 | 52.59% | 95% | 0% | -131.5789 | 1468.1737 | -3550 | -400 | -2481.8263 | 62.05% | 54.02% | 95% | 0% | 2375 | -115
[5 empty] | 2019-08-13 | 40 | 5395 | 2282 | -75 | 1 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 1123.5779 | 780 | 200 | 2103.5779 | 52.59% | 95% | 0% | -85.8124 | 1485.7458 | -3550 | -400 | -2464.2542 | 61.61% | 54.02% | 95% | 0% | 2357 | -75
[5 empty] | 2019-08-13 | 41 | 5395.5 | 2278 | -51 | 1 | 0 | 2329 | 1527.6999 | 1527.6999 | 1527.6999 | 1123.5779 | 780 | 200 | 2103.5779 | 52.59% | 95% | 0% | -58.3524 | 1469.3475 | -3550 | -400 | -2480.6525 | 62.02% | 54.01% | 95% | 0% | 2329 | -51
[5 empty] | 2019-08-13 | 42 | 5396 | 2305 | -46 | 1 | 0 | 2351 | 1562.1599 | 1562.1599 | 1562.1599 | 1123.5779 | 780 | 200 | 2103.5779 | 52.59% | 95% | 0% | -52.6316 | 1509.5284 | -3550 | -400 | -2440.4716 | 61.01% | 54.01% | 95% | 0% | 2351 | -46
[5 empty] | 2019-08-13 | 43 | 5396.5 | 2288 | -46 | 1 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 1123.5779 | 780 | 200 | 2103.5779 | 52.59% | 95% | 0% | -52.6316 | 1482.9002 | -3550 | -400 | -2467.0998 | 61.68% | 54.01% | 95% | 0% | 2334 | -46
[5 empty] | 2019-08-13 | 44 | 5397 | 2180 | -47 | 0 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1123.5779 | 780 | 200 | 2103.5779 | 52.59% | 95% | 0% | -53.7757 | 1314.155 | -2750 | -200 | -1635.845 | 40.9% | 54.01% | 95% | 0% | 2227 | -47
[5 empty] | 2019-08-13 | 45 | 5397.5 | 2121 | -49 | 0 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 1123.5779 | 780 | 200 | 2103.5779 | 52.59% | 95% | 0% | -56.0641 | 1222.5839 | -2750 | -200 | -1727.4161 | 43.19% | 54.01% | 95% | 0% | 2170 | -49
[5 empty] | 2019-08-13 | 46 | 5398 | 2007 | -50 | 0 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 1123.5779 | 780 | 200 | 2103.5779 | 52.59% | 95% | 0% | -57.2082 | 1044.4406 | -2750 | -200 | -1905.5594 | 47.64% | 53.99% | 95% | 0% | 2057 | -50
[5 empty] | 2019-08-13 | 47 | 5398.5 | 1868 | -51 | 0 | 0 | 1919 | 885.4905 | 885.4905 | 885.4905 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -58.3524 | 827.1381 | -2750 | -200 | -2122.8619 | 53.07% | 53.99% | 95% | 0% | 1919 | -51
[5 empty] | 2019-08-13 | 48 | 5399 | 1752 | -52 | 0 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -59.4966 | 645.862 | -2750 | -200 | -2304.138 | 57.6% | 53.99% | 95% | 0% | 1804 | -52
[5 empty] | 2019-08-14 | 1 | 5399.5 | 1656 | -54 | 0 | 0 | 1710 | 558.1204 | 558.1204 | 558.1204 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -61.7849 | 496.3355 | -2750 | -200 | -2453.6645 | 61.34% | 53.99% | 95% | 0% | 1710 | -54
[5 empty] | 2019-08-14 | 2 | 5400 | 1597 | -55 | 0 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -62.9291 | 404.3422 | -2750 | -200 | -2545.6578 | 63.64% | 53.99% | 95% | 0% | 1652 | -55
[5 empty] | 2019-08-14 | 3 | 5400.5 | 1563 | -55 | 0 | 0 | 1618 | 414.0148 | 414.0148 | 414.0148 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -62.9291 | 351.0858 | -2750 | -200 | -2598.9142 | 64.97% | 53.99% | 95% | 0% | 1618 | -55
[5 empty] | 2019-08-14 | 4 | 5401 | 1545 | -55 | 0 | 0 | 1600 | 385.8203 | 385.8203 | 385.8203 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -62.9291 | 322.8912 | -2750 | -200 | -2627.1088 | 65.68% | 53.95% | 95% | 0% | 1600 | -55
[5 empty] | 2019-08-14 | 5 | 5401.5 | 1515 | -56 | 0 | 0 | 1571 | 340.3957 | 340.3957 | 340.3957 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -64.0732 | 276.3225 | -2750 | -200 | -2673.6775 | 66.84% | 53.95% | 95% | 0% | 1571 | -56
[5 empty] | 2019-08-14 | 6 | 5402 | 1484 | -57 | 0 | 0 | 1541 | 293.4048 | 293.4048 | 293.4048 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -65.2174 | 228.1874 | -2750 | -200 | -2721.8126 | 68.05% | 53.93% | 95% | 0% | 1541 | -57
[5 empty] | 2019-08-14 | 7 | 5402.5 | 1474 | -57 | 0 | 0 | 1531 | 277.7411 | 277.7411 | 277.7411 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -65.2174 | 212.5237 | -2750 | -200 | -2737.4763 | 68.44% | 53.93% | 95% | 0% | 1531 | -57
[5 empty] | 2019-08-14 | 8 | 5403 | 1473 | -57 | 0 | 0 | 1530 | 276.1748 | 276.1748 | 276.1748 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -65.2174 | 210.9574 | -2750 | -200 | -2739.0426 | 68.48% | 53.93% | 95% | 0% | 1530 | -57
[5 empty] | 2019-08-14 | 9 | 5403.5 | 1473 | -58 | 0 | 0 | 1531 | 277.7411 | 277.7411 | 277.7411 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -66.3616 | 211.3796 | -2750 | -200 | -2738.6204 | 68.47% | 53.93% | 95% | 0% | 1531 | -58
[5 empty] | 2019-08-14 | 10 | 5404 | 1492 | -58 | 0 | 0 | 1550 | 307.5021 | 307.5021 | 307.5021 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -66.3616 | 241.1405 | -2750 | -200 | -2708.8595 | 67.72% | 53.92% | 95% | 0% | 1550 | -58
[5 empty] | 2019-08-14 | 11 | 5404.5 | 1528 | -60 | 0 | 0 | 1588 | 367.0239 | 367.0239 | 367.0239 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -68.6499 | 298.374 | -2750 | -200 | -2651.626 | 66.29% | 53.92% | 95% | 0% | 1588 | -60
[5 empty] | 2019-08-14 | 12 | 5405 | 1589 | -62 | 0 | 0 | 1651 | 465.7049 | 465.7049 | 465.7049 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -70.9382 | 394.7666 | -2750 | -200 | -2555.2334 | 63.88% | 53.92% | 95% | 0% | 1651 | -62
[5 empty] | 2019-08-14 | 13 | 5405.5 | 1744 | -67 | 0 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -76.659 | 639.6641 | -2750 | -200 | -2310.3359 | 57.76% | 53.92% | 95% | 0% | 1811 | -67
[5 empty] | 2019-08-14 | 14 | 5406 | 1869 | -79 | 0 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -90.389 | 840.5261 | -2750 | -200 | -2109.4739 | 52.74% | 53.91% | 95% | 0% | 1948 | -79
[5 empty] | 2019-08-14 | 15 | 5406.5 | 2034 | -95 | 1 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 1122.0115 | 780 | 200 | 2102.0115 | 52.55% | 95% | 0% | -108.6957 | 1105.7314 | -3550 | -400 | -2844.2686 | 71.11% | 53.91% | 95% | 0% | 2129 | -95
[5 empty] | 2019-08-14 | 16 | 5407 | 2122 | -127 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1120.4452 | 780 | 200 | 2100.4452 | 52.51% | 95% | 0% | -145.3089 | 1257.0818 | -3550 | -400 | -2692.9182 | 67.32% | 53.9% | 95% | 0% | 2249 | -127
[5 empty] | 2019-08-14 | 17 | 5407.5 | 2226 | -145 | 1 | 0 | 2371 | 1593.4872 | 1593.4872 | 1593.4872 | 1120.4452 | 780 | 200 | 2100.4452 | 52.51% | 95% | 0% | -165.9039 | 1427.5833 | -3550 | -400 | -2522.4167 | 63.06% | 53.9% | 95% | 0% | 2371 | -145
[5 empty] | 2019-08-14 | 18 | 5408 | 2251 | -166 | 1 | 0 | 2417 | 1665.54 | 1665.54 | 1665.54 | 1120.4452 | 780 | 200 | 2100.4452 | 52.51% | 95% | 0% | -189.9314 | 1475.6086 | -3550 | -400 | -2474.3914 | 61.86% | 53.9% | 95% | 0% | 2417 | -166
[5 empty] | 2019-08-14 | 19 | 5408.5 | 2239 | -208 | 1 | 0 | 2447 | 1712.5309 | 1712.5309 | 1712.5309 | 1120.4452 | 780 | 200 | 2100.4452 | 52.51% | 95% | 0% | -237.9863 | 1474.5446 | -3550 | -400 | -2475.4554 | 61.89% | 53.9% | 95% | 0% | 2447 | -208
[5 empty] | 2019-08-14 | 20 | 5409 | 2249 | -210 | 1 | 0 | 2459 | 1731.3273 | 1731.3273 | 1731.3273 | 1120.4452 | 780 | 200 | 2100.4452 | 52.51% | 95% | 0% | -240.2746 | 1491.0527 | -3550 | -400 | -2458.9473 | 61.47% | 53.89% | 95% | 0% | 2459 | -210
[5 empty] | 2019-08-14 | 21 | 5409.5 | 2264 | -222 | 1 | 0 | 2486 | 1773.6191 | 1773.6191 | 1773.6191 | 1120.4452 | 780 | 200 | 2100.4452 | 52.51% | 95% | 0% | -254.0046 | 1519.6145 | -3550 | -400 | -2430.3855 | 60.76% | 53.89% | 95% | 0% | 2486 | -222
[5 empty] | 2019-08-14 | 22 | 5410 | 2265 | -223 | 1 | 0 | 2488 | 1776.7519 | 1776.7519 | 1776.7519 | 1120.4452 | 780 | 200 | 2100.4452 | 52.51% | 95% | 0% | -255.1487 | 1521.6031 | -3550 | -400 | -2428.3969 | 60.71% | 53.88% | 95% | 0% | 2488 | -223
[5 empty] | 2019-08-14 | 23 | 5410.5 | 2290 | -206 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 1120.4452 | 780 | 200 | 2100.4452 | 52.51% | 95% | 0% | -235.6979 | 1553.5848 | -3550 | -400 | -2396.4152 | 59.91% | 53.88% | 95% | 0% | 2496 | -206
[5 empty] | 2019-08-14 | 24 | 5411 | 2303 | -211 | 1 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 1120.4452 | 780 | 200 | 2100.4452 | 52.51% | 95% | 0% | -241.4188 | 1576.0586 | -3550 | -400 | -2373.9414 | 59.35% | 53.87% | 95% | 0% | 2514 | -211
[5 empty] | 2019-08-14 | 25 | 5411.5 | 2311 | -225 | 1 | 0 | 2536 | 1851.9373 | 1851.9373 | 1851.9373 | 1120.4452 | 780 | 200 | 2100.4452 | 52.51% | 95% | 0% | -257.4371 | 1594.5003 | -3550 | -400 | -2355.4997 | 58.89% | 53.87% | 95% | 0% | 2536 | -225
[5 empty] | 2019-08-14 | 26 | 5412 | 2300 | -221 | 1 | 0 | 2521 | 1828.4419 | 1828.4419 | 1828.4419 | 1120.4452 | 780 | 200 | 2100.4452 | 52.51% | 95% | 0% | -252.8604 | 1575.5815 | -3550 | -400 | -2374.4185 | 59.36% | 53.87% | 95% | 0% | 2521 | -221
[5 empty] | 2019-08-14 | 27 | 5412.5 | 2276 | -228 | 1 | 0 | 2504 | 1801.8137 | 1801.8137 | 1801.8137 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -260.8696 | 1540.9441 | -3550 | -400 | -2409.0559 | 60.23% | 53.86% | 95% | 0% | 2504 | -228
[5 empty] | 2019-08-14 | 28 | 5413 | 2242 | -235 | 1 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -268.8787 | 1490.6431 | -3550 | -400 | -2459.3569 | 61.48% | 53.86% | 95% | 0% | 2477 | -235
[5 empty] | 2019-08-14 | 29 | 5413.5 | 2238 | -230 | 1 | 0 | 2468 | 1745.4246 | 1745.4246 | 1745.4246 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -263.1579 | 1482.2667 | -3550 | -400 | -2467.7333 | 61.69% | 53.86% | 95% | 0% | 2468 | -230
[5 empty] | 2019-08-14 | 30 | 5414 | 2237 | -219 | 1 | 0 | 2456 | 1726.6282 | 1726.6282 | 1726.6282 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -250.5721 | 1476.0561 | -3550 | -400 | -2473.9439 | 61.85% | 53.86% | 95% | 0% | 2456 | -219
[5 empty] | 2019-08-14 | 31 | 5414.5 | 2221 | -223 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -255.1487 | 1452.6831 | -3550 | -400 | -2497.3169 | 62.43% | 53.86% | 95% | 0% | 2444 | -223
[5 empty] | 2019-08-14 | 32 | 5415 | 2239 | -219 | 1 | 0 | 2458 | 1729.7609 | 1729.7609 | 1729.7609 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -250.5721 | 1479.1888 | -3550 | -400 | -2470.8112 | 61.77% | 53.85% | 95% | 0% | 2458 | -219
[5 empty] | 2019-08-14 | 33 | 5415.5 | 2266 | -199 | 1 | 0 | 2465 | 1740.7255 | 1740.7255 | 1740.7255 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -227.6888 | 1513.0367 | -3550 | -400 | -2436.9633 | 60.92% | 53.85% | 95% | 0% | 2465 | -199
[5 empty] | 2019-08-14 | 34 | 5416 | 2318 | -196 | 1 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -224.2563 | 1593.221 | -3550 | -400 | -2356.779 | 58.92% | 53.84% | 95% | 0% | 2514 | -196
[5 empty] | 2019-08-14 | 35 | 5416.5 | 2375 | -177 | 1 | 0 | 2552 | 1876.9992 | 1876.9992 | 1876.9992 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -202.5172 | 1674.482 | -3550 | -400 | -2275.518 | 56.89% | 53.84% | 95% | 0% | 2552 | -177
[5 empty] | 2019-08-14 | 36 | 5417 | 2422 | -161 | 1 | 0 | 2583 | 1925.5565 | 1925.5565 | 1925.5565 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -184.2105 | 1741.3459 | -3550 | -400 | -2208.6541 | 55.22% | 53.84% | 95% | 0% | 2583 | -161
[5 empty] | 2019-08-14 | 37 | 5417.5 | 2424 | -146 | 1 | 0 | 2570 | 1905.1937 | 1905.1937 | 1905.1937 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -167.0481 | 1738.1457 | -3550 | -400 | -2211.8543 | 55.3% | 53.84% | 95% | 0% | 2570 | -146
[5 empty] | 2019-08-14 | 38 | 5418 | 2410 | -133 | 1 | 0 | 2543 | 1862.9019 | 1862.9019 | 1862.9019 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -152.1739 | 1710.728 | -3550 | -400 | -2239.272 | 55.98% | 53.83% | 95% | 0% | 2543 | -133
[5 empty] | 2019-08-14 | 39 | 5418.5 | 2398 | -113 | 1 | 0 | 2511 | 1812.7782 | 1812.7782 | 1812.7782 | 1118.8788 | 780 | 200 | 2098.8788 | 52.47% | 95% | 0% | -129.2906 | 1683.4876 | -3550 | -400 | -2266.5124 | 56.66% | 53.83% | 95% | 0% | 2511 | -113
[5 empty] | 2019-08-14 | 40 | 5419 | 2383 | -100 | 1 | 0 | 2483 | 1768.92 | 1768.92 | 1768.92 | 1117.3124 | 780 | 200 | 2097.3124 | 52.43% | 95% | 0% | -114.4165 | 1654.5036 | -3550 | -400 | -2295.4964 | 57.39% | 53.83% | 95% | 0% | 2483 | -100
[5 empty] | 2019-08-14 | 41 | 5419.5 | 2359 | -94 | 1 | 0 | 2453 | 1721.9291 | 1721.9291 | 1721.9291 | 1117.3124 | 780 | 200 | 2097.3124 | 52.43% | 95% | 0% | -107.5515 | 1614.3776 | -3550 | -400 | -2335.6224 | 58.39% | 53.83% | 95% | 0% | 2453 | -94
[5 empty] | 2019-08-14 | 42 | 5420 | 2346 | -92 | 1 | 0 | 2438 | 1698.4336 | 1698.4336 | 1698.4336 | 1117.3124 | 780 | 200 | 2097.3124 | 52.43% | 95% | 0% | -105.2632 | 1593.1705 | -3550 | -400 | -2356.8295 | 58.92% | 53.83% | 95% | 0% | 2438 | -92
[5 empty] | 2019-08-14 | 43 | 5420.5 | 2310 | -92 | 1 | 0 | 2402 | 1642.0445 | 1642.0445 | 1642.0445 | 1117.3124 | 780 | 200 | 2097.3124 | 52.43% | 95% | 0% | -105.2632 | 1536.7814 | -3550 | -400 | -2413.2186 | 60.33% | 53.83% | 95% | 0% | 2402 | -92
[5 empty] | 2019-08-14 | 44 | 5421 | 2180 | -92 | 0 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 1117.3124 | 780 | 200 | 2097.3124 | 52.43% | 95% | 0% | -105.2632 | 1333.154 | -2750 | -200 | -1616.846 | 40.42% | 53.82% | 95% | 0% | 2272 | -92
[5 empty] | 2019-08-14 | 45 | 5421.5 | 2049 | -94 | 0 | 0 | 2143 | 1236.3561 | 1236.3561 | 1236.3561 | 1117.3124 | 780 | 200 | 2097.3124 | 52.43% | 95% | 0% | -107.5515 | 1128.8047 | -2750 | -200 | -1821.1953 | 45.53% | 53.82% | 95% | 0% | 2143 | -94
[5 empty] | 2019-08-14 | 46 | 5422 | 1902 | -95 | 0 | 0 | 1997 | 1007.6669 | 1007.6669 | 1007.6669 | 1117.3124 | 780 | 200 | 2097.3124 | 52.43% | 95% | 0% | -108.6957 | 898.9713 | -2750 | -200 | -2051.0287 | 51.28% | 53.82% | 95% | 0% | 1997 | -95
[5 empty] | 2019-08-14 | 47 | 5422.5 | 1748 | -97 | 0 | 0 | 1845 | 769.5796 | 769.5796 | 769.5796 | 1117.3124 | 780 | 200 | 2097.3124 | 52.43% | 95% | 0% | -110.984 | 658.5956 | -2750 | -200 | -2291.4044 | 57.29% | 53.82% | 95% | 0% | 1845 | -97
[5 empty] | 2019-08-14 | 48 | 5423 | 1629 | -99 | 1 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 1117.3124 | 780 | 200 | 2097.3124 | 52.43% | 95% | 0% | -113.2723 | 473.0426 | -3550 | -400 | -3476.9574 | 86.92% | 53.81% | 95% | 0% | 1728 | -99
[5 empty] | 2019-08-15 | 1 | 5423.5 | 1550 | -104 | 1 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 1117.3124 | 780 | 200 | 2097.3124 | 52.43% | 95% | 0% | -118.9931 | 351.4108 | -3550 | -400 | -3598.5892 | 89.96% | 53.81% | 95% | 0% | 1654 | -104
[5 empty] | 2019-08-15 | 2 | 5424 | 1480 | -110 | 1 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 1117.3124 | 780 | 200 | 2097.3124 | 52.43% | 95% | 0% | -125.8581 | 244.2985 | -3550 | -400 | -3705.7015 | 92.64% | 53.81% | 95% | 0% | 1590 | -110
[5 empty] | 2019-08-15 | 3 | 5424.5 | 1435 | -112 | 1 | 0 | 1547 | 302.803 | 302.803 | 302.803 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -128.1465 | 174.6565 | -3550 | -400 | -3775.3435 | 94.38% | 53.8% | 95% | 0% | 1547 | -112
[5 empty] | 2019-08-15 | 4 | 5425 | 1393 | -115 | 1 | 0 | 1508 | 241.7148 | 241.7148 | 241.7148 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -131.5789 | 110.1358 | -3550 | -400 | -3839.8642 | 96% | 53.8% | 95% | 0% | 1508 | -115
[5 empty] | 2019-08-15 | 5 | 5425.5 | 1346 | -118 | 1 | 0 | 1464 | 172.7947 | 172.7947 | 172.7947 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -135.0114 | 37.7833 | -3550 | -400 | -3912.2167 | 97.81% | 53.8% | 95% | 0% | 1464 | -118
[5 empty] | 2019-08-15 | 6 | 5426 | 1323 | -121 | 1 | 0 | 1444 | 141.4674 | 141.4674 | 141.4674 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -138.4439 | 3.0235 | -3550 | -400 | -3946.9765 | 98.67% | 53.79% | 95% | 0% | 1444 | -121
[5 empty] | 2019-08-15 | 7 | 5426.5 | 1312 | -123 | 1 | 0 | 1435 | 127.3702 | 127.3702 | 127.3702 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -140.7323 | -13.3621 | -3550 | -400 | -3963.3621 | 99.08% | 53.79% | 95% | 0% | 1435 | -123
[5 empty] | 2019-08-15 | 8 | 5427 | 1301 | -125 | 1 | 0 | 1426 | 113.2729 | 113.2729 | 113.2729 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -143.0206 | -29.7477 | -3550 | -400 | -3979.7477 | 99.49% | 53.78% | 95% | 0% | 1426 | -125
[5 empty] | 2019-08-15 | 9 | 5427.5 | 1303 | -130 | 1 | 0 | 1433 | 124.2374 | 124.2374 | 124.2374 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -148.7414 | -24.504 | -3550 | -400 | -3974.504 | 99.36% | 53.78% | 95% | 0% | 1433 | -130
[5 empty] | 2019-08-15 | 10 | 5428 | 1298 | -135 | 1 | 0 | 1433 | 124.2374 | 124.2374 | 124.2374 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -154.4622 | -30.2248 | -3550 | -400 | -3980.2248 | 99.51% | 53.78% | 95% | 0% | 1433 | -135
[5 empty] | 2019-08-15 | 11 | 5428.5 | 1339 | -138 | 1 | 0 | 1477 | 193.1575 | 193.1575 | 193.1575 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -157.8947 | 35.2627 | -3550 | -400 | -3914.7373 | 97.87% | 53.77% | 95% | 0% | 1477 | -138
[5 empty] | 2019-08-15 | 12 | 5429 | 1387 | -141 | 1 | 0 | 1528 | 273.042 | 273.042 | 273.042 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -161.3272 | 111.7148 | -3550 | -400 | -3838.2852 | 95.96% | 53.77% | 95% | 0% | 1528 | -141
[5 empty] | 2019-08-15 | 13 | 5429.5 | 1532 | -152 | 1 | 0 | 1684 | 517.3949 | 517.3949 | 517.3949 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -173.913 | 343.4818 | -3550 | -400 | -3606.5182 | 90.16% | 53.77% | 95% | 0% | 1684 | -152
[5 empty] | 2019-08-15 | 14 | 5430 | 1635 | -176 | 1 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -201.373 | 514.9502 | -3550 | -400 | -3435.0498 | 85.88% | 53.76% | 95% | 0% | 1811 | -176
[5 empty] | 2019-08-15 | 15 | 5430.5 | 1755 | -221 | 1 | 0 | 1976 | 974.7733 | 974.7733 | 974.7733 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -252.8604 | 721.9129 | -3550 | -400 | -3228.0871 | 80.7% | 53.76% | 95% | 0% | 1976 | -221
[5 empty] | 2019-08-15 | 16 | 5431 | 1814 | -266 | 1 | 0 | 2080 | 1137.6752 | 1137.6752 | 1137.6752 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -304.3478 | 833.3274 | -3550 | -400 | -3116.6726 | 77.92% | 53.76% | 95% | 0% | 2080 | -266
[5 empty] | 2019-08-15 | 17 | 5431.5 | 1828 | -318 | 1 | 0 | 2146 | 1241.0552 | 1241.0552 | 1241.0552 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -363.8444 | 877.2108 | -3550 | -400 | -3072.7892 | 76.82% | 53.76% | 95% | 0% | 2146 | -318
[5 empty] | 2019-08-15 | 18 | 5432 | 1758 | -392 | 1 | 0 | 2150 | 1247.3207 | 1247.3207 | 1247.3207 | 1115.7461 | 780 | 200 | 2095.7461 | 52.39% | 95% | 0% | -448.5126 | 798.8081 | -3550 | -400 | -3151.1919 | 78.78% | 53.76% | 95% | 0% | 2150 | -392
[5 empty] | 2019-08-15 | 19 | 5432.5 | 1684 | -454 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -519.4508 | 709.0735 | -3550 | -400 | -3240.9265 | 81.02% | 53.75% | 95% | 0% | 2138 | -454
[5 empty] | 2019-08-15 | 20 | 5433 | 1626 | -480 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -549.1991 | 629.2016 | -3550 | -400 | -3320.7984 | 83.02% | 53.74% | 95% | 0% | 2106 | -480
[5 empty] | 2019-08-15 | 21 | 5433.5 | 1523 | -542 | 1 | 0 | 2065 | 1114.1797 | 1114.1797 | 1114.1797 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -620.1373 | 494.0424 | -3550 | -400 | -3455.9576 | 86.4% | 53.74% | 95% | 0% | 2065 | -542
[5 empty] | 2019-08-15 | 22 | 5434 | 1429 | -588 | 1 | 0 | 2017 | 1038.9942 | 1038.9942 | 1038.9942 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -672.7689 | 366.2254 | -3550 | -400 | -3583.7746 | 89.59% | 53.74% | 95% | 0% | 2017 | -588
[5 empty] | 2019-08-15 | 23 | 5434.5 | 1371 | -625 | 1 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -715.103 | 290.9976 | -3550 | -400 | -3659.0024 | 91.48% | 53.74% | 95% | 0% | 1996 | -625
[5 empty] | 2019-08-15 | 24 | 5435 | 1348 | -648 | 1 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -741.4188 | 264.6818 | -3550 | -400 | -3685.3182 | 92.13% | 53.72% | 95% | 0% | 1996 | -648
[5 empty] | 2019-08-15 | 25 | 5435.5 | 1325 | -671 | 1 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -767.7346 | 238.366 | -3550 | -400 | -3711.634 | 92.79% | 53.72% | 95% | 0% | 1996 | -671
[5 empty] | 2019-08-15 | 26 | 5436 | 1263 | -701 | 1 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -802.0595 | 153.9174 | -3550 | -400 | -3796.0826 | 94.9% | 53.71% | 95% | 0% | 1964 | -701
[5 empty] | 2019-08-15 | 27 | 5436.5 | 1223 | -699 | 1 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -799.7712 | 90.4184 | -3550 | -400 | -3859.5816 | 96.49% | 53.71% | 95% | 0% | 1922 | -699
[5 empty] | 2019-08-15 | 28 | 5437 | 1137 | -745 | 1 | 0 | 1882 | 827.535 | 827.535 | 827.535 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -852.4027 | -24.8677 | -3550 | -400 | -3974.8677 | 99.37% | 53.71% | 95% | 0% | 1882 | -745
[5 empty] | 2019-08-15 | 29 | 5437.5 | 1115 | -762 | 1 | 0 | 1877 | 819.7032 | 819.7032 | 819.7032 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -871.8535 | -52.1503 | -3550 | -400 | -4002.1503 | 100.1% | 53.7% | 95% | 0% | 1877 | -762
[5 empty] | 2019-08-15 | 30 | 5438 | 1176 | -710 | 1 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -812.357 | 21.4435 | -3550 | -400 | -3928.5565 | 98.21% | 53.7% | 95% | 0% | 1886 | -710
[5 empty] | 2019-08-15 | 31 | 5438.5 | 1257 | -652 | 1 | 0 | 1909 | 869.8269 | 869.8269 | 869.8269 | 1114.1797 | 780 | 200 | 2094.1797 | 52.35% | 95% | 0% | -745.9954 | 123.8315 | -3550 | -400 | -3826.1685 | 95.65% | 53.7% | 95% | 0% | 1909 | -652
[5 empty] | 2019-08-15 | 32 | 5439 | 1347 | -589 | 1 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 1112.6134 | 780 | 200 | 2092.6134 | 52.32% | 95% | 0% | -673.913 | 238.2057 | -3550 | -400 | -3711.7943 | 92.79% | 53.69% | 95% | 0% | 1936 | -589
[5 empty] | 2019-08-15 | 33 | 5439.5 | 1495 | -507 | 1 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 1112.6134 | 780 | 200 | 2092.6134 | 52.32% | 95% | 0% | -580.0915 | 435.4072 | -3550 | -400 | -3514.5928 | 87.86% | 53.69% | 95% | 0% | 2002 | -507
[5 empty] | 2019-08-15 | 34 | 5440 | 1660 | -441 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 1112.6134 | 780 | 200 | 2092.6134 | 52.32% | 95% | 0% | -504.5767 | 665.9922 | -3550 | -400 | -3284.0078 | 82.1% | 53.69% | 95% | 0% | 2101 | -441
[5 empty] | 2019-08-15 | 35 | 5440.5 | 1792 | -393 | 1 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 1112.6134 | 780 | 200 | 2092.6134 | 52.32% | 95% | 0% | -449.6568 | 852.4867 | -3550 | -400 | -3097.5133 | 77.44% | 53.68% | 95% | 0% | 2185 | -393
[5 empty] | 2019-08-15 | 36 | 5441 | 1921 | -328 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -375.286 | 1027.1047 | -3550 | -400 | -2922.8953 | 73.07% | 53.68% | 95% | 0% | 2249 | -328
[5 empty] | 2019-08-15 | 37 | 5441.5 | 2009 | -273 | 1 | 0 | 2282 | 1454.0808 | 1454.0808 | 1454.0808 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -312.357 | 1141.7238 | -3550 | -400 | -2808.2762 | 70.21% | 53.68% | 95% | 0% | 2282 | -273
[5 empty] | 2019-08-15 | 38 | 5442 | 2109 | -213 | 1 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -243.7071 | 1273.0283 | -3550 | -400 | -2676.9717 | 66.92% | 53.68% | 95% | 0% | 2322 | -213
[5 empty] | 2019-08-15 | 39 | 5442.5 | 2182 | -159 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -181.9222 | 1364.5741 | -3550 | -400 | -2585.4259 | 64.64% | 53.67% | 95% | 0% | 2341 | -159
[5 empty] | 2019-08-15 | 40 | 5443 | 2237 | -113 | 1 | 0 | 2350 | 1560.5936 | 1560.5936 | 1560.5936 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -129.2906 | 1431.303 | -3550 | -400 | -2518.697 | 62.97% | 53.66% | 95% | 0% | 2350 | -113
[5 empty] | 2019-08-15 | 41 | 5443.5 | 2253 | -88 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -100.6865 | 1445.8098 | -3550 | -400 | -2504.1902 | 62.6% | 53.66% | 95% | 0% | 2341 | -88
[5 empty] | 2019-08-15 | 42 | 5444 | 2286 | -82 | 1 | 0 | 2368 | 1588.7881 | 1588.7881 | 1588.7881 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -93.8215 | 1494.9666 | -3550 | -400 | -2455.0334 | 61.38% | 53.66% | 95% | 0% | 2368 | -82
[5 empty] | 2019-08-15 | 43 | 5444.5 | 2275 | -84 | 1 | 0 | 2359 | 1574.6908 | 1574.6908 | 1574.6908 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -96.1098 | 1478.581 | -3550 | -400 | -2471.419 | 61.79% | 53.65% | 95% | 0% | 2359 | -84
[5 empty] | 2019-08-15 | 44 | 5445 | 2167 | -85 | 1 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -97.254 | 1309.8359 | -3550 | -400 | -2640.1641 | 66% | 53.63% | 95% | 0% | 2252 | -85
[5 empty] | 2019-08-15 | 45 | 5445.5 | 2068 | -87 | 0 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -99.5423 | 1155.6102 | -2750 | -200 | -1794.3898 | 44.86% | 53.63% | 95% | 0% | 2155 | -87
[5 empty] | 2019-08-15 | 46 | 5446 | 1931 | -90 | 0 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -102.9748 | 942.2849 | -2750 | -200 | -2007.7151 | 50.19% | 53.63% | 95% | 0% | 2021 | -90
[5 empty] | 2019-08-15 | 47 | 5446.5 | 1769 | -93 | 0 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -106.4073 | 689.8004 | -2750 | -200 | -2260.1996 | 56.5% | 53.63% | 95% | 0% | 1862 | -93
[5 empty] | 2019-08-15 | 48 | 5447 | 1656 | -96 | 0 | 0 | 1752 | 623.9077 | 623.9077 | 623.9077 | 1111.047 | 780 | 200 | 2091.047 | 52.28% | 95% | 0% | -109.8398 | 514.0679 | -2750 | -200 | -2435.9321 | 60.9% | 53.63% | 95% | 0% | 1752 | -96
[5 empty] | 2019-08-16 | 1 | 5447.5 | 1558 | -97 | 0 | 0 | 1655 | 471.9703 | 471.9703 | 471.9703 | 1109.4806 | 780 | 200 | 2089.4806 | 52.24% | 95% | 0% | -110.984 | 360.9863 | -2750 | -200 | -2589.0137 | 64.73% | 53.63% | 95% | 0% | 1655 | -97
[5 empty] | 2019-08-16 | 2 | 5448 | 1516 | -98 | 0 | 0 | 1614 | 407.7494 | 407.7494 | 407.7494 | 1109.4806 | 780 | 200 | 2089.4806 | 52.24% | 95% | 0% | -112.1281 | 295.6212 | -2750 | -200 | -2654.3788 | 66.36% | 53.62% | 95% | 0% | 1614 | -98
[5 empty] | 2019-08-16 | 3 | 5448.5 | 1471 | -101 | 0 | 0 | 1572 | 341.9621 | 341.9621 | 341.9621 | 1109.4806 | 780 | 200 | 2089.4806 | 52.24% | 95% | 0% | -115.5606 | 226.4014 | -2750 | -200 | -2723.5986 | 68.09% | 53.61% | 95% | 0% | 1572 | -101
[5 empty] | 2019-08-16 | 4 | 5449 | 1441 | -104 | 0 | 0 | 1545 | 299.6702 | 299.6702 | 299.6702 | 1109.4806 | 780 | 200 | 2089.4806 | 52.24% | 95% | 0% | -118.9931 | 180.6771 | -2750 | -200 | -2769.3229 | 69.23% | 53.61% | 95% | 0% | 1545 | -104
[5 empty] | 2019-08-16 | 5 | 5449.5 | 1412 | -106 | 0 | 0 | 1518 | 257.3784 | 257.3784 | 257.3784 | 1109.4806 | 780 | 200 | 2089.4806 | 52.24% | 95% | 0% | -121.2815 | 136.0969 | -2750 | -200 | -2813.9031 | 70.35% | 53.6% | 95% | 0% | 1518 | -106
[5 empty] | 2019-08-16 | 6 | 5450 | 1382 | -109 | 0 | 0 | 1491 | 215.0866 | 215.0866 | 215.0866 | 1109.4806 | 780 | 200 | 2089.4806 | 52.24% | 95% | 0% | -124.714 | 90.3726 | -2750 | -200 | -2859.6274 | 71.49% | 53.6% | 95% | 0% | 1491 | -109
[5 empty] | 2019-08-16 | 7 | 5450.5 | 1361 | -113 | 0 | 0 | 1474 | 188.4584 | 188.4584 | 188.4584 | 1109.4806 | 780 | 200 | 2089.4806 | 52.24% | 95% | 0% | -129.2906 | 59.1677 | -2750 | -200 | -2890.8323 | 72.27% | 53.6% | 95% | 0% | 1474 | -113
[5 empty] | 2019-08-16 | 8 | 5451 | 1351 | -116 | 0 | 0 | 1467 | 177.4938 | 177.4938 | 177.4938 | 1109.4806 | 780 | 200 | 2089.4806 | 52.24% | 95% | 0% | -132.7231 | 44.7707 | -2750 | -200 | -2905.2293 | 72.63% | 53.6% | 95% | 0% | 1467 | -116
[5 empty] | 2019-08-16 | 9 | 5451.5 | 1344 | -120 | 0 | 0 | 1464 | 172.7947 | 172.7947 | 172.7947 | 1109.4806 | 780 | 200 | 2089.4806 | 52.24% | 95% | 0% | -137.2998 | 35.495 | -2750 | -200 | -2914.505 | 72.86% | 53.59% | 95% | 0% | 1464 | -120
[5 empty] | 2019-08-16 | 10 | 5452 | 1348 | -124 | 0 | 0 | 1472 | 185.3256 | 185.3256 | 185.3256 | 1109.4806 | 780 | 200 | 2089.4806 | 52.24% | 95% | 0% | -141.8764 | 43.4492 | -2750 | -200 | -2906.5508 | 72.66% | 53.59% | 95% | 0% | 1472 | -124
[5 empty] | 2019-08-16 | 11 | 5452.5 | 1388 | -129 | 0 | 0 | 1517 | 255.812 | 255.812 | 255.812 | 1107.9143 | 780 | 200 | 2087.9143 | 52.2% | 95% | 0% | -147.5973 | 108.2148 | -2750 | -200 | -2841.7852 | 71.04% | 53.59% | 95% | 0% | 1517 | -129
[5 empty] | 2019-08-16 | 12 | 5453 | 1419 | -134 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 1107.9143 | 780 | 200 | 2087.9143 | 52.2% | 95% | 0% | -153.3181 | 158.8831 | -2750 | -200 | -2791.1169 | 69.78% | 53.59% | 95% | 0% | 1553 | -134
[5 empty] | 2019-08-16 | 13 | 5453.5 | 1544 | -141 | 0 | 0 | 1685 | 518.9613 | 518.9613 | 518.9613 | 1107.9143 | 780 | 200 | 2087.9143 | 52.2% | 95% | 0% | -161.3272 | 357.634 | -2750 | -200 | -2592.366 | 64.81% | 53.58% | 95% | 0% | 1685 | -141
[5 empty] | 2019-08-16 | 14 | 5454 | 1651 | -160 | 0 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1107.9143 | 780 | 200 | 2087.9143 | 52.2% | 95% | 0% | -183.0664 | 533.2568 | -2750 | -200 | -2416.7432 | 60.42% | 53.58% | 95% | 0% | 1811 | -160
[5 empty] | 2019-08-16 | 15 | 5454.5 | 1792 | -185 | 1 | 0 | 1977 | 976.3397 | 976.3397 | 976.3397 | 1107.9143 | 780 | 200 | 2087.9143 | 52.2% | 95% | 0% | -211.6705 | 764.6692 | -3550 | -400 | -3185.3308 | 79.63% | 53.58% | 95% | 0% | 1977 | -185
[5 empty] | 2019-08-16 | 16 | 5455 | 1876 | -209 | 1 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 1107.9143 | 780 | 200 | 2087.9143 | 52.2% | 95% | 0% | -239.1304 | 906.3766 | -3550 | -400 | -3043.6234 | 76.09% | 53.58% | 95% | 0% | 2085 | -209
[5 empty] | 2019-08-16 | 17 | 5455.5 | 1950 | -239 | 1 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 1107.9143 | 780 | 200 | 2087.9143 | 52.2% | 95% | 0% | -273.4554 | 1034.9535 | -3550 | -400 | -2915.0465 | 72.88% | 53.58% | 95% | 0% | 2189 | -239
[5 empty] | 2019-08-16 | 18 | 5456 | 1979 | -267 | 1 | 0 | 2246 | 1397.6917 | 1397.6917 | 1397.6917 | 1107.9143 | 780 | 200 | 2087.9143 | 52.2% | 95% | 0% | -305.492 | 1092.1997 | -3550 | -400 | -2857.8003 | 71.45% | 53.57% | 95% | 0% | 2246 | -267
[5 empty] | 2019-08-16 | 19 | 5456.5 | 1997 | -287 | 1 | 0 | 2284 | 1457.2135 | 1457.2135 | 1457.2135 | 1107.9143 | 780 | 200 | 2087.9143 | 52.2% | 95% | 0% | -328.3753 | 1128.8382 | -3550 | -400 | -2821.1618 | 70.53% | 53.57% | 95% | 0% | 2284 | -287
[5 empty] | 2019-08-16 | 20 | 5457 | 1998 | -286 | 1 | 0 | 2284 | 1457.2135 | 1457.2135 | 1457.2135 | 1107.9143 | 780 | 200 | 2087.9143 | 52.2% | 95% | 0% | -327.2311 | 1129.9824 | -3550 | -400 | -2820.0176 | 70.5% | 53.57% | 95% | 0% | 2284 | -286
[5 empty] | 2019-08-16 | 21 | 5457.5 | 2004 | -289 | 1 | 0 | 2293 | 1471.3108 | 1471.3108 | 1471.3108 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -330.6636 | 1140.6472 | -3550 | -400 | -2809.3528 | 70.23% | 53.56% | 95% | 0% | 2293 | -289
[5 empty] | 2019-08-16 | 22 | 5458 | 1994 | -305 | 1 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -348.9703 | 1131.7387 | -3550 | -400 | -2818.2613 | 70.46% | 53.55% | 95% | 0% | 2299 | -305
[5 empty] | 2019-08-16 | 23 | 5458.5 | 1994 | -313 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -358.1236 | 1135.1163 | -3550 | -400 | -2814.8837 | 70.37% | 53.55% | 95% | 0% | 2307 | -313
[5 empty] | 2019-08-16 | 24 | 5459 | 1983 | -329 | 1 | 0 | 2312 | 1501.0717 | 1501.0717 | 1501.0717 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -376.4302 | 1124.6415 | -3550 | -400 | -2825.3585 | 70.63% | 53.55% | 95% | 0% | 2312 | -329
[5 empty] | 2019-08-16 | 25 | 5459.5 | 1972 | -343 | 1 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -392.4485 | 1113.3223 | -3550 | -400 | -2836.6777 | 70.92% | 53.54% | 95% | 0% | 2315 | -343
[5 empty] | 2019-08-16 | 26 | 5460 | 1937 | -362 | 1 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -414.1876 | 1066.5213 | -3550 | -400 | -2883.4787 | 72.09% | 53.54% | 95% | 0% | 2299 | -362
[5 empty] | 2019-08-16 | 27 | 5460.5 | 1937 | -339 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -387.8719 | 1056.8108 | -3550 | -400 | -2893.1892 | 72.33% | 53.53% | 95% | 0% | 2276 | -339
[5 empty] | 2019-08-16 | 28 | 5461 | 1916 | -328 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -375.286 | 1019.2729 | -3550 | -400 | -2930.7271 | 73.27% | 53.52% | 95% | 0% | 2244 | -328
[5 empty] | 2019-08-16 | 29 | 5461.5 | 1919 | -310 | 1 | 0 | 2229 | 1371.0635 | 1371.0635 | 1371.0635 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -354.6911 | 1016.3724 | -3550 | -400 | -2933.6276 | 73.34% | 53.52% | 95% | 0% | 2229 | -310
[5 empty] | 2019-08-16 | 30 | 5462 | 1925 | -298 | 1 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -340.9611 | 1020.7042 | -3550 | -400 | -2929.2958 | 73.23% | 53.51% | 95% | 0% | 2223 | -298
[5 empty] | 2019-08-16 | 31 | 5462.5 | 1895 | -297 | 1 | 0 | 2192 | 1313.108 | 1313.108 | 1313.108 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -339.8169 | 973.2911 | -3550 | -400 | -2976.7089 | 74.42% | 53.5% | 95% | 0% | 2192 | -297
[5 empty] | 2019-08-16 | 32 | 5463 | 1920 | -271 | 1 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -310.0686 | 1001.473 | -3550 | -400 | -2948.527 | 73.71% | 53.5% | 95% | 0% | 2191 | -271
[5 empty] | 2019-08-16 | 33 | 5463.5 | 1968 | -261 | 1 | 0 | 2229 | 1371.0635 | 1371.0635 | 1371.0635 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -298.627 | 1072.4365 | -3550 | -400 | -2877.5635 | 71.94% | 53.5% | 95% | 0% | 2229 | -261
[5 empty] | 2019-08-16 | 34 | 5464 | 2016 | -247 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 1106.3479 | 780 | 200 | 2086.3479 | 52.16% | 95% | 0% | -282.6087 | 1141.7112 | -3550 | -400 | -2808.2888 | 70.21% | 53.5% | 95% | 0% | 2263 | -247
[5 empty] | 2019-08-16 | 35 | 5464.5 | 2083 | -229 | 1 | 0 | 2312 | 1501.0717 | 1501.0717 | 1501.0717 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -262.0137 | 1239.058 | -3550 | -400 | -2710.942 | 67.77% | 53.49% | 95% | 0% | 2312 | -229
[5 empty] | 2019-08-16 | 36 | 5465 | 2107 | -211 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -241.4188 | 1269.0511 | -3550 | -400 | -2680.9489 | 67.02% | 53.48% | 95% | 0% | 2318 | -211
[5 empty] | 2019-08-16 | 37 | 5465.5 | 2125 | -199 | 1 | 0 | 2324 | 1519.8681 | 1519.8681 | 1519.8681 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -227.6888 | 1292.1793 | -3550 | -400 | -2657.8207 | 66.45% | 53.47% | 95% | 0% | 2324 | -199
[5 empty] | 2019-08-16 | 38 | 5466 | 2111 | -185 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -211.6705 | 1264.3394 | -3550 | -400 | -2685.6606 | 67.14% | 53.47% | 95% | 0% | 2296 | -185
[5 empty] | 2019-08-16 | 39 | 5466.5 | 2095 | -172 | 1 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -196.7963 | 1233.789 | -3550 | -400 | -2716.211 | 67.91% | 53.46% | 95% | 0% | 2267 | -172
[5 empty] | 2019-08-16 | 40 | 5467 | 2071 | -161 | 1 | 0 | 2232 | 1375.7626 | 1375.7626 | 1375.7626 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -184.2105 | 1191.552 | -3550 | -400 | -2758.448 | 68.96% | 53.46% | 95% | 0% | 2232 | -161
[5 empty] | 2019-08-16 | 41 | 5467.5 | 2050 | -151 | 1 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -172.7689 | 1154.4364 | -3550 | -400 | -2795.5636 | 69.89% | 53.46% | 95% | 0% | 2201 | -151
[5 empty] | 2019-08-16 | 42 | 5468 | 2047 | -146 | 1 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -167.0481 | 1147.6263 | -3550 | -400 | -2802.3737 | 70.06% | 53.45% | 95% | 0% | 2193 | -146
[5 empty] | 2019-08-16 | 43 | 5468.5 | 2017 | -143 | 1 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -163.6156 | 1099.3688 | -3550 | -400 | -2850.6312 | 71.27% | 53.44% | 95% | 0% | 2160 | -143
[5 empty] | 2019-08-16 | 44 | 5469 | 1931 | -140 | 0 | 0 | 2071 | 1123.5779 | 1123.5779 | 1123.5779 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -160.1831 | 963.3948 | -2750 | -200 | -1986.6052 | 49.67% | 53.43% | 95% | 0% | 2071 | -140
[5 empty] | 2019-08-16 | 45 | 5469.5 | 1819 | -139 | 0 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -159.0389 | 787.5398 | -2750 | -200 | -2162.4602 | 54.06% | 53.43% | 95% | 0% | 1958 | -139
[5 empty] | 2019-08-16 | 46 | 5470 | 1718 | -138 | 0 | 0 | 1856 | 786.8096 | 786.8096 | 786.8096 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -157.8947 | 628.9148 | -2750 | -200 | -2321.0852 | 58.03% | 53.43% | 95% | 0% | 1856 | -138
[5 empty] | 2019-08-16 | 47 | 5470.5 | 1588 | -138 | 0 | 0 | 1726 | 583.1822 | 583.1822 | 583.1822 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -157.8947 | 425.2875 | -2750 | -200 | -2524.7125 | 63.12% | 53.43% | 95% | 0% | 1726 | -138
[5 empty] | 2019-08-16 | 48 | 5471 | 1489 | -137 | 0 | 0 | 1626 | 426.5458 | 426.5458 | 426.5458 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -156.7506 | 269.7952 | -2750 | -200 | -2680.2048 | 67.01% | 53.43% | 95% | 0% | 1626 | -137
[5 empty] | 2019-08-17 | 1 | 5471.5 | 1402 | -138 | 0 | 0 | 1540 | 291.8384 | 291.8384 | 291.8384 | 1104.7815 | 780 | 200 | 2084.7815 | 52.12% | 95% | 0% | -157.8947 | 133.9437 | -2750 | -200 | -2816.0563 | 70.4% | 53.43% | 95% | 0% | 1540 | -138
[5 empty] | 2019-08-17 | 2 | 5472 | 1344 | -138 | 0 | 0 | 1482 | 200.9893 | 200.9893 | 200.9893 | 1103.2152 | 780 | 200 | 2083.2152 | 52.08% | 95% | 0% | -157.8947 | 43.0945 | -2750 | -200 | -2906.9055 | 72.67% | 53.43% | 95% | 0% | 1482 | -138
[5 empty] | 2019-08-17 | 3 | 5472.5 | 1295 | -139 | 0 | 0 | 1434 | 125.8038 | 125.8038 | 125.8038 | 1103.2152 | 780 | 200 | 2083.2152 | 52.08% | 95% | 0% | -159.0389 | -33.2351 | -2750 | -200 | -2983.2351 | 74.58% | 53.42% | 95% | 0% | 1434 | -139
[5 empty] | 2019-08-17 | 4 | 5473 | 1273 | -139 | 0 | 0 | 1412 | 91.3438 | 91.3438 | 91.3438 | 1103.2152 | 780 | 200 | 2083.2152 | 52.08% | 95% | 0% | -159.0389 | -67.6951 | -2750 | -200 | -3017.6951 | 75.44% | 53.42% | 95% | 0% | 1412 | -139
[5 empty] | 2019-08-17 | 5 | 5473.5 | 1236 | -141 | 0 | 0 | 1377 | 36.521 | 36.521 | 36.521 | 1103.2152 | 780 | 200 | 2083.2152 | 52.08% | 95% | 0% | -161.3272 | -124.8062 | -2750 | -200 | -3074.8062 | 76.87% | 53.42% | 95% | 0% | 1377 | -141
[5 empty] | 2019-08-17 | 6 | 5474 | 1201 | -143 | 0 | 0 | 1344 | -15.169 | -15.169 | -15.169 | 1103.2152 | 780 | 200 | 2083.2152 | 52.08% | 95% | 0% | -163.6156 | -178.7846 | -2750 | -200 | -3128.7846 | 78.22% | 53.42% | 95% | 0% | 1344 | -143
[5 empty] | 2019-08-17 | 7 | 5474.5 | 1182 | -143 | 0 | 0 | 1325 | -44.9299 | -44.9299 | -44.9299 | 1103.2152 | 780 | 200 | 2083.2152 | 52.08% | 95% | 0% | -163.6156 | -208.5455 | -2750 | -200 | -3158.5455 | 78.96% | 53.42% | 95% | 0% | 1325 | -143
[5 empty] | 2019-08-17 | 8 | 5475 | 1178 | -144 | 0 | 0 | 1322 | -49.629 | -49.629 | -49.629 | 1103.2152 | 780 | 200 | 2083.2152 | 52.08% | 95% | 0% | -164.7597 | -214.3887 | -2750 | -200 | -3164.3887 | 79.11% | 53.42% | 95% | 0% | 1322 | -144
[5 empty] | 2019-08-17 | 9 | 5475.5 | 1176 | -143 | 0 | 0 | 1319 | -54.3281 | -54.3281 | -54.3281 | 1103.2152 | 780 | 200 | 2083.2152 | 52.08% | 95% | 0% | -163.6156 | -217.9437 | -2750 | -200 | -3167.9437 | 79.2% | 53.41% | 95% | 0% | 1319 | -143
[5 empty] | 2019-08-17 | 10 | 5476 | 1174 | -141 | 0 | 0 | 1315 | -60.5936 | -60.5936 | -60.5936 | 1103.2152 | 780 | 200 | 2083.2152 | 52.08% | 95% | 0% | -161.3272 | -221.9208 | -2750 | -200 | -3171.9208 | 79.3% | 53.4% | 95% | 0% | 1315 | -141
[5 empty] | 2019-08-17 | 11 | 5476.5 | 1192 | -141 | 0 | 0 | 1333 | -32.399 | -32.399 | -32.399 | 1103.2152 | 780 | 200 | 2083.2152 | 52.08% | 95% | 0% | -161.3272 | -193.7262 | -2750 | -200 | -3143.7262 | 78.59% | 53.39% | 95% | 0% | 1333 | -141
[5 empty] | 2019-08-17 | 12 | 5477 | 1202 | -140 | 0 | 0 | 1342 | -18.3017 | -18.3017 | -18.3017 | 1103.2152 | 780 | 200 | 2083.2152 | 52.08% | 95% | 0% | -160.1831 | -178.4848 | -2750 | -200 | -3128.4848 | 78.21% | 53.39% | 95% | 0% | 1342 | -140
[5 empty] | 2019-08-17 | 13 | 5477.5 | 1270 | -147 | 0 | 0 | 1417 | 99.1756 | 99.1756 | 99.1756 | 1103.2152 | 780 | 200 | 2083.2152 | 52.08% | 95% | 0% | -168.1922 | -69.0166 | -2750 | -200 | -3019.0166 | 75.48% | 53.39% | 95% | 0% | 1417 | -147
[5 empty] | 2019-08-17 | 14 | 5478 | 1311 | -174 | 0 | 0 | 1485 | 205.6884 | 205.6884 | 205.6884 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -199.0847 | 6.6037 | -2750 | -200 | -2943.3963 | 73.58% | 53.39% | 95% | 0% | 1485 | -174
[5 empty] | 2019-08-17 | 15 | 5478.5 | 1356 | -215 | 1 | 0 | 1571 | 340.3957 | 340.3957 | 340.3957 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -245.9954 | 94.4003 | -3550 | -400 | -3855.5997 | 96.39% | 53.38% | 95% | 0% | 1571 | -215
[5 empty] | 2019-08-17 | 16 | 5479 | 1352 | -271 | 1 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -310.0686 | 111.778 | -3550 | -400 | -3838.222 | 95.96% | 53.38% | 95% | 0% | 1623 | -271
[5 empty] | 2019-08-17 | 17 | 5479.5 | 1347 | -342 | 1 | 0 | 1689 | 525.2267 | 525.2267 | 525.2267 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -391.3043 | 133.9224 | -3550 | -400 | -3816.0776 | 95.4% | 53.38% | 95% | 0% | 1689 | -342
[5 empty] | 2019-08-17 | 18 | 5480 | 1319 | -394 | 1 | 0 | 1713 | 562.8195 | 562.8195 | 562.8195 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -450.8009 | 112.0185 | -3550 | -400 | -3837.9815 | 95.95% | 53.38% | 95% | 0% | 1713 | -394
[5 empty] | 2019-08-17 | 19 | 5480.5 | 1270 | -467 | 1 | 0 | 1737 | 600.4122 | 600.4122 | 600.4122 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -534.3249 | 66.0873 | -3550 | -400 | -3883.9127 | 97.1% | 53.38% | 95% | 0% | 1737 | -467
[5 empty] | 2019-08-17 | 20 | 5481 | 1209 | -524 | 1 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -599.5423 | -5.3956 | -3550 | -400 | -3955.3956 | 98.88% | 53.38% | 95% | 0% | 1733 | -524
[5 empty] | 2019-08-17 | 21 | 5481.5 | 1164 | -564 | 1 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -645.3089 | -58.994 | -3550 | -400 | -4008.994 | 100.2% | 53.38% | 95% | 0% | 1728 | -564
[5 empty] | 2019-08-17 | 22 | 5482 | 1151 | -568 | 1 | 0 | 1719 | 572.2176 | 572.2176 | 572.2176 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -649.8856 | -77.6679 | -3550 | -400 | -4027.6679 | 100.7% | 53.37% | 95% | 0% | 1719 | -568
[5 empty] | 2019-08-17 | 23 | 5482.5 | 1093 | -598 | 1 | 0 | 1691 | 528.3594 | 528.3594 | 528.3594 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -684.2105 | -155.8511 | -3550 | -400 | -4105.8511 | 102.6% | 53.37% | 95% | 0% | 1691 | -598
[5 empty] | 2019-08-17 | 24 | 5483 | 957 | -696 | 1 | 0 | 1653 | 468.8376 | 468.8376 | 468.8376 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -796.3387 | -327.5011 | -3550 | -400 | -4277.5011 | 106.9% | 53.37% | 95% | 0% | 1653 | -696
[5 empty] | 2019-08-17 | 25 | 5483.5 | 881 | -728 | 1 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -832.9519 | -433.0344 | -3550 | -400 | -4383.0344 | 109.6% | 53.37% | 95% | 0% | 1609 | -728
[5 empty] | 2019-08-17 | 26 | 5484 | 809 | -764 | 1 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -874.1419 | -530.6134 | -3550 | -400 | -4480.6134 | 112% | 53.37% | 95% | 0% | 1573 | -764
[5 empty] | 2019-08-17 | 27 | 5484.5 | 758 | -771 | 1 | 0 | 1529 | 274.6084 | 274.6084 | 274.6084 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -882.151 | -607.5426 | -3550 | -400 | -4557.5426 | 113.9% | 53.36% | 95% | 0% | 1529 | -771
[5 empty] | 2019-08-17 | 28 | 5485 | 717 | -754 | 1 | 0 | 1471 | 183.7593 | 183.7593 | 183.7593 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -862.7002 | -678.941 | -3550 | -400 | -4628.941 | 115.7% | 53.35% | 95% | 0% | 1471 | -754
[5 empty] | 2019-08-17 | 29 | 5485.5 | 717 | -732 | 1 | 0 | 1449 | 149.2993 | 149.2993 | 149.2993 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -837.5286 | -688.2293 | -3550 | -400 | -4638.2293 | 116% | 53.35% | 95% | 0% | 1449 | -732
[5 empty] | 2019-08-17 | 30 | 5486 | 713 | -713 | 1 | 0 | 1426 | 113.2729 | 113.2729 | 113.2729 | 1101.6488 | 780 | 200 | 2081.6488 | 52.04% | 95% | 0% | -815.7895 | -702.5166 | -3550 | -400 | -4652.5166 | 116.3% | 53.34% | 95% | 0% | 1426 | -713
[5 empty] | 2019-08-17 | 31 | 5486.5 | 769 | -665 | 1 | 0 | 1434 | 125.8038 | 125.8038 | 125.8038 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -760.8696 | -635.0658 | -3550 | -400 | -4585.0658 | 114.6% | 53.34% | 95% | 0% | 1434 | -665
[5 empty] | 2019-08-17 | 32 | 5487 | 839 | -621 | 1 | 0 | 1460 | 166.5293 | 166.5293 | 166.5293 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -710.5263 | -543.997 | -3550 | -400 | -4493.997 | 112.3% | 53.33% | 95% | 0% | 1460 | -621
[5 empty] | 2019-08-17 | 33 | 5487.5 | 975 | -568 | 1 | 0 | 1543 | 296.5375 | 296.5375 | 296.5375 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -649.8856 | -353.3481 | -3550 | -400 | -4303.3481 | 107.6% | 53.33% | 95% | 0% | 1543 | -568
[5 empty] | 2019-08-17 | 34 | 5488 | 1123 | -511 | 1 | 0 | 1634 | 439.0767 | 439.0767 | 439.0767 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -584.6682 | -145.5915 | -3550 | -400 | -4095.5915 | 102.4% | 53.33% | 95% | 0% | 1634 | -511
[5 empty] | 2019-08-17 | 35 | 5488.5 | 1296 | -451 | 1 | 0 | 1747 | 616.0758 | 616.0758 | 616.0758 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -516.0183 | 100.0575 | -3550 | -400 | -3849.9425 | 96.25% | 53.32% | 95% | 0% | 1747 | -451
[5 empty] | 2019-08-17 | 36 | 5489 | 1467 | -383 | 1 | 0 | 1850 | 777.4114 | 777.4114 | 777.4114 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -438.2151 | 339.1963 | -3550 | -400 | -3610.8037 | 90.27% | 53.32% | 95% | 0% | 1850 | -383
[5 empty] | 2019-08-17 | 37 | 5489.5 | 1582 | -310 | 1 | 0 | 1892 | 843.1987 | 843.1987 | 843.1987 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -354.6911 | 488.5076 | -3550 | -400 | -3461.4924 | 86.54% | 53.31% | 95% | 0% | 1892 | -310
[5 empty] | 2019-08-17 | 38 | 5490 | 1685 | -246 | 1 | 0 | 1931 | 904.2869 | 904.2869 | 904.2869 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -281.4645 | 622.8224 | -3550 | -400 | -3327.1776 | 83.18% | 53.31% | 95% | 0% | 1931 | -246
[5 empty] | 2019-08-17 | 39 | 5490.5 | 1752 | -197 | 1 | 0 | 1949 | 932.4815 | 932.4815 | 932.4815 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -225.4005 | 707.081 | -3550 | -400 | -3242.919 | 81.07% | 53.3% | 95% | 0% | 1949 | -197
[5 empty] | 2019-08-17 | 40 | 5491 | 1792 | -163 | 1 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -186.4989 | 755.3808 | -3550 | -400 | -3194.6192 | 79.87% | 53.3% | 95% | 0% | 1955 | -163
[5 empty] | 2019-08-17 | 41 | 5491.5 | 1805 | -146 | 1 | 0 | 1951 | 935.6142 | 935.6142 | 935.6142 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -167.0481 | 768.5661 | -3550 | -400 | -3181.4339 | 79.54% | 53.29% | 95% | 0% | 1951 | -146
[5 empty] | 2019-08-17 | 42 | 5492 | 1847 | -144 | 1 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -164.7597 | 833.509 | -3550 | -400 | -3116.491 | 77.91% | 53.29% | 95% | 0% | 1991 | -144
[5 empty] | 2019-08-17 | 43 | 5492.5 | 1820 | -145 | 1 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -165.9039 | 791.6394 | -3550 | -400 | -3158.3606 | 78.96% | 53.29% | 95% | 0% | 1965 | -145
[5 empty] | 2019-08-17 | 44 | 5493 | 1754 | -146 | 0 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -167.0481 | 688.6815 | -2750 | -200 | -2261.3185 | 56.53% | 53.29% | 95% | 0% | 1900 | -146
[5 empty] | 2019-08-17 | 45 | 5493.5 | 1669 | -147 | 0 | 0 | 1816 | 724.155 | 724.155 | 724.155 | 1100.0824 | 780 | 200 | 2080.0824 | 52% | 95% | 0% | -168.1922 | 555.9628 | -2750 | -200 | -2394.0372 | 59.85% | 53.28% | 95% | 0% | 1816 | -147
[5 empty] | 2019-08-17 | 46 | 5494 | 1598 | -148 | 0 | 0 | 1746 | 614.5095 | 614.5095 | 614.5095 | 1098.5161 | 780 | 200 | 2078.5161 | 51.96% | 95% | 0% | -169.3364 | 445.1731 | -2750 | -200 | -2504.8269 | 62.62% | 53.28% | 95% | 0% | 1746 | -148
[5 empty] | 2019-08-17 | 47 | 5494.5 | 1495 | -148 | 0 | 0 | 1643 | 453.1739 | 453.1739 | 453.1739 | 1098.5161 | 780 | 200 | 2078.5161 | 51.96% | 95% | 0% | -169.3364 | 283.8376 | -2750 | -200 | -2666.1624 | 66.65% | 53.28% | 95% | 0% | 1643 | -148
[5 empty] | 2019-08-17 | 48 | 5495 | 1398 | -149 | 0 | 0 | 1547 | 302.803 | 302.803 | 302.803 | 1098.5161 | 780 | 200 | 2078.5161 | 51.96% | 95% | 0% | -170.4805 | 132.3224 | -2750 | -200 | -2817.6776 | 70.44% | 53.27% | 95% | 0% | 1547 | -149
[5 empty] | 2019-08-18 | 1 | 5495.5 | 1334 | -146 | 0 | 0 | 1480 | 197.8566 | 197.8566 | 197.8566 | 1098.5161 | 780 | 200 | 2078.5161 | 51.96% | 95% | 0% | -167.0481 | 30.8085 | -2750 | -200 | -2919.1915 | 72.98% | 53.27% | 95% | 0% | 1480 | -146
[5 empty] | 2019-08-18 | 2 | 5496 | 1289 | -144 | 0 | 0 | 1433 | 124.2374 | 124.2374 | 124.2374 | 1098.5161 | 780 | 200 | 2078.5161 | 51.96% | 95% | 0% | -164.7597 | -40.5223 | -2750 | -200 | -2990.5223 | 74.76% | 53.26% | 95% | 0% | 1433 | -144
[5 empty] | 2019-08-18 | 3 | 5496.5 | 1245 | -144 | 0 | 0 | 1389 | 55.3174 | 55.3174 | 55.3174 | 1098.5161 | 780 | 200 | 2078.5161 | 51.96% | 95% | 0% | -164.7597 | -109.4423 | -2750 | -200 | -3059.4423 | 76.49% | 53.25% | 95% | 0% | 1389 | -144
[5 empty] | 2019-08-18 | 4 | 5497 | 1223 | -143 | 0 | 0 | 1366 | 19.291 | 19.291 | 19.291 | 1098.5161 | 780 | 200 | 2078.5161 | 51.96% | 95% | 0% | -163.6156 | -144.3245 | -2750 | -200 | -3094.3245 | 77.36% | 53.25% | 95% | 0% | 1366 | -143
[5 empty] | 2019-08-18 | 5 | 5497.5 | 1196 | -142 | 0 | 0 | 1338 | -24.5672 | -24.5672 | -24.5672 | 1098.5161 | 780 | 200 | 2078.5161 | 51.96% | 95% | 0% | -162.4714 | -187.0386 | -2750 | -200 | -3137.0386 | 78.43% | 53.24% | 95% | 0% | 1338 | -142
[5 empty] | 2019-08-18 | 6 | 5498 | 1171 | -142 | 0 | 0 | 1313 | -63.7263 | -63.7263 | -63.7263 | 1096.9497 | 780 | 200 | 2076.9497 | 51.92% | 95% | 0% | -162.4714 | -226.1977 | -2750 | -200 | -3176.1977 | 79.4% | 53.24% | 95% | 0% | 1313 | -142
[5 empty] | 2019-08-18 | 7 | 5498.5 | 1154 | -141 | 0 | 0 | 1295 | -91.9209 | -91.9209 | -91.9209 | 1096.9497 | 780 | 200 | 2076.9497 | 51.92% | 95% | 0% | -161.3272 | -253.2481 | -2750 | -200 | -3203.2481 | 80.08% | 53.24% | 95% | 0% | 1295 | -141
[5 empty] | 2019-08-18 | 8 | 5499 | 1148 | -141 | 0 | 0 | 1289 | -101.319 | -101.319 | -101.319 | 1096.9497 | 780 | 200 | 2076.9497 | 51.92% | 95% | 0% | -161.3272 | -262.6463 | -2750 | -200 | -3212.6463 | 80.32% | 53.24% | 95% | 0% | 1289 | -141
[5 empty] | 2019-08-18 | 9 | 5499.5 | 1143 | -138 | 0 | 0 | 1281 | -113.85 | -113.85 | -113.85 | 1096.9497 | 780 | 200 | 2076.9497 | 51.92% | 95% | 0% | -157.8947 | -271.7447 | -2750 | -200 | -3221.7447 | 80.54% | 53.24% | 95% | 0% | 1281 | -138
[5 empty] | 2019-08-18 | 10 | 5500 | 1139 | -134 | 1 | 0 | 1273 | -126.3809 | -126.3809 | -126.3809 | 1096.9497 | 780 | 200 | 2076.9497 | 51.92% | 95% | 0% | -153.3181 | -279.699 | -3550 | -400 | -4229.699 | 105.7% | 53.24% | 95% | 0% | 1273 | -134
[5 empty] | 2019-08-18 | 11 | 5500.5 | 1151 | -133 | 1 | 0 | 1284 | -109.1509 | -109.1509 | -109.1509 | 1096.9497 | 780 | 200 | 2076.9497 | 51.92% | 95% | 0% | -152.1739 | -261.3248 | -3550 | -400 | -4211.3248 | 105.3% | 53.24% | 95% | 0% | 1284 | -133
[5 empty] | 2019-08-18 | 12 | 5501 | 1154 | -133 | 1 | 0 | 1287 | -104.4518 | -104.4518 | -104.4518 | 1096.9497 | 780 | 200 | 2076.9497 | 51.92% | 95% | 0% | -152.1739 | -256.6257 | -3550 | -400 | -4206.6257 | 105.2% | 53.23% | 95% | 0% | 1287 | -133
[5 empty] | 2019-08-18 | 13 | 5501.5 | 1175 | -138 | 1 | 0 | 1313 | -63.7263 | -63.7263 | -63.7263 | 1096.9497 | 780 | 200 | 2076.9497 | 51.92% | 95% | 0% | -157.8947 | -221.621 | -3550 | -400 | -4171.621 | 104.3% | 53.22% | 95% | 0% | 1313 | -138
[5 empty] | 2019-08-18 | 14 | 5502 | 1192 | -160 | 1 | 0 | 1352 | -2.6381 | -2.6381 | -2.6381 | 1096.9497 | 780 | 200 | 2076.9497 | 51.92% | 95% | 0% | -183.0664 | -185.7044 | -3550 | -400 | -4135.7044 | 103.4% | 53.22% | 95% | 0% | 1352 | -160
[5 empty] | 2019-08-18 | 15 | 5502.5 | 1205 | -200 | 1 | 0 | 1405 | 80.3792 | 80.3792 | 80.3792 | 1096.9497 | 780 | 200 | 2076.9497 | 51.92% | 95% | 0% | -228.833 | -148.4537 | -3550 | -400 | -4098.4537 | 102.5% | 53.22% | 95% | 0% | 1405 | -200
[5 empty] | 2019-08-18 | 16 | 5503 | 1225 | -236 | 1 | 0 | 1461 | 168.0956 | 168.0956 | 168.0956 | 1096.9497 | 780 | 200 | 2076.9497 | 51.92% | 95% | 0% | -270.0229 | -101.9273 | -3550 | -400 | -4051.9273 | 101.3% | 53.22% | 95% | 0% | 1461 | -236
[5 empty] | 2019-08-18 | 17 | 5503.5 | 1247 | -286 | 1 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 1095.3833 | 780 | 200 | 2075.3833 | 51.88% | 95% | 0% | -327.2311 | -46.3573 | -3550 | -400 | -3996.3573 | 99.91% | 53.22% | 95% | 0% | 1533 | -286
[5 empty] | 2019-08-18 | 18 | 5504 | 1245 | -324 | 1 | 0 | 1569 | 337.263 | 337.263 | 337.263 | 1095.3833 | 780 | 200 | 2075.3833 | 51.88% | 95% | 0% | -370.7094 | -33.4464 | -3550 | -400 | -3983.4464 | 99.59% | 53.22% | 95% | 0% | 1569 | -324
[5 empty] | 2019-08-18 | 19 | 5504.5 | 1212 | -397 | 1 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 1095.3833 | 780 | 200 | 2075.3833 | 51.88% | 95% | 0% | -454.2334 | -54.3158 | -3550 | -400 | -4004.3158 | 100.1% | 53.22% | 95% | 0% | 1609 | -397
[5 empty] | 2019-08-18 | 20 | 5505 | 1165 | -461 | 1 | 0 | 1626 | 426.5458 | 426.5458 | 426.5458 | 1095.3833 | 780 | 200 | 2075.3833 | 51.88% | 95% | 0% | -527.46 | -100.9142 | -3550 | -400 | -4050.9142 | 101.3% | 53.21% | 95% | 0% | 1626 | -461
[5 empty] | 2019-08-18 | 21 | 5505.5 | 1140 | -494 | 1 | 0 | 1634 | 439.0767 | 439.0767 | 439.0767 | 1095.3833 | 780 | 200 | 2075.3833 | 51.88% | 95% | 0% | -565.2174 | -126.1407 | -3550 | -400 | -4076.1407 | 101.9% | 53.21% | 95% | 0% | 1634 | -494
[5 empty] | 2019-08-18 | 22 | 5506 | 1060 | -549 | 1 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 1095.3833 | 780 | 200 | 2075.3833 | 51.88% | 95% | 0% | -628.1465 | -228.2289 | -3550 | -400 | -4178.2289 | 104.5% | 53.21% | 95% | 0% | 1609 | -549
[5 empty] | 2019-08-18 | 23 | 5506.5 | 987 | -620 | 1 | 0 | 1607 | 396.7848 | 396.7848 | 396.7848 | 1095.3833 | 780 | 200 | 2075.3833 | 51.88% | 95% | 0% | -709.3822 | -312.5973 | -3550 | -400 | -4262.5973 | 106.6% | 53.21% | 95% | 0% | 1607 | -620
[5 empty] | 2019-08-18 | 24 | 5507 | 917 | -660 | 1 | 0 | 1577 | 349.7939 | 349.7939 | 349.7939 | 1095.3833 | 780 | 200 | 2075.3833 | 51.88% | 95% | 0% | -755.1487 | -405.3548 | -3550 | -400 | -4355.3548 | 108.9% | 53.2% | 95% | 0% | 1577 | -660
[5 empty] | 2019-08-18 | 25 | 5507.5 | 872 | -695 | 1 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 1093.817 | 780 | 200 | 2073.817 | 51.85% | 95% | 0% | -795.1945 | -461.0643 | -3550 | -400 | -4411.0643 | 110.3% | 53.2% | 95% | 0% | 1567 | -695
[5 empty] | 2019-08-18 | 26 | 5508 | 795 | -737 | 1 | 0 | 1532 | 279.3075 | 279.3075 | 279.3075 | 1093.817 | 780 | 200 | 2073.817 | 51.85% | 95% | 0% | -843.2494 | -563.9419 | -3550 | -400 | -4513.9419 | 112.8% | 53.2% | 95% | 0% | 1532 | -737
[5 empty] | 2019-08-18 | 27 | 5508.5 | 746 | -730 | 1 | 0 | 1476 | 191.5911 | 191.5911 | 191.5911 | 1093.817 | 780 | 200 | 2073.817 | 51.85% | 95% | 0% | -835.2403 | -643.6492 | -3550 | -400 | -4593.6492 | 114.8% | 53.18% | 95% | 0% | 1476 | -730
[5 empty] | 2019-08-18 | 28 | 5509 | 742 | -732 | 1 | 0 | 1474 | 188.4584 | 188.4584 | 188.4584 | 1093.817 | 780 | 200 | 2073.817 | 51.85% | 95% | 0% | -837.5286 | -649.0702 | -3550 | -400 | -4599.0702 | 115% | 53.18% | 95% | 0% | 1474 | -732
[5 empty] | 2019-08-18 | 29 | 5509.5 | 798 | -677 | 1 | 0 | 1475 | 190.0247 | 190.0247 | 190.0247 | 1093.817 | 780 | 200 | 2073.817 | 51.85% | 95% | 0% | -774.5995 | -584.5748 | -3550 | -400 | -4534.5748 | 113.4% | 53.18% | 95% | 0% | 1475 | -677
[5 empty] | 2019-08-18 | 30 | 5510 | 772 | -696 | 1 | 0 | 1468 | 179.0602 | 179.0602 | 179.0602 | 1093.817 | 780 | 200 | 2073.817 | 51.85% | 95% | 0% | -796.3387 | -617.2785 | -3550 | -400 | -4567.2785 | 114.2% | 53.18% | 95% | 0% | 1468 | -696
[5 empty] | 2019-08-18 | 31 | 5510.5 | 812 | -672 | 1 | 0 | 1484 | 204.122 | 204.122 | 204.122 | 1093.817 | 780 | 200 | 2073.817 | 51.85% | 95% | 0% | -768.8787 | -564.7567 | -3550 | -400 | -4514.7567 | 112.9% | 53.18% | 95% | 0% | 1484 | -672
[5 empty] | 2019-08-18 | 32 | 5511 | 934 | -592 | 1 | 0 | 1526 | 269.9093 | 269.9093 | 269.9093 | 1093.817 | 780 | 200 | 2073.817 | 51.85% | 95% | 0% | -677.3455 | -407.4362 | -3550 | -400 | -4357.4362 | 108.9% | 53.17% | 95% | 0% | 1526 | -592
[5 empty] | 2019-08-18 | 33 | 5511.5 | 1092 | -522 | 1 | 0 | 1614 | 407.7494 | 407.7494 | 407.7494 | 1093.817 | 780 | 200 | 2073.817 | 51.85% | 95% | 0% | -597.254 | -189.5046 | -3550 | -400 | -4139.5046 | 103.5% | 53.17% | 95% | 0% | 1614 | -522
[5 empty] | 2019-08-18 | 34 | 5512 | 1206 | -468 | 1 | 0 | 1674 | 501.7312 | 501.7312 | 501.7312 | 1093.817 | 780 | 200 | 2073.817 | 51.85% | 95% | 0% | -535.4691 | -33.7379 | -3550 | -400 | -3983.7379 | 99.59% | 53.17% | 95% | 0% | 1674 | -468
[5 empty] | 2019-08-18 | 35 | 5512.5 | 1369 | -399 | 1 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 1093.817 | 780 | 200 | 2073.817 | 51.85% | 95% | 0% | -456.5217 | 192.4478 | -3550 | -400 | -3757.5522 | 93.94% | 53.15% | 95% | 0% | 1768 | -399
[5 empty] | 2019-08-18 | 36 | 5513 | 1473 | -362 | 1 | 0 | 1835 | 753.9159 | 753.9159 | 753.9159 | 1093.817 | 780 | 200 | 2073.817 | 51.85% | 95% | 0% | -414.1876 | 339.7283 | -3550 | -400 | -3610.2717 | 90.26% | 53.15% | 95% | 0% | 1835 | -362
[5 empty] | 2019-08-18 | 37 | 5513.5 | 1565 | -320 | 1 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -366.1327 | 466.1014 | -3550 | -400 | -3483.8986 | 87.1% | 53.14% | 95% | 0% | 1885 | -320
[5 empty] | 2019-08-18 | 38 | 5514 | 1666 | -255 | 1 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -291.762 | 596.8612 | -3550 | -400 | -3353.1388 | 83.83% | 53.14% | 95% | 0% | 1921 | -255
[5 empty] | 2019-08-18 | 39 | 5514.5 | 1739 | -209 | 1 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -239.1304 | 691.7847 | -3550 | -400 | -3258.2153 | 81.46% | 53.14% | 95% | 0% | 1948 | -209
[5 empty] | 2019-08-18 | 40 | 5515 | 1797 | -172 | 1 | 0 | 1969 | 963.8087 | 963.8087 | 963.8087 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -196.7963 | 767.0124 | -3550 | -400 | -3182.9876 | 79.57% | 53.14% | 95% | 0% | 1969 | -172
[5 empty] | 2019-08-18 | 41 | 5515.5 | 1829 | -151 | 1 | 0 | 1980 | 981.0387 | 981.0387 | 981.0387 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -172.7689 | 808.2699 | -3550 | -400 | -3141.7301 | 78.54% | 53.14% | 95% | 0% | 1980 | -151
[5 empty] | 2019-08-18 | 42 | 5516 | 1839 | -146 | 1 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -167.0481 | 821.8225 | -3550 | -400 | -3128.1775 | 78.2% | 53.14% | 95% | 0% | 1985 | -146
[5 empty] | 2019-08-18 | 43 | 5516.5 | 1823 | -144 | 1 | 0 | 1967 | 960.676 | 960.676 | 960.676 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -164.7597 | 795.9163 | -3550 | -400 | -3154.0837 | 78.85% | 53.13% | 95% | 0% | 1967 | -144
[5 empty] | 2019-08-18 | 44 | 5517 | 1766 | -142 | 0 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -162.4714 | 705.7891 | -2750 | -200 | -2244.2109 | 56.11% | 53.13% | 95% | 0% | 1908 | -142
[5 empty] | 2019-08-18 | 45 | 5517.5 | 1713 | -142 | 0 | 0 | 1855 | 785.2432 | 785.2432 | 785.2432 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -162.4714 | 622.7718 | -2750 | -200 | -2327.2282 | 58.18% | 53.12% | 95% | 0% | 1855 | -142
[5 empty] | 2019-08-18 | 46 | 5518 | 1603 | -142 | 0 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -162.4714 | 450.4717 | -2750 | -200 | -2499.5283 | 62.49% | 53.12% | 95% | 0% | 1745 | -142
[5 empty] | 2019-08-18 | 47 | 5518.5 | 1473 | -141 | 0 | 0 | 1614 | 407.7494 | 407.7494 | 407.7494 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -161.3272 | 246.4222 | -2750 | -200 | -2703.5778 | 67.59% | 53.12% | 95% | 0% | 1614 | -141
[5 empty] | 2019-08-18 | 48 | 5519 | 1382 | -141 | 0 | 0 | 1523 | 265.2102 | 265.2102 | 265.2102 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -161.3272 | 103.883 | -2750 | -200 | -2846.117 | 71.15% | 53.11% | 95% | 0% | 1523 | -141
[5 empty] | 2019-08-19 | 1 | 5519.5 | 1309 | -140 | 0 | 0 | 1449 | 149.2993 | 149.2993 | 149.2993 | 1092.2506 | 780 | 200 | 2072.2506 | 51.81% | 95% | 0% | -160.1831 | -10.8838 | -2750 | -200 | -2960.8838 | 74.02% | 53.11% | 95% | 0% | 1449 | -140
[5 empty] | 2019-08-19 | 2 | 5520 | 1267 | -138 | 0 | 0 | 1405 | 80.3792 | 80.3792 | 80.3792 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -157.8947 | -77.5155 | -2750 | -200 | -3027.5155 | 75.69% | 53.11% | 95% | 0% | 1405 | -138
[5 empty] | 2019-08-19 | 3 | 5520.5 | 1237 | -138 | 0 | 0 | 1375 | 33.3883 | 33.3883 | 33.3883 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -157.8947 | -124.5064 | -2750 | -200 | -3074.5064 | 76.86% | 53.1% | 95% | 0% | 1375 | -138
[5 empty] | 2019-08-19 | 4 | 5521 | 1226 | -138 | 0 | 0 | 1364 | 16.1583 | 16.1583 | 16.1583 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -157.8947 | -141.7365 | -2750 | -200 | -3091.7365 | 77.29% | 53.1% | 95% | 0% | 1364 | -138
[5 empty] | 2019-08-19 | 5 | 5521.5 | 1207 | -137 | 0 | 0 | 1344 | -15.169 | -15.169 | -15.169 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -156.7506 | -171.9196 | -2750 | -200 | -3121.9196 | 78.05% | 53.09% | 95% | 0% | 1344 | -137
[5 empty] | 2019-08-19 | 6 | 5522 | 1176 | -137 | 0 | 0 | 1313 | -63.7263 | -63.7263 | -63.7263 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -156.7506 | -220.4769 | -2750 | -200 | -3170.4769 | 79.26% | 53.09% | 95% | 0% | 1313 | -137
[5 empty] | 2019-08-19 | 7 | 5522.5 | 1166 | -136 | 0 | 0 | 1302 | -80.9563 | -80.9563 | -80.9563 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -155.6064 | -236.5627 | -2750 | -200 | -3186.5627 | 79.66% | 53.09% | 95% | 0% | 1302 | -136
[5 empty] | 2019-08-19 | 8 | 5523 | 1163 | -136 | 0 | 0 | 1299 | -85.6554 | -85.6554 | -85.6554 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -155.6064 | -241.2618 | -2750 | -200 | -3191.2618 | 79.78% | 53.09% | 95% | 0% | 1299 | -136
[5 empty] | 2019-08-19 | 9 | 5523.5 | 1182 | -133 | 0 | 0 | 1315 | -60.5936 | -60.5936 | -60.5936 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -152.1739 | -212.7675 | -2750 | -200 | -3162.7675 | 79.07% | 53.08% | 95% | 0% | 1315 | -133
[5 empty] | 2019-08-19 | 10 | 5524 | 1204 | -130 | 0 | 0 | 1334 | -30.8326 | -30.8326 | -30.8326 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -148.7414 | -179.5741 | -2750 | -200 | -3129.5741 | 78.24% | 53.08% | 95% | 0% | 1334 | -130
[5 empty] | 2019-08-19 | 11 | 5524.5 | 1279 | -129 | 0 | 0 | 1408 | 85.0783 | 85.0783 | 85.0783 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -147.5973 | -62.5189 | -2750 | -200 | -3012.5189 | 75.31% | 53.08% | 95% | 0% | 1408 | -129
[5 empty] | 2019-08-19 | 12 | 5525 | 1344 | -127 | 0 | 0 | 1471 | 183.7593 | 183.7593 | 183.7593 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -145.3089 | 38.4504 | -2750 | -200 | -2911.5496 | 72.79% | 53.07% | 95% | 0% | 1471 | -127
[5 empty] | 2019-08-19 | 13 | 5525.5 | 1503 | -134 | 0 | 0 | 1637 | 443.7758 | 443.7758 | 443.7758 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -153.3181 | 290.4577 | -2750 | -200 | -2659.5423 | 66.49% | 53.07% | 95% | 0% | 1637 | -134
[5 empty] | 2019-08-19 | 14 | 5526 | 1606 | -155 | 1 | 0 | 1761 | 638.0049 | 638.0049 | 638.0049 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -177.3455 | 460.6594 | -3550 | -400 | -3489.3406 | 87.23% | 53.07% | 95% | 0% | 1761 | -155
[5 empty] | 2019-08-19 | 15 | 5526.5 | 1746 | -191 | 1 | 0 | 1937 | 913.6851 | 913.6851 | 913.6851 | 1090.6843 | 780 | 200 | 2070.6843 | 51.77% | 95% | 0% | -218.5355 | 695.1496 | -3550 | -400 | -3254.8504 | 81.37% | 53.07% | 95% | 0% | 1937 | -191
[5 empty] | 2019-08-19 | 16 | 5527 | 1792 | -244 | 1 | 0 | 2036 | 1068.7552 | 1068.7552 | 1068.7552 | 1089.1179 | 780 | 200 | 2069.1179 | 51.73% | 95% | 0% | -279.1762 | 789.579 | -3550 | -400 | -3160.421 | 79.01% | 53.06% | 95% | 0% | 2036 | -244
[5 empty] | 2019-08-19 | 17 | 5527.5 | 1834 | -300 | 1 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 1089.1179 | 780 | 200 | 2069.1179 | 51.73% | 95% | 0% | -343.2494 | 879.0094 | -3550 | -400 | -3070.9906 | 76.77% | 53.06% | 95% | 0% | 2134 | -300
[5 empty] | 2019-08-19 | 18 | 5528 | 1790 | -348 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1089.1179 | 780 | 200 | 2069.1179 | 51.73% | 95% | 0% | -398.1693 | 830.355 | -3550 | -400 | -3119.645 | 77.99% | 53.05% | 95% | 0% | 2138 | -348
[5 empty] | 2019-08-19 | 19 | 5528.5 | 1743 | -398 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1089.1179 | 780 | 200 | 2069.1179 | 51.73% | 95% | 0% | -455.3776 | 777.8458 | -3550 | -400 | -3172.1542 | 79.3% | 53.05% | 95% | 0% | 2141 | -398
[5 empty] | 2019-08-19 | 20 | 5529 | 1680 | -447 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 1089.1179 | 780 | 200 | 2069.1179 | 51.73% | 95% | 0% | -511.4416 | 699.8527 | -3550 | -400 | -3250.1473 | 81.25% | 53.05% | 95% | 0% | 2127 | -447
[5 empty] | 2019-08-19 | 21 | 5529.5 | 1579 | -521 | 1 | 0 | 2100 | 1169.0025 | 1169.0025 | 1169.0025 | 1089.1179 | 780 | 200 | 2069.1179 | 51.73% | 95% | 0% | -596.1098 | 572.8926 | -3550 | -400 | -3377.1074 | 84.43% | 53.05% | 95% | 0% | 2100 | -521
[5 empty] | 2019-08-19 | 22 | 5530 | 1519 | -557 | 1 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 1089.1179 | 780 | 200 | 2069.1179 | 51.73% | 95% | 0% | -637.2998 | 494.11 | -3550 | -400 | -3455.89 | 86.4% | 53.03% | 95% | 0% | 2076 | -557
[5 empty] | 2019-08-19 | 23 | 5530.5 | 1455 | -608 | 1 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 1089.1179 | 780 | 200 | 2069.1179 | 51.73% | 95% | 0% | -695.6522 | 415.3948 | -3550 | -400 | -3534.6052 | 88.37% | 53.03% | 95% | 0% | 2063 | -608
[5 empty] | 2019-08-19 | 24 | 5531 | 1398 | -641 | 1 | 0 | 2039 | 1073.4542 | 1073.4542 | 1073.4542 | 1089.1179 | 780 | 200 | 2069.1179 | 51.73% | 95% | 0% | -733.4096 | 340.0446 | -3550 | -400 | -3609.9554 | 90.25% | 53.02% | 95% | 0% | 2039 | -641
[5 empty] | 2019-08-19 | 25 | 5531.5 | 1380 | -650 | 1 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 1089.1179 | 780 | 200 | 2069.1179 | 51.73% | 95% | 0% | -743.7071 | 315.6499 | -3550 | -400 | -3634.3501 | 90.86% | 53.02% | 95% | 0% | 2030 | -650
[5 empty] | 2019-08-19 | 26 | 5532 | 1399 | -636 | 1 | 0 | 2035 | 1067.1888 | 1067.1888 | 1067.1888 | 1089.1179 | 780 | 200 | 2069.1179 | 51.73% | 95% | 0% | -727.6888 | 339.5 | -3550 | -400 | -3610.5 | 90.26% | 53.01% | 95% | 0% | 2035 | -636
[5 empty] | 2019-08-19 | 27 | 5532.5 | 1361 | -665 | 1 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 1089.1179 | 780 | 200 | 2069.1179 | 51.73% | 95% | 0% | -760.8696 | 292.2219 | -3550 | -400 | -3657.7781 | 91.44% | 53.01% | 95% | 0% | 2026 | -665
[5 empty] | 2019-08-19 | 28 | 5533 | 1365 | -644 | 1 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 1087.5515 | 780 | 200 | 2067.5515 | 51.69% | 95% | 0% | -736.8421 | 289.6212 | -3550 | -400 | -3660.3788 | 91.51% | 53% | 95% | 0% | 2009 | -644
[5 empty] | 2019-08-19 | 29 | 5533.5 | 1349 | -647 | 1 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 1087.5515 | 780 | 200 | 2067.5515 | 51.69% | 95% | 0% | -740.2746 | 265.826 | -3550 | -400 | -3684.174 | 92.1% | 53% | 95% | 0% | 1996 | -647
[5 empty] | 2019-08-19 | 30 | 5534 | 1348 | -634 | 1 | 0 | 1982 | 984.1715 | 984.1715 | 984.1715 | 1087.5515 | 780 | 200 | 2067.5515 | 51.69% | 95% | 0% | -725.4005 | 258.771 | -3550 | -400 | -3691.229 | 92.28% | 53% | 95% | 0% | 1982 | -634
[5 empty] | 2019-08-19 | 31 | 5534.5 | 1357 | -636 | 1 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 1087.5515 | 780 | 200 | 2067.5515 | 51.69% | 95% | 0% | -727.6888 | 273.7127 | -3550 | -400 | -3676.2873 | 91.91% | 53% | 95% | 0% | 1993 | -636
[5 empty] | 2019-08-19 | 32 | 5535 | 1410 | -591 | 1 | 0 | 2001 | 1013.9324 | 1013.9324 | 1013.9324 | 1087.5515 | 780 | 200 | 2067.5515 | 51.69% | 95% | 0% | -676.2014 | 337.731 | -3550 | -400 | -3612.269 | 90.31% | 53% | 95% | 0% | 2001 | -591
[5 empty] | 2019-08-19 | 33 | 5535.5 | 1487 | -551 | 1 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 1087.5515 | 780 | 200 | 2067.5515 | 51.69% | 95% | 0% | -630.4348 | 441.4531 | -3550 | -400 | -3508.5469 | 87.71% | 52.99% | 95% | 0% | 2038 | -551
[5 empty] | 2019-08-19 | 34 | 5536 | 1642 | -489 | 1 | 0 | 2131 | 1217.5598 | 1217.5598 | 1217.5598 | 1087.5515 | 780 | 200 | 2067.5515 | 51.69% | 95% | 0% | -559.4966 | 658.0632 | -3550 | -400 | -3291.9368 | 82.3% | 52.99% | 95% | 0% | 2131 | -489
[5 empty] | 2019-08-19 | 35 | 5536.5 | 1799 | -407 | 1 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 1087.5515 | 780 | 200 | 2067.5515 | 51.69% | 95% | 0% | -465.6751 | 869.362 | -3550 | -400 | -3080.638 | 77.02% | 52.99% | 95% | 0% | 2206 | -407
[5 empty] | 2019-08-19 | 36 | 5537 | 1919 | -338 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 1087.5515 | 780 | 200 | 2067.5515 | 51.69% | 95% | 0% | -386.7277 | 1028.194 | -3550 | -400 | -2921.806 | 73.05% | 52.99% | 95% | 0% | 2257 | -338
[5 empty] | 2019-08-19 | 37 | 5537.5 | 2024 | -295 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 1087.5515 | 780 | 200 | 2067.5515 | 51.69% | 95% | 0% | -337.5286 | 1174.5077 | -3550 | -400 | -2775.4923 | 69.39% | 52.98% | 95% | 0% | 2319 | -295
[5 empty] | 2019-08-19 | 38 | 5538 | 2118 | -224 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 1087.5515 | 780 | 200 | 2067.5515 | 51.69% | 95% | 0% | -256.2929 | 1291.7697 | -3550 | -400 | -2658.2303 | 66.46% | 52.98% | 95% | 0% | 2342 | -224
[5 empty] | 2019-08-19 | 39 | 5538.5 | 2171 | -175 | 1 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 1087.5515 | 780 | 200 | 2067.5515 | 51.69% | 95% | 0% | -200.2288 | 1354.0993 | -3550 | -400 | -2595.9007 | 64.9% | 52.98% | 95% | 0% | 2346 | -175
[5 empty] | 2019-08-19 | 40 | 5539 | 2205 | -134 | 1 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 1085.9852 | 780 | 200 | 2065.9852 | 51.65% | 95% | 0% | -153.3181 | 1390.0455 | -3550 | -400 | -2559.9545 | 64% | 52.98% | 95% | 0% | 2339 | -134
[5 empty] | 2019-08-19 | 41 | 5539.5 | 2215 | -114 | 1 | 0 | 2329 | 1527.6999 | 1527.6999 | 1527.6999 | 1085.9852 | 780 | 200 | 2065.9852 | 51.65% | 95% | 0% | -130.4348 | 1397.2651 | -3550 | -400 | -2552.7349 | 63.82% | 52.97% | 95% | 0% | 2329 | -114
[5 empty] | 2019-08-19 | 42 | 5540 | 2222 | -108 | 1 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 1085.9852 | 780 | 200 | 2065.9852 | 51.65% | 95% | 0% | -123.5698 | 1405.6965 | -3550 | -400 | -2544.3035 | 63.61% | 52.97% | 95% | 0% | 2330 | -108
[5 empty] | 2019-08-19 | 43 | 5540.5 | 2193 | -106 | 1 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 1085.9852 | 780 | 200 | 2065.9852 | 51.65% | 95% | 0% | -121.2815 | 1359.4275 | -3550 | -400 | -2590.5725 | 64.76% | 52.97% | 95% | 0% | 2299 | -106
[5 empty] | 2019-08-19 | 44 | 5541 | 2105 | -104 | 0 | 0 | 2209 | 1339.7362 | 1339.7362 | 1339.7362 | 1085.9852 | 780 | 200 | 2065.9852 | 51.65% | 95% | 0% | -118.9931 | 1220.7431 | -2750 | -200 | -1729.2569 | 43.23% | 52.97% | 95% | 0% | 2209 | -104
[5 empty] | 2019-08-19 | 45 | 5541.5 | 1998 | -104 | 0 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 1085.9852 | 780 | 200 | 2065.9852 | 51.65% | 95% | 0% | -118.9931 | 1053.1421 | -2750 | -200 | -1896.8579 | 47.42% | 52.97% | 95% | 0% | 2102 | -104
[5 empty] | 2019-08-19 | 46 | 5542 | 1854 | -103 | 0 | 0 | 1957 | 945.0124 | 945.0124 | 945.0124 | 1085.9852 | 780 | 200 | 2065.9852 | 51.65% | 95% | 0% | -117.849 | 827.1634 | -2750 | -200 | -2122.8366 | 53.07% | 52.97% | 95% | 0% | 1957 | -103
[5 empty] | 2019-08-19 | 47 | 5542.5 | 1707 | -104 | 0 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1085.9852 | 780 | 200 | 2065.9852 | 51.65% | 95% | 0% | -118.9931 | 597.33 | -2750 | -200 | -2352.67 | 58.82% | 52.96% | 95% | 0% | 1811 | -104
[5 empty] | 2019-08-19 | 48 | 5543 | 1602 | -104 | 0 | 0 | 1706 | 551.8549 | 551.8549 | 551.8549 | 1085.9852 | 780 | 200 | 2065.9852 | 51.65% | 95% | 0% | -118.9931 | 432.8618 | -2750 | -200 | -2517.1382 | 62.93% | 52.96% | 95% | 0% | 1706 | -104
[5 empty] | 2019-08-20 | 1 | 5543.5 | 1517 | -100 | 0 | 0 | 1617 | 412.4485 | 412.4485 | 412.4485 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -114.4165 | 298.032 | -2750 | -200 | -2651.968 | 66.3% | 52.96% | 95% | 0% | 1617 | -100
[5 empty] | 2019-08-20 | 2 | 5544 | 1471 | -96 | 0 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -109.8398 | 224.2904 | -2750 | -200 | -2725.7096 | 68.14% | 52.95% | 95% | 0% | 1567 | -96
[5 empty] | 2019-08-20 | 3 | 5544.5 | 1442 | -95 | 0 | 0 | 1537 | 287.1393 | 287.1393 | 287.1393 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -108.6957 | 178.4437 | -2750 | -200 | -2771.5563 | 69.29% | 52.95% | 95% | 0% | 1537 | -95
[5 empty] | 2019-08-20 | 4 | 5545 | 1422 | -93 | 0 | 0 | 1515 | 252.6793 | 252.6793 | 252.6793 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -106.4073 | 146.272 | -2750 | -200 | -2803.728 | 70.09% | 52.94% | 95% | 0% | 1515 | -93
[5 empty] | 2019-08-20 | 5 | 5545.5 | 1405 | -92 | 0 | 0 | 1497 | 224.4847 | 224.4847 | 224.4847 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -105.2632 | 119.2216 | -2750 | -200 | -2830.7784 | 70.77% | 52.93% | 95% | 0% | 1497 | -92
[5 empty] | 2019-08-20 | 6 | 5546 | 1385 | -91 | 0 | 0 | 1476 | 191.5911 | 191.5911 | 191.5911 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -104.119 | 87.4721 | -2750 | -200 | -2862.5279 | 71.56% | 52.92% | 95% | 0% | 1476 | -91
[5 empty] | 2019-08-20 | 7 | 5546.5 | 1373 | -90 | 0 | 0 | 1463 | 171.2284 | 171.2284 | 171.2284 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -102.9748 | 68.2535 | -2750 | -200 | -2881.7465 | 72.04% | 52.92% | 95% | 0% | 1463 | -90
[5 empty] | 2019-08-20 | 8 | 5547 | 1365 | -89 | 0 | 0 | 1454 | 157.1311 | 157.1311 | 157.1311 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -101.8307 | 55.3004 | -2750 | -200 | -2894.6996 | 72.37% | 52.92% | 95% | 0% | 1454 | -89
[5 empty] | 2019-08-20 | 9 | 5547.5 | 1383 | -85 | 0 | 0 | 1468 | 179.0602 | 179.0602 | 179.0602 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -97.254 | 81.8062 | -2750 | -200 | -2868.1938 | 71.7% | 52.92% | 95% | 0% | 1468 | -85
[5 empty] | 2019-08-20 | 10 | 5548 | 1411 | -81 | 0 | 0 | 1492 | 216.6529 | 216.6529 | 216.6529 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -92.6773 | 123.9756 | -2750 | -200 | -2826.0244 | 70.65% | 52.92% | 95% | 0% | 1492 | -81
[5 empty] | 2019-08-20 | 11 | 5548.5 | 1482 | -79 | 0 | 0 | 1561 | 324.7321 | 324.7321 | 324.7321 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -90.389 | 234.3431 | -2750 | -200 | -2715.6569 | 67.89% | 52.92% | 95% | 0% | 1561 | -79
[5 empty] | 2019-08-20 | 12 | 5549 | 1553 | -77 | 1 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -88.1007 | 344.7105 | -3550 | -400 | -3605.2895 | 90.13% | 52.91% | 95% | 0% | 1630 | -77
[5 empty] | 2019-08-20 | 13 | 5549.5 | 1678 | -81 | 1 | 0 | 1759 | 634.8722 | 634.8722 | 634.8722 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -92.6773 | 542.1949 | -3550 | -400 | -3407.8051 | 85.2% | 52.91% | 95% | 0% | 1759 | -81
[5 empty] | 2019-08-20 | 14 | 5550 | 1813 | -104 | 1 | 0 | 1917 | 882.3578 | 882.3578 | 882.3578 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -118.9931 | 763.3647 | -3550 | -400 | -3186.6353 | 79.67% | 52.91% | 95% | 0% | 1917 | -104
[5 empty] | 2019-08-20 | 15 | 5550.5 | 1946 | -147 | 1 | 0 | 2093 | 1158.0379 | 1158.0379 | 1158.0379 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -168.1922 | 989.8457 | -3550 | -400 | -2960.1543 | 74% | 52.91% | 95% | 0% | 2093 | -147
[5 empty] | 2019-08-20 | 16 | 5551 | 1964 | -200 | 1 | 0 | 2164 | 1269.2498 | 1269.2498 | 1269.2498 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -228.833 | 1040.4168 | -3550 | -400 | -2909.5832 | 72.74% | 52.9% | 95% | 0% | 2164 | -200
[5 empty] | 2019-08-20 | 17 | 5551.5 | 1984 | -262 | 1 | 0 | 2246 | 1397.6917 | 1397.6917 | 1397.6917 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -299.7712 | 1097.9205 | -3550 | -400 | -2852.0795 | 71.3% | 52.9% | 95% | 0% | 2246 | -262
[5 empty] | 2019-08-20 | 18 | 5552 | 1920 | -338 | 1 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -386.7277 | 1029.7604 | -3550 | -400 | -2920.2396 | 73.01% | 52.9% | 95% | 0% | 2258 | -338
[5 empty] | 2019-08-20 | 19 | 5552.5 | 1866 | -390 | 1 | 0 | 2256 | 1413.3553 | 1413.3553 | 1413.3553 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -446.2243 | 967.1311 | -3550 | -400 | -2982.8689 | 74.57% | 52.9% | 95% | 0% | 2256 | -390
[5 empty] | 2019-08-20 | 20 | 5553 | 1774 | -444 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 1084.4188 | 780 | 200 | 2064.4188 | 51.61% | 95% | 0% | -508.0092 | 845.8243 | -3550 | -400 | -3104.1757 | 77.6% | 52.9% | 95% | 0% | 2218 | -444
[5 empty] | 2019-08-20 | 21 | 5553.5 | 1697 | -482 | 1 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 1082.8524 | 780 | 200 | 2062.8524 | 51.57% | 95% | 0% | -551.4874 | 741.2578 | -3550 | -400 | -3208.7422 | 80.22% | 52.88% | 95% | 0% | 2179 | -482
[5 empty] | 2019-08-20 | 22 | 5554 | 1638 | -522 | 1 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1082.8524 | 780 | 200 | 2062.8524 | 51.57% | 95% | 0% | -597.254 | 665.7303 | -3550 | -400 | -3284.2697 | 82.11% | 52.88% | 95% | 0% | 2160 | -522
[5 empty] | 2019-08-20 | 23 | 5554.5 | 1629 | -530 | 1 | 0 | 2159 | 1261.418 | 1261.418 | 1261.418 | 1082.8524 | 780 | 200 | 2062.8524 | 51.57% | 95% | 0% | -606.4073 | 655.0106 | -3550 | -400 | -3294.9894 | 82.37% | 52.88% | 95% | 0% | 2159 | -530
[5 empty] | 2019-08-20 | 24 | 5555 | 1590 | -561 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 1082.8524 | 780 | 200 | 2062.8524 | 51.57% | 95% | 0% | -641.8764 | 607.0106 | -3550 | -400 | -3342.9894 | 83.57% | 52.88% | 95% | 0% | 2151 | -561
[5 empty] | 2019-08-20 | 25 | 5555.5 | 1647 | -506 | 1 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 1082.8524 | 780 | 200 | 2062.8524 | 51.57% | 95% | 0% | -578.9474 | 673.0724 | -3550 | -400 | -3276.9276 | 81.92% | 52.88% | 95% | 0% | 2153 | -506
[5 empty] | 2019-08-20 | 26 | 5556 | 1557 | -578 | 1 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 1082.8524 | 780 | 200 | 2062.8524 | 51.57% | 95% | 0% | -661.3272 | 562.498 | -3550 | -400 | -3387.502 | 84.69% | 52.88% | 95% | 0% | 2135 | -578
[5 empty] | 2019-08-20 | 27 | 5556.5 | 1527 | -580 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1082.8524 | 780 | 200 | 2062.8524 | 51.57% | 95% | 0% | -663.6156 | 516.3515 | -3550 | -400 | -3433.6485 | 85.84% | 52.87% | 95% | 0% | 2107 | -580
[5 empty] | 2019-08-20 | 28 | 5557 | 1487 | -585 | 1 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 1082.8524 | 780 | 200 | 2062.8524 | 51.57% | 95% | 0% | -669.3364 | 455.8079 | -3550 | -400 | -3494.1921 | 87.35% | 52.87% | 95% | 0% | 2072 | -585
[5 empty] | 2019-08-20 | 29 | 5557.5 | 1463 | -597 | 1 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 1082.8524 | 780 | 200 | 2062.8524 | 51.57% | 95% | 0% | -683.0664 | 423.2815 | -3550 | -400 | -3526.7185 | 88.17% | 52.87% | 95% | 0% | 2060 | -597
[5 empty] | 2019-08-20 | 30 | 5558 | 1491 | -561 | 1 | 0 | 2052 | 1093.817 | 1093.817 | 1093.817 | 1082.8524 | 780 | 200 | 2062.8524 | 51.57% | 95% | 0% | -641.8764 | 451.9406 | -3550 | -400 | -3498.0594 | 87.45% | 52.86% | 95% | 0% | 2052 | -561
[5 empty] | 2019-08-20 | 31 | 5558.5 | 1507 | -541 | 1 | 0 | 2048 | 1087.5515 | 1087.5515 | 1087.5515 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -618.9931 | 468.5584 | -3550 | -400 | -3481.4416 | 87.04% | 52.85% | 95% | 0% | 2048 | -541
[5 empty] | 2019-08-20 | 32 | 5559 | 1589 | -495 | 1 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -566.3616 | 577.5791 | -3550 | -400 | -3372.4209 | 84.31% | 52.85% | 95% | 0% | 2084 | -495
[5 empty] | 2019-08-20 | 33 | 5559.5 | 1688 | -452 | 1 | 0 | 2140 | 1231.657 | 1231.657 | 1231.657 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -517.1625 | 714.4946 | -3550 | -400 | -3235.5054 | 80.89% | 52.85% | 95% | 0% | 2140 | -452
[5 empty] | 2019-08-20 | 34 | 5560 | 1838 | -398 | 1 | 0 | 2236 | 1382.028 | 1382.028 | 1382.028 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -455.3776 | 926.6505 | -3550 | -400 | -3023.3495 | 75.58% | 52.85% | 95% | 0% | 2236 | -398
[5 empty] | 2019-08-20 | 35 | 5560.5 | 1998 | -331 | 1 | 0 | 2329 | 1527.6999 | 1527.6999 | 1527.6999 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -378.7185 | 1148.9814 | -3550 | -400 | -2801.0186 | 70.03% | 52.85% | 95% | 0% | 2329 | -331
[5 empty] | 2019-08-20 | 36 | 5561 | 2111 | -267 | 1 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -305.492 | 1298.9598 | -3550 | -400 | -2651.0402 | 66.28% | 52.85% | 95% | 0% | 2378 | -267
[5 empty] | 2019-08-20 | 37 | 5561.5 | 2194 | -202 | 1 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -231.1213 | 1401.525 | -3550 | -400 | -2548.475 | 63.71% | 52.85% | 95% | 0% | 2396 | -202
[5 empty] | 2019-08-20 | 38 | 5562 | 2276 | -154 | 1 | 0 | 2430 | 1685.9027 | 1685.9027 | 1685.9027 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -176.2014 | 1509.7013 | -3550 | -400 | -2440.2987 | 61.01% | 52.83% | 95% | 0% | 2430 | -154
[5 empty] | 2019-08-20 | 39 | 5562.5 | 2344 | -106 | 1 | 0 | 2450 | 1717.23 | 1717.23 | 1717.23 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -121.2815 | 1595.9485 | -3550 | -400 | -2354.0515 | 58.85% | 52.83% | 95% | 0% | 2450 | -106
[5 empty] | 2019-08-20 | 40 | 5563 | 2366 | -72 | 1 | 0 | 2438 | 1698.4336 | 1698.4336 | 1698.4336 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -82.3799 | 1616.0538 | -3550 | -400 | -2333.9462 | 58.35% | 52.82% | 95% | 0% | 2438 | -72
[5 empty] | 2019-08-20 | 41 | 5563.5 | 2372 | -59 | 1 | 0 | 2431 | 1687.4691 | 1687.4691 | 1687.4691 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -67.5057 | 1619.9634 | -3550 | -400 | -2330.0366 | 58.25% | 52.82% | 95% | 0% | 2431 | -59
[5 empty] | 2019-08-20 | 42 | 5564 | 2409 | -57 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -65.2174 | 1677.0744 | -3550 | -400 | -2272.9256 | 56.82% | 52.82% | 95% | 0% | 2466 | -57
[5 empty] | 2019-08-20 | 43 | 5564.5 | 2357 | -57 | 1 | 0 | 2414 | 1660.8409 | 1660.8409 | 1660.8409 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -65.2174 | 1595.6235 | -3550 | -400 | -2354.3765 | 58.86% | 52.82% | 95% | 0% | 2414 | -57
[5 empty] | 2019-08-20 | 44 | 5565 | 2258 | -57 | 0 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -65.2174 | 1440.5534 | -2750 | -200 | -1509.4466 | 37.74% | 52.81% | 95% | 0% | 2315 | -57
[5 empty] | 2019-08-20 | 45 | 5565.5 | 2134 | -57 | 0 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -65.2174 | 1246.3242 | -2750 | -200 | -1703.6758 | 42.59% | 52.8% | 95% | 0% | 2191 | -57
[5 empty] | 2019-08-20 | 46 | 5566 | 1992 | -58 | 0 | 0 | 2050 | 1090.6843 | 1090.6843 | 1090.6843 | 1081.2861 | 780 | 200 | 2061.2861 | 51.53% | 95% | 0% | -66.3616 | 1024.3227 | -2750 | -200 | -1925.6773 | 48.14% | 52.79% | 95% | 0% | 2050 | -58
[5 empty] | 2019-08-20 | 47 | 5566.5 | 1850 | -58 | 0 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -66.3616 | 801.899 | -2750 | -200 | -2148.101 | 53.7% | 52.79% | 95% | 0% | 1908 | -58
[5 empty] | 2019-08-20 | 48 | 5567 | 1732 | -58 | 0 | 0 | 1790 | 683.4295 | 683.4295 | 683.4295 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -66.3616 | 617.068 | -2750 | -200 | -2332.932 | 58.32% | 52.79% | 95% | 0% | 1790 | -58
[5 empty] | 2019-08-21 | 1 | 5567.5 | 1637 | -59 | 0 | 0 | 1696 | 536.1913 | 536.1913 | 536.1913 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -67.5057 | 468.6855 | -2750 | -200 | -2481.3145 | 62.03% | 52.78% | 95% | 0% | 1696 | -59
[5 empty] | 2019-08-21 | 2 | 5568 | 1587 | -59 | 0 | 0 | 1646 | 457.873 | 457.873 | 457.873 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -67.5057 | 390.3673 | -2750 | -200 | -2559.6327 | 63.99% | 52.78% | 95% | 0% | 1646 | -59
[5 empty] | 2019-08-21 | 3 | 5568.5 | 1547 | -60 | 0 | 0 | 1607 | 396.7848 | 396.7848 | 396.7848 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -68.6499 | 328.1349 | -2750 | -200 | -2621.8651 | 65.55% | 52.77% | 95% | 0% | 1607 | -60
[5 empty] | 2019-08-21 | 4 | 5569 | 1528 | -60 | 0 | 0 | 1588 | 367.0239 | 367.0239 | 367.0239 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -68.6499 | 298.374 | -2750 | -200 | -2651.626 | 66.29% | 52.77% | 95% | 0% | 1588 | -60
[5 empty] | 2019-08-21 | 5 | 5569.5 | 1505 | -61 | 0 | 0 | 1566 | 332.5639 | 332.5639 | 332.5639 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -69.7941 | 262.7698 | -2750 | -200 | -2687.2302 | 67.18% | 52.77% | 95% | 0% | 1566 | -61
[5 empty] | 2019-08-21 | 6 | 5570 | 1483 | -62 | 0 | 0 | 1545 | 299.6702 | 299.6702 | 299.6702 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -70.9382 | 228.732 | -2750 | -200 | -2721.268 | 68.03% | 52.76% | 95% | 0% | 1545 | -62
[5 empty] | 2019-08-21 | 7 | 5570.5 | 1463 | -62 | 0 | 0 | 1525 | 268.343 | 268.343 | 268.343 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -70.9382 | 197.4047 | -2750 | -200 | -2752.5953 | 68.81% | 52.76% | 95% | 0% | 1525 | -62
[5 empty] | 2019-08-21 | 8 | 5571 | 1443 | -62 | 1 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -70.9382 | 166.0774 | -3550 | -400 | -3783.9226 | 94.6% | 52.76% | 95% | 0% | 1505 | -62
[5 empty] | 2019-08-21 | 9 | 5571.5 | 1443 | -64 | 1 | 0 | 1507 | 240.1484 | 240.1484 | 240.1484 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -73.2265 | 166.9218 | -3550 | -400 | -3783.0782 | 94.58% | 52.76% | 95% | 0% | 1507 | -64
[5 empty] | 2019-08-21 | 10 | 5572 | 1453 | -66 | 1 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -75.5149 | 183.4299 | -3550 | -400 | -3766.5701 | 94.16% | 52.75% | 95% | 0% | 1519 | -66
[5 empty] | 2019-08-21 | 11 | 5572.5 | 1509 | -67 | 1 | 0 | 1576 | 348.2275 | 348.2275 | 348.2275 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -76.659 | 271.5685 | -3550 | -400 | -3678.4315 | 91.96% | 52.75% | 95% | 0% | 1576 | -67
[5 empty] | 2019-08-21 | 12 | 5573 | 1572 | -69 | 1 | 0 | 1641 | 450.0412 | 450.0412 | 450.0412 | 1079.7197 | 780 | 200 | 2059.7197 | 51.49% | 95% | 0% | -78.9474 | 371.0939 | -3550 | -400 | -3578.9061 | 89.47% | 52.74% | 95% | 0% | 1641 | -69
[5 empty] | 2019-08-21 | 13 | 5573.5 | 1701 | -77 | 1 | 0 | 1778 | 664.6331 | 664.6331 | 664.6331 | 1078.1533 | 780 | 200 | 2058.1533 | 51.45% | 95% | 0% | -88.1007 | 576.5325 | -3550 | -400 | -3373.4675 | 84.34% | 52.74% | 95% | 0% | 1778 | -77
[5 empty] | 2019-08-21 | 14 | 5574 | 1802 | -107 | 1 | 0 | 1909 | 869.8269 | 869.8269 | 869.8269 | 1078.1533 | 780 | 200 | 2058.1533 | 51.45% | 95% | 0% | -122.4256 | 747.4012 | -3550 | -400 | -3202.5988 | 80.06% | 52.74% | 95% | 0% | 1909 | -107
[5 empty] | 2019-08-21 | 15 | 5574.5 | 1932 | -149 | 1 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 1078.1533 | 780 | 200 | 2058.1533 | 51.45% | 95% | 0% | -170.4805 | 968.761 | -3550 | -400 | -2981.239 | 74.53% | 52.74% | 95% | 0% | 2081 | -149
[5 empty] | 2019-08-21 | 16 | 5575 | 1969 | -192 | 1 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 1078.1533 | 780 | 200 | 2058.1533 | 51.45% | 95% | 0% | -219.6796 | 1044.8711 | -3550 | -400 | -2905.1289 | 72.63% | 52.74% | 95% | 0% | 2161 | -192
[5 empty] | 2019-08-21 | 17 | 5575.5 | 1972 | -245 | 1 | 0 | 2217 | 1352.2671 | 1352.2671 | 1352.2671 | 1078.1533 | 780 | 200 | 2058.1533 | 51.45% | 95% | 0% | -280.3204 | 1071.9467 | -3550 | -400 | -2878.0533 | 71.95% | 52.74% | 95% | 0% | 2217 | -245
[5 empty] | 2019-08-21 | 18 | 5576 | 1922 | -306 | 1 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 1078.1533 | 780 | 200 | 2058.1533 | 51.45% | 95% | 0% | -350.1144 | 1019.3827 | -3550 | -400 | -2930.6173 | 73.27% | 52.74% | 95% | 0% | 2228 | -306
[5 empty] | 2019-08-21 | 19 | 5576.5 | 1855 | -387 | 1 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 1078.1533 | 780 | 200 | 2058.1533 | 51.45% | 95% | 0% | -442.7918 | 948.6345 | -3550 | -400 | -3001.3655 | 75.03% | 52.73% | 95% | 0% | 2242 | -387
[5 empty] | 2019-08-21 | 20 | 5577 | 1782 | -454 | 1 | 0 | 2236 | 1382.028 | 1382.028 | 1382.028 | 1078.1533 | 780 | 200 | 2058.1533 | 51.45% | 95% | 0% | -519.4508 | 862.5772 | -3550 | -400 | -3087.4228 | 77.19% | 52.73% | 95% | 0% | 2236 | -454
[5 empty] | 2019-08-21 | 21 | 5577.5 | 1663 | -518 | 1 | 0 | 2181 | 1295.878 | 1295.878 | 1295.878 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -592.6773 | 703.2006 | -3550 | -400 | -3246.7994 | 81.17% | 52.72% | 95% | 0% | 2181 | -518
[5 empty] | 2019-08-21 | 22 | 5578 | 1558 | -577 | 1 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -660.1831 | 563.6422 | -3550 | -400 | -3386.3578 | 84.66% | 52.72% | 95% | 0% | 2135 | -577
[5 empty] | 2019-08-21 | 23 | 5578.5 | 1479 | -621 | 1 | 0 | 2100 | 1169.0025 | 1169.0025 | 1169.0025 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -710.5263 | 458.4762 | -3550 | -400 | -3491.5238 | 87.29% | 52.71% | 95% | 0% | 2100 | -621
[5 empty] | 2019-08-21 | 24 | 5579 | 1435 | -642 | 1 | 0 | 2077 | 1132.9761 | 1132.9761 | 1132.9761 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -734.5538 | 398.4223 | -3550 | -400 | -3551.5777 | 88.79% | 52.7% | 95% | 0% | 2077 | -642
[5 empty] | 2019-08-21 | 25 | 5579.5 | 1429 | -654 | 1 | 0 | 2083 | 1142.3743 | 1142.3743 | 1142.3743 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -748.2838 | 394.0905 | -3550 | -400 | -3555.9095 | 88.9% | 52.69% | 95% | 0% | 2083 | -654
[5 empty] | 2019-08-21 | 26 | 5580 | 1402 | -667 | 1 | 0 | 2069 | 1120.4452 | 1120.4452 | 1120.4452 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -763.1579 | 357.2873 | -3550 | -400 | -3592.7127 | 89.82% | 52.69% | 95% | 0% | 2069 | -667
[5 empty] | 2019-08-21 | 27 | 5580.5 | 1392 | -668 | 1 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -764.3021 | 342.0458 | -3550 | -400 | -3607.9542 | 90.2% | 52.68% | 95% | 0% | 2060 | -668
[5 empty] | 2019-08-21 | 28 | 5581 | 1392 | -653 | 1 | 0 | 2045 | 1082.8524 | 1082.8524 | 1082.8524 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -747.1396 | 335.7128 | -3550 | -400 | -3614.2872 | 90.36% | 52.68% | 95% | 0% | 2045 | -653
[5 empty] | 2019-08-21 | 29 | 5581.5 | 1427 | -608 | 1 | 0 | 2035 | 1067.1888 | 1067.1888 | 1067.1888 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -695.6522 | 371.5366 | -3550 | -400 | -3578.4634 | 89.46% | 52.68% | 95% | 0% | 2035 | -608
[5 empty] | 2019-08-21 | 30 | 5582 | 1489 | -559 | 1 | 0 | 2048 | 1087.5515 | 1087.5515 | 1087.5515 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -639.5881 | 447.9634 | -3550 | -400 | -3502.0366 | 87.55% | 52.68% | 95% | 0% | 2048 | -559
[5 empty] | 2019-08-21 | 31 | 5582.5 | 1525 | -539 | 1 | 0 | 2064 | 1112.6134 | 1112.6134 | 1112.6134 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -616.7048 | 495.9085 | -3550 | -400 | -3454.0915 | 86.35% | 52.68% | 95% | 0% | 2064 | -539
[5 empty] | 2019-08-21 | 32 | 5583 | 1597 | -502 | 1 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -574.3707 | 593.0654 | -3550 | -400 | -3356.9346 | 83.92% | 52.68% | 95% | 0% | 2099 | -502
[5 empty] | 2019-08-21 | 33 | 5583.5 | 1694 | -450 | 1 | 0 | 2144 | 1237.9225 | 1237.9225 | 1237.9225 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -514.8741 | 723.0484 | -3550 | -400 | -3226.9516 | 80.67% | 52.67% | 95% | 0% | 2144 | -450
[5 empty] | 2019-08-21 | 34 | 5584 | 1834 | -394 | 1 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -450.8009 | 918.6962 | -3550 | -400 | -3031.3038 | 75.78% | 52.66% | 95% | 0% | 2228 | -394
[5 empty] | 2019-08-21 | 35 | 5584.5 | 1937 | -352 | 1 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -402.746 | 1062.2993 | -3550 | -400 | -2887.7007 | 72.19% | 52.65% | 95% | 0% | 2289 | -352
[5 empty] | 2019-08-21 | 36 | 5585 | 2021 | -305 | 1 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 1076.587 | 780 | 200 | 2056.587 | 51.41% | 95% | 0% | -348.9703 | 1174.0306 | -3550 | -400 | -2775.9694 | 69.4% | 52.65% | 95% | 0% | 2326 | -305
[5 empty] | 2019-08-21 | 37 | 5585.5 | 2108 | -249 | 1 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -284.897 | 1286.6611 | -3550 | -400 | -2663.3389 | 66.58% | 52.64% | 95% | 0% | 2357 | -249
[5 empty] | 2019-08-21 | 38 | 5586 | 2148 | -209 | 1 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -239.1304 | 1332.4277 | -3550 | -400 | -2617.5723 | 65.44% | 52.64% | 95% | 0% | 2357 | -209
[5 empty] | 2019-08-21 | 39 | 5586.5 | 2163 | -180 | 1 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -205.9497 | 1343.6794 | -3550 | -400 | -2606.3206 | 65.16% | 52.64% | 95% | 0% | 2343 | -180
[5 empty] | 2019-08-21 | 40 | 5587 | 2185 | -155 | 1 | 0 | 2340 | 1544.9299 | 1544.9299 | 1544.9299 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -177.3455 | 1367.5844 | -3550 | -400 | -2582.4156 | 64.56% | 52.64% | 95% | 0% | 2340 | -155
[5 empty] | 2019-08-21 | 41 | 5587.5 | 2203 | -145 | 1 | 0 | 2348 | 1557.4608 | 1557.4608 | 1557.4608 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -165.9039 | 1391.557 | -3550 | -400 | -2558.443 | 63.96% | 52.64% | 95% | 0% | 2348 | -145
[5 empty] | 2019-08-21 | 42 | 5588 | 2219 | -140 | 0 | 0 | 2359 | 1574.6908 | 1574.6908 | 1574.6908 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -160.1831 | 1414.5078 | -2750 | -200 | -1535.4922 | 38.39% | 52.63% | 95% | 0% | 2359 | -140
[5 empty] | 2019-08-21 | 43 | 5588.5 | 2178 | -136 | 0 | 0 | 2314 | 1504.2045 | 1504.2045 | 1504.2045 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -155.6064 | 1348.598 | -2750 | -200 | -1601.402 | 40.04% | 52.63% | 95% | 0% | 2314 | -136
[5 empty] | 2019-08-21 | 44 | 5589 | 2046 | -132 | 0 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -151.0297 | 1140.1491 | -2750 | -200 | -1809.8509 | 45.25% | 52.63% | 95% | 0% | 2178 | -132
[5 empty] | 2019-08-21 | 45 | 5589.5 | 1916 | -129 | 0 | 0 | 2045 | 1082.8524 | 1082.8524 | 1082.8524 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -147.5973 | 935.2552 | -2750 | -200 | -2014.7448 | 50.37% | 52.62% | 95% | 0% | 2045 | -129
[5 empty] | 2019-08-21 | 46 | 5590 | 1779 | -126 | 0 | 0 | 1905 | 863.5614 | 863.5614 | 863.5614 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -144.1648 | 719.3967 | -2750 | -200 | -2230.6033 | 55.77% | 52.61% | 95% | 0% | 1905 | -126
[5 empty] | 2019-08-21 | 47 | 5590.5 | 1649 | -125 | 0 | 0 | 1774 | 658.3677 | 658.3677 | 658.3677 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -143.0206 | 515.3471 | -2750 | -200 | -2434.6529 | 60.87% | 52.61% | 95% | 0% | 1774 | -125
[5 empty] | 2019-08-21 | 48 | 5591 | 1556 | -123 | 0 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -140.7323 | 368.8308 | -2750 | -200 | -2581.1692 | 64.53% | 52.6% | 95% | 0% | 1679 | -123
[5 empty] | 2019-08-22 | 1 | 5591.5 | 1464 | -121 | 0 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 1075.0206 | 780 | 200 | 2055.0206 | 51.38% | 95% | 0% | -138.4439 | 223.8809 | -2750 | -200 | -2726.1191 | 68.15% | 52.6% | 95% | 0% | 1585 | -121
[5 empty] | 2019-08-22 | 2 | 5592 | 1420 | -119 | 1 | 0 | 1539 | 290.2721 | 290.2721 | 290.2721 | 1073.4542 | 780 | 200 | 2053.4542 | 51.34% | 95% | 0% | -136.1556 | 154.1164 | -3550 | -400 | -3795.8836 | 94.9% | 52.59% | 95% | 0% | 1539 | -119
[5 empty] | 2019-08-22 | 3 | 5592.5 | 1380 | -118 | 1 | 0 | 1498 | 226.0511 | 226.0511 | 226.0511 | 1073.4542 | 780 | 200 | 2053.4542 | 51.34% | 95% | 0% | -135.0114 | 91.0397 | -3550 | -400 | -3858.9603 | 96.47% | 52.59% | 95% | 0% | 1498 | -118
[5 empty] | 2019-08-22 | 4 | 5593 | 1372 | -117 | 1 | 0 | 1489 | 211.9538 | 211.9538 | 211.9538 | 1073.4542 | 780 | 200 | 2053.4542 | 51.34% | 95% | 0% | -133.8673 | 78.0866 | -3550 | -400 | -3871.9134 | 96.8% | 52.59% | 95% | 0% | 1489 | -117
[5 empty] | 2019-08-22 | 5 | 5593.5 | 1341 | -117 | 1 | 0 | 1458 | 163.3965 | 163.3965 | 163.3965 | 1073.4542 | 780 | 200 | 2053.4542 | 51.34% | 95% | 0% | -133.8673 | 29.5293 | -3550 | -400 | -3920.4707 | 98.01% | 52.59% | 95% | 0% | 1458 | -117
[5 empty] | 2019-08-22 | 6 | 5594 | 1312 | -117 | 1 | 0 | 1429 | 117.972 | 117.972 | 117.972 | 1073.4542 | 780 | 200 | 2053.4542 | 51.34% | 95% | 0% | -133.8673 | -15.8953 | -3550 | -400 | -3965.8953 | 99.15% | 52.59% | 95% | 0% | 1429 | -117
[5 empty] | 2019-08-22 | 7 | 5594.5 | 1296 | -118 | 1 | 0 | 1414 | 94.4765 | 94.4765 | 94.4765 | 1073.4542 | 780 | 200 | 2053.4542 | 51.34% | 95% | 0% | -135.0114 | -40.5349 | -3550 | -400 | -3990.5349 | 99.76% | 52.57% | 95% | 0% | 1414 | -118
[5 empty] | 2019-08-22 | 8 | 5595 | 1283 | -119 | 1 | 0 | 1402 | 75.6801 | 75.6801 | 75.6801 | 1073.4542 | 780 | 200 | 2053.4542 | 51.34% | 95% | 0% | -136.1556 | -60.4755 | -3550 | -400 | -4010.4755 | 100.3% | 52.57% | 95% | 0% | 1402 | -119
[5 empty] | 2019-08-22 | 9 | 5595.5 | 1294 | -118 | 1 | 0 | 1412 | 91.3438 | 91.3438 | 91.3438 | 1073.4542 | 780 | 200 | 2053.4542 | 51.34% | 95% | 0% | -135.0114 | -43.6677 | -3550 | -400 | -3993.6677 | 99.84% | 52.57% | 95% | 0% | 1412 | -118
[5 empty] | 2019-08-22 | 10 | 5596 | 1317 | -117 | 1 | 0 | 1434 | 125.8038 | 125.8038 | 125.8038 | 1073.4542 | 780 | 200 | 2053.4542 | 51.34% | 95% | 0% | -133.8673 | -8.0635 | -3550 | -400 | -3958.0635 | 98.95% | 52.57% | 95% | 0% | 1434 | -117
[5 empty] | 2019-08-22 | 11 | 5596.5 | 1377 | -117 | 1 | 0 | 1494 | 219.7857 | 219.7857 | 219.7857 | 1073.4542 | 780 | 200 | 2053.4542 | 51.34% | 95% | 0% | -133.8673 | 85.9184 | -3550 | -400 | -3864.0816 | 96.6% | 52.57% | 95% | 0% | 1494 | -117
[5 empty] | 2019-08-22 | 12 | 5597 | 1443 | -116 | 1 | 0 | 1559 | 321.5993 | 321.5993 | 321.5993 | 1073.4542 | 780 | 200 | 2053.4542 | 51.34% | 95% | 0% | -132.7231 | 188.8762 | -3550 | -400 | -3761.1238 | 94.03% | 52.57% | 95% | 0% | 1559 | -116
[5 empty] | 2019-08-22 | 13 | 5597.5 | 1596 | -121 | 1 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -138.4439 | 430.641 | -3550 | -400 | -3519.359 | 87.98% | 52.56% | 95% | 0% | 1717 | -121
[5 empty] | 2019-08-22 | 14 | 5598 | 1705 | -141 | 1 | 0 | 1846 | 771.1459 | 771.1459 | 771.1459 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -161.3272 | 609.8187 | -3550 | -400 | -3340.1813 | 83.5% | 52.56% | 95% | 0% | 1846 | -141
[5 empty] | 2019-08-22 | 15 | 5598.5 | 1839 | -185 | 1 | 0 | 2024 | 1049.9588 | 1049.9588 | 1049.9588 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -211.6705 | 838.2883 | -3550 | -400 | -3111.7117 | 77.79% | 52.56% | 95% | 0% | 2024 | -185
[5 empty] | 2019-08-22 | 16 | 5599 | 1877 | -229 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -262.0137 | 916.3869 | -3550 | -400 | -3033.6131 | 75.84% | 52.56% | 95% | 0% | 2106 | -229
[5 empty] | 2019-08-22 | 17 | 5599.5 | 1884 | -280 | 1 | 0 | 2164 | 1269.2498 | 1269.2498 | 1269.2498 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -320.3661 | 948.8837 | -3550 | -400 | -3001.1163 | 75.03% | 52.56% | 95% | 0% | 2164 | -280
[5 empty] | 2019-08-22 | 18 | 5600 | 1822 | -340 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -389.016 | 877.101 | -3550 | -400 | -3072.899 | 76.82% | 52.56% | 95% | 0% | 2162 | -340
[5 empty] | 2019-08-22 | 19 | 5600.5 | 1757 | -399 | 1 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -456.5217 | 800.1971 | -3550 | -400 | -3149.8029 | 78.75% | 52.55% | 95% | 0% | 2156 | -399
[5 empty] | 2019-08-22 | 20 | 5601 | 1664 | -453 | 1 | 0 | 2117 | 1195.6307 | 1195.6307 | 1195.6307 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -518.3066 | 677.324 | -3550 | -400 | -3272.676 | 81.82% | 52.55% | 95% | 0% | 2117 | -453
[5 empty] | 2019-08-22 | 21 | 5601.5 | 1590 | -495 | 1 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -566.3616 | 579.1455 | -3550 | -400 | -3370.8545 | 84.27% | 52.55% | 95% | 0% | 2085 | -495
[5 empty] | 2019-08-22 | 22 | 5602 | 1582 | -519 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -593.8215 | 576.7473 | -3550 | -400 | -3373.2527 | 84.33% | 52.55% | 95% | 0% | 2101 | -519
[5 empty] | 2019-08-22 | 23 | 5602.5 | 1584 | -530 | 1 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -606.4073 | 584.5243 | -3550 | -400 | -3365.4757 | 84.14% | 52.54% | 95% | 0% | 2114 | -530
[5 empty] | 2019-08-22 | 24 | 5603 | 1583 | -537 | 1 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -614.4165 | 585.9133 | -3550 | -400 | -3364.0867 | 84.1% | 52.54% | 95% | 0% | 2120 | -537
[5 empty] | 2019-08-22 | 25 | 5603.5 | 1615 | -523 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -598.3982 | 630.1262 | -3550 | -400 | -3319.8738 | 83% | 52.54% | 95% | 0% | 2138 | -523
[5 empty] | 2019-08-22 | 26 | 5604 | 1558 | -565 | 1 | 0 | 2123 | 1205.0289 | 1205.0289 | 1205.0289 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -646.4531 | 558.5758 | -3550 | -400 | -3391.4242 | 84.79% | 52.53% | 95% | 0% | 2123 | -565
[5 empty] | 2019-08-22 | 27 | 5604.5 | 1515 | -589 | 1 | 0 | 2104 | 1175.2679 | 1175.2679 | 1175.2679 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -673.913 | 501.3549 | -3550 | -400 | -3448.6451 | 86.22% | 52.53% | 95% | 0% | 2104 | -589
[5 empty] | 2019-08-22 | 28 | 5605 | 1510 | -575 | 1 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 1071.8879 | 780 | 200 | 2051.8879 | 51.3% | 95% | 0% | -657.8947 | 487.6123 | -3550 | -400 | -3462.3877 | 86.56% | 52.53% | 95% | 0% | 2085 | -575
[5 empty] | 2019-08-22 | 29 | 5605.5 | 1523 | -552 | 1 | 0 | 2075 | 1129.8434 | 1129.8434 | 1129.8434 | 1070.3215 | 780 | 200 | 2050.3215 | 51.26% | 95% | 0% | -631.5789 | 498.2644 | -3550 | -400 | -3451.7356 | 86.29% | 52.52% | 95% | 0% | 2075 | -552
[5 empty] | 2019-08-22 | 30 | 5606 | 1531 | -534 | 1 | 0 | 2065 | 1114.1797 | 1114.1797 | 1114.1797 | 1070.3215 | 780 | 200 | 2050.3215 | 51.26% | 95% | 0% | -610.984 | 503.1957 | -3550 | -400 | -3446.8043 | 86.17% | 52.52% | 95% | 0% | 2065 | -534
[5 empty] | 2019-08-22 | 31 | 5606.5 | 1570 | -487 | 1 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 1070.3215 | 780 | 200 | 2050.3215 | 51.26% | 95% | 0% | -557.2082 | 544.4406 | -3550 | -400 | -3405.5594 | 85.14% | 52.51% | 95% | 0% | 2057 | -487
[5 empty] | 2019-08-22 | 32 | 5607 | 1599 | -486 | 1 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 1070.3215 | 780 | 200 | 2050.3215 | 51.26% | 95% | 0% | -556.0641 | 589.4429 | -3550 | -400 | -3360.5571 | 84.01% | 52.51% | 95% | 0% | 2085 | -486
[5 empty] | 2019-08-22 | 33 | 5607.5 | 1714 | -439 | 1 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 1070.3215 | 780 | 200 | 2050.3215 | 51.26% | 95% | 0% | -502.2883 | 749.7315 | -3550 | -400 | -3200.2685 | 80.01% | 52.51% | 95% | 0% | 2153 | -439
[5 empty] | 2019-08-22 | 34 | 5608 | 1825 | -402 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1070.3215 | 780 | 200 | 2050.3215 | 51.26% | 95% | 0% | -459.9542 | 907.9765 | -3550 | -400 | -3042.0235 | 76.05% | 52.51% | 95% | 0% | 2227 | -402
[5 empty] | 2019-08-22 | 35 | 5608.5 | 1925 | -360 | 1 | 0 | 2285 | 1458.7799 | 1458.7799 | 1458.7799 | 1070.3215 | 780 | 200 | 2050.3215 | 51.26% | 95% | 0% | -411.8993 | 1046.8806 | -3550 | -400 | -2903.1194 | 72.58% | 52.51% | 95% | 0% | 2285 | -360
[5 empty] | 2019-08-22 | 36 | 5609 | 2041 | -298 | 1 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 1070.3215 | 780 | 200 | 2050.3215 | 51.26% | 95% | 0% | -340.9611 | 1202.4025 | -3550 | -400 | -2747.5975 | 68.69% | 52.49% | 95% | 0% | 2339 | -298
[5 empty] | 2019-08-22 | 37 | 5609.5 | 2119 | -249 | 1 | 0 | 2368 | 1588.7881 | 1588.7881 | 1588.7881 | 1070.3215 | 780 | 200 | 2050.3215 | 51.26% | 95% | 0% | -284.897 | 1303.8911 | -3550 | -400 | -2646.1089 | 66.15% | 52.49% | 95% | 0% | 2368 | -249
[5 empty] | 2019-08-22 | 38 | 5610 | 2152 | -210 | 1 | 0 | 2362 | 1579.3899 | 1579.3899 | 1579.3899 | 1070.3215 | 780 | 200 | 2050.3215 | 51.26% | 95% | 0% | -240.2746 | 1339.1153 | -3550 | -400 | -2610.8847 | 65.27% | 52.48% | 95% | 0% | 2362 | -210
[5 empty] | 2019-08-22 | 39 | 5610.5 | 2186 | -179 | 1 | 0 | 2365 | 1584.089 | 1584.089 | 1584.089 | 1070.3215 | 780 | 200 | 2050.3215 | 51.26% | 95% | 0% | -204.8055 | 1379.2835 | -3550 | -400 | -2570.7165 | 64.27% | 52.47% | 95% | 0% | 2365 | -179
[5 empty] | 2019-08-22 | 40 | 5611 | 2206 | -158 | 1 | 0 | 2364 | 1582.5227 | 1582.5227 | 1582.5227 | 1070.3215 | 780 | 200 | 2050.3215 | 51.26% | 95% | 0% | -180.778 | 1401.7446 | -3550 | -400 | -2548.2554 | 63.71% | 52.47% | 95% | 0% | 2364 | -158
[5 empty] | 2019-08-22 | 41 | 5611.5 | 2218 | -148 | 1 | 0 | 2366 | 1585.6554 | 1585.6554 | 1585.6554 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -169.3364 | 1416.319 | -3550 | -400 | -2533.681 | 63.34% | 52.46% | 95% | 0% | 2366 | -148
[5 empty] | 2019-08-22 | 42 | 5612 | 2251 | -143 | 1 | 0 | 2394 | 1629.5136 | 1629.5136 | 1629.5136 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -163.6156 | 1465.898 | -3550 | -400 | -2484.102 | 62.1% | 52.46% | 95% | 0% | 2394 | -143
[5 empty] | 2019-08-22 | 43 | 5612.5 | 2185 | -138 | 0 | 0 | 2323 | 1518.3017 | 1518.3017 | 1518.3017 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -157.8947 | 1360.407 | -2750 | -200 | -1589.593 | 39.74% | 52.45% | 95% | 0% | 2323 | -138
[5 empty] | 2019-08-22 | 44 | 5613 | 2082 | -133 | 0 | 0 | 2215 | 1349.1344 | 1349.1344 | 1349.1344 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -152.1739 | 1196.9605 | -2750 | -200 | -1753.0395 | 43.83% | 52.43% | 95% | 0% | 2215 | -133
[5 empty] | 2019-08-22 | 45 | 5613.5 | 1959 | -130 | 0 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -148.7414 | 1003.031 | -2750 | -200 | -1946.969 | 48.67% | 52.43% | 95% | 0% | 2089 | -130
[5 empty] | 2019-08-22 | 46 | 5614 | 1841 | -127 | 0 | 0 | 1968 | 962.2424 | 962.2424 | 962.2424 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -145.3089 | 816.9334 | -2750 | -200 | -2133.0666 | 53.33% | 52.43% | 95% | 0% | 1968 | -127
[5 empty] | 2019-08-22 | 47 | 5614.5 | 1717 | -124 | 0 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -141.8764 | 621.4377 | -2750 | -200 | -2328.5623 | 58.21% | 52.42% | 95% | 0% | 1841 | -124
[5 empty] | 2019-08-22 | 48 | 5615 | 1619 | -121 | 0 | 0 | 1740 | 605.1113 | 605.1113 | 605.1113 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -138.4439 | 466.6674 | -2750 | -200 | -2483.3326 | 62.08% | 52.42% | 95% | 0% | 1740 | -121
[5 empty] | 2019-08-23 | 1 | 5615.5 | 1536 | -118 | 0 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -135.0114 | 335.3925 | -2750 | -200 | -2614.6075 | 65.37% | 52.42% | 95% | 0% | 1654 | -118
[5 empty] | 2019-08-23 | 2 | 5616 | 1480 | -114 | 0 | 0 | 1594 | 376.4221 | 376.4221 | 376.4221 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -130.4348 | 245.9873 | -2750 | -200 | -2704.0127 | 67.6% | 52.41% | 95% | 0% | 1594 | -114
[5 empty] | 2019-08-23 | 3 | 5616.5 | 1439 | -114 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -130.4348 | 181.7664 | -2750 | -200 | -2768.2336 | 69.21% | 52.4% | 95% | 0% | 1553 | -114
[5 empty] | 2019-08-23 | 4 | 5617 | 1406 | -114 | 0 | 0 | 1520 | 260.5111 | 260.5111 | 260.5111 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -130.4348 | 130.0763 | -2750 | -200 | -2819.9237 | 70.5% | 52.4% | 95% | 0% | 1520 | -114
[5 empty] | 2019-08-23 | 5 | 5617.5 | 1391 | -112 | 0 | 0 | 1503 | 233.8829 | 233.8829 | 233.8829 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -128.1465 | 105.7365 | -2750 | -200 | -2844.2635 | 71.11% | 52.4% | 95% | 0% | 1503 | -112
[5 empty] | 2019-08-23 | 6 | 5618 | 1368 | -110 | 0 | 0 | 1478 | 194.7238 | 194.7238 | 194.7238 | 1068.7552 | 780 | 200 | 2048.7552 | 51.22% | 95% | 0% | -125.8581 | 68.8657 | -2750 | -200 | -2881.1343 | 72.03% | 52.4% | 95% | 0% | 1478 | -110
[5 empty] | 2019-08-23 | 7 | 5618.5 | 1360 | -109 | 0 | 0 | 1469 | 180.6265 | 180.6265 | 180.6265 | 1067.1888 | 780 | 200 | 2047.1888 | 51.18% | 95% | 0% | -124.714 | 55.9126 | -2750 | -200 | -2894.0874 | 72.35% | 52.4% | 95% | 0% | 1469 | -109
[5 empty] | 2019-08-23 | 8 | 5619 | 1358 | -107 | 0 | 0 | 1465 | 174.3611 | 174.3611 | 174.3611 | 1067.1888 | 780 | 200 | 2047.1888 | 51.18% | 95% | 0% | -122.4256 | 51.9355 | -2750 | -200 | -2898.0645 | 72.45% | 52.4% | 95% | 0% | 1465 | -107
[5 empty] | 2019-08-23 | 9 | 5619.5 | 1371 | -104 | 0 | 0 | 1475 | 190.0247 | 190.0247 | 190.0247 | 1067.1888 | 780 | 200 | 2047.1888 | 51.18% | 95% | 0% | -118.9931 | 71.0316 | -2750 | -200 | -2878.9684 | 71.97% | 52.4% | 95% | 0% | 1475 | -104
[5 empty] | 2019-08-23 | 10 | 5620 | 1377 | -102 | 0 | 0 | 1479 | 196.2902 | 196.2902 | 196.2902 | 1067.1888 | 780 | 200 | 2047.1888 | 51.18% | 95% | 0% | -116.7048 | 79.5854 | -2750 | -200 | -2870.4146 | 71.76% | 52.39% | 95% | 0% | 1479 | -102
[5 empty] | 2019-08-23 | 11 | 5620.5 | 1445 | -100 | 0 | 0 | 1545 | 299.6702 | 299.6702 | 299.6702 | 1067.1888 | 780 | 200 | 2047.1888 | 51.18% | 95% | 0% | -114.4165 | 185.2538 | -2750 | -200 | -2764.7462 | 69.12% | 52.39% | 95% | 0% | 1545 | -100
[5 empty] | 2019-08-23 | 12 | 5621 | 1507 | -98 | 0 | 0 | 1605 | 393.6521 | 393.6521 | 393.6521 | 1067.1888 | 780 | 200 | 2047.1888 | 51.18% | 95% | 0% | -112.1281 | 281.524 | -2750 | -200 | -2668.476 | 66.71% | 52.39% | 95% | 0% | 1605 | -98
[5 empty] | 2019-08-23 | 13 | 5621.5 | 1658 | -100 | 0 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 1067.1888 | 780 | 200 | 2047.1888 | 51.18% | 95% | 0% | -114.4165 | 518.8894 | -2750 | -200 | -2431.1106 | 60.78% | 52.39% | 95% | 0% | 1758 | -100
[5 empty] | 2019-08-23 | 14 | 5622 | 1768 | -122 | 0 | 0 | 1890 | 840.066 | 840.066 | 840.066 | 1067.1888 | 780 | 200 | 2047.1888 | 51.18% | 95% | 0% | -139.5881 | 700.4779 | -2750 | -200 | -2249.5221 | 56.24% | 52.39% | 95% | 0% | 1890 | -122
[5 empty] | 2019-08-23 | 15 | 5622.5 | 1905 | -164 | 1 | 0 | 2069 | 1120.4452 | 1120.4452 | 1120.4452 | 1067.1888 | 780 | 200 | 2047.1888 | 51.18% | 95% | 0% | -187.643 | 932.8022 | -3550 | -400 | -3017.1978 | 75.43% | 52.39% | 95% | 0% | 2069 | -164
[5 empty] | 2019-08-23 | 16 | 5623 | 1965 | -211 | 1 | 0 | 2176 | 1288.0462 | 1288.0462 | 1288.0462 | 1065.6224 | 780 | 200 | 2045.6224 | 51.14% | 95% | 0% | -241.4188 | 1046.6274 | -3550 | -400 | -2903.3726 | 72.58% | 52.38% | 95% | 0% | 2176 | -211
[5 empty] | 2019-08-23 | 17 | 5623.5 | 1994 | -266 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 1065.6224 | 780 | 200 | 2045.6224 | 51.14% | 95% | 0% | -304.3478 | 1115.2729 | -3550 | -400 | -2834.7271 | 70.87% | 52.38% | 95% | 0% | 2260 | -266
[5 empty] | 2019-08-23 | 18 | 5624 | 1946 | -332 | 1 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 1065.6224 | 780 | 200 | 2045.6224 | 51.14% | 95% | 0% | -379.8627 | 1067.9526 | -3550 | -400 | -2882.0474 | 72.05% | 52.38% | 95% | 0% | 2278 | -332
[5 empty] | 2019-08-23 | 19 | 5624.5 | 1875 | -398 | 1 | 0 | 2273 | 1439.9835 | 1439.9835 | 1439.9835 | 1065.6224 | 780 | 200 | 2045.6224 | 51.14% | 95% | 0% | -455.3776 | 984.6059 | -3550 | -400 | -2965.3941 | 74.13% | 52.37% | 95% | 0% | 2273 | -398
[5 empty] | 2019-08-23 | 20 | 5625 | 1780 | -465 | 1 | 0 | 2245 | 1396.1253 | 1396.1253 | 1396.1253 | 1065.6224 | 780 | 200 | 2045.6224 | 51.14% | 95% | 0% | -532.0366 | 864.0887 | -3550 | -400 | -3085.9113 | 77.15% | 52.37% | 95% | 0% | 2245 | -465
[5 empty] | 2019-08-23 | 21 | 5625.5 | 1691 | -513 | 1 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 1065.6224 | 780 | 200 | 2045.6224 | 51.14% | 95% | 0% | -586.9565 | 744.9478 | -3550 | -400 | -3205.0522 | 80.13% | 52.36% | 95% | 0% | 2204 | -513
[5 empty] | 2019-08-23 | 22 | 5626 | 1593 | -568 | 1 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 1065.6224 | 780 | 200 | 2045.6224 | 51.14% | 95% | 0% | -649.8856 | 614.6651 | -3550 | -400 | -3335.3349 | 83.38% | 52.36% | 95% | 0% | 2161 | -568
[5 empty] | 2019-08-23 | 23 | 5626.5 | 1508 | -611 | 1 | 0 | 2119 | 1198.7634 | 1198.7634 | 1198.7634 | 1065.6224 | 780 | 200 | 2045.6224 | 51.14% | 95% | 0% | -699.0847 | 499.6787 | -3550 | -400 | -3450.3213 | 86.26% | 52.35% | 95% | 0% | 2119 | -611
[5 empty] | 2019-08-23 | 24 | 5627 | 1447 | -655 | 1 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 1065.6224 | 780 | 200 | 2045.6224 | 51.14% | 95% | 0% | -749.4279 | 422.7073 | -3550 | -400 | -3527.2927 | 88.18% | 52.35% | 95% | 0% | 2102 | -655
[5 empty] | 2019-08-23 | 25 | 5627.5 | 1374 | -692 | 1 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 1065.6224 | 780 | 200 | 2045.6224 | 51.14% | 95% | 0% | -791.762 | 323.9841 | -3550 | -400 | -3626.0159 | 90.65% | 52.35% | 95% | 0% | 2066 | -692
[5 empty] | 2019-08-23 | 26 | 5628 | 1319 | -709 | 1 | 0 | 2028 | 1056.2242 | 1056.2242 | 1056.2242 | 1065.6224 | 780 | 200 | 2045.6224 | 51.14% | 95% | 0% | -811.2128 | 245.0114 | -3550 | -400 | -3704.9886 | 92.62% | 52.34% | 95% | 0% | 2028 | -709
[5 empty] | 2019-08-23 | 27 | 5628.5 | 1268 | -723 | 1 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1065.6224 | 780 | 200 | 2045.6224 | 51.14% | 95% | 0% | -827.2311 | 171.0376 | -3550 | -400 | -3778.9624 | 94.47% | 52.34% | 95% | 0% | 1991 | -723
[5 empty] | 2019-08-23 | 28 | 5629 | 1231 | -728 | 1 | 0 | 1959 | 948.1451 | 948.1451 | 948.1451 | 1064.0561 | 780 | 200 | 2044.0561 | 51.1% | 95% | 0% | -832.9519 | 115.1931 | -3550 | -400 | -3834.8069 | 95.87% | 52.34% | 95% | 0% | 1959 | -728
[5 empty] | 2019-08-23 | 29 | 5629.5 | 1237 | -718 | 1 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 1064.0561 | 780 | 200 | 2044.0561 | 51.1% | 95% | 0% | -821.5103 | 120.3693 | -3550 | -400 | -3829.6307 | 95.74% | 52.34% | 95% | 0% | 1955 | -718
[5 empty] | 2019-08-23 | 30 | 5630 | 1264 | -690 | 1 | 0 | 1954 | 940.3133 | 940.3133 | 940.3133 | 1064.0561 | 780 | 200 | 2044.0561 | 51.1% | 95% | 0% | -789.4737 | 150.8396 | -3550 | -400 | -3799.1604 | 94.98% | 52.34% | 95% | 0% | 1954 | -690
[5 empty] | 2019-08-23 | 31 | 5630.5 | 1327 | -648 | 1 | 0 | 1975 | 973.2069 | 973.2069 | 973.2069 | 1064.0561 | 780 | 200 | 2044.0561 | 51.1% | 95% | 0% | -741.4188 | 231.7882 | -3550 | -400 | -3718.2118 | 92.96% | 52.34% | 95% | 0% | 1975 | -648
[5 empty] | 2019-08-23 | 32 | 5631 | 1407 | -601 | 1 | 0 | 2008 | 1024.8969 | 1024.8969 | 1024.8969 | 1064.0561 | 780 | 200 | 2044.0561 | 51.1% | 95% | 0% | -687.643 | 337.2539 | -3550 | -400 | -3612.7461 | 90.32% | 52.34% | 95% | 0% | 2008 | -601
[5 empty] | 2019-08-23 | 33 | 5631.5 | 1499 | -538 | 1 | 0 | 2037 | 1070.3215 | 1070.3215 | 1070.3215 | 1064.0561 | 780 | 200 | 2044.0561 | 51.1% | 95% | 0% | -615.5606 | 454.7609 | -3550 | -400 | -3495.2391 | 87.38% | 52.34% | 95% | 0% | 2037 | -538
[5 empty] | 2019-08-23 | 34 | 5632 | 1642 | -472 | 1 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 1064.0561 | 780 | 200 | 2044.0561 | 51.1% | 95% | 0% | -540.0458 | 650.8858 | -3550 | -400 | -3299.1142 | 82.48% | 52.33% | 95% | 0% | 2114 | -472
[5 empty] | 2019-08-23 | 35 | 5632.5 | 1788 | -394 | 1 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 1064.0561 | 780 | 200 | 2044.0561 | 51.1% | 95% | 0% | -450.8009 | 846.6434 | -3550 | -400 | -3103.3566 | 77.58% | 52.32% | 95% | 0% | 2182 | -394
[5 empty] | 2019-08-23 | 36 | 5633 | 1933 | -317 | 1 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 1064.0561 | 780 | 200 | 2044.0561 | 51.1% | 95% | 0% | -362.7002 | 1041.2569 | -3550 | -400 | -2908.7431 | 72.72% | 52.32% | 95% | 0% | 2250 | -317
[5 empty] | 2019-08-23 | 37 | 5633.5 | 2028 | -245 | 1 | 0 | 2273 | 1439.9835 | 1439.9835 | 1439.9835 | 1064.0561 | 780 | 200 | 2044.0561 | 51.1% | 95% | 0% | -280.3204 | 1159.6631 | -3550 | -400 | -2790.3369 | 69.76% | 52.32% | 95% | 0% | 2273 | -245
[5 empty] | 2019-08-23 | 38 | 5634 | 2112 | -175 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1064.0561 | 780 | 200 | 2044.0561 | 51.1% | 95% | 0% | -200.2288 | 1261.6838 | -3550 | -400 | -2688.3162 | 67.21% | 52.31% | 95% | 0% | 2287 | -175
[5 empty] | 2019-08-23 | 39 | 5634.5 | 2193 | -121 | 1 | 0 | 2314 | 1504.2045 | 1504.2045 | 1504.2045 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -138.4439 | 1365.7605 | -3550 | -400 | -2584.2395 | 64.61% | 52.31% | 95% | 0% | 2314 | -121
[5 empty] | 2019-08-23 | 40 | 5635 | 2208 | -85 | 1 | 0 | 2293 | 1471.3108 | 1471.3108 | 1471.3108 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -97.254 | 1374.0568 | -3550 | -400 | -2575.9432 | 64.4% | 52.31% | 95% | 0% | 2293 | -85
[5 empty] | 2019-08-23 | 41 | 5635.5 | 2213 | -77 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -88.1007 | 1378.511 | -3550 | -400 | -2571.489 | 64.29% | 52.31% | 95% | 0% | 2290 | -77
[5 empty] | 2019-08-23 | 42 | 5636 | 2227 | -78 | 1 | 0 | 2305 | 1490.1072 | 1490.1072 | 1490.1072 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -89.2449 | 1400.8623 | -3550 | -400 | -2549.1377 | 63.73% | 52.29% | 95% | 0% | 2305 | -78
[5 empty] | 2019-08-23 | 43 | 5636.5 | 2176 | -80 | 0 | 0 | 2256 | 1413.3553 | 1413.3553 | 1413.3553 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -91.5332 | 1321.8221 | -2750 | -200 | -1628.1779 | 40.7% | 52.29% | 95% | 0% | 2256 | -80
[5 empty] | 2019-08-23 | 44 | 5637 | 2094 | -81 | 0 | 0 | 2175 | 1286.4798 | 1286.4798 | 1286.4798 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -92.6773 | 1193.8025 | -2750 | -200 | -1756.1975 | 43.9% | 52.29% | 95% | 0% | 2175 | -81
[5 empty] | 2019-08-23 | 45 | 5637.5 | 2017 | -83 | 0 | 0 | 2100 | 1169.0025 | 1169.0025 | 1169.0025 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -94.9657 | 1074.0368 | -2750 | -200 | -1875.9632 | 46.9% | 52.29% | 95% | 0% | 2100 | -83
[5 empty] | 2019-08-23 | 46 | 5638 | 1906 | -84 | 0 | 0 | 1990 | 996.7024 | 996.7024 | 996.7024 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -96.1098 | 900.5926 | -2750 | -200 | -2049.4074 | 51.24% | 52.28% | 95% | 0% | 1990 | -84
[5 empty] | 2019-08-23 | 47 | 5638.5 | 1792 | -85 | 0 | 0 | 1877 | 819.7032 | 819.7032 | 819.7032 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -97.254 | 722.4492 | -2750 | -200 | -2227.5508 | 55.69% | 52.28% | 95% | 0% | 1877 | -85
[5 empty] | 2019-08-23 | 48 | 5639 | 1694 | -86 | 0 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -98.3982 | 569.3677 | -2750 | -200 | -2380.6323 | 59.52% | 52.28% | 95% | 0% | 1780 | -86
[5 empty] | 2019-08-24 | 1 | 5639.5 | 1612 | -85 | 0 | 0 | 1697 | 537.7576 | 537.7576 | 537.7576 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -97.254 | 440.5036 | -2750 | -200 | -2509.4964 | 62.74% | 52.26% | 95% | 0% | 1697 | -85
[5 empty] | 2019-08-24 | 2 | 5640 | 1543 | -84 | 0 | 0 | 1627 | 428.1121 | 428.1121 | 428.1121 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -96.1098 | 332.0023 | -2750 | -200 | -2617.9977 | 65.45% | 52.26% | 95% | 0% | 1627 | -84
[5 empty] | 2019-08-24 | 3 | 5640.5 | 1495 | -83 | 1 | 0 | 1578 | 351.3603 | 351.3603 | 351.3603 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -94.9657 | 256.3946 | -3550 | -400 | -3693.6054 | 92.34% | 52.25% | 95% | 0% | 1578 | -83
[5 empty] | 2019-08-24 | 4 | 5641 | 1480 | -82 | 1 | 0 | 1562 | 326.2984 | 326.2984 | 326.2984 | 1062.4897 | 780 | 200 | 2042.4897 | 51.06% | 95% | 0% | -93.8215 | 232.4769 | -3550 | -400 | -3717.5231 | 92.94% | 52.25% | 95% | 0% | 1562 | -82
[5 empty] | 2019-08-24 | 5 | 5641.5 | 1458 | -81 | 1 | 0 | 1539 | 290.2721 | 290.2721 | 290.2721 | 1060.9233 | 780 | 200 | 2040.9233 | 51.02% | 95% | 0% | -92.6773 | 197.5947 | -3550 | -400 | -3752.4053 | 93.81% | 52.25% | 95% | 0% | 1539 | -81
[5 empty] | 2019-08-24 | 6 | 5642 | 1422 | -81 | 1 | 0 | 1503 | 233.8829 | 233.8829 | 233.8829 | 1060.9233 | 780 | 200 | 2040.9233 | 51.02% | 95% | 0% | -92.6773 | 141.2056 | -3550 | -400 | -3808.7944 | 95.22% | 52.24% | 95% | 0% | 1503 | -81
[5 empty] | 2019-08-24 | 7 | 5642.5 | 1409 | -80 | 1 | 0 | 1489 | 211.9538 | 211.9538 | 211.9538 | 1060.9233 | 780 | 200 | 2040.9233 | 51.02% | 95% | 0% | -91.5332 | 120.4207 | -3550 | -400 | -3829.5793 | 95.74% | 52.23% | 95% | 0% | 1489 | -80
[5 empty] | 2019-08-24 | 8 | 5643 | 1408 | -79 | 1 | 0 | 1487 | 208.8211 | 208.8211 | 208.8211 | 1060.9233 | 780 | 200 | 2040.9233 | 51.02% | 95% | 0% | -90.389 | 118.4321 | -3550 | -400 | -3831.5679 | 95.79% | 52.23% | 95% | 0% | 1487 | -79
[5 empty] | 2019-08-24 | 9 | 5643.5 | 1405 | -78 | 1 | 0 | 1483 | 202.5556 | 202.5556 | 202.5556 | 1060.9233 | 780 | 200 | 2040.9233 | 51.02% | 95% | 0% | -89.2449 | 113.3108 | -3550 | -400 | -3836.6892 | 95.92% | 52.23% | 95% | 0% | 1483 | -78
[5 empty] | 2019-08-24 | 10 | 5644 | 1407 | -78 | 1 | 0 | 1485 | 205.6884 | 205.6884 | 205.6884 | 1060.9233 | 780 | 200 | 2040.9233 | 51.02% | 95% | 0% | -89.2449 | 116.4435 | -3550 | -400 | -3833.5565 | 95.84% | 52.23% | 95% | 0% | 1485 | -78
[5 empty] | 2019-08-24 | 11 | 5644.5 | 1421 | -78 | 1 | 0 | 1499 | 227.6175 | 227.6175 | 227.6175 | 1060.9233 | 780 | 200 | 2040.9233 | 51.02% | 95% | 0% | -89.2449 | 138.3726 | -3550 | -400 | -3811.6274 | 95.29% | 52.23% | 95% | 0% | 1499 | -78
[5 empty] | 2019-08-24 | 12 | 5645 | 1438 | -78 | 1 | 0 | 1516 | 254.2457 | 254.2457 | 254.2457 | 1060.9233 | 780 | 200 | 2040.9233 | 51.02% | 95% | 0% | -89.2449 | 165.0008 | -3550 | -400 | -3784.9992 | 94.62% | 52.22% | 95% | 0% | 1516 | -78
[5 empty] | 2019-08-24 | 13 | 5645.5 | 1491 | -82 | 1 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 1060.9233 | 780 | 200 | 2040.9233 | 51.02% | 95% | 0% | -93.8215 | 249.7069 | -3550 | -400 | -3700.2931 | 92.51% | 52.22% | 95% | 0% | 1573 | -82
[5 empty] | 2019-08-24 | 14 | 5646 | 1506 | -111 | 1 | 0 | 1617 | 412.4485 | 412.4485 | 412.4485 | 1060.9233 | 780 | 200 | 2040.9233 | 51.02% | 95% | 0% | -127.0023 | 285.4462 | -3550 | -400 | -3664.5538 | 91.61% | 52.22% | 95% | 0% | 1617 | -111
[5 empty] | 2019-08-24 | 15 | 5646.5 | 1550 | -157 | 1 | 0 | 1707 | 553.4213 | 553.4213 | 553.4213 | 1060.9233 | 780 | 200 | 2040.9233 | 51.02% | 95% | 0% | -179.6339 | 373.7874 | -3550 | -400 | -3576.2126 | 89.41% | 52.21% | 95% | 0% | 1707 | -157
[5 empty] | 2019-08-24 | 16 | 5647 | 1560 | -203 | 1 | 0 | 1763 | 641.1377 | 641.1377 | 641.1377 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -232.2654 | 408.8722 | -3550 | -400 | -3541.1278 | 88.53% | 52.21% | 95% | 0% | 1763 | -203
[5 empty] | 2019-08-24 | 17 | 5647.5 | 1581 | -258 | 1 | 0 | 1839 | 760.1814 | 760.1814 | 760.1814 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -295.1945 | 464.9869 | -3550 | -400 | -3485.0131 | 87.13% | 52.21% | 95% | 0% | 1839 | -258
[5 empty] | 2019-08-24 | 18 | 5648 | 1526 | -342 | 1 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -391.3043 | 414.3016 | -3550 | -400 | -3535.6984 | 88.39% | 52.2% | 95% | 0% | 1868 | -342
[5 empty] | 2019-08-24 | 19 | 5648.5 | 1469 | -412 | 1 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -471.3959 | 354.5728 | -3550 | -400 | -3595.4272 | 89.89% | 52.2% | 95% | 0% | 1881 | -412
[5 empty] | 2019-08-24 | 20 | 5649 | 1382 | -478 | 1 | 0 | 1860 | 793.075 | 793.075 | 793.075 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -546.9108 | 246.1643 | -3550 | -400 | -3703.8357 | 92.6% | 52.2% | 95% | 0% | 1860 | -478
[5 empty] | 2019-08-24 | 21 | 5649.5 | 1305 | -539 | 1 | 0 | 1844 | 768.0132 | 768.0132 | 768.0132 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -616.7048 | 151.3084 | -3550 | -400 | -3798.6916 | 94.97% | 52.2% | 95% | 0% | 1844 | -539
[5 empty] | 2019-08-24 | 22 | 5650 | 1237 | -591 | 1 | 0 | 1828 | 742.9514 | 742.9514 | 742.9514 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -676.2014 | 66.75 | -3550 | -400 | -3883.25 | 97.08% | 52.2% | 95% | 0% | 1828 | -591
[5 empty] | 2019-08-24 | 23 | 5650.5 | 1139 | -641 | 1 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -733.4096 | -65.6437 | -3550 | -400 | -4015.6437 | 100.4% | 52.2% | 95% | 0% | 1780 | -641
[5 empty] | 2019-08-24 | 24 | 5651 | 1062 | -681 | 1 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -779.1762 | -169.3658 | -3550 | -400 | -4119.3658 | 103% | 52.2% | 95% | 0% | 1743 | -681
[5 empty] | 2019-08-24 | 25 | 5651.5 | 1017 | -713 | 1 | 0 | 1730 | 589.4477 | 589.4477 | 589.4477 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -815.7895 | -226.3418 | -3550 | -400 | -4176.3418 | 104.4% | 52.19% | 95% | 0% | 1730 | -713
[5 empty] | 2019-08-24 | 26 | 5652 | 966 | -737 | 1 | 0 | 1703 | 547.1558 | 547.1558 | 547.1558 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -843.2494 | -296.0936 | -3550 | -400 | -4246.0936 | 106.2% | 52.19% | 95% | 0% | 1703 | -737
[5 empty] | 2019-08-24 | 27 | 5652.5 | 920 | -742 | 1 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -848.9703 | -366.0354 | -3550 | -400 | -4316.0354 | 107.9% | 52.19% | 95% | 0% | 1662 | -742
[5 empty] | 2019-08-24 | 28 | 5653 | 930 | -714 | 1 | 0 | 1644 | 454.7403 | 454.7403 | 454.7403 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -816.9336 | -362.1933 | -3550 | -400 | -4312.1933 | 107.8% | 52.18% | 95% | 0% | 1644 | -714
[5 empty] | 2019-08-24 | 29 | 5653.5 | 924 | -709 | 1 | 0 | 1633 | 437.5103 | 437.5103 | 437.5103 | 1059.357 | 780 | 200 | 2039.357 | 50.98% | 95% | 0% | -811.2128 | -373.7025 | -3550 | -400 | -4323.7025 | 108.1% | 52.18% | 95% | 0% | 1633 | -709
[5 empty] | 2019-08-24 | 30 | 5654 | 954 | -676 | 1 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 1057.7906 | 780 | 200 | 2037.7906 | 50.94% | 95% | 0% | -773.4554 | -340.6442 | -3550 | -400 | -4290.6442 | 107.3% | 52.17% | 95% | 0% | 1630 | -676
[5 empty] | 2019-08-24 | 31 | 5654.5 | 994 | -635 | 1 | 0 | 1629 | 431.2448 | 431.2448 | 431.2448 | 1057.7906 | 780 | 200 | 2037.7906 | 50.94% | 95% | 0% | -726.5446 | -295.2998 | -3550 | -400 | -4245.2998 | 106.1% | 52.17% | 95% | 0% | 1629 | -635
[5 empty] | 2019-08-24 | 32 | 5655 | 1082 | -580 | 1 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 1057.7906 | 780 | 200 | 2037.7906 | 50.94% | 95% | 0% | -663.6156 | -180.6807 | -3550 | -400 | -4130.6807 | 103.3% | 52.17% | 95% | 0% | 1662 | -580
[5 empty] | 2019-08-24 | 33 | 5655.5 | 1239 | -505 | 1 | 0 | 1744 | 611.3768 | 611.3768 | 611.3768 | 1057.7906 | 780 | 200 | 2037.7906 | 50.94% | 95% | 0% | -577.8032 | 33.5735 | -3550 | -400 | -3916.4265 | 97.91% | 52.17% | 95% | 0% | 1744 | -505
[5 empty] | 2019-08-24 | 34 | 5656 | 1404 | -433 | 1 | 0 | 1837 | 757.0486 | 757.0486 | 757.0486 | 1057.7906 | 780 | 200 | 2037.7906 | 50.94% | 95% | 0% | -495.4233 | 261.6253 | -3550 | -400 | -3688.3747 | 92.21% | 52.15% | 95% | 0% | 1837 | -433
[5 empty] | 2019-08-24 | 35 | 5656.5 | 1604 | -356 | 1 | 0 | 1960 | 949.7115 | 949.7115 | 949.7115 | 1057.7906 | 780 | 200 | 2037.7906 | 50.94% | 95% | 0% | -407.3227 | 542.3888 | -3550 | -400 | -3407.6112 | 85.19% | 52.15% | 95% | 0% | 1960 | -356
[5 empty] | 2019-08-24 | 36 | 5657 | 1748 | -269 | 1 | 0 | 2017 | 1038.9942 | 1038.9942 | 1038.9942 | 1057.7906 | 780 | 200 | 2037.7906 | 50.94% | 95% | 0% | -307.7803 | 731.2139 | -3550 | -400 | -3218.7861 | 80.47% | 52.15% | 95% | 0% | 2017 | -269
[5 empty] | 2019-08-24 | 37 | 5657.5 | 1885 | -202 | 1 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 1057.7906 | 780 | 200 | 2037.7906 | 50.94% | 95% | 0% | -231.1213 | 917.5185 | -3550 | -400 | -3032.4815 | 75.81% | 52.15% | 95% | 0% | 2087 | -202
[5 empty] | 2019-08-24 | 38 | 5658 | 1971 | -145 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1057.7906 | 780 | 200 | 2037.7906 | 50.94% | 95% | 0% | -165.9039 | 1028.1604 | -3550 | -400 | -2921.8396 | 73.05% | 52.14% | 95% | 0% | 2116 | -145
[5 empty] | 2019-08-24 | 39 | 5658.5 | 2026 | -105 | 1 | 0 | 2131 | 1217.5598 | 1217.5598 | 1217.5598 | 1057.7906 | 780 | 200 | 2037.7906 | 50.94% | 95% | 0% | -120.1373 | 1097.4225 | -3550 | -400 | -2852.5775 | 71.31% | 52.14% | 95% | 0% | 2131 | -105
[5 empty] | 2019-08-24 | 40 | 5659 | 2053 | -74 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 1057.7906 | 780 | 200 | 2037.7906 | 50.94% | 95% | 0% | -84.6682 | 1126.6261 | -3550 | -400 | -2823.3739 | 70.58% | 52.13% | 95% | 0% | 2127 | -74
[5 empty] | 2019-08-24 | 41 | 5659.5 | 2072 | -63 | 1 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 1056.2242 | 780 | 200 | 2036.2242 | 50.91% | 95% | 0% | -72.0824 | 1151.7428 | -3550 | -400 | -2798.2572 | 69.96% | 52.13% | 95% | 0% | 2135 | -63
[5 empty] | 2019-08-24 | 42 | 5660 | 2101 | -62 | 1 | 0 | 2163 | 1267.6834 | 1267.6834 | 1267.6834 | 1056.2242 | 780 | 200 | 2036.2242 | 50.91% | 95% | 0% | -70.9382 | 1196.7452 | -3550 | -400 | -2753.2548 | 68.83% | 52.13% | 95% | 0% | 2163 | -62
[5 empty] | 2019-08-24 | 43 | 5660.5 | 2055 | -60 | 0 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 1056.2242 | 780 | 200 | 2036.2242 | 50.91% | 95% | 0% | -68.6499 | 1123.8481 | -2750 | -200 | -1826.1519 | 45.65% | 52.12% | 95% | 0% | 2115 | -60
[5 empty] | 2019-08-24 | 44 | 5661 | 1964 | -59 | 0 | 0 | 2023 | 1048.3924 | 1048.3924 | 1048.3924 | 1056.2242 | 780 | 200 | 2036.2242 | 50.91% | 95% | 0% | -67.5057 | 980.8867 | -2750 | -200 | -1969.1133 | 49.23% | 52.12% | 95% | 0% | 2023 | -59
[5 empty] | 2019-08-24 | 45 | 5661.5 | 1907 | -57 | 0 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 1056.2242 | 780 | 200 | 2036.2242 | 50.91% | 95% | 0% | -65.2174 | 890.7595 | -2750 | -200 | -2059.2405 | 51.48% | 52.12% | 95% | 0% | 1964 | -57
[5 empty] | 2019-08-24 | 46 | 5662 | 1842 | -56 | 0 | 0 | 1898 | 852.5969 | 852.5969 | 852.5969 | 1056.2242 | 780 | 200 | 2036.2242 | 50.91% | 95% | 0% | -64.0732 | 788.5236 | -2750 | -200 | -2161.4764 | 54.04% | 52.12% | 95% | 0% | 1898 | -56
[5 empty] | 2019-08-24 | 47 | 5662.5 | 1771 | -54 | 0 | 0 | 1825 | 738.2523 | 738.2523 | 738.2523 | 1056.2242 | 780 | 200 | 2036.2242 | 50.91% | 95% | 0% | -61.7849 | 676.4674 | -2750 | -200 | -2273.5326 | 56.84% | 52.12% | 95% | 0% | 1825 | -54
[5 empty] | 2019-08-24 | 48 | 5663 | 1683 | -53 | 0 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 1056.2242 | 780 | 200 | 2036.2242 | 50.91% | 95% | 0% | -60.6407 | 538.2051 | -2750 | -200 | -2411.7949 | 60.29% | 52.1% | 95% | 0% | 1736 | -53
[5 empty] | 2019-08-25 | 1 | 5663.5 | 1618 | -52 | 0 | 0 | 1670 | 495.4658 | 495.4658 | 495.4658 | 1056.2242 | 780 | 200 | 2036.2242 | 50.91% | 95% | 0% | -59.4966 | 435.9692 | -2750 | -200 | -2514.0308 | 62.85% | 52.09% | 95% | 0% | 1670 | -52
[5 empty] | 2019-08-25 | 2 | 5664 | 1567 | -51 | 0 | 0 | 1618 | 414.0148 | 414.0148 | 414.0148 | 1056.2242 | 780 | 200 | 2036.2242 | 50.91% | 95% | 0% | -58.3524 | 355.6624 | -2750 | -200 | -2594.3376 | 64.86% | 52.08% | 95% | 0% | 1618 | -51
[5 empty] | 2019-08-25 | 3 | 5664.5 | 1527 | -49 | 0 | 0 | 1576 | 348.2275 | 348.2275 | 348.2275 | 1056.2242 | 780 | 200 | 2036.2242 | 50.91% | 95% | 0% | -56.0641 | 292.1635 | -2750 | -200 | -2657.8365 | 66.45% | 52.07% | 95% | 0% | 1576 | -49
[5 empty] | 2019-08-25 | 4 | 5665 | 1502 | -47 | 0 | 0 | 1549 | 305.9357 | 305.9357 | 305.9357 | 1054.6579 | 780 | 200 | 2034.6579 | 50.87% | 95% | 0% | -53.7757 | 252.16 | -2750 | -200 | -2697.84 | 67.45% | 52.06% | 95% | 0% | 1549 | -47
[5 empty] | 2019-08-25 | 5 | 5665.5 | 1477 | -47 | 0 | 0 | 1524 | 266.7766 | 266.7766 | 266.7766 | 1054.6579 | 780 | 200 | 2034.6579 | 50.87% | 95% | 0% | -53.7757 | 213.0008 | -2750 | -200 | -2736.9992 | 68.42% | 52.06% | 95% | 0% | 1524 | -47
[5 empty] | 2019-08-25 | 6 | 5666 | 1446 | -46 | 0 | 0 | 1492 | 216.6529 | 216.6529 | 216.6529 | 1054.6579 | 780 | 200 | 2034.6579 | 50.87% | 95% | 0% | -52.6316 | 164.0213 | -2750 | -200 | -2785.9787 | 69.65% | 52.06% | 95% | 0% | 1492 | -46
[5 empty] | 2019-08-25 | 7 | 5666.5 | 1426 | -45 | 0 | 0 | 1471 | 183.7593 | 183.7593 | 183.7593 | 1054.6579 | 780 | 200 | 2034.6579 | 50.87% | 95% | 0% | -51.4874 | 132.2719 | -2750 | -200 | -2817.7281 | 70.44% | 52.05% | 95% | 0% | 1471 | -45
[5 empty] | 2019-08-25 | 8 | 5667 | 1420 | -44 | 0 | 0 | 1464 | 172.7947 | 172.7947 | 172.7947 | 1054.6579 | 780 | 200 | 2034.6579 | 50.87% | 95% | 0% | -50.3432 | 122.4515 | -2750 | -200 | -2827.5485 | 70.69% | 52.04% | 95% | 0% | 1464 | -44
[5 empty] | 2019-08-25 | 9 | 5667.5 | 1412 | -43 | 0 | 0 | 1455 | 158.6974 | 158.6974 | 158.6974 | 1054.6579 | 780 | 200 | 2034.6579 | 50.87% | 95% | 0% | -49.1991 | 109.4984 | -2750 | -200 | -2840.5016 | 71.01% | 52.04% | 95% | 0% | 1455 | -43
[5 empty] | 2019-08-25 | 10 | 5668 | 1410 | -42 | 1 | 0 | 1452 | 153.9984 | 153.9984 | 153.9984 | 1054.6579 | 780 | 200 | 2034.6579 | 50.87% | 95% | 0% | -48.0549 | 105.9434 | -3550 | -400 | -3844.0566 | 96.1% | 52.04% | 95% | 0% | 1452 | -42
[5 empty] | 2019-08-25 | 11 | 5668.5 | 1419 | -40 | 1 | 0 | 1459 | 164.9629 | 164.9629 | 164.9629 | 1054.6579 | 780 | 200 | 2034.6579 | 50.87% | 95% | 0% | -45.7666 | 119.1963 | -3550 | -400 | -3830.8037 | 95.77% | 52.04% | 95% | 0% | 1459 | -40
[5 empty] | 2019-08-25 | 12 | 5669 | 1422 | -38 | 1 | 0 | 1460 | 166.5293 | 166.5293 | 166.5293 | 1054.6579 | 780 | 200 | 2034.6579 | 50.87% | 95% | 0% | -43.4783 | 123.051 | -3550 | -400 | -3826.949 | 95.67% | 52.04% | 95% | 0% | 1460 | -38
[5 empty] | 2019-08-25 | 13 | 5669.5 | 1454 | -37 | 1 | 0 | 1491 | 215.0866 | 215.0866 | 215.0866 | 1054.6579 | 780 | 200 | 2034.6579 | 50.87% | 95% | 0% | -42.3341 | 172.7525 | -3550 | -400 | -3777.2475 | 94.43% | 52.04% | 95% | 0% | 1491 | -37
[5 empty] | 2019-08-25 | 14 | 5670 | 1473 | -51 | 1 | 0 | 1524 | 266.7766 | 266.7766 | 266.7766 | 1054.6579 | 780 | 200 | 2034.6579 | 50.87% | 95% | 0% | -58.3524 | 208.4242 | -3550 | -400 | -3741.5758 | 93.54% | 52.04% | 95% | 0% | 1524 | -51
[5 empty] | 2019-08-25 | 15 | 5670.5 | 1503 | -80 | 1 | 0 | 1583 | 359.1921 | 359.1921 | 359.1921 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -91.5332 | 267.6589 | -3550 | -400 | -3682.3411 | 92.06% | 52.04% | 95% | 0% | 1583 | -80
[5 empty] | 2019-08-25 | 16 | 5671 | 1516 | -125 | 1 | 0 | 1641 | 450.0412 | 450.0412 | 450.0412 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -143.0206 | 307.0206 | -3550 | -400 | -3642.9794 | 91.07% | 52.04% | 95% | 0% | 1641 | -125
[5 empty] | 2019-08-25 | 17 | 5671.5 | 1514 | -186 | 1 | 0 | 1700 | 542.4567 | 542.4567 | 542.4567 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -212.8146 | 329.6421 | -3550 | -400 | -3620.3579 | 90.51% | 52.03% | 95% | 0% | 1700 | -186
[5 empty] | 2019-08-25 | 18 | 5672 | 1488 | -260 | 1 | 0 | 1748 | 617.6422 | 617.6422 | 617.6422 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -297.4828 | 320.1594 | -3550 | -400 | -3629.8406 | 90.75% | 52.03% | 95% | 0% | 1748 | -260
[5 empty] | 2019-08-25 | 19 | 5672.5 | 1423 | -344 | 1 | 0 | 1767 | 647.4031 | 647.4031 | 647.4031 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -393.5927 | 253.8105 | -3550 | -400 | -3696.1895 | 92.4% | 52.02% | 95% | 0% | 1767 | -344
[5 empty] | 2019-08-25 | 20 | 5673 | 1369 | -404 | 1 | 0 | 1773 | 656.8013 | 656.8013 | 656.8013 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -462.2426 | 194.5588 | -3550 | -400 | -3755.4412 | 93.89% | 52.02% | 95% | 0% | 1773 | -404
[5 empty] | 2019-08-25 | 21 | 5673.5 | 1308 | -472 | 1 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -540.0458 | 127.7201 | -3550 | -400 | -3822.2799 | 95.56% | 52.02% | 95% | 0% | 1780 | -472
[5 empty] | 2019-08-25 | 22 | 5674 | 1239 | -531 | 1 | 0 | 1770 | 652.1022 | 652.1022 | 652.1022 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -607.5515 | 44.5507 | -3550 | -400 | -3905.4493 | 97.64% | 52.02% | 95% | 0% | 1770 | -531
[5 empty] | 2019-08-25 | 23 | 5674.5 | 1182 | -580 | 1 | 0 | 1762 | 639.5713 | 639.5713 | 639.5713 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -663.6156 | -24.0442 | -3550 | -400 | -3974.0442 | 99.35% | 52.02% | 95% | 0% | 1762 | -580
[5 empty] | 2019-08-25 | 24 | 5675 | 1127 | -622 | 1 | 0 | 1749 | 619.2086 | 619.2086 | 619.2086 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -711.6705 | -92.4619 | -3550 | -400 | -4042.4619 | 101.1% | 52.01% | 95% | 0% | 1749 | -622
[5 empty] | 2019-08-25 | 25 | 5675.5 | 1093 | -643 | 1 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -735.6979 | -136.8521 | -3550 | -400 | -4086.8521 | 102.2% | 52.01% | 95% | 0% | 1736 | -643
[5 empty] | 2019-08-25 | 26 | 5676 | 1072 | -657 | 1 | 0 | 1729 | 587.8813 | 587.8813 | 587.8813 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -751.7162 | -163.835 | -3550 | -400 | -4113.835 | 102.8% | 52.01% | 95% | 0% | 1729 | -657
[5 empty] | 2019-08-25 | 27 | 5676.5 | 1036 | -664 | 1 | 0 | 1700 | 542.4567 | 542.4567 | 542.4567 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -759.7254 | -217.2687 | -3550 | -400 | -4167.2687 | 104.2% | 52.01% | 95% | 0% | 1700 | -664
[5 empty] | 2019-08-25 | 28 | 5677 | 1003 | -664 | 1 | 0 | 1667 | 490.7667 | 490.7667 | 490.7667 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -759.7254 | -268.9587 | -3550 | -400 | -4218.9587 | 105.5% | 52.01% | 95% | 0% | 1667 | -664
[5 empty] | 2019-08-25 | 29 | 5677.5 | 1002 | -653 | 1 | 0 | 1655 | 471.9703 | 471.9703 | 471.9703 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -747.1396 | -275.1693 | -3550 | -400 | -4225.1693 | 105.6% | 52% | 95% | 0% | 1655 | -653
[5 empty] | 2019-08-25 | 30 | 5678 | 1027 | -626 | 1 | 0 | 1653 | 468.8376 | 468.8376 | 468.8376 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -716.2471 | -247.4095 | -3550 | -400 | -4197.4095 | 104.9% | 52% | 95% | 0% | 1653 | -626
[5 empty] | 2019-08-25 | 31 | 5678.5 | 1087 | -587 | 1 | 0 | 1674 | 501.7312 | 501.7312 | 501.7312 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -671.6247 | -169.8935 | -3550 | -400 | -4119.8935 | 103% | 52% | 95% | 0% | 1674 | -587
[5 empty] | 2019-08-25 | 32 | 5679 | 1184 | -538 | 1 | 0 | 1722 | 576.9167 | 576.9167 | 576.9167 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -615.5606 | -38.6439 | -3550 | -400 | -3988.6439 | 99.72% | 52% | 95% | 0% | 1722 | -538
[5 empty] | 2019-08-25 | 33 | 5679.5 | 1301 | -477 | 1 | 0 | 1778 | 664.6331 | 664.6331 | 664.6331 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -545.7666 | 118.8666 | -3550 | -400 | -3831.1334 | 95.78% | 52% | 95% | 0% | 1778 | -477
[5 empty] | 2019-08-25 | 34 | 5680 | 1437 | -414 | 1 | 0 | 1851 | 778.9777 | 778.9777 | 778.9777 | 1053.0915 | 780 | 200 | 2033.0915 | 50.83% | 95% | 0% | -473.6842 | 305.2935 | -3550 | -400 | -3644.7065 | 91.12% | 52% | 95% | 0% | 1851 | -414
[5 empty] | 2019-08-25 | 35 | 5680.5 | 1587 | -344 | 1 | 0 | 1931 | 904.2869 | 904.2869 | 904.2869 | 1051.5251 | 780 | 200 | 2031.5251 | 50.79% | 95% | 0% | -393.5927 | 510.6942 | -3550 | -400 | -3439.3058 | 85.98% | 51.99% | 95% | 0% | 1931 | -344
[5 empty] | 2019-08-25 | 36 | 5681 | 1726 | -272 | 1 | 0 | 1998 | 1009.2333 | 1009.2333 | 1009.2333 | 1051.5251 | 780 | 200 | 2031.5251 | 50.79% | 95% | 0% | -311.2128 | 698.0205 | -3550 | -400 | -3251.9795 | 81.3% | 51.99% | 95% | 0% | 1998 | -272
[5 empty] | 2019-08-25 | 37 | 5681.5 | 1849 | -208 | 1 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 1051.5251 | 780 | 200 | 2031.5251 | 50.79% | 95% | 0% | -237.9863 | 863.6625 | -3550 | -400 | -3086.3375 | 77.16% | 51.99% | 95% | 0% | 2057 | -208
[5 empty] | 2019-08-25 | 38 | 5682 | 1936 | -148 | 1 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 1051.5251 | 780 | 200 | 2031.5251 | 50.79% | 95% | 0% | -169.3364 | 974.6043 | -3550 | -400 | -2975.3957 | 74.38% | 51.98% | 95% | 0% | 2084 | -148
[5 empty] | 2019-08-25 | 39 | 5682.5 | 2028 | -97 | 1 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 1051.5251 | 780 | 200 | 2031.5251 | 50.79% | 95% | 0% | -110.984 | 1097.1776 | -3550 | -400 | -2852.8224 | 71.32% | 51.98% | 95% | 0% | 2125 | -97
[5 empty] | 2019-08-25 | 40 | 5683 | 2078 | -63 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1051.5251 | 780 | 200 | 2031.5251 | 50.79% | 95% | 0% | -72.0824 | 1161.141 | -3550 | -400 | -2788.859 | 69.72% | 51.98% | 95% | 0% | 2141 | -63
[5 empty] | 2019-08-25 | 41 | 5683.5 | 2109 | -53 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 1051.5251 | 780 | 200 | 2031.5251 | 50.79% | 95% | 0% | -60.6407 | 1205.4763 | -3550 | -400 | -2744.5237 | 68.61% | 51.97% | 95% | 0% | 2162 | -53
[5 empty] | 2019-08-25 | 42 | 5684 | 2134 | -51 | 1 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 1051.5251 | 780 | 200 | 2031.5251 | 50.79% | 95% | 0% | -58.3524 | 1243.791 | -3550 | -400 | -2706.209 | 67.66% | 51.97% | 95% | 0% | 2185 | -51
[5 empty] | 2019-08-25 | 43 | 5684.5 | 2110 | -50 | 0 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1049.9588 | 780 | 200 | 2029.9588 | 50.75% | 95% | 0% | -57.2082 | 1205.7761 | -2750 | -200 | -1744.2239 | 43.61% | 51.96% | 95% | 0% | 2160 | -50
[5 empty] | 2019-08-25 | 44 | 5685 | 2048 | -48 | 0 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 1049.9588 | 780 | 200 | 2029.9588 | 50.75% | 95% | 0% | -54.9199 | 1107.8171 | -2750 | -200 | -1842.1829 | 46.05% | 51.95% | 95% | 0% | 2096 | -48
[5 empty] | 2019-08-25 | 45 | 5685.5 | 1989 | -46 | 0 | 0 | 2035 | 1067.1888 | 1067.1888 | 1067.1888 | 1049.9588 | 780 | 200 | 2029.9588 | 50.75% | 95% | 0% | -52.6316 | 1014.5572 | -2750 | -200 | -1935.4428 | 48.39% | 51.95% | 95% | 0% | 2035 | -46
[5 empty] | 2019-08-25 | 46 | 5686 | 1900 | -44 | 0 | 0 | 1944 | 924.6496 | 924.6496 | 924.6496 | 1049.9588 | 780 | 200 | 2029.9588 | 50.75% | 95% | 0% | -50.3432 | 874.3064 | -2750 | -200 | -2075.6936 | 51.89% | 51.95% | 95% | 0% | 1944 | -44
[5 empty] | 2019-08-25 | 47 | 5686.5 | 1800 | -42 | 0 | 0 | 1842 | 764.8805 | 764.8805 | 764.8805 | 1049.9588 | 780 | 200 | 2029.9588 | 50.75% | 95% | 0% | -48.0549 | 716.8255 | -2750 | -200 | -2233.1745 | 55.83% | 51.95% | 95% | 0% | 1842 | -42
[5 empty] | 2019-08-25 | 48 | 5687 | 1712 | -41 | 1 | 0 | 1753 | 625.474 | 625.474 | 625.474 | 1049.9588 | 780 | 200 | 2029.9588 | 50.75% | 95% | 0% | -46.9108 | 578.5633 | -3550 | -400 | -3371.4367 | 84.29% | 51.94% | 95% | 0% | 1753 | -41
[5 empty] | 2019-08-26 | 1 | 5687.5 | 1631 | -40 | 1 | 0 | 1671 | 497.0322 | 497.0322 | 497.0322 | 1049.9588 | 780 | 200 | 2029.9588 | 50.75% | 95% | 0% | -45.7666 | 451.2656 | -3550 | -400 | -3498.7344 | 87.47% | 51.93% | 95% | 0% | 1671 | -40
[5 empty] | 2019-08-26 | 2 | 5688 | 1590 | -38 | 1 | 0 | 1628 | 429.6785 | 429.6785 | 429.6785 | 1048.3924 | 780 | 200 | 2028.3924 | 50.71% | 95% | 0% | -43.4783 | 386.2002 | -3550 | -400 | -3563.7998 | 89.09% | 51.93% | 95% | 0% | 1628 | -38
[5 empty] | 2019-08-26 | 3 | 5688.5 | 1557 | -38 | 1 | 0 | 1595 | 377.9885 | 377.9885 | 377.9885 | 1048.3924 | 780 | 200 | 2028.3924 | 50.71% | 95% | 0% | -43.4783 | 334.5102 | -3550 | -400 | -3615.4898 | 90.39% | 51.93% | 95% | 0% | 1595 | -38
[5 empty] | 2019-08-26 | 4 | 5689 | 1525 | -38 | 1 | 0 | 1563 | 327.8648 | 327.8648 | 327.8648 | 1048.3924 | 780 | 200 | 2028.3924 | 50.71% | 95% | 0% | -43.4783 | 284.3865 | -3550 | -400 | -3665.6135 | 91.64% | 51.92% | 95% | 0% | 1563 | -38
[5 empty] | 2019-08-26 | 5 | 5689.5 | 1496 | -37 | 1 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 1048.3924 | 780 | 200 | 2028.3924 | 50.71% | 95% | 0% | -42.3341 | 238.5398 | -3550 | -400 | -3711.4602 | 92.79% | 51.91% | 95% | 0% | 1533 | -37
[5 empty] | 2019-08-26 | 6 | 5690 | 1471 | -36 | 1 | 0 | 1507 | 240.1484 | 240.1484 | 240.1484 | 1048.3924 | 780 | 200 | 2028.3924 | 50.71% | 95% | 0% | -41.1899 | 198.9585 | -3550 | -400 | -3751.0415 | 93.78% | 51.91% | 95% | 0% | 1507 | -36
[5 empty] | 2019-08-26 | 7 | 5690.5 | 1458 | -34 | 1 | 0 | 1492 | 216.6529 | 216.6529 | 216.6529 | 1048.3924 | 780 | 200 | 2028.3924 | 50.71% | 95% | 0% | -38.9016 | 177.7513 | -3550 | -400 | -3772.2487 | 94.31% | 51.89% | 95% | 0% | 1492 | -34
[5 empty] | 2019-08-26 | 8 | 5691 | 1457 | -33 | 1 | 0 | 1490 | 213.5202 | 213.5202 | 213.5202 | 1048.3924 | 780 | 200 | 2028.3924 | 50.71% | 95% | 0% | -37.7574 | 175.7628 | -3550 | -400 | -3774.2372 | 94.36% | 51.89% | 95% | 0% | 1490 | -33
[5 empty] | 2019-08-26 | 9 | 5691.5 | 1457 | -32 | 1 | 0 | 1489 | 211.9538 | 211.9538 | 211.9538 | 1048.3924 | 780 | 200 | 2028.3924 | 50.71% | 95% | 0% | -36.6133 | 175.3406 | -3550 | -400 | -3774.6594 | 94.37% | 51.88% | 95% | 0% | 1489 | -32
[5 empty] | 2019-08-26 | 10 | 5692 | 1463 | -31 | 1 | 0 | 1494 | 219.7857 | 219.7857 | 219.7857 | 1048.3924 | 780 | 200 | 2028.3924 | 50.71% | 95% | 0% | -35.4691 | 184.3165 | -3550 | -400 | -3765.6835 | 94.14% | 51.88% | 95% | 0% | 1494 | -31
[5 empty] | 2019-08-26 | 11 | 5692.5 | 1495 | -31 | 1 | 0 | 1526 | 269.9093 | 269.9093 | 269.9093 | 1048.3924 | 780 | 200 | 2028.3924 | 50.71% | 95% | 0% | -35.4691 | 234.4402 | -3550 | -400 | -3715.5598 | 92.89% | 51.87% | 95% | 0% | 1526 | -31
[5 empty] | 2019-08-26 | 12 | 5693 | 1525 | -31 | 1 | 0 | 1556 | 316.9002 | 316.9002 | 316.9002 | 1048.3924 | 780 | 200 | 2028.3924 | 50.71% | 95% | 0% | -35.4691 | 281.4311 | -3550 | -400 | -3668.5689 | 91.71% | 51.87% | 95% | 0% | 1556 | -31
[5 empty] | 2019-08-26 | 13 | 5693.5 | 1573 | -33 | 1 | 0 | 1606 | 395.2185 | 395.2185 | 395.2185 | 1046.8261 | 780 | 200 | 2026.8261 | 50.67% | 95% | 0% | -37.7574 | 357.461 | -3550 | -400 | -3592.539 | 89.81% | 51.87% | 95% | 0% | 1606 | -33
[5 empty] | 2019-08-26 | 14 | 5694 | 1617 | -50 | 1 | 0 | 1667 | 490.7667 | 490.7667 | 490.7667 | 1046.8261 | 780 | 200 | 2026.8261 | 50.67% | 95% | 0% | -57.2082 | 433.5585 | -3550 | -400 | -3516.4415 | 87.91% | 51.86% | 95% | 0% | 1667 | -50
[5 empty] | 2019-08-26 | 15 | 5694.5 | 1671 | -85 | 1 | 0 | 1756 | 630.1731 | 630.1731 | 630.1731 | 1046.8261 | 780 | 200 | 2026.8261 | 50.67% | 95% | 0% | -97.254 | 532.9191 | -3550 | -400 | -3417.0809 | 85.43% | 51.86% | 95% | 0% | 1756 | -85
[5 empty] | 2019-08-26 | 16 | 5695 | 1680 | -131 | 1 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 1046.8261 | 780 | 200 | 2026.8261 | 50.67% | 95% | 0% | -149.8856 | 566.4376 | -3550 | -400 | -3383.5624 | 84.59% | 51.86% | 95% | 0% | 1811 | -131
[5 empty] | 2019-08-26 | 17 | 5695.5 | 1680 | -188 | 1 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 1046.8261 | 780 | 200 | 2026.8261 | 50.67% | 95% | 0% | -215.103 | 590.503 | -3550 | -400 | -3359.497 | 83.99% | 51.86% | 95% | 0% | 1868 | -188
[5 empty] | 2019-08-26 | 18 | 5696 | 1657 | -249 | 1 | 0 | 1906 | 865.1278 | 865.1278 | 865.1278 | 1046.8261 | 780 | 200 | 2026.8261 | 50.67% | 95% | 0% | -284.897 | 580.2308 | -3550 | -400 | -3369.7692 | 84.24% | 51.86% | 95% | 0% | 1906 | -249
[5 empty] | 2019-08-26 | 19 | 5696.5 | 1634 | -313 | 1 | 0 | 1947 | 929.3487 | 929.3487 | 929.3487 | 1046.8261 | 780 | 200 | 2026.8261 | 50.67% | 95% | 0% | -358.1236 | 571.2252 | -3550 | -400 | -3378.7748 | 84.47% | 51.85% | 95% | 0% | 1947 | -313
[5 empty] | 2019-08-26 | 20 | 5697 | 1589 | -374 | 1 | 0 | 1963 | 954.4106 | 954.4106 | 954.4106 | 1046.8261 | 780 | 200 | 2026.8261 | 50.67% | 95% | 0% | -427.9176 | 526.4929 | -3550 | -400 | -3423.5071 | 85.59% | 51.85% | 95% | 0% | 1963 | -374
[5 empty] | 2019-08-26 | 21 | 5697.5 | 1505 | -434 | 1 | 0 | 1939 | 916.8178 | 916.8178 | 916.8178 | 1046.8261 | 780 | 200 | 2026.8261 | 50.67% | 95% | 0% | -496.5675 | 420.2503 | -3550 | -400 | -3529.7497 | 88.24% | 51.85% | 95% | 0% | 1939 | -434
[5 empty] | 2019-08-26 | 22 | 5698 | 1427 | -491 | 1 | 0 | 1918 | 883.9242 | 883.9242 | 883.9242 | 1046.8261 | 780 | 200 | 2026.8261 | 50.67% | 95% | 0% | -561.7849 | 322.1393 | -3550 | -400 | -3627.8607 | 90.7% | 51.84% | 95% | 0% | 1918 | -491
[5 empty] | 2019-08-26 | 23 | 5698.5 | 1354 | -544 | 1 | 0 | 1898 | 852.5969 | 852.5969 | 852.5969 | 1046.8261 | 780 | 200 | 2026.8261 | 50.67% | 95% | 0% | -622.4256 | 230.1712 | -3550 | -400 | -3719.8288 | 93% | 51.83% | 95% | 0% | 1898 | -544
[5 empty] | 2019-08-26 | 24 | 5699 | 1269 | -601 | 1 | 0 | 1870 | 808.7387 | 808.7387 | 808.7387 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -687.643 | 121.0956 | -3550 | -400 | -3828.9044 | 95.72% | 51.83% | 95% | 0% | 1870 | -601
[5 empty] | 2019-08-26 | 25 | 5699.5 | 1204 | -642 | 1 | 0 | 1846 | 771.1459 | 771.1459 | 771.1459 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -734.5538 | 36.5921 | -3550 | -400 | -3913.4079 | 97.84% | 51.82% | 95% | 0% | 1846 | -642
[5 empty] | 2019-08-26 | 26 | 5700 | 1155 | -670 | 1 | 0 | 1825 | 738.2523 | 738.2523 | 738.2523 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -766.5904 | -28.3381 | -3550 | -400 | -3978.3381 | 99.46% | 51.82% | 95% | 0% | 1825 | -670
[5 empty] | 2019-08-26 | 27 | 5700.5 | 1110 | -681 | 1 | 0 | 1791 | 684.9959 | 684.9959 | 684.9959 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -779.1762 | -94.1803 | -3550 | -400 | -4044.1803 | 101.1% | 51.81% | 95% | 0% | 1791 | -681
[5 empty] | 2019-08-26 | 28 | 5701 | 1088 | -680 | 1 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -778.032 | -129.0625 | -3550 | -400 | -4079.0625 | 102% | 51.81% | 95% | 0% | 1768 | -680
[5 empty] | 2019-08-26 | 29 | 5701.5 | 1099 | -662 | 1 | 0 | 1761 | 638.0049 | 638.0049 | 638.0049 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -757.4371 | -119.4321 | -3550 | -400 | -4069.4321 | 101.7% | 51.81% | 95% | 0% | 1761 | -662
[5 empty] | 2019-08-26 | 30 | 5702 | 1133 | -631 | 1 | 0 | 1764 | 642.704 | 642.704 | 642.704 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -721.968 | -79.2639 | -3550 | -400 | -4029.2639 | 100.7% | 51.81% | 95% | 0% | 1764 | -631
[5 empty] | 2019-08-26 | 31 | 5702.5 | 1206 | -588 | 1 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -672.7689 | 16.9261 | -3550 | -400 | -3933.0739 | 98.33% | 51.81% | 95% | 0% | 1794 | -588
[5 empty] | 2019-08-26 | 32 | 5703 | 1322 | -531 | 1 | 0 | 1853 | 782.1105 | 782.1105 | 782.1105 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -607.5515 | 174.559 | -3550 | -400 | -3775.441 | 94.39% | 51.81% | 95% | 0% | 1853 | -531
[5 empty] | 2019-08-26 | 33 | 5703.5 | 1441 | -467 | 1 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -534.3249 | 333.9356 | -3550 | -400 | -3616.0644 | 90.4% | 51.79% | 95% | 0% | 1908 | -467
[5 empty] | 2019-08-26 | 34 | 5704 | 1590 | -401 | 1 | 0 | 1991 | 998.2688 | 998.2688 | 998.2688 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -458.8101 | 539.4587 | -3550 | -400 | -3410.5413 | 85.26% | 51.79% | 95% | 0% | 1991 | -401
[5 empty] | 2019-08-26 | 35 | 5704.5 | 1798 | -332 | 1 | 0 | 2130 | 1215.9934 | 1215.9934 | 1215.9934 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -379.8627 | 836.1307 | -3550 | -400 | -3113.8693 | 77.85% | 51.79% | 95% | 0% | 2130 | -332
[5 empty] | 2019-08-26 | 36 | 5705 | 1951 | -258 | 1 | 0 | 2209 | 1339.7362 | 1339.7362 | 1339.7362 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -295.1945 | 1044.5417 | -3550 | -400 | -2905.4583 | 72.64% | 51.78% | 95% | 0% | 2209 | -258
[5 empty] | 2019-08-26 | 37 | 5705.5 | 2054 | -193 | 1 | 0 | 2247 | 1399.258 | 1399.258 | 1399.258 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -220.8238 | 1178.4342 | -3550 | -400 | -2771.5658 | 69.29% | 51.78% | 95% | 0% | 2247 | -193
[5 empty] | 2019-08-26 | 38 | 5706 | 2133 | -131 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -149.8856 | 1276.0006 | -3550 | -400 | -2673.9994 | 66.85% | 51.77% | 95% | 0% | 2264 | -131
[5 empty] | 2019-08-26 | 39 | 5706.5 | 2203 | -84 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 1045.2597 | 780 | 200 | 2025.2597 | 50.63% | 95% | 0% | -96.1098 | 1365.8028 | -3550 | -400 | -2584.1972 | 64.6% | 51.77% | 95% | 0% | 2287 | -84
[5 empty] | 2019-08-26 | 40 | 5707 | 2227 | -55 | 1 | 0 | 2282 | 1454.0808 | 1454.0808 | 1454.0808 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -62.9291 | 1391.1517 | -3550 | -400 | -2558.8483 | 63.97% | 51.76% | 95% | 0% | 2282 | -55
[5 empty] | 2019-08-26 | 41 | 5707.5 | 2272 | -47 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -53.7757 | 1458.2605 | -3550 | -400 | -2491.7395 | 62.29% | 51.75% | 95% | 0% | 2319 | -47
[5 empty] | 2019-08-26 | 42 | 5708 | 2298 | -45 | 1 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -51.4874 | 1498.1416 | -3550 | -400 | -2451.8584 | 61.3% | 51.74% | 95% | 0% | 2343 | -45
[5 empty] | 2019-08-26 | 43 | 5708.5 | 2246 | -44 | 0 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -50.3432 | 1416.2685 | -2750 | -200 | -1533.7315 | 38.34% | 51.74% | 95% | 0% | 2290 | -44
[5 empty] | 2019-08-26 | 44 | 5709 | 2189 | -42 | 0 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -48.0549 | 1326.1413 | -2750 | -200 | -1623.8587 | 40.6% | 51.74% | 95% | 0% | 2231 | -42
[5 empty] | 2019-08-26 | 45 | 5709.5 | 2092 | -41 | 0 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -46.9108 | 1173.7817 | -2750 | -200 | -1776.2183 | 44.41% | 51.74% | 95% | 0% | 2133 | -41
[5 empty] | 2019-08-26 | 46 | 5710 | 1981 | -39 | 0 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -44.6224 | 999.0709 | -2750 | -200 | -1950.9291 | 48.77% | 51.74% | 95% | 0% | 2020 | -39
[5 empty] | 2019-08-26 | 47 | 5710.5 | 1860 | -38 | 0 | 0 | 1898 | 852.5969 | 852.5969 | 852.5969 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -43.4783 | 809.1186 | -2750 | -200 | -2140.8814 | 53.52% | 51.73% | 95% | 0% | 1898 | -38
[5 empty] | 2019-08-26 | 48 | 5711 | 1759 | -37 | 0 | 0 | 1796 | 692.8277 | 692.8277 | 692.8277 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -42.3341 | 650.4936 | -2750 | -200 | -2299.5064 | 57.49% | 51.73% | 95% | 0% | 1796 | -37
[5 empty] | 2019-08-27 | 1 | 5711.5 | 1673 | -37 | 0 | 0 | 1710 | 558.1204 | 558.1204 | 558.1204 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -42.3341 | 515.7863 | -2750 | -200 | -2434.2137 | 60.86% | 51.73% | 95% | 0% | 1710 | -37
[5 empty] | 2019-08-27 | 2 | 5712 | 1626 | -36 | 0 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -41.1899 | 441.7449 | -2750 | -200 | -2508.2551 | 62.71% | 51.73% | 95% | 0% | 1662 | -36
[5 empty] | 2019-08-27 | 3 | 5712.5 | 1595 | -35 | 0 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -40.0458 | 392.7654 | -2750 | -200 | -2557.2346 | 63.93% | 51.73% | 95% | 0% | 1630 | -35
[5 empty] | 2019-08-27 | 4 | 5713 | 1567 | -34 | 0 | 0 | 1601 | 387.3866 | 387.3866 | 387.3866 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -38.9016 | 348.485 | -2750 | -200 | -2601.515 | 65.04% | 51.72% | 95% | 0% | 1601 | -34
[5 empty] | 2019-08-27 | 5 | 5713.5 | 1542 | -33 | 0 | 0 | 1575 | 346.6612 | 346.6612 | 346.6612 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -37.7574 | 308.9037 | -2750 | -200 | -2641.0963 | 66.03% | 51.72% | 95% | 0% | 1575 | -33
[5 empty] | 2019-08-27 | 6 | 5714 | 1523 | -31 | 0 | 0 | 1554 | 313.7675 | 313.7675 | 313.7675 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -35.4691 | 278.2984 | -2750 | -200 | -2671.7016 | 66.79% | 51.72% | 95% | 0% | 1554 | -31
[5 empty] | 2019-08-27 | 7 | 5714.5 | 1518 | -30 | 0 | 0 | 1548 | 304.3693 | 304.3693 | 304.3693 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -34.3249 | 270.0444 | -2750 | -200 | -2679.9556 | 67% | 51.72% | 95% | 0% | 1548 | -30
[5 empty] | 2019-08-27 | 8 | 5715 | 1518 | -29 | 0 | 0 | 1547 | 302.803 | 302.803 | 302.803 | 1043.6933 | 780 | 200 | 2023.6933 | 50.59% | 95% | 0% | -33.1808 | 269.6222 | -2750 | -200 | -2680.3778 | 67.01% | 51.72% | 95% | 0% | 1547 | -29
[5 empty] | 2019-08-27 | 9 | 5715.5 | 1519 | -29 | 0 | 0 | 1548 | 304.3693 | 304.3693 | 304.3693 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -33.1808 | 271.1886 | -2750 | -200 | -2678.8114 | 66.97% | 51.72% | 95% | 0% | 1548 | -29
[5 empty] | 2019-08-27 | 10 | 5716 | 1532 | -29 | 1 | 0 | 1561 | 324.7321 | 324.7321 | 324.7321 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -33.1808 | 291.5513 | -3550 | -400 | -3658.4487 | 91.46% | 51.71% | 95% | 0% | 1561 | -29
[5 empty] | 2019-08-27 | 11 | 5716.5 | 1594 | -29 | 1 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -33.1808 | 388.6659 | -3550 | -400 | -3561.3341 | 89.03% | 51.71% | 95% | 0% | 1623 | -29
[5 empty] | 2019-08-27 | 12 | 5717 | 1650 | -28 | 1 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -32.0366 | 475.9601 | -3550 | -400 | -3474.0399 | 86.85% | 51.7% | 95% | 0% | 1678 | -28
[5 empty] | 2019-08-27 | 13 | 5717.5 | 1803 | -30 | 1 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -34.3249 | 716.4582 | -3550 | -400 | -3233.5418 | 80.84% | 51.7% | 95% | 0% | 1833 | -30
[5 empty] | 2019-08-27 | 14 | 5718 | 1923 | -50 | 1 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -57.2082 | 912.866 | -3550 | -400 | -3037.134 | 75.93% | 51.69% | 95% | 0% | 1973 | -50
[5 empty] | 2019-08-27 | 15 | 5718.5 | 2068 | -84 | 1 | 0 | 2152 | 1250.4534 | 1250.4534 | 1250.4534 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -96.1098 | 1154.3436 | -3550 | -400 | -2795.6564 | 69.89% | 51.69% | 95% | 0% | 2152 | -84
[5 empty] | 2019-08-27 | 16 | 5719 | 2126 | -128 | 1 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -146.4531 | 1263.7695 | -3550 | -400 | -2686.2305 | 67.16% | 51.69% | 95% | 0% | 2254 | -128
[5 empty] | 2019-08-27 | 17 | 5719.5 | 2155 | -187 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -213.9588 | 1334.1038 | -3550 | -400 | -2615.8962 | 65.4% | 51.68% | 95% | 0% | 2342 | -187
[5 empty] | 2019-08-27 | 18 | 5720 | 2124 | -243 | 1 | 0 | 2367 | 1587.2218 | 1587.2218 | 1587.2218 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -278.032 | 1309.1897 | -3550 | -400 | -2640.8103 | 66.02% | 51.68% | 95% | 0% | 2367 | -243
[5 empty] | 2019-08-27 | 19 | 5720.5 | 2038 | -304 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -347.8261 | 1200.2366 | -3550 | -400 | -2749.7634 | 68.74% | 51.67% | 95% | 0% | 2342 | -304
[5 empty] | 2019-08-27 | 20 | 5721 | 1974 | -361 | 1 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -413.0435 | 1124.0546 | -3550 | -400 | -2825.9454 | 70.65% | 51.67% | 95% | 0% | 2335 | -361
[5 empty] | 2019-08-27 | 21 | 5721.5 | 1895 | -416 | 1 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -475.9725 | 1023.5328 | -3550 | -400 | -2926.4672 | 73.16% | 51.66% | 95% | 0% | 2311 | -416
[5 empty] | 2019-08-27 | 22 | 5722 | 1837 | -476 | 1 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 1042.127 | 780 | 200 | 2022.127 | 50.55% | 95% | 0% | -544.6224 | 958.0157 | -3550 | -400 | -2991.9843 | 74.8% | 51.66% | 95% | 0% | 2313 | -476
[5 empty] | 2019-08-27 | 23 | 5722.5 | 1791 | -516 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -590.389 | 902.8509 | -3550 | -400 | -3047.1491 | 76.18% | 51.65% | 95% | 0% | 2307 | -516
[5 empty] | 2019-08-27 | 24 | 5723 | 1785 | -538 | 1 | 0 | 2323 | 1518.3017 | 1518.3017 | 1518.3017 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -615.5606 | 902.7411 | -3550 | -400 | -3047.2589 | 76.18% | 51.64% | 95% | 0% | 2323 | -538
[5 empty] | 2019-08-27 | 25 | 5723.5 | 1788 | -547 | 1 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -625.8581 | 911.24 | -3550 | -400 | -3038.76 | 75.97% | 51.64% | 95% | 0% | 2335 | -547
[5 empty] | 2019-08-27 | 26 | 5724 | 1772 | -543 | 1 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -621.2815 | 884.4894 | -3550 | -400 | -3065.5106 | 76.64% | 51.63% | 95% | 0% | 2315 | -543
[5 empty] | 2019-08-27 | 27 | 5724.5 | 1774 | -545 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -623.5698 | 888.4665 | -3550 | -400 | -3061.5335 | 76.54% | 51.63% | 95% | 0% | 2319 | -545
[5 empty] | 2019-08-27 | 28 | 5725 | 1790 | -535 | 1 | 0 | 2325 | 1521.4345 | 1521.4345 | 1521.4345 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -612.1281 | 909.3063 | -3550 | -400 | -3040.6937 | 76.02% | 51.63% | 95% | 0% | 2325 | -535
[5 empty] | 2019-08-27 | 29 | 5725.5 | 1831 | -499 | 1 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -570.9382 | 958.3281 | -3550 | -400 | -2991.6719 | 74.79% | 51.61% | 95% | 0% | 2330 | -499
[5 empty] | 2019-08-27 | 30 | 5726 | 1881 | -461 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -527.46 | 1020.6027 | -3550 | -400 | -2929.3973 | 73.23% | 51.61% | 95% | 0% | 2342 | -461
[5 empty] | 2019-08-27 | 31 | 5726.5 | 1927 | -422 | 1 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -482.8375 | 1076.1897 | -3550 | -400 | -2873.8103 | 71.85% | 51.61% | 95% | 0% | 2349 | -422
[5 empty] | 2019-08-27 | 32 | 5727 | 2017 | -372 | 1 | 0 | 2389 | 1621.6818 | 1621.6818 | 1621.6818 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -425.6293 | 1196.0525 | -3550 | -400 | -2753.9475 | 68.85% | 51.6% | 95% | 0% | 2389 | -372
[5 empty] | 2019-08-27 | 33 | 5727.5 | 2125 | -331 | 1 | 0 | 2456 | 1726.6282 | 1726.6282 | 1726.6282 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -378.7185 | 1347.9097 | -3550 | -400 | -2602.0903 | 65.05% | 51.59% | 95% | 0% | 2456 | -331
[5 empty] | 2019-08-27 | 34 | 5728 | 2237 | -276 | 1 | 0 | 2513 | 1815.911 | 1815.911 | 1815.911 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -315.7895 | 1500.1215 | -3550 | -400 | -2449.8785 | 61.25% | 51.59% | 95% | 0% | 2513 | -276
[5 empty] | 2019-08-27 | 35 | 5728.5 | 2328 | -239 | 1 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -273.4554 | 1627.0393 | -3550 | -400 | -2322.9607 | 58.07% | 51.58% | 95% | 0% | 2567 | -239
[5 empty] | 2019-08-27 | 36 | 5729 | 2414 | -186 | 1 | 0 | 2600 | 1952.1847 | 1952.1847 | 1952.1847 | 1040.5606 | 780 | 200 | 2020.5606 | 50.51% | 95% | 0% | -212.8146 | 1739.37 | -3550 | -400 | -2210.63 | 55.27% | 51.57% | 95% | 0% | 2600 | -186
[5 empty] | 2019-08-27 | 37 | 5729.5 | 2486 | -122 | 1 | 0 | 2608 | 1964.7156 | 1964.7156 | 1964.7156 | 1038.9942 | 780 | 200 | 2018.9942 | 50.47% | 95% | 0% | -139.5881 | 1825.1275 | -3550 | -400 | -2124.8725 | 53.12% | 51.57% | 95% | 0% | 2608 | -122
[5 empty] | 2019-08-27 | 38 | 5730 | 2512 | -87 | 1 | 0 | 2599 | 1950.6183 | 1950.6183 | 1950.6183 | 1038.9942 | 780 | 200 | 2018.9942 | 50.47% | 95% | 0% | -99.5423 | 1851.076 | -3550 | -400 | -2098.924 | 52.47% | 51.56% | 95% | 0% | 2599 | -87
[5 empty] | 2019-08-27 | 39 | 5730.5 | 2529 | -65 | 1 | 0 | 2594 | 1942.7865 | 1942.7865 | 1942.7865 | 1038.9942 | 780 | 200 | 2018.9942 | 50.47% | 95% | 0% | -74.3707 | 1868.4158 | -3550 | -400 | -2081.5842 | 52.04% | 51.56% | 95% | 0% | 2594 | -65
[5 empty] | 2019-08-27 | 40 | 5731 | 2506 | -55 | 1 | 0 | 2561 | 1891.0965 | 1891.0965 | 1891.0965 | 1038.9942 | 780 | 200 | 2018.9942 | 50.47% | 95% | 0% | -62.9291 | 1828.1674 | -3550 | -400 | -2121.8326 | 53.05% | 51.55% | 95% | 0% | 2561 | -55
[5 empty] | 2019-08-27 | 41 | 5731.5 | 2559 | -53 | 0 | 0 | 2612 | 1970.981 | 1970.981 | 1970.981 | 1038.9942 | 780 | 200 | 2018.9942 | 50.47% | 95% | 0% | -60.6407 | 1910.3403 | -2750 | -200 | -1039.6597 | 25.99% | 51.55% | 95% | 0% | 2612 | -53
[5 empty] | 2019-08-27 | 42 | 5732 | 2519 | -53 | 1 | 0 | 2572 | 1908.3265 | 1908.3265 | 1908.3265 | 1038.9942 | 780 | 200 | 2018.9942 | 50.47% | 95% | 0% | -60.6407 | 1847.6857 | -3550 | -400 | -2102.3143 | 52.56% | 51.55% | 95% | 0% | 2572 | -53
[5 empty] | 2019-08-27 | 43 | 5732.5 | 2435 | -54 | 0 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 1038.9942 | 780 | 200 | 2018.9942 | 50.47% | 95% | 0% | -61.7849 | 1716.5333 | -2750 | -200 | -1233.4667 | 30.84% | 51.54% | 95% | 0% | 2489 | -54
[5 empty] | 2019-08-27 | 44 | 5733 | 2325 | -54 | 0 | 0 | 2379 | 1606.0181 | 1606.0181 | 1606.0181 | 1038.9942 | 780 | 200 | 2018.9942 | 50.47% | 95% | 0% | -61.7849 | 1544.2332 | -2750 | -200 | -1405.7668 | 35.14% | 51.54% | 95% | 0% | 2379 | -54
[5 empty] | 2019-08-27 | 45 | 5733.5 | 2187 | -57 | 0 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 1038.9942 | 780 | 200 | 2018.9942 | 50.47% | 95% | 0% | -65.2174 | 1329.3416 | -2750 | -200 | -1620.6584 | 40.52% | 51.54% | 95% | 0% | 2244 | -57
[5 empty] | 2019-08-27 | 46 | 5734 | 2061 | -59 | 0 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -67.5057 | 1132.824 | -2750 | -200 | -1817.176 | 45.43% | 51.53% | 95% | 0% | 2120 | -59
[5 empty] | 2019-08-27 | 47 | 5734.5 | 1925 | -63 | 0 | 0 | 1988 | 993.5697 | 993.5697 | 993.5697 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -72.0824 | 921.4873 | -2750 | -200 | -2028.5127 | 50.71% | 51.53% | 95% | 0% | 1988 | -63
[5 empty] | 2019-08-27 | 48 | 5735 | 1823 | -66 | 0 | 0 | 1889 | 838.4996 | 838.4996 | 838.4996 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -75.5149 | 762.9847 | -2750 | -200 | -2187.0153 | 54.68% | 51.51% | 95% | 0% | 1889 | -66
[5 empty] | 2019-08-28 | 1 | 5735.5 | 1727 | -71 | 0 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -81.2357 | 614.7247 | -2750 | -200 | -2335.2753 | 58.38% | 51.51% | 95% | 0% | 1798 | -71
[5 empty] | 2019-08-28 | 2 | 5736 | 1663 | -75 | 0 | 0 | 1738 | 601.9786 | 601.9786 | 601.9786 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -85.8124 | 516.1662 | -2750 | -200 | -2433.8338 | 60.85% | 51.51% | 95% | 0% | 1738 | -75
[5 empty] | 2019-08-28 | 3 | 5736.5 | 1613 | -79 | 0 | 0 | 1692 | 529.9258 | 529.9258 | 529.9258 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -90.389 | 439.5368 | -2750 | -200 | -2510.4632 | 62.76% | 51.51% | 95% | 0% | 1692 | -79
[5 empty] | 2019-08-28 | 4 | 5737 | 1574 | -83 | 0 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -94.9657 | 380.1374 | -2750 | -200 | -2569.8626 | 64.25% | 51.51% | 95% | 0% | 1657 | -83
[5 empty] | 2019-08-28 | 5 | 5737.5 | 1540 | -84 | 0 | 0 | 1624 | 423.413 | 423.413 | 423.413 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -96.1098 | 327.3032 | -2750 | -200 | -2622.6968 | 65.57% | 51.5% | 95% | 0% | 1624 | -84
[5 empty] | 2019-08-28 | 6 | 5738 | 1510 | -86 | 0 | 0 | 1596 | 379.5548 | 379.5548 | 379.5548 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -98.3982 | 281.1567 | -2750 | -200 | -2668.8433 | 66.72% | 51.5% | 95% | 0% | 1596 | -86
[5 empty] | 2019-08-28 | 7 | 5738.5 | 1493 | -88 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -100.6865 | 255.3729 | -2750 | -200 | -2694.6271 | 67.37% | 51.5% | 95% | 0% | 1581 | -88
[5 empty] | 2019-08-28 | 8 | 5739 | 1474 | -89 | 0 | 0 | 1563 | 327.8648 | 327.8648 | 327.8648 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -101.8307 | 226.0341 | -2750 | -200 | -2723.9659 | 68.1% | 51.5% | 95% | 0% | 1563 | -89
[5 empty] | 2019-08-28 | 9 | 5739.5 | 1479 | -91 | 0 | 0 | 1570 | 338.8293 | 338.8293 | 338.8293 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -104.119 | 234.7104 | -2750 | -200 | -2715.2896 | 67.88% | 51.5% | 95% | 0% | 1570 | -91
[5 empty] | 2019-08-28 | 10 | 5740 | 1500 | -93 | 1 | 0 | 1593 | 374.8557 | 374.8557 | 374.8557 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -106.4073 | 268.4484 | -3550 | -400 | -3681.5516 | 92.04% | 51.49% | 95% | 0% | 1593 | -93
[5 empty] | 2019-08-28 | 11 | 5740.5 | 1558 | -94 | 1 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 1037.4279 | 780 | 200 | 2017.4279 | 50.44% | 95% | 0% | -107.5515 | 359.7197 | -3550 | -400 | -3590.2803 | 89.76% | 51.49% | 95% | 0% | 1652 | -94
[5 empty] | 2019-08-28 | 12 | 5741 | 1630 | -95 | 1 | 0 | 1725 | 581.6158 | 581.6158 | 581.6158 | 1035.8615 | 780 | 200 | 2015.8615 | 50.4% | 95% | 0% | -108.6957 | 472.9202 | -3550 | -400 | -3477.0798 | 86.93% | 51.49% | 95% | 0% | 1725 | -95
[5 empty] | 2019-08-28 | 13 | 5741.5 | 1766 | -96 | 1 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 1035.8615 | 780 | 200 | 2015.8615 | 50.4% | 95% | 0% | -109.8398 | 686.3679 | -3550 | -400 | -3263.6321 | 81.59% | 51.49% | 95% | 0% | 1862 | -96
[5 empty] | 2019-08-28 | 14 | 5742 | 1889 | -104 | 1 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 1035.8615 | 780 | 200 | 2015.8615 | 50.4% | 95% | 0% | -118.9931 | 882.4083 | -3550 | -400 | -3067.5917 | 76.69% | 51.48% | 95% | 0% | 1993 | -104
[5 empty] | 2019-08-28 | 15 | 5742.5 | 2051 | -124 | 1 | 0 | 2175 | 1286.4798 | 1286.4798 | 1286.4798 | 1035.8615 | 780 | 200 | 2015.8615 | 50.4% | 95% | 0% | -141.8764 | 1144.6034 | -3550 | -400 | -2805.3966 | 70.13% | 51.48% | 95% | 0% | 2175 | -124
[5 empty] | 2019-08-28 | 16 | 5743 | 2132 | -149 | 1 | 0 | 2281 | 1452.5144 | 1452.5144 | 1452.5144 | 1035.8615 | 780 | 200 | 2015.8615 | 50.4% | 95% | 0% | -170.4805 | 1282.0339 | -3550 | -400 | -2667.9661 | 66.7% | 51.47% | 95% | 0% | 2281 | -149
[5 empty] | 2019-08-28 | 17 | 5743.5 | 2184 | -189 | 1 | 0 | 2373 | 1596.62 | 1596.62 | 1596.62 | 1035.8615 | 780 | 200 | 2015.8615 | 50.4% | 95% | 0% | -216.2471 | 1380.3728 | -3550 | -400 | -2569.6272 | 64.24% | 51.47% | 95% | 0% | 2373 | -189
[5 empty] | 2019-08-28 | 18 | 5744 | 2182 | -235 | 1 | 0 | 2417 | 1665.54 | 1665.54 | 1665.54 | 1035.8615 | 780 | 200 | 2015.8615 | 50.4% | 95% | 0% | -268.8787 | 1396.6613 | -3550 | -400 | -2553.3387 | 63.83% | 51.46% | 95% | 0% | 2417 | -235
[5 empty] | 2019-08-28 | 19 | 5744.5 | 2148 | -287 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 1035.8615 | 780 | 200 | 2015.8615 | 50.4% | 95% | 0% | -328.3753 | 1365.3593 | -3550 | -400 | -2584.6407 | 64.62% | 51.46% | 95% | 0% | 2435 | -287
[5 empty] | 2019-08-28 | 20 | 5745 | 2084 | -332 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 1035.8615 | 780 | 200 | 2015.8615 | 50.4% | 95% | 0% | -379.8627 | 1284.1109 | -3550 | -400 | -2665.8891 | 66.65% | 51.45% | 95% | 0% | 2416 | -332
[5 empty] | 2019-08-28 | 21 | 5745.5 | 2009 | -377 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 1035.8615 | 780 | 200 | 2015.8615 | 50.4% | 95% | 0% | -431.3501 | 1185.6326 | -3550 | -400 | -2764.3674 | 69.11% | 51.44% | 95% | 0% | 2386 | -377
[5 empty] | 2019-08-28 | 22 | 5746 | 1959 | -411 | 1 | 0 | 2370 | 1591.9209 | 1591.9209 | 1591.9209 | 1035.8615 | 780 | 200 | 2015.8615 | 50.4% | 95% | 0% | -470.2517 | 1121.6691 | -3550 | -400 | -2828.3309 | 70.71% | 51.44% | 95% | 0% | 2370 | -411
[5 empty] | 2019-08-28 | 23 | 5746.5 | 1942 | -416 | 1 | 0 | 2358 | 1573.1245 | 1573.1245 | 1573.1245 | 1034.2951 | 780 | 200 | 2014.2951 | 50.36% | 95% | 0% | -475.9725 | 1097.1519 | -3550 | -400 | -2852.8481 | 71.32% | 51.44% | 95% | 0% | 2358 | -416
[5 empty] | 2019-08-28 | 24 | 5747 | 1882 | -463 | 1 | 0 | 2345 | 1552.7617 | 1552.7617 | 1552.7617 | 1034.2951 | 780 | 200 | 2014.2951 | 50.36% | 95% | 0% | -529.7483 | 1023.0135 | -3550 | -400 | -2926.9865 | 73.17% | 51.43% | 95% | 0% | 2345 | -463
[5 empty] | 2019-08-28 | 25 | 5747.5 | 1863 | -493 | 1 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 1034.2951 | 780 | 200 | 2014.2951 | 50.36% | 95% | 0% | -564.0732 | 1005.9185 | -3550 | -400 | -2944.0815 | 73.6% | 51.43% | 95% | 0% | 2356 | -493
[5 empty] | 2019-08-28 | 26 | 5748 | 1823 | -507 | 1 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 1034.2951 | 780 | 200 | 2014.2951 | 50.36% | 95% | 0% | -580.0915 | 949.1747 | -3550 | -400 | -3000.8253 | 75.02% | 51.43% | 95% | 0% | 2330 | -507
[5 empty] | 2019-08-28 | 27 | 5748.5 | 1832 | -486 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 1034.2951 | 780 | 200 | 2014.2951 | 50.36% | 95% | 0% | -556.0641 | 954.4058 | -3550 | -400 | -2995.5942 | 74.89% | 51.42% | 95% | 0% | 2318 | -486
[5 empty] | 2019-08-28 | 28 | 5749 | 1847 | -469 | 1 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 1034.2951 | 780 | 200 | 2014.2951 | 50.36% | 95% | 0% | -536.6133 | 970.7239 | -3550 | -400 | -2979.2761 | 74.48% | 51.42% | 95% | 0% | 2316 | -469
[5 empty] | 2019-08-28 | 29 | 5749.5 | 1873 | -446 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 1034.2951 | 780 | 200 | 2014.2951 | 50.36% | 95% | 0% | -510.2975 | 1001.7388 | -3550 | -400 | -2948.2612 | 73.71% | 51.42% | 95% | 0% | 2319 | -446
[5 empty] | 2019-08-28 | 30 | 5750 | 1923 | -400 | 1 | 0 | 2323 | 1518.3017 | 1518.3017 | 1518.3017 | 1034.2951 | 780 | 200 | 2014.2951 | 50.36% | 95% | 0% | -457.6659 | 1060.6358 | -3550 | -400 | -2889.3642 | 72.23% | 51.4% | 95% | 0% | 2323 | -400
[5 empty] | 2019-08-28 | 31 | 5750.5 | 1997 | -341 | 1 | 0 | 2338 | 1541.7972 | 1541.7972 | 1541.7972 | 1034.2951 | 780 | 200 | 2014.2951 | 50.36% | 95% | 0% | -390.1602 | 1151.637 | -3550 | -400 | -2798.363 | 69.96% | 51.4% | 95% | 0% | 2338 | -341
[5 empty] | 2019-08-28 | 32 | 5751 | 2040 | -328 | 1 | 0 | 2368 | 1588.7881 | 1588.7881 | 1588.7881 | 1034.2951 | 780 | 200 | 2014.2951 | 50.36% | 95% | 0% | -375.286 | 1213.5021 | -3550 | -400 | -2736.4979 | 68.41% | 51.4% | 95% | 0% | 2368 | -328
[5 empty] | 2019-08-28 | 33 | 5751.5 | 2143 | -269 | 1 | 0 | 2412 | 1657.7082 | 1657.7082 | 1657.7082 | 1034.2951 | 780 | 200 | 2014.2951 | 50.36% | 95% | 0% | -307.7803 | 1349.9278 | -3550 | -400 | -2600.0722 | 65% | 51.4% | 95% | 0% | 2412 | -269
[5 empty] | 2019-08-28 | 34 | 5752 | 2239 | -237 | 1 | 0 | 2476 | 1757.9555 | 1757.9555 | 1757.9555 | 1034.2951 | 780 | 200 | 2014.2951 | 50.36% | 95% | 0% | -271.167 | 1486.7884 | -3550 | -400 | -2463.2116 | 61.58% | 51.4% | 95% | 0% | 2476 | -237
[5 empty] | 2019-08-28 | 35 | 5752.5 | 2319 | -197 | 1 | 0 | 2516 | 1820.6101 | 1820.6101 | 1820.6101 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -225.4005 | 1595.2096 | -3550 | -400 | -2354.7904 | 58.87% | 51.4% | 95% | 0% | 2516 | -197
[5 empty] | 2019-08-28 | 36 | 5753 | 2348 | -182 | 1 | 0 | 2530 | 1842.5392 | 1842.5392 | 1842.5392 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -208.238 | 1634.3012 | -3550 | -400 | -2315.6988 | 57.89% | 51.39% | 95% | 0% | 2530 | -182
[5 empty] | 2019-08-28 | 37 | 5753.5 | 2398 | -151 | 1 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -172.7689 | 1699.5312 | -3550 | -400 | -2250.4688 | 56.26% | 51.39% | 95% | 0% | 2549 | -151
[5 empty] | 2019-08-28 | 38 | 5754 | 2423 | -123 | 1 | 0 | 2546 | 1867.601 | 1867.601 | 1867.601 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -140.7323 | 1726.8687 | -3550 | -400 | -2223.1313 | 55.58% | 51.39% | 95% | 0% | 2546 | -123
[5 empty] | 2019-08-28 | 39 | 5754.5 | 2416 | -100 | 1 | 0 | 2516 | 1820.6101 | 1820.6101 | 1820.6101 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -114.4165 | 1706.1936 | -3550 | -400 | -2243.8064 | 56.1% | 51.38% | 95% | 0% | 2516 | -100
[5 empty] | 2019-08-28 | 40 | 5755 | 2389 | -81 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -92.6773 | 1655.88 | -3550 | -400 | -2294.12 | 57.35% | 51.38% | 95% | 0% | 2470 | -81
[5 empty] | 2019-08-28 | 41 | 5755.5 | 2415 | -75 | 1 | 0 | 2490 | 1779.8846 | 1779.8846 | 1779.8846 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -85.8124 | 1694.0722 | -3550 | -400 | -2255.9278 | 56.4% | 51.38% | 95% | 0% | 2490 | -75
[5 empty] | 2019-08-28 | 42 | 5756 | 2402 | -74 | 1 | 0 | 2476 | 1757.9555 | 1757.9555 | 1757.9555 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -84.6682 | 1673.2873 | -3550 | -400 | -2276.7127 | 56.92% | 51.38% | 95% | 0% | 2476 | -74
[5 empty] | 2019-08-28 | 43 | 5756.5 | 2342 | -73 | 0 | 0 | 2415 | 1662.4073 | 1662.4073 | 1662.4073 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -83.524 | 1578.8832 | -2750 | -200 | -1371.1168 | 34.28% | 51.37% | 95% | 0% | 2415 | -73
[5 empty] | 2019-08-28 | 44 | 5757 | 2218 | -73 | 0 | 0 | 2291 | 1468.1781 | 1468.1781 | 1468.1781 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -83.524 | 1384.654 | -2750 | -200 | -1565.346 | 39.13% | 51.37% | 95% | 0% | 2291 | -73
[5 empty] | 2019-08-28 | 45 | 5757.5 | 2094 | -73 | 0 | 0 | 2167 | 1273.9489 | 1273.9489 | 1273.9489 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -83.524 | 1190.4249 | -2750 | -200 | -1759.5751 | 43.99% | 51.37% | 95% | 0% | 2167 | -73
[5 empty] | 2019-08-28 | 46 | 5758 | 1946 | -74 | 0 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -84.6682 | 959.0251 | -2750 | -200 | -1990.9749 | 49.77% | 51.37% | 95% | 0% | 2020 | -74
[5 empty] | 2019-08-28 | 47 | 5758.5 | 1836 | -74 | 0 | 0 | 1910 | 871.3932 | 871.3932 | 871.3932 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -84.6682 | 786.725 | -2750 | -200 | -2163.275 | 54.08% | 51.37% | 95% | 0% | 1910 | -74
[5 empty] | 2019-08-28 | 48 | 5759 | 1731 | -74 | 0 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 1032.7288 | 780 | 200 | 2012.7288 | 50.32% | 95% | 0% | -84.6682 | 622.2568 | -2750 | -200 | -2327.7432 | 58.19% | 51.36% | 95% | 0% | 1805 | -74
[5 empty] | 2019-08-29 | 1 | 5759.5 | 1634 | -75 | 0 | 0 | 1709 | 556.554 | 556.554 | 556.554 | 1031.1624 | 780 | 200 | 2011.1624 | 50.28% | 95% | 0% | -85.8124 | 470.7416 | -2750 | -200 | -2479.2584 | 61.98% | 51.36% | 95% | 0% | 1709 | -75
[5 empty] | 2019-08-29 | 2 | 5760 | 1582 | -75 | 1 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 1031.1624 | 780 | 200 | 2011.1624 | 50.28% | 95% | 0% | -85.8124 | 389.2907 | -3550 | -400 | -3560.7093 | 89.02% | 51.36% | 95% | 0% | 1657 | -75
[5 empty] | 2019-08-29 | 3 | 5760.5 | 1536 | -77 | 1 | 0 | 1613 | 406.183 | 406.183 | 406.183 | 1031.1624 | 780 | 200 | 2011.1624 | 50.28% | 95% | 0% | -88.1007 | 318.0823 | -3550 | -400 | -3631.9177 | 90.8% | 51.34% | 95% | 0% | 1613 | -77
[5 empty] | 2019-08-29 | 4 | 5761 | 1515 | -79 | 1 | 0 | 1594 | 376.4221 | 376.4221 | 376.4221 | 1031.1624 | 780 | 200 | 2011.1624 | 50.28% | 95% | 0% | -90.389 | 286.0331 | -3550 | -400 | -3663.9669 | 91.6% | 51.34% | 95% | 0% | 1594 | -79
[5 empty] | 2019-08-29 | 5 | 5761.5 | 1484 | -81 | 1 | 0 | 1565 | 330.9975 | 330.9975 | 330.9975 | 1031.1624 | 780 | 200 | 2011.1624 | 50.28% | 95% | 0% | -92.6773 | 238.3202 | -3550 | -400 | -3711.6798 | 92.79% | 51.33% | 95% | 0% | 1565 | -81
[5 empty] | 2019-08-29 | 6 | 5762 | 1462 | -84 | 1 | 0 | 1546 | 301.2366 | 301.2366 | 301.2366 | 1031.1624 | 780 | 200 | 2011.1624 | 50.28% | 95% | 0% | -96.1098 | 205.1268 | -3550 | -400 | -3744.8732 | 93.62% | 51.33% | 95% | 0% | 1546 | -84
[5 empty] | 2019-08-29 | 7 | 5762.5 | 1441 | -85 | 1 | 0 | 1526 | 269.9093 | 269.9093 | 269.9093 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -97.254 | 172.6553 | -3550 | -400 | -3777.3447 | 94.43% | 51.33% | 95% | 0% | 1526 | -85
[5 empty] | 2019-08-29 | 8 | 5763 | 1430 | -87 | 1 | 0 | 1517 | 255.812 | 255.812 | 255.812 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -99.5423 | 156.2697 | -3550 | -400 | -3793.7303 | 94.84% | 51.32% | 95% | 0% | 1517 | -87
[5 empty] | 2019-08-29 | 9 | 5763.5 | 1432 | -89 | 1 | 0 | 1521 | 262.0775 | 262.0775 | 262.0775 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -101.8307 | 160.2468 | -3550 | -400 | -3789.7532 | 94.74% | 51.32% | 95% | 0% | 1521 | -89
[5 empty] | 2019-08-29 | 10 | 5764 | 1443 | -90 | 1 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -102.9748 | 177.899 | -3550 | -400 | -3772.101 | 94.3% | 51.32% | 95% | 0% | 1533 | -90
[5 empty] | 2019-08-29 | 11 | 5764.5 | 1496 | -92 | 1 | 0 | 1588 | 367.0239 | 367.0239 | 367.0239 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -105.2632 | 261.7607 | -3550 | -400 | -3688.2393 | 92.21% | 51.32% | 95% | 0% | 1588 | -92
[5 empty] | 2019-08-29 | 12 | 5765 | 1568 | -95 | 1 | 0 | 1663 | 484.5012 | 484.5012 | 484.5012 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -108.6957 | 375.8056 | -3550 | -400 | -3574.1944 | 89.35% | 51.32% | 95% | 0% | 1663 | -95
[5 empty] | 2019-08-29 | 13 | 5765.5 | 1710 | -98 | 1 | 0 | 1808 | 711.6241 | 711.6241 | 711.6241 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -112.1281 | 599.4959 | -3550 | -400 | -3350.5041 | 83.76% | 51.31% | 95% | 0% | 1808 | -98
[5 empty] | 2019-08-29 | 14 | 5766 | 1832 | -116 | 1 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -132.7231 | 798.192 | -3550 | -400 | -3151.808 | 78.8% | 51.31% | 95% | 0% | 1948 | -116
[5 empty] | 2019-08-29 | 15 | 5766.5 | 1941 | -158 | 1 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -180.778 | 986.6581 | -3550 | -400 | -2963.3419 | 74.08% | 51.3% | 95% | 0% | 2099 | -158
[5 empty] | 2019-08-29 | 16 | 5767 | 1993 | -212 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -242.5629 | 1090.9078 | -3550 | -400 | -2859.0922 | 71.48% | 51.3% | 95% | 0% | 2205 | -212
[5 empty] | 2019-08-29 | 17 | 5767.5 | 1975 | -279 | 1 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -319.222 | 1091.0006 | -3550 | -400 | -2858.9994 | 71.47% | 51.3% | 95% | 0% | 2254 | -279
[5 empty] | 2019-08-29 | 18 | 5768 | 1870 | -357 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -408.4668 | 959.4639 | -3550 | -400 | -2990.5361 | 74.76% | 51.3% | 95% | 0% | 2227 | -357
[5 empty] | 2019-08-29 | 19 | 5768.5 | 1763 | -446 | 1 | 0 | 2209 | 1339.7362 | 1339.7362 | 1339.7362 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -510.2975 | 829.4387 | -3550 | -400 | -3120.5613 | 78.01% | 51.3% | 95% | 0% | 2209 | -446
[5 empty] | 2019-08-29 | 20 | 5769 | 1633 | -528 | 1 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -604.119 | 660.4317 | -3550 | -400 | -3289.5683 | 82.24% | 51.3% | 95% | 0% | 2161 | -528
[5 empty] | 2019-08-29 | 21 | 5769.5 | 1527 | -578 | 1 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 1029.596 | 780 | 200 | 2009.596 | 50.24% | 95% | 0% | -661.3272 | 515.5071 | -3550 | -400 | -3434.4929 | 85.86% | 51.29% | 95% | 0% | 2105 | -578
[5 empty] | 2019-08-29 | 22 | 5770 | 1439 | -620 | 1 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -709.3822 | 395.3994 | -3550 | -400 | -3554.6006 | 88.87% | 51.28% | 95% | 0% | 2059 | -620
[5 empty] | 2019-08-29 | 23 | 5770.5 | 1367 | -658 | 1 | 0 | 2025 | 1051.5251 | 1051.5251 | 1051.5251 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -752.8604 | 298.6647 | -3550 | -400 | -3651.3353 | 91.28% | 51.28% | 95% | 0% | 2025 | -658
[5 empty] | 2019-08-29 | 24 | 5771 | 1330 | -693 | 1 | 0 | 2023 | 1048.3924 | 1048.3924 | 1048.3924 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -792.9062 | 255.4862 | -3550 | -400 | -3694.5138 | 92.36% | 51.28% | 95% | 0% | 2023 | -693
[5 empty] | 2019-08-29 | 25 | 5771.5 | 1310 | -710 | 1 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -812.357 | 231.3363 | -3550 | -400 | -3718.6637 | 92.97% | 51.28% | 95% | 0% | 2020 | -710
[5 empty] | 2019-08-29 | 26 | 5772 | 1311 | -703 | 1 | 0 | 2014 | 1034.2951 | 1034.2951 | 1034.2951 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -804.3478 | 229.9473 | -3550 | -400 | -3720.0527 | 93% | 51.28% | 95% | 0% | 2014 | -703
[5 empty] | 2019-08-29 | 27 | 5772.5 | 1330 | -670 | 1 | 0 | 2000 | 1012.366 | 1012.366 | 1012.366 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -766.5904 | 245.7756 | -3550 | -400 | -3704.2244 | 92.61% | 51.27% | 95% | 0% | 2000 | -670
[5 empty] | 2019-08-29 | 28 | 5773 | 1376 | -619 | 1 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -708.238 | 296.2962 | -3550 | -400 | -3653.7038 | 91.34% | 51.27% | 95% | 0% | 1995 | -619
[5 empty] | 2019-08-29 | 29 | 5773.5 | 1372 | -615 | 1 | 0 | 1987 | 992.0033 | 992.0033 | 992.0033 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -703.6613 | 288.342 | -3550 | -400 | -3661.658 | 91.54% | 51.27% | 95% | 0% | 1987 | -615
[5 empty] | 2019-08-29 | 30 | 5774 | 1402 | -598 | 1 | 0 | 2000 | 1012.366 | 1012.366 | 1012.366 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -684.2105 | 328.1555 | -3550 | -400 | -3621.8445 | 90.55% | 51.27% | 95% | 0% | 2000 | -598
[5 empty] | 2019-08-29 | 31 | 5774.5 | 1458 | -565 | 1 | 0 | 2023 | 1048.3924 | 1048.3924 | 1048.3924 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -646.4531 | 401.9393 | -3550 | -400 | -3548.0607 | 88.7% | 51.26% | 95% | 0% | 2023 | -565
[5 empty] | 2019-08-29 | 32 | 5775 | 1519 | -539 | 1 | 0 | 2058 | 1103.2152 | 1103.2152 | 1103.2152 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -616.7048 | 486.5104 | -3550 | -400 | -3463.4896 | 86.59% | 51.26% | 95% | 0% | 2058 | -539
[5 empty] | 2019-08-29 | 33 | 5775.5 | 1562 | -513 | 1 | 0 | 2075 | 1129.8434 | 1129.8434 | 1129.8434 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -586.9565 | 542.8868 | -3550 | -400 | -3407.1132 | 85.18% | 51.26% | 95% | 0% | 2075 | -513
[5 empty] | 2019-08-29 | 34 | 5776 | 1706 | -439 | 1 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -502.2883 | 737.2005 | -3550 | -400 | -3212.7995 | 80.32% | 51.25% | 95% | 0% | 2145 | -439
[5 empty] | 2019-08-29 | 35 | 5776.5 | 1832 | -395 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 1028.0297 | 780 | 200 | 2008.0297 | 50.2% | 95% | 0% | -451.9451 | 915.9857 | -3550 | -400 | -3034.0143 | 75.85% | 51.25% | 95% | 0% | 2227 | -395
[5 empty] | 2019-08-29 | 36 | 5777 | 1923 | -336 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -384.4394 | 1033.6151 | -3550 | -400 | -2916.3849 | 72.91% | 51.25% | 95% | 0% | 2259 | -336
[5 empty] | 2019-08-29 | 37 | 5777.5 | 2027 | -273 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -312.357 | 1169.9184 | -3550 | -400 | -2780.0816 | 69.5% | 51.24% | 95% | 0% | 2300 | -273
[5 empty] | 2019-08-29 | 38 | 5778 | 2112 | -218 | 1 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -249.4279 | 1279.8384 | -3550 | -400 | -2670.1616 | 66.75% | 51.24% | 95% | 0% | 2330 | -218
[5 empty] | 2019-08-29 | 39 | 5778.5 | 2178 | -177 | 1 | 0 | 2355 | 1568.4254 | 1568.4254 | 1568.4254 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -202.5172 | 1365.9082 | -3550 | -400 | -2584.0918 | 64.6% | 51.24% | 95% | 0% | 2355 | -177
[5 empty] | 2019-08-29 | 40 | 5779 | 2191 | -156 | 1 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -178.4897 | 1377.4048 | -3550 | -400 | -2572.5952 | 64.31% | 51.24% | 95% | 0% | 2347 | -156
[5 empty] | 2019-08-29 | 41 | 5779.5 | 2206 | -153 | 1 | 0 | 2359 | 1574.6908 | 1574.6908 | 1574.6908 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -175.0572 | 1399.6336 | -3550 | -400 | -2550.3664 | 63.76% | 51.24% | 95% | 0% | 2359 | -153
[5 empty] | 2019-08-29 | 42 | 5780 | 2199 | -152 | 1 | 0 | 2351 | 1562.1599 | 1562.1599 | 1562.1599 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -173.913 | 1388.2469 | -3550 | -400 | -2561.7531 | 64.04% | 51.23% | 95% | 0% | 2351 | -152
[5 empty] | 2019-08-29 | 43 | 5780.5 | 2126 | -152 | 0 | 0 | 2278 | 1447.8153 | 1447.8153 | 1447.8153 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -173.913 | 1273.9023 | -2750 | -200 | -1676.0977 | 41.9% | 51.22% | 95% | 0% | 2278 | -152
[5 empty] | 2019-08-29 | 44 | 5781 | 2008 | -152 | 0 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -173.913 | 1089.0713 | -2750 | -200 | -1860.9287 | 46.52% | 51.22% | 95% | 0% | 2160 | -152
[5 empty] | 2019-08-29 | 45 | 5781.5 | 1880 | -154 | 0 | 0 | 2034 | 1065.6224 | 1065.6224 | 1065.6224 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -176.2014 | 889.4211 | -2750 | -200 | -2060.5789 | 51.51% | 51.21% | 95% | 0% | 2034 | -154
[5 empty] | 2019-08-29 | 46 | 5782 | 1759 | -155 | 0 | 0 | 1914 | 877.6587 | 877.6587 | 877.6587 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -177.3455 | 700.3132 | -2750 | -200 | -2249.6868 | 56.24% | 51.21% | 95% | 0% | 1914 | -155
[5 empty] | 2019-08-29 | 47 | 5782.5 | 1620 | -156 | 0 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -178.4897 | 483.0107 | -2750 | -200 | -2466.9893 | 61.67% | 51.19% | 95% | 0% | 1776 | -156
[5 empty] | 2019-08-29 | 48 | 5783 | 1515 | -156 | 0 | 0 | 1671 | 497.0322 | 497.0322 | 497.0322 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -178.4897 | 318.5424 | -2750 | -200 | -2631.4576 | 65.79% | 51.19% | 95% | 0% | 1671 | -156
[5 empty] | 2019-08-30 | 1 | 5783.5 | 1427 | -155 | 0 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -177.3455 | 180.2802 | -2750 | -200 | -2769.7198 | 69.24% | 51.19% | 95% | 0% | 1582 | -155
[5 empty] | 2019-08-30 | 2 | 5784 | 1366 | -155 | 0 | 0 | 1521 | 262.0775 | 262.0775 | 262.0775 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -177.3455 | 84.732 | -2750 | -200 | -2865.268 | 71.63% | 51.17% | 95% | 0% | 1521 | -155
[5 empty] | 2019-08-30 | 3 | 5784.5 | 1319 | -155 | 1 | 0 | 1474 | 188.4584 | 188.4584 | 188.4584 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -177.3455 | 11.1128 | -3550 | -400 | -3938.8872 | 98.47% | 51.17% | 95% | 0% | 1474 | -155
[5 empty] | 2019-08-30 | 4 | 5785 | 1303 | -154 | 1 | 0 | 1457 | 161.8302 | 161.8302 | 161.8302 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -176.2014 | -14.3712 | -3550 | -400 | -3964.3712 | 99.11% | 51.17% | 95% | 0% | 1457 | -154
[5 empty] | 2019-08-30 | 5 | 5785.5 | 1270 | -154 | 1 | 0 | 1424 | 110.1401 | 110.1401 | 110.1401 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -176.2014 | -66.0612 | -3550 | -400 | -4016.0612 | 100.4% | 51.17% | 95% | 0% | 1424 | -154
[5 empty] | 2019-08-30 | 6 | 5786 | 1239 | -155 | 1 | 0 | 1394 | 63.1492 | 63.1492 | 63.1492 | 1026.4633 | 780 | 200 | 2006.4633 | 50.16% | 95% | 0% | -177.3455 | -114.1963 | -3550 | -400 | -4064.1963 | 101.6% | 51.17% | 95% | 0% | 1394 | -155
[5 empty] | 2019-08-30 | 7 | 5786.5 | 1232 | -155 | 1 | 0 | 1387 | 52.1847 | 52.1847 | 52.1847 | 1024.8969 | 780 | 200 | 2004.8969 | 50.12% | 95% | 0% | -177.3455 | -125.1609 | -3550 | -400 | -4075.1609 | 101.9% | 51.17% | 95% | 0% | 1387 | -155
[5 empty] | 2019-08-30 | 8 | 5787 | 1224 | -155 | 1 | 0 | 1379 | 39.6538 | 39.6538 | 39.6538 | 1024.8969 | 780 | 200 | 2004.8969 | 50.12% | 95% | 0% | -177.3455 | -137.6918 | -3550 | -400 | -4087.6918 | 102.2% | 51.17% | 95% | 0% | 1379 | -155
[5 empty] | 2019-08-30 | 9 | 5787.5 | 1226 | -155 | 1 | 0 | 1381 | 42.7865 | 42.7865 | 42.7865 | 1024.8969 | 780 | 200 | 2004.8969 | 50.12% | 95% | 0% | -177.3455 | -134.5591 | -3550 | -400 | -4084.5591 | 102.1% | 51.16% | 95% | 0% | 1381 | -155
[5 empty] | 2019-08-30 | 10 | 5788 | 1235 | -154 | 1 | 0 | 1389 | 55.3174 | 55.3174 | 55.3174 | 1024.8969 | 780 | 200 | 2004.8969 | 50.12% | 95% | 0% | -176.2014 | -120.884 | -3550 | -400 | -4070.884 | 101.8% | 51.15% | 95% | 0% | 1389 | -154
[5 empty] | 2019-08-30 | 11 | 5788.5 | 1287 | -154 | 1 | 0 | 1441 | 136.7683 | 136.7683 | 136.7683 | 1024.8969 | 780 | 200 | 2004.8969 | 50.12% | 95% | 0% | -176.2014 | -39.433 | -3550 | -400 | -3989.433 | 99.74% | 51.15% | 95% | 0% | 1441 | -154
[5 empty] | 2019-08-30 | 12 | 5789 | 1360 | -156 | 1 | 0 | 1516 | 254.2457 | 254.2457 | 254.2457 | 1024.8969 | 780 | 200 | 2004.8969 | 50.12% | 95% | 0% | -178.4897 | 75.756 | -3550 | -400 | -3874.244 | 96.86% | 51.14% | 95% | 0% | 1516 | -156
[5 empty] | 2019-08-30 | 13 | 5789.5 | 1492 | -157 | 1 | 0 | 1649 | 462.5721 | 462.5721 | 462.5721 | 1024.8969 | 780 | 200 | 2004.8969 | 50.12% | 95% | 0% | -179.6339 | 282.9383 | -3550 | -400 | -3667.0617 | 91.68% | 51.14% | 95% | 0% | 1649 | -157
[5 empty] | 2019-08-30 | 14 | 5790 | 1609 | -171 | 1 | 0 | 1780 | 667.7659 | 667.7659 | 667.7659 | 1024.8969 | 780 | 200 | 2004.8969 | 50.12% | 95% | 0% | -195.6522 | 472.1137 | -3550 | -400 | -3477.8863 | 86.95% | 51.13% | 95% | 0% | 1780 | -171
[5 empty] | 2019-08-30 | 15 | 5790.5 | 1760 | -198 | 1 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 1024.8969 | 780 | 200 | 2004.8969 | 50.12% | 95% | 0% | -226.5446 | 720.0341 | -3550 | -400 | -3229.9659 | 80.75% | 51.12% | 95% | 0% | 1958 | -198
[5 empty] | 2019-08-30 | 16 | 5791 | 1834 | -236 | 1 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 1024.8969 | 780 | 200 | 2004.8969 | 50.12% | 95% | 0% | -270.0229 | 851.9887 | -3550 | -400 | -3098.0113 | 77.45% | 51.12% | 95% | 0% | 2070 | -236
[5 empty] | 2019-08-30 | 17 | 5791.5 | 1854 | -284 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 1024.8969 | 780 | 200 | 2004.8969 | 50.12% | 95% | 0% | -324.9428 | 903.5815 | -3550 | -400 | -3046.4185 | 76.16% | 51.11% | 95% | 0% | 2138 | -284
[5 empty] | 2019-08-30 | 18 | 5792 | 1784 | -361 | 1 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 1024.8969 | 780 | 200 | 2004.8969 | 50.12% | 95% | 0% | -413.0435 | 826.4454 | -3550 | -400 | -3123.5546 | 78.09% | 51.11% | 95% | 0% | 2145 | -361
[5 empty] | 2019-08-30 | 19 | 5792.5 | 1744 | -425 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -486.27 | 790.8116 | -3550 | -400 | -3159.1884 | 78.98% | 51.11% | 95% | 0% | 2169 | -425
[5 empty] | 2019-08-30 | 20 | 5793 | 1652 | -489 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -559.4966 | 673.7268 | -3550 | -400 | -3276.2732 | 81.91% | 51.1% | 95% | 0% | 2141 | -489
[5 empty] | 2019-08-30 | 21 | 5793.5 | 1565 | -534 | 1 | 0 | 2099 | 1167.4361 | 1167.4361 | 1167.4361 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -610.984 | 556.4521 | -3550 | -400 | -3393.5479 | 84.84% | 51.1% | 95% | 0% | 2099 | -534
[5 empty] | 2019-08-30 | 22 | 5794 | 1501 | -568 | 1 | 0 | 2069 | 1120.4452 | 1120.4452 | 1120.4452 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -649.8856 | 470.5596 | -3550 | -400 | -3479.4404 | 86.99% | 51.1% | 95% | 0% | 2069 | -568
[5 empty] | 2019-08-30 | 23 | 5794.5 | 1448 | -598 | 1 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -684.2105 | 400.2083 | -3550 | -400 | -3549.7917 | 88.74% | 51.09% | 95% | 0% | 2046 | -598
[5 empty] | 2019-08-30 | 24 | 5795 | 1406 | -625 | 1 | 0 | 2031 | 1060.9233 | 1060.9233 | 1060.9233 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -715.103 | 345.8204 | -3550 | -400 | -3604.1796 | 90.1% | 51.09% | 95% | 0% | 2031 | -625
[5 empty] | 2019-08-30 | 25 | 5795.5 | 1358 | -656 | 1 | 0 | 2014 | 1034.2951 | 1034.2951 | 1034.2951 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -750.5721 | 283.7231 | -3550 | -400 | -3666.2769 | 91.66% | 51.09% | 95% | 0% | 2014 | -656
[5 empty] | 2019-08-30 | 26 | 5796 | 1327 | -663 | 1 | 0 | 1990 | 996.7024 | 996.7024 | 996.7024 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -758.5812 | 238.1212 | -3550 | -400 | -3711.8788 | 92.8% | 51.09% | 95% | 0% | 1990 | -663
[5 empty] | 2019-08-30 | 27 | 5796.5 | 1295 | -659 | 1 | 0 | 1954 | 940.3133 | 940.3133 | 940.3133 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -754.0046 | 186.3087 | -3550 | -400 | -3763.6913 | 94.09% | 51.09% | 95% | 0% | 1954 | -659
[5 empty] | 2019-08-30 | 28 | 5797 | 1269 | -653 | 1 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -747.1396 | 143.05 | -3550 | -400 | -3806.95 | 95.17% | 51.08% | 95% | 0% | 1922 | -653
[5 empty] | 2019-08-30 | 29 | 5797.5 | 1267 | -634 | 1 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -725.4005 | 131.8955 | -3550 | -400 | -3818.1045 | 95.45% | 51.08% | 95% | 0% | 1901 | -634
[5 empty] | 2019-08-30 | 30 | 5798 | 1320 | -593 | 1 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -678.4897 | 197.6026 | -3550 | -400 | -3752.3974 | 93.81% | 51.08% | 95% | 0% | 1913 | -593
[5 empty] | 2019-08-30 | 31 | 5798.5 | 1304 | -596 | 1 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -681.9222 | 173.8074 | -3550 | -400 | -3776.1926 | 94.4% | 51.08% | 95% | 0% | 1900 | -596
[5 empty] | 2019-08-30 | 32 | 5799 | 1358 | -564 | 1 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 1023.3306 | 780 | 200 | 2003.3306 | 50.08% | 95% | 0% | -645.3089 | 244.8807 | -3550 | -400 | -3705.1193 | 92.63% | 51.08% | 95% | 0% | 1922 | -564
[5 empty] | 2019-08-30 | 33 | 5799.5 | 1445 | -519 | 1 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 1021.7642 | 780 | 200 | 2001.7642 | 50.04% | 95% | 0% | -593.8215 | 362.1554 | -3550 | -400 | -3587.8446 | 89.7% | 51.07% | 95% | 0% | 1964 | -519
[5 empty] | 2019-08-30 | 34 | 5800 | 1596 | -447 | 1 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 1021.7642 | 780 | 200 | 2001.7642 | 50.04% | 95% | 0% | -511.4416 | 568.2781 | -3550 | -400 | -3381.7219 | 84.54% | 51.07% | 95% | 0% | 2043 | -447
[5 empty] | 2019-08-30 | 35 | 5800.5 | 1731 | -378 | 1 | 0 | 2109 | 1183.0998 | 1183.0998 | 1183.0998 | 1021.7642 | 780 | 200 | 2001.7642 | 50.04% | 95% | 0% | -432.4943 | 750.6055 | -3550 | -400 | -3199.3945 | 79.98% | 51.06% | 95% | 0% | 2109 | -378
[5 empty] | 2019-08-30 | 36 | 5801 | 1854 | -303 | 1 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 1021.7642 | 780 | 200 | 2001.7642 | 50.04% | 95% | 0% | -346.6819 | 911.6033 | -3550 | -400 | -3038.3967 | 75.96% | 51.05% | 95% | 0% | 2157 | -303
[5 empty] | 2019-08-30 | 37 | 5801.5 | 1926 | -263 | 1 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 1021.7642 | 780 | 200 | 2001.7642 | 50.04% | 95% | 0% | -300.9153 | 1007.4936 | -3550 | -400 | -2942.5064 | 73.56% | 51.05% | 95% | 0% | 2189 | -263
[5 empty] | 2019-08-30 | 38 | 5802 | 2004 | -202 | 1 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 1021.7642 | 780 | 200 | 2001.7642 | 50.04% | 95% | 0% | -231.1213 | 1103.9158 | -3550 | -400 | -2846.0842 | 71.15% | 51.05% | 95% | 0% | 2206 | -202
[5 empty] | 2019-08-30 | 39 | 5802.5 | 2054 | -163 | 1 | 0 | 2217 | 1352.2671 | 1352.2671 | 1352.2671 | 1021.7642 | 780 | 200 | 2001.7642 | 50.04% | 95% | 0% | -186.4989 | 1165.7683 | -3550 | -400 | -2784.2317 | 69.61% | 51.04% | 95% | 0% | 2217 | -163
[5 empty] | 2019-08-30 | 40 | 5803 | 2059 | -135 | 1 | 0 | 2194 | 1316.2407 | 1316.2407 | 1316.2407 | 1021.7642 | 780 | 200 | 2001.7642 | 50.04% | 95% | 0% | -154.4622 | 1161.7785 | -3550 | -400 | -2788.2215 | 69.71% | 51.04% | 95% | 0% | 2194 | -135
[5 empty] | 2019-08-30 | 41 | 5803.5 | 2107 | -133 | 1 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -152.1739 | 1236.1196 | -3550 | -400 | -2713.8804 | 67.85% | 51.04% | 95% | 0% | 2240 | -133
[5 empty] | 2019-08-30 | 42 | 5804 | 2098 | -125 | 1 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -143.0206 | 1218.6447 | -3550 | -400 | -2731.3553 | 68.28% | 51.04% | 95% | 0% | 2223 | -125
[5 empty] | 2019-08-30 | 43 | 5804.5 | 2044 | -125 | 0 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -143.0206 | 1134.061 | -2750 | -200 | -1815.939 | 45.4% | 51.03% | 95% | 0% | 2169 | -125
[5 empty] | 2019-08-30 | 44 | 5805 | 1974 | -121 | 0 | 0 | 2095 | 1161.1707 | 1161.1707 | 1161.1707 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -138.4439 | 1022.7267 | -2750 | -200 | -1927.2733 | 48.18% | 51.03% | 95% | 0% | 2095 | -121
[5 empty] | 2019-08-30 | 45 | 5805.5 | 1864 | -121 | 0 | 0 | 1985 | 988.8706 | 988.8706 | 988.8706 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -138.4439 | 850.4266 | -2750 | -200 | -2099.5734 | 52.49% | 51.03% | 95% | 0% | 1985 | -121
[5 empty] | 2019-08-30 | 46 | 5806 | 1741 | -122 | 0 | 0 | 1863 | 797.7741 | 797.7741 | 797.7741 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -139.5881 | 658.186 | -2750 | -200 | -2291.814 | 57.3% | 51.03% | 95% | 0% | 1863 | -122
[5 empty] | 2019-08-30 | 47 | 5806.5 | 1635 | -122 | 0 | 0 | 1757 | 631.7395 | 631.7395 | 631.7395 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -139.5881 | 492.1514 | -2750 | -200 | -2457.8486 | 61.45% | 51.03% | 95% | 0% | 1757 | -122
[5 empty] | 2019-08-30 | 48 | 5807 | 1530 | -124 | 0 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -141.8764 | 328.5275 | -2750 | -200 | -2621.4725 | 65.54% | 51.02% | 95% | 0% | 1654 | -124
[5 empty] | 2019-08-31 | 1 | 5807.5 | 1428 | -124 | 0 | 0 | 1552 | 310.6348 | 310.6348 | 310.6348 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -141.8764 | 168.7584 | -2750 | -200 | -2781.2416 | 69.53% | 51.01% | 95% | 0% | 1552 | -124
[5 empty] | 2019-08-31 | 2 | 5808 | 1376 | -126 | 0 | 0 | 1502 | 232.3166 | 232.3166 | 232.3166 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -144.1648 | 88.1518 | -2750 | -200 | -2861.8482 | 71.55% | 51.01% | 95% | 0% | 1502 | -126
[5 empty] | 2019-08-31 | 3 | 5808.5 | 1312 | -126 | 0 | 0 | 1438 | 132.0692 | 132.0692 | 132.0692 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -144.1648 | -12.0955 | -2750 | -200 | -2962.0955 | 74.05% | 50.99% | 95% | 0% | 1438 | -126
[5 empty] | 2019-08-31 | 4 | 5809 | 1269 | -131 | 0 | 0 | 1400 | 72.5474 | 72.5474 | 72.5474 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -149.8856 | -77.3382 | -2750 | -200 | -3027.3382 | 75.68% | 50.99% | 95% | 0% | 1400 | -131
[5 empty] | 2019-08-31 | 5 | 5809.5 | 1249 | -131 | 0 | 0 | 1380 | 41.2201 | 41.2201 | 41.2201 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -149.8856 | -108.6655 | -2750 | -200 | -3058.6655 | 76.47% | 50.99% | 95% | 0% | 1380 | -131
[5 empty] | 2019-08-31 | 6 | 5810 | 1213 | -137 | 0 | 0 | 1350 | -5.7708 | -5.7708 | -5.7708 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -156.7506 | -162.5214 | -2750 | -200 | -3112.5214 | 77.81% | 50.98% | 95% | 0% | 1350 | -137
[5 empty] | 2019-08-31 | 7 | 5810.5 | 1190 | -137 | 0 | 0 | 1327 | -41.7972 | -41.7972 | -41.7972 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -156.7506 | -198.5478 | -2750 | -200 | -3148.5478 | 78.71% | 50.98% | 95% | 0% | 1327 | -137
[5 empty] | 2019-08-31 | 8 | 5811 | 1160 | -143 | 0 | 0 | 1303 | -79.3899 | -79.3899 | -79.3899 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -163.6156 | -243.0055 | -2750 | -200 | -3193.0055 | 79.83% | 50.98% | 95% | 0% | 1303 | -143
[5 empty] | 2019-08-31 | 9 | 5811.5 | 1144 | -143 | 0 | 0 | 1287 | -104.4518 | -104.4518 | -104.4518 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -163.6156 | -268.0673 | -2750 | -200 | -3218.0673 | 80.45% | 50.98% | 95% | 0% | 1287 | -143
[5 empty] | 2019-08-31 | 10 | 5812 | 1124 | -150 | 0 | 0 | 1274 | -124.8145 | -124.8145 | -124.8145 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -171.6247 | -296.4392 | -2750 | -200 | -3246.4392 | 81.16% | 50.98% | 95% | 0% | 1274 | -150
[5 empty] | 2019-08-31 | 11 | 5812.5 | 1145 | -150 | 0 | 0 | 1295 | -91.9209 | -91.9209 | -91.9209 | 1020.1979 | 780 | 200 | 2000.1979 | 50% | 95% | 0% | -171.6247 | -263.5456 | -2750 | -200 | -3213.5456 | 80.34% | 50.97% | 95% | 0% | 1295 | -150
[5 empty] | 2019-08-31 | 12 | 5813 | 1169 | -155 | 0 | 0 | 1324 | -46.4963 | -46.4963 | -46.4963 | 1018.6315 | 780 | 200 | 1998.6315 | 49.97% | 95% | 0% | -177.3455 | -223.8418 | -2750 | -200 | -3173.8418 | 79.35% | 50.97% | 95% | 0% | 1324 | -155
[5 empty] | 2019-08-31 | 13 | 5813.5 | 1228 | -156 | 0 | 0 | 1384 | 47.4856 | 47.4856 | 47.4856 | 1018.6315 | 780 | 200 | 1998.6315 | 49.97% | 95% | 0% | -178.4897 | -131.0041 | -2750 | -200 | -3081.0041 | 77.03% | 50.97% | 95% | 0% | 1384 | -156
[5 empty] | 2019-08-31 | 14 | 5814 | 1256 | -177 | 1 | 0 | 1433 | 124.2374 | 124.2374 | 124.2374 | 1018.6315 | 780 | 200 | 1998.6315 | 49.97% | 95% | 0% | -202.5172 | -78.2797 | -3550 | -400 | -4028.2797 | 100.7% | 50.96% | 95% | 0% | 1433 | -177
[5 empty] | 2019-08-31 | 15 | 5814.5 | 1319 | -216 | 1 | 0 | 1535 | 284.0066 | 284.0066 | 284.0066 | 1018.6315 | 780 | 200 | 1998.6315 | 49.97% | 95% | 0% | -247.1396 | 36.867 | -3550 | -400 | -3913.133 | 97.83% | 50.96% | 95% | 0% | 1535 | -216
[5 empty] | 2019-08-31 | 16 | 5815 | 1340 | -266 | 1 | 0 | 1606 | 395.2185 | 395.2185 | 395.2185 | 1018.6315 | 780 | 200 | 1998.6315 | 49.97% | 95% | 0% | -304.3478 | 90.8706 | -3550 | -400 | -3859.1294 | 96.48% | 50.95% | 95% | 0% | 1606 | -266
[5 empty] | 2019-08-31 | 17 | 5815.5 | 1370 | -321 | 1 | 0 | 1691 | 528.3594 | 528.3594 | 528.3594 | 1018.6315 | 780 | 200 | 1998.6315 | 49.97% | 95% | 0% | -367.2769 | 161.0826 | -3550 | -400 | -3788.9174 | 94.72% | 50.95% | 95% | 0% | 1691 | -321
[5 empty] | 2019-08-31 | 18 | 5816 | 1350 | -378 | 1 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 1018.6315 | 780 | 200 | 1998.6315 | 49.97% | 95% | 0% | -432.4943 | 153.8206 | -3550 | -400 | -3796.1794 | 94.9% | 50.95% | 95% | 0% | 1728 | -378
[5 empty] | 2019-08-31 | 19 | 5816.5 | 1357 | -412 | 1 | 0 | 1769 | 650.5359 | 650.5359 | 650.5359 | 1018.6315 | 780 | 200 | 1998.6315 | 49.97% | 95% | 0% | -471.3959 | 179.14 | -3550 | -400 | -3770.86 | 94.27% | 50.95% | 95% | 0% | 1769 | -412
[5 empty] | 2019-08-31 | 20 | 5817 | 1323 | -456 | 1 | 0 | 1779 | 666.1995 | 666.1995 | 666.1995 | 1018.6315 | 780 | 200 | 1998.6315 | 49.97% | 95% | 0% | -521.7391 | 144.4604 | -3550 | -400 | -3805.5396 | 95.14% | 50.94% | 95% | 0% | 1779 | -456
[5 empty] | 2019-08-31 | 21 | 5817.5 | 1255 | -497 | 1 | 0 | 1752 | 623.9077 | 623.9077 | 623.9077 | 1018.6315 | 780 | 200 | 1998.6315 | 49.97% | 95% | 0% | -568.6499 | 55.2578 | -3550 | -400 | -3894.7422 | 97.37% | 50.93% | 95% | 0% | 1752 | -497
[5 empty] | 2019-08-31 | 22 | 5818 | 1234 | -506 | 1 | 0 | 1740 | 605.1113 | 605.1113 | 605.1113 | 1017.0651 | 780 | 200 | 1997.0651 | 49.93% | 95% | 0% | -578.9474 | 26.1639 | -3550 | -400 | -3923.8361 | 98.1% | 50.93% | 95% | 0% | 1740 | -506
[5 empty] | 2019-08-31 | 23 | 5818.5 | 1174 | -567 | 1 | 0 | 1741 | 606.6777 | 606.6777 | 606.6777 | 1017.0651 | 780 | 200 | 1997.0651 | 49.93% | 95% | 0% | -648.7414 | -42.0638 | -3550 | -400 | -3992.0638 | 99.8% | 50.93% | 95% | 0% | 1741 | -567
[5 empty] | 2019-08-31 | 24 | 5819 | 1144 | -598 | 1 | 0 | 1742 | 608.244 | 608.244 | 608.244 | 1017.0651 | 780 | 200 | 1997.0651 | 49.93% | 95% | 0% | -684.2105 | -75.9665 | -3550 | -400 | -4025.9665 | 100.6% | 50.92% | 95% | 0% | 1742 | -598
[5 empty] | 2019-08-31 | 25 | 5819.5 | 1137 | -604 | 1 | 0 | 1741 | 606.6777 | 606.6777 | 606.6777 | 1017.0651 | 780 | 200 | 1997.0651 | 49.93% | 95% | 0% | -691.0755 | -84.3979 | -3550 | -400 | -4034.3979 | 100.9% | 50.92% | 95% | 0% | 1741 | -604
[5 empty] | 2019-08-31 | 26 | 5820 | 1135 | -594 | 1 | 0 | 1729 | 587.8813 | 587.8813 | 587.8813 | 1017.0651 | 780 | 200 | 1997.0651 | 49.93% | 95% | 0% | -679.6339 | -91.7526 | -3550 | -400 | -4041.7526 | 101% | 50.92% | 95% | 0% | 1729 | -594
[5 empty] | 2019-08-31 | 27 | 5820.5 | 1095 | -563 | 1 | 0 | 1658 | 476.6694 | 476.6694 | 476.6694 | 1017.0651 | 780 | 200 | 1997.0651 | 49.93% | 95% | 0% | -644.1648 | -167.4953 | -3550 | -400 | -4117.4953 | 102.9% | 50.92% | 95% | 0% | 1658 | -563
[5 empty] | 2019-08-31 | 28 | 5821 | 1042 | -581 | 1 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 1017.0651 | 780 | 200 | 1997.0651 | 49.93% | 95% | 0% | -664.7597 | -242.9131 | -3550 | -400 | -4192.9131 | 104.8% | 50.91% | 95% | 0% | 1623 | -581
[5 empty] | 2019-08-31 | 29 | 5821.5 | 987 | -600 | 1 | 0 | 1587 | 365.4575 | 365.4575 | 365.4575 | 1017.0651 | 780 | 200 | 1997.0651 | 49.93% | 95% | 0% | -686.4989 | -321.0413 | -3550 | -400 | -4271.0413 | 106.8% | 50.91% | 95% | 0% | 1587 | -600
[5 empty] | 2019-08-31 | 30 | 5822 | 992 | -586 | 1 | 0 | 1578 | 351.3603 | 351.3603 | 351.3603 | 1017.0651 | 780 | 200 | 1997.0651 | 49.93% | 95% | 0% | -670.4805 | -319.1203 | -3550 | -400 | -4269.1203 | 106.7% | 50.91% | 95% | 0% | 1578 | -586
[5 empty] | 2019-08-31 | 31 | 5822.5 | 1030 | -564 | 1 | 0 | 1594 | 376.4221 | 376.4221 | 376.4221 | 1017.0651 | 780 | 200 | 1997.0651 | 49.93% | 95% | 0% | -645.3089 | -268.8868 | -3550 | -400 | -4218.8868 | 105.5% | 50.91% | 95% | 0% | 1594 | -564
[5 empty] | 2019-08-31 | 32 | 5823 | 1109 | -504 | 1 | 0 | 1613 | 406.183 | 406.183 | 406.183 | 1017.0651 | 780 | 200 | 1997.0651 | 49.93% | 95% | 0% | -576.659 | -170.476 | -3550 | -400 | -4120.476 | 103% | 50.91% | 95% | 0% | 1613 | -504
[5 empty] | 2019-08-31 | 33 | 5823.5 | 1169 | -491 | 1 | 0 | 1660 | 479.8021 | 479.8021 | 479.8021 | 1017.0651 | 780 | 200 | 1997.0651 | 49.93% | 95% | 0% | -561.7849 | -81.9828 | -3550 | -400 | -4031.9828 | 100.8% | 50.9% | 95% | 0% | 1660 | -491
[5 empty] | 2019-08-31 | 34 | 5824 | 1308 | -446 | 1 | 0 | 1754 | 627.0404 | 627.0404 | 627.0404 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -510.2975 | 116.7429 | -3550 | -400 | -3833.2571 | 95.83% | 50.9% | 95% | 0% | 1754 | -446
[5 empty] | 2019-08-31 | 35 | 5824.5 | 1450 | -408 | 1 | 0 | 1858 | 789.9423 | 789.9423 | 789.9423 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -466.8192 | 323.1231 | -3550 | -400 | -3626.8769 | 90.67% | 50.89% | 95% | 0% | 1858 | -408
[5 empty] | 2019-08-31 | 36 | 5825 | 1577 | -358 | 1 | 0 | 1935 | 910.5523 | 910.5523 | 910.5523 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -409.611 | 500.9414 | -3550 | -400 | -3449.0586 | 86.23% | 50.89% | 95% | 0% | 1935 | -358
[5 empty] | 2019-08-31 | 37 | 5825.5 | 1681 | -303 | 1 | 0 | 1984 | 987.3042 | 987.3042 | 987.3042 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -346.6819 | 640.6223 | -3550 | -400 | -3309.3777 | 82.73% | 50.88% | 95% | 0% | 1984 | -303
[5 empty] | 2019-08-31 | 38 | 5826 | 1784 | -218 | 1 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -249.4279 | 766.0708 | -3550 | -400 | -3183.9292 | 79.6% | 50.88% | 95% | 0% | 2002 | -218
[5 empty] | 2019-08-31 | 39 | 5826.5 | 1862 | -170 | 1 | 0 | 2032 | 1062.4897 | 1062.4897 | 1062.4897 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -194.508 | 867.9817 | -3550 | -400 | -3082.0183 | 77.05% | 50.88% | 95% | 0% | 2032 | -170
[5 empty] | 2019-08-31 | 40 | 5827 | 1928 | -131 | 1 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -149.8856 | 954.8959 | -3550 | -400 | -2995.1041 | 74.88% | 50.88% | 95% | 0% | 2059 | -131
[5 empty] | 2019-08-31 | 41 | 5827.5 | 1985 | -128 | 1 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -146.4531 | 1042.9121 | -3550 | -400 | -2907.0879 | 72.68% | 50.87% | 95% | 0% | 2113 | -128
[5 empty] | 2019-08-31 | 42 | 5828 | 1994 | -122 | 1 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -139.5881 | 1054.4762 | -3550 | -400 | -2895.5238 | 72.39% | 50.86% | 95% | 0% | 2116 | -122
[5 empty] | 2019-08-31 | 43 | 5828.5 | 1924 | -122 | 0 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -139.5881 | 944.8307 | -2750 | -200 | -2005.1693 | 50.13% | 50.86% | 95% | 0% | 2046 | -122
[5 empty] | 2019-08-31 | 44 | 5829 | 1851 | -121 | 0 | 0 | 1972 | 968.5078 | 968.5078 | 968.5078 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -138.4439 | 830.0639 | -2750 | -200 | -2119.9361 | 53% | 50.86% | 95% | 0% | 1972 | -121
[5 empty] | 2019-08-31 | 45 | 5829.5 | 1779 | -121 | 0 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -138.4439 | 717.2857 | -2750 | -200 | -2232.7143 | 55.82% | 50.86% | 95% | 0% | 1900 | -121
[5 empty] | 2019-08-31 | 46 | 5830 | 1708 | -121 | 0 | 0 | 1829 | 744.5177 | 744.5177 | 744.5177 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -138.4439 | 606.0738 | -2750 | -200 | -2343.9262 | 58.6% | 50.86% | 95% | 0% | 1829 | -121
[5 empty] | 2019-08-31 | 47 | 5830.5 | 1600 | -121 | 0 | 0 | 1721 | 575.3504 | 575.3504 | 575.3504 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -138.4439 | 436.9064 | -2750 | -200 | -2513.0936 | 62.83% | 50.85% | 95% | 0% | 1721 | -121
[5 empty] | 2019-08-31 | 48 | 5831 | 1506 | -121 | 0 | 0 | 1627 | 428.1121 | 428.1121 | 428.1121 | 1015.4988 | 780 | 200 | 1995.4988 | 49.89% | 95% | 0% | -138.4439 | 289.6682 | -2750 | -200 | -2660.3318 | 66.51% | 50.85% | 95% | 0% | 1627 | -121
[5 empty] | 2019-09-01 | 1 | 5831.5 | 1410 | -121 | 0 | 0 | 1531 | 277.7411 | 277.7411 | 277.7411 | 1013.9324 | 780 | 200 | 1993.9324 | 49.85% | 95% | 0% | -138.4439 | 139.2972 | -2750 | -200 | -2810.7028 | 70.27% | 50.85% | 95% | 0% | 1531 | -121
[5 empty] | 2019-09-01 | 2 | 5832 | 1352 | -117 | 0 | 0 | 1469 | 180.6265 | 180.6265 | 180.6265 | 1013.9324 | 780 | 200 | 1993.9324 | 49.85% | 95% | 0% | -133.8673 | 46.7593 | -2750 | -200 | -2903.2407 | 72.58% | 50.84% | 95% | 0% | 1469 | -117
[5 empty] | 2019-09-01 | 3 | 5832.5 | 1295 | -117 | 0 | 0 | 1412 | 91.3438 | 91.3438 | 91.3438 | 1013.9324 | 780 | 200 | 1993.9324 | 49.85% | 95% | 0% | -133.8673 | -42.5235 | -2750 | -200 | -2992.5235 | 74.81% | 50.84% | 95% | 0% | 1412 | -117
[5 empty] | 2019-09-01 | 4 | 5833 | 1274 | -117 | 0 | 0 | 1391 | 58.4501 | 58.4501 | 58.4501 | 1013.9324 | 780 | 200 | 1993.9324 | 49.85% | 95% | 0% | -133.8673 | -75.4172 | -2750 | -200 | -3025.4172 | 75.64% | 50.82% | 95% | 0% | 1391 | -117
[5 empty] | 2019-09-01 | 5 | 5833.5 | 1241 | -117 | 0 | 0 | 1358 | 6.7601 | 6.7601 | 6.7601 | 1013.9324 | 780 | 200 | 1993.9324 | 49.85% | 95% | 0% | -133.8673 | -127.1072 | -2750 | -200 | -3077.1072 | 76.93% | 50.82% | 95% | 0% | 1358 | -117
[5 empty] | 2019-09-01 | 6 | 5834 | 1209 | -116 | 0 | 0 | 1325 | -44.9299 | -44.9299 | -44.9299 | 1013.9324 | 780 | 200 | 1993.9324 | 49.85% | 95% | 0% | -132.7231 | -177.653 | -2750 | -200 | -3127.653 | 78.19% | 50.82% | 95% | 0% | 1325 | -116
[5 empty] | 2019-09-01 | 7 | 5834.5 | 1195 | -116 | 0 | 0 | 1311 | -66.859 | -66.859 | -66.859 | 1012.366 | 780 | 200 | 1992.366 | 49.81% | 95% | 0% | -132.7231 | -199.5821 | -2750 | -200 | -3149.5821 | 78.74% | 50.82% | 95% | 0% | 1311 | -116
[5 empty] | 2019-09-01 | 8 | 5835 | 1190 | -114 | 0 | 0 | 1304 | -77.8236 | -77.8236 | -77.8236 | 1012.366 | 780 | 200 | 1992.366 | 49.81% | 95% | 0% | -130.4348 | -208.2584 | -2750 | -200 | -3158.2584 | 78.96% | 50.81% | 95% | 0% | 1304 | -114
[5 empty] | 2019-09-01 | 9 | 5835.5 | 1194 | -114 | 0 | 0 | 1308 | -71.5581 | -71.5581 | -71.5581 | 1012.366 | 780 | 200 | 1992.366 | 49.81% | 95% | 0% | -130.4348 | -201.9929 | -2750 | -200 | -3151.9929 | 78.8% | 50.81% | 95% | 0% | 1308 | -114
[5 empty] | 2019-09-01 | 10 | 5836 | 1184 | -110 | 0 | 0 | 1294 | -93.4872 | -93.4872 | -93.4872 | 1012.366 | 780 | 200 | 1992.366 | 49.81% | 95% | 0% | -125.8581 | -219.3453 | -2750 | -200 | -3169.3453 | 79.23% | 50.81% | 95% | 0% | 1294 | -110
[5 empty] | 2019-09-01 | 11 | 5836.5 | 1197 | -110 | 0 | 0 | 1307 | -73.1245 | -73.1245 | -73.1245 | 1012.366 | 780 | 200 | 1992.366 | 49.81% | 95% | 0% | -125.8581 | -198.9826 | -2750 | -200 | -3148.9826 | 78.72% | 50.81% | 95% | 0% | 1307 | -110
[5 empty] | 2019-09-01 | 12 | 5837 | 1225 | -108 | 0 | 0 | 1333 | -32.399 | -32.399 | -32.399 | 1012.366 | 780 | 200 | 1992.366 | 49.81% | 95% | 0% | -123.5698 | -155.9688 | -2750 | -200 | -3105.9688 | 77.65% | 50.81% | 95% | 0% | 1333 | -108
[5 empty] | 2019-09-01 | 13 | 5837.5 | 1249 | -108 | 0 | 0 | 1357 | 5.1937 | 5.1937 | 5.1937 | 1012.366 | 780 | 200 | 1992.366 | 49.81% | 95% | 0% | -123.5698 | -118.3761 | -2750 | -200 | -3068.3761 | 76.71% | 50.81% | 95% | 0% | 1357 | -108
[5 empty] | 2019-09-01 | 14 | 5838 | 1274 | -119 | 0 | 0 | 1393 | 61.5829 | 61.5829 | 61.5829 | 1012.366 | 780 | 200 | 1992.366 | 49.81% | 95% | 0% | -136.1556 | -74.5728 | -2750 | -200 | -3024.5728 | 75.61% | 50.8% | 95% | 0% | 1393 | -119
[5 empty] | 2019-09-01 | 15 | 5838.5 | 1307 | -163 | 0 | 0 | 1470 | 182.1929 | 182.1929 | 182.1929 | 1012.366 | 780 | 200 | 1992.366 | 49.81% | 95% | 0% | -186.4989 | -4.3059 | -2750 | -200 | -2954.3059 | 73.86% | 50.8% | 95% | 0% | 1470 | -163
[5 empty] | 2019-09-01 | 16 | 5839 | 1294 | -223 | 1 | 0 | 1517 | 255.812 | 255.812 | 255.812 | 1012.366 | 780 | 200 | 1992.366 | 49.81% | 95% | 0% | -255.1487 | 0.66329 | -3550 | -400 | -3949.3367 | 98.73% | 50.79% | 95% | 0% | 1517 | -223
[5 empty] | 2019-09-01 | 17 | 5839.5 | 1303 | -281 | 1 | 0 | 1584 | 360.7585 | 360.7585 | 360.7585 | 1012.366 | 780 | 200 | 1992.366 | 49.81% | 95% | 0% | -321.5103 | 39.2482 | -3550 | -400 | -3910.7518 | 97.77% | 50.79% | 95% | 0% | 1584 | -281
[5 empty] | 2019-09-01 | 18 | 5840 | 1235 | -368 | 1 | 0 | 1603 | 390.5194 | 390.5194 | 390.5194 | 1010.7997 | 780 | 200 | 1990.7997 | 49.77% | 95% | 0% | -421.0526 | -30.5333 | -3550 | -400 | -3980.5333 | 99.51% | 50.79% | 95% | 0% | 1603 | -368
[5 empty] | 2019-09-01 | 19 | 5840.5 | 1201 | -435 | 1 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 1010.7997 | 780 | 200 | 1990.7997 | 49.77% | 95% | 0% | -497.7117 | -55.5023 | -3550 | -400 | -4005.5023 | 100.1% | 50.79% | 95% | 0% | 1636 | -435
[5 empty] | 2019-09-01 | 20 | 5841 | 1138 | -502 | 1 | 0 | 1640 | 448.4749 | 448.4749 | 448.4749 | 1010.7997 | 780 | 200 | 1990.7997 | 49.77% | 95% | 0% | -574.3707 | -125.8959 | -3550 | -400 | -4075.8959 | 101.9% | 50.78% | 95% | 0% | 1640 | -502
[5 empty] | 2019-09-01 | 21 | 5841.5 | 1063 | -575 | 1 | 0 | 1638 | 445.3421 | 445.3421 | 445.3421 | 1010.7997 | 780 | 200 | 1990.7997 | 49.77% | 95% | 0% | -657.8947 | -212.5526 | -3550 | -400 | -4162.5526 | 104.1% | 50.78% | 95% | 0% | 1638 | -575
[5 empty] | 2019-09-01 | 22 | 5842 | 1019 | -613 | 1 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 1010.7997 | 780 | 200 | 1990.7997 | 49.77% | 95% | 0% | -701.373 | -265.4291 | -3550 | -400 | -4215.4291 | 105.4% | 50.77% | 95% | 0% | 1632 | -613
[5 empty] | 2019-09-01 | 23 | 5842.5 | 1016 | -627 | 1 | 0 | 1643 | 453.1739 | 453.1739 | 453.1739 | 1010.7997 | 780 | 200 | 1990.7997 | 49.77% | 95% | 0% | -717.3913 | -264.2174 | -3550 | -400 | -4214.2174 | 105.4% | 50.77% | 95% | 0% | 1643 | -627
[5 empty] | 2019-09-01 | 24 | 5843 | 1041 | -622 | 1 | 0 | 1663 | 484.5012 | 484.5012 | 484.5012 | 1010.7997 | 780 | 200 | 1990.7997 | 49.77% | 95% | 0% | -711.6705 | -227.1692 | -3550 | -400 | -4177.1692 | 104.4% | 50.76% | 95% | 0% | 1663 | -622
[5 empty] | 2019-09-01 | 25 | 5843.5 | 1018 | -649 | 1 | 0 | 1667 | 490.7667 | 490.7667 | 490.7667 | 1010.7997 | 780 | 200 | 1990.7997 | 49.77% | 95% | 0% | -742.5629 | -251.7962 | -3550 | -400 | -4201.7962 | 105% | 50.76% | 95% | 0% | 1667 | -649
[5 empty] | 2019-09-01 | 26 | 5844 | 1004 | -657 | 1 | 0 | 1661 | 481.3685 | 481.3685 | 481.3685 | 1010.7997 | 780 | 200 | 1990.7997 | 49.77% | 95% | 0% | -751.7162 | -270.3477 | -3550 | -400 | -4220.3477 | 105.5% | 50.76% | 95% | 0% | 1661 | -657
[5 empty] | 2019-09-01 | 27 | 5844.5 | 1022 | -620 | 1 | 0 | 1642 | 451.6076 | 451.6076 | 451.6076 | 1010.7997 | 780 | 200 | 1990.7997 | 49.77% | 95% | 0% | -709.3822 | -257.7746 | -3550 | -400 | -4207.7746 | 105.2% | 50.76% | 95% | 0% | 1642 | -620
[5 empty] | 2019-09-01 | 28 | 5845 | 971 | -653 | 1 | 0 | 1624 | 423.413 | 423.413 | 423.413 | 1010.7997 | 780 | 200 | 1990.7997 | 49.77% | 95% | 0% | -747.1396 | -323.7266 | -3550 | -400 | -4273.7266 | 106.8% | 50.75% | 95% | 0% | 1624 | -653
[5 empty] | 2019-09-01 | 29 | 5845.5 | 975 | -631 | 1 | 0 | 1606 | 395.2185 | 395.2185 | 395.2185 | 1009.2333 | 780 | 200 | 1989.2333 | 49.73% | 95% | 0% | -721.968 | -326.7495 | -3550 | -400 | -4276.7495 | 106.9% | 50.74% | 95% | 0% | 1606 | -631
[5 empty] | 2019-09-01 | 30 | 5846 | 976 | -609 | 1 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 1009.2333 | 780 | 200 | 1989.2333 | 49.73% | 95% | 0% | -696.7963 | -334.4715 | -3550 | -400 | -4284.4715 | 107.1% | 50.74% | 95% | 0% | 1585 | -609
[5 empty] | 2019-09-01 | 31 | 5846.5 | 1011 | -592 | 1 | 0 | 1603 | 390.5194 | 390.5194 | 390.5194 | 1009.2333 | 780 | 200 | 1989.2333 | 49.73% | 95% | 0% | -677.3455 | -286.8262 | -3550 | -400 | -4236.8262 | 105.9% | 50.73% | 95% | 0% | 1603 | -592
[5 empty] | 2019-09-01 | 32 | 5847 | 1065 | -560 | 1 | 0 | 1625 | 424.9794 | 424.9794 | 424.9794 | 1009.2333 | 780 | 200 | 1989.2333 | 49.73% | 95% | 0% | -640.7323 | -215.7529 | -3550 | -400 | -4165.7529 | 104.1% | 50.73% | 95% | 0% | 1625 | -560
[5 empty] | 2019-09-01 | 33 | 5847.5 | 1209 | -494 | 1 | 0 | 1703 | 547.1558 | 547.1558 | 547.1558 | 1009.2333 | 780 | 200 | 1989.2333 | 49.73% | 95% | 0% | -565.2174 | -18.0616 | -3550 | -400 | -3968.0616 | 99.2% | 50.73% | 95% | 0% | 1703 | -494
[5 empty] | 2019-09-01 | 34 | 5848 | 1357 | -424 | 1 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 1009.2333 | 780 | 200 | 1989.2333 | 49.73% | 95% | 0% | -485.1259 | 184.2064 | -3550 | -400 | -3765.7936 | 94.14% | 50.72% | 95% | 0% | 1781 | -424
[5 empty] | 2019-09-01 | 35 | 5848.5 | 1485 | -388 | 1 | 0 | 1873 | 813.4378 | 813.4378 | 813.4378 | 1009.2333 | 780 | 200 | 1989.2333 | 49.73% | 95% | 0% | -443.9359 | 369.5018 | -3550 | -400 | -3580.4982 | 89.51% | 50.72% | 95% | 0% | 1873 | -388
[5 empty] | 2019-09-01 | 36 | 5849 | 1656 | -303 | 1 | 0 | 1959 | 948.1451 | 948.1451 | 948.1451 | 1009.2333 | 780 | 200 | 1989.2333 | 49.73% | 95% | 0% | -346.6819 | 601.4632 | -3550 | -400 | -3348.5368 | 83.71% | 50.72% | 95% | 0% | 1959 | -303
[5 empty] | 2019-09-01 | 37 | 5849.5 | 1774 | -244 | 1 | 0 | 2018 | 1040.5606 | 1040.5606 | 1040.5606 | 1009.2333 | 780 | 200 | 1989.2333 | 49.73% | 95% | 0% | -279.1762 | 761.3844 | -3550 | -400 | -3188.6156 | 79.72% | 50.71% | 95% | 0% | 2018 | -244
[5 empty] | 2019-09-01 | 38 | 5850 | 1928 | -158 | 1 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -180.778 | 966.2953 | -3550 | -400 | -2983.7047 | 74.59% | 50.71% | 95% | 0% | 2086 | -158
[5 empty] | 2019-09-01 | 39 | 5850.5 | 1993 | -114 | 1 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -130.4348 | 1049.5322 | -3550 | -400 | -2900.4678 | 72.51% | 50.71% | 95% | 0% | 2107 | -114
[5 empty] | 2019-09-01 | 40 | 5851 | 2045 | -81 | 1 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -92.6773 | 1117.0506 | -3550 | -400 | -2832.9494 | 70.82% | 50.7% | 95% | 0% | 2126 | -81
[5 empty] | 2019-09-01 | 41 | 5851.5 | 2080 | -79 | 1 | 0 | 2159 | 1261.418 | 1261.418 | 1261.418 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -90.389 | 1171.029 | -3550 | -400 | -2778.971 | 69.47% | 50.69% | 95% | 0% | 2159 | -79
[5 empty] | 2019-09-01 | 42 | 5852 | 2073 | -73 | 0 | 0 | 2146 | 1241.0552 | 1241.0552 | 1241.0552 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -83.524 | 1157.5312 | -2750 | -200 | -1792.4688 | 44.81% | 50.69% | 95% | 0% | 2146 | -73
[5 empty] | 2019-09-01 | 43 | 5852.5 | 2017 | -73 | 0 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -83.524 | 1069.8148 | -2750 | -200 | -1880.1852 | 47% | 50.69% | 95% | 0% | 2090 | -73
[5 empty] | 2019-09-01 | 44 | 5853 | 1952 | -70 | 0 | 0 | 2022 | 1046.8261 | 1046.8261 | 1046.8261 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -80.0915 | 966.7345 | -2750 | -200 | -1983.2655 | 49.58% | 50.68% | 95% | 0% | 2022 | -70
[5 empty] | 2019-09-01 | 45 | 5853.5 | 1880 | -70 | 0 | 0 | 1950 | 934.0478 | 934.0478 | 934.0478 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -80.0915 | 853.9563 | -2750 | -200 | -2096.0437 | 52.4% | 50.67% | 95% | 0% | 1950 | -70
[5 empty] | 2019-09-01 | 46 | 5854 | 1776 | -68 | 0 | 0 | 1844 | 768.0132 | 768.0132 | 768.0132 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -77.8032 | 690.21 | -2750 | -200 | -2259.79 | 56.49% | 50.66% | 95% | 0% | 1844 | -68
[5 empty] | 2019-09-01 | 47 | 5854.5 | 1648 | -68 | 0 | 0 | 1716 | 567.5185 | 567.5185 | 567.5185 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -77.8032 | 489.7153 | -2750 | -200 | -2460.2847 | 61.51% | 50.66% | 95% | 0% | 1716 | -68
[5 empty] | 2019-09-01 | 48 | 5855 | 1555 | -68 | 0 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -77.8032 | 344.0435 | -2750 | -200 | -2605.9565 | 65.15% | 50.66% | 95% | 0% | 1623 | -68
[5 empty] | 2019-09-02 | 1 | 5855.5 | 1481 | -68 | 0 | 0 | 1549 | 305.9357 | 305.9357 | 305.9357 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -77.8032 | 228.1325 | -2750 | -200 | -2721.8675 | 68.05% | 50.66% | 95% | 0% | 1549 | -68
[5 empty] | 2019-09-02 | 2 | 5856 | 1434 | -64 | 0 | 0 | 1498 | 226.0511 | 226.0511 | 226.0511 | 1007.6669 | 780 | 200 | 1987.6669 | 49.69% | 95% | 0% | -73.2265 | 152.8246 | -2750 | -200 | -2797.1754 | 69.93% | 50.65% | 95% | 0% | 1498 | -64
[5 empty] | 2019-09-02 | 3 | 5856.5 | 1410 | -65 | 0 | 0 | 1475 | 190.0247 | 190.0247 | 190.0247 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -74.3707 | 115.654 | -2750 | -200 | -2834.346 | 70.86% | 50.65% | 95% | 0% | 1475 | -65
[5 empty] | 2019-09-02 | 4 | 5857 | 1399 | -66 | 0 | 0 | 1465 | 174.3611 | 174.3611 | 174.3611 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -75.5149 | 98.8462 | -2750 | -200 | -2851.1538 | 71.28% | 50.64% | 95% | 0% | 1465 | -66
[5 empty] | 2019-09-02 | 5 | 5857.5 | 1367 | -68 | 0 | 0 | 1435 | 127.3702 | 127.3702 | 127.3702 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -77.8032 | 49.567 | -2750 | -200 | -2900.433 | 72.51% | 50.64% | 95% | 0% | 1435 | -68
[5 empty] | 2019-09-02 | 6 | 5858 | 1351 | -69 | 0 | 0 | 1420 | 103.8747 | 103.8747 | 103.8747 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -78.9474 | 24.9273 | -2750 | -200 | -2925.0727 | 73.13% | 50.64% | 95% | 0% | 1420 | -69
[5 empty] | 2019-09-02 | 7 | 5858.5 | 1333 | -70 | 0 | 0 | 1403 | 77.2465 | 77.2465 | 77.2465 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -80.0915 | -2.845 | -2750 | -200 | -2952.845 | 73.82% | 50.64% | 95% | 0% | 1403 | -70
[5 empty] | 2019-09-02 | 8 | 5859 | 1330 | -71 | 0 | 0 | 1401 | 74.1138 | 74.1138 | 74.1138 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -81.2357 | -7.1219 | -2750 | -200 | -2957.1219 | 73.93% | 50.63% | 95% | 0% | 1401 | -71
[5 empty] | 2019-09-02 | 9 | 5859.5 | 1339 | -71 | 0 | 0 | 1410 | 88.211 | 88.211 | 88.211 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -81.2357 | 6.9753 | -2750 | -200 | -2943.0247 | 73.58% | 50.62% | 95% | 0% | 1410 | -71
[5 empty] | 2019-09-02 | 10 | 5860 | 1355 | -72 | 0 | 0 | 1427 | 114.8392 | 114.8392 | 114.8392 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -82.3799 | 32.4594 | -2750 | -200 | -2917.5406 | 72.94% | 50.62% | 95% | 0% | 1427 | -72
[5 empty] | 2019-09-02 | 11 | 5860.5 | 1416 | -73 | 0 | 0 | 1489 | 211.9538 | 211.9538 | 211.9538 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -83.524 | 128.4298 | -2750 | -200 | -2821.5702 | 70.54% | 50.62% | 95% | 0% | 1489 | -73
[5 empty] | 2019-09-02 | 12 | 5861 | 1500 | -74 | 0 | 0 | 1574 | 345.0948 | 345.0948 | 345.0948 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -84.6682 | 260.4266 | -2750 | -200 | -2689.5734 | 67.24% | 50.62% | 95% | 0% | 1574 | -74
[5 empty] | 2019-09-02 | 13 | 5861.5 | 1661 | -75 | 0 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -85.8124 | 513.0335 | -2750 | -200 | -2436.9665 | 60.92% | 50.62% | 95% | 0% | 1736 | -75
[5 empty] | 2019-09-02 | 14 | 5862 | 1798 | -89 | 0 | 0 | 1887 | 835.3669 | 835.3669 | 835.3669 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -101.8307 | 733.5362 | -2750 | -200 | -2216.4638 | 55.41% | 50.61% | 95% | 0% | 1887 | -89
[5 empty] | 2019-09-02 | 15 | 5862.5 | 1940 | -134 | 0 | 0 | 2074 | 1128.277 | 1128.277 | 1128.277 | 1006.1006 | 780 | 200 | 1986.1006 | 49.65% | 95% | 0% | -153.3181 | 974.9589 | -2750 | -200 | -1975.0411 | 49.38% | 50.6% | 95% | 0% | 2074 | -134
[5 empty] | 2019-09-02 | 16 | 5863 | 1955 | -198 | 0 | 0 | 2153 | 1252.0198 | 1252.0198 | 1252.0198 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -226.5446 | 1025.4752 | -2750 | -200 | -1924.5248 | 48.11% | 50.6% | 95% | 0% | 2153 | -198
[5 empty] | 2019-09-02 | 17 | 5863.5 | 1939 | -267 | 1 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -305.492 | 1029.5451 | -3550 | -400 | -2920.4549 | 73.01% | 50.6% | 95% | 0% | 2206 | -267
[5 empty] | 2019-09-02 | 18 | 5864 | 1880 | -343 | 1 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -392.4485 | 969.2168 | -3550 | -400 | -2980.7832 | 74.52% | 50.6% | 95% | 0% | 2223 | -343
[5 empty] | 2019-09-02 | 19 | 5864.5 | 1780 | -431 | 1 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -493.135 | 849.7339 | -3550 | -400 | -3100.2661 | 77.51% | 50.59% | 95% | 0% | 2211 | -431
[5 empty] | 2019-09-02 | 20 | 5865 | 1657 | -492 | 1 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -562.9291 | 682.8253 | -3550 | -400 | -3267.1747 | 81.68% | 50.59% | 95% | 0% | 2149 | -492
[5 empty] | 2019-09-02 | 21 | 5865.5 | 1565 | -539 | 1 | 0 | 2104 | 1175.2679 | 1175.2679 | 1175.2679 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -616.7048 | 558.5631 | -3550 | -400 | -3391.4369 | 84.79% | 50.59% | 95% | 0% | 2104 | -539
[5 empty] | 2019-09-02 | 22 | 5866 | 1486 | -580 | 1 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -663.6156 | 452.1305 | -3550 | -400 | -3497.8695 | 87.45% | 50.59% | 95% | 0% | 2066 | -580
[5 empty] | 2019-09-02 | 23 | 5866.5 | 1461 | -594 | 1 | 0 | 2055 | 1098.5161 | 1098.5161 | 1098.5161 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -679.6339 | 418.8822 | -3550 | -400 | -3531.1178 | 88.28% | 50.58% | 95% | 0% | 2055 | -594
[5 empty] | 2019-09-02 | 24 | 5867 | 1496 | -575 | 1 | 0 | 2071 | 1123.5779 | 1123.5779 | 1123.5779 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -657.8947 | 465.6832 | -3550 | -400 | -3484.3168 | 87.11% | 50.58% | 95% | 0% | 2071 | -575
[5 empty] | 2019-09-02 | 25 | 5867.5 | 1521 | -579 | 1 | 0 | 2100 | 1169.0025 | 1169.0025 | 1169.0025 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -662.4714 | 506.5311 | -3550 | -400 | -3443.4689 | 86.09% | 50.58% | 95% | 0% | 2100 | -579
[5 empty] | 2019-09-02 | 26 | 5868 | 1516 | -586 | 1 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -670.4805 | 501.6547 | -3550 | -400 | -3448.3453 | 86.21% | 50.58% | 95% | 0% | 2102 | -586
[5 empty] | 2019-09-02 | 27 | 5868.5 | 1511 | -590 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -675.0572 | 495.5116 | -3550 | -400 | -3454.4884 | 86.36% | 50.58% | 95% | 0% | 2101 | -590
[5 empty] | 2019-09-02 | 28 | 5869 | 1549 | -556 | 1 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -636.1556 | 540.6787 | -3550 | -400 | -3409.3213 | 85.23% | 50.57% | 95% | 0% | 2105 | -556
[5 empty] | 2019-09-02 | 29 | 5869.5 | 1612 | -511 | 1 | 0 | 2123 | 1205.0289 | 1205.0289 | 1205.0289 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -584.6682 | 620.3607 | -3550 | -400 | -3329.6393 | 83.24% | 50.57% | 95% | 0% | 2123 | -511
[5 empty] | 2019-09-02 | 30 | 5870 | 1688 | -455 | 1 | 0 | 2143 | 1236.3561 | 1236.3561 | 1236.3561 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -520.595 | 715.7612 | -3550 | -400 | -3234.2388 | 80.86% | 50.57% | 95% | 0% | 2143 | -455
[5 empty] | 2019-09-02 | 31 | 5870.5 | 1764 | -408 | 1 | 0 | 2172 | 1281.7807 | 1281.7807 | 1281.7807 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -466.8192 | 814.9615 | -3550 | -400 | -3135.0385 | 78.38% | 50.56% | 95% | 0% | 2172 | -408
[5 empty] | 2019-09-02 | 32 | 5871 | 1827 | -384 | 1 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -439.3593 | 903.5097 | -3550 | -400 | -3046.4903 | 76.16% | 50.56% | 95% | 0% | 2211 | -384
[5 empty] | 2019-09-02 | 33 | 5871.5 | 1921 | -347 | 1 | 0 | 2268 | 1432.1517 | 1432.1517 | 1432.1517 | 1004.5342 | 780 | 200 | 1984.5342 | 49.61% | 95% | 0% | -397.0252 | 1035.1265 | -3550 | -400 | -2914.8735 | 72.87% | 50.56% | 95% | 0% | 2268 | -347
[5 empty] | 2019-09-02 | 34 | 5872 | 2016 | -303 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 1002.9678 | 780 | 200 | 1982.9678 | 49.57% | 95% | 0% | -346.6819 | 1165.3544 | -3550 | -400 | -2784.6456 | 69.62% | 50.56% | 95% | 0% | 2319 | -303
[5 empty] | 2019-09-02 | 35 | 5872.5 | 2108 | -273 | 1 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 1002.9678 | 780 | 200 | 1982.9678 | 49.57% | 95% | 0% | -312.357 | 1296.7939 | -3550 | -400 | -2653.2061 | 66.33% | 50.56% | 95% | 0% | 2381 | -273
[5 empty] | 2019-09-02 | 36 | 5873 | 2188 | -237 | 1 | 0 | 2425 | 1678.0709 | 1678.0709 | 1678.0709 | 1002.9678 | 780 | 200 | 1982.9678 | 49.57% | 95% | 0% | -271.167 | 1406.9039 | -3550 | -400 | -2543.0961 | 63.58% | 50.55% | 95% | 0% | 2425 | -237
[5 empty] | 2019-09-02 | 37 | 5873.5 | 2207 | -213 | 1 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 1002.9678 | 780 | 200 | 1982.9678 | 49.57% | 95% | 0% | -243.7071 | 1426.532 | -3550 | -400 | -2523.468 | 63.09% | 50.55% | 95% | 0% | 2420 | -213
[5 empty] | 2019-09-02 | 38 | 5874 | 2234 | -192 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1002.9678 | 780 | 200 | 1982.9678 | 49.57% | 95% | 0% | -219.6796 | 1459.9576 | -3550 | -400 | -2490.0424 | 62.25% | 50.55% | 95% | 0% | 2426 | -192
[5 empty] | 2019-09-02 | 39 | 5874.5 | 2239 | -174 | 1 | 0 | 2413 | 1659.2745 | 1659.2745 | 1659.2745 | 1002.9678 | 780 | 200 | 1982.9678 | 49.57% | 95% | 0% | -199.0847 | 1460.1899 | -3550 | -400 | -2489.8101 | 62.25% | 50.54% | 95% | 0% | 2413 | -174
[5 empty] | 2019-09-02 | 40 | 5875 | 2240 | -167 | 1 | 0 | 2407 | 1649.8763 | 1649.8763 | 1649.8763 | 1002.9678 | 780 | 200 | 1982.9678 | 49.57% | 95% | 0% | -191.0755 | 1458.8008 | -3550 | -400 | -2491.1992 | 62.28% | 50.54% | 95% | 0% | 2407 | -167
[5 empty] | 2019-09-02 | 41 | 5875.5 | 2264 | -162 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 1002.9678 | 780 | 200 | 1982.9678 | 49.57% | 95% | 0% | -185.3547 | 1494.2826 | -3550 | -400 | -2455.7174 | 61.39% | 50.54% | 95% | 0% | 2426 | -162
[5 empty] | 2019-09-02 | 42 | 5876 | 2198 | -159 | 0 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 1002.9678 | 780 | 200 | 1982.9678 | 49.57% | 95% | 0% | -181.9222 | 1389.6359 | -2750 | -200 | -1560.3641 | 39.01% | 50.54% | 95% | 0% | 2357 | -159
[5 empty] | 2019-09-02 | 43 | 5876.5 | 2103 | -156 | 0 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 1002.9678 | 780 | 200 | 1982.9678 | 49.57% | 95% | 0% | -178.4897 | 1239.5647 | -2750 | -200 | -1710.4353 | 42.76% | 50.53% | 95% | 0% | 2259 | -156
[5 empty] | 2019-09-02 | 44 | 5877 | 1959 | -154 | 0 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -176.2014 | 1013.1638 | -2750 | -200 | -1936.8362 | 48.42% | 50.53% | 95% | 0% | 2113 | -154
[5 empty] | 2019-09-02 | 45 | 5877.5 | 1831 | -151 | 0 | 0 | 1982 | 984.1715 | 984.1715 | 984.1715 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -172.7689 | 811.4026 | -2750 | -200 | -2138.5974 | 53.46% | 50.53% | 95% | 0% | 1982 | -151
[5 empty] | 2019-09-02 | 46 | 5878 | 1699 | -147 | 0 | 0 | 1846 | 771.1459 | 771.1459 | 771.1459 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -168.1922 | 602.9537 | -2750 | -200 | -2347.0463 | 58.68% | 50.52% | 95% | 0% | 1846 | -147
[5 empty] | 2019-09-02 | 47 | 5878.5 | 1564 | -145 | 0 | 0 | 1709 | 556.554 | 556.554 | 556.554 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -165.9039 | 390.6501 | -2750 | -200 | -2559.3499 | 63.98% | 50.52% | 95% | 0% | 1709 | -145
[5 empty] | 2019-09-02 | 48 | 5879 | 1473 | -142 | 0 | 0 | 1615 | 409.3157 | 409.3157 | 409.3157 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -162.4714 | 246.8444 | -2750 | -200 | -2703.1556 | 67.58% | 50.51% | 95% | 0% | 1615 | -142
[5 empty] | 2019-09-03 | 1 | 5879.5 | 1398 | -139 | 0 | 0 | 1537 | 287.1393 | 287.1393 | 287.1393 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -159.0389 | 128.1004 | -2750 | -200 | -2821.8996 | 70.55% | 50.51% | 95% | 0% | 1537 | -139
[5 empty] | 2019-09-03 | 2 | 5880 | 1354 | -136 | 0 | 0 | 1490 | 213.5202 | 213.5202 | 213.5202 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -155.6064 | 57.9138 | -2750 | -200 | -2892.0862 | 72.3% | 50.5% | 95% | 0% | 1490 | -136
[5 empty] | 2019-09-03 | 3 | 5880.5 | 1324 | -133 | 0 | 0 | 1457 | 161.8302 | 161.8302 | 161.8302 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -152.1739 | 9.6563 | -2750 | -200 | -2940.3437 | 73.51% | 50.49% | 95% | 0% | 1457 | -133
[5 empty] | 2019-09-03 | 4 | 5881 | 1325 | -129 | 0 | 0 | 1454 | 157.1311 | 157.1311 | 157.1311 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -147.5973 | 9.5338 | -2750 | -200 | -2940.4662 | 73.51% | 50.49% | 95% | 0% | 1454 | -129
[5 empty] | 2019-09-03 | 5 | 5881.5 | 1317 | -125 | 0 | 0 | 1442 | 138.3347 | 138.3347 | 138.3347 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -143.0206 | -4.6859 | -2750 | -200 | -2954.6859 | 73.87% | 50.49% | 95% | 0% | 1442 | -125
[5 empty] | 2019-09-03 | 6 | 5882 | 1293 | -121 | 0 | 0 | 1414 | 94.4765 | 94.4765 | 94.4765 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -138.4439 | -43.9674 | -2750 | -200 | -2993.9674 | 74.85% | 50.48% | 95% | 0% | 1414 | -121
[5 empty] | 2019-09-03 | 7 | 5882.5 | 1303 | -116 | 0 | 0 | 1419 | 102.3083 | 102.3083 | 102.3083 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -132.7231 | -30.4148 | -2750 | -200 | -2980.4148 | 74.51% | 50.48% | 95% | 0% | 1419 | -116
[5 empty] | 2019-09-03 | 8 | 5883 | 1307 | -111 | 0 | 0 | 1418 | 100.742 | 100.742 | 100.742 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -127.0023 | -26.2603 | -2750 | -200 | -2976.2603 | 74.41% | 50.48% | 95% | 0% | 1418 | -111
[5 empty] | 2019-09-03 | 9 | 5883.5 | 1325 | -107 | 0 | 0 | 1432 | 122.6711 | 122.6711 | 122.6711 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -122.4256 | 0.24543 | -2750 | -200 | -2949.7546 | 73.74% | 50.48% | 95% | 0% | 1432 | -107
[5 empty] | 2019-09-03 | 10 | 5884 | 1354 | -102 | 0 | 0 | 1456 | 160.2638 | 160.2638 | 160.2638 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -116.7048 | 43.559 | -2750 | -200 | -2906.441 | 72.66% | 50.48% | 95% | 0% | 1456 | -102
[5 empty] | 2019-09-03 | 11 | 5884.5 | 1422 | -98 | 0 | 0 | 1520 | 260.5111 | 260.5111 | 260.5111 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -112.1281 | 148.383 | -2750 | -200 | -2801.617 | 70.04% | 50.48% | 95% | 0% | 1520 | -98
[5 empty] | 2019-09-03 | 12 | 5885 | 1507 | -94 | 0 | 0 | 1601 | 387.3866 | 387.3866 | 387.3866 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -107.5515 | 279.8352 | -2750 | -200 | -2670.1648 | 66.75% | 50.47% | 95% | 0% | 1601 | -94
[5 empty] | 2019-09-03 | 13 | 5885.5 | 1676 | -91 | 0 | 0 | 1767 | 647.4031 | 647.4031 | 647.4031 | 1001.4015 | 780 | 200 | 1981.4015 | 49.54% | 95% | 0% | -104.119 | 543.2841 | -2750 | -200 | -2406.7159 | 60.17% | 50.47% | 95% | 0% | 1767 | -91
[5 empty] | 2019-09-03 | 14 | 5886 | 1844 | -93 | 0 | 0 | 1937 | 913.6851 | 913.6851 | 913.6851 | 999.8351 | 780 | 200 | 1979.8351 | 49.5% | 95% | 0% | -106.4073 | 807.2778 | -2750 | -200 | -2142.7222 | 53.57% | 50.47% | 95% | 0% | 1937 | -93
[5 empty] | 2019-09-03 | 15 | 5886.5 | 2039 | -116 | 0 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 999.8351 | 780 | 200 | 1979.8351 | 49.5% | 95% | 0% | -132.7231 | 1122.4294 | -2750 | -200 | -1827.5706 | 45.69% | 50.47% | 95% | 0% | 2155 | -116
[5 empty] | 2019-09-03 | 16 | 5887 | 2108 | -154 | 1 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 999.8351 | 780 | 200 | 1979.8351 | 49.5% | 95% | 0% | -176.2014 | 1246.5521 | -3550 | -400 | -2703.4479 | 67.59% | 50.46% | 95% | 0% | 2262 | -154
[5 empty] | 2019-09-03 | 17 | 5887.5 | 2134 | -207 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 999.8351 | 780 | 200 | 1979.8351 | 49.5% | 95% | 0% | -236.8421 | 1309.6542 | -3550 | -400 | -2640.3458 | 66.01% | 50.46% | 95% | 0% | 2341 | -207
[5 empty] | 2019-09-03 | 18 | 5888 | 2076 | -262 | 1 | 0 | 2338 | 1541.7972 | 1541.7972 | 1541.7972 | 999.8351 | 780 | 200 | 1979.8351 | 49.5% | 95% | 0% | -299.7712 | 1242.026 | -3550 | -400 | -2707.974 | 67.7% | 50.46% | 95% | 0% | 2338 | -262
[5 empty] | 2019-09-03 | 19 | 5888.5 | 2004 | -330 | 1 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 999.8351 | 780 | 200 | 1979.8351 | 49.5% | 95% | 0% | -377.5744 | 1157.9574 | -3550 | -400 | -2792.0426 | 69.8% | 50.46% | 95% | 0% | 2334 | -330
[5 empty] | 2019-09-03 | 20 | 5889 | 1917 | -384 | 1 | 0 | 2301 | 1483.8417 | 1483.8417 | 1483.8417 | 999.8351 | 780 | 200 | 1979.8351 | 49.5% | 95% | 0% | -439.3593 | 1044.4824 | -3550 | -400 | -2905.5176 | 72.64% | 50.46% | 95% | 0% | 2301 | -384
[5 empty] | 2019-09-03 | 21 | 5889.5 | 1829 | -428 | 1 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 999.8351 | 780 | 200 | 1979.8351 | 49.5% | 95% | 0% | -489.7025 | 925.2192 | -3550 | -400 | -3024.7808 | 75.62% | 50.46% | 95% | 0% | 2257 | -428
[5 empty] | 2019-09-03 | 22 | 5890 | 1776 | -465 | 1 | 0 | 2241 | 1389.8599 | 1389.8599 | 1389.8599 | 999.8351 | 780 | 200 | 1979.8351 | 49.5% | 95% | 0% | -532.0366 | 857.8232 | -3550 | -400 | -3092.1768 | 77.3% | 50.45% | 95% | 0% | 2241 | -465
[5 empty] | 2019-09-03 | 23 | 5890.5 | 1777 | -463 | 1 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 999.8351 | 780 | 200 | 1979.8351 | 49.5% | 95% | 0% | -529.7483 | 858.5452 | -3550 | -400 | -3091.4548 | 77.29% | 50.45% | 95% | 0% | 2240 | -463
[5 empty] | 2019-09-03 | 24 | 5891 | 1773 | -471 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 999.8351 | 780 | 200 | 1979.8351 | 49.5% | 95% | 0% | -538.9016 | 855.6573 | -3550 | -400 | -3094.3427 | 77.36% | 50.45% | 95% | 0% | 2244 | -471
[5 empty] | 2019-09-03 | 25 | 5891.5 | 1768 | -473 | 1 | 0 | 2241 | 1389.8599 | 1389.8599 | 1389.8599 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -541.1899 | 848.6699 | -3550 | -400 | -3101.3301 | 77.53% | 50.44% | 95% | 0% | 2241 | -473
[5 empty] | 2019-09-03 | 26 | 5892 | 1740 | -487 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -557.2082 | 810.7225 | -3550 | -400 | -3139.2775 | 78.48% | 50.44% | 95% | 0% | 2227 | -487
[5 empty] | 2019-09-03 | 27 | 5892.5 | 1738 | -483 | 1 | 0 | 2221 | 1358.5326 | 1358.5326 | 1358.5326 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -552.6316 | 805.901 | -3550 | -400 | -3144.099 | 78.6% | 50.44% | 95% | 0% | 2221 | -483
[5 empty] | 2019-09-03 | 28 | 5893 | 1726 | -478 | 1 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -546.9108 | 784.9936 | -3550 | -400 | -3165.0064 | 79.13% | 50.44% | 95% | 0% | 2204 | -478
[5 empty] | 2019-09-03 | 29 | 5893.5 | 1724 | -481 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -550.3432 | 783.1275 | -3550 | -400 | -3166.8725 | 79.17% | 50.43% | 95% | 0% | 2205 | -481
[5 empty] | 2019-09-03 | 30 | 5894 | 1725 | -472 | 1 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -540.0458 | 780.8941 | -3550 | -400 | -3169.1059 | 79.23% | 50.42% | 95% | 0% | 2197 | -472
[5 empty] | 2019-09-03 | 31 | 5894.5 | 1770 | -436 | 1 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -498.8558 | 836.1813 | -3550 | -400 | -3113.8187 | 77.85% | 50.41% | 95% | 0% | 2206 | -436
[5 empty] | 2019-09-03 | 32 | 5895 | 1876 | -380 | 1 | 0 | 2256 | 1413.3553 | 1413.3553 | 1413.3553 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -434.7826 | 978.5727 | -3550 | -400 | -2971.4273 | 74.29% | 50.41% | 95% | 0% | 2256 | -380
[5 empty] | 2019-09-03 | 33 | 5895.5 | 1985 | -323 | 1 | 0 | 2308 | 1494.8063 | 1494.8063 | 1494.8063 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -369.5652 | 1125.241 | -3550 | -400 | -2824.759 | 70.62% | 50.41% | 95% | 0% | 2308 | -323
[5 empty] | 2019-09-03 | 34 | 5896 | 2079 | -294 | 1 | 0 | 2373 | 1596.62 | 1596.62 | 1596.62 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -336.3844 | 1260.2355 | -3550 | -400 | -2689.7645 | 67.24% | 50.41% | 95% | 0% | 2373 | -294
[5 empty] | 2019-09-03 | 35 | 5896.5 | 2171 | -271 | 1 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -310.0686 | 1394.6304 | -3550 | -400 | -2555.3696 | 63.88% | 50.4% | 95% | 0% | 2442 | -271
[5 empty] | 2019-09-03 | 36 | 5897 | 2228 | -232 | 1 | 0 | 2460 | 1732.8937 | 1732.8937 | 1732.8937 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -265.4462 | 1467.4474 | -3550 | -400 | -2482.5526 | 62.06% | 50.4% | 95% | 0% | 2460 | -232
[5 empty] | 2019-09-03 | 37 | 5897.5 | 2280 | -186 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -212.8146 | 1529.4772 | -3550 | -400 | -2420.5228 | 60.51% | 50.39% | 95% | 0% | 2466 | -186
[5 empty] | 2019-09-03 | 38 | 5898 | 2313 | -157 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -179.6339 | 1568.9234 | -3550 | -400 | -2381.0766 | 59.53% | 50.39% | 95% | 0% | 2470 | -157
[5 empty] | 2019-09-03 | 39 | 5898.5 | 2341 | -138 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -157.8947 | 1604.7598 | -3550 | -400 | -2345.2402 | 58.63% | 50.39% | 95% | 0% | 2479 | -138
[5 empty] | 2019-09-03 | 40 | 5899 | 2342 | -132 | 1 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -151.0297 | 1603.793 | -3550 | -400 | -2346.207 | 58.66% | 50.39% | 95% | 0% | 2474 | -132
[5 empty] | 2019-09-03 | 41 | 5899.5 | 2369 | -131 | 0 | 0 | 2500 | 1795.5482 | 1795.5482 | 1795.5482 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -149.8856 | 1645.6626 | -2750 | -200 | -1304.3374 | 32.61% | 50.39% | 95% | 0% | 2500 | -131
[5 empty] | 2019-09-03 | 42 | 5900 | 2302 | -130 | 0 | 0 | 2432 | 1689.0354 | 1689.0354 | 1689.0354 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -148.7414 | 1540.294 | -2750 | -200 | -1409.706 | 35.24% | 50.37% | 95% | 0% | 2432 | -130
[5 empty] | 2019-09-03 | 43 | 5900.5 | 2193 | -131 | 0 | 0 | 2324 | 1519.8681 | 1519.8681 | 1519.8681 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -149.8856 | 1369.9825 | -2750 | -200 | -1580.0175 | 39.5% | 50.37% | 95% | 0% | 2324 | -131
[5 empty] | 2019-09-03 | 44 | 5901 | 2055 | -132 | 0 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -151.0297 | 1154.2464 | -2750 | -200 | -1795.7536 | 44.89% | 50.37% | 95% | 0% | 2187 | -132
[5 empty] | 2019-09-03 | 45 | 5901.5 | 1926 | -132 | 0 | 0 | 2058 | 1103.2152 | 1103.2152 | 1103.2152 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -151.0297 | 952.1854 | -2750 | -200 | -1997.8146 | 49.95% | 50.36% | 95% | 0% | 2058 | -132
[5 empty] | 2019-09-03 | 46 | 5902 | 1771 | -132 | 0 | 0 | 1903 | 860.4287 | 860.4287 | 860.4287 | 998.2688 | 780 | 200 | 1978.2688 | 49.46% | 95% | 0% | -151.0297 | 709.3989 | -2750 | -200 | -2240.6011 | 56.02% | 50.36% | 95% | 0% | 1903 | -132
[5 empty] | 2019-09-03 | 47 | 5902.5 | 1644 | -132 | 0 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 996.7024 | 780 | 200 | 1976.7024 | 49.42% | 95% | 0% | -151.0297 | 510.4707 | -2750 | -200 | -2439.5293 | 60.99% | 50.36% | 95% | 0% | 1776 | -132
[5 empty] | 2019-09-03 | 48 | 5903 | 1532 | -132 | 0 | 0 | 1664 | 486.0676 | 486.0676 | 486.0676 | 996.7024 | 780 | 200 | 1976.7024 | 49.42% | 95% | 0% | -151.0297 | 335.0379 | -2750 | -200 | -2614.9621 | 65.37% | 50.35% | 95% | 0% | 1664 | -132
[5 empty] | 2019-09-04 | 1 | 5903.5 | 1449 | -131 | 0 | 0 | 1580 | 354.493 | 354.493 | 354.493 | 996.7024 | 780 | 200 | 1976.7024 | 49.42% | 95% | 0% | -149.8856 | 204.6074 | -2750 | -200 | -2745.3926 | 68.63% | 50.34% | 95% | 0% | 1580 | -131
[5 empty] | 2019-09-04 | 2 | 5904 | 1401 | -130 | 0 | 0 | 1531 | 277.7411 | 277.7411 | 277.7411 | 996.7024 | 780 | 200 | 1976.7024 | 49.42% | 95% | 0% | -148.7414 | 128.9997 | -2750 | -200 | -2821.0003 | 70.53% | 50.34% | 95% | 0% | 1531 | -130
[5 empty] | 2019-09-04 | 3 | 5904.5 | 1365 | -131 | 0 | 0 | 1496 | 222.9184 | 222.9184 | 222.9184 | 996.7024 | 780 | 200 | 1976.7024 | 49.42% | 95% | 0% | -149.8856 | 73.0328 | -2750 | -200 | -2876.9672 | 71.92% | 50.34% | 95% | 0% | 1496 | -131
[5 empty] | 2019-09-04 | 4 | 5905 | 1362 | -133 | 0 | 0 | 1495 | 221.352 | 221.352 | 221.352 | 996.7024 | 780 | 200 | 1976.7024 | 49.42% | 95% | 0% | -152.1739 | 69.1781 | -2750 | -200 | -2880.8219 | 72.02% | 50.33% | 95% | 0% | 1495 | -133
[5 empty] | 2019-09-04 | 5 | 5905.5 | 1337 | -134 | 0 | 0 | 1471 | 183.7593 | 183.7593 | 183.7593 | 996.7024 | 780 | 200 | 1976.7024 | 49.42% | 95% | 0% | -153.3181 | 30.4412 | -2750 | -200 | -2919.5588 | 72.99% | 50.32% | 95% | 0% | 1471 | -134
[5 empty] | 2019-09-04 | 6 | 5906 | 1321 | -135 | 0 | 0 | 1456 | 160.2638 | 160.2638 | 160.2638 | 996.7024 | 780 | 200 | 1976.7024 | 49.42% | 95% | 0% | -154.4622 | 5.8016 | -2750 | -200 | -2944.1984 | 73.6% | 50.32% | 95% | 0% | 1456 | -135
[5 empty] | 2019-09-04 | 7 | 5906.5 | 1310 | -135 | 0 | 0 | 1445 | 143.0338 | 143.0338 | 143.0338 | 996.7024 | 780 | 200 | 1976.7024 | 49.42% | 95% | 0% | -154.4622 | -11.4284 | -2750 | -200 | -2961.4284 | 74.04% | 50.32% | 95% | 0% | 1445 | -135
[5 empty] | 2019-09-04 | 8 | 5907 | 1310 | -136 | 0 | 0 | 1446 | 144.6002 | 144.6002 | 144.6002 | 996.7024 | 780 | 200 | 1976.7024 | 49.42% | 95% | 0% | -155.6064 | -11.0062 | -2750 | -200 | -2961.0062 | 74.03% | 50.31% | 95% | 0% | 1446 | -136
[5 empty] | 2019-09-04 | 9 | 5907.5 | 1307 | -135 | 0 | 0 | 1442 | 138.3347 | 138.3347 | 138.3347 | 996.7024 | 780 | 200 | 1976.7024 | 49.42% | 95% | 0% | -154.4622 | -16.1275 | -2750 | -200 | -2966.1275 | 74.15% | 50.31% | 95% | 0% | 1442 | -135
[5 empty] | 2019-09-04 | 10 | 5908 | 1324 | -134 | 0 | 0 | 1458 | 163.3965 | 163.3965 | 163.3965 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -153.3181 | 10.0785 | -2750 | -200 | -2939.9215 | 73.5% | 50.31% | 95% | 0% | 1458 | -134
[5 empty] | 2019-09-04 | 11 | 5908.5 | 1372 | -133 | 0 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -152.1739 | 84.8418 | -2750 | -200 | -2865.1582 | 71.63% | 50.3% | 95% | 0% | 1505 | -133
[5 empty] | 2019-09-04 | 12 | 5909 | 1451 | -132 | 0 | 0 | 1583 | 359.1921 | 359.1921 | 359.1921 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -151.0297 | 208.1623 | -2750 | -200 | -2741.8377 | 68.55% | 50.3% | 95% | 0% | 1583 | -132
[5 empty] | 2019-09-04 | 13 | 5909.5 | 1643 | -132 | 0 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -151.0297 | 508.9043 | -2750 | -200 | -2441.0957 | 61.03% | 50.3% | 95% | 0% | 1775 | -132
[5 empty] | 2019-09-04 | 14 | 5910 | 1804 | -135 | 0 | 0 | 1939 | 916.8178 | 916.8178 | 916.8178 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -154.4622 | 762.3556 | -2750 | -200 | -2187.6444 | 54.69% | 50.3% | 95% | 0% | 1939 | -135
[5 empty] | 2019-09-04 | 15 | 5910.5 | 2016 | -155 | 0 | 0 | 2171 | 1280.2143 | 1280.2143 | 1280.2143 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -177.3455 | 1102.8688 | -2750 | -200 | -1847.1312 | 46.18% | 50.29% | 95% | 0% | 2171 | -155
[5 empty] | 2019-09-04 | 16 | 5911 | 2083 | -188 | 0 | 0 | 2271 | 1436.8508 | 1436.8508 | 1436.8508 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -215.103 | 1221.7478 | -2750 | -200 | -1728.2522 | 43.21% | 50.28% | 95% | 0% | 2271 | -188
[5 empty] | 2019-09-04 | 17 | 5911.5 | 2067 | -245 | 1 | 0 | 2312 | 1501.0717 | 1501.0717 | 1501.0717 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -280.3204 | 1220.7514 | -3550 | -400 | -2729.2486 | 68.23% | 50.28% | 95% | 0% | 2312 | -245
[5 empty] | 2019-09-04 | 18 | 5912 | 1932 | -332 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -379.8627 | 1046.0235 | -3550 | -400 | -2903.9765 | 72.6% | 50.27% | 95% | 0% | 2264 | -332
[5 empty] | 2019-09-04 | 19 | 5912.5 | 1856 | -379 | 1 | 0 | 2235 | 1380.4617 | 1380.4617 | 1380.4617 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -433.6384 | 946.8232 | -3550 | -400 | -3003.1768 | 75.08% | 50.27% | 95% | 0% | 2235 | -379
[5 empty] | 2019-09-04 | 20 | 5913 | 1735 | -449 | 1 | 0 | 2184 | 1300.5771 | 1300.5771 | 1300.5771 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -513.73 | 786.8471 | -3550 | -400 | -3163.1529 | 79.08% | 50.27% | 95% | 0% | 2184 | -449
[5 empty] | 2019-09-04 | 21 | 5913.5 | 1582 | -530 | 1 | 0 | 2112 | 1187.7988 | 1187.7988 | 1187.7988 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -606.4073 | 581.3915 | -3550 | -400 | -3368.6085 | 84.22% | 50.27% | 95% | 0% | 2112 | -530
[5 empty] | 2019-09-04 | 22 | 5914 | 1452 | -620 | 1 | 0 | 2072 | 1125.1443 | 1125.1443 | 1125.1443 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -709.3822 | 415.7621 | -3550 | -400 | -3534.2379 | 88.36% | 50.26% | 95% | 0% | 2072 | -620
[5 empty] | 2019-09-04 | 23 | 5914.5 | 1407 | -660 | 1 | 0 | 2067 | 1117.3124 | 1117.3124 | 1117.3124 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -755.1487 | 362.1637 | -3550 | -400 | -3587.8363 | 89.7% | 50.26% | 95% | 0% | 2067 | -660
[5 empty] | 2019-09-04 | 24 | 5915 | 1309 | -701 | 1 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -802.0595 | 225.9702 | -3550 | -400 | -3724.0298 | 93.1% | 50.26% | 95% | 0% | 2010 | -701
[5 empty] | 2019-09-04 | 25 | 5915.5 | 1266 | -726 | 1 | 0 | 1992 | 999.8351 | 999.8351 | 999.8351 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -830.6636 | 169.1715 | -3550 | -400 | -3780.8285 | 94.52% | 50.25% | 95% | 0% | 1992 | -726
[5 empty] | 2019-09-04 | 26 | 5916 | 1226 | -738 | 1 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 995.136 | 780 | 200 | 1975.136 | 49.38% | 95% | 0% | -844.3936 | 111.5833 | -3550 | -400 | -3838.4167 | 95.96% | 50.25% | 95% | 0% | 1964 | -738
[5 empty] | 2019-09-04 | 27 | 5916.5 | 1274 | -693 | 1 | 0 | 1967 | 960.676 | 960.676 | 960.676 | 993.5697 | 780 | 200 | 1973.5697 | 49.34% | 95% | 0% | -792.9062 | 167.7698 | -3550 | -400 | -3782.2302 | 94.56% | 50.24% | 95% | 0% | 1967 | -693
[5 empty] | 2019-09-04 | 28 | 5917 | 1283 | -662 | 1 | 0 | 1945 | 926.216 | 926.216 | 926.216 | 993.5697 | 780 | 200 | 1973.5697 | 49.34% | 95% | 0% | -757.4371 | 168.7789 | -3550 | -400 | -3781.2211 | 94.53% | 50.24% | 95% | 0% | 1945 | -662
[5 empty] | 2019-09-04 | 29 | 5917.5 | 1300 | -636 | 1 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 993.5697 | 780 | 200 | 1973.5697 | 49.34% | 95% | 0% | -727.6888 | 184.4299 | -3550 | -400 | -3765.5701 | 94.14% | 50.24% | 95% | 0% | 1936 | -636
[5 empty] | 2019-09-04 | 30 | 5918 | 1333 | -624 | 1 | 0 | 1957 | 945.0124 | 945.0124 | 945.0124 | 993.5697 | 780 | 200 | 1973.5697 | 49.34% | 95% | 0% | -713.9588 | 231.0536 | -3550 | -400 | -3718.9464 | 92.97% | 50.24% | 95% | 0% | 1957 | -624
[5 empty] | 2019-09-04 | 31 | 5918.5 | 1383 | -588 | 1 | 0 | 1971 | 966.9415 | 966.9415 | 966.9415 | 993.5697 | 780 | 200 | 1973.5697 | 49.34% | 95% | 0% | -672.7689 | 294.1726 | -3550 | -400 | -3655.8274 | 91.4% | 50.24% | 95% | 0% | 1971 | -588
[5 empty] | 2019-09-04 | 32 | 5919 | 1485 | -545 | 1 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 993.5697 | 780 | 200 | 1973.5697 | 49.34% | 95% | 0% | -623.5698 | 435.7872 | -3550 | -400 | -3514.2128 | 87.86% | 50.23% | 95% | 0% | 2030 | -545
[5 empty] | 2019-09-04 | 33 | 5919.5 | 1604 | -498 | 1 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 993.5697 | 780 | 200 | 1973.5697 | 49.34% | 95% | 0% | -569.7941 | 602.3412 | -3550 | -400 | -3347.6588 | 83.69% | 50.23% | 95% | 0% | 2102 | -498
[5 empty] | 2019-09-04 | 34 | 5920 | 1771 | -440 | 1 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 993.5697 | 780 | 200 | 1973.5697 | 49.34% | 95% | 0% | -503.4325 | 839.4364 | -3550 | -400 | -3110.5636 | 77.76% | 50.23% | 95% | 0% | 2211 | -440
[5 empty] | 2019-09-04 | 35 | 5920.5 | 1877 | -392 | 1 | 0 | 2269 | 1433.7181 | 1433.7181 | 1433.7181 | 993.5697 | 780 | 200 | 1973.5697 | 49.34% | 95% | 0% | -448.5126 | 985.2055 | -3550 | -400 | -2964.7945 | 74.12% | 50.23% | 95% | 0% | 2269 | -392
[5 empty] | 2019-09-04 | 36 | 5921 | 1975 | -321 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 993.5697 | 780 | 200 | 1973.5697 | 49.34% | 95% | 0% | -367.2769 | 1108.733 | -3550 | -400 | -2841.267 | 71.03% | 50.22% | 95% | 0% | 2296 | -321
[5 empty] | 2019-09-04 | 37 | 5921.5 | 2042 | -289 | 1 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 993.5697 | 780 | 200 | 1973.5697 | 49.34% | 95% | 0% | -330.6636 | 1200.169 | -3550 | -400 | -2749.831 | 68.75% | 50.22% | 95% | 0% | 2331 | -289
[5 empty] | 2019-09-04 | 38 | 5922 | 2096 | -251 | 1 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 993.5697 | 780 | 200 | 1973.5697 | 49.34% | 95% | 0% | -287.1854 | 1268.7091 | -3550 | -400 | -2681.2909 | 67.03% | 50.22% | 95% | 0% | 2347 | -251
[5 empty] | 2019-09-04 | 39 | 5922.5 | 2129 | -220 | 1 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 992.0033 | 780 | 200 | 1972.0033 | 49.3% | 95% | 0% | -251.7162 | 1307.311 | -3550 | -400 | -2642.689 | 66.07% | 50.21% | 95% | 0% | 2349 | -220
[5 empty] | 2019-09-04 | 40 | 5923 | 2145 | -204 | 1 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 992.0033 | 780 | 200 | 1972.0033 | 49.3% | 95% | 0% | -233.4096 | 1325.6176 | -3550 | -400 | -2624.3824 | 65.61% | 50.21% | 95% | 0% | 2349 | -204
[5 empty] | 2019-09-04 | 41 | 5923.5 | 2183 | -200 | 1 | 0 | 2383 | 1612.2836 | 1612.2836 | 1612.2836 | 992.0033 | 780 | 200 | 1972.0033 | 49.3% | 95% | 0% | -228.833 | 1383.4506 | -3550 | -400 | -2566.5494 | 64.16% | 50.21% | 95% | 0% | 2383 | -200
[5 empty] | 2019-09-04 | 42 | 5924 | 2113 | -198 | 1 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 992.0033 | 780 | 200 | 1972.0033 | 49.3% | 95% | 0% | -226.5446 | 1272.9607 | -3550 | -400 | -2677.0393 | 66.93% | 50.2% | 95% | 0% | 2311 | -198
[5 empty] | 2019-09-04 | 43 | 5924.5 | 1996 | -198 | 0 | 0 | 2194 | 1316.2407 | 1316.2407 | 1316.2407 | 992.0033 | 780 | 200 | 1972.0033 | 49.3% | 95% | 0% | -226.5446 | 1089.6961 | -2750 | -200 | -1860.3039 | 46.51% | 50.2% | 95% | 0% | 2194 | -198
[5 empty] | 2019-09-04 | 44 | 5925 | 1865 | -198 | 0 | 0 | 2063 | 1111.047 | 1111.047 | 1111.047 | 992.0033 | 780 | 200 | 1972.0033 | 49.3% | 95% | 0% | -226.5446 | 884.5024 | -2750 | -200 | -2065.4976 | 51.64% | 50.2% | 95% | 0% | 2063 | -198
[5 empty] | 2019-09-04 | 45 | 5925.5 | 1744 | -195 | 0 | 0 | 1939 | 916.8178 | 916.8178 | 916.8178 | 992.0033 | 780 | 200 | 1972.0033 | 49.3% | 95% | 0% | -223.1121 | 693.7057 | -2750 | -200 | -2256.2943 | 56.41% | 50.19% | 95% | 0% | 1939 | -195
[5 empty] | 2019-09-04 | 46 | 5926 | 1613 | -192 | 0 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 992.0033 | 780 | 200 | 1972.0033 | 49.3% | 95% | 0% | -219.6796 | 487.2453 | -2750 | -200 | -2462.7547 | 61.57% | 50.19% | 95% | 0% | 1805 | -192
[5 empty] | 2019-09-04 | 47 | 5926.5 | 1482 | -190 | 0 | 0 | 1672 | 498.5985 | 498.5985 | 498.5985 | 992.0033 | 780 | 200 | 1972.0033 | 49.3% | 95% | 0% | -217.3913 | 281.2072 | -2750 | -200 | -2668.7928 | 66.72% | 50.18% | 95% | 0% | 1672 | -190
[5 empty] | 2019-09-04 | 48 | 5927 | 1397 | -189 | 0 | 0 | 1586 | 363.8912 | 363.8912 | 363.8912 | 992.0033 | 780 | 200 | 1972.0033 | 49.3% | 95% | 0% | -216.2471 | 147.644 | -2750 | -200 | -2802.356 | 70.06% | 50.18% | 95% | 0% | 1586 | -189
[5 empty] | 2019-09-05 | 1 | 5927.5 | 1320 | -181 | 1 | 0 | 1501 | 230.7502 | 230.7502 | 230.7502 | 990.4369 | 780 | 200 | 1970.4369 | 49.26% | 95% | 0% | -207.0938 | 23.6564 | -3550 | -400 | -3926.3436 | 98.16% | 50.18% | 95% | 0% | 1501 | -181
[5 empty] | 2019-09-05 | 2 | 5928 | 1277 | -174 | 1 | 0 | 1451 | 152.432 | 152.432 | 152.432 | 990.4369 | 780 | 200 | 1970.4369 | 49.26% | 95% | 0% | -199.0847 | -46.6527 | -3550 | -400 | -3996.6527 | 99.92% | 50.18% | 95% | 0% | 1451 | -174
[5 empty] | 2019-09-05 | 3 | 5928.5 | 1254 | -172 | 1 | 0 | 1426 | 113.2729 | 113.2729 | 113.2729 | 990.4369 | 780 | 200 | 1970.4369 | 49.26% | 95% | 0% | -196.7963 | -83.5235 | -3550 | -400 | -4033.5235 | 100.8% | 50.18% | 95% | 0% | 1426 | -172
[5 empty] | 2019-09-05 | 4 | 5929 | 1240 | -170 | 1 | 0 | 1410 | 88.211 | 88.211 | 88.211 | 990.4369 | 780 | 200 | 1970.4369 | 49.26% | 95% | 0% | -194.508 | -106.297 | -3550 | -400 | -4056.297 | 101.4% | 50.18% | 95% | 0% | 1410 | -170
[5 empty] | 2019-09-05 | 5 | 5929.5 | 1235 | -167 | 1 | 0 | 1402 | 75.6801 | 75.6801 | 75.6801 | 990.4369 | 780 | 200 | 1970.4369 | 49.26% | 95% | 0% | -191.0755 | -115.3954 | -3550 | -400 | -4065.3954 | 101.6% | 50.17% | 95% | 0% | 1402 | -167
[5 empty] | 2019-09-05 | 6 | 5930 | 1236 | -164 | 1 | 0 | 1400 | 72.5474 | 72.5474 | 72.5474 | 990.4369 | 780 | 200 | 1970.4369 | 49.26% | 95% | 0% | -187.643 | -115.0956 | -3550 | -400 | -4065.0956 | 101.6% | 50.17% | 95% | 0% | 1400 | -164
[5 empty] | 2019-09-05 | 7 | 5930.5 | 1221 | -160 | 1 | 0 | 1381 | 42.7865 | 42.7865 | 42.7865 | 990.4369 | 780 | 200 | 1970.4369 | 49.26% | 95% | 0% | -183.0664 | -140.2799 | -3550 | -400 | -4090.2799 | 102.3% | 50.16% | 95% | 0% | 1381 | -160
[5 empty] | 2019-09-05 | 8 | 5931 | 1231 | -157 | 1 | 0 | 1388 | 53.751 | 53.751 | 53.751 | 990.4369 | 780 | 200 | 1970.4369 | 49.26% | 95% | 0% | -179.6339 | -125.8828 | -3550 | -400 | -4075.8828 | 101.9% | 50.15% | 95% | 0% | 1388 | -157
[5 empty] | 2019-09-05 | 9 | 5931.5 | 1250 | -150 | 1 | 0 | 1400 | 72.5474 | 72.5474 | 72.5474 | 990.4369 | 780 | 200 | 1970.4369 | 49.26% | 95% | 0% | -171.6247 | -99.0773 | -3550 | -400 | -4049.0773 | 101.2% | 50.15% | 95% | 0% | 1400 | -150
[5 empty] | 2019-09-05 | 10 | 5932 | 1280 | -142 | 1 | 0 | 1422 | 107.0074 | 107.0074 | 107.0074 | 990.4369 | 780 | 200 | 1970.4369 | 49.26% | 95% | 0% | -162.4714 | -55.464 | -3550 | -400 | -4005.464 | 100.1% | 50.14% | 95% | 0% | 1422 | -142
[5 empty] | 2019-09-05 | 11 | 5932.5 | 1355 | -139 | 1 | 0 | 1494 | 219.7857 | 219.7857 | 219.7857 | 990.4369 | 780 | 200 | 1970.4369 | 49.26% | 95% | 0% | -159.0389 | 60.7468 | -3550 | -400 | -3889.2532 | 97.23% | 50.14% | 95% | 0% | 1494 | -139
[5 empty] | 2019-09-05 | 12 | 5933 | 1434 | -136 | 1 | 0 | 1570 | 338.8293 | 338.8293 | 338.8293 | 990.4369 | 780 | 200 | 1970.4369 | 49.26% | 95% | 0% | -155.6064 | 183.2229 | -3550 | -400 | -3766.7771 | 94.17% | 50.13% | 95% | 0% | 1570 | -136
[5 empty] | 2019-09-05 | 13 | 5933.5 | 1635 | -133 | 1 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -152.1739 | 496.7956 | -3550 | -400 | -3453.2044 | 86.33% | 50.13% | 95% | 0% | 1768 | -133
[5 empty] | 2019-09-05 | 14 | 5934 | 1799 | -141 | 1 | 0 | 1940 | 918.3842 | 918.3842 | 918.3842 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -161.3272 | 757.0569 | -3550 | -400 | -3192.9431 | 79.82% | 50.13% | 95% | 0% | 1940 | -141
[5 empty] | 2019-09-05 | 15 | 5934.5 | 1975 | -185 | 1 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -211.6705 | 1051.3139 | -3550 | -400 | -2898.6861 | 72.47% | 50.13% | 95% | 0% | 2160 | -185
[5 empty] | 2019-09-05 | 16 | 5935 | 1977 | -245 | 1 | 0 | 2222 | 1360.0989 | 1360.0989 | 1360.0989 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -280.3204 | 1079.7786 | -3550 | -400 | -2870.2214 | 71.76% | 50.13% | 95% | 0% | 2222 | -245
[5 empty] | 2019-09-05 | 17 | 5935.5 | 1940 | -319 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -364.9886 | 1053.0659 | -3550 | -400 | -2896.9341 | 72.42% | 50.12% | 95% | 0% | 2259 | -319
[5 empty] | 2019-09-05 | 18 | 5936 | 1831 | -400 | 1 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -457.6659 | 916.5303 | -3550 | -400 | -3033.4697 | 75.84% | 50.12% | 95% | 0% | 2231 | -400
[5 empty] | 2019-09-05 | 19 | 5936.5 | 1726 | -463 | 1 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -529.7483 | 778.6606 | -3550 | -400 | -3171.3394 | 79.28% | 50.12% | 95% | 0% | 2189 | -463
[5 empty] | 2019-09-05 | 20 | 5937 | 1637 | -528 | 1 | 0 | 2165 | 1270.8162 | 1270.8162 | 1270.8162 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -604.119 | 666.6972 | -3550 | -400 | -3283.3028 | 82.08% | 50.11% | 95% | 0% | 2165 | -528
[5 empty] | 2019-09-05 | 21 | 5937.5 | 1563 | -562 | 1 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -643.0206 | 565.141 | -3550 | -400 | -3384.859 | 84.62% | 50.11% | 95% | 0% | 2125 | -562
[5 empty] | 2019-09-05 | 22 | 5938 | 1509 | -587 | 1 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -671.6247 | 491.1123 | -3550 | -400 | -3458.8877 | 86.47% | 50.11% | 95% | 0% | 2096 | -587
[5 empty] | 2019-09-05 | 23 | 5938.5 | 1458 | -629 | 1 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -719.6796 | 428.9601 | -3550 | -400 | -3521.0399 | 88.03% | 50.11% | 95% | 0% | 2087 | -629
[5 empty] | 2019-09-05 | 24 | 5939 | 1435 | -638 | 1 | 0 | 2073 | 1126.7106 | 1126.7106 | 1126.7106 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -729.9771 | 396.7335 | -3550 | -400 | -3553.2665 | 88.83% | 50.1% | 95% | 0% | 2073 | -638
[5 empty] | 2019-09-05 | 25 | 5939.5 | 1438 | -648 | 1 | 0 | 2086 | 1147.0734 | 1147.0734 | 1147.0734 | 988.8706 | 780 | 200 | 1968.8706 | 49.22% | 95% | 0% | -741.4188 | 405.6546 | -3550 | -400 | -3544.3454 | 88.61% | 50.1% | 95% | 0% | 2086 | -648
[5 empty] | 2019-09-05 | 26 | 5940 | 1458 | -640 | 1 | 0 | 2098 | 1165.8697 | 1165.8697 | 1165.8697 | 987.3042 | 780 | 200 | 1967.3042 | 49.18% | 95% | 0% | -732.2654 | 433.6043 | -3550 | -400 | -3516.3957 | 87.91% | 50.1% | 95% | 0% | 2098 | -640
[5 empty] | 2019-09-05 | 27 | 5940.5 | 1417 | -644 | 1 | 0 | 2061 | 1107.9143 | 1107.9143 | 1107.9143 | 987.3042 | 780 | 200 | 1967.3042 | 49.18% | 95% | 0% | -736.8421 | 371.0722 | -3550 | -400 | -3578.9278 | 89.47% | 50.1% | 95% | 0% | 2061 | -644
[5 empty] | 2019-09-05 | 28 | 5941 | 1417 | -630 | 1 | 0 | 2047 | 1085.9852 | 1085.9852 | 1085.9852 | 987.3042 | 780 | 200 | 1967.3042 | 49.18% | 95% | 0% | -720.8238 | 365.1614 | -3550 | -400 | -3584.8386 | 89.62% | 50.1% | 95% | 0% | 2047 | -630
[5 empty] | 2019-09-05 | 29 | 5941.5 | 1446 | -578 | 1 | 0 | 2024 | 1049.9588 | 1049.9588 | 1049.9588 | 987.3042 | 780 | 200 | 1967.3042 | 49.18% | 95% | 0% | -661.3272 | 388.6315 | -3550 | -400 | -3561.3685 | 89.03% | 50.1% | 95% | 0% | 2024 | -578
[5 empty] | 2019-09-05 | 30 | 5942 | 1412 | -590 | 1 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 987.3042 | 780 | 200 | 1967.3042 | 49.18% | 95% | 0% | -675.0572 | 340.4416 | -3550 | -400 | -3609.5584 | 90.24% | 50.1% | 95% | 0% | 2002 | -590
[5 empty] | 2019-09-05 | 31 | 5942.5 | 1421 | -567 | 1 | 0 | 1988 | 993.5697 | 993.5697 | 993.5697 | 987.3042 | 780 | 200 | 1967.3042 | 49.18% | 95% | 0% | -648.7414 | 344.8282 | -3550 | -400 | -3605.1718 | 90.13% | 50.09% | 95% | 0% | 1988 | -567
[5 empty] | 2019-09-05 | 32 | 5943 | 1505 | -535 | 1 | 0 | 2040 | 1075.0206 | 1075.0206 | 1075.0206 | 987.3042 | 780 | 200 | 1967.3042 | 49.18% | 95% | 0% | -612.1281 | 462.8925 | -3550 | -400 | -3487.1075 | 87.18% | 50.09% | 95% | 0% | 2040 | -535
[5 empty] | 2019-09-05 | 33 | 5943.5 | 1631 | -496 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 987.3042 | 780 | 200 | 1967.3042 | 49.18% | 95% | 0% | -567.5057 | 643.7886 | -3550 | -400 | -3306.2114 | 82.66% | 50.08% | 95% | 0% | 2127 | -496
[5 empty] | 2019-09-05 | 34 | 5944 | 1764 | -453 | 1 | 0 | 2217 | 1352.2671 | 1352.2671 | 1352.2671 | 987.3042 | 780 | 200 | 1967.3042 | 49.18% | 95% | 0% | -518.3066 | 833.9605 | -3550 | -400 | -3116.0395 | 77.9% | 50.08% | 95% | 0% | 2217 | -453
[5 empty] | 2019-09-05 | 35 | 5944.5 | 1941 | -364 | 1 | 0 | 2305 | 1490.1072 | 1490.1072 | 1490.1072 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -416.476 | 1073.6312 | -3550 | -400 | -2876.3688 | 71.91% | 50.08% | 95% | 0% | 2305 | -364
[5 empty] | 2019-09-05 | 36 | 5945 | 2044 | -303 | 1 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -346.6819 | 1209.2126 | -3550 | -400 | -2740.7874 | 68.52% | 50.08% | 95% | 0% | 2347 | -303
[5 empty] | 2019-09-05 | 37 | 5945.5 | 2138 | -242 | 1 | 0 | 2380 | 1607.5845 | 1607.5845 | 1607.5845 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -276.8879 | 1330.6966 | -3550 | -400 | -2619.3034 | 65.48% | 50.07% | 95% | 0% | 2380 | -242
[5 empty] | 2019-09-05 | 38 | 5946 | 2251 | -175 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -200.2288 | 1479.4084 | -3550 | -400 | -2470.5916 | 61.76% | 50.07% | 95% | 0% | 2426 | -175
[5 empty] | 2019-09-05 | 39 | 5946.5 | 2320 | -137 | 1 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -156.7506 | 1571.444 | -3550 | -400 | -2378.556 | 59.46% | 50.07% | 95% | 0% | 2457 | -137
[5 empty] | 2019-09-05 | 40 | 5947 | 2356 | -124 | 1 | 0 | 2480 | 1764.2209 | 1764.2209 | 1764.2209 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -141.8764 | 1622.3445 | -3550 | -400 | -2327.6555 | 58.19% | 50.07% | 95% | 0% | 2480 | -124
[5 empty] | 2019-09-05 | 41 | 5947.5 | 2378 | -124 | 0 | 0 | 2502 | 1798.681 | 1798.681 | 1798.681 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -141.8764 | 1656.8045 | -2750 | -200 | -1293.1955 | 32.33% | 50.07% | 95% | 0% | 2502 | -124
[5 empty] | 2019-09-05 | 42 | 5948 | 2304 | -124 | 0 | 0 | 2428 | 1682.77 | 1682.77 | 1682.77 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -141.8764 | 1540.8936 | -2750 | -200 | -1409.1064 | 35.23% | 50.06% | 95% | 0% | 2428 | -124
[5 empty] | 2019-09-05 | 43 | 5948.5 | 2201 | -127 | 0 | 0 | 2328 | 1526.1336 | 1526.1336 | 1526.1336 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -145.3089 | 1380.8246 | -2750 | -200 | -1569.1754 | 39.23% | 50.06% | 95% | 0% | 2328 | -127
[5 empty] | 2019-09-05 | 44 | 5949 | 2093 | -130 | 0 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -148.7414 | 1212.9239 | -2750 | -200 | -1737.0761 | 43.43% | 50.06% | 95% | 0% | 2223 | -130
[5 empty] | 2019-09-05 | 45 | 5949.5 | 1949 | -135 | 0 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -154.4622 | 989.4784 | -2750 | -200 | -1960.5216 | 49.01% | 50.05% | 95% | 0% | 2084 | -135
[5 empty] | 2019-09-05 | 46 | 5950 | 1803 | -139 | 0 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -159.0389 | 762.478 | -2750 | -200 | -2187.522 | 54.69% | 50.05% | 95% | 0% | 1942 | -139
[5 empty] | 2019-09-05 | 47 | 5950.5 | 1642 | -143 | 0 | 0 | 1785 | 675.5977 | 675.5977 | 675.5977 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -163.6156 | 511.9821 | -2750 | -200 | -2438.0179 | 60.95% | 50.05% | 95% | 0% | 1785 | -143
[5 empty] | 2019-09-05 | 48 | 5951 | 1519 | -148 | 0 | 0 | 1667 | 490.7667 | 490.7667 | 490.7667 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -169.3364 | 321.4303 | -2750 | -200 | -2628.5697 | 65.71% | 50.04% | 95% | 0% | 1667 | -148
[5 empty] | 2019-09-06 | 1 | 5951.5 | 1420 | -151 | 0 | 0 | 1571 | 340.3957 | 340.3957 | 340.3957 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -172.7689 | 167.6268 | -2750 | -200 | -2782.3732 | 69.56% | 50.03% | 95% | 0% | 1571 | -151
[5 empty] | 2019-09-06 | 2 | 5952 | 1356 | -154 | 0 | 0 | 1510 | 244.8475 | 244.8475 | 244.8475 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -176.2014 | 68.6461 | -2750 | -200 | -2881.3539 | 72.03% | 50.03% | 95% | 0% | 1510 | -154
[5 empty] | 2019-09-06 | 3 | 5952.5 | 1296 | -158 | 0 | 0 | 1454 | 157.1311 | 157.1311 | 157.1311 | 985.7378 | 780 | 200 | 1965.7378 | 49.14% | 95% | 0% | -180.778 | -23.647 | -2750 | -200 | -2973.647 | 74.34% | 50.02% | 95% | 0% | 1454 | -158
[5 empty] | 2019-09-06 | 4 | 5953 | 1275 | -162 | 0 | 0 | 1437 | 130.5029 | 130.5029 | 130.5029 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -185.3547 | -54.8518 | -2750 | -200 | -3004.8518 | 75.12% | 50.02% | 95% | 0% | 1437 | -162
[5 empty] | 2019-09-06 | 5 | 5953.5 | 1246 | -164 | 0 | 0 | 1410 | 88.211 | 88.211 | 88.211 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -187.643 | -99.432 | -2750 | -200 | -3049.432 | 76.24% | 50.02% | 95% | 0% | 1410 | -164
[5 empty] | 2019-09-06 | 6 | 5954 | 1218 | -165 | 0 | 0 | 1383 | 45.9192 | 45.9192 | 45.9192 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -188.7872 | -142.868 | -2750 | -200 | -3092.868 | 77.32% | 50.02% | 95% | 0% | 1383 | -165
[5 empty] | 2019-09-06 | 7 | 5954.5 | 1201 | -167 | 0 | 0 | 1368 | 22.4237 | 22.4237 | 22.4237 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -191.0755 | -168.6518 | -2750 | -200 | -3118.6518 | 77.97% | 50.02% | 95% | 0% | 1368 | -167
[5 empty] | 2019-09-06 | 8 | 5955 | 1190 | -169 | 0 | 0 | 1359 | 8.3265 | 8.3265 | 8.3265 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -193.3638 | -185.0374 | -2750 | -200 | -3135.0374 | 78.38% | 50.02% | 95% | 0% | 1359 | -169
[5 empty] | 2019-09-06 | 9 | 5955.5 | 1182 | -166 | 0 | 0 | 1348 | -8.9035 | -8.9035 | -8.9035 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -189.9314 | -198.8349 | -2750 | -200 | -3148.8349 | 78.72% | 50.01% | 95% | 0% | 1348 | -166
[5 empty] | 2019-09-06 | 10 | 5956 | 1200 | -164 | 0 | 0 | 1364 | 16.1583 | 16.1583 | 16.1583 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -187.643 | -171.4847 | -2750 | -200 | -3121.4847 | 78.04% | 50.01% | 95% | 0% | 1364 | -164
[5 empty] | 2019-09-06 | 11 | 5956.5 | 1264 | -164 | 0 | 0 | 1428 | 116.4056 | 116.4056 | 116.4056 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -187.643 | -71.2374 | -2750 | -200 | -3021.2374 | 75.53% | 50.01% | 95% | 0% | 1428 | -164
[5 empty] | 2019-09-06 | 12 | 5957 | 1353 | -163 | 0 | 0 | 1516 | 254.2457 | 254.2457 | 254.2457 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -186.4989 | 67.7468 | -2750 | -200 | -2882.2532 | 72.06% | 50.01% | 95% | 0% | 1516 | -163
[5 empty] | 2019-09-06 | 13 | 5957.5 | 1544 | -163 | 0 | 0 | 1707 | 553.4213 | 553.4213 | 553.4213 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -186.4989 | 366.9224 | -2750 | -200 | -2583.0776 | 64.58% | 50.01% | 95% | 0% | 1707 | -163
[5 empty] | 2019-09-06 | 14 | 5958 | 1708 | -165 | 0 | 0 | 1873 | 813.4378 | 813.4378 | 813.4378 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -188.7872 | 624.6506 | -2750 | -200 | -2325.3494 | 58.13% | 50.01% | 95% | 0% | 1873 | -165
[5 empty] | 2019-09-06 | 15 | 5958.5 | 1918 | -178 | 0 | 0 | 2096 | 1162.737 | 1162.737 | 1162.737 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -203.6613 | 959.0757 | -2750 | -200 | -1990.9243 | 49.77% | 50.01% | 95% | 0% | 2096 | -178
[5 empty] | 2019-09-06 | 16 | 5959 | 2016 | -198 | 0 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 984.1715 | 780 | 200 | 1964.1715 | 49.1% | 95% | 0% | -226.5446 | 1121.0234 | -2750 | -200 | -1828.9766 | 45.72% | 50% | 95% | 0% | 2214 | -198
[5 empty] | 2019-09-06 | 17 | 5959.5 | 2079 | -226 | 1 | 0 | 2305 | 1490.1072 | 1490.1072 | 1490.1072 | 982.6051 | 780 | 200 | 1962.6051 | 49.07% | 95% | 0% | -258.5812 | 1231.5259 | -3550 | -400 | -2718.4741 | 67.96% | 50% | 95% | 0% | 2305 | -226
[5 empty] | 2019-09-06 | 18 | 5960 | 2080 | -249 | 1 | 0 | 2329 | 1527.6999 | 1527.6999 | 1527.6999 | 982.6051 | 780 | 200 | 1962.6051 | 49.07% | 95% | 0% | -284.897 | 1242.8029 | -3550 | -400 | -2707.1971 | 67.68% | 49.99% | 95% | 0% | 2329 | -249
[5 empty] | 2019-09-06 | 19 | 5960.5 | 2087 | -267 | 1 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 982.6051 | 780 | 200 | 1962.6051 | 49.07% | 95% | 0% | -305.492 | 1261.367 | -3550 | -400 | -2688.633 | 67.22% | 49.99% | 95% | 0% | 2354 | -267
[5 empty] | 2019-09-06 | 20 | 5961 | 2038 | -306 | 1 | 0 | 2344 | 1551.1954 | 1551.1954 | 1551.1954 | 982.6051 | 780 | 200 | 1962.6051 | 49.07% | 95% | 0% | -350.1144 | 1201.081 | -3550 | -400 | -2748.919 | 68.72% | 49.99% | 95% | 0% | 2344 | -306
[5 empty] | 2019-09-06 | 21 | 5961.5 | 1959 | -350 | 1 | 0 | 2309 | 1496.3726 | 1496.3726 | 1496.3726 | 982.6051 | 780 | 200 | 1962.6051 | 49.07% | 95% | 0% | -400.4577 | 1095.915 | -3550 | -400 | -2854.085 | 71.35% | 49.99% | 95% | 0% | 2309 | -350
[5 empty] | 2019-09-06 | 22 | 5962 | 1933 | -373 | 1 | 0 | 2306 | 1491.6735 | 1491.6735 | 1491.6735 | 982.6051 | 780 | 200 | 1962.6051 | 49.07% | 95% | 0% | -426.7735 | 1064.9001 | -3550 | -400 | -2885.0999 | 72.13% | 49.98% | 95% | 0% | 2306 | -373
[5 empty] | 2019-09-06 | 23 | 5962.5 | 1863 | -412 | 1 | 0 | 2275 | 1443.1162 | 1443.1162 | 1443.1162 | 982.6051 | 780 | 200 | 1962.6051 | 49.07% | 95% | 0% | -471.3959 | 971.7204 | -3550 | -400 | -2978.2796 | 74.46% | 49.98% | 95% | 0% | 2275 | -412
[5 empty] | 2019-09-06 | 24 | 5963 | 1852 | -402 | 1 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 982.6051 | 780 | 200 | 1962.6051 | 49.07% | 95% | 0% | -459.9542 | 950.2684 | -3550 | -400 | -2999.7316 | 74.99% | 49.97% | 95% | 0% | 2254 | -402
[5 empty] | 2019-09-06 | 25 | 5963.5 | 1826 | -427 | 1 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 982.6051 | 780 | 200 | 1962.6051 | 49.07% | 95% | 0% | -488.5584 | 920.0979 | -3550 | -400 | -3029.9021 | 75.75% | 49.97% | 95% | 0% | 2253 | -427
[5 empty] | 2019-09-06 | 26 | 5964 | 1813 | -432 | 1 | 0 | 2245 | 1396.1253 | 1396.1253 | 1396.1253 | 982.6051 | 780 | 200 | 1962.6051 | 49.07% | 95% | 0% | -494.2792 | 901.8461 | -3550 | -400 | -3048.1539 | 76.2% | 49.97% | 95% | 0% | 2245 | -432
[5 empty] | 2019-09-06 | 27 | 5964.5 | 1780 | -433 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 982.6051 | 780 | 200 | 1962.6051 | 49.07% | 95% | 0% | -495.4233 | 850.5783 | -3550 | -400 | -3099.4217 | 77.49% | 49.97% | 95% | 0% | 2213 | -433
[5 empty] | 2019-09-06 | 28 | 5965 | 1715 | -448 | 1 | 0 | 2163 | 1267.6834 | 1267.6834 | 1267.6834 | 982.6051 | 780 | 200 | 1962.6051 | 49.07% | 95% | 0% | -512.5858 | 755.0976 | -3550 | -400 | -3194.9024 | 79.87% | 49.96% | 95% | 0% | 2163 | -448
[5 empty] | 2019-09-06 | 29 | 5965.5 | 1663 | -457 | 1 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -522.8833 | 677.4465 | -3550 | -400 | -3272.5535 | 81.81% | 49.96% | 95% | 0% | 2120 | -457
[5 empty] | 2019-09-06 | 30 | 5966 | 1649 | -433 | 1 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -495.4233 | 645.3846 | -3550 | -400 | -3304.6154 | 82.62% | 49.95% | 95% | 0% | 2082 | -433
[5 empty] | 2019-09-06 | 31 | 5966.5 | 1631 | -427 | 1 | 0 | 2058 | 1103.2152 | 1103.2152 | 1103.2152 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -488.5584 | 614.6568 | -3550 | -400 | -3335.3432 | 83.38% | 49.95% | 95% | 0% | 2058 | -427
[5 empty] | 2019-09-06 | 32 | 5967 | 1645 | -442 | 1 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -505.7208 | 642.9189 | -3550 | -400 | -3307.0811 | 82.68% | 49.95% | 95% | 0% | 2087 | -442
[5 empty] | 2019-09-06 | 33 | 5967.5 | 1709 | -442 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -505.7208 | 743.1662 | -3550 | -400 | -3206.8338 | 80.17% | 49.95% | 95% | 0% | 2151 | -442
[5 empty] | 2019-09-06 | 34 | 5968 | 1778 | -418 | 1 | 0 | 2196 | 1319.3735 | 1319.3735 | 1319.3735 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -478.2609 | 841.1126 | -3550 | -400 | -3108.8874 | 77.72% | 49.95% | 95% | 0% | 2196 | -418
[5 empty] | 2019-09-06 | 35 | 5968.5 | 1870 | -364 | 1 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -416.476 | 962.4193 | -3550 | -400 | -2987.5807 | 74.69% | 49.94% | 95% | 0% | 2234 | -364
[5 empty] | 2019-09-06 | 36 | 5969 | 1953 | -306 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -350.1144 | 1067.94 | -3550 | -400 | -2882.06 | 72.05% | 49.94% | 95% | 0% | 2259 | -306
[5 empty] | 2019-09-06 | 37 | 5969.5 | 2060 | -259 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -296.3387 | 1215.6976 | -3550 | -400 | -2734.3024 | 68.36% | 49.94% | 95% | 0% | 2319 | -259
[5 empty] | 2019-09-06 | 38 | 5970 | 2114 | -194 | 1 | 0 | 2308 | 1494.8063 | 1494.8063 | 1494.8063 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -221.968 | 1272.8383 | -3550 | -400 | -2677.1617 | 66.93% | 49.93% | 95% | 0% | 2308 | -194
[5 empty] | 2019-09-06 | 39 | 5970.5 | 2154 | -152 | 1 | 0 | 2306 | 1491.6735 | 1491.6735 | 1491.6735 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -173.913 | 1317.7605 | -3550 | -400 | -2632.2395 | 65.81% | 49.93% | 95% | 0% | 2306 | -152
[5 empty] | 2019-09-06 | 40 | 5971 | 2180 | -138 | 1 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -157.8947 | 1352.5752 | -3550 | -400 | -2597.4248 | 64.94% | 49.93% | 95% | 0% | 2318 | -138
[5 empty] | 2019-09-06 | 41 | 5971.5 | 2200 | -134 | 1 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -153.3181 | 1382.2137 | -3550 | -400 | -2567.7863 | 64.19% | 49.92% | 95% | 0% | 2334 | -134
[5 empty] | 2019-09-06 | 42 | 5972 | 2134 | -130 | 0 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -148.7414 | 1277.1448 | -2750 | -200 | -1672.8552 | 41.82% | 49.92% | 95% | 0% | 2264 | -130
[5 empty] | 2019-09-06 | 43 | 5972.5 | 2058 | -127 | 0 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -145.3089 | 1156.8345 | -2750 | -200 | -1793.1655 | 44.83% | 49.92% | 95% | 0% | 2185 | -127
[5 empty] | 2019-09-06 | 44 | 5973 | 2011 | -124 | 0 | 0 | 2135 | 1223.8252 | 1223.8252 | 1223.8252 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -141.8764 | 1081.9488 | -2750 | -200 | -1868.0512 | 46.7% | 49.92% | 95% | 0% | 2135 | -124
[5 empty] | 2019-09-06 | 45 | 5973.5 | 1924 | -121 | 0 | 0 | 2045 | 1082.8524 | 1082.8524 | 1082.8524 | 981.0387 | 780 | 200 | 1961.0387 | 49.03% | 95% | 0% | -138.4439 | 944.4085 | -2750 | -200 | -2005.5915 | 50.14% | 49.91% | 95% | 0% | 2045 | -121
[5 empty] | 2019-09-06 | 46 | 5974 | 1811 | -118 | 0 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -135.0114 | 766.1427 | -2750 | -200 | -2183.8573 | 54.6% | 49.9% | 95% | 0% | 1929 | -118
[5 empty] | 2019-09-06 | 47 | 5974.5 | 1702 | -116 | 0 | 0 | 1818 | 727.2877 | 727.2877 | 727.2877 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -132.7231 | 594.5646 | -2750 | -200 | -2355.4354 | 58.89% | 49.9% | 95% | 0% | 1818 | -116
[5 empty] | 2019-09-06 | 48 | 5975 | 1610 | -113 | 0 | 0 | 1723 | 578.4831 | 578.4831 | 578.4831 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -129.2906 | 449.1925 | -2750 | -200 | -2500.8075 | 62.52% | 49.9% | 95% | 0% | 1723 | -113
[5 empty] | 2019-09-07 | 1 | 5975.5 | 1534 | -106 | 0 | 0 | 1640 | 448.4749 | 448.4749 | 448.4749 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -121.2815 | 327.1934 | -2750 | -200 | -2622.8066 | 65.57% | 49.9% | 95% | 0% | 1640 | -106
[5 empty] | 2019-09-07 | 2 | 5976 | 1483 | -99 | 0 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -113.2723 | 244.3534 | -2750 | -200 | -2705.6466 | 67.64% | 49.9% | 95% | 0% | 1582 | -99
[5 empty] | 2019-09-07 | 3 | 5976.5 | 1444 | -98 | 0 | 0 | 1542 | 294.9711 | 294.9711 | 294.9711 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -112.1281 | 182.843 | -2750 | -200 | -2767.157 | 69.18% | 49.89% | 95% | 0% | 1542 | -98
[5 empty] | 2019-09-07 | 4 | 5977 | 1428 | -97 | 0 | 0 | 1525 | 268.343 | 268.343 | 268.343 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -110.984 | 157.359 | -2750 | -200 | -2792.641 | 69.82% | 49.89% | 95% | 0% | 1525 | -97
[5 empty] | 2019-09-07 | 5 | 5977.5 | 1398 | -95 | 0 | 0 | 1493 | 218.2193 | 218.2193 | 218.2193 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -108.6957 | 109.5236 | -2750 | -200 | -2840.4764 | 71.01% | 49.89% | 95% | 0% | 1493 | -95
[5 empty] | 2019-09-07 | 6 | 5978 | 1377 | -94 | 0 | 0 | 1471 | 183.7593 | 183.7593 | 183.7593 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -107.5515 | 76.2078 | -2750 | -200 | -2873.7922 | 71.84% | 49.89% | 95% | 0% | 1471 | -94
[5 empty] | 2019-09-07 | 7 | 5978.5 | 1358 | -93 | 0 | 0 | 1451 | 152.432 | 152.432 | 152.432 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -106.4073 | 46.0247 | -2750 | -200 | -2903.9753 | 72.6% | 49.89% | 95% | 0% | 1451 | -93
[5 empty] | 2019-09-07 | 8 | 5979 | 1344 | -91 | 0 | 0 | 1435 | 127.3702 | 127.3702 | 127.3702 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -104.119 | 23.2512 | -2750 | -200 | -2926.7488 | 73.17% | 49.89% | 95% | 0% | 1435 | -91
[5 empty] | 2019-09-07 | 9 | 5979.5 | 1344 | -89 | 0 | 0 | 1433 | 124.2374 | 124.2374 | 124.2374 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -101.8307 | 22.4068 | -2750 | -200 | -2927.5932 | 73.19% | 49.88% | 95% | 0% | 1433 | -89
[5 empty] | 2019-09-07 | 10 | 5980 | 1349 | -86 | 0 | 0 | 1435 | 127.3702 | 127.3702 | 127.3702 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -98.3982 | 28.972 | -2750 | -200 | -2921.028 | 73.03% | 49.88% | 95% | 0% | 1435 | -86
[5 empty] | 2019-09-07 | 11 | 5980.5 | 1390 | -85 | 0 | 0 | 1475 | 190.0247 | 190.0247 | 190.0247 | 979.4724 | 780 | 200 | 1959.4724 | 48.99% | 95% | 0% | -97.254 | 92.7707 | -2750 | -200 | -2857.2293 | 71.43% | 49.88% | 95% | 0% | 1475 | -85
[5 empty] | 2019-09-07 | 12 | 5981 | 1422 | -84 | 0 | 0 | 1506 | 238.582 | 238.582 | 238.582 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -96.1098 | 142.4722 | -2750 | -200 | -2807.5278 | 70.19% | 49.88% | 95% | 0% | 1506 | -84
[5 empty] | 2019-09-07 | 13 | 5981.5 | 1505 | -83 | 0 | 0 | 1588 | 367.0239 | 367.0239 | 367.0239 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -94.9657 | 272.0582 | -2750 | -200 | -2677.9418 | 66.95% | 49.87% | 95% | 0% | 1588 | -83
[5 empty] | 2019-09-07 | 14 | 5982 | 1578 | -84 | 1 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -96.1098 | 386.825 | -3550 | -400 | -3563.175 | 89.08% | 49.87% | 95% | 0% | 1662 | -84
[5 empty] | 2019-09-07 | 15 | 5982.5 | 1675 | -100 | 1 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -114.4165 | 545.5176 | -3550 | -400 | -3404.4824 | 85.11% | 49.87% | 95% | 0% | 1775 | -100
[5 empty] | 2019-09-07 | 16 | 5983 | 1746 | -128 | 1 | 0 | 1874 | 815.0041 | 815.0041 | 815.0041 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -146.4531 | 668.551 | -3550 | -400 | -3281.449 | 82.04% | 49.86% | 95% | 0% | 1874 | -128
[5 empty] | 2019-09-07 | 17 | 5983.5 | 1797 | -171 | 1 | 0 | 1968 | 962.2424 | 962.2424 | 962.2424 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -195.6522 | 766.5902 | -3550 | -400 | -3183.4098 | 79.59% | 49.86% | 95% | 0% | 1968 | -171
[5 empty] | 2019-09-07 | 18 | 5984 | 1772 | -226 | 1 | 0 | 1998 | 1009.2333 | 1009.2333 | 1009.2333 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -258.5812 | 750.6521 | -3550 | -400 | -3199.3479 | 79.98% | 49.85% | 95% | 0% | 1998 | -226
[5 empty] | 2019-09-07 | 19 | 5984.5 | 1731 | -285 | 1 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -326.087 | 711.3409 | -3550 | -400 | -3238.6591 | 80.97% | 49.85% | 95% | 0% | 2016 | -285
[5 empty] | 2019-09-07 | 20 | 5985 | 1647 | -350 | 1 | 0 | 1997 | 1007.6669 | 1007.6669 | 1007.6669 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -400.4577 | 607.2093 | -3550 | -400 | -3342.7907 | 83.57% | 49.85% | 95% | 0% | 1997 | -350
[5 empty] | 2019-09-07 | 21 | 5985.5 | 1599 | -389 | 1 | 0 | 1988 | 993.5697 | 993.5697 | 993.5697 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -445.0801 | 548.4896 | -3550 | -400 | -3401.5104 | 85.04% | 49.85% | 95% | 0% | 1988 | -389
[5 empty] | 2019-09-07 | 22 | 5986 | 1555 | -431 | 1 | 0 | 1986 | 990.4369 | 990.4369 | 990.4369 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -493.135 | 497.3019 | -3550 | -400 | -3452.6981 | 86.32% | 49.84% | 95% | 0% | 1986 | -431
[5 empty] | 2019-09-07 | 23 | 5986.5 | 1549 | -429 | 1 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -490.8467 | 487.0593 | -3550 | -400 | -3462.9407 | 86.57% | 49.84% | 95% | 0% | 1978 | -429
[5 empty] | 2019-09-07 | 24 | 5987 | 1575 | -394 | 1 | 0 | 1969 | 963.8087 | 963.8087 | 963.8087 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -450.8009 | 513.0078 | -3550 | -400 | -3436.9922 | 85.92% | 49.84% | 95% | 0% | 1969 | -394
[5 empty] | 2019-09-07 | 25 | 5987.5 | 1581 | -383 | 1 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 977.906 | 780 | 200 | 1957.906 | 48.95% | 95% | 0% | -438.2151 | 517.7618 | -3550 | -400 | -3432.2382 | 85.81% | 49.83% | 95% | 0% | 1964 | -383
[5 empty] | 2019-09-07 | 26 | 5988 | 1560 | -405 | 1 | 0 | 1965 | 957.5433 | 957.5433 | 957.5433 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -463.3867 | 494.1566 | -3550 | -400 | -3455.8434 | 86.4% | 49.83% | 95% | 0% | 1965 | -405
[5 empty] | 2019-09-07 | 27 | 5988.5 | 1495 | -406 | 1 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -464.5309 | 392.7651 | -3550 | -400 | -3557.2349 | 88.93% | 49.83% | 95% | 0% | 1901 | -406
[5 empty] | 2019-09-07 | 28 | 5989 | 1446 | -429 | 1 | 0 | 1875 | 816.5705 | 816.5705 | 816.5705 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -490.8467 | 325.7238 | -3550 | -400 | -3624.2762 | 90.61% | 49.83% | 95% | 0% | 1875 | -429
[5 empty] | 2019-09-07 | 29 | 5989.5 | 1389 | -435 | 1 | 0 | 1824 | 736.6859 | 736.6859 | 736.6859 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -497.7117 | 238.9742 | -3550 | -400 | -3711.0258 | 92.78% | 49.83% | 95% | 0% | 1824 | -435
[5 empty] | 2019-09-07 | 30 | 5990 | 1374 | -435 | 1 | 0 | 1809 | 713.1904 | 713.1904 | 713.1904 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -497.7117 | 215.4788 | -3550 | -400 | -3734.5212 | 93.36% | 49.82% | 95% | 0% | 1809 | -435
[5 empty] | 2019-09-07 | 31 | 5990.5 | 1413 | -406 | 1 | 0 | 1819 | 728.8541 | 728.8541 | 728.8541 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -464.5309 | 264.3232 | -3550 | -400 | -3685.6768 | 92.14% | 49.82% | 95% | 0% | 1819 | -406
[5 empty] | 2019-09-07 | 32 | 5991 | 1416 | -410 | 1 | 0 | 1826 | 739.8186 | 739.8186 | 739.8186 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -469.1076 | 270.7111 | -3550 | -400 | -3679.2889 | 91.98% | 49.82% | 95% | 0% | 1826 | -410
[5 empty] | 2019-09-07 | 33 | 5991.5 | 1499 | -379 | 1 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -433.6384 | 387.6311 | -3550 | -400 | -3562.3689 | 89.06% | 49.82% | 95% | 0% | 1878 | -379
[5 empty] | 2019-09-07 | 34 | 5992 | 1615 | -338 | 1 | 0 | 1953 | 938.7469 | 938.7469 | 938.7469 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -386.7277 | 552.0192 | -3550 | -400 | -3397.9808 | 84.95% | 49.82% | 95% | 0% | 1953 | -338
[5 empty] | 2019-09-07 | 35 | 5992.5 | 1766 | -286 | 1 | 0 | 2052 | 1093.817 | 1093.817 | 1093.817 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -327.2311 | 766.5859 | -3550 | -400 | -3183.4141 | 79.59% | 49.82% | 95% | 0% | 2052 | -286
[5 empty] | 2019-09-07 | 36 | 5993 | 1902 | -222 | 1 | 0 | 2124 | 1206.5952 | 1206.5952 | 1206.5952 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -254.0046 | 952.5906 | -3550 | -400 | -2997.4094 | 74.94% | 49.81% | 95% | 0% | 2124 | -222
[5 empty] | 2019-09-07 | 37 | 5993.5 | 2012 | -166 | 1 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -189.9314 | 1101.2475 | -3550 | -400 | -2848.7525 | 71.22% | 49.8% | 95% | 0% | 2178 | -166
[5 empty] | 2019-09-07 | 38 | 5994 | 2110 | -108 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -123.5698 | 1230.2637 | -3550 | -400 | -2719.7363 | 67.99% | 49.8% | 95% | 0% | 2218 | -108
[5 empty] | 2019-09-07 | 39 | 5994.5 | 2173 | -70 | 1 | 0 | 2243 | 1392.9926 | 1392.9926 | 1392.9926 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -80.0915 | 1312.901 | -3550 | -400 | -2637.099 | 65.93% | 49.8% | 95% | 0% | 2243 | -70
[5 empty] | 2019-09-07 | 40 | 5995 | 2196 | -57 | 1 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -65.2174 | 1343.4388 | -3550 | -400 | -2606.5612 | 65.16% | 49.79% | 95% | 0% | 2253 | -57
[5 empty] | 2019-09-07 | 41 | 5995.5 | 2238 | -54 | 1 | 0 | 2292 | 1469.7444 | 1469.7444 | 1469.7444 | 976.3397 | 780 | 200 | 1956.3397 | 48.91% | 95% | 0% | -61.7849 | 1407.9595 | -3550 | -400 | -2542.0405 | 63.55% | 49.79% | 95% | 0% | 2292 | -54
[5 empty] | 2019-09-07 | 42 | 5996 | 2206 | -52 | 0 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 974.7733 | 780 | 200 | 1954.7733 | 48.87% | 95% | 0% | -59.4966 | 1356.9915 | -2750 | -200 | -1593.0085 | 39.83% | 49.79% | 95% | 0% | 2258 | -52
[5 empty] | 2019-09-07 | 43 | 5996.5 | 2131 | -50 | 0 | 0 | 2181 | 1295.878 | 1295.878 | 1295.878 | 974.7733 | 780 | 200 | 1954.7733 | 48.87% | 95% | 0% | -57.2082 | 1238.6698 | -2750 | -200 | -1711.3302 | 42.78% | 49.78% | 95% | 0% | 2181 | -50
[5 empty] | 2019-09-07 | 44 | 5997 | 2054 | -48 | 0 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 974.7733 | 780 | 200 | 1954.7733 | 48.87% | 95% | 0% | -54.9199 | 1117.2153 | -2750 | -200 | -1832.7847 | 45.82% | 49.77% | 95% | 0% | 2102 | -48
[5 empty] | 2019-09-07 | 45 | 5997.5 | 1962 | -48 | 0 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 974.7733 | 780 | 200 | 1954.7733 | 48.87% | 95% | 0% | -54.9199 | 973.1098 | -2750 | -200 | -1976.8902 | 49.42% | 49.77% | 95% | 0% | 2010 | -48
[5 empty] | 2019-09-07 | 46 | 5998 | 1862 | -47 | 0 | 0 | 1909 | 869.8269 | 869.8269 | 869.8269 | 974.7733 | 780 | 200 | 1954.7733 | 48.87% | 95% | 0% | -53.7757 | 816.0511 | -2750 | -200 | -2133.9489 | 53.35% | 49.77% | 95% | 0% | 1909 | -47
[5 empty] | 2019-09-07 | 47 | 5998.5 | 1758 | -46 | 0 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 974.7733 | 780 | 200 | 1954.7733 | 48.87% | 95% | 0% | -52.6316 | 652.727 | -2750 | -200 | -2297.273 | 57.43% | 49.77% | 95% | 0% | 1804 | -46
[5 empty] | 2019-09-07 | 48 | 5999 | 1667 | -45 | 0 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 974.7733 | 780 | 200 | 1954.7733 | 48.87% | 95% | 0% | -51.4874 | 509.7657 | -2750 | -200 | -2440.2343 | 61.01% | 49.77% | 95% | 0% | 1712 | -45
[5 empty] | 2019-09-08 | 1 | 5999.5 | 1588 | -44 | 0 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 974.7733 | 780 | 200 | 1954.7733 | 48.87% | 95% | 0% | -50.3432 | 385.6007 | -2750 | -200 | -2564.3993 | 64.11% | 49.77% | 95% | 0% | 1632 | -44
[5 empty] | 2019-09-08 | 2 | 6000 | 1535 | -44 | 0 | 0 | 1579 | 352.9266 | 352.9266 | 352.9266 | 974.7733 | 780 | 200 | 1954.7733 | 48.87% | 95% | 0% | -50.3432 | 302.5834 | -2750 | -200 | -2647.4166 | 66.19% | 49.76% | 95% | 0% | 1579 | -44
[5 empty] | 2019-09-08 | 3 | 6000.5 | 1491 | -44 | 0 | 0 | 1535 | 284.0066 | 284.0066 | 284.0066 | 974.7733 | 780 | 200 | 1954.7733 | 48.87% | 95% | 0% | -50.3432 | 233.6633 | -2750 | -200 | -2716.3367 | 67.91% | 49.76% | 95% | 0% | 1535 | -44
[5 empty] | 2019-09-08 | 4 | 6001 | 1472 | -44 | 0 | 0 | 1516 | 254.2457 | 254.2457 | 254.2457 | 974.7733 | 780 | 200 | 1954.7733 | 48.87% | 95% | 0% | -50.3432 | 203.9024 | -2750 | -200 | -2746.0976 | 68.65% | 49.76% | 95% | 0% | 1516 | -44
[5 empty] | 2019-09-08 | 5 | 6001.5 | 1451 | -44 | 0 | 0 | 1495 | 221.352 | 221.352 | 221.352 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -50.3432 | 171.0088 | -2750 | -200 | -2778.9912 | 69.47% | 49.76% | 95% | 0% | 1495 | -44
[5 empty] | 2019-09-08 | 6 | 6002 | 1435 | -44 | 0 | 0 | 1479 | 196.2902 | 196.2902 | 196.2902 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -50.3432 | 145.9469 | -2750 | -200 | -2804.0531 | 70.1% | 49.76% | 95% | 0% | 1479 | -44
[5 empty] | 2019-09-08 | 7 | 6002.5 | 1419 | -44 | 0 | 0 | 1463 | 171.2284 | 171.2284 | 171.2284 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -50.3432 | 120.8851 | -2750 | -200 | -2829.1149 | 70.73% | 49.75% | 95% | 0% | 1463 | -44
[5 empty] | 2019-09-08 | 8 | 6003 | 1398 | -44 | 0 | 0 | 1442 | 138.3347 | 138.3347 | 138.3347 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -50.3432 | 87.9915 | -2750 | -200 | -2862.0085 | 71.55% | 49.74% | 95% | 0% | 1442 | -44
[5 empty] | 2019-09-08 | 9 | 6003.5 | 1401 | -44 | 0 | 0 | 1445 | 143.0338 | 143.0338 | 143.0338 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -50.3432 | 92.6906 | -2750 | -200 | -2857.3094 | 71.43% | 49.73% | 95% | 0% | 1445 | -44
[5 empty] | 2019-09-08 | 10 | 6004 | 1378 | -45 | 0 | 0 | 1423 | 108.5738 | 108.5738 | 108.5738 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -51.4874 | 57.0864 | -2750 | -200 | -2892.9136 | 72.32% | 49.73% | 95% | 0% | 1423 | -45
[5 empty] | 2019-09-08 | 11 | 6004.5 | 1406 | -43 | 0 | 0 | 1449 | 149.2993 | 149.2993 | 149.2993 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -49.1991 | 100.1002 | -2750 | -200 | -2849.8998 | 71.25% | 49.71% | 95% | 0% | 1449 | -43
[5 empty] | 2019-09-08 | 12 | 6005 | 1432 | -42 | 1 | 0 | 1474 | 188.4584 | 188.4584 | 188.4584 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -48.0549 | 140.4034 | -3550 | -400 | -3809.5966 | 95.24% | 49.71% | 95% | 0% | 1474 | -42
[5 empty] | 2019-09-08 | 13 | 6005.5 | 1470 | -43 | 1 | 0 | 1513 | 249.5466 | 249.5466 | 249.5466 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -49.1991 | 200.3475 | -3550 | -400 | -3749.6525 | 93.74% | 49.71% | 95% | 0% | 1513 | -43
[5 empty] | 2019-09-08 | 14 | 6006 | 1487 | -50 | 1 | 0 | 1537 | 287.1393 | 287.1393 | 287.1393 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -57.2082 | 229.9311 | -3550 | -400 | -3720.0689 | 93% | 49.7% | 95% | 0% | 1537 | -50
[5 empty] | 2019-09-08 | 15 | 6006.5 | 1524 | -88 | 1 | 0 | 1612 | 404.6167 | 404.6167 | 404.6167 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -100.6865 | 303.9302 | -3550 | -400 | -3646.0698 | 91.15% | 49.7% | 95% | 0% | 1612 | -88
[5 empty] | 2019-09-08 | 16 | 6007 | 1518 | -150 | 1 | 0 | 1668 | 492.3331 | 492.3331 | 492.3331 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -171.6247 | 320.7083 | -3550 | -400 | -3629.2917 | 90.73% | 49.7% | 95% | 0% | 1668 | -150
[5 empty] | 2019-09-08 | 17 | 6007.5 | 1521 | -223 | 1 | 0 | 1744 | 611.3768 | 611.3768 | 611.3768 | 973.2069 | 780 | 200 | 1953.2069 | 48.83% | 95% | 0% | -255.1487 | 356.228 | -3550 | -400 | -3593.772 | 89.84% | 49.7% | 95% | 0% | 1744 | -223
[5 empty] | 2019-09-08 | 18 | 6008 | 1478 | -300 | 1 | 0 | 1778 | 664.6331 | 664.6331 | 664.6331 | 971.6406 | 780 | 200 | 1951.6406 | 48.79% | 95% | 0% | -343.2494 | 321.3837 | -3550 | -400 | -3628.6163 | 90.72% | 49.69% | 95% | 0% | 1778 | -300
[5 empty] | 2019-09-08 | 19 | 6008.5 | 1433 | -373 | 1 | 0 | 1806 | 708.4913 | 708.4913 | 708.4913 | 971.6406 | 780 | 200 | 1951.6406 | 48.79% | 95% | 0% | -426.7735 | 281.7179 | -3550 | -400 | -3668.2821 | 91.71% | 49.69% | 95% | 0% | 1806 | -373
[5 empty] | 2019-09-08 | 20 | 6009 | 1359 | -448 | 1 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 971.6406 | 780 | 200 | 1951.6406 | 48.79% | 95% | 0% | -512.5858 | 197.4719 | -3550 | -400 | -3752.5281 | 93.81% | 49.69% | 95% | 0% | 1807 | -448
[5 empty] | 2019-09-08 | 21 | 6009.5 | 1295 | -504 | 1 | 0 | 1799 | 697.5268 | 697.5268 | 697.5268 | 971.6406 | 780 | 200 | 1951.6406 | 48.79% | 95% | 0% | -576.659 | 120.8678 | -3550 | -400 | -3829.1322 | 95.73% | 49.67% | 95% | 0% | 1799 | -504
[5 empty] | 2019-09-08 | 22 | 6010 | 1252 | -544 | 1 | 0 | 1796 | 692.8277 | 692.8277 | 692.8277 | 971.6406 | 780 | 200 | 1951.6406 | 48.79% | 95% | 0% | -622.4256 | 70.4021 | -3550 | -400 | -3879.5979 | 96.99% | 49.67% | 95% | 0% | 1796 | -544
[5 empty] | 2019-09-08 | 23 | 6010.5 | 1242 | -556 | 1 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 971.6406 | 780 | 200 | 1951.6406 | 48.79% | 95% | 0% | -636.1556 | 59.8048 | -3550 | -400 | -3890.1952 | 97.25% | 49.67% | 95% | 0% | 1798 | -556
[5 empty] | 2019-09-08 | 24 | 6011 | 1228 | -566 | 1 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 971.6406 | 780 | 200 | 1951.6406 | 48.79% | 95% | 0% | -647.5973 | 42.0977 | -3550 | -400 | -3907.9023 | 97.7% | 49.67% | 95% | 0% | 1794 | -566
[5 empty] | 2019-09-08 | 25 | 6011.5 | 1250 | -557 | 1 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 971.6406 | 780 | 200 | 1951.6406 | 48.79% | 95% | 0% | -637.2998 | 72.7579 | -3550 | -400 | -3877.2421 | 96.93% | 49.67% | 95% | 0% | 1807 | -557
[5 empty] | 2019-09-08 | 26 | 6012 | 1234 | -573 | 1 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 971.6406 | 780 | 200 | 1951.6406 | 48.79% | 95% | 0% | -655.6064 | 54.4513 | -3550 | -400 | -3895.5487 | 97.39% | 49.67% | 95% | 0% | 1807 | -573
[5 empty] | 2019-09-08 | 27 | 6012.5 | 1240 | -550 | 1 | 0 | 1790 | 683.4295 | 683.4295 | 683.4295 | 971.6406 | 780 | 200 | 1951.6406 | 48.79% | 95% | 0% | -629.2906 | 54.1389 | -3550 | -400 | -3895.8611 | 97.4% | 49.66% | 95% | 0% | 1790 | -550
[5 empty] | 2019-09-08 | 28 | 6013 | 1228 | -545 | 1 | 0 | 1773 | 656.8013 | 656.8013 | 656.8013 | 971.6406 | 780 | 200 | 1951.6406 | 48.79% | 95% | 0% | -623.5698 | 33.2315 | -3550 | -400 | -3916.7685 | 97.92% | 49.66% | 95% | 0% | 1773 | -545
[5 empty] | 2019-09-08 | 29 | 6013.5 | 1245 | -517 | 1 | 0 | 1762 | 639.5713 | 639.5713 | 639.5713 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -591.5332 | 48.0381 | -3550 | -400 | -3901.9619 | 97.55% | 49.66% | 95% | 0% | 1762 | -517
[5 empty] | 2019-09-08 | 30 | 6014 | 1271 | -494 | 1 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -565.2174 | 79.053 | -3550 | -400 | -3870.947 | 96.77% | 49.66% | 95% | 0% | 1765 | -494
[5 empty] | 2019-09-08 | 31 | 6014.5 | 1347 | -448 | 1 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -512.5858 | 178.6755 | -3550 | -400 | -3771.3245 | 94.28% | 49.65% | 95% | 0% | 1795 | -448
[5 empty] | 2019-09-08 | 32 | 6015 | 1436 | -417 | 1 | 0 | 1853 | 782.1105 | 782.1105 | 782.1105 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -477.1167 | 304.9938 | -3550 | -400 | -3645.0062 | 91.13% | 49.65% | 95% | 0% | 1853 | -417
[5 empty] | 2019-09-08 | 33 | 6015.5 | 1541 | -370 | 1 | 0 | 1911 | 872.9596 | 872.9596 | 872.9596 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -423.341 | 449.6186 | -3550 | -400 | -3500.3814 | 87.51% | 49.64% | 95% | 0% | 1911 | -370
[5 empty] | 2019-09-08 | 34 | 6016 | 1687 | -328 | 1 | 0 | 2015 | 1035.8615 | 1035.8615 | 1035.8615 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -375.286 | 660.5755 | -3550 | -400 | -3289.4245 | 82.24% | 49.63% | 95% | 0% | 2015 | -328
[5 empty] | 2019-09-08 | 35 | 6016.5 | 1870 | -256 | 1 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -292.9062 | 916.8218 | -3550 | -400 | -3033.1782 | 75.83% | 49.63% | 95% | 0% | 2126 | -256
[5 empty] | 2019-09-08 | 36 | 6017 | 2006 | -189 | 1 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -216.2471 | 1101.56 | -3550 | -400 | -2848.44 | 71.21% | 49.62% | 95% | 0% | 2195 | -189
[5 empty] | 2019-09-08 | 37 | 6017.5 | 2106 | -133 | 1 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -152.1739 | 1234.5532 | -3550 | -400 | -2715.4468 | 67.89% | 49.62% | 95% | 0% | 2239 | -133
[5 empty] | 2019-09-08 | 38 | 6018 | 2191 | -88 | 1 | 0 | 2279 | 1449.3817 | 1449.3817 | 1449.3817 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -100.6865 | 1348.6952 | -3550 | -400 | -2601.3048 | 65.03% | 49.62% | 95% | 0% | 2279 | -88
[5 empty] | 2019-09-08 | 39 | 6018.5 | 2249 | -53 | 1 | 0 | 2302 | 1485.4081 | 1485.4081 | 1485.4081 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -60.6407 | 1424.7673 | -3550 | -400 | -2525.2327 | 63.13% | 49.62% | 95% | 0% | 2302 | -53
[5 empty] | 2019-09-08 | 40 | 6019 | 2284 | -45 | 1 | 0 | 2329 | 1527.6999 | 1527.6999 | 1527.6999 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -51.4874 | 1476.2125 | -3550 | -400 | -2473.7875 | 61.84% | 49.61% | 95% | 0% | 2329 | -45
[5 empty] | 2019-09-08 | 41 | 6019.5 | 2312 | -45 | 1 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -51.4874 | 1520.0707 | -3550 | -400 | -2429.9293 | 60.75% | 49.61% | 95% | 0% | 2357 | -45
[5 empty] | 2019-09-08 | 42 | 6020 | 2244 | -45 | 0 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 970.0742 | 780 | 200 | 1950.0742 | 48.75% | 95% | 0% | -51.4874 | 1413.5579 | -2750 | -200 | -1536.4421 | 38.41% | 49.61% | 95% | 0% | 2289 | -45
[5 empty] | 2019-09-08 | 43 | 6020.5 | 2195 | -46 | 0 | 0 | 2241 | 1389.8599 | 1389.8599 | 1389.8599 | 968.5078 | 780 | 200 | 1948.5078 | 48.71% | 95% | 0% | -52.6316 | 1337.2283 | -2750 | -200 | -1612.7717 | 40.32% | 49.6% | 95% | 0% | 2241 | -46
[5 empty] | 2019-09-08 | 44 | 6021 | 2090 | -47 | 0 | 0 | 2137 | 1226.958 | 1226.958 | 1226.958 | 968.5078 | 780 | 200 | 1948.5078 | 48.71% | 95% | 0% | -53.7757 | 1173.1822 | -2750 | -200 | -1776.8178 | 44.42% | 49.6% | 95% | 0% | 2137 | -47
[5 empty] | 2019-09-08 | 45 | 6021.5 | 1978 | -48 | 0 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 968.5078 | 780 | 200 | 1948.5078 | 48.71% | 95% | 0% | -54.9199 | 998.1716 | -2750 | -200 | -1951.8284 | 48.8% | 49.6% | 95% | 0% | 2026 | -48
[5 empty] | 2019-09-08 | 46 | 6022 | 1832 | -49 | 0 | 0 | 1881 | 825.9687 | 825.9687 | 825.9687 | 968.5078 | 780 | 200 | 1948.5078 | 48.71% | 95% | 0% | -56.0641 | 769.9046 | -2750 | -200 | -2180.0954 | 54.5% | 49.6% | 95% | 0% | 1881 | -49
[5 empty] | 2019-09-08 | 47 | 6022.5 | 1720 | -51 | 0 | 0 | 1771 | 653.6686 | 653.6686 | 653.6686 | 968.5078 | 780 | 200 | 1948.5078 | 48.71% | 95% | 0% | -58.3524 | 595.3162 | -2750 | -200 | -2354.6838 | 58.87% | 49.6% | 95% | 0% | 1771 | -51
[5 empty] | 2019-09-08 | 48 | 6023 | 1621 | -52 | 0 | 0 | 1673 | 500.1649 | 500.1649 | 500.1649 | 968.5078 | 780 | 200 | 1948.5078 | 48.71% | 95% | 0% | -59.4966 | 440.6683 | -2750 | -200 | -2509.3317 | 62.73% | 49.59% | 95% | 0% | 1673 | -52
[5 empty] | 2019-09-09 | 1 | 6023.5 | 1534 | -56 | 0 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 968.5078 | 780 | 200 | 1948.5078 | 48.71% | 95% | 0% | -64.0732 | 306.0834 | -2750 | -200 | -2643.9166 | 66.1% | 49.59% | 95% | 0% | 1590 | -56
[5 empty] | 2019-09-09 | 2 | 6024 | 1489 | -60 | 0 | 0 | 1549 | 305.9357 | 305.9357 | 305.9357 | 968.5078 | 780 | 200 | 1948.5078 | 48.71% | 95% | 0% | -68.6499 | 237.2858 | -2750 | -200 | -2712.7142 | 67.82% | 49.58% | 95% | 0% | 1549 | -60
[5 empty] | 2019-09-09 | 3 | 6024.5 | 1463 | -62 | 1 | 0 | 1525 | 268.343 | 268.343 | 268.343 | 968.5078 | 780 | 200 | 1948.5078 | 48.71% | 95% | 0% | -70.9382 | 197.4047 | -3550 | -400 | -3752.5953 | 93.81% | 49.58% | 95% | 0% | 1525 | -62
[5 empty] | 2019-09-09 | 4 | 6025 | 1448 | -65 | 1 | 0 | 1513 | 249.5466 | 249.5466 | 249.5466 | 968.5078 | 780 | 200 | 1948.5078 | 48.71% | 95% | 0% | -74.3707 | 175.1759 | -3550 | -400 | -3774.8241 | 94.37% | 49.58% | 95% | 0% | 1513 | -65
[5 empty] | 2019-09-09 | 5 | 6025.5 | 1429 | -67 | 1 | 0 | 1496 | 222.9184 | 222.9184 | 222.9184 | 966.9415 | 780 | 200 | 1946.9415 | 48.67% | 95% | 0% | -76.659 | 146.2593 | -3550 | -400 | -3803.7407 | 95.09% | 49.58% | 95% | 0% | 1496 | -67
[5 empty] | 2019-09-09 | 6 | 6026 | 1405 | -69 | 1 | 0 | 1474 | 188.4584 | 188.4584 | 188.4584 | 966.9415 | 780 | 200 | 1946.9415 | 48.67% | 95% | 0% | -78.9474 | 109.511 | -3550 | -400 | -3840.489 | 96.01% | 49.58% | 95% | 0% | 1474 | -69
[5 empty] | 2019-09-09 | 7 | 6026.5 | 1385 | -70 | 1 | 0 | 1455 | 158.6974 | 158.6974 | 158.6974 | 966.9415 | 780 | 200 | 1946.9415 | 48.67% | 95% | 0% | -80.0915 | 78.6059 | -3550 | -400 | -3871.3941 | 96.78% | 49.57% | 95% | 0% | 1455 | -70
[5 empty] | 2019-09-09 | 8 | 6027 | 1379 | -71 | 1 | 0 | 1450 | 150.8656 | 150.8656 | 150.8656 | 966.9415 | 780 | 200 | 1946.9415 | 48.67% | 95% | 0% | -81.2357 | 69.6299 | -3550 | -400 | -3880.3701 | 97.01% | 49.57% | 95% | 0% | 1450 | -71
[5 empty] | 2019-09-09 | 9 | 6027.5 | 1392 | -72 | 1 | 0 | 1464 | 172.7947 | 172.7947 | 172.7947 | 966.9415 | 780 | 200 | 1946.9415 | 48.67% | 95% | 0% | -82.3799 | 90.4149 | -3550 | -400 | -3859.5851 | 96.49% | 49.57% | 95% | 0% | 1464 | -72
[5 empty] | 2019-09-09 | 10 | 6028 | 1404 | -74 | 1 | 0 | 1478 | 194.7238 | 194.7238 | 194.7238 | 966.9415 | 780 | 200 | 1946.9415 | 48.67% | 95% | 0% | -84.6682 | 110.0556 | -3550 | -400 | -3839.9444 | 96% | 49.56% | 95% | 0% | 1478 | -74
[5 empty] | 2019-09-09 | 11 | 6028.5 | 1458 | -73 | 1 | 0 | 1531 | 277.7411 | 277.7411 | 277.7411 | 966.9415 | 780 | 200 | 1946.9415 | 48.67% | 95% | 0% | -83.524 | 194.2171 | -3550 | -400 | -3755.7829 | 93.89% | 49.56% | 95% | 0% | 1531 | -73
[5 empty] | 2019-09-09 | 12 | 6029 | 1561 | -73 | 1 | 0 | 1634 | 439.0767 | 439.0767 | 439.0767 | 966.9415 | 780 | 200 | 1946.9415 | 48.67% | 95% | 0% | -83.524 | 355.5526 | -3550 | -400 | -3594.4474 | 89.86% | 49.55% | 95% | 0% | 1634 | -73
[5 empty] | 2019-09-09 | 13 | 6029.5 | 1784 | -72 | 1 | 0 | 1856 | 786.8096 | 786.8096 | 786.8096 | 965.3751 | 780 | 200 | 1945.3751 | 48.63% | 95% | 0% | -82.3799 | 704.4297 | -3550 | -400 | -3245.5703 | 81.14% | 49.55% | 95% | 0% | 1856 | -72
[5 empty] | 2019-09-09 | 14 | 6030 | 1982 | -71 | 1 | 0 | 2053 | 1095.3833 | 1095.3833 | 1095.3833 | 965.3751 | 780 | 200 | 1945.3751 | 48.63% | 95% | 0% | -81.2357 | 1014.1476 | -3550 | -400 | -2935.8524 | 73.4% | 49.55% | 95% | 0% | 2053 | -71
[5 empty] | 2019-09-09 | 15 | 6030.5 | 2212 | -75 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 965.3751 | 780 | 200 | 1945.3751 | 48.63% | 95% | 0% | -85.8124 | 1376.1003 | -3550 | -400 | -2573.8997 | 64.35% | 49.55% | 95% | 0% | 2287 | -75
[5 empty] | 2019-09-09 | 16 | 6031 | 2340 | -87 | 1 | 0 | 2427 | 1681.2036 | 1681.2036 | 1681.2036 | 965.3751 | 780 | 200 | 1945.3751 | 48.63% | 95% | 0% | -99.5423 | 1581.6613 | -3550 | -400 | -2368.3387 | 59.21% | 49.55% | 95% | 0% | 2427 | -87
[5 empty] | 2019-09-09 | 17 | 6031.5 | 2413 | -103 | 1 | 0 | 2516 | 1820.6101 | 1820.6101 | 1820.6101 | 965.3751 | 780 | 200 | 1945.3751 | 48.63% | 95% | 0% | -117.849 | 1702.7611 | -3550 | -400 | -2247.2389 | 56.18% | 49.55% | 95% | 0% | 2516 | -103
[5 empty] | 2019-09-09 | 18 | 6032 | 2403 | -114 | 1 | 0 | 2517 | 1822.1764 | 1822.1764 | 1822.1764 | 965.3751 | 780 | 200 | 1945.3751 | 48.63% | 95% | 0% | -130.4348 | 1691.7416 | -3550 | -400 | -2258.2584 | 56.46% | 49.54% | 95% | 0% | 2517 | -114
[5 empty] | 2019-09-09 | 19 | 6032.5 | 2451 | -126 | 1 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 965.3751 | 780 | 200 | 1945.3751 | 48.63% | 95% | 0% | -144.1648 | 1771.9935 | -3550 | -400 | -2178.0065 | 54.45% | 49.54% | 95% | 0% | 2577 | -126
[5 empty] | 2019-09-09 | 20 | 6033 | 2451 | -140 | 1 | 0 | 2591 | 1938.0874 | 1938.0874 | 1938.0874 | 965.3751 | 780 | 200 | 1945.3751 | 48.63% | 95% | 0% | -160.1831 | 1777.9043 | -3550 | -400 | -2172.0957 | 54.3% | 49.54% | 95% | 0% | 2591 | -140
[5 empty] | 2019-09-09 | 21 | 6033.5 | 2441 | -153 | 1 | 0 | 2594 | 1942.7865 | 1942.7865 | 1942.7865 | 965.3751 | 780 | 200 | 1945.3751 | 48.63% | 95% | 0% | -175.0572 | 1767.7293 | -3550 | -400 | -2182.2707 | 54.56% | 49.53% | 95% | 0% | 2594 | -153
[5 empty] | 2019-09-09 | 22 | 6034 | 2439 | -169 | 1 | 0 | 2608 | 1964.7156 | 1964.7156 | 1964.7156 | 965.3751 | 780 | 200 | 1945.3751 | 48.63% | 95% | 0% | -193.3638 | 1771.3517 | -3550 | -400 | -2178.6483 | 54.47% | 49.53% | 95% | 0% | 2608 | -169
[5 empty] | 2019-09-09 | 23 | 6034.5 | 2443 | -184 | 1 | 0 | 2627 | 1994.4765 | 1994.4765 | 1994.4765 | 965.3751 | 780 | 200 | 1945.3751 | 48.63% | 95% | 0% | -210.5263 | 1783.9502 | -3550 | -400 | -2166.0498 | 54.15% | 49.53% | 95% | 0% | 2627 | -184
[5 empty] | 2019-09-09 | 24 | 6035 | 2418 | -194 | 1 | 0 | 2612 | 1970.981 | 1970.981 | 1970.981 | 963.8087 | 780 | 200 | 1943.8087 | 48.6% | 95% | 0% | -221.968 | 1749.0131 | -3550 | -400 | -2200.9869 | 55.02% | 49.53% | 95% | 0% | 2612 | -194
[5 empty] | 2019-09-09 | 25 | 6035.5 | 2411 | -204 | 1 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 963.8087 | 780 | 200 | 1943.8087 | 48.6% | 95% | 0% | -233.4096 | 1742.2705 | -3550 | -400 | -2207.7295 | 55.19% | 49.52% | 95% | 0% | 2615 | -204
[5 empty] | 2019-09-09 | 26 | 6036 | 2388 | -209 | 1 | 0 | 2597 | 1947.4856 | 1947.4856 | 1947.4856 | 963.8087 | 780 | 200 | 1943.8087 | 48.6% | 95% | 0% | -239.1304 | 1708.3551 | -3550 | -400 | -2241.6449 | 56.04% | 49.51% | 95% | 0% | 2597 | -209
[5 empty] | 2019-09-09 | 27 | 6036.5 | 2347 | -223 | 1 | 0 | 2570 | 1905.1937 | 1905.1937 | 1905.1937 | 963.8087 | 780 | 200 | 1943.8087 | 48.6% | 95% | 0% | -255.1487 | 1650.045 | -3550 | -400 | -2299.955 | 57.5% | 49.51% | 95% | 0% | 2570 | -223
[5 empty] | 2019-09-09 | 28 | 6037 | 2323 | -213 | 1 | 0 | 2536 | 1851.9373 | 1851.9373 | 1851.9373 | 963.8087 | 780 | 200 | 1943.8087 | 48.6% | 95% | 0% | -243.7071 | 1608.2303 | -3550 | -400 | -2341.7697 | 58.54% | 49.51% | 95% | 0% | 2536 | -213
[5 empty] | 2019-09-09 | 29 | 6037.5 | 2304 | -210 | 1 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 963.8087 | 780 | 200 | 1943.8087 | 48.6% | 95% | 0% | -240.2746 | 1577.2027 | -3550 | -400 | -2372.7973 | 59.32% | 49.51% | 95% | 0% | 2514 | -210
[5 empty] | 2019-09-09 | 30 | 6038 | 2315 | -194 | 1 | 0 | 2509 | 1809.6455 | 1809.6455 | 1809.6455 | 963.8087 | 780 | 200 | 1943.8087 | 48.6% | 95% | 0% | -221.968 | 1587.6775 | -3550 | -400 | -2362.3225 | 59.06% | 49.51% | 95% | 0% | 2509 | -194
[5 empty] | 2019-09-09 | 31 | 6038.5 | 2322 | -179 | 1 | 0 | 2501 | 1797.1146 | 1797.1146 | 1797.1146 | 963.8087 | 780 | 200 | 1943.8087 | 48.6% | 95% | 0% | -204.8055 | 1592.3091 | -3550 | -400 | -2357.6909 | 58.94% | 49.5% | 95% | 0% | 2501 | -179
[5 empty] | 2019-09-09 | 32 | 6039 | 2385 | -162 | 1 | 0 | 2547 | 1869.1674 | 1869.1674 | 1869.1674 | 963.8087 | 780 | 200 | 1943.8087 | 48.6% | 95% | 0% | -185.3547 | 1683.8127 | -3550 | -400 | -2266.1873 | 56.65% | 49.49% | 95% | 0% | 2547 | -162
[5 empty] | 2019-09-09 | 33 | 6039.5 | 2485 | -149 | 1 | 0 | 2634 | 2005.4411 | 2005.4411 | 2005.4411 | 963.8087 | 780 | 200 | 1943.8087 | 48.6% | 95% | 0% | -170.4805 | 1834.9605 | -3550 | -400 | -2115.0395 | 52.88% | 49.49% | 95% | 0% | 2634 | -149
[5 empty] | 2019-09-09 | 34 | 6040 | 2566 | -131 | 1 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 963.8087 | 780 | 200 | 1943.8087 | 48.6% | 95% | 0% | -149.8856 | 1954.2364 | -3550 | -400 | -1995.7636 | 49.89% | 49.47% | 95% | 0% | 2697 | -131
[5 empty] | 2019-09-09 | 35 | 6040.5 | 2630 | -114 | 1 | 0 | 2744 | 2177.7411 | 2177.7411 | 2177.7411 | 962.2424 | 780 | 200 | 1942.2424 | 48.56% | 95% | 0% | -130.4348 | 2047.3064 | -3550 | -400 | -1902.6936 | 47.57% | 49.47% | 95% | 0% | 2744 | -114
[5 empty] | 2019-09-09 | 36 | 6041 | 2668 | -86 | 1 | 0 | 2754 | 2193.4048 | 2193.4048 | 2193.4048 | 962.2424 | 780 | 200 | 1942.2424 | 48.56% | 95% | 0% | -98.3982 | 2095.0066 | -3550 | -400 | -1854.9934 | 46.37% | 49.47% | 95% | 0% | 2754 | -86
[5 empty] | 2019-09-09 | 37 | 6041.5 | 2682 | -70 | 1 | 0 | 2752 | 2190.2721 | 2190.2721 | 2190.2721 | 962.2424 | 780 | 200 | 1942.2424 | 48.56% | 95% | 0% | -80.0915 | 2110.1805 | -3550 | -400 | -1839.8195 | 46% | 49.46% | 95% | 0% | 2752 | -70
[5 empty] | 2019-09-09 | 38 | 6042 | 2687 | -55 | 1 | 0 | 2742 | 2174.6084 | 2174.6084 | 2174.6084 | 962.2424 | 780 | 200 | 1942.2424 | 48.56% | 95% | 0% | -62.9291 | 2111.6793 | -3550 | -400 | -1838.3207 | 45.96% | 49.46% | 95% | 0% | 2742 | -55
[5 empty] | 2019-09-09 | 39 | 6042.5 | 2675 | -48 | 1 | 0 | 2723 | 2144.8475 | 2144.8475 | 2144.8475 | 962.2424 | 780 | 200 | 1942.2424 | 48.56% | 95% | 0% | -54.9199 | 2089.9276 | -3550 | -400 | -1860.0724 | 46.5% | 49.46% | 95% | 0% | 2723 | -48
[5 empty] | 2019-09-09 | 40 | 6043 | 2695 | -46 | 1 | 0 | 2741 | 2173.042 | 2173.042 | 2173.042 | 962.2424 | 780 | 200 | 1942.2424 | 48.56% | 95% | 0% | -52.6316 | 2120.4105 | -3550 | -400 | -1829.5895 | 45.74% | 49.45% | 95% | 0% | 2741 | -46
[5 empty] | 2019-09-09 | 41 | 6043.5 | 2662 | -45 | 1 | 0 | 2707 | 2119.7857 | 2119.7857 | 2119.7857 | 962.2424 | 780 | 200 | 1942.2424 | 48.56% | 95% | 0% | -51.4874 | 2068.2982 | -3550 | -400 | -1881.7018 | 47.04% | 49.45% | 95% | 0% | 2707 | -45
[5 empty] | 2019-09-09 | 42 | 6044 | 2557 | -44 | 0 | 0 | 2601 | 1953.751 | 1953.751 | 1953.751 | 962.2424 | 780 | 200 | 1942.2424 | 48.56% | 95% | 0% | -50.3432 | 1903.4078 | -2750 | -200 | -1046.5922 | 26.16% | 49.44% | 95% | 0% | 2601 | -44
[5 empty] | 2019-09-09 | 43 | 6044.5 | 2449 | -43 | 0 | 0 | 2492 | 1783.0173 | 1783.0173 | 1783.0173 | 962.2424 | 780 | 200 | 1942.2424 | 48.56% | 95% | 0% | -49.1991 | 1733.8182 | -2750 | -200 | -1216.1818 | 30.4% | 49.44% | 95% | 0% | 2492 | -43
[5 empty] | 2019-09-09 | 44 | 6045 | 2310 | -43 | 0 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 962.2424 | 780 | 200 | 1942.2424 | 48.56% | 95% | 0% | -49.1991 | 1516.0936 | -2750 | -200 | -1433.9064 | 35.85% | 49.44% | 95% | 0% | 2353 | -43
[5 empty] | 2019-09-09 | 45 | 6045.5 | 2159 | -42 | 0 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 962.2424 | 780 | 200 | 1942.2424 | 48.56% | 95% | 0% | -48.0549 | 1279.1504 | -2750 | -200 | -1670.8496 | 41.77% | 49.43% | 95% | 0% | 2201 | -42
[5 empty] | 2019-09-09 | 46 | 6046 | 1999 | -42 | 1 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -48.0549 | 1028.5321 | -3550 | -400 | -2921.4679 | 73.04% | 49.43% | 95% | 0% | 2041 | -42
[5 empty] | 2019-09-09 | 47 | 6046.5 | 1869 | -41 | 1 | 0 | 1910 | 871.3932 | 871.3932 | 871.3932 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -46.9108 | 824.4825 | -3550 | -400 | -3125.5175 | 78.14% | 49.43% | 95% | 0% | 1910 | -41
[5 empty] | 2019-09-09 | 48 | 6047 | 1770 | -41 | 1 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -46.9108 | 669.4124 | -3550 | -400 | -3280.5876 | 82.01% | 49.42% | 95% | 0% | 1811 | -41
[5 empty] | 2019-09-10 | 1 | 6047.5 | 1684 | -40 | 1 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -45.7666 | 534.2829 | -3550 | -400 | -3415.7171 | 85.39% | 49.42% | 95% | 0% | 1724 | -40
[5 empty] | 2019-09-10 | 2 | 6048 | 1634 | -40 | 1 | 0 | 1674 | 501.7312 | 501.7312 | 501.7312 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -45.7666 | 455.9647 | -3550 | -400 | -3494.0353 | 87.35% | 49.41% | 95% | 0% | 1674 | -40
[5 empty] | 2019-09-10 | 3 | 6048.5 | 1612 | -40 | 1 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -45.7666 | 421.5046 | -3550 | -400 | -3528.4954 | 88.21% | 49.41% | 95% | 0% | 1652 | -40
[5 empty] | 2019-09-10 | 4 | 6049 | 1597 | -40 | 1 | 0 | 1637 | 443.7758 | 443.7758 | 443.7758 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -45.7666 | 398.0092 | -3550 | -400 | -3551.9908 | 88.8% | 49.41% | 95% | 0% | 1637 | -40
[5 empty] | 2019-09-10 | 5 | 6049.5 | 1578 | -39 | 1 | 0 | 1617 | 412.4485 | 412.4485 | 412.4485 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -44.6224 | 367.826 | -3550 | -400 | -3582.174 | 89.55% | 49.41% | 95% | 0% | 1617 | -39
[5 empty] | 2019-09-10 | 6 | 6050 | 1560 | -39 | 1 | 0 | 1599 | 384.2539 | 384.2539 | 384.2539 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -44.6224 | 339.6315 | -3550 | -400 | -3610.3685 | 90.26% | 49.4% | 95% | 0% | 1599 | -39
[5 empty] | 2019-09-10 | 7 | 6050.5 | 1545 | -38 | 1 | 0 | 1583 | 359.1921 | 359.1921 | 359.1921 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -43.4783 | 315.7138 | -3550 | -400 | -3634.2862 | 90.86% | 49.4% | 95% | 0% | 1583 | -38
[5 empty] | 2019-09-10 | 8 | 6051 | 1544 | -38 | 1 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -43.4783 | 314.1475 | -3550 | -400 | -3635.8525 | 90.9% | 49.4% | 95% | 0% | 1582 | -38
[5 empty] | 2019-09-10 | 9 | 6051.5 | 1551 | -37 | 1 | 0 | 1588 | 367.0239 | 367.0239 | 367.0239 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -42.3341 | 324.6898 | -3550 | -400 | -3625.3102 | 90.63% | 49.4% | 95% | 0% | 1588 | -37
[5 empty] | 2019-09-10 | 10 | 6052 | 1564 | -36 | 1 | 0 | 1600 | 385.8203 | 385.8203 | 385.8203 | 960.676 | 780 | 200 | 1940.676 | 48.52% | 95% | 0% | -41.1899 | 344.6303 | -3550 | -400 | -3605.3697 | 90.13% | 49.4% | 95% | 0% | 1600 | -36
[5 empty] | 2019-09-10 | 11 | 6052.5 | 1629 | -36 | 1 | 0 | 1665 | 487.634 | 487.634 | 487.634 | 959.1096 | 780 | 200 | 1939.1096 | 48.48% | 95% | 0% | -41.1899 | 446.444 | -3550 | -400 | -3503.556 | 87.59% | 49.39% | 95% | 0% | 1665 | -36
[5 empty] | 2019-09-10 | 12 | 6053 | 1729 | -36 | 1 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 959.1096 | 780 | 200 | 1939.1096 | 48.48% | 95% | 0% | -41.1899 | 603.0805 | -3550 | -400 | -3346.9195 | 83.67% | 49.38% | 95% | 0% | 1765 | -36
[5 empty] | 2019-09-10 | 13 | 6053.5 | 1931 | -36 | 1 | 0 | 1967 | 960.676 | 960.676 | 960.676 | 959.1096 | 780 | 200 | 1939.1096 | 48.48% | 95% | 0% | -41.1899 | 919.4861 | -3550 | -400 | -3030.5139 | 75.76% | 49.38% | 95% | 0% | 1967 | -36
[5 empty] | 2019-09-10 | 14 | 6054 | 2103 | -39 | 1 | 0 | 2142 | 1234.7898 | 1234.7898 | 1234.7898 | 959.1096 | 780 | 200 | 1939.1096 | 48.48% | 95% | 0% | -44.6224 | 1190.1674 | -3550 | -400 | -2759.8326 | 69% | 49.38% | 95% | 0% | 2142 | -39
[5 empty] | 2019-09-10 | 15 | 6054.5 | 2312 | -53 | 1 | 0 | 2365 | 1584.089 | 1584.089 | 1584.089 | 959.1096 | 780 | 200 | 1939.1096 | 48.48% | 95% | 0% | -60.6407 | 1523.4483 | -3550 | -400 | -2426.5517 | 60.66% | 49.38% | 95% | 0% | 2365 | -53
[5 empty] | 2019-09-10 | 16 | 6055 | 2354 | -81 | 1 | 0 | 2435 | 1693.7345 | 1693.7345 | 1693.7345 | 959.1096 | 780 | 200 | 1939.1096 | 48.48% | 95% | 0% | -92.6773 | 1601.0572 | -3550 | -400 | -2348.9428 | 58.72% | 49.36% | 95% | 0% | 2435 | -81
[5 empty] | 2019-09-10 | 17 | 6055.5 | 2339 | -124 | 1 | 0 | 2463 | 1737.5927 | 1737.5927 | 1737.5927 | 959.1096 | 780 | 200 | 1939.1096 | 48.48% | 95% | 0% | -141.8764 | 1595.7163 | -3550 | -400 | -2354.2837 | 58.86% | 49.36% | 95% | 0% | 2463 | -124
[5 empty] | 2019-09-10 | 18 | 6056 | 2262 | -166 | 1 | 0 | 2428 | 1682.77 | 1682.77 | 1682.77 | 959.1096 | 780 | 200 | 1939.1096 | 48.48% | 95% | 0% | -189.9314 | 1492.8386 | -3550 | -400 | -2457.1614 | 61.43% | 49.36% | 95% | 0% | 2428 | -166
[5 empty] | 2019-09-10 | 19 | 6056.5 | 2205 | -220 | 1 | 0 | 2425 | 1678.0709 | 1678.0709 | 1678.0709 | 959.1096 | 780 | 200 | 1939.1096 | 48.48% | 95% | 0% | -251.7162 | 1426.3547 | -3550 | -400 | -2523.6453 | 63.09% | 49.36% | 95% | 0% | 2425 | -220
[5 empty] | 2019-09-10 | 20 | 6057 | 2156 | -278 | 1 | 0 | 2434 | 1692.1682 | 1692.1682 | 1692.1682 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -318.0778 | 1374.0904 | -3550 | -400 | -2575.9096 | 64.4% | 49.35% | 95% | 0% | 2434 | -278
[5 empty] | 2019-09-10 | 21 | 6057.5 | 2031 | -359 | 1 | 0 | 2390 | 1623.2481 | 1623.2481 | 1623.2481 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -410.7551 | 1212.493 | -3550 | -400 | -2737.507 | 68.44% | 49.35% | 95% | 0% | 2390 | -359
[5 empty] | 2019-09-10 | 22 | 6058 | 1974 | -375 | 1 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -429.0618 | 1129.9654 | -3550 | -400 | -2820.0346 | 70.5% | 49.35% | 95% | 0% | 2349 | -375
[5 empty] | 2019-09-10 | 23 | 6058.5 | 1904 | -411 | 1 | 0 | 2315 | 1505.7708 | 1505.7708 | 1505.7708 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -470.2517 | 1035.5191 | -3550 | -400 | -2914.4809 | 72.86% | 49.34% | 95% | 0% | 2315 | -411
[5 empty] | 2019-09-10 | 24 | 6059 | 1874 | -446 | 1 | 0 | 2320 | 1513.6026 | 1513.6026 | 1513.6026 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -510.2975 | 1003.3052 | -3550 | -400 | -2946.6948 | 73.67% | 49.34% | 95% | 0% | 2320 | -446
[5 empty] | 2019-09-10 | 25 | 6059.5 | 1877 | -451 | 1 | 0 | 2328 | 1526.1336 | 1526.1336 | 1526.1336 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -516.0183 | 1010.1152 | -3550 | -400 | -2939.8848 | 73.5% | 49.34% | 95% | 0% | 2328 | -451
[5 empty] | 2019-09-10 | 26 | 6060 | 1858 | -469 | 1 | 0 | 2327 | 1524.5672 | 1524.5672 | 1524.5672 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -536.6133 | 987.9539 | -3550 | -400 | -2962.0461 | 74.05% | 49.34% | 95% | 0% | 2327 | -469
[5 empty] | 2019-09-10 | 27 | 6060.5 | 1851 | -454 | 1 | 0 | 2305 | 1490.1072 | 1490.1072 | 1490.1072 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -519.4508 | 970.6564 | -3550 | -400 | -2979.3436 | 74.48% | 49.34% | 95% | 0% | 2305 | -454
[5 empty] | 2019-09-10 | 28 | 6061 | 1884 | -418 | 1 | 0 | 2302 | 1485.4081 | 1485.4081 | 1485.4081 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -478.2609 | 1007.1472 | -3550 | -400 | -2942.8528 | 73.57% | 49.33% | 95% | 0% | 2302 | -418
[5 empty] | 2019-09-10 | 29 | 6061.5 | 1887 | -408 | 1 | 0 | 2295 | 1474.4435 | 1474.4435 | 1474.4435 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -466.8192 | 1007.6243 | -3550 | -400 | -2942.3757 | 73.56% | 49.33% | 95% | 0% | 2295 | -408
[5 empty] | 2019-09-10 | 30 | 6062 | 1913 | -374 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -427.9176 | 1033.995 | -3550 | -400 | -2916.005 | 72.9% | 49.32% | 95% | 0% | 2287 | -374
[5 empty] | 2019-09-10 | 31 | 6062.5 | 1921 | -343 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -392.4485 | 1033.4377 | -3550 | -400 | -2916.5623 | 72.91% | 49.31% | 95% | 0% | 2264 | -343
[5 empty] | 2019-09-10 | 32 | 6063 | 1986 | -333 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -381.0069 | 1131.0294 | -3550 | -400 | -2818.9706 | 70.47% | 49.3% | 95% | 0% | 2319 | -333
[5 empty] | 2019-09-10 | 33 | 6063.5 | 2064 | -311 | 1 | 0 | 2375 | 1599.7527 | 1599.7527 | 1599.7527 | 957.5433 | 780 | 200 | 1937.5433 | 48.44% | 95% | 0% | -355.8352 | 1243.9174 | -3550 | -400 | -2706.0826 | 67.65% | 49.3% | 95% | 0% | 2375 | -311
[5 empty] | 2019-09-10 | 34 | 6064 | 2132 | -305 | 1 | 0 | 2437 | 1696.8673 | 1696.8673 | 1696.8673 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -348.9703 | 1347.897 | -3550 | -400 | -2602.103 | 65.05% | 49.3% | 95% | 0% | 2437 | -305
[5 empty] | 2019-09-10 | 35 | 6064.5 | 2230 | -264 | 1 | 0 | 2494 | 1786.15 | 1786.15 | 1786.15 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -302.0595 | 1484.0905 | -3550 | -400 | -2465.9095 | 61.65% | 49.3% | 95% | 0% | 2494 | -264
[5 empty] | 2019-09-10 | 36 | 6065 | 2338 | -208 | 1 | 0 | 2546 | 1867.601 | 1867.601 | 1867.601 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -237.9863 | 1629.6147 | -3550 | -400 | -2320.3853 | 58.01% | 49.3% | 95% | 0% | 2546 | -208
[5 empty] | 2019-09-10 | 37 | 6065.5 | 2410 | -158 | 1 | 0 | 2568 | 1902.061 | 1902.061 | 1902.061 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -180.778 | 1721.283 | -3550 | -400 | -2228.717 | 55.72% | 49.3% | 95% | 0% | 2568 | -158
[5 empty] | 2019-09-10 | 38 | 6066 | 2451 | -133 | 1 | 0 | 2584 | 1927.1228 | 1927.1228 | 1927.1228 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -152.1739 | 1774.9489 | -3550 | -400 | -2175.0511 | 54.38% | 49.3% | 95% | 0% | 2584 | -133
[5 empty] | 2019-09-10 | 39 | 6066.5 | 2490 | -118 | 1 | 0 | 2608 | 1964.7156 | 1964.7156 | 1964.7156 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -135.0114 | 1829.7041 | -3550 | -400 | -2120.2959 | 53.01% | 49.29% | 95% | 0% | 2608 | -118
[5 empty] | 2019-09-10 | 40 | 6067 | 2520 | -120 | 1 | 0 | 2640 | 2014.8392 | 2014.8392 | 2014.8392 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -137.2998 | 1877.5395 | -3550 | -400 | -2072.4605 | 51.81% | 49.27% | 95% | 0% | 2640 | -120
[5 empty] | 2019-09-10 | 41 | 6067.5 | 2498 | -124 | 1 | 0 | 2622 | 1986.6447 | 1986.6447 | 1986.6447 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -141.8764 | 1844.7683 | -3550 | -400 | -2105.2317 | 52.63% | 49.27% | 95% | 0% | 2622 | -124
[5 empty] | 2019-09-10 | 42 | 6068 | 2400 | -127 | 0 | 0 | 2527 | 1837.8401 | 1837.8401 | 1837.8401 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -145.3089 | 1692.5311 | -2750 | -200 | -1257.4689 | 31.44% | 49.26% | 95% | 0% | 2527 | -127
[5 empty] | 2019-09-10 | 43 | 6068.5 | 2263 | -131 | 0 | 0 | 2394 | 1629.5136 | 1629.5136 | 1629.5136 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -149.8856 | 1479.628 | -2750 | -200 | -1470.372 | 36.76% | 49.26% | 95% | 0% | 2394 | -131
[5 empty] | 2019-09-10 | 44 | 6069 | 2119 | -134 | 0 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -153.3181 | 1255.3381 | -2750 | -200 | -1694.6619 | 42.37% | 49.25% | 95% | 0% | 2253 | -134
[5 empty] | 2019-09-10 | 45 | 6069.5 | 1949 | -139 | 0 | 0 | 2088 | 1150.2061 | 1150.2061 | 1150.2061 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -159.0389 | 991.1672 | -2750 | -200 | -1958.8328 | 48.97% | 49.24% | 95% | 0% | 2088 | -139
[5 empty] | 2019-09-10 | 46 | 6070 | 1784 | -144 | 0 | 0 | 1928 | 899.5878 | 899.5878 | 899.5878 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -164.7597 | 734.8281 | -2750 | -200 | -2215.1719 | 55.38% | 49.24% | 95% | 0% | 1928 | -144
[5 empty] | 2019-09-10 | 47 | 6070.5 | 1623 | -150 | 0 | 0 | 1773 | 656.8013 | 656.8013 | 656.8013 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -171.6247 | 485.1766 | -2750 | -200 | -2464.8234 | 61.62% | 49.24% | 95% | 0% | 1773 | -150
[5 empty] | 2019-09-10 | 48 | 6071 | 1502 | -155 | 0 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -177.3455 | 297.7575 | -2750 | -200 | -2652.2425 | 66.31% | 49.24% | 95% | 0% | 1657 | -155
[5 empty] | 2019-09-11 | 1 | 6071.5 | 1400 | -159 | 0 | 0 | 1559 | 321.5993 | 321.5993 | 321.5993 | 955.9769 | 780 | 200 | 1935.9769 | 48.4% | 95% | 0% | -181.9222 | 139.6771 | -2750 | -200 | -2810.3229 | 70.26% | 49.23% | 95% | 0% | 1559 | -159
[5 empty] | 2019-09-11 | 2 | 6072 | 1334 | -163 | 0 | 0 | 1497 | 224.4847 | 224.4847 | 224.4847 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -186.4989 | 37.9859 | -2750 | -200 | -2912.0141 | 72.8% | 49.23% | 95% | 0% | 1497 | -163
[5 empty] | 2019-09-11 | 3 | 6072.5 | 1293 | -168 | 0 | 0 | 1461 | 168.0956 | 168.0956 | 168.0956 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -192.2197 | -24.124 | -2750 | -200 | -2974.124 | 74.35% | 49.23% | 95% | 0% | 1461 | -168
[5 empty] | 2019-09-11 | 4 | 6073 | 1275 | -172 | 0 | 0 | 1447 | 146.1665 | 146.1665 | 146.1665 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -196.7963 | -50.6298 | -2750 | -200 | -3000.6298 | 75.02% | 49.23% | 95% | 0% | 1447 | -172
[5 empty] | 2019-09-11 | 5 | 6073.5 | 1232 | -175 | 0 | 0 | 1407 | 83.512 | 83.512 | 83.512 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -200.2288 | -116.7169 | -2750 | -200 | -3066.7169 | 76.67% | 49.23% | 95% | 0% | 1407 | -175
[5 empty] | 2019-09-11 | 6 | 6074 | 1203 | -179 | 0 | 0 | 1382 | 44.3528 | 44.3528 | 44.3528 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -204.8055 | -160.4526 | -2750 | -200 | -3110.4526 | 77.76% | 49.22% | 95% | 0% | 1382 | -179
[5 empty] | 2019-09-11 | 7 | 6074.5 | 1187 | -181 | 0 | 0 | 1368 | 22.4237 | 22.4237 | 22.4237 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -207.0938 | -184.6701 | -2750 | -200 | -3134.6701 | 78.37% | 49.22% | 95% | 0% | 1368 | -181
[5 empty] | 2019-09-11 | 8 | 6075 | 1161 | -183 | 0 | 0 | 1344 | -15.169 | -15.169 | -15.169 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -209.3822 | -224.5512 | -2750 | -200 | -3174.5512 | 79.36% | 49.21% | 95% | 0% | 1344 | -183
[5 empty] | 2019-09-11 | 9 | 6075.5 | 1170 | -180 | 0 | 0 | 1350 | -5.7708 | -5.7708 | -5.7708 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -205.9497 | -211.7205 | -2750 | -200 | -3161.7205 | 79.04% | 49.21% | 95% | 0% | 1350 | -180
[5 empty] | 2019-09-11 | 10 | 6076 | 1181 | -176 | 0 | 0 | 1357 | 5.1937 | 5.1937 | 5.1937 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -201.373 | -196.1793 | -2750 | -200 | -3146.1793 | 78.65% | 49.21% | 95% | 0% | 1357 | -176
[5 empty] | 2019-09-11 | 11 | 6076.5 | 1250 | -176 | 0 | 0 | 1426 | 113.2729 | 113.2729 | 113.2729 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -201.373 | -88.1001 | -2750 | -200 | -3038.1001 | 75.95% | 49.21% | 95% | 0% | 1426 | -176
[5 empty] | 2019-09-11 | 12 | 6077 | 1335 | -175 | 0 | 0 | 1510 | 244.8475 | 244.8475 | 244.8475 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -200.2288 | 44.6187 | -2750 | -200 | -2905.3813 | 72.63% | 49.21% | 95% | 0% | 1510 | -175
[5 empty] | 2019-09-11 | 13 | 6077.5 | 1571 | -177 | 0 | 0 | 1748 | 617.6422 | 617.6422 | 617.6422 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -202.5172 | 415.125 | -2750 | -200 | -2534.875 | 63.37% | 49.21% | 95% | 0% | 1748 | -177
[5 empty] | 2019-09-11 | 14 | 6078 | 1745 | -180 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -205.9497 | 688.939 | -2750 | -200 | -2261.061 | 56.53% | 49.2% | 95% | 0% | 1925 | -180
[5 empty] | 2019-09-11 | 15 | 6078.5 | 1969 | -187 | 0 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 954.4106 | 780 | 200 | 1934.4106 | 48.36% | 95% | 0% | -213.9588 | 1042.7601 | -2750 | -200 | -1907.2399 | 47.68% | 49.2% | 95% | 0% | 2156 | -187
[5 empty] | 2019-09-11 | 16 | 6079 | 2080 | -202 | 1 | 0 | 2282 | 1454.0808 | 1454.0808 | 1454.0808 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -231.1213 | 1222.9595 | -3550 | -400 | -2727.0405 | 68.18% | 49.19% | 95% | 0% | 2282 | -202
[5 empty] | 2019-09-11 | 17 | 6079.5 | 2131 | -225 | 1 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -257.4371 | 1312.5547 | -3550 | -400 | -2637.4453 | 65.94% | 49.18% | 95% | 0% | 2356 | -225
[5 empty] | 2019-09-11 | 18 | 6080 | 2087 | -255 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -291.762 | 1256.3006 | -3550 | -400 | -2693.6994 | 67.34% | 49.18% | 95% | 0% | 2342 | -255
[5 empty] | 2019-09-11 | 19 | 6080.5 | 2079 | -288 | 1 | 0 | 2367 | 1587.2218 | 1587.2218 | 1587.2218 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -329.5195 | 1257.7023 | -3550 | -400 | -2692.2977 | 67.31% | 49.18% | 95% | 0% | 2367 | -288
[5 empty] | 2019-09-11 | 20 | 6081 | 2025 | -326 | 1 | 0 | 2351 | 1562.1599 | 1562.1599 | 1562.1599 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -372.9977 | 1189.1622 | -3550 | -400 | -2760.8378 | 69.02% | 49.18% | 95% | 0% | 2351 | -326
[5 empty] | 2019-09-11 | 21 | 6081.5 | 1922 | -379 | 1 | 0 | 2301 | 1483.8417 | 1483.8417 | 1483.8417 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -433.6384 | 1050.2033 | -3550 | -400 | -2899.7967 | 72.49% | 49.17% | 95% | 0% | 2301 | -379
[5 empty] | 2019-09-11 | 22 | 6082 | 1868 | -420 | 1 | 0 | 2288 | 1463.479 | 1463.479 | 1463.479 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -480.5492 | 982.9298 | -3550 | -400 | -2967.0702 | 74.18% | 49.17% | 95% | 0% | 2288 | -420
[5 empty] | 2019-09-11 | 23 | 6082.5 | 1834 | -447 | 1 | 0 | 2281 | 1452.5144 | 1452.5144 | 1452.5144 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -511.4416 | 941.0728 | -3550 | -400 | -3008.9272 | 75.22% | 49.17% | 95% | 0% | 2281 | -447
[5 empty] | 2019-09-11 | 24 | 6083 | 1805 | -465 | 1 | 0 | 2270 | 1435.2844 | 1435.2844 | 1435.2844 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -532.0366 | 903.2478 | -3550 | -400 | -3046.7522 | 76.17% | 49.17% | 95% | 0% | 2270 | -465
[5 empty] | 2019-09-11 | 25 | 6083.5 | 1784 | -477 | 1 | 0 | 2261 | 1421.1871 | 1421.1871 | 1421.1871 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -545.7666 | 875.4205 | -3550 | -400 | -3074.5795 | 76.86% | 49.16% | 95% | 0% | 2261 | -477
[5 empty] | 2019-09-11 | 26 | 6084 | 1759 | -490 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -560.6407 | 841.75 | -3550 | -400 | -3108.25 | 77.71% | 49.16% | 95% | 0% | 2249 | -490
[5 empty] | 2019-09-11 | 27 | 6084.5 | 1728 | -499 | 1 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -570.9382 | 796.9925 | -3550 | -400 | -3153.0075 | 78.83% | 49.16% | 95% | 0% | 2227 | -499
[5 empty] | 2019-09-11 | 28 | 6085 | 1716 | -494 | 1 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 952.8442 | 780 | 200 | 1932.8442 | 48.32% | 95% | 0% | -565.2174 | 776.0852 | -3550 | -400 | -3173.9148 | 79.35% | 49.16% | 95% | 0% | 2210 | -494
[5 empty] | 2019-09-11 | 29 | 6085.5 | 1689 | -492 | 1 | 0 | 2181 | 1295.878 | 1295.878 | 1295.878 | 951.2778 | 780 | 200 | 1931.2778 | 48.28% | 95% | 0% | -562.9291 | 732.9489 | -3550 | -400 | -3217.0511 | 80.43% | 49.16% | 95% | 0% | 2181 | -492
[5 empty] | 2019-09-11 | 30 | 6086 | 1687 | -475 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 951.2778 | 780 | 200 | 1931.2778 | 48.28% | 95% | 0% | -543.4783 | 722.6388 | -3550 | -400 | -3227.3612 | 80.68% | 49.15% | 95% | 0% | 2162 | -475
[5 empty] | 2019-09-11 | 31 | 6086.5 | 1687 | -459 | 1 | 0 | 2146 | 1241.0552 | 1241.0552 | 1241.0552 | 951.2778 | 780 | 200 | 1931.2778 | 48.28% | 95% | 0% | -525.1716 | 715.8836 | -3550 | -400 | -3234.1164 | 80.85% | 49.13% | 95% | 0% | 2146 | -459
[5 empty] | 2019-09-11 | 32 | 6087 | 1770 | -431 | 1 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 951.2778 | 780 | 200 | 1931.2778 | 48.28% | 95% | 0% | -493.135 | 834.0703 | -3550 | -400 | -3115.9297 | 77.9% | 49.13% | 95% | 0% | 2201 | -431
[5 empty] | 2019-09-11 | 33 | 6087.5 | 1876 | -398 | 1 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 951.2778 | 780 | 200 | 1931.2778 | 48.28% | 95% | 0% | -455.3776 | 986.1723 | -3550 | -400 | -2963.8277 | 74.1% | 49.11% | 95% | 0% | 2274 | -398
[5 empty] | 2019-09-11 | 34 | 6088 | 1988 | -364 | 1 | 0 | 2352 | 1563.7263 | 1563.7263 | 1563.7263 | 951.2778 | 780 | 200 | 1931.2778 | 48.28% | 95% | 0% | -416.476 | 1147.2503 | -3550 | -400 | -2802.7497 | 70.07% | 49.1% | 95% | 0% | 2352 | -364
[5 empty] | 2019-09-11 | 35 | 6088.5 | 2108 | -315 | 1 | 0 | 2423 | 1674.9382 | 1674.9382 | 1674.9382 | 951.2778 | 780 | 200 | 1931.2778 | 48.28% | 95% | 0% | -360.4119 | 1314.5263 | -3550 | -400 | -2635.4737 | 65.89% | 49.1% | 95% | 0% | 2423 | -315
[5 empty] | 2019-09-11 | 36 | 6089 | 2196 | -262 | 1 | 0 | 2458 | 1729.7609 | 1729.7609 | 1729.7609 | 951.2778 | 780 | 200 | 1931.2778 | 48.28% | 95% | 0% | -299.7712 | 1429.9898 | -3550 | -400 | -2520.0102 | 63% | 49.1% | 95% | 0% | 2458 | -262
[5 empty] | 2019-09-11 | 37 | 6089.5 | 2269 | -210 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 951.2778 | 780 | 200 | 1931.2778 | 48.28% | 95% | 0% | -240.2746 | 1522.38 | -3550 | -400 | -2427.62 | 60.69% | 49.09% | 95% | 0% | 2479 | -210
[5 empty] | 2019-09-11 | 38 | 6090 | 2324 | -163 | 1 | 0 | 2487 | 1775.1855 | 1775.1855 | 1775.1855 | 951.2778 | 780 | 200 | 1931.2778 | 48.28% | 95% | 0% | -186.4989 | 1588.6866 | -3550 | -400 | -2361.3134 | 59.03% | 49.09% | 95% | 0% | 2487 | -163
[5 empty] | 2019-09-11 | 39 | 6090.5 | 2365 | -133 | 1 | 0 | 2498 | 1792.4155 | 1792.4155 | 1792.4155 | 949.7115 | 780 | 200 | 1929.7115 | 48.24% | 95% | 0% | -152.1739 | 1640.2416 | -3550 | -400 | -2309.7584 | 57.74% | 49.08% | 95% | 0% | 2498 | -133
[5 empty] | 2019-09-11 | 40 | 6091 | 2425 | -124 | 1 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 949.7115 | 780 | 200 | 1929.7115 | 48.24% | 95% | 0% | -141.8764 | 1730.4237 | -3550 | -400 | -2219.5763 | 55.49% | 49.07% | 95% | 0% | 2549 | -124
[5 empty] | 2019-09-11 | 41 | 6091.5 | 2457 | -119 | 1 | 0 | 2576 | 1914.5919 | 1914.5919 | 1914.5919 | 949.7115 | 780 | 200 | 1929.7115 | 48.24% | 95% | 0% | -136.1556 | 1778.4363 | -3550 | -400 | -2171.5637 | 54.29% | 49.07% | 95% | 0% | 2576 | -119
[5 empty] | 2019-09-11 | 42 | 6092 | 2381 | -113 | 0 | 0 | 2494 | 1786.15 | 1786.15 | 1786.15 | 949.7115 | 780 | 200 | 1929.7115 | 48.24% | 95% | 0% | -129.2906 | 1656.8594 | -2750 | -200 | -1293.1406 | 32.33% | 49.06% | 95% | 0% | 2494 | -113
[5 empty] | 2019-09-11 | 43 | 6092.5 | 2288 | -111 | 0 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 949.7115 | 780 | 200 | 1929.7115 | 48.24% | 95% | 0% | -127.0023 | 1510.3431 | -2750 | -200 | -1439.6569 | 35.99% | 49.06% | 95% | 0% | 2399 | -111
[5 empty] | 2019-09-11 | 44 | 6093 | 2154 | -109 | 0 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 949.7115 | 780 | 200 | 1929.7115 | 48.24% | 95% | 0% | -124.714 | 1299.6059 | -2750 | -200 | -1650.3941 | 41.26% | 49.05% | 95% | 0% | 2263 | -109
[5 empty] | 2019-09-11 | 45 | 6093.5 | 2034 | -107 | 0 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 949.7115 | 780 | 200 | 1929.7115 | 48.24% | 95% | 0% | -122.4256 | 1110.7978 | -2750 | -200 | -1839.2022 | 45.98% | 49.05% | 95% | 0% | 2141 | -107
[5 empty] | 2019-09-11 | 46 | 6094 | 1886 | -106 | 0 | 0 | 1992 | 999.8351 | 999.8351 | 999.8351 | 949.7115 | 780 | 200 | 1929.7115 | 48.24% | 95% | 0% | -121.2815 | 878.5537 | -2750 | -200 | -2071.4463 | 51.79% | 49.04% | 95% | 0% | 1992 | -106
[5 empty] | 2019-09-11 | 47 | 6094.5 | 1743 | -105 | 0 | 0 | 1848 | 774.2786 | 774.2786 | 774.2786 | 949.7115 | 780 | 200 | 1929.7115 | 48.24% | 95% | 0% | -120.1373 | 654.1413 | -2750 | -200 | -2295.8587 | 57.4% | 49.04% | 95% | 0% | 1848 | -105
[5 empty] | 2019-09-11 | 48 | 6095 | 1655 | -103 | 0 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 949.7115 | 780 | 200 | 1929.7115 | 48.24% | 95% | 0% | -117.849 | 515.4569 | -2750 | -200 | -2434.5431 | 60.86% | 49.04% | 95% | 0% | 1758 | -103
[5 empty] | 2019-09-12 | 1 | 6095.5 | 1573 | -102 | 0 | 0 | 1675 | 503.2976 | 503.2976 | 503.2976 | 949.7115 | 780 | 200 | 1929.7115 | 48.24% | 95% | 0% | -116.7048 | 386.5928 | -2750 | -200 | -2563.4072 | 64.09% | 49.03% | 95% | 0% | 1675 | -102
[5 empty] | 2019-09-12 | 2 | 6096 | 1521 | -101 | 0 | 0 | 1622 | 420.2803 | 420.2803 | 420.2803 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -115.5606 | 304.7197 | -2750 | -200 | -2645.2803 | 66.13% | 49.03% | 95% | 0% | 1622 | -101
[5 empty] | 2019-09-12 | 3 | 6096.5 | 1489 | -101 | 0 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -115.5606 | 254.596 | -2750 | -200 | -2695.404 | 67.39% | 49.03% | 95% | 0% | 1590 | -101
[5 empty] | 2019-09-12 | 4 | 6097 | 1473 | -101 | 0 | 0 | 1574 | 345.0948 | 345.0948 | 345.0948 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -115.5606 | 229.5342 | -2750 | -200 | -2720.4658 | 68.01% | 49.03% | 95% | 0% | 1574 | -101
[5 empty] | 2019-09-12 | 5 | 6097.5 | 1446 | -101 | 1 | 0 | 1547 | 302.803 | 302.803 | 302.803 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -115.5606 | 187.2423 | -3550 | -400 | -3762.7577 | 94.07% | 49.02% | 95% | 0% | 1547 | -101
[5 empty] | 2019-09-12 | 6 | 6098 | 1425 | -101 | 1 | 0 | 1526 | 269.9093 | 269.9093 | 269.9093 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -115.5606 | 154.3487 | -3550 | -400 | -3795.6513 | 94.89% | 49.02% | 95% | 0% | 1526 | -101
[5 empty] | 2019-09-12 | 7 | 6098.5 | 1411 | -100 | 1 | 0 | 1511 | 246.4138 | 246.4138 | 246.4138 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -114.4165 | 131.9974 | -3550 | -400 | -3818.0026 | 95.45% | 49.02% | 95% | 0% | 1511 | -100
[5 empty] | 2019-09-12 | 8 | 6099 | 1403 | -100 | 1 | 0 | 1503 | 233.8829 | 233.8829 | 233.8829 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -114.4165 | 119.4665 | -3550 | -400 | -3830.5335 | 95.76% | 49.01% | 95% | 0% | 1503 | -100
[5 empty] | 2019-09-12 | 9 | 6099.5 | 1399 | -102 | 1 | 0 | 1501 | 230.7502 | 230.7502 | 230.7502 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -116.7048 | 114.0454 | -3550 | -400 | -3835.9546 | 95.9% | 49.01% | 95% | 0% | 1501 | -102
[5 empty] | 2019-09-12 | 10 | 6100 | 1417 | -103 | 1 | 0 | 1520 | 260.5111 | 260.5111 | 260.5111 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -117.849 | 142.6622 | -3550 | -400 | -3807.3378 | 95.18% | 49% | 95% | 0% | 1520 | -103
[5 empty] | 2019-09-12 | 11 | 6100.5 | 1472 | -102 | 1 | 0 | 1574 | 345.0948 | 345.0948 | 345.0948 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -116.7048 | 228.39 | -3550 | -400 | -3721.61 | 93.04% | 49% | 95% | 0% | 1574 | -102
[5 empty] | 2019-09-12 | 12 | 6101 | 1559 | -101 | 1 | 0 | 1660 | 479.8021 | 479.8021 | 479.8021 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -115.5606 | 364.2415 | -3550 | -400 | -3585.7585 | 89.64% | 48.99% | 95% | 0% | 1660 | -101
[5 empty] | 2019-09-12 | 13 | 6101.5 | 1756 | -101 | 1 | 0 | 1857 | 788.3759 | 788.3759 | 788.3759 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -115.5606 | 672.8153 | -3550 | -400 | -3277.1847 | 81.93% | 48.99% | 95% | 0% | 1857 | -101
[5 empty] | 2019-09-12 | 14 | 6102 | 1952 | -104 | 1 | 0 | 2056 | 1100.0824 | 1100.0824 | 1100.0824 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -118.9931 | 981.0893 | -3550 | -400 | -2968.9107 | 74.22% | 48.99% | 95% | 0% | 2056 | -104
[5 empty] | 2019-09-12 | 15 | 6102.5 | 2139 | -126 | 1 | 0 | 2265 | 1427.4526 | 1427.4526 | 1427.4526 | 948.1451 | 780 | 200 | 1928.1451 | 48.2% | 95% | 0% | -144.1648 | 1283.2878 | -3550 | -400 | -2666.7122 | 66.67% | 48.99% | 95% | 0% | 2265 | -126
[5 empty] | 2019-09-12 | 16 | 6103 | 2182 | -160 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -183.0664 | 1364.9963 | -3550 | -400 | -2585.0037 | 64.63% | 48.99% | 95% | 0% | 2342 | -160
[5 empty] | 2019-09-12 | 17 | 6103.5 | 2193 | -189 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -216.2471 | 1394.4701 | -3550 | -400 | -2555.5299 | 63.89% | 48.98% | 95% | 0% | 2382 | -189
[5 empty] | 2019-09-12 | 18 | 6104 | 2125 | -249 | 1 | 0 | 2374 | 1598.1863 | 1598.1863 | 1598.1863 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -284.897 | 1313.2893 | -3550 | -400 | -2636.7107 | 65.92% | 48.97% | 95% | 0% | 2374 | -249
[5 empty] | 2019-09-12 | 19 | 6104.5 | 2126 | -296 | 1 | 0 | 2422 | 1673.3718 | 1673.3718 | 1673.3718 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -338.6728 | 1334.699 | -3550 | -400 | -2615.301 | 65.38% | 48.97% | 95% | 0% | 2422 | -296
[5 empty] | 2019-09-12 | 20 | 6105 | 2049 | -350 | 1 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -400.4577 | 1236.8878 | -3550 | -400 | -2713.1122 | 67.83% | 48.97% | 95% | 0% | 2399 | -350
[5 empty] | 2019-09-12 | 21 | 6105.5 | 1967 | -392 | 1 | 0 | 2359 | 1574.6908 | 1574.6908 | 1574.6908 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -448.5126 | 1126.1783 | -3550 | -400 | -2823.8217 | 70.6% | 48.96% | 95% | 0% | 2359 | -392
[5 empty] | 2019-09-12 | 22 | 6106 | 1913 | -400 | 1 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -457.6659 | 1044.9722 | -3550 | -400 | -2905.0278 | 72.63% | 48.96% | 95% | 0% | 2313 | -400
[5 empty] | 2019-09-12 | 23 | 6106.5 | 1878 | -419 | 1 | 0 | 2297 | 1477.5763 | 1477.5763 | 1477.5763 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -479.405 | 998.1712 | -3550 | -400 | -2951.8288 | 73.8% | 48.96% | 95% | 0% | 2297 | -419
[5 empty] | 2019-09-12 | 24 | 6107 | 1835 | -448 | 1 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -512.5858 | 943.0613 | -3550 | -400 | -3006.9387 | 75.17% | 48.96% | 95% | 0% | 2283 | -448
[5 empty] | 2019-09-12 | 25 | 6107.5 | 1829 | -468 | 1 | 0 | 2297 | 1477.5763 | 1477.5763 | 1477.5763 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -535.4691 | 942.1071 | -3550 | -400 | -3007.8929 | 75.2% | 48.95% | 95% | 0% | 2297 | -468
[5 empty] | 2019-09-12 | 26 | 6108 | 1796 | -484 | 1 | 0 | 2280 | 1450.9481 | 1450.9481 | 1450.9481 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -553.7757 | 897.1723 | -3550 | -400 | -3052.8277 | 76.32% | 48.95% | 95% | 0% | 2280 | -484
[5 empty] | 2019-09-12 | 27 | 6108.5 | 1760 | -489 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -559.4966 | 842.8942 | -3550 | -400 | -3107.1058 | 77.68% | 48.95% | 95% | 0% | 2249 | -489
[5 empty] | 2019-09-12 | 28 | 6109 | 1718 | -488 | 1 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -558.3524 | 776.6847 | -3550 | -400 | -3173.3153 | 79.33% | 48.95% | 95% | 0% | 2206 | -488
[5 empty] | 2019-09-12 | 29 | 6109.5 | 1681 | -497 | 1 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 946.5787 | 780 | 200 | 1926.5787 | 48.16% | 95% | 0% | -568.6499 | 722.529 | -3550 | -400 | -3227.471 | 80.69% | 48.95% | 95% | 0% | 2178 | -497
[5 empty] | 2019-09-12 | 30 | 6110 | 1685 | -484 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 945.0124 | 780 | 200 | 1925.0124 | 48.13% | 95% | 0% | -553.7757 | 723.3059 | -3550 | -400 | -3226.6941 | 80.67% | 48.95% | 95% | 0% | 2169 | -484
[5 empty] | 2019-09-12 | 31 | 6110.5 | 1699 | -462 | 1 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 945.0124 | 780 | 200 | 1925.0124 | 48.13% | 95% | 0% | -528.6041 | 735.9466 | -3550 | -400 | -3214.0534 | 80.35% | 48.95% | 95% | 0% | 2161 | -462
[5 empty] | 2019-09-12 | 32 | 6111 | 1780 | -423 | 1 | 0 | 2203 | 1330.338 | 1330.338 | 1330.338 | 945.0124 | 780 | 200 | 1925.0124 | 48.13% | 95% | 0% | -483.9817 | 846.3563 | -3550 | -400 | -3103.6437 | 77.59% | 48.95% | 95% | 0% | 2203 | -423
[5 empty] | 2019-09-12 | 33 | 6111.5 | 1913 | -373 | 1 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 945.0124 | 780 | 200 | 1925.0124 | 48.13% | 95% | 0% | -426.7735 | 1033.5728 | -3550 | -400 | -2916.4272 | 72.91% | 48.93% | 95% | 0% | 2286 | -373
[5 empty] | 2019-09-12 | 34 | 6112 | 2025 | -345 | 1 | 0 | 2370 | 1591.9209 | 1591.9209 | 1591.9209 | 945.0124 | 780 | 200 | 1925.0124 | 48.13% | 95% | 0% | -394.7368 | 1197.184 | -3550 | -400 | -2752.816 | 68.82% | 48.93% | 95% | 0% | 2370 | -345
[5 empty] | 2019-09-12 | 35 | 6112.5 | 2155 | -283 | 1 | 0 | 2438 | 1698.4336 | 1698.4336 | 1698.4336 | 945.0124 | 780 | 200 | 1925.0124 | 48.13% | 95% | 0% | -323.7986 | 1374.635 | -3550 | -400 | -2575.365 | 64.38% | 48.93% | 95% | 0% | 2438 | -283
[5 empty] | 2019-09-12 | 36 | 6113 | 2254 | -223 | 1 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 945.0124 | 780 | 200 | 1925.0124 | 48.13% | 95% | 0% | -255.1487 | 1504.3731 | -3550 | -400 | -2445.6269 | 61.14% | 48.9% | 95% | 0% | 2477 | -223
[5 empty] | 2019-09-12 | 37 | 6113.5 | 2328 | -177 | 1 | 0 | 2505 | 1803.38 | 1803.38 | 1803.38 | 945.0124 | 780 | 200 | 1925.0124 | 48.13% | 95% | 0% | -202.5172 | 1600.8629 | -3550 | -400 | -2349.1371 | 58.73% | 48.89% | 95% | 0% | 2505 | -177
[5 empty] | 2019-09-12 | 38 | 6114 | 2362 | -155 | 1 | 0 | 2517 | 1822.1764 | 1822.1764 | 1822.1764 | 945.0124 | 780 | 200 | 1925.0124 | 48.13% | 95% | 0% | -177.3455 | 1644.8309 | -3550 | -400 | -2305.1691 | 57.63% | 48.89% | 95% | 0% | 2517 | -155
[5 empty] | 2019-09-12 | 39 | 6114.5 | 2415 | -142 | 1 | 0 | 2557 | 1884.831 | 1884.831 | 1884.831 | 945.0124 | 780 | 200 | 1925.0124 | 48.13% | 95% | 0% | -162.4714 | 1722.3596 | -3550 | -400 | -2227.6404 | 55.69% | 48.89% | 95% | 0% | 2557 | -142
[5 empty] | 2019-09-12 | 40 | 6115 | 2453 | -138 | 1 | 0 | 2591 | 1938.0874 | 1938.0874 | 1938.0874 | 943.446 | 780 | 200 | 1923.446 | 48.09% | 95% | 0% | -157.8947 | 1780.1926 | -3550 | -400 | -2169.8074 | 54.25% | 48.88% | 95% | 0% | 2591 | -138
[5 empty] | 2019-09-12 | 41 | 6115.5 | 2424 | -134 | 1 | 0 | 2558 | 1886.3974 | 1886.3974 | 1886.3974 | 943.446 | 780 | 200 | 1923.446 | 48.09% | 95% | 0% | -153.3181 | 1733.0793 | -3550 | -400 | -2216.9207 | 55.42% | 48.88% | 95% | 0% | 2558 | -134
[5 empty] | 2019-09-12 | 42 | 6116 | 2350 | -130 | 0 | 0 | 2480 | 1764.2209 | 1764.2209 | 1764.2209 | 943.446 | 780 | 200 | 1923.446 | 48.09% | 95% | 0% | -148.7414 | 1615.4795 | -2750 | -200 | -1334.5205 | 33.36% | 48.87% | 95% | 0% | 2480 | -130
[5 empty] | 2019-09-12 | 43 | 6116.5 | 2265 | -126 | 0 | 0 | 2391 | 1624.8145 | 1624.8145 | 1624.8145 | 943.446 | 780 | 200 | 1923.446 | 48.09% | 95% | 0% | -144.1648 | 1480.6497 | -2750 | -200 | -1469.3503 | 36.73% | 48.87% | 95% | 0% | 2391 | -126
[5 empty] | 2019-09-12 | 44 | 6117 | 2152 | -122 | 0 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 943.446 | 780 | 200 | 1923.446 | 48.09% | 95% | 0% | -139.5881 | 1301.9618 | -2750 | -200 | -1648.0382 | 41.2% | 48.87% | 95% | 0% | 2274 | -122
[5 empty] | 2019-09-12 | 45 | 6117.5 | 2016 | -118 | 0 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 943.446 | 780 | 200 | 1923.446 | 48.09% | 95% | 0% | -135.0114 | 1087.2474 | -2750 | -200 | -1862.7526 | 46.57% | 48.87% | 95% | 0% | 2134 | -118
[5 empty] | 2019-09-12 | 46 | 6118 | 1901 | -115 | 0 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 943.446 | 780 | 200 | 1923.446 | 48.09% | 95% | 0% | -131.5789 | 905.8489 | -2750 | -200 | -2044.1511 | 51.1% | 48.86% | 95% | 0% | 2016 | -115
[5 empty] | 2019-09-12 | 47 | 6118.5 | 1764 | -113 | 0 | 0 | 1877 | 819.7032 | 819.7032 | 819.7032 | 943.446 | 780 | 200 | 1923.446 | 48.09% | 95% | 0% | -129.2906 | 690.4126 | -2750 | -200 | -2259.5874 | 56.49% | 48.86% | 95% | 0% | 1877 | -113
[5 empty] | 2019-09-12 | 48 | 6119 | 1653 | -111 | 0 | 0 | 1764 | 642.704 | 642.704 | 642.704 | 943.446 | 780 | 200 | 1923.446 | 48.09% | 95% | 0% | -127.0023 | 515.7018 | -2750 | -200 | -2434.2982 | 60.86% | 48.85% | 95% | 0% | 1764 | -111
[5 empty] | 2019-09-13 | 1 | 6119.5 | 1562 | -108 | 0 | 0 | 1670 | 495.4658 | 495.4658 | 495.4658 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -123.5698 | 371.896 | -2750 | -200 | -2578.104 | 64.45% | 48.85% | 95% | 0% | 1670 | -108
[5 empty] | 2019-09-13 | 2 | 6120 | 1499 | -105 | 0 | 0 | 1604 | 392.0857 | 392.0857 | 392.0857 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -120.1373 | 271.9484 | -2750 | -200 | -2678.0516 | 66.95% | 48.84% | 95% | 0% | 1604 | -105
[5 empty] | 2019-09-13 | 3 | 6120.5 | 1474 | -104 | 1 | 0 | 1578 | 351.3603 | 351.3603 | 351.3603 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -118.9931 | 232.3671 | -3550 | -400 | -3717.6329 | 92.94% | 48.82% | 95% | 0% | 1578 | -104
[5 empty] | 2019-09-13 | 4 | 6121 | 1476 | -103 | 1 | 0 | 1579 | 352.9266 | 352.9266 | 352.9266 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -117.849 | 235.0777 | -3550 | -400 | -3714.9223 | 92.87% | 48.82% | 95% | 0% | 1579 | -103
[5 empty] | 2019-09-13 | 5 | 6121.5 | 1457 | -101 | 1 | 0 | 1558 | 320.033 | 320.033 | 320.033 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -115.5606 | 204.4723 | -3550 | -400 | -3745.5277 | 93.64% | 48.82% | 95% | 0% | 1558 | -101
[5 empty] | 2019-09-13 | 6 | 6122 | 1432 | -99 | 1 | 0 | 1531 | 277.7411 | 277.7411 | 277.7411 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -113.2723 | 164.4688 | -3550 | -400 | -3785.5312 | 94.64% | 48.81% | 95% | 0% | 1531 | -99
[5 empty] | 2019-09-13 | 7 | 6122.5 | 1417 | -97 | 1 | 0 | 1514 | 251.1129 | 251.1129 | 251.1129 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -110.984 | 140.129 | -3550 | -400 | -3809.871 | 95.25% | 48.81% | 95% | 0% | 1514 | -97
[5 empty] | 2019-09-13 | 8 | 6123 | 1425 | -94 | 1 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -107.5515 | 151.3933 | -3550 | -400 | -3798.6067 | 94.97% | 48.8% | 95% | 0% | 1519 | -94
[5 empty] | 2019-09-13 | 9 | 6123.5 | 1432 | -90 | 1 | 0 | 1522 | 263.6439 | 263.6439 | 263.6439 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -102.9748 | 160.669 | -3550 | -400 | -3789.331 | 94.73% | 48.8% | 95% | 0% | 1522 | -90
[5 empty] | 2019-09-13 | 10 | 6124 | 1449 | -87 | 1 | 0 | 1536 | 285.573 | 285.573 | 285.573 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -99.5423 | 186.0306 | -3550 | -400 | -3763.9694 | 94.1% | 48.8% | 95% | 0% | 1536 | -87
[5 empty] | 2019-09-13 | 11 | 6124.5 | 1521 | -85 | 1 | 0 | 1606 | 395.2185 | 395.2185 | 395.2185 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -97.254 | 297.9645 | -3550 | -400 | -3652.0355 | 91.3% | 48.8% | 95% | 0% | 1606 | -85
[5 empty] | 2019-09-13 | 12 | 6125 | 1602 | -84 | 1 | 0 | 1686 | 520.5276 | 520.5276 | 520.5276 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -96.1098 | 424.4178 | -3550 | -400 | -3525.5822 | 88.14% | 48.79% | 95% | 0% | 1686 | -84
[5 empty] | 2019-09-13 | 13 | 6125.5 | 1803 | -81 | 1 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -92.6773 | 737.9904 | -3550 | -400 | -3212.0096 | 80.3% | 48.78% | 95% | 0% | 1884 | -81
[5 empty] | 2019-09-13 | 14 | 6126 | 1979 | -82 | 1 | 0 | 2061 | 1107.9143 | 1107.9143 | 1107.9143 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -93.8215 | 1014.0928 | -3550 | -400 | -2935.9072 | 73.4% | 48.77% | 95% | 0% | 2061 | -82
[5 empty] | 2019-09-13 | 15 | 6126.5 | 2188 | -114 | 1 | 0 | 2302 | 1485.4081 | 1485.4081 | 1485.4081 | 941.8796 | 780 | 200 | 1921.8796 | 48.05% | 95% | 0% | -130.4348 | 1354.9733 | -3550 | -400 | -2595.0267 | 64.88% | 48.73% | 95% | 0% | 2302 | -114
[5 empty] | 2019-09-13 | 16 | 6127 | 2225 | -175 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -200.2288 | 1438.683 | -3550 | -400 | -2511.317 | 62.78% | 48.72% | 95% | 0% | 2400 | -175
[5 empty] | 2019-09-13 | 17 | 6127.5 | 2180 | -242 | 1 | 0 | 2422 | 1673.3718 | 1673.3718 | 1673.3718 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -276.8879 | 1396.4839 | -3550 | -400 | -2553.5161 | 63.84% | 48.71% | 95% | 0% | 2422 | -242
[5 empty] | 2019-09-13 | 18 | 6128 | 2059 | -316 | 1 | 0 | 2375 | 1599.7527 | 1599.7527 | 1599.7527 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -361.5561 | 1238.1966 | -3550 | -400 | -2711.8034 | 67.8% | 48.71% | 95% | 0% | 2375 | -316
[5 empty] | 2019-09-13 | 19 | 6128.5 | 1951 | -380 | 1 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -434.7826 | 1096.05 | -3550 | -400 | -2853.95 | 71.35% | 48.7% | 95% | 0% | 2331 | -380
[5 empty] | 2019-09-13 | 20 | 6129 | 1827 | -454 | 1 | 0 | 2281 | 1452.5144 | 1452.5144 | 1452.5144 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -519.4508 | 933.0636 | -3550 | -400 | -3016.9364 | 75.42% | 48.7% | 95% | 0% | 2281 | -454
[5 empty] | 2019-09-13 | 21 | 6129.5 | 1695 | -530 | 1 | 0 | 2225 | 1364.798 | 1364.798 | 1364.798 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -606.4073 | 758.3907 | -3550 | -400 | -3191.6093 | 79.79% | 48.69% | 95% | 0% | 2225 | -530
[5 empty] | 2019-09-13 | 22 | 6130 | 1585 | -583 | 1 | 0 | 2168 | 1275.5153 | 1275.5153 | 1275.5153 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -667.0481 | 608.4672 | -3550 | -400 | -3341.5328 | 83.54% | 48.69% | 95% | 0% | 2168 | -583
[5 empty] | 2019-09-13 | 23 | 6130.5 | 1508 | -617 | 1 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -705.9497 | 502.2119 | -3550 | -400 | -3447.7881 | 86.19% | 48.68% | 95% | 0% | 2125 | -617
[5 empty] | 2019-09-13 | 24 | 6131 | 1442 | -646 | 1 | 0 | 2088 | 1150.2061 | 1150.2061 | 1150.2061 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -739.1304 | 411.0757 | -3550 | -400 | -3538.9243 | 88.47% | 48.68% | 95% | 0% | 2088 | -646
[5 empty] | 2019-09-13 | 25 | 6131.5 | 1410 | -667 | 1 | 0 | 2077 | 1132.9761 | 1132.9761 | 1132.9761 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -763.1579 | 369.8182 | -3550 | -400 | -3580.1818 | 89.5% | 48.68% | 95% | 0% | 2077 | -667
[5 empty] | 2019-09-13 | 26 | 6132 | 1365 | -682 | 1 | 0 | 2047 | 1085.9852 | 1085.9852 | 1085.9852 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -780.3204 | 305.6648 | -3550 | -400 | -3644.3352 | 91.11% | 48.68% | 95% | 0% | 2047 | -682
[5 empty] | 2019-09-13 | 27 | 6132.5 | 1298 | -711 | 1 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -813.5011 | 212.9622 | -3550 | -400 | -3737.0378 | 93.43% | 48.68% | 95% | 0% | 2009 | -711
[5 empty] | 2019-09-13 | 28 | 6133 | 1279 | -697 | 1 | 0 | 1976 | 974.7733 | 974.7733 | 974.7733 | 940.3133 | 780 | 200 | 1920.3133 | 48.01% | 95% | 0% | -797.4828 | 177.2905 | -3550 | -400 | -3772.7095 | 94.32% | 48.68% | 95% | 0% | 1976 | -697
[5 empty] | 2019-09-13 | 29 | 6133.5 | 1276 | -690 | 1 | 0 | 1966 | 959.1096 | 959.1096 | 959.1096 | 938.7469 | 780 | 200 | 1918.7469 | 47.97% | 95% | 0% | -789.4737 | 169.636 | -3550 | -400 | -3780.364 | 94.51% | 48.67% | 95% | 0% | 1966 | -690
[5 empty] | 2019-09-13 | 30 | 6134 | 1304 | -654 | 1 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 938.7469 | 780 | 200 | 1918.7469 | 47.97% | 95% | 0% | -748.2838 | 198.295 | -3550 | -400 | -3751.705 | 93.79% | 48.67% | 95% | 0% | 1958 | -654
[5 empty] | 2019-09-13 | 31 | 6134.5 | 1373 | -590 | 1 | 0 | 1963 | 954.4106 | 954.4106 | 954.4106 | 938.7469 | 780 | 200 | 1918.7469 | 47.97% | 95% | 0% | -675.0572 | 279.3533 | -3550 | -400 | -3670.6467 | 91.77% | 48.67% | 95% | 0% | 1963 | -590
[5 empty] | 2019-09-13 | 32 | 6135 | 1487 | -526 | 1 | 0 | 2013 | 1032.7288 | 1032.7288 | 1032.7288 | 938.7469 | 780 | 200 | 1918.7469 | 47.97% | 95% | 0% | -601.8307 | 430.8981 | -3550 | -400 | -3519.1019 | 87.98% | 48.66% | 95% | 0% | 2013 | -526
[5 empty] | 2019-09-13 | 33 | 6135.5 | 1640 | -454 | 1 | 0 | 2094 | 1159.6043 | 1159.6043 | 1159.6043 | 938.7469 | 780 | 200 | 1918.7469 | 47.97% | 95% | 0% | -519.4508 | 640.1535 | -3550 | -400 | -3309.8465 | 82.75% | 48.66% | 95% | 0% | 2094 | -454
[5 empty] | 2019-09-13 | 34 | 6136 | 1803 | -383 | 1 | 0 | 2186 | 1303.7098 | 1303.7098 | 1303.7098 | 938.7469 | 780 | 200 | 1918.7469 | 47.97% | 95% | 0% | -438.2151 | 865.4947 | -3550 | -400 | -3084.5053 | 77.11% | 48.65% | 95% | 0% | 2186 | -383
[5 empty] | 2019-09-13 | 35 | 6136.5 | 1983 | -311 | 1 | 0 | 2294 | 1472.8772 | 1472.8772 | 1472.8772 | 938.7469 | 780 | 200 | 1918.7469 | 47.97% | 95% | 0% | -355.8352 | 1117.0419 | -3550 | -400 | -2832.9581 | 70.82% | 48.65% | 95% | 0% | 2294 | -311
[5 empty] | 2019-09-13 | 36 | 6137 | 2130 | -228 | 1 | 0 | 2358 | 1573.1245 | 1573.1245 | 1573.1245 | 938.7469 | 780 | 200 | 1918.7469 | 47.97% | 95% | 0% | -260.8696 | 1312.2549 | -3550 | -400 | -2637.7451 | 65.94% | 48.65% | 95% | 0% | 2358 | -228
[5 empty] | 2019-09-13 | 37 | 6137.5 | 2242 | -155 | 1 | 0 | 2397 | 1634.2127 | 1634.2127 | 1634.2127 | 938.7469 | 780 | 200 | 1918.7469 | 47.97% | 95% | 0% | -177.3455 | 1456.8672 | -3550 | -400 | -2493.1328 | 62.33% | 48.65% | 95% | 0% | 2397 | -155
[5 empty] | 2019-09-13 | 38 | 6138 | 2343 | -91 | 1 | 0 | 2434 | 1692.1682 | 1692.1682 | 1692.1682 | 938.7469 | 780 | 200 | 1918.7469 | 47.97% | 95% | 0% | -104.119 | 1588.0492 | -3550 | -400 | -2361.9508 | 59.05% | 48.65% | 95% | 0% | 2434 | -91
[5 empty] | 2019-09-13 | 39 | 6138.5 | 2401 | -57 | 1 | 0 | 2458 | 1729.7609 | 1729.7609 | 1729.7609 | 937.1805 | 780 | 200 | 1917.1805 | 47.93% | 95% | 0% | -65.2174 | 1664.5435 | -3550 | -400 | -2285.4565 | 57.14% | 48.65% | 95% | 0% | 2458 | -57
[5 empty] | 2019-09-13 | 40 | 6139 | 2436 | -53 | 1 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 937.1805 | 780 | 200 | 1917.1805 | 47.93% | 95% | 0% | -60.6407 | 1717.6775 | -3550 | -400 | -2232.3225 | 55.81% | 48.64% | 95% | 0% | 2489 | -53
[5 empty] | 2019-09-13 | 41 | 6139.5 | 2411 | -53 | 1 | 0 | 2464 | 1739.1591 | 1739.1591 | 1739.1591 | 937.1805 | 780 | 200 | 1917.1805 | 47.93% | 95% | 0% | -60.6407 | 1678.5184 | -3550 | -400 | -2271.4816 | 56.79% | 48.64% | 95% | 0% | 2464 | -53
[5 empty] | 2019-09-13 | 42 | 6140 | 2357 | -54 | 0 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 937.1805 | 780 | 200 | 1917.1805 | 47.93% | 95% | 0% | -61.7849 | 1594.3569 | -2750 | -200 | -1355.6431 | 33.89% | 48.64% | 95% | 0% | 2411 | -54
[5 empty] | 2019-09-13 | 43 | 6140.5 | 2285 | -54 | 0 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 937.1805 | 780 | 200 | 1917.1805 | 47.93% | 95% | 0% | -61.7849 | 1481.5787 | -2750 | -200 | -1468.4213 | 36.71% | 48.64% | 95% | 0% | 2339 | -54
[5 empty] | 2019-09-13 | 44 | 6141 | 2187 | -55 | 0 | 0 | 2242 | 1391.4262 | 1391.4262 | 1391.4262 | 937.1805 | 780 | 200 | 1917.1805 | 47.93% | 95% | 0% | -62.9291 | 1328.4972 | -2750 | -200 | -1621.5028 | 40.54% | 48.64% | 95% | 0% | 2242 | -55
[5 empty] | 2019-09-13 | 45 | 6141.5 | 2073 | -55 | 0 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 937.1805 | 780 | 200 | 1917.1805 | 47.93% | 95% | 0% | -62.9291 | 1149.9316 | -2750 | -200 | -1800.0684 | 45% | 48.64% | 95% | 0% | 2128 | -55
[5 empty] | 2019-09-13 | 46 | 6142 | 1954 | -55 | 0 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 937.1805 | 780 | 200 | 1917.1805 | 47.93% | 95% | 0% | -62.9291 | 963.5343 | -2750 | -200 | -1986.4657 | 49.66% | 48.64% | 95% | 0% | 2009 | -55
[5 empty] | 2019-09-13 | 47 | 6142.5 | 1827 | -55 | 0 | 0 | 1882 | 827.535 | 827.535 | 827.535 | 935.6142 | 780 | 200 | 1915.6142 | 47.89% | 95% | 0% | -62.9291 | 764.606 | -2750 | -200 | -2185.394 | 54.63% | 48.63% | 95% | 0% | 1882 | -55
[5 empty] | 2019-09-13 | 48 | 6143 | 1724 | -54 | 0 | 0 | 1778 | 664.6331 | 664.6331 | 664.6331 | 935.6142 | 780 | 200 | 1915.6142 | 47.89% | 95% | 0% | -61.7849 | 602.8482 | -2750 | -200 | -2347.1518 | 58.68% | 48.63% | 95% | 0% | 1778 | -54
[5 empty] | 2019-09-14 | 1 | 6143.5 | 1644 | -55 | 0 | 0 | 1699 | 540.8904 | 540.8904 | 540.8904 | 935.6142 | 780 | 200 | 1915.6142 | 47.89% | 95% | 0% | -62.9291 | 477.9613 | -2750 | -200 | -2472.0387 | 61.8% | 48.62% | 95% | 0% | 1699 | -55
[5 empty] | 2019-09-14 | 2 | 6144 | 1585 | -56 | 0 | 0 | 1641 | 450.0412 | 450.0412 | 450.0412 | 935.6142 | 780 | 200 | 1915.6142 | 47.89% | 95% | 0% | -64.0732 | 385.968 | -2750 | -200 | -2564.032 | 64.1% | 48.62% | 95% | 0% | 1641 | -56
[5 empty] | 2019-09-14 | 3 | 6144.5 | 1537 | -57 | 0 | 0 | 1594 | 376.4221 | 376.4221 | 376.4221 | 935.6142 | 780 | 200 | 1915.6142 | 47.89% | 95% | 0% | -65.2174 | 311.2047 | -2750 | -200 | -2638.7953 | 65.97% | 48.61% | 95% | 0% | 1594 | -57
[5 empty] | 2019-09-14 | 4 | 6145 | 1506 | -57 | 0 | 0 | 1563 | 327.8648 | 327.8648 | 327.8648 | 935.6142 | 780 | 200 | 1915.6142 | 47.89% | 95% | 0% | -65.2174 | 262.6474 | -2750 | -200 | -2687.3526 | 67.18% | 48.61% | 95% | 0% | 1563 | -57
[5 empty] | 2019-09-14 | 5 | 6145.5 | 1480 | -59 | 0 | 0 | 1539 | 290.2721 | 290.2721 | 290.2721 | 935.6142 | 780 | 200 | 1915.6142 | 47.89% | 95% | 0% | -67.5057 | 222.7663 | -2750 | -200 | -2727.2337 | 68.18% | 48.61% | 95% | 0% | 1539 | -59
[5 empty] | 2019-09-14 | 6 | 6146 | 1447 | -61 | 0 | 0 | 1508 | 241.7148 | 241.7148 | 241.7148 | 935.6142 | 780 | 200 | 1915.6142 | 47.89% | 95% | 0% | -69.7941 | 171.9207 | -2750 | -200 | -2778.0793 | 69.45% | 48.61% | 95% | 0% | 1508 | -61
[5 empty] | 2019-09-14 | 7 | 6146.5 | 1430 | -63 | 0 | 0 | 1493 | 218.2193 | 218.2193 | 218.2193 | 935.6142 | 780 | 200 | 1915.6142 | 47.89% | 95% | 0% | -72.0824 | 146.1369 | -2750 | -200 | -2803.8631 | 70.1% | 48.6% | 95% | 0% | 1493 | -63
[5 empty] | 2019-09-14 | 8 | 6147 | 1408 | -65 | 0 | 0 | 1473 | 186.892 | 186.892 | 186.892 | 934.0478 | 780 | 200 | 1914.0478 | 47.85% | 95% | 0% | -74.3707 | 112.5213 | -2750 | -200 | -2837.4787 | 70.94% | 48.6% | 95% | 0% | 1473 | -65
[5 empty] | 2019-09-14 | 9 | 6147.5 | 1402 | -68 | 0 | 0 | 1470 | 182.1929 | 182.1929 | 182.1929 | 934.0478 | 780 | 200 | 1914.0478 | 47.85% | 95% | 0% | -77.8032 | 104.3897 | -2750 | -200 | -2845.6103 | 71.14% | 48.59% | 95% | 0% | 1470 | -68
[5 empty] | 2019-09-14 | 10 | 6148 | 1393 | -71 | 1 | 0 | 1464 | 172.7947 | 172.7947 | 172.7947 | 934.0478 | 780 | 200 | 1914.0478 | 47.85% | 95% | 0% | -81.2357 | 91.559 | -3550 | -400 | -3858.441 | 96.46% | 48.59% | 95% | 0% | 1464 | -71
[5 empty] | 2019-09-14 | 11 | 6148.5 | 1415 | -75 | 1 | 0 | 1490 | 213.5202 | 213.5202 | 213.5202 | 934.0478 | 780 | 200 | 1914.0478 | 47.85% | 95% | 0% | -85.8124 | 127.7078 | -3550 | -400 | -3822.2922 | 95.56% | 48.59% | 95% | 0% | 1490 | -75
[5 empty] | 2019-09-14 | 12 | 6149 | 1446 | -79 | 1 | 0 | 1525 | 268.343 | 268.343 | 268.343 | 934.0478 | 780 | 200 | 1914.0478 | 47.85% | 95% | 0% | -90.389 | 177.9539 | -3550 | -400 | -3772.0461 | 94.3% | 48.58% | 95% | 0% | 1525 | -79
[5 empty] | 2019-09-14 | 13 | 6149.5 | 1522 | -83 | 1 | 0 | 1605 | 393.6521 | 393.6521 | 393.6521 | 934.0478 | 780 | 200 | 1914.0478 | 47.85% | 95% | 0% | -94.9657 | 298.6864 | -3550 | -400 | -3651.3136 | 91.28% | 48.58% | 95% | 0% | 1605 | -83
[5 empty] | 2019-09-14 | 14 | 6150 | 1568 | -90 | 1 | 0 | 1658 | 476.6694 | 476.6694 | 476.6694 | 934.0478 | 780 | 200 | 1914.0478 | 47.85% | 95% | 0% | -102.9748 | 373.6946 | -3550 | -400 | -3576.3054 | 89.41% | 48.57% | 95% | 0% | 1658 | -90
[5 empty] | 2019-09-14 | 15 | 6150.5 | 1657 | -118 | 1 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 934.0478 | 780 | 200 | 1914.0478 | 47.85% | 95% | 0% | -135.0114 | 524.9226 | -3550 | -400 | -3425.0774 | 85.63% | 48.56% | 95% | 0% | 1775 | -118
[5 empty] | 2019-09-14 | 16 | 6151 | 1654 | -175 | 1 | 0 | 1829 | 744.5177 | 744.5177 | 744.5177 | 934.0478 | 780 | 200 | 1914.0478 | 47.85% | 95% | 0% | -200.2288 | 544.2889 | -3550 | -400 | -3405.7111 | 85.14% | 48.56% | 95% | 0% | 1829 | -175
[5 empty] | 2019-09-14 | 17 | 6151.5 | 1627 | -251 | 1 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 934.0478 | 780 | 200 | 1914.0478 | 47.85% | 95% | 0% | -287.1854 | 534.0842 | -3550 | -400 | -3415.9158 | 85.4% | 48.55% | 95% | 0% | 1878 | -251
[5 empty] | 2019-09-14 | 18 | 6152 | 1557 | -342 | 1 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 932.4815 | 780 | 200 | 1912.4815 | 47.81% | 95% | 0% | -391.3043 | 462.8589 | -3550 | -400 | -3487.1411 | 87.18% | 48.55% | 95% | 0% | 1899 | -342
[5 empty] | 2019-09-14 | 19 | 6152.5 | 1470 | -425 | 1 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 932.4815 | 780 | 200 | 1912.4815 | 47.81% | 95% | 0% | -486.27 | 361.6278 | -3550 | -400 | -3588.3722 | 89.71% | 48.54% | 95% | 0% | 1895 | -425
[5 empty] | 2019-09-14 | 20 | 6153 | 1344 | -505 | 1 | 0 | 1849 | 775.845 | 775.845 | 775.845 | 932.4815 | 780 | 200 | 1912.4815 | 47.81% | 95% | 0% | -577.8032 | 198.0418 | -3550 | -400 | -3751.9582 | 93.8% | 48.54% | 95% | 0% | 1849 | -505
[5 empty] | 2019-09-14 | 21 | 6153.5 | 1247 | -573 | 1 | 0 | 1820 | 730.4204 | 730.4204 | 730.4204 | 932.4815 | 780 | 200 | 1912.4815 | 47.81% | 95% | 0% | -655.6064 | 74.814 | -3550 | -400 | -3875.186 | 96.88% | 48.54% | 95% | 0% | 1820 | -573
[5 empty] | 2019-09-14 | 22 | 6154 | 1167 | -616 | 1 | 0 | 1783 | 672.465 | 672.465 | 672.465 | 932.4815 | 780 | 200 | 1912.4815 | 47.81% | 95% | 0% | -704.8055 | -32.3405 | -3550 | -400 | -3982.3405 | 99.56% | 48.53% | 95% | 0% | 1783 | -616
[5 empty] | 2019-09-14 | 23 | 6154.5 | 1049 | -677 | 1 | 0 | 1726 | 583.1822 | 583.1822 | 583.1822 | 932.4815 | 780 | 200 | 1912.4815 | 47.81% | 95% | 0% | -774.5995 | -191.4173 | -3550 | -400 | -4141.4173 | 103.5% | 48.53% | 95% | 0% | 1726 | -677
[5 empty] | 2019-09-14 | 24 | 6155 | 953 | -724 | 1 | 0 | 1677 | 506.4303 | 506.4303 | 506.4303 | 932.4815 | 780 | 200 | 1912.4815 | 47.81% | 95% | 0% | -828.3753 | -321.9449 | -3550 | -400 | -4271.9449 | 106.8% | 48.53% | 95% | 0% | 1677 | -724
[5 empty] | 2019-09-14 | 25 | 6155.5 | 905 | -749 | 1 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 932.4815 | 780 | 200 | 1912.4815 | 47.81% | 95% | 0% | -856.9794 | -386.5754 | -3550 | -400 | -4336.5754 | 108.4% | 48.53% | 95% | 0% | 1654 | -749
[5 empty] | 2019-09-14 | 26 | 6156 | 898 | -739 | 1 | 0 | 1637 | 443.7758 | 443.7758 | 443.7758 | 932.4815 | 780 | 200 | 1912.4815 | 47.81% | 95% | 0% | -845.5378 | -401.762 | -3550 | -400 | -4351.762 | 108.8% | 48.53% | 95% | 0% | 1637 | -739
[5 empty] | 2019-09-14 | 27 | 6156.5 | 866 | -736 | 1 | 0 | 1602 | 388.953 | 388.953 | 388.953 | 932.4815 | 780 | 200 | 1912.4815 | 47.81% | 95% | 0% | -842.1053 | -453.1523 | -3550 | -400 | -4403.1523 | 110.1% | 48.52% | 95% | 0% | 1602 | -736
[5 empty] | 2019-09-14 | 28 | 6157 | 884 | -696 | 1 | 0 | 1580 | 354.493 | 354.493 | 354.493 | 932.4815 | 780 | 200 | 1912.4815 | 47.81% | 95% | 0% | -796.3387 | -441.8457 | -3550 | -400 | -4391.8457 | 109.8% | 48.52% | 95% | 0% | 1580 | -696
[5 empty] | 2019-09-14 | 29 | 6157.5 | 888 | -670 | 1 | 0 | 1558 | 320.033 | 320.033 | 320.033 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -766.5904 | -446.5574 | -3550 | -400 | -4396.5574 | 109.9% | 48.5% | 95% | 0% | 1558 | -670
[5 empty] | 2019-09-14 | 30 | 6158 | 910 | -658 | 1 | 0 | 1568 | 335.6966 | 335.6966 | 335.6966 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -752.8604 | -417.1638 | -3550 | -400 | -4367.1638 | 109.2% | 48.5% | 95% | 0% | 1568 | -658
[5 empty] | 2019-09-14 | 31 | 6158.5 | 983 | -606 | 1 | 0 | 1589 | 368.5903 | 368.5903 | 368.5903 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -693.3638 | -324.7736 | -3550 | -400 | -4274.7736 | 106.9% | 48.5% | 95% | 0% | 1589 | -606
[5 empty] | 2019-09-14 | 32 | 6159 | 1065 | -550 | 1 | 0 | 1615 | 409.3157 | 409.3157 | 409.3157 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -629.2906 | -219.9749 | -3550 | -400 | -4169.9749 | 104.2% | 48.49% | 95% | 0% | 1615 | -550
[5 empty] | 2019-09-14 | 33 | 6159.5 | 1208 | -486 | 1 | 0 | 1694 | 533.0585 | 533.0585 | 533.0585 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -556.0641 | -23.0055 | -3550 | -400 | -3973.0055 | 99.33% | 48.49% | 95% | 0% | 1694 | -486
[5 empty] | 2019-09-14 | 34 | 6160 | 1383 | -412 | 1 | 0 | 1795 | 691.2613 | 691.2613 | 691.2613 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -471.3959 | 219.8655 | -3550 | -400 | -3730.1345 | 93.25% | 48.49% | 95% | 0% | 1795 | -412
[5 empty] | 2019-09-14 | 35 | 6160.5 | 1609 | -324 | 1 | 0 | 1933 | 907.4196 | 907.4196 | 907.4196 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -370.7094 | 536.7102 | -3550 | -400 | -3413.2898 | 85.33% | 48.49% | 95% | 0% | 1933 | -324
[5 empty] | 2019-09-14 | 36 | 6161 | 1734 | -275 | 1 | 0 | 2009 | 1026.4633 | 1026.4633 | 1026.4633 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -314.6453 | 711.818 | -3550 | -400 | -3238.182 | 80.95% | 48.48% | 95% | 0% | 2009 | -275
[5 empty] | 2019-09-14 | 37 | 6161.5 | 1837 | -229 | 1 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -262.0137 | 853.7324 | -3550 | -400 | -3096.2676 | 77.41% | 48.48% | 95% | 0% | 2066 | -229
[5 empty] | 2019-09-14 | 38 | 6162 | 1935 | -176 | 1 | 0 | 2111 | 1186.2325 | 1186.2325 | 1186.2325 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -201.373 | 984.8595 | -3550 | -400 | -2965.1405 | 74.13% | 48.48% | 95% | 0% | 2111 | -176
[5 empty] | 2019-09-14 | 39 | 6162.5 | 1982 | -150 | 1 | 0 | 2132 | 1219.1261 | 1219.1261 | 1219.1261 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -171.6247 | 1047.5014 | -3550 | -400 | -2902.4986 | 72.56% | 48.47% | 95% | 0% | 2132 | -150
[5 empty] | 2019-09-14 | 40 | 6163 | 2039 | -148 | 1 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -169.3364 | 1135.9398 | -3550 | -400 | -2814.0602 | 70.35% | 48.46% | 95% | 0% | 2187 | -148
[5 empty] | 2019-09-14 | 41 | 6163.5 | 2042 | -147 | 1 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -168.1922 | 1140.2167 | -3550 | -400 | -2809.7833 | 70.24% | 48.45% | 95% | 0% | 2189 | -147
[5 empty] | 2019-09-14 | 42 | 6164 | 1979 | -147 | 0 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -168.1922 | 1041.5357 | -2750 | -200 | -1908.4643 | 47.71% | 48.43% | 95% | 0% | 2126 | -147
[5 empty] | 2019-09-14 | 43 | 6164.5 | 1895 | -148 | 0 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -169.3364 | 910.3833 | -2750 | -200 | -2039.6167 | 50.99% | 48.42% | 95% | 0% | 2043 | -148
[5 empty] | 2019-09-14 | 44 | 6165 | 1810 | -148 | 0 | 0 | 1958 | 946.5787 | 946.5787 | 946.5787 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -169.3364 | 777.2423 | -2750 | -200 | -2172.7577 | 54.32% | 48.42% | 95% | 0% | 1958 | -148
[5 empty] | 2019-09-14 | 45 | 6165.5 | 1716 | -146 | 0 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -167.0481 | 629.1597 | -2750 | -200 | -2320.8403 | 58.02% | 48.42% | 95% | 0% | 1862 | -146
[5 empty] | 2019-09-14 | 46 | 6166 | 1638 | -145 | 1 | 0 | 1783 | 672.465 | 672.465 | 672.465 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -165.9039 | 506.5611 | -3550 | -400 | -3443.4389 | 86.09% | 48.42% | 95% | 0% | 1783 | -145
[5 empty] | 2019-09-14 | 47 | 6166.5 | 1519 | -144 | 1 | 0 | 1663 | 484.5012 | 484.5012 | 484.5012 | 930.9151 | 780 | 200 | 1910.9151 | 47.77% | 95% | 0% | -164.7597 | 319.7415 | -3550 | -400 | -3630.2585 | 90.76% | 48.41% | 95% | 0% | 1663 | -144
[5 empty] | 2019-09-14 | 48 | 6167 | 1447 | -143 | 1 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 929.3487 | 780 | 200 | 1909.3487 | 47.73% | 95% | 0% | -163.6156 | 206.5411 | -3550 | -400 | -3743.4589 | 93.59% | 48.41% | 95% | 0% | 1590 | -143
[5 empty] | 2019-09-15 | 1 | 6167.5 | 1356 | -142 | 1 | 0 | 1498 | 226.0511 | 226.0511 | 226.0511 | 929.3487 | 780 | 200 | 1909.3487 | 47.73% | 95% | 0% | -162.4714 | 63.5797 | -3550 | -400 | -3886.4203 | 97.16% | 48.4% | 95% | 0% | 1498 | -142
[5 empty] | 2019-09-15 | 2 | 6168 | 1303 | -140 | 1 | 0 | 1443 | 139.9011 | 139.9011 | 139.9011 | 929.3487 | 780 | 200 | 1909.3487 | 47.73% | 95% | 0% | -160.1831 | -20.282 | -3550 | -400 | -3970.282 | 99.26% | 48.39% | 95% | 0% | 1443 | -140
[5 empty] | 2019-09-15 | 3 | 6168.5 | 1272 | -139 | 1 | 0 | 1411 | 89.7774 | 89.7774 | 89.7774 | 929.3487 | 780 | 200 | 1909.3487 | 47.73% | 95% | 0% | -159.0389 | -69.2615 | -3550 | -400 | -4019.2615 | 100.5% | 48.39% | 95% | 0% | 1411 | -139
[5 empty] | 2019-09-15 | 4 | 6169 | 1257 | -137 | 1 | 0 | 1394 | 63.1492 | 63.1492 | 63.1492 | 929.3487 | 780 | 200 | 1909.3487 | 47.73% | 95% | 0% | -156.7506 | -93.6014 | -3550 | -400 | -4043.6014 | 101.1% | 48.38% | 95% | 0% | 1394 | -137
[5 empty] | 2019-09-15 | 5 | 6169.5 | 1220 | -135 | 1 | 0 | 1355 | 2.061 | 2.061 | 2.061 | 929.3487 | 780 | 200 | 1909.3487 | 47.73% | 95% | 0% | -154.4622 | -152.4012 | -3550 | -400 | -4102.4012 | 102.6% | 48.38% | 95% | 0% | 1355 | -135
[5 empty] | 2019-09-15 | 6 | 6170 | 1196 | -133 | 1 | 0 | 1329 | -38.6645 | -38.6645 | -38.6645 | 929.3487 | 780 | 200 | 1909.3487 | 47.73% | 95% | 0% | -152.1739 | -190.8384 | -3550 | -400 | -4140.8384 | 103.5% | 48.38% | 95% | 0% | 1329 | -133
[5 empty] | 2019-09-15 | 7 | 6170.5 | 1180 | -130 | 1 | 0 | 1310 | -68.4254 | -68.4254 | -68.4254 | 929.3487 | 780 | 200 | 1909.3487 | 47.73% | 95% | 0% | -148.7414 | -217.1668 | -3550 | -400 | -4167.1668 | 104.2% | 48.38% | 95% | 0% | 1310 | -130
[5 empty] | 2019-09-15 | 8 | 6171 | 1175 | -128 | 1 | 0 | 1303 | -79.3899 | -79.3899 | -79.3899 | 929.3487 | 780 | 200 | 1909.3487 | 47.73% | 95% | 0% | -146.4531 | -225.843 | -3550 | -400 | -4175.843 | 104.4% | 48.38% | 95% | 0% | 1303 | -128
[5 empty] | 2019-09-15 | 9 | 6171.5 | 1172 | -124 | 1 | 0 | 1296 | -90.3545 | -90.3545 | -90.3545 | 929.3487 | 780 | 200 | 1909.3487 | 47.73% | 95% | 0% | -141.8764 | -232.2309 | -3550 | -400 | -4182.2309 | 104.6% | 48.38% | 95% | 0% | 1296 | -124
[5 empty] | 2019-09-15 | 10 | 6172 | 1176 | -121 | 1 | 0 | 1297 | -88.7881 | -88.7881 | -88.7881 | 929.3487 | 780 | 200 | 1909.3487 | 47.73% | 95% | 0% | -138.4439 | -227.2321 | -3550 | -400 | -4177.2321 | 104.4% | 48.38% | 95% | 0% | 1297 | -121
[5 empty] | 2019-09-15 | 11 | 6172.5 | 1193 | -118 | 1 | 0 | 1311 | -66.859 | -66.859 | -66.859 | 929.3487 | 780 | 200 | 1909.3487 | 47.73% | 95% | 0% | -135.0114 | -201.8705 | -3550 | -400 | -4151.8705 | 103.8% | 48.37% | 95% | 0% | 1311 | -118
[5 empty] | 2019-09-15 | 12 | 6173 | 1237 | -115 | 1 | 0 | 1352 | -2.6381 | -2.6381 | -2.6381 | 927.7824 | 780 | 200 | 1907.7824 | 47.69% | 95% | 0% | -131.5789 | -134.217 | -3550 | -400 | -4084.217 | 102.1% | 48.36% | 95% | 0% | 1352 | -115
[5 empty] | 2019-09-15 | 13 | 6173.5 | 1312 | -112 | 1 | 0 | 1424 | 110.1401 | 110.1401 | 110.1401 | 927.7824 | 780 | 200 | 1907.7824 | 47.69% | 95% | 0% | -128.1465 | -18.0063 | -3550 | -400 | -3968.0063 | 99.2% | 48.36% | 95% | 0% | 1424 | -112
[5 empty] | 2019-09-15 | 14 | 6174 | 1345 | -109 | 1 | 0 | 1454 | 157.1311 | 157.1311 | 157.1311 | 927.7824 | 780 | 200 | 1907.7824 | 47.69% | 95% | 0% | -124.714 | 32.4171 | -3550 | -400 | -3917.5829 | 97.94% | 48.36% | 95% | 0% | 1454 | -109
[5 empty] | 2019-09-15 | 15 | 6174.5 | 1394 | -126 | 1 | 0 | 1520 | 260.5111 | 260.5111 | 260.5111 | 927.7824 | 780 | 200 | 1907.7824 | 47.69% | 95% | 0% | -144.1648 | 116.3464 | -3550 | -400 | -3833.6536 | 95.84% | 48.36% | 95% | 0% | 1520 | -126
[5 empty] | 2019-09-15 | 16 | 6175 | 1429 | -164 | 1 | 0 | 1593 | 374.8557 | 374.8557 | 374.8557 | 927.7824 | 780 | 200 | 1907.7824 | 47.69% | 95% | 0% | -187.643 | 187.2127 | -3550 | -400 | -3762.7873 | 94.07% | 48.35% | 95% | 0% | 1593 | -164
[5 empty] | 2019-09-15 | 17 | 6175.5 | 1457 | -215 | 1 | 0 | 1672 | 498.5985 | 498.5985 | 498.5985 | 927.7824 | 780 | 200 | 1907.7824 | 47.69% | 95% | 0% | -245.9954 | 252.6031 | -3550 | -400 | -3697.3969 | 92.43% | 48.34% | 95% | 0% | 1672 | -215
[5 empty] | 2019-09-15 | 18 | 6176 | 1455 | -269 | 1 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 927.7824 | 780 | 200 | 1907.7824 | 47.69% | 95% | 0% | -307.7803 | 272.2691 | -3550 | -400 | -3677.7309 | 91.94% | 48.34% | 95% | 0% | 1724 | -269
[5 empty] | 2019-09-15 | 19 | 6176.5 | 1454 | -320 | 1 | 0 | 1774 | 658.3677 | 658.3677 | 658.3677 | 927.7824 | 780 | 200 | 1907.7824 | 47.69% | 95% | 0% | -366.1327 | 292.235 | -3550 | -400 | -3657.765 | 91.44% | 48.34% | 95% | 0% | 1774 | -320
[5 empty] | 2019-09-15 | 20 | 6177 | 1434 | -363 | 1 | 0 | 1797 | 694.3941 | 694.3941 | 694.3941 | 927.7824 | 780 | 200 | 1907.7824 | 47.69% | 95% | 0% | -415.3318 | 279.0623 | -3550 | -400 | -3670.9377 | 91.77% | 48.33% | 95% | 0% | 1797 | -363
[5 empty] | 2019-09-15 | 21 | 6177.5 | 1420 | -404 | 1 | 0 | 1824 | 736.6859 | 736.6859 | 736.6859 | 927.7824 | 780 | 200 | 1907.7824 | 47.69% | 95% | 0% | -462.2426 | 274.4433 | -3550 | -400 | -3675.5567 | 91.89% | 48.32% | 95% | 0% | 1824 | -404
[5 empty] | 2019-09-15 | 22 | 6178 | 1396 | -434 | 1 | 0 | 1830 | 746.0841 | 746.0841 | 746.0841 | 927.7824 | 780 | 200 | 1907.7824 | 47.69% | 95% | 0% | -496.5675 | 249.5166 | -3550 | -400 | -3700.4834 | 92.51% | 48.32% | 95% | 0% | 1830 | -434
[5 empty] | 2019-09-15 | 23 | 6178.5 | 1349 | -475 | 1 | 0 | 1824 | 736.6859 | 736.6859 | 736.6859 | 927.7824 | 780 | 200 | 1907.7824 | 47.69% | 95% | 0% | -543.4783 | 193.2076 | -3550 | -400 | -3756.7924 | 93.92% | 48.32% | 95% | 0% | 1824 | -475
[5 empty] | 2019-09-15 | 24 | 6179 | 1336 | -496 | 1 | 0 | 1832 | 749.2168 | 749.2168 | 749.2168 | 926.216 | 780 | 200 | 1906.216 | 47.66% | 95% | 0% | -567.5057 | 181.7111 | -3550 | -400 | -3768.2889 | 94.21% | 48.32% | 95% | 0% | 1832 | -496
[5 empty] | 2019-09-15 | 25 | 6179.5 | 1365 | -493 | 1 | 0 | 1858 | 789.9423 | 789.9423 | 789.9423 | 926.216 | 780 | 200 | 1906.216 | 47.66% | 95% | 0% | -564.0732 | 225.8691 | -3550 | -400 | -3724.1309 | 93.1% | 48.31% | 95% | 0% | 1858 | -493
[5 empty] | 2019-09-15 | 26 | 6180 | 1362 | -500 | 1 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 926.216 | 780 | 200 | 1906.216 | 47.66% | 95% | 0% | -572.0824 | 224.1254 | -3550 | -400 | -3725.8746 | 93.15% | 48.31% | 95% | 0% | 1862 | -500
[5 empty] | 2019-09-15 | 27 | 6180.5 | 1363 | -499 | 1 | 0 | 1862 | 796.2077 | 796.2077 | 796.2077 | 926.216 | 780 | 200 | 1906.216 | 47.66% | 95% | 0% | -570.9382 | 225.2695 | -3550 | -400 | -3724.7305 | 93.12% | 48.3% | 95% | 0% | 1862 | -499
[5 empty] | 2019-09-15 | 28 | 6181 | 1359 | -486 | 1 | 0 | 1845 | 769.5796 | 769.5796 | 769.5796 | 926.216 | 780 | 200 | 1906.216 | 47.66% | 95% | 0% | -556.0641 | 213.5155 | -3550 | -400 | -3736.4845 | 93.41% | 48.3% | 95% | 0% | 1845 | -486
[5 empty] | 2019-09-15 | 29 | 6181.5 | 1389 | -468 | 1 | 0 | 1857 | 788.3759 | 788.3759 | 788.3759 | 926.216 | 780 | 200 | 1906.216 | 47.66% | 95% | 0% | -535.4691 | 252.9068 | -3550 | -400 | -3697.0932 | 92.43% | 48.3% | 95% | 0% | 1857 | -468
[5 empty] | 2019-09-15 | 30 | 6182 | 1423 | -438 | 1 | 0 | 1861 | 794.6414 | 794.6414 | 794.6414 | 926.216 | 780 | 200 | 1906.216 | 47.66% | 95% | 0% | -501.1442 | 293.4972 | -3550 | -400 | -3656.5028 | 91.41% | 48.3% | 95% | 0% | 1861 | -438
[5 empty] | 2019-09-15 | 31 | 6182.5 | 1502 | -406 | 1 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 926.216 | 780 | 200 | 1906.216 | 47.66% | 95% | 0% | -464.5309 | 403.7296 | -3550 | -400 | -3546.2704 | 88.66% | 48.29% | 95% | 0% | 1908 | -406
[5 empty] | 2019-09-15 | 32 | 6183 | 1590 | -369 | 1 | 0 | 1959 | 948.1451 | 948.1451 | 948.1451 | 926.216 | 780 | 200 | 1906.216 | 47.66% | 95% | 0% | -422.1968 | 525.9483 | -3550 | -400 | -3424.0517 | 85.6% | 48.29% | 95% | 0% | 1959 | -369
[5 empty] | 2019-09-15 | 33 | 6183.5 | 1731 | -314 | 1 | 0 | 2045 | 1082.8524 | 1082.8524 | 1082.8524 | 926.216 | 780 | 200 | 1906.216 | 47.66% | 95% | 0% | -359.2677 | 723.5847 | -3550 | -400 | -3226.4153 | 80.66% | 48.29% | 95% | 0% | 2045 | -314
[5 empty] | 2019-09-15 | 34 | 6184 | 1878 | -260 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 924.6496 | 780 | 200 | 1904.6496 | 47.62% | 95% | 0% | -297.4828 | 931.0415 | -3550 | -400 | -3018.9585 | 75.47% | 48.28% | 95% | 0% | 2138 | -260
[5 empty] | 2019-09-15 | 35 | 6184.5 | 2053 | -194 | 1 | 0 | 2247 | 1399.258 | 1399.258 | 1399.258 | 924.6496 | 780 | 200 | 1904.6496 | 47.62% | 95% | 0% | -221.968 | 1177.2901 | -3550 | -400 | -2772.7099 | 69.32% | 48.28% | 95% | 0% | 2247 | -194
[5 empty] | 2019-09-15 | 36 | 6185 | 2176 | -136 | 1 | 0 | 2312 | 1501.0717 | 1501.0717 | 1501.0717 | 924.6496 | 780 | 200 | 1904.6496 | 47.62% | 95% | 0% | -155.6064 | 1345.4653 | -3550 | -400 | -2604.5347 | 65.11% | 48.28% | 95% | 0% | 2312 | -136
[5 empty] | 2019-09-15 | 37 | 6185.5 | 2240 | -96 | 1 | 0 | 2336 | 1538.6645 | 1538.6645 | 1538.6645 | 924.6496 | 780 | 200 | 1904.6496 | 47.62% | 95% | 0% | -109.8398 | 1428.8247 | -3550 | -400 | -2521.1753 | 63.03% | 48.28% | 95% | 0% | 2336 | -96
[5 empty] | 2019-09-15 | 38 | 6186 | 2281 | -67 | 1 | 0 | 2348 | 1557.4608 | 1557.4608 | 1557.4608 | 924.6496 | 780 | 200 | 1904.6496 | 47.62% | 95% | 0% | -76.659 | 1480.8018 | -3550 | -400 | -2469.1982 | 61.73% | 48.28% | 95% | 0% | 2348 | -67
[5 empty] | 2019-09-15 | 39 | 6186.5 | 2320 | -56 | 1 | 0 | 2376 | 1601.319 | 1601.319 | 1601.319 | 924.6496 | 780 | 200 | 1904.6496 | 47.62% | 95% | 0% | -64.0732 | 1537.2458 | -3550 | -400 | -2412.7542 | 60.32% | 48.28% | 95% | 0% | 2376 | -56
[5 empty] | 2019-09-15 | 40 | 6187 | 2373 | -53 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 923.0833 | 780 | 200 | 1903.0833 | 47.58% | 95% | 0% | -60.6407 | 1618.9965 | -3550 | -400 | -2331.0035 | 58.28% | 48.27% | 95% | 0% | 2426 | -53
[5 empty] | 2019-09-15 | 41 | 6187.5 | 2351 | -52 | 0 | 0 | 2403 | 1643.6109 | 1643.6109 | 1643.6109 | 923.0833 | 780 | 200 | 1903.0833 | 47.58% | 95% | 0% | -59.4966 | 1584.1143 | -2750 | -200 | -1365.8857 | 34.15% | 48.27% | 95% | 0% | 2403 | -52
[5 empty] | 2019-09-15 | 42 | 6188 | 2275 | -51 | 0 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 923.0833 | 780 | 200 | 1903.0833 | 47.58% | 95% | 0% | -58.3524 | 1464.6484 | -2750 | -200 | -1485.3516 | 37.13% | 48.25% | 95% | 0% | 2326 | -51
[5 empty] | 2019-09-15 | 43 | 6188.5 | 2208 | -50 | 0 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 923.0833 | 780 | 200 | 1903.0833 | 47.58% | 95% | 0% | -57.2082 | 1359.2798 | -2750 | -200 | -1590.7202 | 39.77% | 48.25% | 95% | 0% | 2258 | -50
[5 empty] | 2019-09-15 | 44 | 6189 | 2107 | -50 | 0 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 923.0833 | 780 | 200 | 1903.0833 | 47.58% | 95% | 0% | -57.2082 | 1201.077 | -2750 | -200 | -1748.923 | 43.72% | 48.25% | 95% | 0% | 2157 | -50
[5 empty] | 2019-09-15 | 45 | 6189.5 | 2001 | -49 | 0 | 0 | 2050 | 1090.6843 | 1090.6843 | 1090.6843 | 923.0833 | 780 | 200 | 1903.0833 | 47.58% | 95% | 0% | -56.0641 | 1034.6202 | -2750 | -200 | -1915.3798 | 47.88% | 48.25% | 95% | 0% | 2050 | -49
[5 empty] | 2019-09-15 | 46 | 6190 | 1879 | -49 | 0 | 0 | 1928 | 899.5878 | 899.5878 | 899.5878 | 923.0833 | 780 | 200 | 1903.0833 | 47.58% | 95% | 0% | -56.0641 | 843.5237 | -2750 | -200 | -2106.4763 | 52.66% | 48.24% | 95% | 0% | 1928 | -49
[5 empty] | 2019-09-15 | 47 | 6190.5 | 1756 | -49 | 0 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -56.0641 | 650.8609 | -2750 | -200 | -2299.1391 | 57.48% | 48.24% | 95% | 0% | 1805 | -49
[5 empty] | 2019-09-15 | 48 | 6191 | 1668 | -49 | 0 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -56.0641 | 513.0208 | -2750 | -200 | -2436.9792 | 60.92% | 48.23% | 95% | 0% | 1717 | -49
[5 empty] | 2019-09-16 | 1 | 6191.5 | 1597 | -47 | 0 | 0 | 1644 | 454.7403 | 454.7403 | 454.7403 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -53.7757 | 400.9646 | -2750 | -200 | -2549.0354 | 63.73% | 48.23% | 95% | 0% | 1644 | -47
[5 empty] | 2019-09-16 | 2 | 6192 | 1554 | -46 | 0 | 0 | 1600 | 385.8203 | 385.8203 | 385.8203 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -52.6316 | 333.1887 | -2750 | -200 | -2616.8113 | 65.42% | 48.22% | 95% | 0% | 1600 | -46
[5 empty] | 2019-09-16 | 3 | 6192.5 | 1531 | -47 | 0 | 0 | 1578 | 351.3603 | 351.3603 | 351.3603 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -53.7757 | 297.5845 | -2750 | -200 | -2652.4155 | 66.31% | 48.22% | 95% | 0% | 1578 | -47
[5 empty] | 2019-09-16 | 4 | 6193 | 1520 | -47 | 0 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -53.7757 | 280.3545 | -2750 | -200 | -2669.6455 | 66.74% | 48.21% | 95% | 0% | 1567 | -47
[5 empty] | 2019-09-16 | 5 | 6193.5 | 1509 | -48 | 0 | 0 | 1557 | 318.4666 | 318.4666 | 318.4666 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -54.9199 | 263.5467 | -2750 | -200 | -2686.4533 | 67.16% | 48.21% | 95% | 0% | 1557 | -48
[5 empty] | 2019-09-16 | 6 | 6194 | 1480 | -49 | 0 | 0 | 1529 | 274.6084 | 274.6084 | 274.6084 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -56.0641 | 218.5443 | -2750 | -200 | -2731.4557 | 68.29% | 48.21% | 95% | 0% | 1529 | -49
[5 empty] | 2019-09-16 | 7 | 6194.5 | 1469 | -50 | 0 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -57.2082 | 201.7365 | -2750 | -200 | -2748.2635 | 68.71% | 48.21% | 95% | 0% | 1519 | -50
[5 empty] | 2019-09-16 | 8 | 6195 | 1465 | -51 | 0 | 0 | 1516 | 254.2457 | 254.2457 | 254.2457 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -58.3524 | 195.8933 | -2750 | -200 | -2754.1067 | 68.85% | 48.2% | 95% | 0% | 1516 | -51
[5 empty] | 2019-09-16 | 9 | 6195.5 | 1471 | -52 | 0 | 0 | 1523 | 265.2102 | 265.2102 | 265.2102 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -59.4966 | 205.7137 | -2750 | -200 | -2744.2863 | 68.61% | 48.2% | 95% | 0% | 1523 | -52
[5 empty] | 2019-09-16 | 10 | 6196 | 1486 | -53 | 1 | 0 | 1539 | 290.2721 | 290.2721 | 290.2721 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -60.6407 | 229.6313 | -3550 | -400 | -3720.3687 | 93.01% | 48.2% | 95% | 0% | 1539 | -53
[5 empty] | 2019-09-16 | 11 | 6196.5 | 1531 | -54 | 1 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -61.7849 | 300.5399 | -3550 | -400 | -3649.4601 | 91.24% | 48.18% | 95% | 0% | 1585 | -54
[5 empty] | 2019-09-16 | 12 | 6197 | 1633 | -54 | 1 | 0 | 1687 | 522.094 | 522.094 | 522.094 | 921.5169 | 780 | 200 | 1901.5169 | 47.54% | 95% | 0% | -61.7849 | 460.3091 | -3550 | -400 | -3489.6909 | 87.24% | 48.18% | 95% | 0% | 1687 | -54
[5 empty] | 2019-09-16 | 13 | 6197.5 | 1849 | -54 | 1 | 0 | 1903 | 860.4287 | 860.4287 | 860.4287 | 919.9505 | 780 | 200 | 1899.9505 | 47.5% | 95% | 0% | -61.7849 | 798.6438 | -3550 | -400 | -3151.3562 | 78.78% | 48.18% | 95% | 0% | 1903 | -54
[5 empty] | 2019-09-16 | 14 | 6198 | 2038 | -54 | 1 | 0 | 2092 | 1156.4716 | 1156.4716 | 1156.4716 | 919.9505 | 780 | 200 | 1899.9505 | 47.5% | 95% | 0% | -61.7849 | 1094.6867 | -3550 | -400 | -2855.3133 | 71.38% | 48.18% | 95% | 0% | 2092 | -54
[5 empty] | 2019-09-16 | 15 | 6198.5 | 2267 | -59 | 1 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 919.9505 | 780 | 200 | 1899.9505 | 47.5% | 95% | 0% | -67.5057 | 1455.4951 | -3550 | -400 | -2494.5049 | 62.36% | 48.18% | 95% | 0% | 2326 | -59
[5 empty] | 2019-09-16 | 16 | 6199 | 2354 | -74 | 1 | 0 | 2428 | 1682.77 | 1682.77 | 1682.77 | 919.9505 | 780 | 200 | 1899.9505 | 47.5% | 95% | 0% | -84.6682 | 1598.1018 | -3550 | -400 | -2351.8982 | 58.8% | 48.18% | 95% | 0% | 2428 | -74
[5 empty] | 2019-09-16 | 17 | 6199.5 | 2414 | -103 | 1 | 0 | 2517 | 1822.1764 | 1822.1764 | 1822.1764 | 919.9505 | 780 | 200 | 1899.9505 | 47.5% | 95% | 0% | -117.849 | 1704.3275 | -3550 | -400 | -2245.6725 | 56.14% | 48.18% | 95% | 0% | 2517 | -103
[5 empty] | 2019-09-16 | 18 | 6200 | 2346 | -141 | 1 | 0 | 2487 | 1775.1855 | 1775.1855 | 1775.1855 | 918.3842 | 780 | 200 | 1898.3842 | 47.46% | 95% | 0% | -161.3272 | 1613.8583 | -3550 | -400 | -2336.1417 | 58.4% | 48.17% | 95% | 0% | 2487 | -141
[5 empty] | 2019-09-16 | 19 | 6200.5 | 2336 | -183 | 1 | 0 | 2519 | 1825.3092 | 1825.3092 | 1825.3092 | 918.3842 | 780 | 200 | 1898.3842 | 47.46% | 95% | 0% | -209.3822 | 1615.927 | -3550 | -400 | -2334.073 | 58.35% | 48.17% | 95% | 0% | 2519 | -183
[5 empty] | 2019-09-16 | 20 | 6201 | 2301 | -220 | 1 | 0 | 2521 | 1828.4419 | 1828.4419 | 1828.4419 | 918.3842 | 780 | 200 | 1898.3842 | 47.46% | 95% | 0% | -251.7162 | 1576.7256 | -3550 | -400 | -2373.2744 | 59.33% | 48.17% | 95% | 0% | 2521 | -220
[5 empty] | 2019-09-16 | 21 | 6201.5 | 2242 | -261 | 1 | 0 | 2503 | 1800.2473 | 1800.2473 | 1800.2473 | 918.3842 | 780 | 200 | 1898.3842 | 47.46% | 95% | 0% | -298.627 | 1501.6203 | -3550 | -400 | -2448.3797 | 61.21% | 48.16% | 95% | 0% | 2503 | -261
[5 empty] | 2019-09-16 | 22 | 6202 | 2222 | -294 | 1 | 0 | 2516 | 1820.6101 | 1820.6101 | 1820.6101 | 918.3842 | 780 | 200 | 1898.3842 | 47.46% | 95% | 0% | -336.3844 | 1484.2256 | -3550 | -400 | -2465.7744 | 61.64% | 48.15% | 95% | 0% | 2516 | -294
[5 empty] | 2019-09-16 | 23 | 6202.5 | 2176 | -343 | 1 | 0 | 2519 | 1825.3092 | 1825.3092 | 1825.3092 | 918.3842 | 780 | 200 | 1898.3842 | 47.46% | 95% | 0% | -392.4485 | 1432.8606 | -3550 | -400 | -2517.1394 | 62.93% | 48.15% | 95% | 0% | 2519 | -343
[5 empty] | 2019-09-16 | 24 | 6203 | 2168 | -341 | 1 | 0 | 2509 | 1809.6455 | 1809.6455 | 1809.6455 | 918.3842 | 780 | 200 | 1898.3842 | 47.46% | 95% | 0% | -390.1602 | 1419.4853 | -3550 | -400 | -2530.5147 | 63.26% | 48.14% | 95% | 0% | 2509 | -341
[5 empty] | 2019-09-16 | 25 | 6203.5 | 2148 | -352 | 1 | 0 | 2500 | 1795.5482 | 1795.5482 | 1795.5482 | 918.3842 | 780 | 200 | 1898.3842 | 47.46% | 95% | 0% | -402.746 | 1392.8022 | -3550 | -400 | -2557.1978 | 63.93% | 48.14% | 95% | 0% | 2500 | -352
[5 empty] | 2019-09-16 | 26 | 6204 | 2108 | -368 | 1 | 0 | 2476 | 1757.9555 | 1757.9555 | 1757.9555 | 918.3842 | 780 | 200 | 1898.3842 | 47.46% | 95% | 0% | -421.0526 | 1336.9029 | -3550 | -400 | -2613.0971 | 65.33% | 48.13% | 95% | 0% | 2476 | -368
[5 empty] | 2019-09-16 | 27 | 6204.5 | 2067 | -377 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -431.3501 | 1276.4817 | -3550 | -400 | -2673.5183 | 66.84% | 48.13% | 95% | 0% | 2444 | -377
[5 empty] | 2019-09-16 | 28 | 6205 | 2049 | -375 | 1 | 0 | 2424 | 1676.5045 | 1676.5045 | 1676.5045 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -429.0618 | 1247.4427 | -3550 | -400 | -2702.5573 | 67.56% | 48.12% | 95% | 0% | 2424 | -375
[5 empty] | 2019-09-16 | 29 | 6205.5 | 2035 | -373 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -426.7735 | 1224.6692 | -3550 | -400 | -2725.3308 | 68.13% | 48.12% | 95% | 0% | 2408 | -373
[5 empty] | 2019-09-16 | 30 | 6206 | 2053 | -358 | 1 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -409.611 | 1246.5308 | -3550 | -400 | -2703.4692 | 67.59% | 48.12% | 95% | 0% | 2411 | -358
[5 empty] | 2019-09-16 | 31 | 6206.5 | 2058 | -345 | 1 | 0 | 2403 | 1643.6109 | 1643.6109 | 1643.6109 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -394.7368 | 1248.874 | -3550 | -400 | -2701.126 | 67.53% | 48.12% | 95% | 0% | 2403 | -345
[5 empty] | 2019-09-16 | 32 | 6207 | 2116 | -331 | 1 | 0 | 2447 | 1712.5309 | 1712.5309 | 1712.5309 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -378.7185 | 1333.8124 | -3550 | -400 | -2616.1876 | 65.4% | 48.12% | 95% | 0% | 2447 | -331
[5 empty] | 2019-09-16 | 33 | 6207.5 | 2214 | -294 | 1 | 0 | 2508 | 1808.0791 | 1808.0791 | 1808.0791 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -336.3844 | 1471.6947 | -3550 | -400 | -2478.3053 | 61.96% | 48.11% | 95% | 0% | 2508 | -294
[5 empty] | 2019-09-16 | 34 | 6208 | 2320 | -246 | 1 | 0 | 2566 | 1898.9283 | 1898.9283 | 1898.9283 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -281.4645 | 1617.4637 | -3550 | -400 | -2332.5363 | 58.31% | 48.11% | 95% | 0% | 2566 | -246
[5 empty] | 2019-09-16 | 35 | 6208.5 | 2420 | -197 | 1 | 0 | 2617 | 1978.8129 | 1978.8129 | 1978.8129 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -225.4005 | 1753.4124 | -3550 | -400 | -2196.5876 | 54.91% | 48.1% | 95% | 0% | 2617 | -197
[5 empty] | 2019-09-16 | 36 | 6209 | 2475 | -161 | 1 | 0 | 2636 | 2008.5738 | 2008.5738 | 2008.5738 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -184.2105 | 1824.3633 | -3550 | -400 | -2125.6367 | 53.14% | 48.1% | 95% | 0% | 2636 | -161
[5 empty] | 2019-09-16 | 37 | 6209.5 | 2516 | -127 | 1 | 0 | 2643 | 2019.5383 | 2019.5383 | 2019.5383 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -145.3089 | 1874.2294 | -3550 | -400 | -2075.7706 | 51.89% | 48.1% | 95% | 0% | 2643 | -127
[5 empty] | 2019-09-16 | 38 | 6210 | 2557 | -96 | 1 | 0 | 2653 | 2035.202 | 2035.202 | 2035.202 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -109.8398 | 1925.3622 | -3550 | -400 | -2024.6378 | 50.62% | 48.1% | 95% | 0% | 2653 | -96
[5 empty] | 2019-09-16 | 39 | 6210.5 | 2614 | -83 | 1 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 916.8178 | 780 | 200 | 1896.8178 | 47.42% | 95% | 0% | -94.9657 | 2009.1563 | -3550 | -400 | -1940.8437 | 48.52% | 48.09% | 95% | 0% | 2697 | -83
[5 empty] | 2019-09-16 | 40 | 6211 | 2631 | -82 | 1 | 0 | 2713 | 2129.1838 | 2129.1838 | 2129.1838 | 915.2514 | 780 | 200 | 1895.2514 | 47.38% | 95% | 0% | -93.8215 | 2035.3623 | -3550 | -400 | -1914.6377 | 47.87% | 48.08% | 95% | 0% | 2713 | -82
[5 empty] | 2019-09-16 | 41 | 6211.5 | 2587 | -82 | 1 | 0 | 2669 | 2060.2638 | 2060.2638 | 2060.2638 | 915.2514 | 780 | 200 | 1895.2514 | 47.38% | 95% | 0% | -93.8215 | 1966.4423 | -3550 | -400 | -1983.5577 | 49.59% | 48.08% | 95% | 0% | 2669 | -82
[5 empty] | 2019-09-16 | 42 | 6212 | 2500 | -82 | 0 | 0 | 2582 | 1923.9901 | 1923.9901 | 1923.9901 | 915.2514 | 780 | 200 | 1895.2514 | 47.38% | 95% | 0% | -93.8215 | 1830.1686 | -2750 | -200 | -1119.8314 | 28% | 48.07% | 95% | 0% | 2582 | -82
[5 empty] | 2019-09-16 | 43 | 6212.5 | 2384 | -83 | 0 | 0 | 2467 | 1743.8582 | 1743.8582 | 1743.8582 | 915.2514 | 780 | 200 | 1895.2514 | 47.38% | 95% | 0% | -94.9657 | 1648.8925 | -2750 | -200 | -1301.1075 | 32.53% | 48.07% | 95% | 0% | 2467 | -83
[5 empty] | 2019-09-16 | 44 | 6213 | 2233 | -83 | 0 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 915.2514 | 780 | 200 | 1895.2514 | 47.38% | 95% | 0% | -94.9657 | 1412.3715 | -2750 | -200 | -1537.6285 | 38.44% | 48.07% | 95% | 0% | 2316 | -83
[5 empty] | 2019-09-16 | 45 | 6213.5 | 2086 | -84 | 0 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 915.2514 | 780 | 200 | 1895.2514 | 47.38% | 95% | 0% | -96.1098 | 1182.5381 | -2750 | -200 | -1767.4619 | 44.19% | 48.06% | 95% | 0% | 2170 | -84
[5 empty] | 2019-09-16 | 46 | 6214 | 1936 | -85 | 0 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 915.2514 | 780 | 200 | 1895.2514 | 47.38% | 95% | 0% | -97.254 | 948.0057 | -2750 | -200 | -2001.9943 | 50.05% | 48.06% | 95% | 0% | 2021 | -85
[5 empty] | 2019-09-16 | 47 | 6214.5 | 1799 | -86 | 0 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 915.2514 | 780 | 200 | 1895.2514 | 47.38% | 95% | 0% | -98.3982 | 733.836 | -2750 | -200 | -2216.164 | 55.4% | 48.05% | 95% | 0% | 1885 | -86
[5 empty] | 2019-09-16 | 48 | 6215 | 1688 | -87 | 0 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 915.2514 | 780 | 200 | 1895.2514 | 47.38% | 95% | 0% | -99.5423 | 560.3917 | -2750 | -200 | -2389.6083 | 59.74% | 48.05% | 95% | 0% | 1775 | -87
[5 empty] | 2019-09-17 | 1 | 6215.5 | 1603 | -85 | 0 | 0 | 1688 | 523.6603 | 523.6603 | 523.6603 | 915.2514 | 780 | 200 | 1895.2514 | 47.38% | 95% | 0% | -97.254 | 426.4063 | -2750 | -200 | -2523.5937 | 63.09% | 48.04% | 95% | 0% | 1688 | -85
[5 empty] | 2019-09-17 | 2 | 6216 | 1546 | -84 | 0 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 915.2514 | 780 | 200 | 1895.2514 | 47.38% | 95% | 0% | -96.1098 | 336.7014 | -2750 | -200 | -2613.2986 | 65.33% | 48.04% | 95% | 0% | 1630 | -84
[5 empty] | 2019-09-17 | 3 | 6216.5 | 1516 | -84 | 0 | 0 | 1600 | 385.8203 | 385.8203 | 385.8203 | 915.2514 | 780 | 200 | 1895.2514 | 47.38% | 95% | 0% | -96.1098 | 289.7104 | -2750 | -200 | -2660.2896 | 66.51% | 48.03% | 95% | 0% | 1600 | -84
[5 empty] | 2019-09-17 | 4 | 6217 | 1497 | -85 | 0 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 913.6851 | 780 | 200 | 1893.6851 | 47.34% | 95% | 0% | -97.254 | 260.3717 | -2750 | -200 | -2689.6283 | 67.24% | 48.02% | 95% | 0% | 1582 | -85
[5 empty] | 2019-09-17 | 5 | 6217.5 | 1479 | -86 | 0 | 0 | 1565 | 330.9975 | 330.9975 | 330.9975 | 913.6851 | 780 | 200 | 1893.6851 | 47.34% | 95% | 0% | -98.3982 | 232.5994 | -2750 | -200 | -2717.4006 | 67.94% | 48.02% | 95% | 0% | 1565 | -86
[5 empty] | 2019-09-17 | 6 | 6218 | 1456 | -86 | 0 | 0 | 1542 | 294.9711 | 294.9711 | 294.9711 | 913.6851 | 780 | 200 | 1893.6851 | 47.34% | 95% | 0% | -98.3982 | 196.573 | -2750 | -200 | -2753.427 | 68.84% | 48.02% | 95% | 0% | 1542 | -86
[5 empty] | 2019-09-17 | 7 | 6218.5 | 1439 | -87 | 0 | 0 | 1526 | 269.9093 | 269.9093 | 269.9093 | 913.6851 | 780 | 200 | 1893.6851 | 47.34% | 95% | 0% | -99.5423 | 170.367 | -2750 | -200 | -2779.633 | 69.49% | 48.01% | 95% | 0% | 1526 | -87
[5 empty] | 2019-09-17 | 8 | 6219 | 1437 | -87 | 0 | 0 | 1524 | 266.7766 | 266.7766 | 266.7766 | 913.6851 | 780 | 200 | 1893.6851 | 47.34% | 95% | 0% | -99.5423 | 167.2343 | -2750 | -200 | -2782.7657 | 69.57% | 48.01% | 95% | 0% | 1524 | -87
[5 empty] | 2019-09-17 | 9 | 6219.5 | 1447 | -87 | 0 | 0 | 1534 | 282.4402 | 282.4402 | 282.4402 | 913.6851 | 780 | 200 | 1893.6851 | 47.34% | 95% | 0% | -99.5423 | 182.8979 | -2750 | -200 | -2767.1021 | 69.18% | 48% | 95% | 0% | 1534 | -87
[5 empty] | 2019-09-17 | 10 | 6220 | 1461 | -87 | 0 | 0 | 1548 | 304.3693 | 304.3693 | 304.3693 | 913.6851 | 780 | 200 | 1893.6851 | 47.34% | 95% | 0% | -99.5423 | 204.827 | -2750 | -200 | -2745.173 | 68.63% | 48% | 95% | 0% | 1548 | -87
[5 empty] | 2019-09-17 | 11 | 6220.5 | 1528 | -87 | 0 | 0 | 1615 | 409.3157 | 409.3157 | 409.3157 | 913.6851 | 780 | 200 | 1893.6851 | 47.34% | 95% | 0% | -99.5423 | 309.7734 | -2750 | -200 | -2640.2266 | 66.01% | 47.98% | 95% | 0% | 1615 | -87
[5 empty] | 2019-09-17 | 12 | 6221 | 1625 | -86 | 0 | 0 | 1711 | 559.6867 | 559.6867 | 559.6867 | 913.6851 | 780 | 200 | 1893.6851 | 47.34% | 95% | 0% | -98.3982 | 461.2886 | -2750 | -200 | -2488.7114 | 62.22% | 47.98% | 95% | 0% | 1711 | -86
[5 empty] | 2019-09-17 | 13 | 6221.5 | 1823 | -86 | 0 | 0 | 1909 | 869.8269 | 869.8269 | 869.8269 | 913.6851 | 780 | 200 | 1893.6851 | 47.34% | 95% | 0% | -98.3982 | 771.4287 | -2750 | -200 | -2178.5713 | 54.46% | 47.97% | 95% | 0% | 1909 | -86
[5 empty] | 2019-09-17 | 14 | 6222 | 2022 | -87 | 0 | 0 | 2109 | 1183.0998 | 1183.0998 | 1183.0998 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -99.5423 | 1083.5574 | -2750 | -200 | -1866.4426 | 46.66% | 47.97% | 95% | 0% | 2109 | -87
[5 empty] | 2019-09-17 | 15 | 6222.5 | 2232 | -111 | 0 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -127.0023 | 1422.6267 | -2750 | -200 | -1527.3733 | 38.18% | 47.97% | 95% | 0% | 2343 | -111
[5 empty] | 2019-09-17 | 16 | 6223 | 2255 | -170 | 0 | 0 | 2425 | 1678.0709 | 1678.0709 | 1678.0709 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -194.508 | 1483.5629 | -2750 | -200 | -1466.4371 | 36.66% | 47.97% | 95% | 0% | 2425 | -170
[5 empty] | 2019-09-17 | 17 | 6223.5 | 2206 | -246 | 0 | 0 | 2452 | 1720.3627 | 1720.3627 | 1720.3627 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -281.4645 | 1438.8982 | -2750 | -200 | -1511.1018 | 37.78% | 47.97% | 95% | 0% | 2452 | -246
[5 empty] | 2019-09-17 | 18 | 6224 | 2081 | -325 | 1 | 0 | 2406 | 1648.31 | 1648.31 | 1648.31 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -371.8535 | 1276.4564 | -3550 | -400 | -2673.5436 | 66.84% | 47.96% | 95% | 0% | 2406 | -325
[5 empty] | 2019-09-17 | 19 | 6224.5 | 1960 | -401 | 1 | 0 | 2361 | 1577.8236 | 1577.8236 | 1577.8236 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -458.8101 | 1119.0135 | -3550 | -400 | -2830.9865 | 70.77% | 47.96% | 95% | 0% | 2361 | -401
[5 empty] | 2019-09-17 | 20 | 6225 | 1820 | -481 | 1 | 0 | 2301 | 1483.8417 | 1483.8417 | 1483.8417 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -550.3432 | 933.4985 | -3550 | -400 | -3016.5015 | 75.41% | 47.96% | 95% | 0% | 2301 | -481
[5 empty] | 2019-09-17 | 21 | 6225.5 | 1666 | -548 | 1 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -627.0023 | 720.5657 | -3550 | -400 | -3229.4343 | 80.74% | 47.95% | 95% | 0% | 2214 | -548
[5 empty] | 2019-09-17 | 22 | 6226 | 1573 | -607 | 1 | 0 | 2180 | 1294.3116 | 1294.3116 | 1294.3116 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -694.508 | 599.8036 | -3550 | -400 | -3350.1964 | 83.75% | 47.94% | 95% | 0% | 2180 | -607
[5 empty] | 2019-09-17 | 23 | 6226.5 | 1510 | -645 | 1 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -737.9863 | 517.1662 | -3550 | -400 | -3432.8338 | 85.82% | 47.94% | 95% | 0% | 2155 | -645
[5 empty] | 2019-09-17 | 24 | 6227 | 1477 | -664 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -759.7254 | 473.498 | -3550 | -400 | -3476.502 | 86.91% | 47.93% | 95% | 0% | 2141 | -664
[5 empty] | 2019-09-17 | 25 | 6227.5 | 1461 | -672 | 1 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -768.8787 | 451.8138 | -3550 | -400 | -3498.1862 | 87.45% | 47.93% | 95% | 0% | 2133 | -672
[5 empty] | 2019-09-17 | 26 | 6228 | 1417 | -686 | 1 | 0 | 2103 | 1173.7016 | 1173.7016 | 1173.7016 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -784.897 | 388.8045 | -3550 | -400 | -3561.1955 | 89.03% | 47.93% | 95% | 0% | 2103 | -686
[5 empty] | 2019-09-17 | 27 | 6228.5 | 1402 | -674 | 1 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -771.167 | 360.2427 | -3550 | -400 | -3589.7573 | 89.74% | 47.92% | 95% | 0% | 2076 | -674
[5 empty] | 2019-09-17 | 28 | 6229 | 1406 | -650 | 1 | 0 | 2056 | 1100.0824 | 1100.0824 | 1100.0824 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -743.7071 | 356.3753 | -3550 | -400 | -3593.6247 | 89.84% | 47.92% | 95% | 0% | 2056 | -650
[5 empty] | 2019-09-17 | 29 | 6229.5 | 1434 | -632 | 1 | 0 | 2066 | 1115.7461 | 1115.7461 | 1115.7461 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -723.1121 | 392.634 | -3550 | -400 | -3557.366 | 88.93% | 47.92% | 95% | 0% | 2066 | -632
[5 empty] | 2019-09-17 | 30 | 6230 | 1469 | -601 | 1 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -687.643 | 434.3685 | -3550 | -400 | -3515.6315 | 87.89% | 47.91% | 95% | 0% | 2070 | -601
[5 empty] | 2019-09-17 | 31 | 6230.5 | 1554 | -548 | 1 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -627.0023 | 545.1329 | -3550 | -400 | -3404.8671 | 85.12% | 47.91% | 95% | 0% | 2102 | -548
[5 empty] | 2019-09-17 | 32 | 6231 | 1675 | -501 | 1 | 0 | 2176 | 1288.0462 | 1288.0462 | 1288.0462 | 912.1187 | 780 | 200 | 1892.1187 | 47.3% | 95% | 0% | -573.2265 | 714.8196 | -3550 | -400 | -3235.1804 | 80.88% | 47.9% | 95% | 0% | 2176 | -501
[5 empty] | 2019-09-17 | 33 | 6231.5 | 1845 | -426 | 1 | 0 | 2271 | 1436.8508 | 1436.8508 | 1436.8508 | 910.5523 | 780 | 200 | 1890.5523 | 47.26% | 95% | 0% | -487.4142 | 949.4366 | -3550 | -400 | -3000.5634 | 75.01% | 47.9% | 95% | 0% | 2271 | -426
[5 empty] | 2019-09-17 | 34 | 6232 | 2018 | -363 | 1 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 910.5523 | 780 | 200 | 1890.5523 | 47.26% | 95% | 0% | -415.3318 | 1193.8191 | -3550 | -400 | -2756.1809 | 68.9% | 47.9% | 95% | 0% | 2381 | -363
[5 empty] | 2019-09-17 | 35 | 6232.5 | 2202 | -288 | 1 | 0 | 2490 | 1779.8846 | 1779.8846 | 1779.8846 | 910.5523 | 780 | 200 | 1890.5523 | 47.26% | 95% | 0% | -329.5195 | 1450.3651 | -3550 | -400 | -2499.6349 | 62.49% | 47.9% | 95% | 0% | 2490 | -288
[5 empty] | 2019-09-17 | 36 | 6233 | 2331 | -209 | 1 | 0 | 2540 | 1858.2028 | 1858.2028 | 1858.2028 | 910.5523 | 780 | 200 | 1890.5523 | 47.26% | 95% | 0% | -239.1304 | 1619.0724 | -3550 | -400 | -2330.9276 | 58.27% | 47.9% | 95% | 0% | 2540 | -209
[5 empty] | 2019-09-17 | 37 | 6233.5 | 2443 | -140 | 1 | 0 | 2583 | 1925.5565 | 1925.5565 | 1925.5565 | 910.5523 | 780 | 200 | 1890.5523 | 47.26% | 95% | 0% | -160.1831 | 1765.3734 | -3550 | -400 | -2184.6266 | 54.62% | 47.89% | 95% | 0% | 2583 | -140
[5 empty] | 2019-09-17 | 38 | 6234 | 2529 | -83 | 1 | 0 | 2612 | 1970.981 | 1970.981 | 1970.981 | 910.5523 | 780 | 200 | 1890.5523 | 47.26% | 95% | 0% | -94.9657 | 1876.0154 | -3550 | -400 | -2073.9846 | 51.85% | 47.89% | 95% | 0% | 2612 | -83
[5 empty] | 2019-09-17 | 39 | 6234.5 | 2588 | -59 | 1 | 0 | 2647 | 2025.8038 | 2025.8038 | 2025.8038 | 910.5523 | 780 | 200 | 1890.5523 | 47.26% | 95% | 0% | -67.5057 | 1958.2981 | -3550 | -400 | -1991.7019 | 49.79% | 47.88% | 95% | 0% | 2647 | -59
[5 empty] | 2019-09-17 | 40 | 6235 | 2631 | -56 | 1 | 0 | 2687 | 2088.4584 | 2088.4584 | 2088.4584 | 910.5523 | 780 | 200 | 1890.5523 | 47.26% | 95% | 0% | -64.0732 | 2024.3851 | -3550 | -400 | -1925.6149 | 48.14% | 47.88% | 95% | 0% | 2687 | -56
[5 empty] | 2019-09-17 | 41 | 6235.5 | 2602 | -54 | 1 | 0 | 2656 | 2039.9011 | 2039.9011 | 2039.9011 | 910.5523 | 780 | 200 | 1890.5523 | 47.26% | 95% | 0% | -61.7849 | 1978.1162 | -3550 | -400 | -1971.8838 | 49.3% | 47.87% | 95% | 0% | 2656 | -54
[5 empty] | 2019-09-17 | 42 | 6236 | 2522 | -52 | 0 | 0 | 2574 | 1911.4592 | 1911.4592 | 1911.4592 | 910.5523 | 780 | 200 | 1890.5523 | 47.26% | 95% | 0% | -59.4966 | 1851.9626 | -2750 | -200 | -1098.0374 | 27.45% | 47.87% | 95% | 0% | 2574 | -52
[5 empty] | 2019-09-17 | 43 | 6236.5 | 2429 | -49 | 0 | 0 | 2478 | 1761.0882 | 1761.0882 | 1761.0882 | 908.986 | 780 | 200 | 1888.986 | 47.22% | 95% | 0% | -56.0641 | 1705.0241 | -2750 | -200 | -1244.9759 | 31.12% | 47.87% | 95% | 0% | 2478 | -49
[5 empty] | 2019-09-17 | 44 | 6237 | 2319 | -47 | 0 | 0 | 2366 | 1585.6554 | 1585.6554 | 1585.6554 | 908.986 | 780 | 200 | 1888.986 | 47.22% | 95% | 0% | -53.7757 | 1531.8797 | -2750 | -200 | -1418.1203 | 35.45% | 47.87% | 95% | 0% | 2366 | -47
[5 empty] | 2019-09-17 | 45 | 6237.5 | 2173 | -44 | 0 | 0 | 2217 | 1352.2671 | 1352.2671 | 1352.2671 | 908.986 | 780 | 200 | 1888.986 | 47.22% | 95% | 0% | -50.3432 | 1301.9239 | -2750 | -200 | -1648.0761 | 41.2% | 47.87% | 95% | 0% | 2217 | -44
[5 empty] | 2019-09-17 | 46 | 6238 | 2035 | -41 | 0 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 908.986 | 780 | 200 | 1888.986 | 47.22% | 95% | 0% | -46.9108 | 1084.499 | -2750 | -200 | -1865.501 | 46.64% | 47.85% | 95% | 0% | 2076 | -41
[5 empty] | 2019-09-17 | 47 | 6238.5 | 1902 | -39 | 0 | 0 | 1941 | 919.9505 | 919.9505 | 919.9505 | 908.986 | 780 | 200 | 1888.986 | 47.22% | 95% | 0% | -44.6224 | 875.3281 | -2750 | -200 | -2074.6719 | 51.87% | 47.85% | 95% | 0% | 1941 | -39
[5 empty] | 2019-09-17 | 48 | 6239 | 1798 | -36 | 0 | 0 | 1834 | 752.3495 | 752.3495 | 752.3495 | 908.986 | 780 | 200 | 1888.986 | 47.22% | 95% | 0% | -41.1899 | 711.1596 | -2750 | -200 | -2238.8404 | 55.97% | 47.85% | 95% | 0% | 1834 | -36
[5 empty] | 2019-09-18 | 1 | 6239.5 | 1724 | -33 | 0 | 0 | 1757 | 631.7395 | 631.7395 | 631.7395 | 908.986 | 780 | 200 | 1888.986 | 47.22% | 95% | 0% | -37.7574 | 593.9821 | -2750 | -200 | -2356.0179 | 58.9% | 47.84% | 95% | 0% | 1757 | -33
[5 empty] | 2019-09-18 | 2 | 6240 | 1679 | -31 | 0 | 0 | 1710 | 558.1204 | 558.1204 | 558.1204 | 908.986 | 780 | 200 | 1888.986 | 47.22% | 95% | 0% | -35.4691 | 522.6513 | -2750 | -200 | -2427.3487 | 60.68% | 47.83% | 95% | 0% | 1710 | -31
[5 empty] | 2019-09-18 | 3 | 6240.5 | 1647 | -30 | 0 | 0 | 1677 | 506.4303 | 506.4303 | 506.4303 | 908.986 | 780 | 200 | 1888.986 | 47.22% | 95% | 0% | -34.3249 | 472.1054 | -2750 | -200 | -2477.8946 | 61.95% | 47.83% | 95% | 0% | 1677 | -30
[5 empty] | 2019-09-18 | 4 | 6241 | 1634 | -29 | 0 | 0 | 1663 | 484.5012 | 484.5012 | 484.5012 | 907.4196 | 780 | 200 | 1887.4196 | 47.19% | 95% | 0% | -33.1808 | 451.3205 | -2750 | -200 | -2498.6795 | 62.47% | 47.83% | 95% | 0% | 1663 | -29
[5 empty] | 2019-09-18 | 5 | 6241.5 | 1612 | -29 | 0 | 0 | 1641 | 450.0412 | 450.0412 | 450.0412 | 907.4196 | 780 | 200 | 1887.4196 | 47.19% | 95% | 0% | -33.1808 | 416.8604 | -2750 | -200 | -2533.1396 | 63.33% | 47.82% | 95% | 0% | 1641 | -29
[5 empty] | 2019-09-18 | 6 | 6242 | 1594 | -28 | 0 | 0 | 1622 | 420.2803 | 420.2803 | 420.2803 | 907.4196 | 780 | 200 | 1887.4196 | 47.19% | 95% | 0% | -32.0366 | 388.2437 | -2750 | -200 | -2561.7563 | 64.04% | 47.82% | 95% | 0% | 1622 | -28
[5 empty] | 2019-09-18 | 7 | 6242.5 | 1584 | -28 | 0 | 0 | 1612 | 404.6167 | 404.6167 | 404.6167 | 907.4196 | 780 | 200 | 1887.4196 | 47.19% | 95% | 0% | -32.0366 | 372.58 | -2750 | -200 | -2577.42 | 64.44% | 47.82% | 95% | 0% | 1612 | -28
[5 empty] | 2019-09-18 | 8 | 6243 | 1582 | -27 | 0 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 907.4196 | 780 | 200 | 1887.4196 | 47.19% | 95% | 0% | -30.8924 | 369.0251 | -2750 | -200 | -2580.9749 | 64.52% | 47.81% | 95% | 0% | 1609 | -27
[5 empty] | 2019-09-18 | 9 | 6243.5 | 1590 | -27 | 0 | 0 | 1617 | 412.4485 | 412.4485 | 412.4485 | 907.4196 | 780 | 200 | 1887.4196 | 47.19% | 95% | 0% | -30.8924 | 381.556 | -2750 | -200 | -2568.444 | 64.21% | 47.8% | 95% | 0% | 1617 | -27
[5 empty] | 2019-09-18 | 10 | 6244 | 1603 | -28 | 1 | 0 | 1631 | 434.3776 | 434.3776 | 434.3776 | 907.4196 | 780 | 200 | 1887.4196 | 47.19% | 95% | 0% | -32.0366 | 402.341 | -3550 | -400 | -3547.659 | 88.69% | 47.8% | 95% | 0% | 1631 | -28
[5 empty] | 2019-09-18 | 11 | 6244.5 | 1662 | -28 | 1 | 0 | 1690 | 526.7931 | 526.7931 | 526.7931 | 907.4196 | 780 | 200 | 1887.4196 | 47.19% | 95% | 0% | -32.0366 | 494.7565 | -3550 | -400 | -3455.2435 | 86.38% | 47.8% | 95% | 0% | 1690 | -28
[5 empty] | 2019-09-18 | 12 | 6245 | 1752 | -29 | 1 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 905.8533 | 780 | 200 | 1885.8533 | 47.15% | 95% | 0% | -33.1808 | 636.1515 | -3550 | -400 | -3313.8485 | 82.85% | 47.8% | 95% | 0% | 1781 | -29
[5 empty] | 2019-09-18 | 13 | 6245.5 | 1958 | -29 | 1 | 0 | 1987 | 992.0033 | 992.0033 | 992.0033 | 905.8533 | 780 | 200 | 1885.8533 | 47.15% | 95% | 0% | -33.1808 | 958.8225 | -3550 | -400 | -2991.1775 | 74.78% | 47.8% | 95% | 0% | 1987 | -29
[5 empty] | 2019-09-18 | 14 | 6246 | 2153 | -31 | 1 | 0 | 2184 | 1300.5771 | 1300.5771 | 1300.5771 | 905.8533 | 780 | 200 | 1885.8533 | 47.15% | 95% | 0% | -35.4691 | 1265.108 | -3550 | -400 | -2684.892 | 67.12% | 47.8% | 95% | 0% | 2184 | -31
[5 empty] | 2019-09-18 | 15 | 6246.5 | 2324 | -52 | 1 | 0 | 2376 | 1601.319 | 1601.319 | 1601.319 | 905.8533 | 780 | 200 | 1885.8533 | 47.15% | 95% | 0% | -59.4966 | 1541.8225 | -3550 | -400 | -2408.1775 | 60.2% | 47.79% | 95% | 0% | 2376 | -52
[5 empty] | 2019-09-18 | 16 | 6247 | 2368 | -104 | 1 | 0 | 2472 | 1751.69 | 1751.69 | 1751.69 | 905.8533 | 780 | 200 | 1885.8533 | 47.15% | 95% | 0% | -118.9931 | 1632.6969 | -3550 | -400 | -2317.3031 | 57.93% | 47.79% | 95% | 0% | 2472 | -104
[5 empty] | 2019-09-18 | 17 | 6247.5 | 2294 | -166 | 1 | 0 | 2460 | 1732.8937 | 1732.8937 | 1732.8937 | 905.8533 | 780 | 200 | 1885.8533 | 47.15% | 95% | 0% | -189.9314 | 1542.9623 | -3550 | -400 | -2407.0377 | 60.18% | 47.79% | 95% | 0% | 2460 | -166
[5 empty] | 2019-09-18 | 18 | 6248 | 2188 | -233 | 1 | 0 | 2421 | 1671.8054 | 1671.8054 | 1671.8054 | 904.2869 | 780 | 200 | 1884.2869 | 47.11% | 95% | 0% | -266.5904 | 1405.2151 | -3550 | -400 | -2544.7849 | 63.62% | 47.78% | 95% | 0% | 2421 | -233
[5 empty] | 2019-09-18 | 19 | 6248.5 | 2089 | -304 | 1 | 0 | 2393 | 1627.9472 | 1627.9472 | 1627.9472 | 904.2869 | 780 | 200 | 1884.2869 | 47.11% | 95% | 0% | -347.8261 | 1280.1212 | -3550 | -400 | -2669.8788 | 66.75% | 47.78% | 95% | 0% | 2393 | -304
[5 empty] | 2019-09-18 | 20 | 6249 | 1981 | -381 | 1 | 0 | 2362 | 1579.3899 | 1579.3899 | 1579.3899 | 904.2869 | 780 | 200 | 1884.2869 | 47.11% | 95% | 0% | -435.9268 | 1143.4632 | -3550 | -400 | -2806.5368 | 70.16% | 47.77% | 95% | 0% | 2362 | -381
[5 empty] | 2019-09-18 | 21 | 6249.5 | 1879 | -442 | 1 | 0 | 2321 | 1515.169 | 1515.169 | 1515.169 | 904.2869 | 780 | 200 | 1884.2869 | 47.11% | 95% | 0% | -505.7208 | 1009.4482 | -3550 | -400 | -2940.5518 | 73.51% | 47.77% | 95% | 0% | 2321 | -442
[5 empty] | 2019-09-18 | 22 | 6250 | 1807 | -490 | 1 | 0 | 2297 | 1477.5763 | 1477.5763 | 1477.5763 | 904.2869 | 780 | 200 | 1884.2869 | 47.11% | 95% | 0% | -560.6407 | 916.9355 | -3550 | -400 | -3033.0645 | 75.83% | 47.77% | 95% | 0% | 2297 | -490
[5 empty] | 2019-09-18 | 23 | 6250.5 | 1750 | -529 | 1 | 0 | 2279 | 1449.3817 | 1449.3817 | 1449.3817 | 904.2869 | 780 | 200 | 1884.2869 | 47.11% | 95% | 0% | -605.2632 | 844.1185 | -3550 | -400 | -3105.8815 | 77.65% | 47.77% | 95% | 0% | 2279 | -529
[5 empty] | 2019-09-18 | 24 | 6251 | 1689 | -560 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 904.2869 | 780 | 200 | 1884.2869 | 47.11% | 95% | 0% | -640.7323 | 761.6585 | -3550 | -400 | -3188.3415 | 79.71% | 47.76% | 95% | 0% | 2249 | -560
[5 empty] | 2019-09-18 | 25 | 6251.5 | 1684 | -572 | 1 | 0 | 2256 | 1413.3553 | 1413.3553 | 1413.3553 | 904.2869 | 780 | 200 | 1884.2869 | 47.11% | 95% | 0% | -654.4622 | 758.8931 | -3550 | -400 | -3191.1069 | 79.78% | 47.76% | 95% | 0% | 2256 | -572
[5 empty] | 2019-09-18 | 26 | 6252 | 1649 | -580 | 1 | 0 | 2229 | 1371.0635 | 1371.0635 | 1371.0635 | 904.2869 | 780 | 200 | 1884.2869 | 47.11% | 95% | 0% | -663.6156 | 707.4479 | -3550 | -400 | -3242.5521 | 81.06% | 47.75% | 95% | 0% | 2229 | -580
[5 empty] | 2019-09-18 | 27 | 6252.5 | 1596 | -586 | 1 | 0 | 2182 | 1297.4444 | 1297.4444 | 1297.4444 | 902.7205 | 780 | 200 | 1882.7205 | 47.07% | 95% | 0% | -670.4805 | 626.9638 | -3550 | -400 | -3323.0362 | 83.08% | 47.75% | 95% | 0% | 2182 | -586
[5 empty] | 2019-09-18 | 28 | 6253 | 1583 | -585 | 1 | 0 | 2168 | 1275.5153 | 1275.5153 | 1275.5153 | 902.7205 | 780 | 200 | 1882.7205 | 47.07% | 95% | 0% | -669.3364 | 606.1789 | -3550 | -400 | -3343.8211 | 83.6% | 47.75% | 95% | 0% | 2168 | -585
[5 empty] | 2019-09-18 | 29 | 6253.5 | 1600 | -568 | 1 | 0 | 2168 | 1275.5153 | 1275.5153 | 1275.5153 | 902.7205 | 780 | 200 | 1882.7205 | 47.07% | 95% | 0% | -649.8856 | 625.6297 | -3550 | -400 | -3324.3703 | 83.11% | 47.75% | 95% | 0% | 2168 | -568
[5 empty] | 2019-09-18 | 30 | 6254 | 1641 | -522 | 1 | 0 | 2163 | 1267.6834 | 1267.6834 | 1267.6834 | 902.7205 | 780 | 200 | 1882.7205 | 47.07% | 95% | 0% | -597.254 | 670.4294 | -3550 | -400 | -3279.5706 | 81.99% | 47.73% | 95% | 0% | 2163 | -522
[5 empty] | 2019-09-18 | 31 | 6254.5 | 1723 | -469 | 1 | 0 | 2192 | 1313.108 | 1313.108 | 1313.108 | 902.7205 | 780 | 200 | 1882.7205 | 47.07% | 95% | 0% | -536.6133 | 776.4947 | -3550 | -400 | -3173.5053 | 79.34% | 47.72% | 95% | 0% | 2192 | -469
[5 empty] | 2019-09-18 | 32 | 6255 | 1861 | -415 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 902.7205 | 780 | 200 | 1882.7205 | 47.07% | 95% | 0% | -474.8284 | 969.8542 | -3550 | -400 | -2980.1458 | 74.5% | 47.71% | 95% | 0% | 2276 | -415
[5 empty] | 2019-09-18 | 33 | 6255.5 | 2015 | -350 | 1 | 0 | 2365 | 1584.089 | 1584.089 | 1584.089 | 902.7205 | 780 | 200 | 1882.7205 | 47.07% | 95% | 0% | -400.4577 | 1183.6314 | -3550 | -400 | -2766.3686 | 69.16% | 47.71% | 95% | 0% | 2365 | -350
[5 empty] | 2019-09-18 | 34 | 6256 | 2177 | -292 | 1 | 0 | 2469 | 1746.9909 | 1746.9909 | 1746.9909 | 902.7205 | 780 | 200 | 1882.7205 | 47.07% | 95% | 0% | -334.0961 | 1412.8948 | -3550 | -400 | -2537.1052 | 63.43% | 47.71% | 95% | 0% | 2469 | -292
[5 empty] | 2019-09-18 | 35 | 6256.5 | 2334 | -222 | 1 | 0 | 2556 | 1883.2646 | 1883.2646 | 1883.2646 | 902.7205 | 780 | 200 | 1882.7205 | 47.07% | 95% | 0% | -254.0046 | 1629.2601 | -3550 | -400 | -2320.7399 | 58.02% | 47.7% | 95% | 0% | 2556 | -222
[5 empty] | 2019-09-18 | 36 | 6257 | 2438 | -153 | 1 | 0 | 2591 | 1938.0874 | 1938.0874 | 1938.0874 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -175.0572 | 1763.0302 | -3550 | -400 | -2186.9698 | 54.67% | 47.68% | 95% | 0% | 2591 | -153
[5 empty] | 2019-09-18 | 37 | 6257.5 | 2558 | -94 | 1 | 0 | 2652 | 2033.6356 | 2033.6356 | 2033.6356 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -107.5515 | 1926.0841 | -3550 | -400 | -2023.9159 | 50.6% | 47.68% | 95% | 0% | 2652 | -94
[5 empty] | 2019-09-18 | 38 | 6258 | 2639 | -49 | 1 | 0 | 2688 | 2090.0247 | 2090.0247 | 2090.0247 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -56.0641 | 2033.9607 | -3550 | -400 | -1916.0393 | 47.9% | 47.68% | 95% | 0% | 2688 | -49
[5 empty] | 2019-09-18 | 39 | 6258.5 | 2683 | -35 | 1 | 0 | 2718 | 2137.0157 | 2137.0157 | 2137.0157 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -40.0458 | 2096.9699 | -3550 | -400 | -1853.0301 | 46.33% | 47.68% | 95% | 0% | 2718 | -35
[5 empty] | 2019-09-18 | 40 | 6259 | 2709 | -33 | 1 | 0 | 2742 | 2174.6084 | 2174.6084 | 2174.6084 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -37.7574 | 2136.851 | -3550 | -400 | -1813.149 | 45.33% | 47.68% | 95% | 0% | 2742 | -33
[5 empty] | 2019-09-18 | 41 | 6259.5 | 2668 | -32 | 0 | 0 | 2700 | 2108.8211 | 2108.8211 | 2108.8211 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -36.6133 | 2072.2078 | -2750 | -200 | -877.7922 | 21.94% | 47.67% | 95% | 0% | 2700 | -32
[5 empty] | 2019-09-18 | 42 | 6260 | 2604 | -31 | 0 | 0 | 2635 | 2007.0074 | 2007.0074 | 2007.0074 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -35.4691 | 1971.5383 | -2750 | -200 | -978.4617 | 24.46% | 47.67% | 95% | 0% | 2635 | -31
[5 empty] | 2019-09-18 | 43 | 6260.5 | 2507 | -31 | 0 | 0 | 2538 | 1855.0701 | 1855.0701 | 1855.0701 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -35.4691 | 1819.601 | -2750 | -200 | -1130.399 | 28.26% | 47.67% | 95% | 0% | 2538 | -31
[5 empty] | 2019-09-18 | 44 | 6261 | 2368 | -30 | 0 | 0 | 2398 | 1635.7791 | 1635.7791 | 1635.7791 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -34.3249 | 1601.4541 | -2750 | -200 | -1348.5459 | 33.71% | 47.67% | 95% | 0% | 2398 | -30
[5 empty] | 2019-09-18 | 45 | 6261.5 | 2228 | -30 | 0 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -34.3249 | 1382.1631 | -2750 | -200 | -1567.8369 | 39.2% | 47.67% | 95% | 0% | 2258 | -30
[5 empty] | 2019-09-18 | 46 | 6262 | 2095 | -29 | 0 | 0 | 2124 | 1206.5952 | 1206.5952 | 1206.5952 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -33.1808 | 1173.4144 | -2750 | -200 | -1776.5856 | 44.41% | 47.66% | 95% | 0% | 2124 | -29
[5 empty] | 2019-09-18 | 47 | 6262.5 | 1952 | -29 | 0 | 0 | 1981 | 982.6051 | 982.6051 | 982.6051 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -33.1808 | 949.4243 | -2750 | -200 | -2000.5757 | 50.01% | 47.66% | 95% | 0% | 1981 | -29
[5 empty] | 2019-09-18 | 48 | 6263 | 1835 | -29 | 0 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -33.1808 | 766.1597 | -2750 | -200 | -2183.8403 | 54.6% | 47.66% | 95% | 0% | 1864 | -29
[5 empty] | 2019-09-19 | 1 | 6263.5 | 1753 | -29 | 0 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 901.1542 | 780 | 200 | 1881.1542 | 47.03% | 95% | 0% | -33.1808 | 637.7178 | -2750 | -200 | -2312.2822 | 57.81% | 47.66% | 95% | 0% | 1782 | -29
[5 empty] | 2019-09-19 | 2 | 6264 | 1706 | -28 | 0 | 0 | 1734 | 595.7131 | 595.7131 | 595.7131 | 899.5878 | 780 | 200 | 1879.5878 | 46.99% | 95% | 0% | -32.0366 | 563.6765 | -2750 | -200 | -2386.3235 | 59.66% | 47.66% | 95% | 0% | 1734 | -28
[5 empty] | 2019-09-19 | 3 | 6264.5 | 1666 | -28 | 0 | 0 | 1694 | 533.0585 | 533.0585 | 533.0585 | 899.5878 | 780 | 200 | 1879.5878 | 46.99% | 95% | 0% | -32.0366 | 501.0219 | -2750 | -200 | -2448.9781 | 61.22% | 47.65% | 95% | 0% | 1694 | -28
[5 empty] | 2019-09-19 | 4 | 6265 | 1658 | -28 | 0 | 0 | 1686 | 520.5276 | 520.5276 | 520.5276 | 899.5878 | 780 | 200 | 1879.5878 | 46.99% | 95% | 0% | -32.0366 | 488.491 | -2750 | -200 | -2461.509 | 61.54% | 47.65% | 95% | 0% | 1686 | -28
[5 empty] | 2019-09-19 | 5 | 6265.5 | 1643 | -28 | 0 | 0 | 1671 | 497.0322 | 497.0322 | 497.0322 | 899.5878 | 780 | 200 | 1879.5878 | 46.99% | 95% | 0% | -32.0366 | 464.9955 | -2750 | -200 | -2485.0045 | 62.13% | 47.65% | 95% | 0% | 1671 | -28
[5 empty] | 2019-09-19 | 6 | 6266 | 1619 | -28 | 0 | 0 | 1647 | 459.4394 | 459.4394 | 459.4394 | 899.5878 | 780 | 200 | 1879.5878 | 46.99% | 95% | 0% | -32.0366 | 427.4028 | -2750 | -200 | -2522.5972 | 63.06% | 47.64% | 95% | 0% | 1647 | -28
[5 empty] | 2019-09-19 | 7 | 6266.5 | 1601 | -28 | 0 | 0 | 1629 | 431.2448 | 431.2448 | 431.2448 | 899.5878 | 780 | 200 | 1879.5878 | 46.99% | 95% | 0% | -32.0366 | 399.2082 | -2750 | -200 | -2550.7918 | 63.77% | 47.64% | 95% | 0% | 1629 | -28
[5 empty] | 2019-09-19 | 8 | 6267 | 1595 | -28 | 0 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 899.5878 | 780 | 200 | 1879.5878 | 46.99% | 95% | 0% | -32.0366 | 389.81 | -2750 | -200 | -2560.19 | 64% | 47.64% | 95% | 0% | 1623 | -28
[5 empty] | 2019-09-19 | 9 | 6267.5 | 1602 | -29 | 0 | 0 | 1631 | 434.3776 | 434.3776 | 434.3776 | 899.5878 | 780 | 200 | 1879.5878 | 46.99% | 95% | 0% | -33.1808 | 401.1968 | -2750 | -200 | -2548.8032 | 63.72% | 47.64% | 95% | 0% | 1631 | -29
[5 empty] | 2019-09-19 | 10 | 6268 | 1622 | -29 | 0 | 0 | 1651 | 465.7049 | 465.7049 | 465.7049 | 899.5878 | 780 | 200 | 1879.5878 | 46.99% | 95% | 0% | -33.1808 | 432.5241 | -2750 | -200 | -2517.4759 | 62.94% | 47.63% | 95% | 0% | 1651 | -29
[5 empty] | 2019-09-19 | 11 | 6268.5 | 1669 | -29 | 1 | 0 | 1698 | 539.324 | 539.324 | 539.324 | 899.5878 | 780 | 200 | 1879.5878 | 46.99% | 95% | 0% | -33.1808 | 506.1432 | -3550 | -400 | -3443.8568 | 86.1% | 47.63% | 95% | 0% | 1698 | -29
[5 empty] | 2019-09-19 | 12 | 6269 | 1765 | -29 | 1 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 899.5878 | 780 | 200 | 1879.5878 | 46.99% | 95% | 0% | -33.1808 | 656.5142 | -3550 | -400 | -3293.4858 | 82.34% | 47.62% | 95% | 0% | 1794 | -29
[5 empty] | 2019-09-19 | 13 | 6269.5 | 1976 | -29 | 1 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 899.5878 | 780 | 200 | 1879.5878 | 46.99% | 95% | 0% | -33.1808 | 987.0171 | -3550 | -400 | -2962.9829 | 74.07% | 47.62% | 95% | 0% | 2005 | -29
[5 empty] | 2019-09-19 | 14 | 6270 | 2153 | -31 | 1 | 0 | 2184 | 1300.5771 | 1300.5771 | 1300.5771 | 898.0214 | 780 | 200 | 1878.0214 | 46.95% | 95% | 0% | -35.4691 | 1265.108 | -3550 | -400 | -2684.892 | 67.12% | 47.62% | 95% | 0% | 2184 | -31
[5 empty] | 2019-09-19 | 15 | 6270.5 | 2365 | -51 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 898.0214 | 780 | 200 | 1878.0214 | 46.95% | 95% | 0% | -58.3524 | 1605.6212 | -3550 | -400 | -2344.3788 | 58.61% | 47.61% | 95% | 0% | 2416 | -51
[5 empty] | 2019-09-19 | 16 | 6271 | 2395 | -100 | 1 | 0 | 2495 | 1787.7164 | 1787.7164 | 1787.7164 | 898.0214 | 780 | 200 | 1878.0214 | 46.95% | 95% | 0% | -114.4165 | 1673.2999 | -3550 | -400 | -2276.7001 | 56.92% | 47.61% | 95% | 0% | 2495 | -100
[5 empty] | 2019-09-19 | 17 | 6271.5 | 2350 | -168 | 1 | 0 | 2518 | 1823.7428 | 1823.7428 | 1823.7428 | 898.0214 | 780 | 200 | 1878.0214 | 46.95% | 95% | 0% | -192.2197 | 1631.5231 | -3550 | -400 | -2318.4769 | 57.96% | 47.61% | 95% | 0% | 2518 | -168
[5 empty] | 2019-09-19 | 18 | 6272 | 2226 | -239 | 1 | 0 | 2465 | 1740.7255 | 1740.7255 | 1740.7255 | 898.0214 | 780 | 200 | 1878.0214 | 46.95% | 95% | 0% | -273.4554 | 1467.2701 | -3550 | -400 | -2482.7299 | 62.07% | 47.61% | 95% | 0% | 2465 | -239
[5 empty] | 2019-09-19 | 19 | 6272.5 | 2129 | -315 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 898.0214 | 780 | 200 | 1878.0214 | 46.95% | 95% | 0% | -360.4119 | 1347.4199 | -3550 | -400 | -2602.5801 | 65.06% | 47.6% | 95% | 0% | 2444 | -315
[5 empty] | 2019-09-19 | 20 | 6273 | 2010 | -388 | 1 | 0 | 2398 | 1635.7791 | 1635.7791 | 1635.7791 | 898.0214 | 780 | 200 | 1878.0214 | 46.95% | 95% | 0% | -443.9359 | 1191.8431 | -3550 | -400 | -2758.1569 | 68.95% | 47.6% | 95% | 0% | 2398 | -388
[5 empty] | 2019-09-19 | 21 | 6273.5 | 1861 | -455 | 1 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 898.0214 | 780 | 200 | 1878.0214 | 46.95% | 95% | 0% | -520.595 | 986.7422 | -3550 | -400 | -2963.2578 | 74.08% | 47.6% | 95% | 0% | 2316 | -455
[5 empty] | 2019-09-19 | 22 | 6274 | 1755 | -506 | 1 | 0 | 2261 | 1421.1871 | 1421.1871 | 1421.1871 | 898.0214 | 780 | 200 | 1878.0214 | 46.95% | 95% | 0% | -578.9474 | 842.2398 | -3550 | -400 | -3107.7602 | 77.69% | 47.6% | 95% | 0% | 2261 | -506
[5 empty] | 2019-09-19 | 23 | 6274.5 | 1629 | -559 | 1 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 898.0214 | 780 | 200 | 1878.0214 | 46.95% | 95% | 0% | -639.5881 | 667.2544 | -3550 | -400 | -3282.7456 | 82.07% | 47.58% | 95% | 0% | 2188 | -559
[5 empty] | 2019-09-19 | 24 | 6275 | 1558 | -605 | 1 | 0 | 2163 | 1267.6834 | 1267.6834 | 1267.6834 | 898.0214 | 780 | 200 | 1878.0214 | 46.95% | 95% | 0% | -692.2197 | 575.4637 | -3550 | -400 | -3374.5363 | 84.36% | 47.57% | 95% | 0% | 2163 | -605
[5 empty] | 2019-09-19 | 25 | 6275.5 | 1514 | -635 | 1 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 898.0214 | 780 | 200 | 1878.0214 | 46.95% | 95% | 0% | -726.5446 | 519.2097 | -3550 | -400 | -3430.7903 | 85.77% | 47.57% | 95% | 0% | 2149 | -635
[5 empty] | 2019-09-19 | 26 | 6276 | 1486 | -648 | 1 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 896.4551 | 780 | 200 | 1876.4551 | 46.91% | 95% | 0% | -741.4188 | 480.8401 | -3550 | -400 | -3469.1599 | 86.73% | 47.57% | 95% | 0% | 2134 | -648
[5 empty] | 2019-09-19 | 27 | 6276.5 | 1479 | -647 | 1 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 896.4551 | 780 | 200 | 1876.4551 | 46.91% | 95% | 0% | -740.2746 | 469.4533 | -3550 | -400 | -3480.5467 | 87.01% | 47.56% | 95% | 0% | 2126 | -647
[5 empty] | 2019-09-19 | 28 | 6277 | 1471 | -635 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 896.4551 | 780 | 200 | 1876.4551 | 46.91% | 95% | 0% | -726.5446 | 451.856 | -3550 | -400 | -3498.144 | 87.45% | 47.56% | 95% | 0% | 2106 | -635
[5 empty] | 2019-09-19 | 29 | 6277.5 | 1503 | -609 | 1 | 0 | 2112 | 1187.7988 | 1187.7988 | 1187.7988 | 896.4551 | 780 | 200 | 1876.4551 | 46.91% | 95% | 0% | -696.7963 | 491.0025 | -3550 | -400 | -3458.9975 | 86.47% | 47.55% | 95% | 0% | 2112 | -609
[5 empty] | 2019-09-19 | 30 | 6278 | 1542 | -572 | 1 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 896.4551 | 780 | 200 | 1876.4551 | 46.91% | 95% | 0% | -654.4622 | 536.4693 | -3550 | -400 | -3413.5307 | 85.34% | 47.53% | 95% | 0% | 2114 | -572
[5 empty] | 2019-09-19 | 31 | 6278.5 | 1619 | -520 | 1 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 896.4551 | 780 | 200 | 1876.4551 | 46.91% | 95% | 0% | -594.9657 | 635.125 | -3550 | -400 | -3314.875 | 82.87% | 47.53% | 95% | 0% | 2139 | -520
[5 empty] | 2019-09-19 | 32 | 6279 | 1743 | -459 | 1 | 0 | 2202 | 1328.7716 | 1328.7716 | 1328.7716 | 896.4551 | 780 | 200 | 1876.4551 | 46.91% | 95% | 0% | -525.1716 | 803.6 | -3550 | -400 | -3146.4 | 78.66% | 47.52% | 95% | 0% | 2202 | -459
[5 empty] | 2019-09-19 | 33 | 6279.5 | 1908 | -395 | 1 | 0 | 2303 | 1486.9744 | 1486.9744 | 1486.9744 | 896.4551 | 780 | 200 | 1876.4551 | 46.91% | 95% | 0% | -451.9451 | 1035.0294 | -3550 | -400 | -2914.9706 | 72.87% | 47.52% | 95% | 0% | 2303 | -395
[5 empty] | 2019-09-19 | 34 | 6280 | 2072 | -322 | 1 | 0 | 2394 | 1629.5136 | 1629.5136 | 1629.5136 | 896.4551 | 780 | 200 | 1876.4551 | 46.91% | 95% | 0% | -368.4211 | 1261.0926 | -3550 | -400 | -2688.9074 | 67.22% | 47.52% | 95% | 0% | 2394 | -322
[5 empty] | 2019-09-19 | 35 | 6280.5 | 2252 | -247 | 1 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 896.4551 | 780 | 200 | 1876.4551 | 46.91% | 95% | 0% | -282.6087 | 1511.3732 | -3550 | -400 | -2438.6268 | 60.97% | 47.51% | 95% | 0% | 2499 | -247
[5 empty] | 2019-09-19 | 36 | 6281 | 2376 | -172 | 1 | 0 | 2548 | 1870.7337 | 1870.7337 | 1870.7337 | 896.4551 | 780 | 200 | 1876.4551 | 46.91% | 95% | 0% | -196.7963 | 1673.9374 | -3550 | -400 | -2276.0626 | 56.9% | 47.5% | 95% | 0% | 2548 | -172
[5 empty] | 2019-09-19 | 37 | 6281.5 | 2504 | -104 | 1 | 0 | 2608 | 1964.7156 | 1964.7156 | 1964.7156 | 896.4551 | 780 | 200 | 1876.4551 | 46.91% | 95% | 0% | -118.9931 | 1845.7224 | -3550 | -400 | -2104.2776 | 52.61% | 47.5% | 95% | 0% | 2608 | -104
[5 empty] | 2019-09-19 | 38 | 6282 | 2584 | -55 | 1 | 0 | 2639 | 2013.2729 | 2013.2729 | 2013.2729 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -62.9291 | 1950.3438 | -3550 | -400 | -1999.6562 | 49.99% | 47.5% | 95% | 0% | 2639 | -55
[5 empty] | 2019-09-19 | 39 | 6282.5 | 2649 | -38 | 1 | 0 | 2687 | 2088.4584 | 2088.4584 | 2088.4584 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -43.4783 | 2044.9801 | -3550 | -400 | -1905.0199 | 47.63% | 47.5% | 95% | 0% | 2687 | -38
[5 empty] | 2019-09-19 | 40 | 6283 | 2701 | -38 | 1 | 0 | 2739 | 2169.9093 | 2169.9093 | 2169.9093 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -43.4783 | 2126.4311 | -3550 | -400 | -1823.5689 | 45.59% | 47.49% | 95% | 0% | 2739 | -38
[5 empty] | 2019-09-19 | 41 | 6283.5 | 2665 | -39 | 0 | 0 | 2704 | 2115.0866 | 2115.0866 | 2115.0866 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -44.6224 | 2070.4641 | -2750 | -200 | -879.5359 | 21.99% | 47.49% | 95% | 0% | 2704 | -39
[5 empty] | 2019-09-19 | 42 | 6284 | 2575 | -39 | 0 | 0 | 2614 | 1974.1138 | 1974.1138 | 1974.1138 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -44.6224 | 1929.4913 | -2750 | -200 | -1020.5087 | 25.51% | 47.49% | 95% | 0% | 2614 | -39
[5 empty] | 2019-09-19 | 43 | 6284.5 | 2453 | -40 | 0 | 0 | 2493 | 1784.5837 | 1784.5837 | 1784.5837 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -45.7666 | 1738.8171 | -2750 | -200 | -1211.1829 | 30.28% | 47.48% | 95% | 0% | 2493 | -40
[5 empty] | 2019-09-19 | 44 | 6285 | 2321 | -42 | 0 | 0 | 2363 | 1580.9563 | 1580.9563 | 1580.9563 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -48.0549 | 1532.9014 | -2750 | -200 | -1417.0986 | 35.43% | 47.48% | 95% | 0% | 2363 | -42
[5 empty] | 2019-09-19 | 45 | 6285.5 | 2186 | -42 | 0 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -48.0549 | 1321.4422 | -2750 | -200 | -1628.5578 | 40.71% | 47.47% | 95% | 0% | 2228 | -42
[5 empty] | 2019-09-19 | 46 | 6286 | 2035 | -43 | 0 | 0 | 2078 | 1134.5425 | 1134.5425 | 1134.5425 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -49.1991 | 1085.3434 | -2750 | -200 | -1864.6566 | 46.62% | 47.45% | 95% | 0% | 2078 | -43
[5 empty] | 2019-09-19 | 47 | 6286.5 | 1896 | -43 | 0 | 0 | 1939 | 916.8178 | 916.8178 | 916.8178 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -49.1991 | 867.6187 | -2750 | -200 | -2082.3813 | 52.06% | 47.44% | 95% | 0% | 1939 | -43
[5 empty] | 2019-09-19 | 48 | 6287 | 1783 | -44 | 0 | 0 | 1827 | 741.385 | 741.385 | 741.385 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -50.3432 | 691.0417 | -2750 | -200 | -2258.9583 | 56.47% | 47.44% | 95% | 0% | 1827 | -44
[5 empty] | 2019-09-20 | 1 | 6287.5 | 1688 | -45 | 0 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -51.4874 | 542.6593 | -2750 | -200 | -2407.3407 | 60.18% | 47.44% | 95% | 0% | 1733 | -45
[5 empty] | 2019-09-20 | 2 | 6288 | 1640 | -47 | 0 | 0 | 1687 | 522.094 | 522.094 | 522.094 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -53.7757 | 468.3182 | -2750 | -200 | -2481.6818 | 62.04% | 47.44% | 95% | 0% | 1687 | -47
[5 empty] | 2019-09-20 | 3 | 6288.5 | 1619 | -46 | 0 | 0 | 1665 | 487.634 | 487.634 | 487.634 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -52.6316 | 435.0024 | -2750 | -200 | -2514.9976 | 62.87% | 47.44% | 95% | 0% | 1665 | -46
[5 empty] | 2019-09-20 | 4 | 6289 | 1606 | -46 | 1 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -52.6316 | 414.6396 | -3550 | -400 | -3535.3604 | 88.38% | 47.43% | 95% | 0% | 1652 | -46
[5 empty] | 2019-09-20 | 5 | 6289.5 | 1581 | -45 | 1 | 0 | 1626 | 426.5458 | 426.5458 | 426.5458 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -51.4874 | 375.0583 | -3550 | -400 | -3574.9417 | 89.37% | 47.42% | 95% | 0% | 1626 | -45
[5 empty] | 2019-09-20 | 6 | 6290 | 1564 | -43 | 1 | 0 | 1607 | 396.7848 | 396.7848 | 396.7848 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -49.1991 | 347.5857 | -3550 | -400 | -3602.4143 | 90.06% | 47.42% | 95% | 0% | 1607 | -43
[5 empty] | 2019-09-20 | 7 | 6290.5 | 1544 | -43 | 1 | 0 | 1587 | 365.4575 | 365.4575 | 365.4575 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -49.1991 | 316.2585 | -3550 | -400 | -3633.7415 | 90.84% | 47.42% | 95% | 0% | 1587 | -43
[5 empty] | 2019-09-20 | 8 | 6291 | 1541 | -43 | 1 | 0 | 1584 | 360.7585 | 360.7585 | 360.7585 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -49.1991 | 311.5594 | -3550 | -400 | -3638.4406 | 90.96% | 47.42% | 95% | 0% | 1584 | -43
[5 empty] | 2019-09-20 | 9 | 6291.5 | 1546 | -45 | 1 | 0 | 1591 | 371.723 | 371.723 | 371.723 | 894.8887 | 780 | 200 | 1874.8887 | 46.87% | 95% | 0% | -51.4874 | 320.2356 | -3550 | -400 | -3629.7644 | 90.74% | 47.42% | 95% | 0% | 1591 | -45
[5 empty] | 2019-09-20 | 10 | 6292 | 1557 | -47 | 1 | 0 | 1604 | 392.0857 | 392.0857 | 392.0857 | 893.3223 | 780 | 200 | 1873.3223 | 46.83% | 95% | 0% | -53.7757 | 338.31 | -3550 | -400 | -3611.69 | 90.29% | 47.41% | 95% | 0% | 1604 | -47
[5 empty] | 2019-09-20 | 11 | 6292.5 | 1604 | -49 | 1 | 0 | 1653 | 468.8376 | 468.8376 | 468.8376 | 893.3223 | 780 | 200 | 1873.3223 | 46.83% | 95% | 0% | -56.0641 | 412.7735 | -3550 | -400 | -3537.2265 | 88.43% | 47.41% | 95% | 0% | 1653 | -49
[5 empty] | 2019-09-20 | 12 | 6293 | 1690 | -52 | 1 | 0 | 1742 | 608.244 | 608.244 | 608.244 | 893.3223 | 780 | 200 | 1873.3223 | 46.83% | 95% | 0% | -59.4966 | 548.7475 | -3550 | -400 | -3401.2525 | 85.03% | 47.4% | 95% | 0% | 1742 | -52
[5 empty] | 2019-09-20 | 13 | 6293.5 | 1906 | -53 | 1 | 0 | 1959 | 948.1451 | 948.1451 | 948.1451 | 893.3223 | 780 | 200 | 1873.3223 | 46.83% | 95% | 0% | -60.6407 | 887.5044 | -3550 | -400 | -3062.4956 | 76.56% | 47.4% | 95% | 0% | 1959 | -53
[5 empty] | 2019-09-20 | 14 | 6294 | 2074 | -55 | 1 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 893.3223 | 780 | 200 | 1873.3223 | 46.83% | 95% | 0% | -62.9291 | 1151.498 | -3550 | -400 | -2798.502 | 69.96% | 47.4% | 95% | 0% | 2129 | -55
[5 empty] | 2019-09-20 | 15 | 6294.5 | 2278 | -73 | 1 | 0 | 2351 | 1562.1599 | 1562.1599 | 1562.1599 | 893.3223 | 780 | 200 | 1873.3223 | 46.83% | 95% | 0% | -83.524 | 1478.6359 | -3550 | -400 | -2471.3641 | 61.78% | 47.38% | 95% | 0% | 2351 | -73
[5 empty] | 2019-09-20 | 16 | 6295 | 2304 | -129 | 1 | 0 | 2433 | 1690.6018 | 1690.6018 | 1690.6018 | 893.3223 | 780 | 200 | 1873.3223 | 46.83% | 95% | 0% | -147.5973 | 1543.0046 | -3550 | -400 | -2406.9954 | 60.17% | 47.38% | 95% | 0% | 2433 | -129
[5 empty] | 2019-09-20 | 17 | 6295.5 | 2254 | -199 | 1 | 0 | 2453 | 1721.9291 | 1721.9291 | 1721.9291 | 893.3223 | 780 | 200 | 1873.3223 | 46.83% | 95% | 0% | -227.6888 | 1494.2403 | -3550 | -400 | -2455.7597 | 61.39% | 47.38% | 95% | 0% | 2453 | -199
[5 empty] | 2019-09-20 | 18 | 6296 | 2148 | -273 | 1 | 0 | 2421 | 1671.8054 | 1671.8054 | 1671.8054 | 893.3223 | 780 | 200 | 1873.3223 | 46.83% | 95% | 0% | -312.357 | 1359.4485 | -3550 | -400 | -2590.5515 | 64.76% | 47.37% | 95% | 0% | 2421 | -273
[5 empty] | 2019-09-20 | 19 | 6296.5 | 2010 | -347 | 1 | 0 | 2357 | 1571.5581 | 1571.5581 | 1571.5581 | 893.3223 | 780 | 200 | 1873.3223 | 46.83% | 95% | 0% | -397.0252 | 1174.5329 | -3550 | -400 | -2775.4671 | 69.39% | 47.36% | 95% | 0% | 2357 | -347
[5 empty] | 2019-09-20 | 20 | 6297 | 1883 | -424 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 891.756 | 780 | 200 | 1871.756 | 46.79% | 95% | 0% | -485.1259 | 1008.114 | -3550 | -400 | -2941.886 | 73.55% | 47.35% | 95% | 0% | 2307 | -424
[5 empty] | 2019-09-20 | 21 | 6297.5 | 1735 | -497 | 1 | 0 | 2232 | 1375.7626 | 1375.7626 | 1375.7626 | 891.756 | 780 | 200 | 1871.756 | 46.79% | 95% | 0% | -568.6499 | 807.1127 | -3550 | -400 | -3142.8873 | 78.57% | 47.35% | 95% | 0% | 2232 | -497
[5 empty] | 2019-09-20 | 22 | 6298 | 1671 | -526 | 1 | 0 | 2197 | 1320.9398 | 1320.9398 | 1320.9398 | 891.756 | 780 | 200 | 1871.756 | 46.79% | 95% | 0% | -601.8307 | 719.1092 | -3550 | -400 | -3230.8908 | 80.77% | 47.34% | 95% | 0% | 2197 | -526
[5 empty] | 2019-09-20 | 23 | 6298.5 | 1576 | -575 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 891.756 | 780 | 200 | 1871.756 | 46.79% | 95% | 0% | -657.8947 | 590.9923 | -3550 | -400 | -3359.0077 | 83.98% | 47.34% | 95% | 0% | 2151 | -575
[5 empty] | 2019-09-20 | 24 | 6299 | 1487 | -633 | 1 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 891.756 | 780 | 200 | 1871.756 | 46.79% | 95% | 0% | -724.2563 | 476.0735 | -3550 | -400 | -3473.9265 | 86.85% | 47.34% | 95% | 0% | 2120 | -633
[5 empty] | 2019-09-20 | 25 | 6299.5 | 1430 | -665 | 1 | 0 | 2095 | 1161.1707 | 1161.1707 | 1161.1707 | 891.756 | 780 | 200 | 1871.756 | 46.79% | 95% | 0% | -760.8696 | 400.3011 | -3550 | -400 | -3549.6989 | 88.74% | 47.33% | 95% | 0% | 2095 | -665
[5 empty] | 2019-09-20 | 26 | 6300 | 1354 | -705 | 1 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 891.756 | 780 | 200 | 1871.756 | 46.79% | 95% | 0% | -806.6362 | 298.1454 | -3550 | -400 | -3651.8546 | 91.3% | 47.33% | 95% | 0% | 2059 | -705
[5 empty] | 2019-09-20 | 27 | 6300.5 | 1293 | -719 | 1 | 0 | 2012 | 1031.1624 | 1031.1624 | 1031.1624 | 891.756 | 780 | 200 | 1871.756 | 46.79% | 95% | 0% | -822.6545 | 208.5079 | -3550 | -400 | -3741.4921 | 93.54% | 47.33% | 95% | 0% | 2012 | -719
[5 empty] | 2019-09-20 | 28 | 6301 | 1264 | -713 | 1 | 0 | 1977 | 976.3397 | 976.3397 | 976.3397 | 891.756 | 780 | 200 | 1871.756 | 46.79% | 95% | 0% | -815.7895 | 160.5502 | -3550 | -400 | -3789.4498 | 94.74% | 47.33% | 95% | 0% | 1977 | -713
[5 empty] | 2019-09-20 | 29 | 6301.5 | 1271 | -691 | 1 | 0 | 1962 | 952.8442 | 952.8442 | 952.8442 | 891.756 | 780 | 200 | 1871.756 | 46.79% | 95% | 0% | -790.6178 | 162.2263 | -3550 | -400 | -3787.7737 | 94.69% | 47.33% | 95% | 0% | 1962 | -691
[5 empty] | 2019-09-20 | 30 | 6302 | 1289 | -655 | 1 | 0 | 1944 | 924.6496 | 924.6496 | 924.6496 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -749.4279 | 175.2217 | -3550 | -400 | -3774.7783 | 94.37% | 47.33% | 95% | 0% | 1944 | -655
[5 empty] | 2019-09-20 | 31 | 6302.5 | 1341 | -609 | 1 | 0 | 1950 | 934.0478 | 934.0478 | 934.0478 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -696.7963 | 237.2515 | -3550 | -400 | -3712.7485 | 92.82% | 47.32% | 95% | 0% | 1950 | -609
[5 empty] | 2019-09-20 | 32 | 6303 | 1460 | -551 | 1 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -630.4348 | 399.1613 | -3550 | -400 | -3550.8387 | 88.77% | 47.32% | 95% | 0% | 2011 | -551
[5 empty] | 2019-09-20 | 33 | 6303.5 | 1593 | -483 | 1 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -552.6316 | 578.7781 | -3550 | -400 | -3371.2219 | 84.28% | 47.32% | 95% | 0% | 2076 | -483
[5 empty] | 2019-09-20 | 34 | 6304 | 1751 | -409 | 1 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -467.9634 | 795.0209 | -3550 | -400 | -3154.9791 | 78.87% | 47.31% | 95% | 0% | 2160 | -409
[5 empty] | 2019-09-20 | 35 | 6304.5 | 1935 | -331 | 1 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -378.7185 | 1050.3004 | -3550 | -400 | -2899.6996 | 72.49% | 47.31% | 95% | 0% | 2266 | -331
[5 empty] | 2019-09-20 | 36 | 6305 | 2097 | -255 | 1 | 0 | 2352 | 1563.7263 | 1563.7263 | 1563.7263 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -291.762 | 1271.9643 | -3550 | -400 | -2678.0357 | 66.95% | 47.31% | 95% | 0% | 2352 | -255
[5 empty] | 2019-09-20 | 37 | 6305.5 | 2219 | -185 | 1 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -211.6705 | 1433.5068 | -3550 | -400 | -2516.4932 | 62.91% | 47.31% | 95% | 0% | 2404 | -185
[5 empty] | 2019-09-20 | 38 | 6306 | 2307 | -132 | 1 | 0 | 2439 | 1700 | 1700 | 1700 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -151.0297 | 1548.9703 | -3550 | -400 | -2401.0297 | 60.03% | 47.31% | 95% | 0% | 2439 | -132
[5 empty] | 2019-09-20 | 39 | 6306.5 | 2346 | -117 | 1 | 0 | 2463 | 1737.5927 | 1737.5927 | 1737.5927 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -133.8673 | 1603.7255 | -3550 | -400 | -2346.2745 | 58.66% | 47.3% | 95% | 0% | 2463 | -117
[5 empty] | 2019-09-20 | 40 | 6307 | 2410 | -119 | 1 | 0 | 2529 | 1840.9728 | 1840.9728 | 1840.9728 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -136.1556 | 1704.8172 | -3550 | -400 | -2245.1828 | 56.13% | 47.3% | 95% | 0% | 2529 | -119
[5 empty] | 2019-09-20 | 41 | 6307.5 | 2351 | -121 | 1 | 0 | 2472 | 1751.69 | 1751.69 | 1751.69 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -138.4439 | 1613.2461 | -3550 | -400 | -2336.7539 | 58.42% | 47.3% | 95% | 0% | 2472 | -121
[5 empty] | 2019-09-20 | 42 | 6308 | 2238 | -123 | 0 | 0 | 2361 | 1577.8236 | 1577.8236 | 1577.8236 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -140.7323 | 1437.0913 | -2750 | -200 | -1512.9087 | 37.82% | 47.3% | 95% | 0% | 2361 | -123
[5 empty] | 2019-09-20 | 43 | 6308.5 | 2136 | -126 | 0 | 0 | 2262 | 1422.7535 | 1422.7535 | 1422.7535 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -144.1648 | 1278.5887 | -2750 | -200 | -1671.4113 | 41.79% | 47.3% | 95% | 0% | 2262 | -126
[5 empty] | 2019-09-20 | 44 | 6309 | 2026 | -128 | 0 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 890.1896 | 780 | 200 | 1870.1896 | 46.75% | 95% | 0% | -146.4531 | 1107.1331 | -2750 | -200 | -1842.8669 | 46.07% | 47.29% | 95% | 0% | 2154 | -128
[5 empty] | 2019-09-20 | 45 | 6309.5 | 1886 | -129 | 0 | 0 | 2015 | 1035.8615 | 1035.8615 | 1035.8615 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -147.5973 | 888.2642 | -2750 | -200 | -2061.7358 | 51.54% | 47.28% | 95% | 0% | 2015 | -129
[5 empty] | 2019-09-20 | 46 | 6310 | 1771 | -130 | 0 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -148.7414 | 708.5545 | -2750 | -200 | -2241.4455 | 56.04% | 47.28% | 95% | 0% | 1901 | -130
[5 empty] | 2019-09-20 | 47 | 6310.5 | 1643 | -130 | 0 | 0 | 1773 | 656.8013 | 656.8013 | 656.8013 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -148.7414 | 508.0599 | -2750 | -200 | -2441.9401 | 61.05% | 47.27% | 95% | 0% | 1773 | -130
[5 empty] | 2019-09-20 | 48 | 6311 | 1543 | -130 | 0 | 0 | 1673 | 500.1649 | 500.1649 | 500.1649 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -148.7414 | 351.4235 | -2750 | -200 | -2598.5765 | 64.96% | 47.27% | 95% | 0% | 1673 | -130
[5 empty] | 2019-09-21 | 1 | 6311.5 | 1457 | -129 | 0 | 0 | 1586 | 363.8912 | 363.8912 | 363.8912 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -147.5973 | 216.2939 | -2750 | -200 | -2733.7061 | 68.34% | 47.26% | 95% | 0% | 1586 | -129
[5 empty] | 2019-09-21 | 2 | 6312 | 1404 | -128 | 0 | 0 | 1532 | 279.3075 | 279.3075 | 279.3075 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -146.4531 | 132.8544 | -2750 | -200 | -2817.1456 | 70.43% | 47.26% | 95% | 0% | 1532 | -128
[5 empty] | 2019-09-21 | 3 | 6312.5 | 1360 | -129 | 0 | 0 | 1489 | 211.9538 | 211.9538 | 211.9538 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -147.5973 | 64.3566 | -2750 | -200 | -2885.6434 | 72.14% | 47.25% | 95% | 0% | 1489 | -129
[5 empty] | 2019-09-21 | 4 | 6313 | 1331 | -130 | 0 | 0 | 1461 | 168.0956 | 168.0956 | 168.0956 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -148.7414 | 19.3542 | -2750 | -200 | -2930.6458 | 73.27% | 47.24% | 95% | 0% | 1461 | -130
[5 empty] | 2019-09-21 | 5 | 6313.5 | 1305 | -131 | 0 | 0 | 1436 | 128.9365 | 128.9365 | 128.9365 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -149.8856 | -20.9491 | -2750 | -200 | -2970.9491 | 74.27% | 47.24% | 95% | 0% | 1436 | -131
[5 empty] | 2019-09-21 | 6 | 6314 | 1280 | -131 | 0 | 0 | 1411 | 89.7774 | 89.7774 | 89.7774 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -149.8856 | -60.1082 | -2750 | -200 | -3010.1082 | 75.25% | 47.23% | 95% | 0% | 1411 | -131
[5 empty] | 2019-09-21 | 7 | 6314.5 | 1261 | -132 | 0 | 0 | 1393 | 61.5829 | 61.5829 | 61.5829 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -151.0297 | -89.4469 | -2750 | -200 | -3039.4469 | 75.99% | 47.23% | 95% | 0% | 1393 | -132
[5 empty] | 2019-09-21 | 8 | 6315 | 1251 | -132 | 0 | 0 | 1383 | 45.9192 | 45.9192 | 45.9192 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -151.0297 | -105.1105 | -2750 | -200 | -3055.1105 | 76.38% | 47.23% | 95% | 0% | 1383 | -132
[5 empty] | 2019-09-21 | 9 | 6315.5 | 1242 | -133 | 0 | 0 | 1375 | 33.3883 | 33.3883 | 33.3883 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -152.1739 | -118.7856 | -2750 | -200 | -3068.7856 | 76.72% | 47.22% | 95% | 0% | 1375 | -133
[5 empty] | 2019-09-21 | 10 | 6316 | 1245 | -133 | 0 | 0 | 1378 | 38.0874 | 38.0874 | 38.0874 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -152.1739 | -114.0865 | -2750 | -200 | -3064.0865 | 76.6% | 47.21% | 95% | 0% | 1378 | -133
[5 empty] | 2019-09-21 | 11 | 6316.5 | 1276 | -134 | 0 | 0 | 1410 | 88.211 | 88.211 | 88.211 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -153.3181 | -65.107 | -2750 | -200 | -3015.107 | 75.38% | 47.2% | 95% | 0% | 1410 | -134
[5 empty] | 2019-09-21 | 12 | 6317 | 1309 | -135 | 0 | 0 | 1444 | 141.4674 | 141.4674 | 141.4674 | 888.6232 | 780 | 200 | 1868.6232 | 46.72% | 95% | 0% | -154.4622 | -12.9948 | -2750 | -200 | -2962.9948 | 74.07% | 47.2% | 95% | 0% | 1444 | -135
[5 empty] | 2019-09-21 | 13 | 6317.5 | 1416 | -137 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 887.0569 | 780 | 200 | 1867.0569 | 46.68% | 95% | 0% | -156.7506 | 155.4506 | -2750 | -200 | -2794.5494 | 69.86% | 47.2% | 95% | 0% | 1553 | -137
[5 empty] | 2019-09-21 | 14 | 6318 | 1475 | -138 | 0 | 0 | 1613 | 406.183 | 406.183 | 406.183 | 887.0569 | 780 | 200 | 1867.0569 | 46.68% | 95% | 0% | -157.8947 | 248.2883 | -2750 | -200 | -2701.7117 | 67.54% | 47.19% | 95% | 0% | 1613 | -138
[5 empty] | 2019-09-21 | 15 | 6318.5 | 1564 | -157 | 0 | 0 | 1721 | 575.3504 | 575.3504 | 575.3504 | 887.0569 | 780 | 200 | 1867.0569 | 46.68% | 95% | 0% | -179.6339 | 395.7165 | -2750 | -200 | -2554.2835 | 63.86% | 47.19% | 95% | 0% | 1721 | -157
[5 empty] | 2019-09-21 | 16 | 6319 | 1595 | -213 | 0 | 0 | 1808 | 711.6241 | 711.6241 | 711.6241 | 887.0569 | 780 | 200 | 1867.0569 | 46.68% | 95% | 0% | -243.7071 | 467.917 | -2750 | -200 | -2482.083 | 62.05% | 47.19% | 95% | 0% | 1808 | -213
[5 empty] | 2019-09-21 | 17 | 6319.5 | 1602 | -288 | 0 | 0 | 1890 | 840.066 | 840.066 | 840.066 | 887.0569 | 780 | 200 | 1867.0569 | 46.68% | 95% | 0% | -329.5195 | 510.5465 | -2750 | -200 | -2439.4535 | 60.99% | 47.19% | 95% | 0% | 1890 | -288
[5 empty] | 2019-09-21 | 18 | 6320 | 1533 | -366 | 1 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 887.0569 | 780 | 200 | 1867.0569 | 46.68% | 95% | 0% | -418.7643 | 435.3989 | -3550 | -400 | -3514.6011 | 87.87% | 47.19% | 95% | 0% | 1899 | -366
[5 empty] | 2019-09-21 | 19 | 6320.5 | 1454 | -448 | 1 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 887.0569 | 780 | 200 | 1867.0569 | 46.68% | 95% | 0% | -512.5858 | 346.2765 | -3550 | -400 | -3603.7235 | 90.09% | 47.18% | 95% | 0% | 1902 | -448
[5 empty] | 2019-09-21 | 20 | 6321 | 1346 | -528 | 1 | 0 | 1874 | 815.0041 | 815.0041 | 815.0041 | 887.0569 | 780 | 200 | 1867.0569 | 46.68% | 95% | 0% | -604.119 | 210.8851 | -3550 | -400 | -3739.1149 | 93.48% | 47.18% | 95% | 0% | 1874 | -528
[5 empty] | 2019-09-21 | 21 | 6321.5 | 1250 | -599 | 1 | 0 | 1849 | 775.845 | 775.845 | 775.845 | 887.0569 | 780 | 200 | 1867.0569 | 46.68% | 95% | 0% | -685.3547 | 90.4903 | -3550 | -400 | -3859.5097 | 96.49% | 47.18% | 95% | 0% | 1849 | -599
[5 empty] | 2019-09-21 | 22 | 6322 | 1153 | -659 | 1 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 887.0569 | 780 | 200 | 1867.0569 | 46.68% | 95% | 0% | -754.0046 | -36.115 | -3550 | -400 | -3986.115 | 99.65% | 47.17% | 95% | 0% | 1812 | -659
[5 empty] | 2019-09-21 | 23 | 6322.5 | 1038 | -712 | 1 | 0 | 1750 | 620.7749 | 620.7749 | 620.7749 | 885.4905 | 780 | 200 | 1865.4905 | 46.64% | 95% | 0% | -814.6453 | -193.8704 | -3550 | -400 | -4143.8704 | 103.6% | 47.17% | 95% | 0% | 1750 | -712
[5 empty] | 2019-09-21 | 24 | 6323 | 950 | -755 | 1 | 0 | 1705 | 550.2885 | 550.2885 | 550.2885 | 885.4905 | 780 | 200 | 1865.4905 | 46.64% | 95% | 0% | -863.8444 | -313.5559 | -3550 | -400 | -4263.5559 | 106.6% | 47.17% | 95% | 0% | 1705 | -755
[5 empty] | 2019-09-21 | 25 | 6323.5 | 885 | -777 | 1 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 885.4905 | 780 | 200 | 1865.4905 | 46.64% | 95% | 0% | -889.016 | -406.0811 | -3550 | -400 | -4356.0811 | 108.9% | 47.17% | 95% | 0% | 1662 | -777
[5 empty] | 2019-09-21 | 26 | 6324 | 851 | -788 | 1 | 0 | 1639 | 446.9085 | 446.9085 | 446.9085 | 885.4905 | 780 | 200 | 1865.4905 | 46.64% | 95% | 0% | -901.6018 | -454.6933 | -3550 | -400 | -4404.6933 | 110.1% | 47.16% | 95% | 0% | 1639 | -788
[5 empty] | 2019-09-21 | 27 | 6324.5 | 824 | -785 | 1 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 885.4905 | 780 | 200 | 1865.4905 | 46.64% | 95% | 0% | -898.1693 | -498.2518 | -3550 | -400 | -4448.2518 | 111.2% | 47.16% | 95% | 0% | 1609 | -785
[5 empty] | 2019-09-21 | 28 | 6325 | 821 | -767 | 1 | 0 | 1588 | 367.0239 | 367.0239 | 367.0239 | 885.4905 | 780 | 200 | 1865.4905 | 46.64% | 95% | 0% | -877.5744 | -510.5505 | -3550 | -400 | -4460.5505 | 111.5% | 47.14% | 95% | 0% | 1588 | -767
[5 empty] | 2019-09-21 | 29 | 6325.5 | 847 | -733 | 1 | 0 | 1580 | 354.493 | 354.493 | 354.493 | 885.4905 | 780 | 200 | 1865.4905 | 46.64% | 95% | 0% | -838.6728 | -484.1798 | -3550 | -400 | -4434.1798 | 110.9% | 47.14% | 95% | 0% | 1580 | -733
[5 empty] | 2019-09-21 | 30 | 6326 | 903 | -688 | 1 | 0 | 1591 | 371.723 | 371.723 | 371.723 | 885.4905 | 780 | 200 | 1865.4905 | 46.64% | 95% | 0% | -787.1854 | -415.4624 | -3550 | -400 | -4365.4624 | 109.1% | 47.13% | 95% | 0% | 1591 | -688
[5 empty] | 2019-09-21 | 31 | 6326.5 | 999 | -631 | 1 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 883.9242 | 780 | 200 | 1863.9242 | 46.6% | 95% | 0% | -721.968 | -289.1568 | -3550 | -400 | -4239.1568 | 106% | 47.13% | 95% | 0% | 1630 | -631
[5 empty] | 2019-09-21 | 32 | 6327 | 1095 | -559 | 1 | 0 | 1654 | 470.404 | 470.404 | 470.404 | 883.9242 | 780 | 200 | 1863.9242 | 46.6% | 95% | 0% | -639.5881 | -169.1841 | -3550 | -400 | -4119.1841 | 103% | 47.12% | 95% | 0% | 1654 | -559
[5 empty] | 2019-09-21 | 33 | 6327.5 | 1269 | -473 | 1 | 0 | 1742 | 608.244 | 608.244 | 608.244 | 883.9242 | 780 | 200 | 1863.9242 | 46.6% | 95% | 0% | -541.1899 | 67.0541 | -3550 | -400 | -3882.9459 | 97.07% | 47.12% | 95% | 0% | 1742 | -473
[5 empty] | 2019-09-21 | 34 | 6328 | 1469 | -388 | 1 | 0 | 1857 | 788.3759 | 788.3759 | 788.3759 | 883.9242 | 780 | 200 | 1863.9242 | 46.6% | 95% | 0% | -443.9359 | 344.44 | -3550 | -400 | -3605.56 | 90.14% | 47.11% | 95% | 0% | 1857 | -388
[5 empty] | 2019-09-21 | 35 | 6328.5 | 1685 | -311 | 1 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 883.9242 | 780 | 200 | 1863.9242 | 46.6% | 95% | 0% | -355.8352 | 650.2653 | -3550 | -400 | -3299.7347 | 82.49% | 47.1% | 95% | 0% | 1996 | -311
[5 empty] | 2019-09-21 | 36 | 6329 | 1851 | -240 | 1 | 0 | 2091 | 1154.9052 | 1154.9052 | 1154.9052 | 883.9242 | 780 | 200 | 1863.9242 | 46.6% | 95% | 0% | -274.5995 | 880.3057 | -3550 | -400 | -3069.6943 | 76.74% | 47.1% | 95% | 0% | 2091 | -240
[5 empty] | 2019-09-21 | 37 | 6329.5 | 1970 | -180 | 1 | 0 | 2150 | 1247.3207 | 1247.3207 | 1247.3207 | 883.9242 | 780 | 200 | 1863.9242 | 46.6% | 95% | 0% | -205.9497 | 1041.371 | -3550 | -400 | -2908.629 | 72.72% | 47.09% | 95% | 0% | 2150 | -180
[5 empty] | 2019-09-21 | 38 | 6330 | 2024 | -145 | 1 | 0 | 2169 | 1277.0816 | 1277.0816 | 1277.0816 | 883.9242 | 780 | 200 | 1863.9242 | 46.6% | 95% | 0% | -165.9039 | 1111.1777 | -3550 | -400 | -2838.8223 | 70.97% | 47.09% | 95% | 0% | 2169 | -145
[5 empty] | 2019-09-21 | 39 | 6330.5 | 2076 | -137 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 882.3578 | 780 | 200 | 1862.3578 | 46.56% | 95% | 0% | -156.7506 | 1189.2511 | -3550 | -400 | -2760.7489 | 69.02% | 47.07% | 95% | 0% | 2213 | -137
[5 empty] | 2019-09-21 | 40 | 6331 | 2124 | -134 | 1 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 882.3578 | 780 | 200 | 1862.3578 | 46.56% | 95% | 0% | -153.3181 | 1263.17 | -3550 | -400 | -2686.83 | 67.17% | 47.07% | 95% | 0% | 2258 | -134
[5 empty] | 2019-09-21 | 41 | 6331.5 | 2079 | -132 | 0 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 882.3578 | 780 | 200 | 1862.3578 | 46.56% | 95% | 0% | -151.0297 | 1191.8392 | -2750 | -200 | -1758.1608 | 43.95% | 47.06% | 95% | 0% | 2211 | -132
[5 empty] | 2019-09-21 | 42 | 6332 | 1999 | -130 | 0 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 882.3578 | 780 | 200 | 1862.3578 | 46.56% | 95% | 0% | -148.7414 | 1065.6856 | -2750 | -200 | -1884.3144 | 47.11% | 47.04% | 95% | 0% | 2129 | -130
[5 empty] | 2019-09-21 | 43 | 6332.5 | 1942 | -128 | 0 | 0 | 2070 | 1122.0115 | 1122.0115 | 1122.0115 | 882.3578 | 780 | 200 | 1862.3578 | 46.56% | 95% | 0% | -146.4531 | 975.5585 | -2750 | -200 | -1974.4415 | 49.36% | 47.04% | 95% | 0% | 2070 | -128
[5 empty] | 2019-09-21 | 44 | 6333 | 1870 | -126 | 0 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 882.3578 | 780 | 200 | 1862.3578 | 46.56% | 95% | 0% | -144.1648 | 861.9358 | -2750 | -200 | -2088.0642 | 52.2% | 47.04% | 95% | 0% | 1996 | -126
[5 empty] | 2019-09-21 | 45 | 6333.5 | 1814 | -124 | 0 | 0 | 1938 | 915.2514 | 915.2514 | 915.2514 | 882.3578 | 780 | 200 | 1862.3578 | 46.56% | 95% | 0% | -141.8764 | 773.375 | -2750 | -200 | -2176.625 | 54.42% | 47.04% | 95% | 0% | 1938 | -124
[5 empty] | 2019-09-21 | 46 | 6334 | 1732 | -122 | 0 | 0 | 1854 | 783.6768 | 783.6768 | 783.6768 | 882.3578 | 780 | 200 | 1862.3578 | 46.56% | 95% | 0% | -139.5881 | 644.0887 | -2750 | -200 | -2305.9113 | 57.65% | 47.04% | 95% | 0% | 1854 | -122
[5 empty] | 2019-09-21 | 47 | 6334.5 | 1622 | -121 | 0 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 880.7914 | 780 | 200 | 1860.7914 | 46.52% | 95% | 0% | -138.4439 | 471.3665 | -2750 | -200 | -2478.6335 | 61.97% | 47.04% | 95% | 0% | 1743 | -121
[5 empty] | 2019-09-21 | 48 | 6335 | 1539 | -119 | 0 | 0 | 1658 | 476.6694 | 476.6694 | 476.6694 | 880.7914 | 780 | 200 | 1860.7914 | 46.52% | 95% | 0% | -136.1556 | 340.5138 | -2750 | -200 | -2609.4862 | 65.24% | 47.03% | 95% | 0% | 1658 | -119
[5 empty] | 2019-09-22 | 1 | 6335.5 | 1457 | -116 | 0 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 880.7914 | 780 | 200 | 1860.7914 | 46.52% | 95% | 0% | -132.7231 | 210.8053 | -2750 | -200 | -2739.1947 | 68.48% | 47.03% | 95% | 0% | 1573 | -116
[5 empty] | 2019-09-22 | 2 | 6336 | 1418 | -114 | 0 | 0 | 1532 | 279.3075 | 279.3075 | 279.3075 | 880.7914 | 780 | 200 | 1860.7914 | 46.52% | 95% | 0% | -130.4348 | 148.8727 | -2750 | -200 | -2801.1273 | 70.03% | 47.02% | 95% | 0% | 1532 | -114
[5 empty] | 2019-09-22 | 3 | 6336.5 | 1392 | -113 | 0 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 880.7914 | 780 | 200 | 1860.7914 | 46.52% | 95% | 0% | -129.2906 | 107.725 | -2750 | -200 | -2842.275 | 71.06% | 47.02% | 95% | 0% | 1505 | -113
[5 empty] | 2019-09-22 | 4 | 6337 | 1374 | -113 | 0 | 0 | 1487 | 208.8211 | 208.8211 | 208.8211 | 880.7914 | 780 | 200 | 1860.7914 | 46.52% | 95% | 0% | -129.2906 | 79.5305 | -2750 | -200 | -2870.4695 | 71.76% | 47.01% | 95% | 0% | 1487 | -113
[5 empty] | 2019-09-22 | 5 | 6337.5 | 1345 | -111 | 0 | 0 | 1456 | 160.2638 | 160.2638 | 160.2638 | 880.7914 | 780 | 200 | 1860.7914 | 46.52% | 95% | 0% | -127.0023 | 33.2615 | -2750 | -200 | -2916.7385 | 72.92% | 47.01% | 95% | 0% | 1456 | -111
[5 empty] | 2019-09-22 | 6 | 6338 | 1319 | -110 | 0 | 0 | 1429 | 117.972 | 117.972 | 117.972 | 880.7914 | 780 | 200 | 1860.7914 | 46.52% | 95% | 0% | -125.8581 | -7.8862 | -2750 | -200 | -2957.8862 | 73.95% | 47.01% | 95% | 0% | 1429 | -110
[5 empty] | 2019-09-22 | 7 | 6338.5 | 1297 | -108 | 0 | 0 | 1405 | 80.3792 | 80.3792 | 80.3792 | 880.7914 | 780 | 200 | 1860.7914 | 46.52% | 95% | 0% | -123.5698 | -43.1906 | -2750 | -200 | -2993.1906 | 74.83% | 47% | 95% | 0% | 1405 | -108
[5 empty] | 2019-09-22 | 8 | 6339 | 1291 | -106 | 0 | 0 | 1397 | 67.8483 | 67.8483 | 67.8483 | 879.2251 | 780 | 200 | 1859.2251 | 46.48% | 95% | 0% | -121.2815 | -53.4332 | -2750 | -200 | -3003.4332 | 75.09% | 47% | 95% | 0% | 1397 | -106
[5 empty] | 2019-09-22 | 9 | 6339.5 | 1281 | -104 | 0 | 0 | 1385 | 49.0519 | 49.0519 | 49.0519 | 879.2251 | 780 | 200 | 1859.2251 | 46.48% | 95% | 0% | -118.9931 | -69.9412 | -2750 | -200 | -3019.9412 | 75.5% | 47% | 95% | 0% | 1385 | -104
[5 empty] | 2019-09-22 | 10 | 6340 | 1270 | -103 | 0 | 0 | 1373 | 30.2556 | 30.2556 | 30.2556 | 879.2251 | 780 | 200 | 1859.2251 | 46.48% | 95% | 0% | -117.849 | -87.5934 | -2750 | -200 | -3037.5934 | 75.94% | 47% | 95% | 0% | 1373 | -103
[5 empty] | 2019-09-22 | 11 | 6340.5 | 1280 | -101 | 1 | 0 | 1381 | 42.7865 | 42.7865 | 42.7865 | 879.2251 | 780 | 200 | 1859.2251 | 46.48% | 95% | 0% | -115.5606 | -72.7742 | -3550 | -400 | -4022.7742 | 100.6% | 46.99% | 95% | 0% | 1381 | -101
[5 empty] | 2019-09-22 | 12 | 6341 | 1308 | -98 | 1 | 0 | 1406 | 81.9456 | 81.9456 | 81.9456 | 879.2251 | 780 | 200 | 1859.2251 | 46.48% | 95% | 0% | -112.1281 | -30.1826 | -3550 | -400 | -3980.1826 | 99.5% | 46.99% | 95% | 0% | 1406 | -98
[5 empty] | 2019-09-22 | 13 | 6341.5 | 1386 | -98 | 1 | 0 | 1484 | 204.122 | 204.122 | 204.122 | 879.2251 | 780 | 200 | 1859.2251 | 46.48% | 95% | 0% | -112.1281 | 91.9939 | -3550 | -400 | -3858.0061 | 96.45% | 46.99% | 95% | 0% | 1484 | -98
[5 empty] | 2019-09-22 | 14 | 6342 | 1435 | -98 | 1 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 879.2251 | 780 | 200 | 1859.2251 | 46.48% | 95% | 0% | -112.1281 | 168.7457 | -3550 | -400 | -3781.2543 | 94.53% | 46.99% | 95% | 0% | 1533 | -98
[5 empty] | 2019-09-22 | 15 | 6342.5 | 1512 | -101 | 1 | 0 | 1613 | 406.183 | 406.183 | 406.183 | 879.2251 | 780 | 200 | 1859.2251 | 46.48% | 95% | 0% | -115.5606 | 290.6224 | -3550 | -400 | -3659.3776 | 91.48% | 46.99% | 95% | 0% | 1613 | -101
[5 empty] | 2019-09-22 | 16 | 6343 | 1591 | -110 | 1 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 879.2251 | 780 | 200 | 1859.2251 | 46.48% | 95% | 0% | -125.8581 | 418.165 | -3550 | -400 | -3531.835 | 88.3% | 46.99% | 95% | 0% | 1701 | -110
[5 empty] | 2019-09-22 | 17 | 6343.5 | 1695 | -136 | 1 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 879.2251 | 780 | 200 | 1859.2251 | 46.48% | 95% | 0% | -155.6064 | 592.044 | -3550 | -400 | -3357.956 | 83.95% | 46.99% | 95% | 0% | 1831 | -136
[5 empty] | 2019-09-22 | 18 | 6344 | 1773 | -154 | 1 | 0 | 1927 | 898.0214 | 898.0214 | 898.0214 | 879.2251 | 780 | 200 | 1859.2251 | 46.48% | 95% | 0% | -176.2014 | 721.8201 | -3550 | -400 | -3228.1799 | 80.7% | 46.99% | 95% | 0% | 1927 | -154
[5 empty] | 2019-09-22 | 19 | 6344.5 | 1842 | -169 | 1 | 0 | 2011 | 1029.596 | 1029.596 | 1029.596 | 879.2251 | 780 | 200 | 1859.2251 | 46.48% | 95% | 0% | -193.3638 | 836.2322 | -3550 | -400 | -3113.7678 | 77.84% | 46.99% | 95% | 0% | 2011 | -169
[5 empty] | 2019-09-22 | 20 | 6345 | 1906 | -185 | 1 | 0 | 2091 | 1154.9052 | 1154.9052 | 1154.9052 | 877.6587 | 780 | 200 | 1857.6587 | 46.44% | 95% | 0% | -211.6705 | 943.2347 | -3550 | -400 | -3006.7653 | 75.17% | 46.98% | 95% | 0% | 2091 | -185
[5 empty] | 2019-09-22 | 21 | 6345.5 | 1915 | -202 | 1 | 0 | 2117 | 1195.6307 | 1195.6307 | 1195.6307 | 877.6587 | 780 | 200 | 1857.6587 | 46.44% | 95% | 0% | -231.1213 | 964.5094 | -3550 | -400 | -2985.4906 | 74.64% | 46.98% | 95% | 0% | 2117 | -202
[5 empty] | 2019-09-22 | 22 | 6346 | 1906 | -224 | 1 | 0 | 2130 | 1215.9934 | 1215.9934 | 1215.9934 | 877.6587 | 780 | 200 | 1857.6587 | 46.44% | 95% | 0% | -256.2929 | 959.7005 | -3550 | -400 | -2990.2995 | 74.76% | 46.97% | 95% | 0% | 2130 | -224
[5 empty] | 2019-09-22 | 23 | 6346.5 | 1894 | -251 | 1 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 877.6587 | 780 | 200 | 1857.6587 | 46.44% | 95% | 0% | -287.1854 | 952.3035 | -3550 | -400 | -2997.6965 | 74.94% | 46.97% | 95% | 0% | 2145 | -251
[5 empty] | 2019-09-22 | 24 | 6347 | 1875 | -266 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 877.6587 | 780 | 200 | 1857.6587 | 46.44% | 95% | 0% | -304.3478 | 928.8756 | -3550 | -400 | -3021.1244 | 75.53% | 46.96% | 95% | 0% | 2141 | -266
[5 empty] | 2019-09-22 | 25 | 6347.5 | 1873 | -265 | 1 | 0 | 2138 | 1228.5243 | 1228.5243 | 1228.5243 | 877.6587 | 780 | 200 | 1857.6587 | 46.44% | 95% | 0% | -303.2037 | 925.3207 | -3550 | -400 | -3024.6793 | 75.62% | 46.96% | 95% | 0% | 2138 | -265
[5 empty] | 2019-09-22 | 26 | 6348 | 1828 | -303 | 1 | 0 | 2131 | 1217.5598 | 1217.5598 | 1217.5598 | 877.6587 | 780 | 200 | 1857.6587 | 46.44% | 95% | 0% | -346.6819 | 870.8778 | -3550 | -400 | -3079.1222 | 76.98% | 46.95% | 95% | 0% | 2131 | -303
[5 empty] | 2019-09-22 | 27 | 6348.5 | 1765 | -341 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 877.6587 | 780 | 200 | 1857.6587 | 46.44% | 95% | 0% | -390.1602 | 788.2405 | -3550 | -400 | -3161.7595 | 79.04% | 46.95% | 95% | 0% | 2106 | -341
[5 empty] | 2019-09-22 | 28 | 6349 | 1743 | -344 | 1 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 877.6587 | 780 | 200 | 1857.6587 | 46.44% | 95% | 0% | -393.5927 | 755.0471 | -3550 | -400 | -3194.9529 | 79.87% | 46.95% | 95% | 0% | 2087 | -344
[5 empty] | 2019-09-22 | 29 | 6349.5 | 1777 | -312 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 877.6587 | 780 | 200 | 1857.6587 | 46.44% | 95% | 0% | -356.9794 | 794.7931 | -3550 | -400 | -3155.2069 | 78.88% | 46.94% | 95% | 0% | 2089 | -312
[5 empty] | 2019-09-22 | 30 | 6350 | 1813 | -278 | 1 | 0 | 2091 | 1154.9052 | 1154.9052 | 1154.9052 | 877.6587 | 780 | 200 | 1857.6587 | 46.44% | 95% | 0% | -318.0778 | 836.8274 | -3550 | -400 | -3113.1726 | 77.83% | 46.94% | 95% | 0% | 2091 | -278
[5 empty] | 2019-09-22 | 31 | 6350.5 | 1880 | -235 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 877.6587 | 780 | 200 | 1857.6587 | 46.44% | 95% | 0% | -268.8787 | 923.6192 | -3550 | -400 | -3026.3808 | 75.66% | 46.94% | 95% | 0% | 2115 | -235
[5 empty] | 2019-09-22 | 32 | 6351 | 1941 | -208 | 1 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -237.9863 | 1007.7681 | -3550 | -400 | -2942.2319 | 73.56% | 46.94% | 95% | 0% | 2149 | -208
[5 empty] | 2019-09-22 | 33 | 6351.5 | 2020 | -198 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -226.5446 | 1127.2888 | -3550 | -400 | -2822.7112 | 70.57% | 46.93% | 95% | 0% | 2218 | -198
[5 empty] | 2019-09-22 | 34 | 6352 | 2117 | -170 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -194.508 | 1267.4046 | -3550 | -400 | -2682.5954 | 67.06% | 46.93% | 95% | 0% | 2287 | -170
[5 empty] | 2019-09-22 | 35 | 6352.5 | 2196 | -148 | 1 | 0 | 2344 | 1551.1954 | 1551.1954 | 1551.1954 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -169.3364 | 1381.859 | -3550 | -400 | -2568.141 | 64.2% | 46.92% | 95% | 0% | 2344 | -148
[5 empty] | 2019-09-22 | 36 | 6353 | 2268 | -119 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -136.1556 | 1482.3934 | -3550 | -400 | -2467.6066 | 61.69% | 46.92% | 95% | 0% | 2387 | -119
[5 empty] | 2019-09-22 | 37 | 6353.5 | 2320 | -89 | 1 | 0 | 2409 | 1653.0091 | 1653.0091 | 1653.0091 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -101.8307 | 1551.1784 | -3550 | -400 | -2398.8216 | 59.97% | 46.91% | 95% | 0% | 2409 | -89
[5 empty] | 2019-09-22 | 38 | 6354 | 2353 | -70 | 1 | 0 | 2423 | 1674.9382 | 1674.9382 | 1674.9382 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -80.0915 | 1594.8466 | -3550 | -400 | -2355.1534 | 58.88% | 46.91% | 95% | 0% | 2423 | -70
[5 empty] | 2019-09-22 | 39 | 6354.5 | 2395 | -64 | 1 | 0 | 2459 | 1731.3273 | 1731.3273 | 1731.3273 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -73.2265 | 1658.1007 | -3550 | -400 | -2291.8993 | 57.3% | 46.91% | 95% | 0% | 2459 | -64
[5 empty] | 2019-09-22 | 40 | 6355 | 2391 | -63 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -72.0824 | 1651.4131 | -3550 | -400 | -2298.5869 | 57.46% | 46.9% | 95% | 0% | 2454 | -63
[5 empty] | 2019-09-22 | 41 | 6355.5 | 2335 | -62 | 0 | 0 | 2397 | 1634.2127 | 1634.2127 | 1634.2127 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -70.9382 | 1563.2745 | -2750 | -200 | -1386.7255 | 34.67% | 46.9% | 95% | 0% | 2397 | -62
[5 empty] | 2019-09-22 | 42 | 6356 | 2251 | -60 | 0 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -68.6499 | 1430.8555 | -2750 | -200 | -1519.1445 | 37.98% | 46.89% | 95% | 0% | 2311 | -60
[5 empty] | 2019-09-22 | 43 | 6356.5 | 2179 | -60 | 0 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -68.6499 | 1318.0772 | -2750 | -200 | -1631.9228 | 40.8% | 46.89% | 95% | 0% | 2239 | -60
[5 empty] | 2019-09-22 | 44 | 6357 | 2072 | -61 | 0 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -69.7941 | 1150.8984 | -2750 | -200 | -1799.1016 | 44.98% | 46.88% | 95% | 0% | 2133 | -61
[5 empty] | 2019-09-22 | 45 | 6357.5 | 1960 | -61 | 0 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -69.7941 | 975.4656 | -2750 | -200 | -1974.5344 | 49.36% | 46.88% | 95% | 0% | 2021 | -61
[5 empty] | 2019-09-22 | 46 | 6358 | 1841 | -62 | 0 | 0 | 1903 | 860.4287 | 860.4287 | 860.4287 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -70.9382 | 789.4905 | -2750 | -200 | -2160.5095 | 54.01% | 46.88% | 95% | 0% | 1903 | -62
[5 empty] | 2019-09-22 | 47 | 6358.5 | 1712 | -64 | 0 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 876.0923 | 780 | 200 | 1856.0923 | 46.4% | 95% | 0% | -73.2265 | 588.2739 | -2750 | -200 | -2361.7261 | 59.04% | 46.88% | 95% | 0% | 1776 | -64
[5 empty] | 2019-09-22 | 48 | 6359 | 1615 | -65 | 0 | 0 | 1680 | 511.1294 | 511.1294 | 511.1294 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -74.3707 | 436.7587 | -2750 | -200 | -2513.2413 | 62.83% | 46.88% | 95% | 0% | 1680 | -65
[5 empty] | 2019-09-23 | 1 | 6359.5 | 1535 | -66 | 0 | 0 | 1601 | 387.3866 | 387.3866 | 387.3866 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -75.5149 | 311.8718 | -2750 | -200 | -2638.1282 | 65.95% | 46.87% | 95% | 0% | 1601 | -66
[5 empty] | 2019-09-23 | 2 | 6360 | 1486 | -67 | 0 | 0 | 1553 | 312.2012 | 312.2012 | 312.2012 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -76.659 | 235.5421 | -2750 | -200 | -2714.4579 | 67.86% | 46.87% | 95% | 0% | 1553 | -67
[5 empty] | 2019-09-23 | 3 | 6360.5 | 1465 | -68 | 0 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -77.8032 | 203.0707 | -2750 | -200 | -2746.9293 | 68.67% | 46.87% | 95% | 0% | 1533 | -68
[5 empty] | 2019-09-23 | 4 | 6361 | 1454 | -69 | 0 | 0 | 1523 | 265.2102 | 265.2102 | 265.2102 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -78.9474 | 186.2629 | -2750 | -200 | -2763.7371 | 69.09% | 46.84% | 95% | 0% | 1523 | -69
[5 empty] | 2019-09-23 | 5 | 6361.5 | 1437 | -70 | 0 | 0 | 1507 | 240.1484 | 240.1484 | 240.1484 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -80.0915 | 160.0569 | -2750 | -200 | -2789.9431 | 69.75% | 46.84% | 95% | 0% | 1507 | -70
[5 empty] | 2019-09-23 | 6 | 6362 | 1413 | -70 | 0 | 0 | 1483 | 202.5556 | 202.5556 | 202.5556 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -80.0915 | 122.4641 | -2750 | -200 | -2827.5359 | 70.69% | 46.83% | 95% | 0% | 1483 | -70
[5 empty] | 2019-09-23 | 7 | 6362.5 | 1389 | -71 | 0 | 0 | 1460 | 166.5293 | 166.5293 | 166.5293 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -81.2357 | 85.2936 | -2750 | -200 | -2864.7064 | 71.62% | 46.82% | 95% | 0% | 1460 | -71
[5 empty] | 2019-09-23 | 8 | 6363 | 1380 | -72 | 0 | 0 | 1452 | 153.9984 | 153.9984 | 153.9984 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -82.3799 | 71.6185 | -2750 | -200 | -2878.3815 | 71.96% | 46.82% | 95% | 0% | 1452 | -72
[5 empty] | 2019-09-23 | 9 | 6363.5 | 1396 | -73 | 0 | 0 | 1469 | 180.6265 | 180.6265 | 180.6265 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -83.524 | 97.1025 | -2750 | -200 | -2852.8975 | 71.32% | 46.82% | 95% | 0% | 1469 | -73
[5 empty] | 2019-09-23 | 10 | 6364 | 1408 | -75 | 0 | 0 | 1483 | 202.5556 | 202.5556 | 202.5556 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -85.8124 | 116.7433 | -2750 | -200 | -2833.2567 | 70.83% | 46.8% | 95% | 0% | 1483 | -75
[5 empty] | 2019-09-23 | 11 | 6364.5 | 1473 | -76 | 0 | 0 | 1549 | 305.9357 | 305.9357 | 305.9357 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -86.9565 | 218.9792 | -2750 | -200 | -2731.0208 | 68.28% | 46.8% | 95% | 0% | 1549 | -76
[5 empty] | 2019-09-23 | 12 | 6365 | 1572 | -77 | 0 | 0 | 1649 | 462.5721 | 462.5721 | 462.5721 | 874.526 | 780 | 200 | 1854.526 | 46.36% | 95% | 0% | -88.1007 | 374.4714 | -2750 | -200 | -2575.5286 | 64.39% | 46.8% | 95% | 0% | 1649 | -77
[5 empty] | 2019-09-23 | 13 | 6365.5 | 1800 | -78 | 0 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 872.9596 | 780 | 200 | 1852.9596 | 46.32% | 95% | 0% | -89.2449 | 732.0247 | -2750 | -200 | -2217.9753 | 55.45% | 46.79% | 95% | 0% | 1878 | -78
[5 empty] | 2019-09-23 | 14 | 6366 | 1999 | -78 | 0 | 0 | 2077 | 1132.9761 | 1132.9761 | 1132.9761 | 872.9596 | 780 | 200 | 1852.9596 | 46.32% | 95% | 0% | -89.2449 | 1043.7312 | -2750 | -200 | -1906.2688 | 47.66% | 46.78% | 95% | 0% | 2077 | -78
[5 empty] | 2019-09-23 | 15 | 6366.5 | 2214 | -86 | 0 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 872.9596 | 780 | 200 | 1852.9596 | 46.32% | 95% | 0% | -98.3982 | 1383.8772 | -2750 | -200 | -1566.1228 | 39.15% | 46.78% | 95% | 0% | 2300 | -86
[5 empty] | 2019-09-23 | 16 | 6367 | 2261 | -126 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 872.9596 | 780 | 200 | 1852.9596 | 46.32% | 95% | 0% | -144.1648 | 1474.3843 | -3550 | -400 | -2475.6157 | 61.89% | 46.77% | 95% | 0% | 2387 | -126
[5 empty] | 2019-09-23 | 17 | 6367.5 | 2217 | -187 | 1 | 0 | 2404 | 1645.1772 | 1645.1772 | 1645.1772 | 872.9596 | 780 | 200 | 1852.9596 | 46.32% | 95% | 0% | -213.9588 | 1431.2184 | -3550 | -400 | -2518.7816 | 62.97% | 46.77% | 95% | 0% | 2404 | -187
[5 empty] | 2019-09-23 | 18 | 6368 | 2149 | -247 | 1 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 872.9596 | 780 | 200 | 1852.9596 | 46.32% | 95% | 0% | -282.6087 | 1350.0376 | -3550 | -400 | -2599.9624 | 65% | 46.77% | 95% | 0% | 2396 | -247
[5 empty] | 2019-09-23 | 19 | 6368.5 | 2059 | -312 | 1 | 0 | 2371 | 1593.4872 | 1593.4872 | 1593.4872 | 872.9596 | 780 | 200 | 1852.9596 | 46.32% | 95% | 0% | -356.9794 | 1236.5078 | -3550 | -400 | -2713.4922 | 67.84% | 46.76% | 95% | 0% | 2371 | -312
[5 empty] | 2019-09-23 | 20 | 6369 | 1950 | -380 | 1 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 872.9596 | 780 | 200 | 1852.9596 | 46.32% | 95% | 0% | -434.7826 | 1094.4837 | -3550 | -400 | -2855.5163 | 71.39% | 46.76% | 95% | 0% | 2330 | -380
[5 empty] | 2019-09-23 | 21 | 6369.5 | 1810 | -458 | 1 | 0 | 2268 | 1432.1517 | 1432.1517 | 1432.1517 | 871.3932 | 780 | 200 | 1851.3932 | 46.28% | 95% | 0% | -524.0275 | 908.1242 | -3550 | -400 | -3041.8758 | 76.05% | 46.75% | 95% | 0% | 2268 | -458
[5 empty] | 2019-09-23 | 22 | 6370 | 1778 | -493 | 1 | 0 | 2271 | 1436.8508 | 1436.8508 | 1436.8508 | 871.3932 | 780 | 200 | 1851.3932 | 46.28% | 95% | 0% | -564.0732 | 872.7776 | -3550 | -400 | -3077.2224 | 76.93% | 46.75% | 95% | 0% | 2271 | -493
[5 empty] | 2019-09-23 | 23 | 6370.5 | 1787 | -503 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 871.3932 | 780 | 200 | 1851.3932 | 46.28% | 95% | 0% | -575.5149 | 891.0968 | -3550 | -400 | -3058.9032 | 76.47% | 46.75% | 95% | 0% | 2290 | -503
[5 empty] | 2019-09-23 | 24 | 6371 | 1772 | -522 | 1 | 0 | 2294 | 1472.8772 | 1472.8772 | 1472.8772 | 871.3932 | 780 | 200 | 1851.3932 | 46.28% | 95% | 0% | -597.254 | 875.6232 | -3550 | -400 | -3074.3768 | 76.86% | 46.73% | 95% | 0% | 2294 | -522
[5 empty] | 2019-09-23 | 25 | 6371.5 | 1825 | -476 | 1 | 0 | 2301 | 1483.8417 | 1483.8417 | 1483.8417 | 871.3932 | 780 | 200 | 1851.3932 | 46.28% | 95% | 0% | -544.6224 | 939.2193 | -3550 | -400 | -3010.7807 | 75.27% | 46.73% | 95% | 0% | 2301 | -476
[5 empty] | 2019-09-23 | 26 | 6372 | 1790 | -498 | 1 | 0 | 2288 | 1463.479 | 1463.479 | 1463.479 | 871.3932 | 780 | 200 | 1851.3932 | 46.28% | 95% | 0% | -569.7941 | 893.6849 | -3550 | -400 | -3056.3151 | 76.41% | 46.73% | 95% | 0% | 2288 | -498
[5 empty] | 2019-09-23 | 27 | 6372.5 | 1820 | -470 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 871.3932 | 780 | 200 | 1851.3932 | 46.28% | 95% | 0% | -537.7574 | 928.8543 | -3550 | -400 | -3021.1457 | 75.53% | 46.71% | 95% | 0% | 2290 | -470
[5 empty] | 2019-09-23 | 28 | 6373 | 1889 | -411 | 1 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 871.3932 | 780 | 200 | 1851.3932 | 46.28% | 95% | 0% | -470.2517 | 1012.0236 | -3550 | -400 | -2937.9764 | 73.45% | 46.7% | 95% | 0% | 2300 | -411
[5 empty] | 2019-09-23 | 29 | 6373.5 | 1949 | -370 | 1 | 0 | 2319 | 1512.0363 | 1512.0363 | 1512.0363 | 871.3932 | 780 | 200 | 1851.3932 | 46.28% | 95% | 0% | -423.341 | 1088.6953 | -3550 | -400 | -2861.3047 | 71.53% | 46.7% | 95% | 0% | 2319 | -370
[5 empty] | 2019-09-23 | 30 | 6374 | 1984 | -340 | 1 | 0 | 2324 | 1519.8681 | 1519.8681 | 1519.8681 | 871.3932 | 780 | 200 | 1851.3932 | 46.28% | 95% | 0% | -389.016 | 1130.8521 | -3550 | -400 | -2819.1479 | 70.48% | 46.7% | 95% | 0% | 2324 | -340
[5 empty] | 2019-09-23 | 31 | 6374.5 | 2052 | -309 | 1 | 0 | 2361 | 1577.8236 | 1577.8236 | 1577.8236 | 869.8269 | 780 | 200 | 1849.8269 | 46.25% | 95% | 0% | -353.5469 | 1224.2767 | -3550 | -400 | -2725.7233 | 68.14% | 46.7% | 95% | 0% | 2361 | -309
[5 empty] | 2019-09-23 | 32 | 6375 | 2168 | -264 | 1 | 0 | 2432 | 1689.0354 | 1689.0354 | 1689.0354 | 869.8269 | 780 | 200 | 1849.8269 | 46.25% | 95% | 0% | -302.0595 | 1386.976 | -3550 | -400 | -2563.024 | 64.08% | 46.69% | 95% | 0% | 2432 | -264
[5 empty] | 2019-09-23 | 33 | 6375.5 | 2275 | -225 | 1 | 0 | 2500 | 1795.5482 | 1795.5482 | 1795.5482 | 869.8269 | 780 | 200 | 1849.8269 | 46.25% | 95% | 0% | -257.4371 | 1538.1112 | -3550 | -400 | -2411.8888 | 60.3% | 46.68% | 95% | 0% | 2500 | -225
[5 empty] | 2019-09-23 | 34 | 6376 | 2371 | -204 | 1 | 0 | 2575 | 1913.0256 | 1913.0256 | 1913.0256 | 869.8269 | 780 | 200 | 1849.8269 | 46.25% | 95% | 0% | -233.4096 | 1679.6159 | -3550 | -400 | -2270.3841 | 56.76% | 46.68% | 95% | 0% | 2575 | -204
[5 empty] | 2019-09-23 | 35 | 6376.5 | 2450 | -184 | 1 | 0 | 2634 | 2005.4411 | 2005.4411 | 2005.4411 | 869.8269 | 780 | 200 | 1849.8269 | 46.25% | 95% | 0% | -210.5263 | 1794.9147 | -3550 | -400 | -2155.0853 | 53.88% | 46.68% | 95% | 0% | 2634 | -184
[5 empty] | 2019-09-23 | 36 | 6377 | 2517 | -156 | 1 | 0 | 2673 | 2066.5293 | 2066.5293 | 2066.5293 | 869.8269 | 780 | 200 | 1849.8269 | 46.25% | 95% | 0% | -178.4897 | 1888.0396 | -3550 | -400 | -2061.9604 | 51.55% | 46.67% | 95% | 0% | 2673 | -156
[5 empty] | 2019-09-23 | 37 | 6377.5 | 2543 | -144 | 1 | 0 | 2687 | 2088.4584 | 2088.4584 | 2088.4584 | 869.8269 | 780 | 200 | 1849.8269 | 46.25% | 95% | 0% | -164.7597 | 1923.6986 | -3550 | -400 | -2026.3014 | 50.66% | 46.67% | 95% | 0% | 2687 | -144
[5 empty] | 2019-09-23 | 38 | 6378 | 2550 | -139 | 1 | 0 | 2689 | 2091.5911 | 2091.5911 | 2091.5911 | 869.8269 | 780 | 200 | 1849.8269 | 46.25% | 95% | 0% | -159.0389 | 1932.5522 | -3550 | -400 | -2017.4478 | 50.44% | 46.66% | 95% | 0% | 2689 | -139
[5 empty] | 2019-09-23 | 39 | 6378.5 | 2552 | -142 | 1 | 0 | 2694 | 2099.4229 | 2099.4229 | 2099.4229 | 869.8269 | 780 | 200 | 1849.8269 | 46.25% | 95% | 0% | -162.4714 | 1936.9515 | -3550 | -400 | -2013.0485 | 50.33% | 46.66% | 95% | 0% | 2694 | -142
[5 empty] | 2019-09-23 | 40 | 6379 | 2515 | -145 | 1 | 0 | 2660 | 2046.1665 | 2046.1665 | 2046.1665 | 869.8269 | 780 | 200 | 1849.8269 | 46.25% | 95% | 0% | -165.9039 | 1880.2626 | -3550 | -400 | -2069.7374 | 51.74% | 46.66% | 95% | 0% | 2660 | -145
[5 empty] | 2019-09-23 | 41 | 6379.5 | 2428 | -148 | 0 | 0 | 2576 | 1914.5919 | 1914.5919 | 1914.5919 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -169.3364 | 1745.2555 | -2750 | -200 | -1204.7445 | 30.12% | 46.65% | 95% | 0% | 2576 | -148
[5 empty] | 2019-09-23 | 42 | 6380 | 2309 | -150 | 0 | 0 | 2459 | 1731.3273 | 1731.3273 | 1731.3273 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -171.6247 | 1559.7026 | -2750 | -200 | -1390.2974 | 34.76% | 46.64% | 95% | 0% | 2459 | -150
[5 empty] | 2019-09-23 | 43 | 6380.5 | 2181 | -153 | 0 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -175.0572 | 1360.4745 | -2750 | -200 | -1589.5255 | 39.74% | 46.64% | 95% | 0% | 2334 | -153
[5 empty] | 2019-09-23 | 44 | 6381 | 2034 | -156 | 0 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -178.4897 | 1131.4856 | -2750 | -200 | -1818.5144 | 45.46% | 46.63% | 95% | 0% | 2190 | -156
[5 empty] | 2019-09-23 | 45 | 6381.5 | 1885 | -155 | 0 | 0 | 2040 | 1075.0206 | 1075.0206 | 1075.0206 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -177.3455 | 897.6751 | -2750 | -200 | -2052.3249 | 51.31% | 46.63% | 95% | 0% | 2040 | -155
[5 empty] | 2019-09-23 | 46 | 6382 | 1744 | -155 | 0 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -177.3455 | 676.8177 | -2750 | -200 | -2273.1823 | 56.83% | 46.63% | 95% | 0% | 1899 | -155
[5 empty] | 2019-09-23 | 47 | 6382.5 | 1628 | -154 | 0 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -176.2014 | 494.6972 | -2750 | -200 | -2455.3028 | 61.38% | 46.62% | 95% | 0% | 1782 | -154
[5 empty] | 2019-09-23 | 48 | 6383 | 1534 | -152 | 0 | 0 | 1686 | 520.5276 | 520.5276 | 520.5276 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -173.913 | 346.6146 | -2750 | -200 | -2603.3854 | 65.08% | 46.62% | 95% | 0% | 1686 | -152
[5 empty] | 2019-09-24 | 1 | 6383.5 | 1466 | -146 | 0 | 0 | 1612 | 404.6167 | 404.6167 | 404.6167 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -167.0481 | 237.5686 | -2750 | -200 | -2712.4314 | 67.81% | 46.62% | 95% | 0% | 1612 | -146
[5 empty] | 2019-09-24 | 2 | 6384 | 1426 | -141 | 0 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -161.3272 | 172.803 | -2750 | -200 | -2777.197 | 69.43% | 46.62% | 95% | 0% | 1567 | -141
[5 empty] | 2019-09-24 | 3 | 6384.5 | 1402 | -137 | 0 | 0 | 1539 | 290.2721 | 290.2721 | 290.2721 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -156.7506 | 133.5215 | -2750 | -200 | -2816.4785 | 70.41% | 46.61% | 95% | 0% | 1539 | -137
[5 empty] | 2019-09-24 | 4 | 6385 | 1402 | -133 | 0 | 0 | 1535 | 284.0066 | 284.0066 | 284.0066 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -152.1739 | 131.8327 | -2750 | -200 | -2818.1673 | 70.45% | 46.6% | 95% | 0% | 1535 | -133
[5 empty] | 2019-09-24 | 5 | 6385.5 | 1398 | -130 | 0 | 0 | 1528 | 273.042 | 273.042 | 273.042 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -148.7414 | 124.3006 | -2750 | -200 | -2825.6994 | 70.64% | 46.59% | 95% | 0% | 1528 | -130
[5 empty] | 2019-09-24 | 6 | 6386 | 1378 | -126 | 0 | 0 | 1504 | 235.4493 | 235.4493 | 235.4493 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -144.1648 | 91.2845 | -2750 | -200 | -2858.7155 | 71.47% | 46.59% | 95% | 0% | 1504 | -126
[5 empty] | 2019-09-24 | 7 | 6386.5 | 1373 | -123 | 0 | 0 | 1496 | 222.9184 | 222.9184 | 222.9184 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -140.7323 | 82.1861 | -2750 | -200 | -2867.8139 | 71.7% | 46.59% | 95% | 0% | 1496 | -123
[5 empty] | 2019-09-24 | 8 | 6387 | 1374 | -119 | 0 | 0 | 1493 | 218.2193 | 218.2193 | 218.2193 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -136.1556 | 82.0637 | -2750 | -200 | -2867.9363 | 71.7% | 46.59% | 95% | 0% | 1493 | -119
[5 empty] | 2019-09-24 | 9 | 6387.5 | 1390 | -117 | 0 | 0 | 1507 | 240.1484 | 240.1484 | 240.1484 | 868.2605 | 780 | 200 | 1848.2605 | 46.21% | 95% | 0% | -133.8673 | 106.2811 | -2750 | -200 | -2843.7189 | 71.09% | 46.58% | 95% | 0% | 1507 | -117
[5 empty] | 2019-09-24 | 10 | 6388 | 1410 | -115 | 0 | 0 | 1525 | 268.343 | 268.343 | 268.343 | 866.6941 | 780 | 200 | 1846.6941 | 46.17% | 95% | 0% | -131.5789 | 136.764 | -2750 | -200 | -2813.236 | 70.33% | 46.58% | 95% | 0% | 1525 | -115
[5 empty] | 2019-09-24 | 11 | 6388.5 | 1489 | -112 | 0 | 0 | 1601 | 387.3866 | 387.3866 | 387.3866 | 866.6941 | 780 | 200 | 1846.6941 | 46.17% | 95% | 0% | -128.1465 | 259.2402 | -2750 | -200 | -2690.7598 | 67.27% | 46.58% | 95% | 0% | 1601 | -112
[5 empty] | 2019-09-24 | 12 | 6389 | 1595 | -110 | 0 | 0 | 1705 | 550.2885 | 550.2885 | 550.2885 | 866.6941 | 780 | 200 | 1846.6941 | 46.17% | 95% | 0% | -125.8581 | 424.4304 | -2750 | -200 | -2525.5696 | 63.14% | 46.58% | 95% | 0% | 1705 | -110
[5 empty] | 2019-09-24 | 13 | 6389.5 | 1793 | -107 | 0 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 866.6941 | 780 | 200 | 1846.6941 | 46.17% | 95% | 0% | -122.4256 | 733.304 | -2750 | -200 | -2216.696 | 55.42% | 46.57% | 95% | 0% | 1900 | -107
[5 empty] | 2019-09-24 | 14 | 6390 | 2012 | -104 | 0 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 866.6941 | 780 | 200 | 1846.6941 | 46.17% | 95% | 0% | -118.9931 | 1075.0712 | -2750 | -200 | -1874.9288 | 46.87% | 46.56% | 95% | 0% | 2116 | -104
[5 empty] | 2019-09-24 | 15 | 6390.5 | 2237 | -102 | 0 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 866.6941 | 780 | 200 | 1846.6941 | 46.17% | 95% | 0% | -116.7048 | 1426.6588 | -2750 | -200 | -1523.3412 | 38.08% | 46.56% | 95% | 0% | 2339 | -102
[5 empty] | 2019-09-24 | 16 | 6391 | 2359 | -101 | 0 | 0 | 2460 | 1732.8937 | 1732.8937 | 1732.8937 | 866.6941 | 780 | 200 | 1846.6941 | 46.17% | 95% | 0% | -115.5606 | 1617.333 | -2750 | -200 | -1332.667 | 33.32% | 46.56% | 95% | 0% | 2460 | -101
[5 empty] | 2019-09-24 | 17 | 6391.5 | 2433 | -108 | 0 | 0 | 2541 | 1859.7692 | 1859.7692 | 1859.7692 | 866.6941 | 780 | 200 | 1846.6941 | 46.17% | 95% | 0% | -123.5698 | 1736.1994 | -2750 | -200 | -1213.8006 | 30.35% | 46.56% | 95% | 0% | 2541 | -108
[5 empty] | 2019-09-24 | 18 | 6392 | 2435 | -121 | 1 | 0 | 2556 | 1883.2646 | 1883.2646 | 1883.2646 | 865.1278 | 780 | 200 | 1845.1278 | 46.13% | 95% | 0% | -138.4439 | 1744.8207 | -3550 | -400 | -2205.1793 | 55.13% | 46.55% | 95% | 0% | 2556 | -121
[5 empty] | 2019-09-24 | 19 | 6392.5 | 2488 | -136 | 1 | 0 | 2624 | 1989.7774 | 1989.7774 | 1989.7774 | 865.1278 | 780 | 200 | 1845.1278 | 46.13% | 95% | 0% | -155.6064 | 1834.171 | -3550 | -400 | -2115.829 | 52.9% | 46.54% | 95% | 0% | 2624 | -136
[5 empty] | 2019-09-24 | 20 | 6393 | 2457 | -156 | 1 | 0 | 2613 | 1972.5474 | 1972.5474 | 1972.5474 | 865.1278 | 780 | 200 | 1845.1278 | 46.13% | 95% | 0% | -178.4897 | 1794.0577 | -3550 | -400 | -2155.9423 | 53.9% | 46.54% | 95% | 0% | 2613 | -156
[5 empty] | 2019-09-24 | 21 | 6393.5 | 2426 | -167 | 1 | 0 | 2593 | 1941.2201 | 1941.2201 | 1941.2201 | 865.1278 | 780 | 200 | 1845.1278 | 46.13% | 95% | 0% | -191.0755 | 1750.1446 | -3550 | -400 | -2199.8554 | 55% | 46.53% | 95% | 0% | 2593 | -167
[5 empty] | 2019-09-24 | 22 | 6394 | 2387 | -196 | 1 | 0 | 2583 | 1925.5565 | 1925.5565 | 1925.5565 | 865.1278 | 780 | 200 | 1845.1278 | 46.13% | 95% | 0% | -224.2563 | 1701.3002 | -3550 | -400 | -2248.6998 | 56.22% | 46.53% | 95% | 0% | 2583 | -196
[5 empty] | 2019-09-24 | 23 | 6394.5 | 2344 | -235 | 1 | 0 | 2579 | 1919.291 | 1919.291 | 1919.291 | 865.1278 | 780 | 200 | 1845.1278 | 46.13% | 95% | 0% | -268.8787 | 1650.4123 | -3550 | -400 | -2299.5877 | 57.49% | 46.53% | 95% | 0% | 2579 | -235
[5 empty] | 2019-09-24 | 24 | 6395 | 2241 | -305 | 1 | 0 | 2546 | 1867.601 | 1867.601 | 1867.601 | 865.1278 | 780 | 200 | 1845.1278 | 46.13% | 95% | 0% | -348.9703 | 1518.6307 | -3550 | -400 | -2431.3693 | 60.78% | 46.53% | 95% | 0% | 2546 | -305
[5 empty] | 2019-09-24 | 25 | 6395.5 | 2157 | -364 | 1 | 0 | 2521 | 1828.4419 | 1828.4419 | 1828.4419 | 865.1278 | 780 | 200 | 1845.1278 | 46.13% | 95% | 0% | -416.476 | 1411.9659 | -3550 | -400 | -2538.0341 | 63.45% | 46.52% | 95% | 0% | 2521 | -364
[5 empty] | 2019-09-24 | 26 | 6396 | 2095 | -380 | 1 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 863.5614 | 780 | 200 | 1843.5614 | 46.09% | 95% | 0% | -434.7826 | 1321.6065 | -3550 | -400 | -2628.3935 | 65.71% | 46.52% | 95% | 0% | 2475 | -380
[5 empty] | 2019-09-24 | 27 | 6396.5 | 2023 | -400 | 1 | 0 | 2423 | 1674.9382 | 1674.9382 | 1674.9382 | 863.5614 | 780 | 200 | 1843.5614 | 46.09% | 95% | 0% | -457.6659 | 1217.2723 | -3550 | -400 | -2732.7277 | 68.32% | 46.52% | 95% | 0% | 2423 | -400
[5 empty] | 2019-09-24 | 28 | 6397 | 1955 | -436 | 1 | 0 | 2391 | 1624.8145 | 1624.8145 | 1624.8145 | 863.5614 | 780 | 200 | 1843.5614 | 46.09% | 95% | 0% | -498.8558 | 1125.9587 | -3550 | -400 | -2824.0413 | 70.6% | 46.51% | 95% | 0% | 2391 | -436
[5 empty] | 2019-09-24 | 29 | 6397.5 | 1983 | -403 | 1 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 863.5614 | 780 | 200 | 1843.5614 | 46.09% | 95% | 0% | -461.0984 | 1155.8843 | -3550 | -400 | -2794.1157 | 69.85% | 46.51% | 95% | 0% | 2386 | -403
[5 empty] | 2019-09-24 | 30 | 6398 | 2014 | -361 | 1 | 0 | 2375 | 1599.7527 | 1599.7527 | 1599.7527 | 863.5614 | 780 | 200 | 1843.5614 | 46.09% | 95% | 0% | -413.0435 | 1186.7092 | -3550 | -400 | -2763.2908 | 69.08% | 46.51% | 95% | 0% | 2375 | -361
[5 empty] | 2019-09-24 | 31 | 6398.5 | 2032 | -328 | 1 | 0 | 2360 | 1576.2572 | 1576.2572 | 1576.2572 | 863.5614 | 780 | 200 | 1843.5614 | 46.09% | 95% | 0% | -375.286 | 1200.9712 | -3550 | -400 | -2749.0288 | 68.73% | 46.5% | 95% | 0% | 2360 | -328
[5 empty] | 2019-09-24 | 32 | 6399 | 2140 | -282 | 1 | 0 | 2422 | 1673.3718 | 1673.3718 | 1673.3718 | 863.5614 | 780 | 200 | 1843.5614 | 46.09% | 95% | 0% | -322.6545 | 1350.7173 | -3550 | -400 | -2599.2827 | 64.98% | 46.5% | 95% | 0% | 2422 | -282
[5 empty] | 2019-09-24 | 33 | 6399.5 | 2246 | -255 | 1 | 0 | 2501 | 1797.1146 | 1797.1146 | 1797.1146 | 863.5614 | 780 | 200 | 1843.5614 | 46.09% | 95% | 0% | -291.762 | 1505.3526 | -3550 | -400 | -2444.6474 | 61.12% | 46.49% | 95% | 0% | 2501 | -255
[5 empty] | 2019-09-24 | 34 | 6400 | 2351 | -224 | 1 | 0 | 2575 | 1913.0256 | 1913.0256 | 1913.0256 | 863.5614 | 780 | 200 | 1843.5614 | 46.09% | 95% | 0% | -256.2929 | 1656.7327 | -3550 | -400 | -2293.2673 | 57.33% | 46.49% | 95% | 0% | 2575 | -224
[5 empty] | 2019-09-24 | 35 | 6400.5 | 2478 | -171 | 1 | 0 | 2649 | 2028.9365 | 2028.9365 | 2028.9365 | 861.9951 | 780 | 200 | 1841.9951 | 46.05% | 95% | 0% | -195.6522 | 1833.2843 | -3550 | -400 | -2116.7157 | 52.92% | 46.48% | 95% | 0% | 2649 | -171
[5 empty] | 2019-09-24 | 36 | 6401 | 2554 | -127 | 1 | 0 | 2681 | 2079.0602 | 2079.0602 | 2079.0602 | 861.9951 | 780 | 200 | 1841.9951 | 46.05% | 95% | 0% | -145.3089 | 1933.7513 | -3550 | -400 | -2016.2487 | 50.41% | 46.48% | 95% | 0% | 2681 | -127
[5 empty] | 2019-09-24 | 37 | 6401.5 | 2568 | -104 | 1 | 0 | 2672 | 2064.9629 | 2064.9629 | 2064.9629 | 861.9951 | 780 | 200 | 1841.9951 | 46.05% | 95% | 0% | -118.9931 | 1945.9698 | -3550 | -400 | -2004.0302 | 50.1% | 46.47% | 95% | 0% | 2672 | -104
[5 empty] | 2019-09-24 | 38 | 6402 | 2595 | -88 | 1 | 0 | 2683 | 2082.1929 | 2082.1929 | 2082.1929 | 861.9951 | 780 | 200 | 1841.9951 | 46.05% | 95% | 0% | -100.6865 | 1981.5064 | -3550 | -400 | -1968.4936 | 49.21% | 46.46% | 95% | 0% | 2683 | -88
[5 empty] | 2019-09-24 | 39 | 6402.5 | 2654 | -83 | 1 | 0 | 2737 | 2166.7766 | 2166.7766 | 2166.7766 | 861.9951 | 780 | 200 | 1841.9951 | 46.05% | 95% | 0% | -94.9657 | 2071.8109 | -3550 | -400 | -1878.1891 | 46.95% | 46.46% | 95% | 0% | 2737 | -83
[5 empty] | 2019-09-24 | 40 | 6403 | 2642 | -82 | 1 | 0 | 2724 | 2146.4138 | 2146.4138 | 2146.4138 | 860.4287 | 780 | 200 | 1840.4287 | 46.01% | 95% | 0% | -93.8215 | 2052.5923 | -3550 | -400 | -1897.4077 | 47.44% | 46.46% | 95% | 0% | 2724 | -82
[5 empty] | 2019-09-24 | 41 | 6403.5 | 2561 | -81 | 0 | 0 | 2642 | 2017.972 | 2017.972 | 2017.972 | 860.4287 | 780 | 200 | 1840.4287 | 46.01% | 95% | 0% | -92.6773 | 1925.2946 | -2750 | -200 | -1024.7054 | 25.62% | 46.44% | 95% | 0% | 2642 | -81
[5 empty] | 2019-09-24 | 42 | 6404 | 2469 | -81 | 0 | 0 | 2550 | 1873.8664 | 1873.8664 | 1873.8664 | 860.4287 | 780 | 200 | 1840.4287 | 46.01% | 95% | 0% | -92.6773 | 1781.1891 | -2750 | -200 | -1168.8109 | 29.22% | 46.44% | 95% | 0% | 2550 | -81
[5 empty] | 2019-09-24 | 43 | 6404.5 | 2348 | -81 | 0 | 0 | 2429 | 1684.3364 | 1684.3364 | 1684.3364 | 860.4287 | 780 | 200 | 1840.4287 | 46.01% | 95% | 0% | -92.6773 | 1591.659 | -2750 | -200 | -1358.341 | 33.96% | 46.44% | 95% | 0% | 2429 | -81
[5 empty] | 2019-09-24 | 44 | 6405 | 2201 | -80 | 0 | 0 | 2281 | 1452.5144 | 1452.5144 | 1452.5144 | 860.4287 | 780 | 200 | 1840.4287 | 46.01% | 95% | 0% | -91.5332 | 1360.9812 | -2750 | -200 | -1589.0188 | 39.73% | 46.43% | 95% | 0% | 2281 | -80
[5 empty] | 2019-09-24 | 45 | 6405.5 | 2065 | -81 | 0 | 0 | 2146 | 1241.0552 | 1241.0552 | 1241.0552 | 860.4287 | 780 | 200 | 1840.4287 | 46.01% | 95% | 0% | -92.6773 | 1148.3779 | -2750 | -200 | -1801.6221 | 45.04% | 46.42% | 95% | 0% | 2146 | -81
[5 empty] | 2019-09-24 | 46 | 6406 | 1940 | -81 | 0 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 860.4287 | 780 | 200 | 1840.4287 | 46.01% | 95% | 0% | -92.6773 | 952.5823 | -2750 | -200 | -1997.4177 | 49.94% | 46.41% | 95% | 0% | 2021 | -81
[5 empty] | 2019-09-24 | 47 | 6406.5 | 1812 | -80 | 0 | 0 | 1892 | 843.1987 | 843.1987 | 843.1987 | 860.4287 | 780 | 200 | 1840.4287 | 46.01% | 95% | 0% | -91.5332 | 751.6655 | -2750 | -200 | -2198.3345 | 54.96% | 46.41% | 95% | 0% | 1892 | -80
[5 empty] | 2019-09-24 | 48 | 6407 | 1696 | -79 | 0 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 860.4287 | 780 | 200 | 1840.4287 | 46.01% | 95% | 0% | -90.389 | 569.545 | -2750 | -200 | -2380.455 | 59.51% | 46.41% | 95% | 0% | 1775 | -79
[5 empty] | 2019-09-25 | 1 | 6407.5 | 1612 | -80 | 0 | 0 | 1692 | 529.9258 | 529.9258 | 529.9258 | 860.4287 | 780 | 200 | 1840.4287 | 46.01% | 95% | 0% | -91.5332 | 438.3926 | -2750 | -200 | -2511.6074 | 62.79% | 46.4% | 95% | 0% | 1692 | -80
[5 empty] | 2019-09-25 | 2 | 6408 | 1563 | -80 | 0 | 0 | 1643 | 453.1739 | 453.1739 | 453.1739 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -91.5332 | 361.6408 | -2750 | -200 | -2588.3592 | 64.71% | 46.4% | 95% | 0% | 1643 | -80
[5 empty] | 2019-09-25 | 3 | 6408.5 | 1533 | -79 | 0 | 0 | 1612 | 404.6167 | 404.6167 | 404.6167 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -90.389 | 314.2276 | -2750 | -200 | -2635.7724 | 65.89% | 46.4% | 95% | 0% | 1612 | -79
[5 empty] | 2019-09-25 | 4 | 6409 | 1525 | -78 | 0 | 0 | 1603 | 390.5194 | 390.5194 | 390.5194 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -89.2449 | 301.2745 | -2750 | -200 | -2648.7255 | 66.22% | 46.4% | 95% | 0% | 1603 | -78
[5 empty] | 2019-09-25 | 5 | 6409.5 | 1507 | -77 | 0 | 0 | 1584 | 360.7585 | 360.7585 | 360.7585 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -88.1007 | 272.6578 | -2750 | -200 | -2677.3422 | 66.93% | 46.39% | 95% | 0% | 1584 | -77
[5 empty] | 2019-09-25 | 6 | 6410 | 1488 | -75 | 0 | 0 | 1563 | 327.8648 | 327.8648 | 327.8648 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -85.8124 | 242.0524 | -2750 | -200 | -2707.9476 | 67.7% | 46.39% | 95% | 0% | 1563 | -75
[5 empty] | 2019-09-25 | 7 | 6410.5 | 1479 | -73 | 0 | 0 | 1552 | 310.6348 | 310.6348 | 310.6348 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -83.524 | 227.1108 | -2750 | -200 | -2722.8892 | 68.07% | 46.39% | 95% | 0% | 1552 | -73
[5 empty] | 2019-09-25 | 8 | 6411 | 1470 | -72 | 0 | 0 | 1542 | 294.9711 | 294.9711 | 294.9711 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -82.3799 | 212.5913 | -2750 | -200 | -2737.4087 | 68.44% | 46.39% | 95% | 0% | 1542 | -72
[5 empty] | 2019-09-25 | 9 | 6411.5 | 1486 | -72 | 0 | 0 | 1558 | 320.033 | 320.033 | 320.033 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -82.3799 | 237.6531 | -2750 | -200 | -2712.3469 | 67.81% | 46.39% | 95% | 0% | 1558 | -72
[5 empty] | 2019-09-25 | 10 | 6412 | 1504 | -73 | 0 | 0 | 1577 | 349.7939 | 349.7939 | 349.7939 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -83.524 | 266.2699 | -2750 | -200 | -2683.7301 | 67.09% | 46.38% | 95% | 0% | 1577 | -73
[5 empty] | 2019-09-25 | 11 | 6412.5 | 1561 | -72 | 0 | 0 | 1633 | 437.5103 | 437.5103 | 437.5103 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -82.3799 | 355.1304 | -2750 | -200 | -2594.8696 | 64.87% | 46.38% | 95% | 0% | 1633 | -72
[5 empty] | 2019-09-25 | 12 | 6413 | 1658 | -72 | 0 | 0 | 1730 | 589.4477 | 589.4477 | 589.4477 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -82.3799 | 507.0678 | -2750 | -200 | -2442.9322 | 61.07% | 46.38% | 95% | 0% | 1730 | -72
[5 empty] | 2019-09-25 | 13 | 6413.5 | 1875 | -71 | 0 | 0 | 1946 | 927.7824 | 927.7824 | 927.7824 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -81.2357 | 846.5467 | -2750 | -200 | -2103.4533 | 52.59% | 46.38% | 95% | 0% | 1946 | -71
[5 empty] | 2019-09-25 | 14 | 6414 | 2111 | -70 | 0 | 0 | 2181 | 1295.878 | 1295.878 | 1295.878 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -80.0915 | 1215.7865 | -2750 | -200 | -1734.2135 | 43.36% | 46.38% | 95% | 0% | 2181 | -70
[5 empty] | 2019-09-25 | 15 | 6414.5 | 2344 | -71 | 0 | 0 | 2415 | 1662.4073 | 1662.4073 | 1662.4073 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -81.2357 | 1581.1716 | -2750 | -200 | -1368.8284 | 34.22% | 46.37% | 95% | 0% | 2415 | -71
[5 empty] | 2019-09-25 | 16 | 6415 | 2461 | -80 | 0 | 0 | 2541 | 1859.7692 | 1859.7692 | 1859.7692 | 858.8623 | 780 | 200 | 1838.8623 | 45.97% | 95% | 0% | -91.5332 | 1768.236 | -2750 | -200 | -1181.764 | 29.54% | 46.37% | 95% | 0% | 2541 | -80
[5 empty] | 2019-09-25 | 17 | 6415.5 | 2490 | -95 | 0 | 0 | 2585 | 1928.6892 | 1928.6892 | 1928.6892 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -108.6957 | 1819.9935 | -2750 | -200 | -1130.0065 | 28.25% | 46.37% | 95% | 0% | 2585 | -95
[5 empty] | 2019-09-25 | 18 | 6416 | 2471 | -119 | 1 | 0 | 2590 | 1936.521 | 1936.521 | 1936.521 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -136.1556 | 1800.3654 | -3550 | -400 | -2149.6346 | 53.74% | 46.36% | 95% | 0% | 2590 | -119
[5 empty] | 2019-09-25 | 19 | 6416.5 | 2460 | -151 | 1 | 0 | 2611 | 1969.4147 | 1969.4147 | 1969.4147 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -172.7689 | 1796.6458 | -3550 | -400 | -2153.3542 | 53.83% | 46.36% | 95% | 0% | 2611 | -151
[5 empty] | 2019-09-25 | 20 | 6417 | 2437 | -172 | 1 | 0 | 2609 | 1966.2819 | 1966.2819 | 1966.2819 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -196.7963 | 1769.4856 | -3550 | -400 | -2180.5144 | 54.51% | 46.35% | 95% | 0% | 2609 | -172
[5 empty] | 2019-09-25 | 21 | 6417.5 | 2363 | -201 | 1 | 0 | 2564 | 1895.7955 | 1895.7955 | 1895.7955 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -229.9771 | 1665.8184 | -3550 | -400 | -2284.1816 | 57.1% | 46.34% | 95% | 0% | 2564 | -201
[5 empty] | 2019-09-25 | 22 | 6418 | 2304 | -244 | 1 | 0 | 2548 | 1870.7337 | 1870.7337 | 1870.7337 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -279.1762 | 1591.5575 | -3550 | -400 | -2358.4425 | 58.96% | 46.34% | 95% | 0% | 2548 | -244
[5 empty] | 2019-09-25 | 23 | 6418.5 | 2263 | -288 | 1 | 0 | 2551 | 1875.4328 | 1875.4328 | 1875.4328 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -329.5195 | 1545.9134 | -3550 | -400 | -2404.0866 | 60.1% | 46.34% | 95% | 0% | 2551 | -288
[5 empty] | 2019-09-25 | 24 | 6419 | 2224 | -302 | 1 | 0 | 2526 | 1836.2737 | 1836.2737 | 1836.2737 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -345.5378 | 1490.7359 | -3550 | -400 | -2459.2641 | 61.48% | 46.33% | 95% | 0% | 2526 | -302
[5 empty] | 2019-09-25 | 25 | 6419.5 | 2188 | -329 | 1 | 0 | 2517 | 1822.1764 | 1822.1764 | 1822.1764 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -376.4302 | 1445.7462 | -3550 | -400 | -2504.2538 | 62.61% | 46.33% | 95% | 0% | 2517 | -329
[5 empty] | 2019-09-25 | 26 | 6420 | 2166 | -329 | 1 | 0 | 2495 | 1787.7164 | 1787.7164 | 1787.7164 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -376.4302 | 1411.2862 | -3550 | -400 | -2538.7138 | 63.47% | 46.33% | 95% | 0% | 2495 | -329
[5 empty] | 2019-09-25 | 27 | 6420.5 | 2126 | -329 | 1 | 0 | 2455 | 1725.0618 | 1725.0618 | 1725.0618 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -376.4302 | 1348.6316 | -3550 | -400 | -2601.3684 | 65.03% | 46.33% | 95% | 0% | 2455 | -329
[5 empty] | 2019-09-25 | 28 | 6421 | 2069 | -345 | 1 | 0 | 2414 | 1660.8409 | 1660.8409 | 1660.8409 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -394.7368 | 1266.104 | -3550 | -400 | -2683.896 | 67.1% | 46.32% | 95% | 0% | 2414 | -345
[5 empty] | 2019-09-25 | 29 | 6421.5 | 2060 | -351 | 1 | 0 | 2411 | 1656.1418 | 1656.1418 | 1656.1418 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -401.6018 | 1254.54 | -3550 | -400 | -2695.46 | 67.39% | 46.32% | 95% | 0% | 2411 | -351
[5 empty] | 2019-09-25 | 30 | 6422 | 2096 | -312 | 1 | 0 | 2408 | 1651.4427 | 1651.4427 | 1651.4427 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -356.9794 | 1294.4633 | -3550 | -400 | -2655.5367 | 66.39% | 46.3% | 95% | 0% | 2408 | -312
[5 empty] | 2019-09-25 | 31 | 6422.5 | 2139 | -287 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -328.3753 | 1351.262 | -3550 | -400 | -2598.738 | 64.97% | 46.3% | 95% | 0% | 2426 | -287
[5 empty] | 2019-09-25 | 32 | 6423 | 2199 | -274 | 1 | 0 | 2473 | 1753.2564 | 1753.2564 | 1753.2564 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -313.5011 | 1439.7552 | -3550 | -400 | -2510.2448 | 62.76% | 46.3% | 95% | 0% | 2473 | -274
[5 empty] | 2019-09-25 | 33 | 6423.5 | 2293 | -245 | 1 | 0 | 2538 | 1855.0701 | 1855.0701 | 1855.0701 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -280.3204 | 1574.7497 | -3550 | -400 | -2375.2503 | 59.38% | 46.3% | 95% | 0% | 2538 | -245
[5 empty] | 2019-09-25 | 34 | 6424 | 2413 | -201 | 1 | 0 | 2614 | 1974.1138 | 1974.1138 | 1974.1138 | 857.296 | 780 | 200 | 1837.296 | 45.93% | 95% | 0% | -229.9771 | 1744.1367 | -3550 | -400 | -2205.8633 | 55.15% | 46.3% | 95% | 0% | 2614 | -201
[5 empty] | 2019-09-25 | 35 | 6424.5 | 2514 | -172 | 1 | 0 | 2686 | 2086.892 | 2086.892 | 2086.892 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -196.7963 | 1890.0957 | -3550 | -400 | -2059.9043 | 51.5% | 46.29% | 95% | 0% | 2686 | -172
[5 empty] | 2019-09-25 | 36 | 6425 | 2578 | -128 | 1 | 0 | 2706 | 2118.2193 | 2118.2193 | 2118.2193 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -146.4531 | 1971.7662 | -3550 | -400 | -1978.2338 | 49.46% | 46.28% | 95% | 0% | 2706 | -128
[5 empty] | 2019-09-25 | 37 | 6425.5 | 2619 | -98 | 1 | 0 | 2717 | 2135.4493 | 2135.4493 | 2135.4493 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -112.1281 | 2023.3212 | -3550 | -400 | -1926.6788 | 48.17% | 46.28% | 95% | 0% | 2717 | -98
[5 empty] | 2019-09-25 | 38 | 6426 | 2644 | -85 | 1 | 0 | 2729 | 2154.2457 | 2154.2457 | 2154.2457 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -97.254 | 2056.9917 | -3550 | -400 | -1893.0083 | 47.33% | 46.28% | 95% | 0% | 2729 | -85
[5 empty] | 2019-09-25 | 39 | 6426.5 | 2686 | -88 | 1 | 0 | 2774 | 2224.7321 | 2224.7321 | 2224.7321 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -100.6865 | 2124.0456 | -3550 | -400 | -1825.9544 | 45.65% | 46.27% | 95% | 0% | 2774 | -88
[5 empty] | 2019-09-25 | 40 | 6427 | 2691 | -91 | 1 | 0 | 2782 | 2237.263 | 2237.263 | 2237.263 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -104.119 | 2133.144 | -3550 | -400 | -1816.856 | 45.42% | 46.26% | 95% | 0% | 2782 | -91
[5 empty] | 2019-09-25 | 41 | 6427.5 | 2609 | -95 | 0 | 0 | 2704 | 2115.0866 | 2115.0866 | 2115.0866 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -108.6957 | 2006.3909 | -2750 | -200 | -943.6091 | 23.59% | 46.25% | 95% | 0% | 2704 | -95
[5 empty] | 2019-09-25 | 42 | 6428 | 2494 | -98 | 0 | 0 | 2592 | 1939.6538 | 1939.6538 | 1939.6538 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -112.1281 | 1827.5256 | -2750 | -200 | -1122.4744 | 28.06% | 46.25% | 95% | 0% | 2592 | -98
[5 empty] | 2019-09-25 | 43 | 6428.5 | 2372 | -101 | 0 | 0 | 2473 | 1753.2564 | 1753.2564 | 1753.2564 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -115.5606 | 1637.6957 | -2750 | -200 | -1312.3043 | 32.81% | 46.24% | 95% | 0% | 2473 | -101
[5 empty] | 2019-09-25 | 44 | 6429 | 2233 | -104 | 0 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -118.9931 | 1421.2377 | -2750 | -200 | -1528.7623 | 38.22% | 46.23% | 95% | 0% | 2337 | -104
[5 empty] | 2019-09-25 | 45 | 6429.5 | 2071 | -107 | 0 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -122.4256 | 1168.7533 | -2750 | -200 | -1781.2467 | 44.53% | 46.23% | 95% | 0% | 2178 | -107
[5 empty] | 2019-09-25 | 46 | 6430 | 1930 | -110 | 0 | 0 | 2040 | 1075.0206 | 1075.0206 | 1075.0206 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -125.8581 | 949.1625 | -2750 | -200 | -2000.8375 | 50.02% | 46.22% | 95% | 0% | 2040 | -110
[5 empty] | 2019-09-25 | 47 | 6430.5 | 1772 | -112 | 0 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -128.1465 | 702.5213 | -2750 | -200 | -2247.4787 | 56.19% | 46.21% | 95% | 0% | 1884 | -112
[5 empty] | 2019-09-25 | 48 | 6431 | 1658 | -113 | 0 | 0 | 1771 | 653.6686 | 653.6686 | 653.6686 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -129.2906 | 524.378 | -2750 | -200 | -2425.622 | 60.64% | 46.2% | 95% | 0% | 1771 | -113
[5 empty] | 2019-09-26 | 1 | 6431.5 | 1562 | -117 | 0 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -133.8673 | 375.6958 | -2750 | -200 | -2574.3042 | 64.36% | 46.2% | 95% | 0% | 1679 | -117
[5 empty] | 2019-09-26 | 2 | 6432 | 1487 | -120 | 0 | 0 | 1607 | 396.7848 | 396.7848 | 396.7848 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -137.2998 | 259.4851 | -2750 | -200 | -2690.5149 | 67.26% | 46.19% | 95% | 0% | 1607 | -120
[5 empty] | 2019-09-26 | 3 | 6432.5 | 1458 | -124 | 0 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 855.7296 | 780 | 200 | 1835.7296 | 45.89% | 95% | 0% | -141.8764 | 215.7493 | -2750 | -200 | -2734.2507 | 68.36% | 46.18% | 95% | 0% | 1582 | -124
[5 empty] | 2019-09-26 | 4 | 6433 | 1453 | -128 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -146.4531 | 209.6063 | -2750 | -200 | -2740.3937 | 68.51% | 46.18% | 95% | 0% | 1581 | -128
[5 empty] | 2019-09-26 | 5 | 6433.5 | 1399 | -131 | 0 | 0 | 1530 | 276.1748 | 276.1748 | 276.1748 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -149.8856 | 126.2892 | -2750 | -200 | -2823.7108 | 70.59% | 46.18% | 95% | 0% | 1530 | -131
[5 empty] | 2019-09-26 | 6 | 6434 | 1372 | -133 | 0 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -152.1739 | 84.8418 | -2750 | -200 | -2865.1582 | 71.63% | 46.17% | 95% | 0% | 1505 | -133
[5 empty] | 2019-09-26 | 7 | 6434.5 | 1342 | -135 | 0 | 0 | 1477 | 193.1575 | 193.1575 | 193.1575 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -154.4622 | 38.6952 | -2750 | -200 | -2911.3048 | 72.78% | 46.17% | 95% | 0% | 1477 | -135
[5 empty] | 2019-09-26 | 8 | 6435 | 1323 | -138 | 0 | 0 | 1461 | 168.0956 | 168.0956 | 168.0956 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -157.8947 | 10.2009 | -2750 | -200 | -2939.7991 | 73.49% | 46.17% | 95% | 0% | 1461 | -138
[5 empty] | 2019-09-26 | 9 | 6435.5 | 1311 | -140 | 0 | 0 | 1451 | 152.432 | 152.432 | 152.432 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -160.1831 | -7.7511 | -2750 | -200 | -2957.7511 | 73.94% | 46.16% | 95% | 0% | 1451 | -140
[5 empty] | 2019-09-26 | 10 | 6436 | 1322 | -142 | 0 | 0 | 1464 | 172.7947 | 172.7947 | 172.7947 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -162.4714 | 10.3233 | -2750 | -200 | -2939.6767 | 73.49% | 46.16% | 95% | 0% | 1464 | -142
[5 empty] | 2019-09-26 | 11 | 6436.5 | 1379 | -141 | 0 | 0 | 1520 | 260.5111 | 260.5111 | 260.5111 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -161.3272 | 99.1839 | -2750 | -200 | -2850.8161 | 71.27% | 46.16% | 95% | 0% | 1520 | -141
[5 empty] | 2019-09-26 | 12 | 6437 | 1472 | -140 | 0 | 0 | 1612 | 404.6167 | 404.6167 | 404.6167 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -160.1831 | 244.4336 | -2750 | -200 | -2705.5664 | 67.64% | 46.16% | 95% | 0% | 1612 | -140
[5 empty] | 2019-09-26 | 13 | 6437.5 | 1669 | -139 | 0 | 0 | 1808 | 711.6241 | 711.6241 | 711.6241 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -159.0389 | 552.5852 | -2750 | -200 | -2397.4148 | 59.94% | 46.16% | 95% | 0% | 1808 | -139
[5 empty] | 2019-09-26 | 14 | 6438 | 1907 | -137 | 0 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -156.7506 | 924.5355 | -2750 | -200 | -2025.4645 | 50.64% | 46.15% | 95% | 0% | 2044 | -137
[5 empty] | 2019-09-26 | 15 | 6438.5 | 2139 | -138 | 0 | 0 | 2277 | 1446.249 | 1446.249 | 1446.249 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -157.8947 | 1288.3542 | -2750 | -200 | -1661.6458 | 41.54% | 46.15% | 95% | 0% | 2277 | -138
[5 empty] | 2019-09-26 | 16 | 6439 | 2234 | -153 | 0 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -175.0572 | 1443.4918 | -2750 | -200 | -1506.5082 | 37.66% | 46.15% | 95% | 0% | 2387 | -153
[5 empty] | 2019-09-26 | 17 | 6439.5 | 2242 | -191 | 0 | 0 | 2433 | 1690.6018 | 1690.6018 | 1690.6018 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -218.5355 | 1472.0663 | -2750 | -200 | -1477.9337 | 36.95% | 46.15% | 95% | 0% | 2433 | -191
[5 empty] | 2019-09-26 | 18 | 6440 | 2135 | -246 | 1 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -281.4645 | 1327.6863 | -3550 | -400 | -2622.3137 | 65.56% | 46.15% | 95% | 0% | 2381 | -246
[5 empty] | 2019-09-26 | 19 | 6440.5 | 2064 | -315 | 1 | 0 | 2379 | 1606.0181 | 1606.0181 | 1606.0181 | 854.1632 | 780 | 200 | 1834.1632 | 45.85% | 95% | 0% | -360.4119 | 1245.6062 | -3550 | -400 | -2704.3938 | 67.61% | 46.14% | 95% | 0% | 2379 | -315
[5 empty] | 2019-09-26 | 20 | 6441 | 1976 | -388 | 1 | 0 | 2364 | 1582.5227 | 1582.5227 | 1582.5227 | 852.5969 | 780 | 200 | 1832.5969 | 45.81% | 95% | 0% | -443.9359 | 1138.5867 | -3550 | -400 | -2811.4133 | 70.29% | 46.14% | 95% | 0% | 2364 | -388
[5 empty] | 2019-09-26 | 21 | 6441.5 | 1882 | -435 | 1 | 0 | 2317 | 1508.9035 | 1508.9035 | 1508.9035 | 852.5969 | 780 | 200 | 1832.5969 | 45.81% | 95% | 0% | -497.7117 | 1011.1919 | -3550 | -400 | -2938.8081 | 73.47% | 46.13% | 95% | 0% | 2317 | -435
[5 empty] | 2019-09-26 | 22 | 6442 | 1803 | -481 | 1 | 0 | 2284 | 1457.2135 | 1457.2135 | 1457.2135 | 852.5969 | 780 | 200 | 1832.5969 | 45.81% | 95% | 0% | -550.3432 | 906.8703 | -3550 | -400 | -3043.1297 | 76.08% | 46.13% | 95% | 0% | 2284 | -481
[5 empty] | 2019-09-26 | 23 | 6442.5 | 1741 | -517 | 1 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 852.5969 | 780 | 200 | 1832.5969 | 45.81% | 95% | 0% | -591.5332 | 824.9549 | -3550 | -400 | -3125.0451 | 78.13% | 46.12% | 95% | 0% | 2258 | -517
[5 empty] | 2019-09-26 | 24 | 6443 | 1671 | -553 | 1 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 852.5969 | 780 | 200 | 1832.5969 | 45.81% | 95% | 0% | -632.7231 | 730.5085 | -3550 | -400 | -3219.4915 | 80.49% | 46.12% | 95% | 0% | 2224 | -553
[5 empty] | 2019-09-26 | 25 | 6443.5 | 1686 | -539 | 1 | 0 | 2225 | 1364.798 | 1364.798 | 1364.798 | 852.5969 | 780 | 200 | 1832.5969 | 45.81% | 95% | 0% | -616.7048 | 748.0932 | -3550 | -400 | -3201.9068 | 80.05% | 46.11% | 95% | 0% | 2225 | -539
[5 empty] | 2019-09-26 | 26 | 6444 | 1611 | -580 | 1 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 852.5969 | 780 | 200 | 1832.5969 | 45.81% | 95% | 0% | -663.6156 | 647.9261 | -3550 | -400 | -3302.0739 | 82.55% | 46.11% | 95% | 0% | 2191 | -580
[5 empty] | 2019-09-26 | 27 | 6444.5 | 1616 | -541 | 1 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 852.5969 | 780 | 200 | 1832.5969 | 45.81% | 95% | 0% | -618.9931 | 639.2921 | -3550 | -400 | -3310.7079 | 82.77% | 46.1% | 95% | 0% | 2157 | -541
[5 empty] | 2019-09-26 | 28 | 6445 | 1595 | -546 | 1 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 852.5969 | 780 | 200 | 1832.5969 | 45.81% | 95% | 0% | -624.714 | 608.5095 | -3550 | -400 | -3341.4905 | 83.54% | 46.1% | 95% | 0% | 2141 | -546
[5 empty] | 2019-09-26 | 29 | 6445.5 | 1653 | -504 | 1 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 851.0305 | 780 | 200 | 1831.0305 | 45.78% | 95% | 0% | -576.659 | 681.6262 | -3550 | -400 | -3268.3738 | 81.71% | 46.1% | 95% | 0% | 2157 | -504
[5 empty] | 2019-09-26 | 30 | 6446 | 1653 | -474 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 851.0305 | 780 | 200 | 1831.0305 | 45.78% | 95% | 0% | -542.3341 | 668.9602 | -3550 | -400 | -3281.0398 | 82.03% | 46.1% | 95% | 0% | 2127 | -474
[5 empty] | 2019-09-26 | 31 | 6446.5 | 1665 | -475 | 1 | 0 | 2140 | 1231.657 | 1231.657 | 1231.657 | 851.0305 | 780 | 200 | 1831.0305 | 45.78% | 95% | 0% | -543.4783 | 688.1788 | -3550 | -400 | -3261.8212 | 81.55% | 46.1% | 95% | 0% | 2140 | -475
[5 empty] | 2019-09-26 | 32 | 6447 | 1763 | -438 | 1 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 851.0305 | 780 | 200 | 1831.0305 | 45.78% | 95% | 0% | -501.1442 | 826.0611 | -3550 | -400 | -3123.9389 | 78.1% | 46.09% | 95% | 0% | 2201 | -438
[5 empty] | 2019-09-26 | 33 | 6447.5 | 1894 | -382 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 851.0305 | 780 | 200 | 1831.0305 | 45.78% | 95% | 0% | -437.0709 | 1007.6117 | -3550 | -400 | -2942.3883 | 73.56% | 46.09% | 95% | 0% | 2276 | -382
[5 empty] | 2019-09-26 | 34 | 6448 | 2053 | -310 | 1 | 0 | 2363 | 1580.9563 | 1580.9563 | 1580.9563 | 851.0305 | 780 | 200 | 1831.0305 | 45.78% | 95% | 0% | -354.6911 | 1226.2652 | -3550 | -400 | -2723.7348 | 68.09% | 46.09% | 95% | 0% | 2363 | -310
[5 empty] | 2019-09-26 | 35 | 6448.5 | 2200 | -249 | 1 | 0 | 2449 | 1715.6636 | 1715.6636 | 1715.6636 | 851.0305 | 780 | 200 | 1831.0305 | 45.78% | 95% | 0% | -284.897 | 1430.7666 | -3550 | -400 | -2519.2334 | 62.98% | 46.09% | 95% | 0% | 2449 | -249
[5 empty] | 2019-09-26 | 36 | 6449 | 2295 | -208 | 1 | 0 | 2503 | 1800.2473 | 1800.2473 | 1800.2473 | 851.0305 | 780 | 200 | 1831.0305 | 45.78% | 95% | 0% | -237.9863 | 1562.2611 | -3550 | -400 | -2387.7389 | 59.69% | 46.09% | 95% | 0% | 2503 | -208
[5 empty] | 2019-09-26 | 37 | 6449.5 | 2371 | -167 | 1 | 0 | 2538 | 1855.0701 | 1855.0701 | 1855.0701 | 851.0305 | 780 | 200 | 1831.0305 | 45.78% | 95% | 0% | -191.0755 | 1663.9946 | -3550 | -400 | -2286.0054 | 57.15% | 46.09% | 95% | 0% | 2538 | -167
[5 empty] | 2019-09-26 | 38 | 6450 | 2414 | -141 | 1 | 0 | 2555 | 1881.6983 | 1881.6983 | 1881.6983 | 851.0305 | 780 | 200 | 1831.0305 | 45.78% | 95% | 0% | -161.3272 | 1720.371 | -3550 | -400 | -2229.629 | 55.74% | 46.08% | 95% | 0% | 2555 | -141
[5 empty] | 2019-09-26 | 39 | 6450.5 | 2491 | -137 | 1 | 0 | 2628 | 1996.0429 | 1996.0429 | 1996.0429 | 851.0305 | 780 | 200 | 1831.0305 | 45.78% | 95% | 0% | -156.7506 | 1839.2923 | -3550 | -400 | -2110.7077 | 52.77% | 46.08% | 95% | 0% | 2628 | -137
[5 empty] | 2019-09-26 | 40 | 6451 | 2472 | -134 | 1 | 0 | 2606 | 1961.5829 | 1961.5829 | 1961.5829 | 851.0305 | 780 | 200 | 1831.0305 | 45.78% | 95% | 0% | -153.3181 | 1808.2648 | -3550 | -400 | -2141.7352 | 53.54% | 46.08% | 95% | 0% | 2606 | -134
[5 empty] | 2019-09-26 | 41 | 6451.5 | 2393 | -133 | 0 | 0 | 2526 | 1836.2737 | 1836.2737 | 1836.2737 | 849.4641 | 780 | 200 | 1829.4641 | 45.74% | 95% | 0% | -152.1739 | 1684.0998 | -2750 | -200 | -1265.9002 | 31.65% | 46.08% | 95% | 0% | 2526 | -133
[5 empty] | 2019-09-26 | 42 | 6452 | 2312 | -133 | 0 | 0 | 2445 | 1709.3982 | 1709.3982 | 1709.3982 | 849.4641 | 780 | 200 | 1829.4641 | 45.74% | 95% | 0% | -152.1739 | 1557.2243 | -2750 | -200 | -1392.7757 | 34.82% | 46.08% | 95% | 0% | 2445 | -133
[5 empty] | 2019-09-26 | 43 | 6452.5 | 2209 | -132 | 0 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 849.4641 | 780 | 200 | 1829.4641 | 45.74% | 95% | 0% | -151.0297 | 1395.4665 | -2750 | -200 | -1554.5335 | 38.86% | 46.07% | 95% | 0% | 2341 | -132
[5 empty] | 2019-09-26 | 44 | 6453 | 2074 | -132 | 0 | 0 | 2206 | 1335.0371 | 1335.0371 | 1335.0371 | 849.4641 | 780 | 200 | 1829.4641 | 45.74% | 95% | 0% | -151.0297 | 1184.0073 | -2750 | -200 | -1765.9927 | 44.15% | 46.07% | 95% | 0% | 2206 | -132
[5 empty] | 2019-09-26 | 45 | 6453.5 | 1909 | -132 | 0 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 849.4641 | 780 | 200 | 1829.4641 | 45.74% | 95% | 0% | -151.0297 | 925.5572 | -2750 | -200 | -2024.4428 | 50.61% | 46.07% | 95% | 0% | 2041 | -132
[5 empty] | 2019-09-26 | 46 | 6454 | 1769 | -133 | 0 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 849.4641 | 780 | 200 | 1829.4641 | 45.74% | 95% | 0% | -152.1739 | 706.6884 | -2750 | -200 | -2243.3116 | 56.08% | 46.07% | 95% | 0% | 1902 | -133
[5 empty] | 2019-09-26 | 47 | 6454.5 | 1648 | -131 | 0 | 0 | 1779 | 666.1995 | 666.1995 | 666.1995 | 849.4641 | 780 | 200 | 1829.4641 | 45.74% | 95% | 0% | -149.8856 | 516.3139 | -2750 | -200 | -2433.6861 | 60.84% | 46.06% | 95% | 0% | 1779 | -131
[5 empty] | 2019-09-26 | 48 | 6455 | 1545 | -130 | 0 | 0 | 1675 | 503.2976 | 503.2976 | 503.2976 | 849.4641 | 780 | 200 | 1829.4641 | 45.74% | 95% | 0% | -148.7414 | 354.5562 | -2750 | -200 | -2595.4438 | 64.89% | 46.05% | 95% | 0% | 1675 | -130
[5 empty] | 2019-09-27 | 1 | 6455.5 | 1456 | -128 | 0 | 0 | 1584 | 360.7585 | 360.7585 | 360.7585 | 849.4641 | 780 | 200 | 1829.4641 | 45.74% | 95% | 0% | -146.4531 | 214.3054 | -2750 | -200 | -2735.6946 | 68.39% | 46.05% | 95% | 0% | 1584 | -128
[5 empty] | 2019-09-27 | 2 | 6456 | 1416 | -127 | 0 | 0 | 1543 | 296.5375 | 296.5375 | 296.5375 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -145.3089 | 151.2286 | -2750 | -200 | -2798.7714 | 69.97% | 46.05% | 95% | 0% | 1543 | -127
[5 empty] | 2019-09-27 | 3 | 6456.5 | 1385 | -126 | 0 | 0 | 1511 | 246.4138 | 246.4138 | 246.4138 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -144.1648 | 102.2491 | -2750 | -200 | -2847.7509 | 71.19% | 46.04% | 95% | 0% | 1511 | -126
[5 empty] | 2019-09-27 | 4 | 6457 | 1383 | -124 | 0 | 0 | 1507 | 240.1484 | 240.1484 | 240.1484 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -141.8764 | 98.272 | -2750 | -200 | -2851.728 | 71.29% | 46.04% | 95% | 0% | 1507 | -124
[5 empty] | 2019-09-27 | 5 | 6457.5 | 1363 | -122 | 0 | 0 | 1485 | 205.6884 | 205.6884 | 205.6884 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -139.5881 | 66.1003 | -2750 | -200 | -2883.8997 | 72.1% | 46.03% | 95% | 0% | 1485 | -122
[5 empty] | 2019-09-27 | 6 | 6458 | 1330 | -119 | 0 | 0 | 1449 | 149.2993 | 149.2993 | 149.2993 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -136.1556 | 13.1437 | -2750 | -200 | -2936.8563 | 73.42% | 46.03% | 95% | 0% | 1449 | -119
[5 empty] | 2019-09-27 | 7 | 6458.5 | 1305 | -117 | 0 | 0 | 1422 | 107.0074 | 107.0074 | 107.0074 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -133.8673 | -26.8599 | -2750 | -200 | -2976.8599 | 74.42% | 46.03% | 95% | 0% | 1422 | -117
[5 empty] | 2019-09-27 | 8 | 6459 | 1315 | -115 | 1 | 0 | 1430 | 119.5383 | 119.5383 | 119.5383 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -131.5789 | -12.0406 | -3550 | -400 | -3962.0406 | 99.05% | 46.03% | 95% | 0% | 1430 | -115
[5 empty] | 2019-09-27 | 9 | 6459.5 | 1331 | -113 | 1 | 0 | 1444 | 141.4674 | 141.4674 | 141.4674 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -129.2906 | 12.1768 | -3550 | -400 | -3937.8232 | 98.45% | 46.03% | 95% | 0% | 1444 | -113
[5 empty] | 2019-09-27 | 10 | 6460 | 1350 | -110 | 1 | 0 | 1460 | 166.5293 | 166.5293 | 166.5293 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -125.8581 | 40.6711 | -3550 | -400 | -3909.3289 | 97.73% | 46.02% | 95% | 0% | 1460 | -110
[5 empty] | 2019-09-27 | 11 | 6460.5 | 1403 | -107 | 1 | 0 | 1510 | 244.8475 | 244.8475 | 244.8475 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -122.4256 | 122.4219 | -3550 | -400 | -3827.5781 | 95.69% | 46.02% | 95% | 0% | 1510 | -107
[5 empty] | 2019-09-27 | 12 | 6461 | 1497 | -105 | 1 | 0 | 1602 | 388.953 | 388.953 | 388.953 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -120.1373 | 268.8157 | -3550 | -400 | -3681.1843 | 92.03% | 46.01% | 95% | 0% | 1602 | -105
[5 empty] | 2019-09-27 | 13 | 6461.5 | 1700 | -104 | 1 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -118.9931 | 586.3655 | -3550 | -400 | -3363.6345 | 84.09% | 46.01% | 95% | 0% | 1804 | -104
[5 empty] | 2019-09-27 | 14 | 6462 | 1912 | -104 | 1 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -118.9931 | 918.4347 | -3550 | -400 | -3031.5653 | 75.79% | 46.01% | 95% | 0% | 2016 | -104
[5 empty] | 2019-09-27 | 15 | 6462.5 | 2136 | -110 | 1 | 0 | 2246 | 1397.6917 | 1397.6917 | 1397.6917 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -125.8581 | 1271.8335 | -3550 | -400 | -2678.1665 | 66.95% | 46.01% | 95% | 0% | 2246 | -110
[5 empty] | 2019-09-27 | 16 | 6463 | 2216 | -138 | 1 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -157.8947 | 1408.9643 | -3550 | -400 | -2541.0357 | 63.53% | 46.01% | 95% | 0% | 2354 | -138
[5 empty] | 2019-09-27 | 17 | 6463.5 | 2218 | -188 | 1 | 0 | 2406 | 1648.31 | 1648.31 | 1648.31 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -215.103 | 1433.207 | -3550 | -400 | -2516.793 | 62.92% | 46.01% | 95% | 0% | 2406 | -188
[5 empty] | 2019-09-27 | 18 | 6464 | 2171 | -224 | 1 | 0 | 2395 | 1631.08 | 1631.08 | 1631.08 | 847.8978 | 780 | 200 | 1827.8978 | 45.7% | 95% | 0% | -256.2929 | 1374.7871 | -3550 | -400 | -2575.2129 | 64.38% | 46% | 95% | 0% | 2395 | -224
[5 empty] | 2019-09-27 | 19 | 6464.5 | 2124 | -273 | 1 | 0 | 2397 | 1634.2127 | 1634.2127 | 1634.2127 | 846.3314 | 780 | 200 | 1826.3314 | 45.66% | 95% | 0% | -312.357 | 1321.8557 | -3550 | -400 | -2628.1443 | 65.7% | 46% | 95% | 0% | 2397 | -273
[5 empty] | 2019-09-27 | 20 | 6465 | 2096 | -286 | 1 | 0 | 2382 | 1610.7172 | 1610.7172 | 1610.7172 | 846.3314 | 780 | 200 | 1826.3314 | 45.66% | 95% | 0% | -327.2311 | 1283.4861 | -3550 | -400 | -2666.5139 | 66.66% | 46% | 95% | 0% | 2382 | -286
[5 empty] | 2019-09-27 | 21 | 6465.5 | 2033 | -320 | 1 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 846.3314 | 780 | 200 | 1826.3314 | 45.66% | 95% | 0% | -366.1327 | 1199.1599 | -3550 | -400 | -2750.8401 | 68.77% | 46% | 95% | 0% | 2353 | -320
[5 empty] | 2019-09-27 | 22 | 6466 | 1997 | -323 | 1 | 0 | 2320 | 1513.6026 | 1513.6026 | 1513.6026 | 846.3314 | 780 | 200 | 1826.3314 | 45.66% | 95% | 0% | -369.5652 | 1144.0374 | -3550 | -400 | -2805.9626 | 70.15% | 46% | 95% | 0% | 2320 | -323
[5 empty] | 2019-09-27 | 23 | 6466.5 | 1961 | -335 | 1 | 0 | 2296 | 1476.0099 | 1476.0099 | 1476.0099 | 846.3314 | 780 | 200 | 1826.3314 | 45.66% | 95% | 0% | -383.2952 | 1092.7147 | -3550 | -400 | -2857.2853 | 71.43% | 45.99% | 95% | 0% | 2296 | -335
[5 empty] | 2019-09-27 | 24 | 6467 | 1988 | -324 | 1 | 0 | 2312 | 1501.0717 | 1501.0717 | 1501.0717 | 846.3314 | 780 | 200 | 1826.3314 | 45.66% | 95% | 0% | -370.7094 | 1130.3623 | -3550 | -400 | -2819.6377 | 70.49% | 45.99% | 95% | 0% | 2312 | -324
[5 empty] | 2019-09-27 | 25 | 6467.5 | 1999 | -338 | 1 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 846.3314 | 780 | 200 | 1826.3314 | 45.66% | 95% | 0% | -386.7277 | 1153.5031 | -3550 | -400 | -2796.4969 | 69.91% | 45.99% | 95% | 0% | 2337 | -338
[5 empty] | 2019-09-27 | 26 | 6468 | 1975 | -335 | 1 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 846.3314 | 780 | 200 | 1826.3314 | 45.66% | 95% | 0% | -383.2952 | 1114.6438 | -3550 | -400 | -2835.3562 | 70.88% | 45.99% | 95% | 0% | 2310 | -335
[5 empty] | 2019-09-27 | 27 | 6468.5 | 1919 | -368 | 1 | 0 | 2287 | 1461.9126 | 1461.9126 | 1461.9126 | 846.3314 | 780 | 200 | 1826.3314 | 45.66% | 95% | 0% | -421.0526 | 1040.86 | -3550 | -400 | -2909.14 | 72.73% | 45.98% | 95% | 0% | 2287 | -368
[5 empty] | 2019-09-27 | 28 | 6469 | 1876 | -387 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 846.3314 | 780 | 200 | 1826.3314 | 45.66% | 95% | 0% | -442.7918 | 981.5281 | -3550 | -400 | -2968.4719 | 74.21% | 45.98% | 95% | 0% | 2263 | -387
[5 empty] | 2019-09-27 | 29 | 6469.5 | 1852 | -384 | 1 | 0 | 2236 | 1382.028 | 1382.028 | 1382.028 | 846.3314 | 780 | 200 | 1826.3314 | 45.66% | 95% | 0% | -439.3593 | 942.6688 | -3550 | -400 | -3007.3312 | 75.18% | 45.98% | 95% | 0% | 2236 | -384
[5 empty] | 2019-09-27 | 30 | 6470 | 1863 | -360 | 1 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 846.3314 | 780 | 200 | 1826.3314 | 45.66% | 95% | 0% | -411.8993 | 949.766 | -3550 | -400 | -3000.234 | 75.01% | 45.97% | 95% | 0% | 2223 | -360
[5 empty] | 2019-09-27 | 31 | 6470.5 | 1852 | -374 | 1 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -427.9176 | 938.4468 | -3550 | -400 | -3011.5532 | 75.29% | 45.97% | 95% | 0% | 2226 | -374
[5 empty] | 2019-09-27 | 32 | 6471 | 1933 | -319 | 1 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -364.9886 | 1042.1013 | -3550 | -400 | -2907.8987 | 72.7% | 45.96% | 95% | 0% | 2252 | -319
[5 empty] | 2019-09-27 | 33 | 6471.5 | 1972 | -314 | 1 | 0 | 2286 | 1460.3462 | 1460.3462 | 1460.3462 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -359.2677 | 1101.0785 | -3550 | -400 | -2848.9215 | 71.22% | 45.96% | 95% | 0% | 2286 | -314
[5 empty] | 2019-09-27 | 34 | 6472 | 2054 | -290 | 1 | 0 | 2344 | 1551.1954 | 1551.1954 | 1551.1954 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -331.8078 | 1219.3876 | -3550 | -400 | -2730.6124 | 68.27% | 45.96% | 95% | 0% | 2344 | -290
[5 empty] | 2019-09-27 | 35 | 6472.5 | 2156 | -244 | 1 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -279.1762 | 1359.7356 | -3550 | -400 | -2590.2644 | 64.76% | 45.96% | 95% | 0% | 2400 | -244
[5 empty] | 2019-09-27 | 36 | 6473 | 2251 | -191 | 1 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -218.5355 | 1486.1636 | -3550 | -400 | -2463.8364 | 61.6% | 45.95% | 95% | 0% | 2442 | -191
[5 empty] | 2019-09-27 | 37 | 6473.5 | 2334 | -147 | 1 | 0 | 2481 | 1765.7873 | 1765.7873 | 1765.7873 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -168.1922 | 1597.5951 | -3550 | -400 | -2352.4049 | 58.81% | 45.94% | 95% | 0% | 2481 | -147
[5 empty] | 2019-09-27 | 38 | 6474 | 2377 | -124 | 1 | 0 | 2501 | 1797.1146 | 1797.1146 | 1797.1146 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -141.8764 | 1655.2382 | -3550 | -400 | -2294.7618 | 57.37% | 45.94% | 95% | 0% | 2501 | -124
[5 empty] | 2019-09-27 | 39 | 6474.5 | 2434 | -120 | 1 | 0 | 2554 | 1880.1319 | 1880.1319 | 1880.1319 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -137.2998 | 1742.8321 | -3550 | -400 | -2207.1679 | 55.18% | 45.94% | 95% | 0% | 2554 | -120
[5 empty] | 2019-09-27 | 40 | 6475 | 2434 | -119 | 0 | 0 | 2553 | 1878.5655 | 1878.5655 | 1878.5655 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -136.1556 | 1742.4099 | -2750 | -200 | -1207.5901 | 30.19% | 45.93% | 95% | 0% | 2553 | -119
[5 empty] | 2019-09-27 | 41 | 6475.5 | 2365 | -118 | 0 | 0 | 2483 | 1768.92 | 1768.92 | 1768.92 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -135.0114 | 1633.9086 | -2750 | -200 | -1316.0914 | 32.9% | 45.93% | 95% | 0% | 2483 | -118
[5 empty] | 2019-09-27 | 42 | 6476 | 2260 | -116 | 0 | 0 | 2376 | 1601.319 | 1601.319 | 1601.319 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -132.7231 | 1468.5959 | -2750 | -200 | -1481.4041 | 37.04% | 45.93% | 95% | 0% | 2376 | -116
[5 empty] | 2019-09-27 | 43 | 6476.5 | 2141 | -116 | 0 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -132.7231 | 1282.1986 | -2750 | -200 | -1667.8014 | 41.7% | 45.92% | 95% | 0% | 2257 | -116
[5 empty] | 2019-09-27 | 44 | 6477 | 2019 | -115 | 0 | 0 | 2134 | 1222.2589 | 1222.2589 | 1222.2589 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -131.5789 | 1090.6799 | -2750 | -200 | -1859.3201 | 46.48% | 45.91% | 95% | 0% | 2134 | -115
[5 empty] | 2019-09-27 | 45 | 6477.5 | 1914 | -115 | 0 | 0 | 2029 | 1057.7906 | 1057.7906 | 1057.7906 | 844.765 | 780 | 200 | 1824.765 | 45.62% | 95% | 0% | -131.5789 | 926.2117 | -2750 | -200 | -2023.7883 | 50.59% | 45.91% | 95% | 0% | 2029 | -115
[5 empty] | 2019-09-27 | 46 | 6478 | 1806 | -115 | 0 | 0 | 1921 | 888.6232 | 888.6232 | 888.6232 | 843.1987 | 780 | 200 | 1823.1987 | 45.58% | 95% | 0% | -131.5789 | 757.0443 | -2750 | -200 | -2192.9557 | 54.82% | 45.9% | 95% | 0% | 1921 | -115
[5 empty] | 2019-09-27 | 47 | 6478.5 | 1683 | -115 | 1 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 843.1987 | 780 | 200 | 1823.1987 | 45.58% | 95% | 0% | -131.5789 | 564.3815 | -3550 | -400 | -3385.6185 | 84.64% | 45.9% | 95% | 0% | 1798 | -115
[5 empty] | 2019-09-27 | 48 | 6479 | 1586 | -114 | 1 | 0 | 1700 | 542.4567 | 542.4567 | 542.4567 | 843.1987 | 780 | 200 | 1823.1987 | 45.58% | 95% | 0% | -130.4348 | 412.0219 | -3550 | -400 | -3537.9781 | 88.45% | 45.9% | 95% | 0% | 1700 | -114
[5 empty] | 2019-09-28 | 1 | 6479.5 | 1493 | -111 | 1 | 0 | 1604 | 392.0857 | 392.0857 | 392.0857 | 843.1987 | 780 | 200 | 1823.1987 | 45.58% | 95% | 0% | -127.0023 | 265.0834 | -3550 | -400 | -3684.9166 | 92.12% | 45.89% | 95% | 0% | 1604 | -111
[5 empty] | 2019-09-28 | 2 | 6480 | 1433 | -108 | 1 | 0 | 1541 | 293.4048 | 293.4048 | 293.4048 | 843.1987 | 780 | 200 | 1823.1987 | 45.58% | 95% | 0% | -123.5698 | 169.835 | -3550 | -400 | -3780.165 | 94.5% | 45.89% | 95% | 0% | 1541 | -108
[5 empty] | 2019-09-28 | 3 | 6480.5 | 1397 | -108 | 1 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 843.1987 | 780 | 200 | 1823.1987 | 45.58% | 95% | 0% | -123.5698 | 113.4459 | -3550 | -400 | -3836.5541 | 95.91% | 45.89% | 95% | 0% | 1505 | -108
[5 empty] | 2019-09-28 | 4 | 6481 | 1379 | -108 | 1 | 0 | 1487 | 208.8211 | 208.8211 | 208.8211 | 843.1987 | 780 | 200 | 1823.1987 | 45.58% | 95% | 0% | -123.5698 | 85.2513 | -3550 | -400 | -3864.7487 | 96.62% | 45.89% | 95% | 0% | 1487 | -108
[5 empty] | 2019-09-28 | 5 | 6481.5 | 1346 | -108 | 1 | 0 | 1454 | 157.1311 | 157.1311 | 157.1311 | 843.1987 | 780 | 200 | 1823.1987 | 45.58% | 95% | 0% | -123.5698 | 33.5613 | -3550 | -400 | -3916.4387 | 97.91% | 45.88% | 95% | 0% | 1454 | -108
[5 empty] | 2019-09-28 | 6 | 6482 | 1311 | -109 | 1 | 0 | 1420 | 103.8747 | 103.8747 | 103.8747 | 843.1987 | 780 | 200 | 1823.1987 | 45.58% | 95% | 0% | -124.714 | -20.8393 | -3550 | -400 | -3970.8393 | 99.27% | 45.88% | 95% | 0% | 1420 | -109
[5 empty] | 2019-09-28 | 7 | 6482.5 | 1277 | -108 | 1 | 0 | 1385 | 49.0519 | 49.0519 | 49.0519 | 841.6323 | 780 | 200 | 1821.6323 | 45.54% | 95% | 0% | -123.5698 | -74.5179 | -3550 | -400 | -4024.5179 | 100.6% | 45.88% | 95% | 0% | 1385 | -108
[5 empty] | 2019-09-28 | 8 | 6483 | 1267 | -107 | 1 | 0 | 1374 | 31.8219 | 31.8219 | 31.8219 | 841.6323 | 780 | 200 | 1821.6323 | 45.54% | 95% | 0% | -122.4256 | -90.6037 | -3550 | -400 | -4040.6037 | 101% | 45.86% | 95% | 0% | 1374 | -107
[5 empty] | 2019-09-28 | 9 | 6483.5 | 1257 | -110 | 1 | 0 | 1367 | 20.8574 | 20.8574 | 20.8574 | 841.6323 | 780 | 200 | 1821.6323 | 45.54% | 95% | 0% | -125.8581 | -105.0007 | -3550 | -400 | -4055.0007 | 101.4% | 45.85% | 95% | 0% | 1367 | -110
[5 empty] | 2019-09-28 | 10 | 6484 | 1252 | -113 | 1 | 0 | 1365 | 17.7246 | 17.7246 | 17.7246 | 841.6323 | 780 | 200 | 1821.6323 | 45.54% | 95% | 0% | -129.2906 | -111.566 | -3550 | -400 | -4061.566 | 101.5% | 45.85% | 95% | 0% | 1365 | -113
[5 empty] | 2019-09-28 | 11 | 6484.5 | 1269 | -115 | 1 | 0 | 1384 | 47.4856 | 47.4856 | 47.4856 | 841.6323 | 780 | 200 | 1821.6323 | 45.54% | 95% | 0% | -131.5789 | -84.0934 | -3550 | -400 | -4034.0934 | 100.9% | 45.85% | 95% | 0% | 1384 | -115
[5 empty] | 2019-09-28 | 12 | 6485 | 1298 | -116 | 1 | 0 | 1414 | 94.4765 | 94.4765 | 94.4765 | 841.6323 | 780 | 200 | 1821.6323 | 45.54% | 95% | 0% | -132.7231 | -38.2466 | -3550 | -400 | -3988.2466 | 99.71% | 45.84% | 95% | 0% | 1414 | -116
[5 empty] | 2019-09-28 | 13 | 6485.5 | 1395 | -118 | 1 | 0 | 1513 | 249.5466 | 249.5466 | 249.5466 | 841.6323 | 780 | 200 | 1821.6323 | 45.54% | 95% | 0% | -135.0114 | 114.5351 | -3550 | -400 | -3835.4649 | 95.89% | 45.83% | 95% | 0% | 1513 | -118
[5 empty] | 2019-09-28 | 14 | 6486 | 1479 | -120 | 1 | 0 | 1599 | 384.2539 | 384.2539 | 384.2539 | 841.6323 | 780 | 200 | 1821.6323 | 45.54% | 95% | 0% | -137.2998 | 246.9541 | -3550 | -400 | -3703.0459 | 92.58% | 45.83% | 95% | 0% | 1599 | -120
[5 empty] | 2019-09-28 | 15 | 6486.5 | 1582 | -126 | 1 | 0 | 1708 | 554.9876 | 554.9876 | 554.9876 | 841.6323 | 780 | 200 | 1821.6323 | 45.54% | 95% | 0% | -144.1648 | 410.8229 | -3550 | -400 | -3539.1771 | 88.48% | 45.83% | 95% | 0% | 1708 | -126
[5 empty] | 2019-09-28 | 16 | 6487 | 1661 | -148 | 1 | 0 | 1809 | 713.1904 | 713.1904 | 713.1904 | 840.066 | 780 | 200 | 1820.066 | 45.5% | 95% | 0% | -169.3364 | 543.8541 | -3550 | -400 | -3406.1459 | 85.15% | 45.83% | 95% | 0% | 1809 | -148
[5 empty] | 2019-09-28 | 17 | 6487.5 | 1747 | -180 | 1 | 0 | 1927 | 898.0214 | 898.0214 | 898.0214 | 840.066 | 780 | 200 | 1820.066 | 45.5% | 95% | 0% | -205.9497 | 692.0718 | -3550 | -400 | -3257.9282 | 81.45% | 45.82% | 95% | 0% | 1927 | -180
[5 empty] | 2019-09-28 | 18 | 6488 | 1741 | -228 | 1 | 0 | 1969 | 963.8087 | 963.8087 | 963.8087 | 840.066 | 780 | 200 | 1820.066 | 45.5% | 95% | 0% | -260.8696 | 702.9392 | -3550 | -400 | -3247.0608 | 81.18% | 45.82% | 95% | 0% | 1969 | -228
[5 empty] | 2019-09-28 | 19 | 6488.5 | 1695 | -306 | 1 | 0 | 2001 | 1013.9324 | 1013.9324 | 1013.9324 | 840.066 | 780 | 200 | 1820.066 | 45.5% | 95% | 0% | -350.1144 | 663.818 | -3550 | -400 | -3286.182 | 82.15% | 45.81% | 95% | 0% | 2001 | -306
[5 empty] | 2019-09-28 | 20 | 6489 | 1640 | -359 | 1 | 0 | 1999 | 1010.7997 | 1010.7997 | 1010.7997 | 840.066 | 780 | 200 | 1820.066 | 45.5% | 95% | 0% | -410.7551 | 600.0445 | -3550 | -400 | -3349.9555 | 83.75% | 45.81% | 95% | 0% | 1999 | -359
[5 empty] | 2019-09-28 | 21 | 6489.5 | 1571 | -402 | 1 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 840.066 | 780 | 200 | 1820.066 | 45.5% | 95% | 0% | -459.9542 | 510.12 | -3550 | -400 | -3439.88 | 86% | 45.8% | 95% | 0% | 1973 | -402
[5 empty] | 2019-09-28 | 22 | 6490 | 1488 | -449 | 1 | 0 | 1937 | 913.6851 | 913.6851 | 913.6851 | 840.066 | 780 | 200 | 1820.066 | 45.5% | 95% | 0% | -513.73 | 399.9551 | -3550 | -400 | -3550.0449 | 88.75% | 45.8% | 95% | 0% | 1937 | -449
[5 empty] | 2019-09-28 | 23 | 6490.5 | 1462 | -474 | 1 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 840.066 | 780 | 200 | 1820.066 | 45.5% | 95% | 0% | -542.3341 | 369.7846 | -3550 | -400 | -3580.2154 | 89.51% | 45.8% | 95% | 0% | 1936 | -474
[5 empty] | 2019-09-28 | 24 | 6491 | 1444 | -490 | 1 | 0 | 1934 | 908.986 | 908.986 | 908.986 | 840.066 | 780 | 200 | 1820.066 | 45.5% | 95% | 0% | -560.6407 | 348.3453 | -3550 | -400 | -3601.6547 | 90.04% | 45.8% | 95% | 0% | 1934 | -490
[5 empty] | 2019-09-28 | 25 | 6491.5 | 1413 | -507 | 1 | 0 | 1920 | 887.0569 | 887.0569 | 887.0569 | 840.066 | 780 | 200 | 1820.066 | 45.5% | 95% | 0% | -580.0915 | 306.9654 | -3550 | -400 | -3643.0346 | 91.08% | 45.8% | 95% | 0% | 1920 | -507
[5 empty] | 2019-09-28 | 26 | 6492 | 1348 | -532 | 1 | 0 | 1880 | 824.4023 | 824.4023 | 824.4023 | 840.066 | 780 | 200 | 1820.066 | 45.5% | 95% | 0% | -608.6957 | 215.7067 | -3550 | -400 | -3734.2933 | 93.36% | 45.78% | 95% | 0% | 1880 | -532
[5 empty] | 2019-09-28 | 27 | 6492.5 | 1333 | -511 | 1 | 0 | 1844 | 768.0132 | 768.0132 | 768.0132 | 840.066 | 780 | 200 | 1820.066 | 45.5% | 95% | 0% | -584.6682 | 183.345 | -3550 | -400 | -3766.655 | 94.17% | 45.78% | 95% | 0% | 1844 | -511
[5 empty] | 2019-09-28 | 28 | 6493 | 1300 | -518 | 1 | 0 | 1818 | 727.2877 | 727.2877 | 727.2877 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -592.6773 | 134.6104 | -3550 | -400 | -3815.3896 | 95.38% | 45.78% | 95% | 0% | 1818 | -518
[5 empty] | 2019-09-28 | 29 | 6493.5 | 1336 | -473 | 1 | 0 | 1809 | 713.1904 | 713.1904 | 713.1904 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -541.1899 | 172.0005 | -3550 | -400 | -3777.9995 | 94.45% | 45.77% | 95% | 0% | 1809 | -473
[5 empty] | 2019-09-28 | 30 | 6494 | 1392 | -436 | 1 | 0 | 1828 | 742.9514 | 742.9514 | 742.9514 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -498.8558 | 244.0955 | -3550 | -400 | -3705.9045 | 92.65% | 45.76% | 95% | 0% | 1828 | -436
[5 empty] | 2019-09-28 | 31 | 6494.5 | 1494 | -378 | 1 | 0 | 1872 | 811.8714 | 811.8714 | 811.8714 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -432.4943 | 379.3771 | -3550 | -400 | -3570.6229 | 89.27% | 45.74% | 95% | 0% | 1872 | -378
[5 empty] | 2019-09-28 | 32 | 6495 | 1586 | -321 | 1 | 0 | 1907 | 866.6941 | 866.6941 | 866.6941 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -367.2769 | 499.4173 | -3550 | -400 | -3450.5827 | 86.26% | 45.74% | 95% | 0% | 1907 | -321
[5 empty] | 2019-09-28 | 33 | 6495.5 | 1734 | -256 | 1 | 0 | 1990 | 996.7024 | 996.7024 | 996.7024 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -292.9062 | 703.7962 | -3550 | -400 | -3246.2038 | 81.16% | 45.74% | 95% | 0% | 1990 | -256
[5 empty] | 2019-09-28 | 34 | 6496 | 1907 | -191 | 1 | 0 | 2098 | 1165.8697 | 1165.8697 | 1165.8697 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -218.5355 | 947.3343 | -3550 | -400 | -3002.6657 | 75.07% | 45.74% | 95% | 0% | 2098 | -191
[5 empty] | 2019-09-28 | 35 | 6496.5 | 2088 | -146 | 1 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -167.0481 | 1211.8472 | -3550 | -400 | -2738.1528 | 68.45% | 45.73% | 95% | 0% | 2234 | -146
[5 empty] | 2019-09-28 | 36 | 6497 | 2190 | -109 | 1 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -124.714 | 1355.995 | -3550 | -400 | -2594.005 | 64.85% | 45.72% | 95% | 0% | 2299 | -109
[5 empty] | 2019-09-28 | 37 | 6497.5 | 2267 | -89 | 1 | 0 | 2356 | 1569.9918 | 1569.9918 | 1569.9918 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -101.8307 | 1468.1611 | -3550 | -400 | -2481.8389 | 62.05% | 45.72% | 95% | 0% | 2356 | -89
[5 empty] | 2019-09-28 | 38 | 6498 | 2319 | -79 | 1 | 0 | 2398 | 1635.7791 | 1635.7791 | 1635.7791 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -90.389 | 1545.39 | -3550 | -400 | -2404.61 | 60.12% | 45.71% | 95% | 0% | 2398 | -79
[5 empty] | 2019-09-28 | 39 | 6498.5 | 2333 | -79 | 1 | 0 | 2412 | 1657.7082 | 1657.7082 | 1657.7082 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -90.389 | 1567.3191 | -3550 | -400 | -2382.6809 | 59.57% | 45.71% | 95% | 0% | 2412 | -79
[5 empty] | 2019-09-28 | 40 | 6499 | 2295 | -79 | 1 | 0 | 2374 | 1598.1863 | 1598.1863 | 1598.1863 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -90.389 | 1507.7973 | -3550 | -400 | -2442.2027 | 61.06% | 45.7% | 95% | 0% | 2374 | -79
[5 empty] | 2019-09-28 | 41 | 6499.5 | 2266 | -80 | 0 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 838.4996 | 780 | 200 | 1818.4996 | 45.46% | 95% | 0% | -91.5332 | 1462.7949 | -2750 | -200 | -1487.2051 | 37.18% | 45.7% | 95% | 0% | 2346 | -80
[5 empty] | 2019-09-28 | 42 | 6500 | 2179 | -80 | 0 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -91.5332 | 1326.5212 | -2750 | -200 | -1623.4788 | 40.59% | 45.7% | 95% | 0% | 2259 | -80
[5 empty] | 2019-09-28 | 43 | 6500.5 | 2111 | -80 | 0 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -91.5332 | 1220.0085 | -2750 | -200 | -1729.9915 | 43.25% | 45.7% | 95% | 0% | 2191 | -80
[5 empty] | 2019-09-28 | 44 | 6501 | 2006 | -81 | 0 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -92.6773 | 1055.9624 | -2750 | -200 | -1894.0376 | 47.35% | 45.69% | 95% | 0% | 2087 | -81
[5 empty] | 2019-09-28 | 45 | 6501.5 | 1920 | -84 | 0 | 0 | 2004 | 1018.6315 | 1018.6315 | 1018.6315 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -96.1098 | 922.5217 | -2750 | -200 | -2027.4783 | 50.69% | 45.69% | 95% | 0% | 2004 | -84
[5 empty] | 2019-09-28 | 46 | 6502 | 1825 | -87 | 0 | 0 | 1912 | 874.526 | 874.526 | 874.526 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -99.5423 | 774.9836 | -2750 | -200 | -2175.0164 | 54.38% | 45.69% | 95% | 0% | 1912 | -87
[5 empty] | 2019-09-28 | 47 | 6502.5 | 1722 | -90 | 0 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -102.9748 | 614.9147 | -2750 | -200 | -2335.0853 | 58.38% | 45.69% | 95% | 0% | 1812 | -90
[5 empty] | 2019-09-28 | 48 | 6503 | 1617 | -93 | 0 | 0 | 1710 | 558.1204 | 558.1204 | 558.1204 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -106.4073 | 451.713 | -2750 | -200 | -2498.287 | 62.46% | 45.68% | 95% | 0% | 1710 | -93
[5 empty] | 2019-09-29 | 1 | 6503.5 | 1509 | -100 | 0 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -114.4165 | 285.5011 | -2750 | -200 | -2664.4989 | 66.61% | 45.67% | 95% | 0% | 1609 | -100
[5 empty] | 2019-09-29 | 2 | 6504 | 1435 | -106 | 1 | 0 | 1541 | 293.4048 | 293.4048 | 293.4048 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -121.2815 | 172.1233 | -3550 | -400 | -3777.8767 | 94.45% | 45.67% | 95% | 0% | 1541 | -106
[5 empty] | 2019-09-29 | 3 | 6504.5 | 1386 | -110 | 1 | 0 | 1496 | 222.9184 | 222.9184 | 222.9184 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -125.8581 | 97.0603 | -3550 | -400 | -3852.9397 | 96.32% | 45.66% | 95% | 0% | 1496 | -110
[5 empty] | 2019-09-29 | 4 | 6505 | 1352 | -115 | 1 | 0 | 1467 | 177.4938 | 177.4938 | 177.4938 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -131.5789 | 45.9149 | -3550 | -400 | -3904.0851 | 97.6% | 45.65% | 95% | 0% | 1467 | -115
[5 empty] | 2019-09-29 | 5 | 6505.5 | 1305 | -119 | 1 | 0 | 1424 | 110.1401 | 110.1401 | 110.1401 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -136.1556 | -26.0155 | -3550 | -400 | -3976.0155 | 99.4% | 45.65% | 95% | 0% | 1424 | -119
[5 empty] | 2019-09-29 | 6 | 6506 | 1261 | -124 | 1 | 0 | 1385 | 49.0519 | 49.0519 | 49.0519 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -141.8764 | -92.8245 | -3550 | -400 | -4042.8245 | 101.1% | 45.65% | 95% | 0% | 1385 | -124
[5 empty] | 2019-09-29 | 7 | 6506.5 | 1238 | -127 | 1 | 0 | 1365 | 17.7246 | 17.7246 | 17.7246 | 836.9332 | 780 | 200 | 1816.9332 | 45.42% | 95% | 0% | -145.3089 | -127.5843 | -3550 | -400 | -4077.5843 | 101.9% | 45.65% | 95% | 0% | 1365 | -127
[5 empty] | 2019-09-29 | 8 | 6507 | 1222 | -129 | 1 | 0 | 1351 | -4.2045 | -4.2045 | -4.2045 | 835.3669 | 780 | 200 | 1815.3669 | 45.38% | 95% | 0% | -147.5973 | -151.8017 | -3550 | -400 | -4101.8017 | 102.5% | 45.64% | 95% | 0% | 1351 | -129
[5 empty] | 2019-09-29 | 9 | 6507.5 | 1211 | -130 | 1 | 0 | 1341 | -19.8681 | -19.8681 | -19.8681 | 835.3669 | 780 | 200 | 1815.3669 | 45.38% | 95% | 0% | -148.7414 | -168.6095 | -3550 | -400 | -4118.6095 | 103% | 45.64% | 95% | 0% | 1341 | -130
[5 empty] | 2019-09-29 | 10 | 6508 | 1207 | -131 | 1 | 0 | 1338 | -24.5672 | -24.5672 | -24.5672 | 835.3669 | 780 | 200 | 1815.3669 | 45.38% | 95% | 0% | -149.8856 | -174.4528 | -3550 | -400 | -4124.4528 | 103.1% | 45.63% | 95% | 0% | 1338 | -131
[5 empty] | 2019-09-29 | 11 | 6508.5 | 1220 | -132 | 1 | 0 | 1352 | -2.6381 | -2.6381 | -2.6381 | 835.3669 | 780 | 200 | 1815.3669 | 45.38% | 95% | 0% | -151.0297 | -153.6678 | -3550 | -400 | -4103.6678 | 102.6% | 45.62% | 95% | 0% | 1352 | -132
[5 empty] | 2019-09-29 | 12 | 6509 | 1240 | -132 | 1 | 0 | 1372 | 28.6892 | 28.6892 | 28.6892 | 835.3669 | 780 | 200 | 1815.3669 | 45.38% | 95% | 0% | -151.0297 | -122.3405 | -3550 | -400 | -4072.3405 | 101.8% | 45.61% | 95% | 0% | 1372 | -132
[5 empty] | 2019-09-29 | 13 | 6509.5 | 1313 | -132 | 1 | 0 | 1445 | 143.0338 | 143.0338 | 143.0338 | 835.3669 | 780 | 200 | 1815.3669 | 45.38% | 95% | 0% | -151.0297 | -7.9959 | -3550 | -400 | -3957.9959 | 98.95% | 45.6% | 95% | 0% | 1445 | -132
[5 empty] | 2019-09-29 | 14 | 6510 | 1371 | -131 | 1 | 0 | 1502 | 232.3166 | 232.3166 | 232.3166 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -149.8856 | 82.431 | -3550 | -400 | -3867.569 | 96.69% | 45.6% | 95% | 0% | 1502 | -131
[5 empty] | 2019-09-29 | 15 | 6510.5 | 1450 | -132 | 1 | 0 | 1582 | 357.6257 | 357.6257 | 357.6257 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -151.0297 | 206.596 | -3550 | -400 | -3743.404 | 93.59% | 45.59% | 95% | 0% | 1582 | -132
[5 empty] | 2019-09-29 | 16 | 6511 | 1542 | -135 | 1 | 0 | 1677 | 506.4303 | 506.4303 | 506.4303 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -154.4622 | 351.9681 | -3550 | -400 | -3598.0319 | 89.95% | 45.59% | 95% | 0% | 1677 | -135
[5 empty] | 2019-09-29 | 17 | 6511.5 | 1653 | -149 | 1 | 0 | 1802 | 702.2259 | 702.2259 | 702.2259 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -170.4805 | 531.7453 | -3550 | -400 | -3418.2547 | 85.46% | 45.57% | 95% | 0% | 1802 | -149
[5 empty] | 2019-09-29 | 18 | 6512 | 1731 | -171 | 1 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -195.6522 | 663.2102 | -3550 | -400 | -3286.7898 | 82.17% | 45.57% | 95% | 0% | 1902 | -171
[5 empty] | 2019-09-29 | 19 | 6512.5 | 1774 | -205 | 1 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -234.5538 | 744.9186 | -3550 | -400 | -3205.0814 | 80.13% | 45.57% | 95% | 0% | 1979 | -205
[5 empty] | 2019-09-29 | 20 | 6513 | 1811 | -232 | 1 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -265.4462 | 814.2735 | -3550 | -400 | -3135.7265 | 78.39% | 45.56% | 95% | 0% | 2043 | -232
[5 empty] | 2019-09-29 | 21 | 6513.5 | 1824 | -256 | 1 | 0 | 2080 | 1137.6752 | 1137.6752 | 1137.6752 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -292.9062 | 844.769 | -3550 | -400 | -3105.231 | 77.63% | 45.56% | 95% | 0% | 2080 | -256
[5 empty] | 2019-09-29 | 22 | 6514 | 1785 | -296 | 1 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -338.6728 | 800.5688 | -3550 | -400 | -3149.4312 | 78.74% | 45.56% | 95% | 0% | 2081 | -296
[5 empty] | 2019-09-29 | 23 | 6514.5 | 1810 | -311 | 1 | 0 | 2121 | 1201.8961 | 1201.8961 | 1201.8961 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -355.8352 | 846.0609 | -3550 | -400 | -3103.9391 | 77.6% | 45.55% | 95% | 0% | 2121 | -311
[5 empty] | 2019-09-29 | 24 | 6515 | 1793 | -338 | 1 | 0 | 2131 | 1217.5598 | 1217.5598 | 1217.5598 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -386.7277 | 830.8321 | -3550 | -400 | -3119.1679 | 77.98% | 45.55% | 95% | 0% | 2131 | -338
[5 empty] | 2019-09-29 | 25 | 6515.5 | 1785 | -342 | 1 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -391.3043 | 819.99 | -3550 | -400 | -3130.01 | 78.25% | 45.55% | 95% | 0% | 2127 | -342
[5 empty] | 2019-09-29 | 26 | 6516 | 1765 | -347 | 1 | 0 | 2112 | 1187.7988 | 1187.7988 | 1187.7988 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -397.0252 | 790.7737 | -3550 | -400 | -3159.2263 | 78.98% | 45.55% | 95% | 0% | 2112 | -347
[5 empty] | 2019-09-29 | 27 | 6516.5 | 1723 | -358 | 1 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -409.611 | 729.6306 | -3550 | -400 | -3220.3694 | 80.51% | 45.53% | 95% | 0% | 2081 | -358
[5 empty] | 2019-09-29 | 28 | 6517 | 1699 | -351 | 1 | 0 | 2050 | 1090.6843 | 1090.6843 | 1090.6843 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -401.6018 | 689.0824 | -3550 | -400 | -3260.9176 | 81.52% | 45.53% | 95% | 0% | 2050 | -351
[5 empty] | 2019-09-29 | 29 | 6517.5 | 1704 | -353 | 1 | 0 | 2057 | 1101.6488 | 1101.6488 | 1101.6488 | 833.8005 | 780 | 200 | 1813.8005 | 45.35% | 95% | 0% | -403.8902 | 697.7586 | -3550 | -400 | -3252.2414 | 81.31% | 45.52% | 95% | 0% | 2057 | -353
[5 empty] | 2019-09-29 | 30 | 6518 | 1706 | -340 | 1 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -389.016 | 695.4028 | -3550 | -400 | -3254.5972 | 81.36% | 45.51% | 95% | 0% | 2046 | -340
[5 empty] | 2019-09-29 | 31 | 6518.5 | 1746 | -319 | 1 | 0 | 2065 | 1114.1797 | 1114.1797 | 1114.1797 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -364.9886 | 749.1912 | -3550 | -400 | -3200.8088 | 80.02% | 45.51% | 95% | 0% | 2065 | -319
[5 empty] | 2019-09-29 | 32 | 6519 | 1791 | -304 | 1 | 0 | 2095 | 1161.1707 | 1161.1707 | 1161.1707 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -347.8261 | 813.3446 | -3550 | -400 | -3136.6554 | 78.42% | 45.51% | 95% | 0% | 2095 | -304
[5 empty] | 2019-09-29 | 33 | 6519.5 | 1887 | -281 | 1 | 0 | 2168 | 1275.5153 | 1275.5153 | 1275.5153 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -321.5103 | 954.005 | -3550 | -400 | -2995.995 | 74.9% | 45.5% | 95% | 0% | 2168 | -281
[5 empty] | 2019-09-29 | 34 | 6520 | 1985 | -254 | 1 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -290.6178 | 1096.1093 | -3550 | -400 | -2853.8907 | 71.35% | 45.5% | 95% | 0% | 2239 | -254
[5 empty] | 2019-09-29 | 35 | 6520.5 | 2109 | -207 | 1 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -236.8421 | 1270.4951 | -3550 | -400 | -2679.5049 | 66.99% | 45.49% | 95% | 0% | 2316 | -207
[5 empty] | 2019-09-29 | 36 | 6521 | 2191 | -172 | 1 | 0 | 2363 | 1580.9563 | 1580.9563 | 1580.9563 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -196.7963 | 1384.16 | -3550 | -400 | -2565.84 | 64.15% | 45.49% | 95% | 0% | 2363 | -172
[5 empty] | 2019-09-29 | 37 | 6521.5 | 2246 | -149 | 1 | 0 | 2395 | 1631.08 | 1631.08 | 1631.08 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -170.4805 | 1460.5994 | -3550 | -400 | -2489.4006 | 62.24% | 45.47% | 95% | 0% | 2395 | -149
[5 empty] | 2019-09-29 | 38 | 6522 | 2284 | -136 | 1 | 0 | 2420 | 1670.2391 | 1670.2391 | 1670.2391 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -155.6064 | 1514.6327 | -3550 | -400 | -2435.3673 | 60.88% | 45.47% | 95% | 0% | 2420 | -136
[5 empty] | 2019-09-29 | 39 | 6522.5 | 2333 | -128 | 1 | 0 | 2461 | 1734.46 | 1734.46 | 1734.46 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -146.4531 | 1588.0069 | -3550 | -400 | -2361.9931 | 59.05% | 45.46% | 95% | 0% | 2461 | -128
[5 empty] | 2019-09-29 | 40 | 6523 | 2297 | -121 | 1 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -138.4439 | 1528.6624 | -3550 | -400 | -2421.3376 | 60.53% | 45.46% | 95% | 0% | 2418 | -121
[5 empty] | 2019-09-29 | 41 | 6523.5 | 2252 | -115 | 0 | 0 | 2367 | 1587.2218 | 1587.2218 | 1587.2218 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -131.5789 | 1455.6428 | -2750 | -200 | -1494.3572 | 37.36% | 45.46% | 95% | 0% | 2367 | -115
[5 empty] | 2019-09-29 | 42 | 6524 | 2202 | -109 | 0 | 0 | 2311 | 1499.5054 | 1499.5054 | 1499.5054 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -124.714 | 1374.7914 | -2750 | -200 | -1575.2086 | 39.38% | 45.45% | 95% | 0% | 2311 | -109
[5 empty] | 2019-09-29 | 43 | 6524.5 | 2119 | -104 | 0 | 0 | 2223 | 1361.6653 | 1361.6653 | 1361.6653 | 832.2341 | 780 | 200 | 1812.2341 | 45.31% | 95% | 0% | -118.9931 | 1242.6722 | -2750 | -200 | -1707.3278 | 42.68% | 45.45% | 95% | 0% | 2223 | -104
[5 empty] | 2019-09-29 | 44 | 6525 | 2008 | -100 | 0 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -114.4165 | 1067.1169 | -2750 | -200 | -1882.8831 | 47.07% | 45.45% | 95% | 0% | 2108 | -100
[5 empty] | 2019-09-29 | 45 | 6525.5 | 1891 | -96 | 0 | 0 | 1987 | 992.0033 | 992.0033 | 992.0033 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -109.8398 | 882.1635 | -2750 | -200 | -2067.8365 | 51.7% | 45.44% | 95% | 0% | 1987 | -96
[5 empty] | 2019-09-29 | 46 | 6526 | 1793 | -92 | 0 | 0 | 1885 | 832.2341 | 832.2341 | 832.2341 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -105.2632 | 726.971 | -2750 | -200 | -2223.029 | 55.58% | 45.44% | 95% | 0% | 1885 | -92
[5 empty] | 2019-09-29 | 47 | 6526.5 | 1669 | -88 | 0 | 0 | 1757 | 631.7395 | 631.7395 | 631.7395 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -100.6865 | 531.053 | -2750 | -200 | -2418.947 | 60.47% | 45.43% | 95% | 0% | 1757 | -88
[5 empty] | 2019-09-29 | 48 | 6527 | 1577 | -84 | 0 | 0 | 1661 | 481.3685 | 481.3685 | 481.3685 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -96.1098 | 385.2587 | -2750 | -200 | -2564.7413 | 64.12% | 45.43% | 95% | 0% | 1661 | -84
[5 empty] | 2019-09-30 | 1 | 6527.5 | 1514 | -81 | 0 | 0 | 1595 | 377.9885 | 377.9885 | 377.9885 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -92.6773 | 285.3111 | -2750 | -200 | -2664.6889 | 66.62% | 45.42% | 95% | 0% | 1595 | -81
[5 empty] | 2019-09-30 | 2 | 6528 | 1483 | -78 | 0 | 0 | 1561 | 324.7321 | 324.7321 | 324.7321 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -89.2449 | 235.4872 | -2750 | -200 | -2714.5128 | 67.86% | 45.42% | 95% | 0% | 1561 | -78
[5 empty] | 2019-09-30 | 3 | 6528.5 | 1470 | -77 | 0 | 0 | 1547 | 302.803 | 302.803 | 302.803 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -88.1007 | 214.7023 | -2750 | -200 | -2735.2977 | 68.38% | 45.42% | 95% | 0% | 1547 | -77
[5 empty] | 2019-09-30 | 4 | 6529 | 1470 | -76 | 0 | 0 | 1546 | 301.2366 | 301.2366 | 301.2366 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -86.9565 | 214.2801 | -2750 | -200 | -2735.7199 | 68.39% | 45.41% | 95% | 0% | 1546 | -76
[5 empty] | 2019-09-30 | 5 | 6529.5 | 1458 | -76 | 0 | 0 | 1534 | 282.4402 | 282.4402 | 282.4402 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -86.9565 | 195.4837 | -2750 | -200 | -2754.5163 | 68.86% | 45.41% | 95% | 0% | 1534 | -76
[5 empty] | 2019-09-30 | 6 | 6530 | 1431 | -76 | 0 | 0 | 1507 | 240.1484 | 240.1484 | 240.1484 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -86.9565 | 153.1919 | -2750 | -200 | -2796.8081 | 69.92% | 45.41% | 95% | 0% | 1507 | -76
[5 empty] | 2019-09-30 | 7 | 6530.5 | 1421 | -76 | 0 | 0 | 1497 | 224.4847 | 224.4847 | 224.4847 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -86.9565 | 137.5282 | -2750 | -200 | -2812.4718 | 70.31% | 45.41% | 95% | 0% | 1497 | -76
[5 empty] | 2019-09-30 | 8 | 6531 | 1416 | -75 | 1 | 0 | 1491 | 215.0866 | 215.0866 | 215.0866 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -85.8124 | 129.2742 | -3550 | -400 | -3820.7258 | 95.52% | 45.41% | 95% | 0% | 1491 | -75
[5 empty] | 2019-09-30 | 9 | 6531.5 | 1428 | -74 | 1 | 0 | 1502 | 232.3166 | 232.3166 | 232.3166 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -84.6682 | 147.6484 | -3550 | -400 | -3802.3516 | 95.06% | 45.4% | 95% | 0% | 1502 | -74
[5 empty] | 2019-09-30 | 10 | 6532 | 1448 | -73 | 1 | 0 | 1521 | 262.0775 | 262.0775 | 262.0775 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -83.524 | 178.5535 | -3550 | -400 | -3771.4465 | 94.29% | 45.4% | 95% | 0% | 1521 | -73
[5 empty] | 2019-09-30 | 11 | 6532.5 | 1517 | -70 | 1 | 0 | 1587 | 365.4575 | 365.4575 | 365.4575 | 830.6678 | 780 | 200 | 1810.6678 | 45.27% | 95% | 0% | -80.0915 | 285.366 | -3550 | -400 | -3664.634 | 91.62% | 45.4% | 95% | 0% | 1587 | -70
[5 empty] | 2019-09-30 | 12 | 6533 | 1635 | -66 | 1 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 829.1014 | 780 | 200 | 1809.1014 | 45.23% | 95% | 0% | -75.5149 | 468.5082 | -3550 | -400 | -3481.4918 | 87.04% | 45.4% | 95% | 0% | 1701 | -66
[5 empty] | 2019-09-30 | 13 | 6533.5 | 1862 | -63 | 1 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 829.1014 | 780 | 200 | 1809.1014 | 45.23% | 95% | 0% | -72.0824 | 822.8063 | -3550 | -400 | -3127.1937 | 78.18% | 45.4% | 95% | 0% | 1925 | -63
[5 empty] | 2019-09-30 | 14 | 6534 | 2095 | -59 | 1 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 829.1014 | 780 | 200 | 1809.1014 | 45.23% | 95% | 0% | -67.5057 | 1186.0804 | -3550 | -400 | -2763.9196 | 69.1% | 45.39% | 95% | 0% | 2154 | -59
[5 empty] | 2019-09-30 | 15 | 6534.5 | 2349 | -60 | 1 | 0 | 2409 | 1653.0091 | 1653.0091 | 1653.0091 | 829.1014 | 780 | 200 | 1809.1014 | 45.23% | 95% | 0% | -68.6499 | 1584.3592 | -3550 | -400 | -2365.6408 | 59.14% | 45.39% | 95% | 0% | 2409 | -60
[5 empty] | 2019-09-30 | 16 | 6535 | 2454 | -83 | 1 | 0 | 2537 | 1853.5037 | 1853.5037 | 1853.5037 | 829.1014 | 780 | 200 | 1809.1014 | 45.23% | 95% | 0% | -94.9657 | 1758.538 | -3550 | -400 | -2191.462 | 54.79% | 45.39% | 95% | 0% | 2537 | -83
[5 empty] | 2019-09-30 | 17 | 6535.5 | 2478 | -120 | 1 | 0 | 2598 | 1949.0519 | 1949.0519 | 1949.0519 | 829.1014 | 780 | 200 | 1809.1014 | 45.23% | 95% | 0% | -137.2998 | 1811.7522 | -3550 | -400 | -2138.2478 | 53.46% | 45.39% | 95% | 0% | 2598 | -120
[5 empty] | 2019-09-30 | 18 | 6536 | 2432 | -159 | 1 | 0 | 2591 | 1938.0874 | 1938.0874 | 1938.0874 | 829.1014 | 780 | 200 | 1809.1014 | 45.23% | 95% | 0% | -181.9222 | 1756.1652 | -3550 | -400 | -2193.8348 | 54.85% | 45.38% | 95% | 0% | 2591 | -159
[5 empty] | 2019-09-30 | 19 | 6536.5 | 2380 | -215 | 1 | 0 | 2595 | 1944.3528 | 1944.3528 | 1944.3528 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -245.9954 | 1698.3574 | -3550 | -400 | -2251.6426 | 56.29% | 45.38% | 95% | 0% | 2595 | -215
[5 empty] | 2019-09-30 | 20 | 6537 | 2291 | -278 | 1 | 0 | 2569 | 1903.6274 | 1903.6274 | 1903.6274 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -318.0778 | 1585.5496 | -3550 | -400 | -2364.4504 | 59.11% | 45.38% | 95% | 0% | 2569 | -278
[5 empty] | 2019-09-30 | 21 | 6537.5 | 2204 | -320 | 1 | 0 | 2524 | 1833.141 | 1833.141 | 1833.141 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -366.1327 | 1467.0082 | -3550 | -400 | -2482.9918 | 62.07% | 45.38% | 95% | 0% | 2524 | -320
[5 empty] | 2019-09-30 | 22 | 6538 | 2160 | -343 | 1 | 0 | 2503 | 1800.2473 | 1800.2473 | 1800.2473 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -392.4485 | 1407.7988 | -3550 | -400 | -2542.2012 | 63.56% | 45.35% | 95% | 0% | 2503 | -343
[5 empty] | 2019-09-30 | 23 | 6538.5 | 2160 | -334 | 1 | 0 | 2494 | 1786.15 | 1786.15 | 1786.15 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -382.151 | 1403.999 | -3550 | -400 | -2546.001 | 63.65% | 45.35% | 95% | 0% | 2494 | -334
[5 empty] | 2019-09-30 | 24 | 6539 | 2127 | -362 | 1 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -414.1876 | 1364.1306 | -3550 | -400 | -2585.8694 | 64.65% | 45.35% | 95% | 0% | 2489 | -362
[5 empty] | 2019-09-30 | 25 | 6539.5 | 2159 | -355 | 1 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -406.1785 | 1411.2988 | -3550 | -400 | -2538.7012 | 63.47% | 45.35% | 95% | 0% | 2514 | -355
[5 empty] | 2019-09-30 | 26 | 6540 | 2181 | -340 | 1 | 0 | 2521 | 1828.4419 | 1828.4419 | 1828.4419 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -389.016 | 1439.4259 | -3550 | -400 | -2510.5741 | 62.76% | 45.35% | 95% | 0% | 2521 | -340
[5 empty] | 2019-09-30 | 27 | 6540.5 | 2191 | -308 | 1 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -352.4027 | 1441.5791 | -3550 | -400 | -2508.4209 | 62.71% | 45.34% | 95% | 0% | 2499 | -308
[5 empty] | 2019-09-30 | 28 | 6541 | 2251 | -245 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -280.3204 | 1508.9624 | -3550 | -400 | -2441.0376 | 61.03% | 45.34% | 95% | 0% | 2496 | -245
[5 empty] | 2019-09-30 | 29 | 6541.5 | 2353 | -198 | 1 | 0 | 2551 | 1875.4328 | 1875.4328 | 1875.4328 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -226.5446 | 1648.8882 | -3550 | -400 | -2301.1118 | 57.53% | 45.33% | 95% | 0% | 2551 | -198
[5 empty] | 2019-09-30 | 30 | 6542 | 2398 | -171 | 1 | 0 | 2569 | 1903.6274 | 1903.6274 | 1903.6274 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -195.6522 | 1707.9752 | -3550 | -400 | -2242.0248 | 56.05% | 45.33% | 95% | 0% | 2569 | -171
[5 empty] | 2019-09-30 | 31 | 6542.5 | 2445 | -142 | 1 | 0 | 2587 | 1931.8219 | 1931.8219 | 1931.8219 | 827.535 | 780 | 200 | 1807.535 | 45.19% | 95% | 0% | -162.4714 | 1769.3505 | -3550 | -400 | -2180.6495 | 54.52% | 45.33% | 95% | 0% | 2587 | -142
[5 empty] | 2019-09-30 | 32 | 6543 | 2513 | -128 | 1 | 0 | 2641 | 2016.4056 | 2016.4056 | 2016.4056 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -146.4531 | 1869.9525 | -3550 | -400 | -2080.0475 | 52% | 45.33% | 95% | 0% | 2641 | -128
[5 empty] | 2019-09-30 | 33 | 6543.5 | 2587 | -105 | 1 | 0 | 2692 | 2096.2902 | 2096.2902 | 2096.2902 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -120.1373 | 1976.1529 | -3550 | -400 | -1973.8471 | 49.35% | 45.33% | 95% | 0% | 2692 | -105
[5 empty] | 2019-09-30 | 34 | 6544 | 2688 | -95 | 1 | 0 | 2783 | 2238.8293 | 2238.8293 | 2238.8293 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -108.6957 | 2130.1337 | -3550 | -400 | -1819.8663 | 45.5% | 45.33% | 95% | 0% | 2783 | -95
[5 empty] | 2019-09-30 | 35 | 6544.5 | 2796 | -90 | 1 | 0 | 2886 | 2400.1649 | 2400.1649 | 2400.1649 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -102.9748 | 2297.1901 | -3550 | -400 | -1652.8099 | 41.32% | 45.32% | 95% | 0% | 2886 | -90
[5 empty] | 2019-09-30 | 36 | 6545 | 2846 | -85 | 1 | 0 | 2931 | 2470.6513 | 2470.6513 | 2470.6513 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -97.254 | 2373.3973 | -3550 | -400 | -1576.6027 | 39.42% | 45.32% | 95% | 0% | 2931 | -85
[5 empty] | 2019-09-30 | 37 | 6545.5 | 2850 | -87 | 1 | 0 | 2937 | 2480.0495 | 2480.0495 | 2480.0495 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -99.5423 | 2380.5071 | -3550 | -400 | -1569.4929 | 39.24% | 45.3% | 95% | 0% | 2937 | -87
[5 empty] | 2019-09-30 | 38 | 6546 | 2867 | -91 | 1 | 0 | 2958 | 2512.9431 | 2512.9431 | 2512.9431 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -104.119 | 2408.8241 | -3550 | -400 | -1541.1759 | 38.53% | 45.29% | 95% | 0% | 2958 | -91
[5 empty] | 2019-09-30 | 39 | 6546.5 | 2843 | -97 | 1 | 0 | 2940 | 2484.7486 | 2484.7486 | 2484.7486 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -110.984 | 2373.7646 | -3550 | -400 | -1576.2354 | 39.41% | 45.28% | 95% | 0% | 2940 | -97
[5 empty] | 2019-09-30 | 40 | 6547 | 2749 | -104 | 1 | 0 | 2853 | 2348.4749 | 2348.4749 | 2348.4749 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -118.9931 | 2229.4817 | -3550 | -400 | -1720.5183 | 43.01% | 45.28% | 95% | 0% | 2853 | -104
[5 empty] | 2019-09-30 | 41 | 6547.5 | 2615 | -109 | 0 | 0 | 2724 | 2146.4138 | 2146.4138 | 2146.4138 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -124.714 | 2021.6999 | -2750 | -200 | -928.3001 | 23.21% | 45.27% | 95% | 0% | 2724 | -109
[5 empty] | 2019-09-30 | 42 | 6548 | 2477 | -113 | 0 | 0 | 2590 | 1936.521 | 1936.521 | 1936.521 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -129.2906 | 1807.2304 | -2750 | -200 | -1142.7696 | 28.57% | 45.27% | 95% | 0% | 2590 | -113
[5 empty] | 2019-09-30 | 43 | 6548.5 | 2341 | -118 | 0 | 0 | 2459 | 1731.3273 | 1731.3273 | 1731.3273 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -135.0114 | 1596.3158 | -2750 | -200 | -1353.6842 | 33.84% | 45.27% | 95% | 0% | 2459 | -118
[5 empty] | 2019-09-30 | 44 | 6549 | 2171 | -122 | 0 | 0 | 2293 | 1471.3108 | 1471.3108 | 1471.3108 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -139.5881 | 1331.7227 | -2750 | -200 | -1618.2773 | 40.46% | 45.26% | 95% | 0% | 2293 | -122
[5 empty] | 2019-09-30 | 45 | 6549.5 | 2016 | -125 | 0 | 0 | 2141 | 1233.2234 | 1233.2234 | 1233.2234 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -143.0206 | 1090.2028 | -2750 | -200 | -1859.7972 | 46.49% | 45.26% | 95% | 0% | 2141 | -125
[5 empty] | 2019-09-30 | 46 | 6550 | 1865 | -127 | 0 | 0 | 1992 | 999.8351 | 999.8351 | 999.8351 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -145.3089 | 854.5262 | -2750 | -200 | -2095.4738 | 52.39% | 45.25% | 95% | 0% | 1992 | -127
[5 empty] | 2019-09-30 | 47 | 6550.5 | 1716 | -129 | 0 | 0 | 1845 | 769.5796 | 769.5796 | 769.5796 | 825.9687 | 780 | 200 | 1805.9687 | 45.15% | 95% | 0% | -147.5973 | 621.9823 | -2750 | -200 | -2328.0177 | 58.2% | 45.25% | 95% | 0% | 1845 | -129
[5 empty] | 2019-09-30 | 48 | 6551 | 1596 | -130 | 0 | 0 | 1726 | 583.1822 | 583.1822 | 583.1822 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -148.7414 | 434.4408 | -2750 | -200 | -2515.5592 | 62.89% | 45.25% | 95% | 0% | 1726 | -130
[5 empty] | 2019-10-01 | 1 | 6551.5 | 1518 | -133 | 0 | 0 | 1651 | 465.7049 | 465.7049 | 465.7049 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -152.1739 | 313.531 | -2750 | -200 | -2636.469 | 65.91% | 45.24% | 95% | 0% | 1651 | -133
[5 empty] | 2019-10-01 | 2 | 6552 | 1459 | -136 | 0 | 0 | 1595 | 377.9885 | 377.9885 | 377.9885 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -155.6064 | 222.3821 | -2750 | -200 | -2727.6179 | 68.19% | 45.24% | 95% | 0% | 1595 | -136
[5 empty] | 2019-10-01 | 3 | 6552.5 | 1426 | -136 | 0 | 0 | 1562 | 326.2984 | 326.2984 | 326.2984 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -155.6064 | 170.692 | -2750 | -200 | -2779.308 | 69.48% | 45.24% | 95% | 0% | 1562 | -136
[5 empty] | 2019-10-01 | 4 | 6553 | 1436 | -136 | 0 | 0 | 1572 | 341.9621 | 341.9621 | 341.9621 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -155.6064 | 186.3557 | -2750 | -200 | -2763.6443 | 69.09% | 45.24% | 95% | 0% | 1572 | -136
[5 empty] | 2019-10-01 | 5 | 6553.5 | 1415 | -135 | 0 | 0 | 1550 | 307.5021 | 307.5021 | 307.5021 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -154.4622 | 153.0398 | -2750 | -200 | -2796.9602 | 69.92% | 45.23% | 95% | 0% | 1550 | -135
[5 empty] | 2019-10-01 | 6 | 6554 | 1388 | -134 | 0 | 0 | 1522 | 263.6439 | 263.6439 | 263.6439 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -153.3181 | 110.3258 | -2750 | -200 | -2839.6742 | 70.99% | 45.23% | 95% | 0% | 1522 | -134
[5 empty] | 2019-10-01 | 7 | 6554.5 | 1372 | -133 | 0 | 0 | 1505 | 237.0157 | 237.0157 | 237.0157 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -152.1739 | 84.8418 | -2750 | -200 | -2865.1582 | 71.63% | 45.23% | 95% | 0% | 1505 | -133
[5 empty] | 2019-10-01 | 8 | 6555 | 1361 | -133 | 0 | 0 | 1494 | 219.7857 | 219.7857 | 219.7857 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -152.1739 | 67.6117 | -2750 | -200 | -2882.3883 | 72.06% | 45.22% | 95% | 0% | 1494 | -133
[5 empty] | 2019-10-01 | 9 | 6555.5 | 1374 | -130 | 0 | 0 | 1504 | 235.4493 | 235.4493 | 235.4493 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -148.7414 | 86.7079 | -2750 | -200 | -2863.2921 | 71.58% | 45.21% | 95% | 0% | 1504 | -130
[5 empty] | 2019-10-01 | 10 | 6556 | 1399 | -126 | 0 | 0 | 1525 | 268.343 | 268.343 | 268.343 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -144.1648 | 124.1782 | -2750 | -200 | -2825.8218 | 70.65% | 45.19% | 95% | 0% | 1525 | -126
[5 empty] | 2019-10-01 | 11 | 6556.5 | 1471 | -124 | 0 | 0 | 1595 | 377.9885 | 377.9885 | 377.9885 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -141.8764 | 236.112 | -2750 | -200 | -2713.888 | 67.85% | 45.19% | 95% | 0% | 1595 | -124
[5 empty] | 2019-10-01 | 12 | 6557 | 1589 | -123 | 0 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -140.7323 | 420.5208 | -2750 | -200 | -2529.4792 | 63.24% | 45.19% | 95% | 0% | 1712 | -123
[5 empty] | 2019-10-01 | 13 | 6557.5 | 1808 | -120 | 0 | 0 | 1928 | 899.5878 | 899.5878 | 899.5878 | 824.4023 | 780 | 200 | 1804.4023 | 45.11% | 95% | 0% | -137.2998 | 762.288 | -2750 | -200 | -2187.712 | 54.69% | 45.18% | 95% | 0% | 1928 | -120
[5 empty] | 2019-10-01 | 14 | 6558 | 2052 | -118 | 0 | 0 | 2170 | 1278.648 | 1278.648 | 1278.648 | 822.8359 | 780 | 200 | 1802.8359 | 45.07% | 95% | 0% | -135.0114 | 1143.6365 | -2750 | -200 | -1806.3635 | 45.16% | 45.18% | 95% | 0% | 2170 | -118
[5 empty] | 2019-10-01 | 15 | 6558.5 | 2279 | -117 | 0 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 822.8359 | 780 | 200 | 1802.8359 | 45.07% | 95% | 0% | -133.8673 | 1498.7791 | -2750 | -200 | -1451.2209 | 36.28% | 45.17% | 95% | 0% | 2396 | -117
[5 empty] | 2019-10-01 | 16 | 6559 | 2365 | -129 | 0 | 0 | 2494 | 1786.15 | 1786.15 | 1786.15 | 822.8359 | 780 | 200 | 1802.8359 | 45.07% | 95% | 0% | -147.5973 | 1638.5528 | -2750 | -200 | -1311.4472 | 32.79% | 45.17% | 95% | 0% | 2494 | -129
[5 empty] | 2019-10-01 | 17 | 6559.5 | 2398 | -152 | 0 | 0 | 2550 | 1873.8664 | 1873.8664 | 1873.8664 | 822.8359 | 780 | 200 | 1802.8359 | 45.07% | 95% | 0% | -173.913 | 1699.9534 | -2750 | -200 | -1250.0466 | 31.25% | 45.17% | 95% | 0% | 2550 | -152
[5 empty] | 2019-10-01 | 18 | 6560 | 2375 | -180 | 1 | 0 | 2555 | 1881.6983 | 1881.6983 | 1881.6983 | 822.8359 | 780 | 200 | 1802.8359 | 45.07% | 95% | 0% | -205.9497 | 1675.7486 | -3550 | -400 | -2274.2514 | 56.86% | 45.16% | 95% | 0% | 2555 | -180
[5 empty] | 2019-10-01 | 19 | 6560.5 | 2364 | -221 | 1 | 0 | 2585 | 1928.6892 | 1928.6892 | 1928.6892 | 822.8359 | 780 | 200 | 1802.8359 | 45.07% | 95% | 0% | -252.8604 | 1675.8288 | -3550 | -400 | -2274.1712 | 56.85% | 45.16% | 95% | 0% | 2585 | -221
[5 empty] | 2019-10-01 | 20 | 6561 | 2332 | -253 | 1 | 0 | 2585 | 1928.6892 | 1928.6892 | 1928.6892 | 822.8359 | 780 | 200 | 1802.8359 | 45.07% | 95% | 0% | -289.4737 | 1639.2155 | -3550 | -400 | -2310.7845 | 57.77% | 45.16% | 95% | 0% | 2585 | -253
[5 empty] | 2019-10-01 | 21 | 6561.5 | 2283 | -285 | 1 | 0 | 2568 | 1902.061 | 1902.061 | 1902.061 | 822.8359 | 780 | 200 | 1802.8359 | 45.07% | 95% | 0% | -326.087 | 1575.974 | -3550 | -400 | -2374.026 | 59.35% | 45.16% | 95% | 0% | 2568 | -285
[5 empty] | 2019-10-01 | 22 | 6562 | 2240 | -297 | 1 | 0 | 2537 | 1853.5037 | 1853.5037 | 1853.5037 | 822.8359 | 780 | 200 | 1802.8359 | 45.07% | 95% | 0% | -339.8169 | 1513.6868 | -3550 | -400 | -2436.3132 | 60.91% | 45.16% | 95% | 0% | 2537 | -297
[5 empty] | 2019-10-01 | 23 | 6562.5 | 2189 | -343 | 1 | 0 | 2532 | 1845.6719 | 1845.6719 | 1845.6719 | 822.8359 | 780 | 200 | 1802.8359 | 45.07% | 95% | 0% | -392.4485 | 1453.2234 | -3550 | -400 | -2496.7766 | 62.42% | 45.16% | 95% | 0% | 2532 | -343
[5 empty] | 2019-10-01 | 24 | 6563 | 2172 | -347 | 1 | 0 | 2519 | 1825.3092 | 1825.3092 | 1825.3092 | 822.8359 | 780 | 200 | 1802.8359 | 45.07% | 95% | 0% | -397.0252 | 1428.284 | -3550 | -400 | -2521.716 | 63.04% | 45.15% | 95% | 0% | 2519 | -347
[5 empty] | 2019-10-01 | 25 | 6563.5 | 2154 | -358 | 1 | 0 | 2512 | 1814.3446 | 1814.3446 | 1814.3446 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -409.611 | 1404.7336 | -3550 | -400 | -2545.2664 | 63.63% | 45.15% | 95% | 0% | 2512 | -358
[5 empty] | 2019-10-01 | 26 | 6564 | 2133 | -357 | 1 | 0 | 2490 | 1779.8846 | 1779.8846 | 1779.8846 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -408.4668 | 1371.4178 | -3550 | -400 | -2578.5822 | 64.46% | 45.14% | 95% | 0% | 2490 | -357
[5 empty] | 2019-10-01 | 27 | 6564.5 | 2097 | -382 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -437.0709 | 1325.5836 | -3550 | -400 | -2624.4164 | 65.61% | 45.13% | 95% | 0% | 2479 | -382
[5 empty] | 2019-10-01 | 28 | 6565 | 2068 | -393 | 1 | 0 | 2461 | 1734.46 | 1734.46 | 1734.46 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -449.6568 | 1284.8033 | -3550 | -400 | -2665.1967 | 66.63% | 45.13% | 95% | 0% | 2461 | -393
[5 empty] | 2019-10-01 | 29 | 6565.5 | 2092 | -377 | 1 | 0 | 2469 | 1746.9909 | 1746.9909 | 1746.9909 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -431.3501 | 1315.6408 | -3550 | -400 | -2634.3592 | 65.86% | 45.12% | 95% | 0% | 2469 | -377
[5 empty] | 2019-10-01 | 30 | 6566 | 2085 | -365 | 1 | 0 | 2450 | 1717.23 | 1717.23 | 1717.23 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -417.6201 | 1299.6099 | -3550 | -400 | -2650.3901 | 66.26% | 45.12% | 95% | 0% | 2450 | -365
[5 empty] | 2019-10-01 | 31 | 6566.5 | 2057 | -377 | 1 | 0 | 2434 | 1692.1682 | 1692.1682 | 1692.1682 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -431.3501 | 1260.8181 | -3550 | -400 | -2689.1819 | 67.23% | 45.12% | 95% | 0% | 2434 | -377
[5 empty] | 2019-10-01 | 32 | 6567 | 2163 | -328 | 1 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -375.286 | 1406.1649 | -3550 | -400 | -2543.8351 | 63.6% | 45.11% | 95% | 0% | 2491 | -328
[5 empty] | 2019-10-01 | 33 | 6567.5 | 2317 | -252 | 1 | 0 | 2569 | 1903.6274 | 1903.6274 | 1903.6274 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -288.3295 | 1615.2979 | -3550 | -400 | -2334.7021 | 58.37% | 45.11% | 95% | 0% | 2569 | -252
[5 empty] | 2019-10-01 | 34 | 6568 | 2454 | -198 | 1 | 0 | 2652 | 2033.6356 | 2033.6356 | 2033.6356 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -226.5446 | 1807.091 | -3550 | -400 | -2142.909 | 53.57% | 45.1% | 95% | 0% | 2652 | -198
[5 empty] | 2019-10-01 | 35 | 6568.5 | 2534 | -171 | 1 | 0 | 2705 | 2116.6529 | 2116.6529 | 2116.6529 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -195.6522 | 1921.0008 | -3550 | -400 | -2028.9992 | 50.72% | 45.1% | 95% | 0% | 2705 | -171
[5 empty] | 2019-10-01 | 36 | 6569 | 2597 | -148 | 1 | 0 | 2745 | 2179.3075 | 2179.3075 | 2179.3075 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -169.3364 | 2009.9711 | -3550 | -400 | -1940.0289 | 48.5% | 45.1% | 95% | 0% | 2745 | -148
[5 empty] | 2019-10-01 | 37 | 6569.5 | 2656 | -130 | 1 | 0 | 2786 | 2243.5284 | 2243.5284 | 2243.5284 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -148.7414 | 2094.787 | -3550 | -400 | -1855.213 | 46.38% | 45.1% | 95% | 0% | 2786 | -130
[5 empty] | 2019-10-01 | 38 | 6570 | 2699 | -126 | 1 | 0 | 2825 | 2304.6167 | 2304.6167 | 2304.6167 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -144.1648 | 2160.4519 | -3550 | -400 | -1789.5481 | 44.74% | 45.1% | 95% | 0% | 2825 | -126
[5 empty] | 2019-10-01 | 39 | 6570.5 | 2752 | -128 | 1 | 0 | 2880 | 2390.7667 | 2390.7667 | 2390.7667 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -146.4531 | 2244.3136 | -3550 | -400 | -1705.6864 | 42.64% | 45.09% | 95% | 0% | 2880 | -128
[5 empty] | 2019-10-01 | 40 | 6571 | 2706 | -129 | 0 | 0 | 2835 | 2320.2803 | 2320.2803 | 2320.2803 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -147.5973 | 2172.683 | -2750 | -200 | -777.317 | 19.43% | 45.09% | 95% | 0% | 2835 | -129
[5 empty] | 2019-10-01 | 41 | 6571.5 | 2596 | -128 | 0 | 0 | 2724 | 2146.4138 | 2146.4138 | 2146.4138 | 821.2696 | 780 | 200 | 1801.2696 | 45.03% | 95% | 0% | -146.4531 | 1999.9608 | -2750 | -200 | -950.0392 | 23.75% | 45.07% | 95% | 0% | 2724 | -128
[5 empty] | 2019-10-01 | 42 | 6572 | 2479 | -127 | 0 | 0 | 2606 | 1961.5829 | 1961.5829 | 1961.5829 | 819.7032 | 780 | 200 | 1799.7032 | 44.99% | 95% | 0% | -145.3089 | 1816.2739 | -2750 | -200 | -1133.7261 | 28.34% | 45.07% | 95% | 0% | 2606 | -127
[5 empty] | 2019-10-01 | 43 | 6572.5 | 2361 | -126 | 0 | 0 | 2487 | 1775.1855 | 1775.1855 | 1775.1855 | 819.7032 | 780 | 200 | 1799.7032 | 44.99% | 95% | 0% | -144.1648 | 1631.0207 | -2750 | -200 | -1318.9793 | 32.97% | 45.06% | 95% | 0% | 2487 | -126
[5 empty] | 2019-10-01 | 44 | 6573 | 2217 | -124 | 0 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 819.7032 | 780 | 200 | 1799.7032 | 44.99% | 95% | 0% | -141.8764 | 1404.6199 | -2750 | -200 | -1545.3801 | 38.63% | 45.06% | 95% | 0% | 2341 | -124
[5 empty] | 2019-10-01 | 45 | 6573.5 | 2089 | -122 | 0 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 819.7032 | 780 | 200 | 1799.7032 | 44.99% | 95% | 0% | -139.5881 | 1203.2808 | -2750 | -200 | -1746.7192 | 43.67% | 45.06% | 95% | 0% | 2211 | -122
[5 empty] | 2019-10-01 | 46 | 6574 | 1934 | -120 | 0 | 0 | 2054 | 1096.9497 | 1096.9497 | 1096.9497 | 819.7032 | 780 | 200 | 1799.7032 | 44.99% | 95% | 0% | -137.2998 | 959.6499 | -2750 | -200 | -1990.3501 | 49.76% | 45.05% | 95% | 0% | 2054 | -120
[5 empty] | 2019-10-01 | 47 | 6574.5 | 1789 | -119 | 0 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 819.7032 | 780 | 200 | 1799.7032 | 44.99% | 95% | 0% | -136.1556 | 732.1049 | -2750 | -200 | -2217.8951 | 55.45% | 45.05% | 95% | 0% | 1908 | -119
[5 empty] | 2019-10-01 | 48 | 6575 | 1669 | -117 | 0 | 0 | 1786 | 677.1641 | 677.1641 | 677.1641 | 819.7032 | 780 | 200 | 1799.7032 | 44.99% | 95% | 0% | -133.8673 | 543.2968 | -2750 | -200 | -2406.7032 | 60.17% | 45.05% | 95% | 0% | 1786 | -117
[5 empty] | 2019-10-02 | 1 | 6575.5 | 1600 | -111 | 0 | 0 | 1711 | 559.6867 | 559.6867 | 559.6867 | 819.7032 | 780 | 200 | 1799.7032 | 44.99% | 95% | 0% | -127.0023 | 432.6844 | -2750 | -200 | -2517.3156 | 62.93% | 45.05% | 95% | 0% | 1711 | -111
[5 empty] | 2019-10-02 | 2 | 6576 | 1559 | -105 | 0 | 0 | 1664 | 486.0676 | 486.0676 | 486.0676 | 819.7032 | 780 | 200 | 1799.7032 | 44.99% | 95% | 0% | -120.1373 | 365.9303 | -2750 | -200 | -2584.0697 | 64.6% | 45.04% | 95% | 0% | 1664 | -105
[5 empty] | 2019-10-02 | 3 | 6576.5 | 1535 | -105 | 0 | 0 | 1640 | 448.4749 | 448.4749 | 448.4749 | 818.1369 | 780 | 200 | 1798.1369 | 44.95% | 95% | 0% | -120.1373 | 328.3376 | -2750 | -200 | -2621.6624 | 65.54% | 45.04% | 95% | 0% | 1640 | -105
[5 empty] | 2019-10-02 | 4 | 6577 | 1534 | -105 | 0 | 0 | 1639 | 446.9085 | 446.9085 | 446.9085 | 818.1369 | 780 | 200 | 1798.1369 | 44.95% | 95% | 0% | -120.1373 | 326.7712 | -2750 | -200 | -2623.2288 | 65.58% | 45.03% | 95% | 0% | 1639 | -105
[5 empty] | 2019-10-02 | 5 | 6577.5 | 1508 | -106 | 0 | 0 | 1614 | 407.7494 | 407.7494 | 407.7494 | 818.1369 | 780 | 200 | 1798.1369 | 44.95% | 95% | 0% | -121.2815 | 286.4679 | -2750 | -200 | -2663.5321 | 66.59% | 45.03% | 95% | 0% | 1614 | -106
[5 empty] | 2019-10-02 | 6 | 6578 | 1487 | -107 | 0 | 0 | 1594 | 376.4221 | 376.4221 | 376.4221 | 818.1369 | 780 | 200 | 1798.1369 | 44.95% | 95% | 0% | -122.4256 | 253.9965 | -2750 | -200 | -2696.0035 | 67.4% | 45.03% | 95% | 0% | 1594 | -107
[5 empty] | 2019-10-02 | 7 | 6578.5 | 1465 | -107 | 0 | 0 | 1572 | 341.9621 | 341.9621 | 341.9621 | 818.1369 | 780 | 200 | 1798.1369 | 44.95% | 95% | 0% | -122.4256 | 219.5364 | -2750 | -200 | -2730.4636 | 68.26% | 45.03% | 95% | 0% | 1572 | -107
[5 empty] | 2019-10-02 | 8 | 6579 | 1460 | -107 | 0 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 818.1369 | 780 | 200 | 1798.1369 | 44.95% | 95% | 0% | -122.4256 | 211.7046 | -2750 | -200 | -2738.2954 | 68.46% | 45.03% | 95% | 0% | 1567 | -107
[5 empty] | 2019-10-02 | 9 | 6579.5 | 1473 | -104 | 0 | 0 | 1577 | 349.7939 | 349.7939 | 349.7939 | 818.1369 | 780 | 200 | 1798.1369 | 44.95% | 95% | 0% | -118.9931 | 230.8008 | -2750 | -200 | -2719.1992 | 67.98% | 45.02% | 95% | 0% | 1577 | -104
[5 empty] | 2019-10-02 | 10 | 6580 | 1493 | -102 | 0 | 0 | 1595 | 377.9885 | 377.9885 | 377.9885 | 818.1369 | 780 | 200 | 1798.1369 | 44.95% | 95% | 0% | -116.7048 | 261.2837 | -2750 | -200 | -2688.7163 | 67.22% | 45.02% | 95% | 0% | 1595 | -102
[5 empty] | 2019-10-02 | 11 | 6580.5 | 1552 | -103 | 0 | 0 | 1655 | 471.9703 | 471.9703 | 471.9703 | 816.5705 | 780 | 200 | 1796.5705 | 44.91% | 95% | 0% | -117.849 | 354.1214 | -2750 | -200 | -2595.8786 | 64.9% | 45.02% | 95% | 0% | 1655 | -103
[5 empty] | 2019-10-02 | 12 | 6581 | 1657 | -104 | 0 | 0 | 1761 | 638.0049 | 638.0049 | 638.0049 | 816.5705 | 780 | 200 | 1796.5705 | 44.91% | 95% | 0% | -118.9931 | 519.0118 | -2750 | -200 | -2430.9882 | 60.77% | 45.02% | 95% | 0% | 1761 | -104
[5 empty] | 2019-10-02 | 13 | 6581.5 | 1872 | -105 | 0 | 0 | 1977 | 976.3397 | 976.3397 | 976.3397 | 816.5705 | 780 | 200 | 1796.5705 | 44.91% | 95% | 0% | -120.1373 | 856.2024 | -2750 | -200 | -2093.7976 | 52.34% | 45.02% | 95% | 0% | 1977 | -105
[5 empty] | 2019-10-02 | 14 | 6582 | 2127 | -106 | 0 | 0 | 2233 | 1377.3289 | 1377.3289 | 1377.3289 | 816.5705 | 780 | 200 | 1796.5705 | 44.91% | 95% | 0% | -121.2815 | 1256.0475 | -2750 | -200 | -1693.9525 | 42.35% | 45.02% | 95% | 0% | 2233 | -106
[5 empty] | 2019-10-02 | 15 | 6582.5 | 2380 | -111 | 0 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 816.5705 | 780 | 200 | 1796.5705 | 44.91% | 95% | 0% | -127.0023 | 1654.4487 | -2750 | -200 | -1295.5513 | 32.39% | 45.01% | 95% | 0% | 2491 | -111
[5 empty] | 2019-10-02 | 16 | 6583 | 2447 | -154 | 0 | 0 | 2601 | 1953.751 | 1953.751 | 1953.751 | 816.5705 | 780 | 200 | 1796.5705 | 44.91% | 95% | 0% | -176.2014 | 1777.5497 | -2750 | -200 | -1172.4503 | 29.31% | 45.01% | 95% | 0% | 2601 | -154
[5 empty] | 2019-10-02 | 17 | 6583.5 | 2393 | -232 | 0 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 816.5705 | 780 | 200 | 1796.5705 | 44.91% | 95% | 0% | -265.4462 | 1725.8976 | -2750 | -200 | -1224.1024 | 30.6% | 45% | 95% | 0% | 2625 | -232
[5 empty] | 2019-10-02 | 18 | 6584 | 2248 | -315 | 1 | 0 | 2563 | 1894.2292 | 1894.2292 | 1894.2292 | 816.5705 | 780 | 200 | 1796.5705 | 44.91% | 95% | 0% | -360.4119 | 1533.8173 | -3550 | -400 | -2416.1827 | 60.4% | 45% | 95% | 0% | 2563 | -315
[5 empty] | 2019-10-02 | 19 | 6584.5 | 2117 | -394 | 1 | 0 | 2511 | 1812.7782 | 1812.7782 | 1812.7782 | 816.5705 | 780 | 200 | 1796.5705 | 44.91% | 95% | 0% | -450.8009 | 1361.9773 | -3550 | -400 | -2588.0227 | 64.7% | 45% | 95% | 0% | 2511 | -394
[5 empty] | 2019-10-02 | 20 | 6585 | 1978 | -469 | 1 | 0 | 2447 | 1712.5309 | 1712.5309 | 1712.5309 | 816.5705 | 780 | 200 | 1796.5705 | 44.91% | 95% | 0% | -536.6133 | 1175.9176 | -3550 | -400 | -2774.0824 | 69.35% | 45% | 95% | 0% | 2447 | -469
[5 empty] | 2019-10-02 | 21 | 6585.5 | 1833 | -530 | 1 | 0 | 2363 | 1580.9563 | 1580.9563 | 1580.9563 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -606.4073 | 974.549 | -3550 | -400 | -2975.451 | 74.39% | 44.99% | 95% | 0% | 2363 | -530
[5 empty] | 2019-10-02 | 22 | 6586 | 1731 | -591 | 1 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -676.2014 | 840.534 | -3550 | -400 | -3109.466 | 77.74% | 44.99% | 95% | 0% | 2322 | -591
[5 empty] | 2019-10-02 | 23 | 6586.5 | 1626 | -640 | 1 | 0 | 2266 | 1429.019 | 1429.019 | 1429.019 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -732.2654 | 696.7535 | -3550 | -400 | -3253.2465 | 81.33% | 44.99% | 95% | 0% | 2266 | -640
[5 empty] | 2019-10-02 | 24 | 6587 | 1566 | -668 | 1 | 0 | 2234 | 1378.8953 | 1378.8953 | 1378.8953 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -764.3021 | 614.5932 | -3550 | -400 | -3335.4068 | 83.39% | 44.99% | 95% | 0% | 2234 | -668
[5 empty] | 2019-10-02 | 25 | 6587.5 | 1543 | -670 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -766.5904 | 579.4113 | -3550 | -400 | -3370.5887 | 84.26% | 44.98% | 95% | 0% | 2213 | -670
[5 empty] | 2019-10-02 | 26 | 6588 | 1554 | -649 | 1 | 0 | 2203 | 1330.338 | 1330.338 | 1330.338 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -742.5629 | 587.7751 | -3550 | -400 | -3362.2249 | 84.06% | 44.98% | 95% | 0% | 2203 | -649
[5 empty] | 2019-10-02 | 27 | 6588.5 | 1580 | -633 | 1 | 0 | 2213 | 1346.0016 | 1346.0016 | 1346.0016 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -724.2563 | 621.7454 | -3550 | -400 | -3328.2546 | 83.21% | 44.97% | 95% | 0% | 2213 | -633
[5 empty] | 2019-10-02 | 28 | 6589 | 1601 | -600 | 1 | 0 | 2201 | 1327.2053 | 1327.2053 | 1327.2053 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -686.4989 | 640.7064 | -3550 | -400 | -3309.2936 | 82.73% | 44.96% | 95% | 0% | 2201 | -600
[5 empty] | 2019-10-02 | 29 | 6589.5 | 1651 | -567 | 1 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -648.7414 | 705.0921 | -3550 | -400 | -3244.9079 | 81.12% | 44.96% | 95% | 0% | 2218 | -567
[5 empty] | 2019-10-02 | 30 | 6590 | 1707 | -524 | 1 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -599.5423 | 774.6539 | -3550 | -400 | -3175.3461 | 79.38% | 44.96% | 95% | 0% | 2231 | -524
[5 empty] | 2019-10-02 | 31 | 6590.5 | 1781 | -479 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -548.0549 | 871.5659 | -3550 | -400 | -3078.4341 | 76.96% | 44.96% | 95% | 0% | 2260 | -479
[5 empty] | 2019-10-02 | 32 | 6591 | 1918 | -433 | 1 | 0 | 2351 | 1562.1599 | 1562.1599 | 1562.1599 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -495.4233 | 1066.7366 | -3550 | -400 | -2883.2634 | 72.08% | 44.96% | 95% | 0% | 2351 | -433
[5 empty] | 2019-10-02 | 33 | 6591.5 | 2092 | -363 | 1 | 0 | 2455 | 1725.0618 | 1725.0618 | 1725.0618 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -415.3318 | 1309.73 | -3550 | -400 | -2640.27 | 66.01% | 44.95% | 95% | 0% | 2455 | -363
[5 empty] | 2019-10-02 | 34 | 6592 | 2275 | -287 | 1 | 0 | 2562 | 1892.6628 | 1892.6628 | 1892.6628 | 815.0041 | 780 | 200 | 1795.0041 | 44.88% | 95% | 0% | -328.3753 | 1564.2875 | -3550 | -400 | -2385.7125 | 59.64% | 44.94% | 95% | 0% | 2562 | -287
[5 empty] | 2019-10-02 | 35 | 6592.5 | 2462 | -214 | 1 | 0 | 2676 | 2071.2284 | 2071.2284 | 2071.2284 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -244.8513 | 1826.3771 | -3550 | -400 | -2123.6229 | 53.09% | 44.94% | 95% | 0% | 2676 | -214
[5 empty] | 2019-10-02 | 36 | 6593 | 2620 | -142 | 1 | 0 | 2762 | 2205.9357 | 2205.9357 | 2205.9357 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -162.4714 | 2043.4643 | -3550 | -400 | -1906.5357 | 47.66% | 44.93% | 95% | 0% | 2762 | -142
[5 empty] | 2019-10-02 | 37 | 6593.5 | 2749 | -85 | 1 | 0 | 2834 | 2318.7139 | 2318.7139 | 2318.7139 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -97.254 | 2221.4599 | -3550 | -400 | -1728.5401 | 43.21% | 44.93% | 95% | 0% | 2834 | -85
[5 empty] | 2019-10-02 | 38 | 6594 | 2838 | -67 | 1 | 0 | 2905 | 2429.9258 | 2429.9258 | 2429.9258 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -76.659 | 2353.2668 | -3550 | -400 | -1596.7332 | 39.92% | 44.9% | 95% | 0% | 2905 | -67
[5 empty] | 2019-10-02 | 39 | 6594.5 | 2886 | -63 | 1 | 0 | 2949 | 2498.8458 | 2498.8458 | 2498.8458 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -72.0824 | 2426.7635 | -3550 | -400 | -1523.2365 | 38.08% | 44.9% | 95% | 0% | 2949 | -63
[5 empty] | 2019-10-02 | 40 | 6595 | 2843 | -59 | 0 | 0 | 2902 | 2425.2267 | 2425.2267 | 2425.2267 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -67.5057 | 2357.721 | -2750 | -200 | -592.279 | 14.81% | 44.89% | 95% | 0% | 2902 | -59
[5 empty] | 2019-10-02 | 41 | 6595.5 | 2774 | -56 | 0 | 0 | 2830 | 2312.4485 | 2312.4485 | 2312.4485 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -64.0732 | 2248.3752 | -2750 | -200 | -701.6248 | 17.54% | 44.89% | 95% | 0% | 2830 | -56
[5 empty] | 2019-10-02 | 42 | 6596 | 2697 | -53 | 0 | 0 | 2750 | 2187.1393 | 2187.1393 | 2187.1393 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -60.6407 | 2126.4986 | -2750 | -200 | -823.5014 | 20.59% | 44.89% | 95% | 0% | 2750 | -53
[5 empty] | 2019-10-02 | 43 | 6596.5 | 2599 | -51 | 0 | 0 | 2650 | 2030.5029 | 2030.5029 | 2030.5029 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -58.3524 | 1972.1505 | -2750 | -200 | -977.8495 | 24.45% | 44.89% | 95% | 0% | 2650 | -51
[5 empty] | 2019-10-02 | 44 | 6597 | 2451 | -49 | 0 | 0 | 2500 | 1795.5482 | 1795.5482 | 1795.5482 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -56.0641 | 1739.4842 | -2750 | -200 | -1210.5158 | 30.26% | 44.88% | 95% | 0% | 2500 | -49
[5 empty] | 2019-10-02 | 45 | 6597.5 | 2300 | -47 | 0 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -53.7757 | 1502.1187 | -2750 | -200 | -1447.8813 | 36.2% | 44.88% | 95% | 0% | 2347 | -47
[5 empty] | 2019-10-02 | 46 | 6598 | 2146 | -45 | 0 | 0 | 2191 | 1311.5416 | 1311.5416 | 1311.5416 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -51.4874 | 1260.0542 | -2750 | -200 | -1689.9458 | 42.25% | 44.88% | 95% | 0% | 2191 | -45
[5 empty] | 2019-10-02 | 47 | 6598.5 | 1998 | -43 | 0 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 813.4378 | 780 | 200 | 1793.4378 | 44.84% | 95% | 0% | -49.1991 | 1027.3879 | -2750 | -200 | -1922.6121 | 48.07% | 44.88% | 95% | 0% | 2041 | -43
[5 empty] | 2019-10-02 | 48 | 6599 | 1888 | -42 | 0 | 0 | 1930 | 902.7205 | 902.7205 | 902.7205 | 811.8714 | 780 | 200 | 1791.8714 | 44.8% | 95% | 0% | -48.0549 | 854.6656 | -2750 | -200 | -2095.3344 | 52.38% | 44.88% | 95% | 0% | 1930 | -42
[5 empty] | 2019-10-03 | 1 | 6599.5 | 1808 | -40 | 0 | 0 | 1848 | 774.2786 | 774.2786 | 774.2786 | 811.8714 | 780 | 200 | 1791.8714 | 44.8% | 95% | 0% | -45.7666 | 728.5121 | -2750 | -200 | -2221.4879 | 55.54% | 44.87% | 95% | 0% | 1848 | -40
[5 empty] | 2019-10-03 | 2 | 6600 | 1754 | -39 | 0 | 0 | 1793 | 688.1286 | 688.1286 | 688.1286 | 811.8714 | 780 | 200 | 1791.8714 | 44.8% | 95% | 0% | -44.6224 | 643.5062 | -2750 | -200 | -2306.4938 | 57.66% | 44.86% | 95% | 0% | 1793 | -39
[5 empty] | 2019-10-03 | 3 | 6600.5 | 1735 | -38 | 0 | 0 | 1773 | 656.8013 | 656.8013 | 656.8013 | 811.8714 | 780 | 200 | 1791.8714 | 44.8% | 95% | 0% | -43.4783 | 613.3231 | -2750 | -200 | -2336.6769 | 58.42% | 44.86% | 95% | 0% | 1773 | -38
[5 empty] | 2019-10-03 | 4 | 6601 | 1732 | -38 | 0 | 0 | 1770 | 652.1022 | 652.1022 | 652.1022 | 811.8714 | 780 | 200 | 1791.8714 | 44.8% | 95% | 0% | -43.4783 | 608.624 | -2750 | -200 | -2341.376 | 58.53% | 44.86% | 95% | 0% | 1770 | -38
[5 empty] | 2019-10-03 | 5 | 6601.5 | 1721 | -37 | 0 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 811.8714 | 780 | 200 | 1791.8714 | 44.8% | 95% | 0% | -42.3341 | 590.9718 | -2750 | -200 | -2359.0282 | 58.98% | 44.86% | 95% | 0% | 1758 | -37
[5 empty] | 2019-10-03 | 6 | 6602 | 1704 | -37 | 0 | 0 | 1741 | 606.6777 | 606.6777 | 606.6777 | 811.8714 | 780 | 200 | 1791.8714 | 44.8% | 95% | 0% | -42.3341 | 564.3436 | -2750 | -200 | -2385.6564 | 59.64% | 44.86% | 95% | 0% | 1741 | -37
[5 empty] | 2019-10-03 | 7 | 6602.5 | 1690 | -36 | 0 | 0 | 1726 | 583.1822 | 583.1822 | 583.1822 | 811.8714 | 780 | 200 | 1791.8714 | 44.8% | 95% | 0% | -41.1899 | 541.9923 | -2750 | -200 | -2408.0077 | 60.2% | 44.86% | 95% | 0% | 1726 | -36
[5 empty] | 2019-10-03 | 8 | 6603 | 1686 | -35 | 0 | 0 | 1721 | 575.3504 | 575.3504 | 575.3504 | 810.305 | 780 | 200 | 1790.305 | 44.76% | 95% | 0% | -40.0458 | 535.3046 | -2750 | -200 | -2414.6954 | 60.37% | 44.84% | 95% | 0% | 1721 | -35
[5 empty] | 2019-10-03 | 9 | 6603.5 | 1682 | -37 | 0 | 0 | 1719 | 572.2176 | 572.2176 | 572.2176 | 810.305 | 780 | 200 | 1790.305 | 44.76% | 95% | 0% | -42.3341 | 529.8835 | -2750 | -200 | -2420.1165 | 60.5% | 44.83% | 95% | 0% | 1719 | -37
[5 empty] | 2019-10-03 | 10 | 6604 | 1698 | -39 | 0 | 0 | 1737 | 600.4122 | 600.4122 | 600.4122 | 810.305 | 780 | 200 | 1790.305 | 44.76% | 95% | 0% | -44.6224 | 555.7898 | -2750 | -200 | -2394.2102 | 59.86% | 44.83% | 95% | 0% | 1737 | -39
[5 empty] | 2019-10-03 | 11 | 6604.5 | 1754 | -40 | 0 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 810.305 | 780 | 200 | 1790.305 | 44.76% | 95% | 0% | -45.7666 | 643.9284 | -2750 | -200 | -2306.0716 | 57.65% | 44.83% | 95% | 0% | 1794 | -40
[5 empty] | 2019-10-03 | 12 | 6605 | 1851 | -42 | 0 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 810.305 | 780 | 200 | 1790.305 | 44.76% | 95% | 0% | -48.0549 | 796.7101 | -2750 | -200 | -2153.2899 | 53.83% | 44.82% | 95% | 0% | 1893 | -42
[5 empty] | 2019-10-03 | 13 | 6605.5 | 2069 | -44 | 0 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 810.305 | 780 | 200 | 1790.305 | 44.76% | 95% | 0% | -50.3432 | 1139.022 | -2750 | -200 | -1810.978 | 45.27% | 44.82% | 95% | 0% | 2113 | -44
[5 empty] | 2019-10-03 | 14 | 6606 | 2318 | -46 | 0 | 0 | 2364 | 1582.5227 | 1582.5227 | 1582.5227 | 810.305 | 780 | 200 | 1790.305 | 44.76% | 95% | 0% | -52.6316 | 1529.8911 | -2750 | -200 | -1420.1089 | 35.5% | 44.82% | 95% | 0% | 2364 | -46
[5 empty] | 2019-10-03 | 15 | 6606.5 | 2558 | -52 | 0 | 0 | 2610 | 1967.8483 | 1967.8483 | 1967.8483 | 810.305 | 780 | 200 | 1790.305 | 44.76% | 95% | 0% | -59.4966 | 1908.3517 | -2750 | -200 | -1041.6483 | 26.04% | 44.82% | 95% | 0% | 2610 | -52
[5 empty] | 2019-10-03 | 16 | 6607 | 2678 | -68 | 0 | 0 | 2746 | 2180.8739 | 2180.8739 | 2180.8739 | 810.305 | 780 | 200 | 1790.305 | 44.76% | 95% | 0% | -77.8032 | 2103.0707 | -2750 | -200 | -846.9293 | 21.17% | 44.82% | 95% | 0% | 2746 | -68
[5 empty] | 2019-10-03 | 17 | 6607.5 | 2698 | -90 | 1 | 0 | 2788 | 2246.6612 | 2246.6612 | 2246.6612 | 810.305 | 780 | 200 | 1790.305 | 44.76% | 95% | 0% | -102.9748 | 2143.6863 | -3550 | -400 | -1806.3137 | 45.16% | 44.82% | 95% | 0% | 2788 | -90
[5 empty] | 2019-10-03 | 18 | 6608 | 2654 | -118 | 1 | 0 | 2772 | 2221.5993 | 2221.5993 | 2221.5993 | 810.305 | 780 | 200 | 1790.305 | 44.76% | 95% | 0% | -135.0114 | 2086.5879 | -3550 | -400 | -1863.4121 | 46.59% | 44.82% | 95% | 0% | 2772 | -118
[5 empty] | 2019-10-03 | 19 | 6608.5 | 2635 | -155 | 1 | 0 | 2790 | 2249.7939 | 2249.7939 | 2249.7939 | 808.7387 | 780 | 200 | 1788.7387 | 44.72% | 95% | 0% | -177.3455 | 2072.4484 | -3550 | -400 | -1877.5516 | 46.94% | 44.81% | 95% | 0% | 2790 | -155
[5 empty] | 2019-10-03 | 20 | 6609 | 2549 | -199 | 1 | 0 | 2748 | 2184.0066 | 2184.0066 | 2184.0066 | 808.7387 | 780 | 200 | 1788.7387 | 44.72% | 95% | 0% | -227.6888 | 1956.3178 | -3550 | -400 | -1993.6822 | 49.84% | 44.81% | 95% | 0% | 2748 | -199
[5 empty] | 2019-10-03 | 21 | 6609.5 | 2462 | -237 | 1 | 0 | 2699 | 2107.2547 | 2107.2547 | 2107.2547 | 808.7387 | 780 | 200 | 1788.7387 | 44.72% | 95% | 0% | -271.167 | 1836.0877 | -3550 | -400 | -2113.9123 | 52.85% | 44.81% | 95% | 0% | 2699 | -237
[5 empty] | 2019-10-03 | 22 | 6610 | 2416 | -260 | 1 | 0 | 2676 | 2071.2284 | 2071.2284 | 2071.2284 | 808.7387 | 780 | 200 | 1788.7387 | 44.72% | 95% | 0% | -297.4828 | 1773.7455 | -3550 | -400 | -2176.2545 | 54.41% | 44.81% | 95% | 0% | 2676 | -260
[5 empty] | 2019-10-03 | 23 | 6610.5 | 2357 | -291 | 1 | 0 | 2648 | 2027.3702 | 2027.3702 | 2027.3702 | 808.7387 | 780 | 200 | 1788.7387 | 44.72% | 95% | 0% | -332.9519 | 1694.4182 | -3550 | -400 | -2255.5818 | 56.39% | 44.8% | 95% | 0% | 2648 | -291
[5 empty] | 2019-10-03 | 24 | 6611 | 2361 | -284 | 1 | 0 | 2645 | 2022.6711 | 2022.6711 | 2022.6711 | 808.7387 | 780 | 200 | 1788.7387 | 44.72% | 95% | 0% | -324.9428 | 1697.7283 | -3550 | -400 | -2252.2717 | 56.31% | 44.78% | 95% | 0% | 2645 | -284
[5 empty] | 2019-10-03 | 25 | 6611.5 | 2363 | -293 | 1 | 0 | 2656 | 2039.9011 | 2039.9011 | 2039.9011 | 808.7387 | 780 | 200 | 1788.7387 | 44.72% | 95% | 0% | -335.2403 | 1704.6608 | -3550 | -400 | -2245.3392 | 56.13% | 44.77% | 95% | 0% | 2656 | -293
[5 empty] | 2019-10-03 | 26 | 6612 | 2357 | -286 | 1 | 0 | 2643 | 2019.5383 | 2019.5383 | 2019.5383 | 808.7387 | 780 | 200 | 1788.7387 | 44.72% | 95% | 0% | -327.2311 | 1692.3072 | -3550 | -400 | -2257.6928 | 56.44% | 44.77% | 95% | 0% | 2643 | -286
[5 empty] | 2019-10-03 | 27 | 6612.5 | 2336 | -292 | 1 | 0 | 2628 | 1996.0429 | 1996.0429 | 1996.0429 | 808.7387 | 780 | 200 | 1788.7387 | 44.72% | 95% | 0% | -334.0961 | 1661.9468 | -3550 | -400 | -2288.0532 | 57.2% | 44.76% | 95% | 0% | 2628 | -292
[5 empty] | 2019-10-03 | 28 | 6613 | 2333 | -287 | 1 | 0 | 2620 | 1983.512 | 1983.512 | 1983.512 | 808.7387 | 780 | 200 | 1788.7387 | 44.72% | 95% | 0% | -328.3753 | 1655.1367 | -3550 | -400 | -2294.8633 | 57.37% | 44.75% | 95% | 0% | 2620 | -287
[5 empty] | 2019-10-03 | 29 | 6613.5 | 2330 | -278 | 1 | 0 | 2608 | 1964.7156 | 1964.7156 | 1964.7156 | 808.7387 | 780 | 200 | 1788.7387 | 44.72% | 95% | 0% | -318.0778 | 1646.6378 | -3550 | -400 | -2303.3622 | 57.58% | 44.75% | 95% | 0% | 2608 | -278
[5 empty] | 2019-10-03 | 30 | 6614 | 2331 | -283 | 1 | 0 | 2614 | 1974.1138 | 1974.1138 | 1974.1138 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -323.7986 | 1650.3151 | -3550 | -400 | -2299.6849 | 57.49% | 44.75% | 95% | 0% | 2614 | -283
[5 empty] | 2019-10-03 | 31 | 6614.5 | 2316 | -291 | 1 | 0 | 2607 | 1963.1492 | 1963.1492 | 1963.1492 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -332.9519 | 1630.1973 | -3550 | -400 | -2319.8027 | 58% | 44.75% | 95% | 0% | 2607 | -291
[5 empty] | 2019-10-03 | 32 | 6615 | 2393 | -263 | 1 | 0 | 2656 | 2039.9011 | 2039.9011 | 2039.9011 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -300.9153 | 1738.9857 | -3550 | -400 | -2211.0143 | 55.28% | 44.74% | 95% | 0% | 2656 | -263
[5 empty] | 2019-10-03 | 33 | 6615.5 | 2483 | -243 | 1 | 0 | 2726 | 2149.5466 | 2149.5466 | 2149.5466 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -278.032 | 1871.5145 | -3550 | -400 | -2078.4855 | 51.96% | 44.74% | 95% | 0% | 2726 | -243
[5 empty] | 2019-10-03 | 34 | 6616 | 2595 | -192 | 1 | 0 | 2787 | 2245.0948 | 2245.0948 | 2245.0948 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -219.6796 | 2025.4152 | -3550 | -400 | -1924.5848 | 48.11% | 44.74% | 95% | 0% | 2787 | -192
[5 empty] | 2019-10-03 | 35 | 6616.5 | 2664 | -177 | 1 | 0 | 2841 | 2329.6785 | 2329.6785 | 2329.6785 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -202.5172 | 2127.1613 | -3550 | -400 | -1822.8387 | 45.57% | 44.72% | 95% | 0% | 2841 | -177
[5 empty] | 2019-10-03 | 36 | 6617 | 2709 | -162 | 1 | 0 | 2871 | 2376.6694 | 2376.6694 | 2376.6694 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -185.3547 | 2191.3147 | -3550 | -400 | -1758.6853 | 43.97% | 44.72% | 95% | 0% | 2871 | -162
[5 empty] | 2019-10-03 | 37 | 6617.5 | 2707 | -157 | 1 | 0 | 2864 | 2365.7049 | 2365.7049 | 2365.7049 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -179.6339 | 2186.071 | -3550 | -400 | -1763.929 | 44.1% | 44.72% | 95% | 0% | 2864 | -157
[5 empty] | 2019-10-03 | 38 | 6618 | 2734 | -161 | 1 | 0 | 2895 | 2414.2622 | 2414.2622 | 2414.2622 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -184.2105 | 2230.0516 | -3550 | -400 | -1719.9484 | 43% | 44.72% | 95% | 0% | 2895 | -161
[5 empty] | 2019-10-03 | 39 | 6618.5 | 2748 | -164 | 1 | 0 | 2912 | 2440.8904 | 2440.8904 | 2440.8904 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -187.643 | 2253.2473 | -3550 | -400 | -1696.7527 | 42.42% | 44.72% | 95% | 0% | 2912 | -164
[5 empty] | 2019-10-03 | 40 | 6619 | 2700 | -167 | 0 | 0 | 2867 | 2370.404 | 2370.404 | 2370.404 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -191.0755 | 2179.3284 | -2750 | -200 | -770.6716 | 19.27% | 44.71% | 95% | 0% | 2867 | -167
[5 empty] | 2019-10-03 | 41 | 6619.5 | 2592 | -170 | 0 | 0 | 2762 | 2205.9357 | 2205.9357 | 2205.9357 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -194.508 | 2011.4277 | -2750 | -200 | -938.5723 | 23.46% | 44.71% | 95% | 0% | 2762 | -170
[5 empty] | 2019-10-03 | 42 | 6620 | 2468 | -173 | 0 | 0 | 2641 | 2016.4056 | 2016.4056 | 2016.4056 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -197.9405 | 1818.4651 | -2750 | -200 | -1131.5349 | 28.29% | 44.7% | 95% | 0% | 2641 | -173
[5 empty] | 2019-10-03 | 43 | 6620.5 | 2348 | -176 | 0 | 0 | 2524 | 1833.141 | 1833.141 | 1833.141 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -201.373 | 1631.768 | -2750 | -200 | -1318.232 | 32.96% | 44.69% | 95% | 0% | 2524 | -176
[5 empty] | 2019-10-03 | 44 | 6621 | 2187 | -180 | 0 | 0 | 2367 | 1587.2218 | 1587.2218 | 1587.2218 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -205.9497 | 1381.2721 | -2750 | -200 | -1568.7279 | 39.22% | 44.69% | 95% | 0% | 2367 | -180
[5 empty] | 2019-10-03 | 45 | 6621.5 | 2019 | -180 | 0 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 807.1723 | 780 | 200 | 1787.1723 | 44.68% | 95% | 0% | -205.9497 | 1118.1229 | -2750 | -200 | -1831.8771 | 45.8% | 44.68% | 95% | 0% | 2199 | -180
[5 empty] | 2019-10-03 | 46 | 6622 | 1840 | -180 | 0 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -205.9497 | 837.7437 | -2750 | -200 | -2112.2563 | 52.81% | 44.68% | 95% | 0% | 2020 | -180
[5 empty] | 2019-10-03 | 47 | 6622.5 | 1686 | -177 | 0 | 0 | 1863 | 797.7741 | 797.7741 | 797.7741 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -202.5172 | 595.257 | -2750 | -200 | -2354.743 | 58.87% | 44.68% | 95% | 0% | 1863 | -177
[5 empty] | 2019-10-03 | 48 | 6623 | 1564 | -175 | 0 | 0 | 1739 | 603.5449 | 603.5449 | 603.5449 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -200.2288 | 403.3161 | -2750 | -200 | -2546.6839 | 63.67% | 44.67% | 95% | 0% | 1739 | -175
[5 empty] | 2019-10-04 | 1 | 6623.5 | 1492 | -170 | 0 | 0 | 1662 | 482.9349 | 482.9349 | 482.9349 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -194.508 | 288.4269 | -2750 | -200 | -2661.5731 | 66.54% | 44.67% | 95% | 0% | 1662 | -170
[5 empty] | 2019-10-04 | 2 | 6624 | 1445 | -165 | 0 | 0 | 1610 | 401.4839 | 401.4839 | 401.4839 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -188.7872 | 212.6967 | -2750 | -200 | -2737.3033 | 68.43% | 44.66% | 95% | 0% | 1610 | -165
[5 empty] | 2019-10-04 | 3 | 6624.5 | 1422 | -163 | 0 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -186.4989 | 175.826 | -2750 | -200 | -2774.174 | 69.35% | 44.66% | 95% | 0% | 1585 | -163
[5 empty] | 2019-10-04 | 4 | 6625 | 1445 | -162 | 0 | 0 | 1607 | 396.7848 | 396.7848 | 396.7848 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -185.3547 | 211.4301 | -2750 | -200 | -2738.5699 | 68.46% | 44.65% | 95% | 0% | 1607 | -162
[5 empty] | 2019-10-04 | 5 | 6625.5 | 1434 | -159 | 0 | 0 | 1593 | 374.8557 | 374.8557 | 374.8557 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -181.9222 | 192.9335 | -2750 | -200 | -2757.0665 | 68.93% | 44.64% | 95% | 0% | 1593 | -159
[5 empty] | 2019-10-04 | 6 | 6626 | 1431 | -156 | 0 | 0 | 1587 | 365.4575 | 365.4575 | 365.4575 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -178.4897 | 186.9678 | -2750 | -200 | -2763.0322 | 69.08% | 44.64% | 95% | 0% | 1587 | -156
[5 empty] | 2019-10-04 | 7 | 6626.5 | 1443 | -151 | 0 | 0 | 1594 | 376.4221 | 376.4221 | 376.4221 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -172.7689 | 203.6532 | -2750 | -200 | -2746.3468 | 68.66% | 44.64% | 95% | 0% | 1594 | -151
[5 empty] | 2019-10-04 | 8 | 6627 | 1438 | -147 | 0 | 0 | 1585 | 362.3248 | 362.3248 | 362.3248 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -168.1922 | 194.1326 | -2750 | -200 | -2755.8674 | 68.9% | 44.63% | 95% | 0% | 1585 | -147
[5 empty] | 2019-10-04 | 9 | 6627.5 | 1435 | -146 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -167.0481 | 189.0113 | -2750 | -200 | -2760.9887 | 69.02% | 44.62% | 95% | 0% | 1581 | -146
[5 empty] | 2019-10-04 | 10 | 6628 | 1437 | -144 | 0 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -164.7597 | 191.2996 | -2750 | -200 | -2758.7004 | 68.97% | 44.6% | 95% | 0% | 1581 | -144
[5 empty] | 2019-10-04 | 11 | 6628.5 | 1489 | -144 | 0 | 0 | 1633 | 437.5103 | 437.5103 | 437.5103 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -164.7597 | 272.7506 | -2750 | -200 | -2677.2494 | 66.93% | 44.6% | 95% | 0% | 1633 | -144
[5 empty] | 2019-10-04 | 12 | 6629 | 1589 | -144 | 1 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 805.6059 | 780 | 200 | 1785.6059 | 44.64% | 95% | 0% | -164.7597 | 429.387 | -3550 | -400 | -3520.613 | 88.02% | 44.59% | 95% | 0% | 1733 | -144
[5 empty] | 2019-10-04 | 13 | 6629.5 | 1800 | -145 | 1 | 0 | 1945 | 926.216 | 926.216 | 926.216 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -165.9039 | 760.3121 | -3550 | -400 | -3189.6879 | 79.74% | 44.58% | 95% | 0% | 1945 | -145
[5 empty] | 2019-10-04 | 14 | 6630 | 2031 | -145 | 1 | 0 | 2176 | 1288.0462 | 1288.0462 | 1288.0462 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -165.9039 | 1122.1423 | -3550 | -400 | -2827.8577 | 70.7% | 44.58% | 95% | 0% | 2176 | -145
[5 empty] | 2019-10-04 | 15 | 6630.5 | 2253 | -145 | 1 | 0 | 2398 | 1635.7791 | 1635.7791 | 1635.7791 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -165.9039 | 1469.8752 | -3550 | -400 | -2480.1248 | 62% | 44.58% | 95% | 0% | 2398 | -145
[5 empty] | 2019-10-04 | 16 | 6631 | 2369 | -156 | 1 | 0 | 2525 | 1834.7073 | 1834.7073 | 1834.7073 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -178.4897 | 1656.2176 | -3550 | -400 | -2293.7824 | 57.34% | 44.57% | 95% | 0% | 2525 | -156
[5 empty] | 2019-10-04 | 17 | 6631.5 | 2433 | -177 | 1 | 0 | 2610 | 1967.8483 | 1967.8483 | 1967.8483 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -202.5172 | 1765.3311 | -3550 | -400 | -2184.6689 | 54.62% | 44.57% | 95% | 0% | 2610 | -177
[5 empty] | 2019-10-04 | 18 | 6632 | 2377 | -208 | 1 | 0 | 2585 | 1928.6892 | 1928.6892 | 1928.6892 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -237.9863 | 1690.7029 | -3550 | -400 | -2259.2971 | 56.48% | 44.57% | 95% | 0% | 2585 | -208
[5 empty] | 2019-10-04 | 19 | 6632.5 | 2374 | -242 | 1 | 0 | 2616 | 1977.2465 | 1977.2465 | 1977.2465 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -276.8879 | 1700.3586 | -3550 | -400 | -2249.6414 | 56.24% | 44.57% | 95% | 0% | 2616 | -242
[5 empty] | 2019-10-04 | 20 | 6633 | 2336 | -262 | 1 | 0 | 2598 | 1949.0519 | 1949.0519 | 1949.0519 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -299.7712 | 1649.2808 | -3550 | -400 | -2300.7192 | 57.52% | 44.57% | 95% | 0% | 2598 | -262
[5 empty] | 2019-10-04 | 21 | 6633.5 | 2281 | -279 | 1 | 0 | 2560 | 1889.5301 | 1889.5301 | 1889.5301 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -319.222 | 1570.3081 | -3550 | -400 | -2379.6919 | 59.49% | 44.56% | 95% | 0% | 2560 | -279
[5 empty] | 2019-10-04 | 22 | 6634 | 2234 | -305 | 1 | 0 | 2539 | 1856.6364 | 1856.6364 | 1856.6364 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -348.9703 | 1507.6662 | -3550 | -400 | -2442.3338 | 61.06% | 44.56% | 95% | 0% | 2539 | -305
[5 empty] | 2019-10-04 | 23 | 6634.5 | 2206 | -324 | 1 | 0 | 2530 | 1842.5392 | 1842.5392 | 1842.5392 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -370.7094 | 1471.8298 | -3550 | -400 | -2478.1702 | 61.95% | 44.56% | 95% | 0% | 2530 | -324
[5 empty] | 2019-10-04 | 24 | 6635 | 2211 | -326 | 1 | 0 | 2537 | 1853.5037 | 1853.5037 | 1853.5037 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -372.9977 | 1480.506 | -3550 | -400 | -2469.494 | 61.74% | 44.55% | 95% | 0% | 2537 | -326
[5 empty] | 2019-10-04 | 25 | 6635.5 | 2203 | -334 | 1 | 0 | 2537 | 1853.5037 | 1853.5037 | 1853.5037 | 804.0396 | 780 | 200 | 1784.0396 | 44.6% | 95% | 0% | -382.151 | 1471.3527 | -3550 | -400 | -2478.6473 | 61.97% | 44.55% | 95% | 0% | 2537 | -334
[5 empty] | 2019-10-04 | 26 | 6636 | 2164 | -346 | 1 | 0 | 2510 | 1811.2119 | 1811.2119 | 1811.2119 | 802.4732 | 780 | 200 | 1782.4732 | 44.56% | 95% | 0% | -395.881 | 1415.3309 | -3550 | -400 | -2534.6691 | 63.37% | 44.55% | 95% | 0% | 2510 | -346
[5 empty] | 2019-10-04 | 27 | 6636.5 | 2165 | -326 | 1 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 802.4732 | 780 | 200 | 1782.4732 | 44.56% | 95% | 0% | -372.9977 | 1408.4532 | -3550 | -400 | -2541.5468 | 63.54% | 44.53% | 95% | 0% | 2491 | -326
[5 empty] | 2019-10-04 | 28 | 6637 | 2138 | -326 | 1 | 0 | 2464 | 1739.1591 | 1739.1591 | 1739.1591 | 802.4732 | 780 | 200 | 1782.4732 | 44.56% | 95% | 0% | -372.9977 | 1366.1614 | -3550 | -400 | -2583.8386 | 64.6% | 44.53% | 95% | 0% | 2464 | -326
[5 empty] | 2019-10-04 | 29 | 6637.5 | 2123 | -324 | 1 | 0 | 2447 | 1712.5309 | 1712.5309 | 1712.5309 | 802.4732 | 780 | 200 | 1782.4732 | 44.56% | 95% | 0% | -370.7094 | 1341.8215 | -3550 | -400 | -2608.1785 | 65.2% | 44.53% | 95% | 0% | 2447 | -324
[5 empty] | 2019-10-04 | 30 | 6638 | 2080 | -323 | 1 | 0 | 2403 | 1643.6109 | 1643.6109 | 1643.6109 | 802.4732 | 780 | 200 | 1782.4732 | 44.56% | 95% | 0% | -369.5652 | 1274.0457 | -3550 | -400 | -2675.9543 | 66.9% | 44.52% | 95% | 0% | 2403 | -323
[5 empty] | 2019-10-04 | 31 | 6638.5 | 2078 | -311 | 1 | 0 | 2389 | 1621.6818 | 1621.6818 | 1621.6818 | 802.4732 | 780 | 200 | 1782.4732 | 44.56% | 95% | 0% | -355.8352 | 1265.8465 | -3550 | -400 | -2684.1535 | 67.1% | 44.51% | 95% | 0% | 2389 | -311
[5 empty] | 2019-10-04 | 32 | 6639 | 2155 | -291 | 1 | 0 | 2446 | 1710.9646 | 1710.9646 | 1710.9646 | 802.4732 | 780 | 200 | 1782.4732 | 44.56% | 95% | 0% | -332.9519 | 1378.0126 | -3550 | -400 | -2571.9874 | 64.3% | 44.51% | 95% | 0% | 2446 | -291
[5 empty] | 2019-10-04 | 33 | 6639.5 | 2288 | -229 | 1 | 0 | 2517 | 1822.1764 | 1822.1764 | 1822.1764 | 802.4732 | 780 | 200 | 1782.4732 | 44.56% | 95% | 0% | -262.0137 | 1560.1627 | -3550 | -400 | -2389.8373 | 59.75% | 44.51% | 95% | 0% | 2517 | -229
[5 empty] | 2019-10-04 | 34 | 6640 | 2398 | -177 | 1 | 0 | 2575 | 1913.0256 | 1913.0256 | 1913.0256 | 800.9068 | 780 | 200 | 1780.9068 | 44.52% | 95% | 0% | -202.5172 | 1710.5084 | -3550 | -400 | -2239.4916 | 55.99% | 44.5% | 95% | 0% | 2575 | -177
[5 empty] | 2019-10-04 | 35 | 6640.5 | 2507 | -147 | 1 | 0 | 2654 | 2036.7683 | 2036.7683 | 2036.7683 | 800.9068 | 780 | 200 | 1780.9068 | 44.52% | 95% | 0% | -168.1922 | 1868.5761 | -3550 | -400 | -2081.4239 | 52.04% | 44.5% | 95% | 0% | 2654 | -147
[5 empty] | 2019-10-04 | 36 | 6641 | 2582 | -118 | 1 | 0 | 2700 | 2108.8211 | 2108.8211 | 2108.8211 | 800.9068 | 780 | 200 | 1780.9068 | 44.52% | 95% | 0% | -135.0114 | 1973.8097 | -3550 | -400 | -1976.1903 | 49.4% | 44.48% | 95% | 0% | 2700 | -118
[5 empty] | 2019-10-04 | 37 | 6641.5 | 2620 | -93 | 1 | 0 | 2713 | 2129.1838 | 2129.1838 | 2129.1838 | 800.9068 | 780 | 200 | 1780.9068 | 44.52% | 95% | 0% | -106.4073 | 2022.7765 | -3550 | -400 | -1927.2235 | 48.18% | 44.48% | 95% | 0% | 2713 | -93
[5 empty] | 2019-10-04 | 38 | 6642 | 2677 | -87 | 1 | 0 | 2764 | 2209.0684 | 2209.0684 | 2209.0684 | 800.9068 | 780 | 200 | 1780.9068 | 44.52% | 95% | 0% | -99.5423 | 2109.5261 | -3550 | -400 | -1840.4739 | 46.01% | 44.48% | 95% | 0% | 2764 | -87
[5 empty] | 2019-10-04 | 39 | 6642.5 | 2694 | -84 | 1 | 0 | 2778 | 2230.9975 | 2230.9975 | 2230.9975 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -96.1098 | 2134.8877 | -3550 | -400 | -1815.1123 | 45.38% | 44.47% | 95% | 0% | 2778 | -84
[5 empty] | 2019-10-04 | 40 | 6643 | 2637 | -80 | 0 | 0 | 2717 | 2135.4493 | 2135.4493 | 2135.4493 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -91.5332 | 2043.9161 | -2750 | -200 | -906.0839 | 22.65% | 44.46% | 95% | 0% | 2717 | -80
[5 empty] | 2019-10-04 | 41 | 6643.5 | 2537 | -78 | 0 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -89.2449 | 1886.4353 | -2750 | -200 | -1063.5647 | 26.59% | 44.46% | 95% | 0% | 2615 | -78
[5 empty] | 2019-10-04 | 42 | 6644 | 2456 | -75 | 0 | 0 | 2531 | 1844.1055 | 1844.1055 | 1844.1055 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -85.8124 | 1758.2932 | -2750 | -200 | -1191.7068 | 29.79% | 44.46% | 95% | 0% | 2531 | -75
[5 empty] | 2019-10-04 | 43 | 6644.5 | 2361 | -73 | 0 | 0 | 2434 | 1692.1682 | 1692.1682 | 1692.1682 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -83.524 | 1608.6442 | -2750 | -200 | -1341.3558 | 33.53% | 44.46% | 95% | 0% | 2434 | -73
[5 empty] | 2019-10-04 | 44 | 6645 | 2267 | -70 | 0 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -80.0915 | 1460.1393 | -2750 | -200 | -1489.8607 | 37.25% | 44.46% | 95% | 0% | 2337 | -70
[5 empty] | 2019-10-04 | 45 | 6645.5 | 2149 | -67 | 0 | 0 | 2216 | 1350.7007 | 1350.7007 | 1350.7007 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -76.659 | 1274.0417 | -2750 | -200 | -1675.9583 | 41.9% | 44.45% | 95% | 0% | 2216 | -67
[5 empty] | 2019-10-04 | 46 | 6646 | 2038 | -65 | 0 | 0 | 2103 | 1173.7016 | 1173.7016 | 1173.7016 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -74.3707 | 1099.3309 | -2750 | -200 | -1850.6691 | 46.27% | 44.45% | 95% | 0% | 2103 | -65
[5 empty] | 2019-10-04 | 47 | 6646.5 | 1910 | -63 | 0 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -72.0824 | 897.9918 | -2750 | -200 | -2052.0082 | 51.3% | 44.44% | 95% | 0% | 1973 | -63
[5 empty] | 2019-10-04 | 48 | 6647 | 1811 | -62 | 0 | 0 | 1873 | 813.4378 | 813.4378 | 813.4378 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -70.9382 | 742.4995 | -2750 | -200 | -2207.5005 | 55.19% | 44.44% | 95% | 0% | 1873 | -62
[5 empty] | 2019-10-05 | 1 | 6647.5 | 1741 | -60 | 0 | 0 | 1801 | 700.6595 | 700.6595 | 700.6595 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -68.6499 | 632.0096 | -2750 | -200 | -2317.9904 | 57.95% | 44.44% | 95% | 0% | 1801 | -60
[5 empty] | 2019-10-05 | 2 | 6648 | 1683 | -58 | 0 | 0 | 1741 | 606.6777 | 606.6777 | 606.6777 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -66.3616 | 540.3161 | -2750 | -200 | -2409.6839 | 60.24% | 44.43% | 95% | 0% | 1741 | -58
[5 empty] | 2019-10-05 | 3 | 6648.5 | 1665 | -57 | 0 | 0 | 1722 | 576.9167 | 576.9167 | 576.9167 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -65.2174 | 511.6993 | -2750 | -200 | -2438.3007 | 60.96% | 44.43% | 95% | 0% | 1722 | -57
[5 empty] | 2019-10-05 | 4 | 6649 | 1662 | -57 | 0 | 0 | 1719 | 572.2176 | 572.2176 | 572.2176 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -65.2174 | 507.0003 | -2750 | -200 | -2442.9997 | 61.07% | 44.42% | 95% | 0% | 1719 | -57
[5 empty] | 2019-10-05 | 5 | 6649.5 | 1640 | -57 | 0 | 0 | 1697 | 537.7576 | 537.7576 | 537.7576 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -65.2174 | 472.5402 | -2750 | -200 | -2477.4598 | 61.94% | 44.42% | 95% | 0% | 1697 | -57
[5 empty] | 2019-10-05 | 6 | 6650 | 1612 | -57 | 0 | 0 | 1669 | 493.8994 | 493.8994 | 493.8994 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -65.2174 | 428.682 | -2750 | -200 | -2521.318 | 63.03% | 44.41% | 95% | 0% | 1669 | -57
[5 empty] | 2019-10-05 | 7 | 6650.5 | 1572 | -56 | 0 | 0 | 1628 | 429.6785 | 429.6785 | 429.6785 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -64.0732 | 365.6053 | -2750 | -200 | -2584.3947 | 64.61% | 44.41% | 95% | 0% | 1628 | -56
[5 empty] | 2019-10-05 | 8 | 6651 | 1552 | -56 | 0 | 0 | 1608 | 398.3512 | 398.3512 | 398.3512 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -64.0732 | 334.278 | -2750 | -200 | -2615.722 | 65.39% | 44.41% | 95% | 0% | 1608 | -56
[5 empty] | 2019-10-05 | 9 | 6651.5 | 1529 | -60 | 0 | 0 | 1589 | 368.5903 | 368.5903 | 368.5903 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -68.6499 | 299.9404 | -2750 | -200 | -2650.0596 | 66.25% | 44.41% | 95% | 0% | 1589 | -60
[5 empty] | 2019-10-05 | 10 | 6652 | 1528 | -64 | 0 | 0 | 1592 | 373.2894 | 373.2894 | 373.2894 | 799.3405 | 780 | 200 | 1779.3405 | 44.48% | 95% | 0% | -73.2265 | 300.0628 | -2750 | -200 | -2649.9372 | 66.25% | 44.4% | 95% | 0% | 1592 | -64
[5 empty] | 2019-10-05 | 11 | 6652.5 | 1547 | -67 | 0 | 0 | 1614 | 407.7494 | 407.7494 | 407.7494 | 797.7741 | 780 | 200 | 1777.7741 | 44.44% | 95% | 0% | -76.659 | 331.0903 | -2750 | -200 | -2618.9097 | 65.47% | 44.39% | 95% | 0% | 1614 | -67
[5 empty] | 2019-10-05 | 12 | 6653 | 1587 | -70 | 0 | 0 | 1657 | 475.1031 | 475.1031 | 475.1031 | 797.7741 | 780 | 200 | 1777.7741 | 44.44% | 95% | 0% | -80.0915 | 395.0115 | -2750 | -200 | -2554.9885 | 63.87% | 44.39% | 95% | 0% | 1657 | -70
[5 empty] | 2019-10-05 | 13 | 6653.5 | 1687 | -71 | 0 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 797.7741 | 780 | 200 | 1777.7741 | 44.44% | 95% | 0% | -81.2357 | 552.0702 | -2750 | -200 | -2397.9298 | 59.95% | 44.39% | 95% | 0% | 1758 | -71
[5 empty] | 2019-10-05 | 14 | 6654 | 1788 | -72 | 0 | 0 | 1860 | 793.075 | 793.075 | 793.075 | 797.7741 | 780 | 200 | 1777.7741 | 44.44% | 95% | 0% | -82.3799 | 710.6952 | -2750 | -200 | -2239.3048 | 55.98% | 44.39% | 95% | 0% | 1860 | -72
[5 empty] | 2019-10-05 | 15 | 6654.5 | 1900 | -73 | 1 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 797.7741 | 780 | 200 | 1777.7741 | 44.44% | 95% | 0% | -83.524 | 886.5502 | -3550 | -400 | -3063.4498 | 76.59% | 44.38% | 95% | 0% | 1973 | -73
[5 empty] | 2019-10-05 | 16 | 6655 | 2001 | -80 | 1 | 0 | 2081 | 1139.2415 | 1139.2415 | 1139.2415 | 797.7741 | 780 | 200 | 1777.7741 | 44.44% | 95% | 0% | -91.5332 | 1047.7084 | -3550 | -400 | -2902.2916 | 72.56% | 44.38% | 95% | 0% | 2081 | -80
[5 empty] | 2019-10-05 | 17 | 6655.5 | 2102 | -103 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 797.7741 | 780 | 200 | 1777.7741 | 44.44% | 95% | 0% | -117.849 | 1215.6218 | -3550 | -400 | -2734.3782 | 68.36% | 44.38% | 95% | 0% | 2205 | -103
[5 empty] | 2019-10-05 | 18 | 6656 | 2149 | -127 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 797.7741 | 780 | 200 | 1777.7741 | 44.44% | 95% | 0% | -145.3089 | 1299.3737 | -3550 | -400 | -2650.6263 | 66.27% | 44.38% | 95% | 0% | 2276 | -127
[5 empty] | 2019-10-05 | 19 | 6656.5 | 2146 | -166 | 1 | 0 | 2312 | 1501.0717 | 1501.0717 | 1501.0717 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -189.9314 | 1311.1404 | -3550 | -400 | -2638.8596 | 65.97% | 44.37% | 95% | 0% | 2312 | -166
[5 empty] | 2019-10-05 | 20 | 6657 | 2115 | -207 | 1 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -236.8421 | 1279.8933 | -3550 | -400 | -2670.1067 | 66.75% | 44.37% | 95% | 0% | 2322 | -207
[5 empty] | 2019-10-05 | 21 | 6657.5 | 2093 | -235 | 1 | 0 | 2328 | 1526.1336 | 1526.1336 | 1526.1336 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -268.8787 | 1257.2548 | -3550 | -400 | -2692.7452 | 67.32% | 44.36% | 95% | 0% | 2328 | -235
[5 empty] | 2019-10-05 | 22 | 6658 | 2041 | -273 | 1 | 0 | 2314 | 1504.2045 | 1504.2045 | 1504.2045 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -312.357 | 1191.8475 | -3550 | -400 | -2758.1525 | 68.95% | 44.34% | 95% | 0% | 2314 | -273
[5 empty] | 2019-10-05 | 23 | 6658.5 | 1998 | -306 | 1 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -350.1144 | 1138.4264 | -3550 | -400 | -2811.5736 | 70.29% | 44.34% | 95% | 0% | 2304 | -306
[5 empty] | 2019-10-05 | 24 | 6659 | 1960 | -330 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -377.5744 | 1089.0373 | -3550 | -400 | -2860.9627 | 71.52% | 44.34% | 95% | 0% | 2290 | -330
[5 empty] | 2019-10-05 | 25 | 6659.5 | 1947 | -326 | 1 | 0 | 2273 | 1439.9835 | 1439.9835 | 1439.9835 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -372.9977 | 1066.9858 | -3550 | -400 | -2883.0142 | 72.08% | 44.33% | 95% | 0% | 2273 | -326
[5 empty] | 2019-10-05 | 26 | 6660 | 1880 | -350 | 1 | 0 | 2230 | 1372.6298 | 1372.6298 | 1372.6298 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -400.4577 | 972.1722 | -3550 | -400 | -2977.8278 | 74.45% | 44.32% | 95% | 0% | 2230 | -350
[5 empty] | 2019-10-05 | 27 | 6660.5 | 1829 | -360 | 1 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -411.8993 | 896.5096 | -3550 | -400 | -3053.4904 | 76.34% | 44.32% | 95% | 0% | 2189 | -360
[5 empty] | 2019-10-05 | 28 | 6661 | 1800 | -362 | 1 | 0 | 2162 | 1266.1171 | 1266.1171 | 1266.1171 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -414.1876 | 851.9294 | -3550 | -400 | -3098.0706 | 77.45% | 44.31% | 95% | 0% | 2162 | -362
[5 empty] | 2019-10-05 | 29 | 6661.5 | 1802 | -338 | 1 | 0 | 2140 | 1231.657 | 1231.657 | 1231.657 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -386.7277 | 844.9294 | -3550 | -400 | -3105.0706 | 77.63% | 44.31% | 95% | 0% | 2140 | -338
[5 empty] | 2019-10-05 | 30 | 6662 | 1833 | -318 | 1 | 0 | 2151 | 1248.8871 | 1248.8871 | 1248.8871 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -363.8444 | 885.0427 | -3550 | -400 | -3064.9573 | 76.62% | 44.31% | 95% | 0% | 2151 | -318
[5 empty] | 2019-10-05 | 31 | 6662.5 | 1899 | -273 | 1 | 0 | 2172 | 1281.7807 | 1281.7807 | 1281.7807 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -312.357 | 969.4237 | -3550 | -400 | -2980.5763 | 74.51% | 44.3% | 95% | 0% | 2172 | -273
[5 empty] | 2019-10-05 | 32 | 6663 | 1976 | -227 | 1 | 0 | 2203 | 1330.338 | 1330.338 | 1330.338 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -259.7254 | 1070.6126 | -3550 | -400 | -2879.3874 | 71.98% | 44.3% | 95% | 0% | 2203 | -227
[5 empty] | 2019-10-05 | 33 | 6663.5 | 2055 | -195 | 1 | 0 | 2250 | 1403.9571 | 1403.9571 | 1403.9571 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -223.1121 | 1180.845 | -3550 | -400 | -2769.155 | 69.23% | 44.3% | 95% | 0% | 2250 | -195
[5 empty] | 2019-10-05 | 34 | 6664 | 2164 | -163 | 1 | 0 | 2327 | 1524.5672 | 1524.5672 | 1524.5672 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -186.4989 | 1338.0683 | -3550 | -400 | -2611.9317 | 65.3% | 44.3% | 95% | 0% | 2327 | -163
[5 empty] | 2019-10-05 | 35 | 6664.5 | 2297 | -144 | 1 | 0 | 2441 | 1703.1327 | 1703.1327 | 1703.1327 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -164.7597 | 1538.373 | -3550 | -400 | -2411.627 | 60.29% | 44.28% | 95% | 0% | 2441 | -144
[5 empty] | 2019-10-05 | 36 | 6665 | 2363 | -129 | 1 | 0 | 2492 | 1783.0173 | 1783.0173 | 1783.0173 | 796.2077 | 780 | 200 | 1776.2077 | 44.41% | 95% | 0% | -147.5973 | 1635.4201 | -3550 | -400 | -2314.5799 | 57.86% | 44.28% | 95% | 0% | 2492 | -129
[5 empty] | 2019-10-05 | 37 | 6665.5 | 2397 | -125 | 1 | 0 | 2522 | 1830.0082 | 1830.0082 | 1830.0082 | 794.6414 | 780 | 200 | 1774.6414 | 44.37% | 95% | 0% | -143.0206 | 1686.9876 | -3550 | -400 | -2263.0124 | 56.58% | 44.26% | 95% | 0% | 2522 | -125
[5 empty] | 2019-10-05 | 38 | 6666 | 2433 | -128 | 1 | 0 | 2561 | 1891.0965 | 1891.0965 | 1891.0965 | 794.6414 | 780 | 200 | 1774.6414 | 44.37% | 95% | 0% | -146.4531 | 1744.6434 | -3550 | -400 | -2205.3566 | 55.13% | 44.26% | 95% | 0% | 2561 | -128
[5 empty] | 2019-10-05 | 39 | 6666.5 | 2369 | -132 | 1 | 0 | 2501 | 1797.1146 | 1797.1146 | 1797.1146 | 794.6414 | 780 | 200 | 1774.6414 | 44.37% | 95% | 0% | -151.0297 | 1646.0848 | -3550 | -400 | -2303.9152 | 57.6% | 44.26% | 95% | 0% | 2501 | -132
[5 empty] | 2019-10-05 | 40 | 6667 | 2322 | -136 | 0 | 0 | 2458 | 1729.7609 | 1729.7609 | 1729.7609 | 794.6414 | 780 | 200 | 1774.6414 | 44.37% | 95% | 0% | -155.6064 | 1574.1545 | -2750 | -200 | -1375.8455 | 34.4% | 44.26% | 95% | 0% | 2458 | -136
[5 empty] | 2019-10-05 | 41 | 6667.5 | 2256 | -139 | 0 | 0 | 2395 | 1631.08 | 1631.08 | 1631.08 | 794.6414 | 780 | 200 | 1774.6414 | 44.37% | 95% | 0% | -159.0389 | 1472.0411 | -2750 | -200 | -1477.9589 | 36.95% | 44.25% | 95% | 0% | 2395 | -139
[5 empty] | 2019-10-05 | 42 | 6668 | 2162 | -142 | 0 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 794.6414 | 780 | 200 | 1774.6414 | 44.37% | 95% | 0% | -162.4714 | 1326.0694 | -2750 | -200 | -1623.9306 | 40.6% | 44.25% | 95% | 0% | 2304 | -142
[5 empty] | 2019-10-05 | 43 | 6668.5 | 2074 | -145 | 0 | 0 | 2219 | 1355.3998 | 1355.3998 | 1355.3998 | 794.6414 | 780 | 200 | 1774.6414 | 44.37% | 95% | 0% | -165.9039 | 1189.4959 | -2750 | -200 | -1760.5041 | 44.01% | 44.24% | 95% | 0% | 2219 | -145
[5 empty] | 2019-10-05 | 44 | 6669 | 1980 | -147 | 0 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 794.6414 | 780 | 200 | 1774.6414 | 44.37% | 95% | 0% | -168.1922 | 1043.1021 | -2750 | -200 | -1906.8979 | 47.67% | 44.23% | 95% | 0% | 2127 | -147
[5 empty] | 2019-10-05 | 45 | 6669.5 | 1884 | -148 | 0 | 0 | 2032 | 1062.4897 | 1062.4897 | 1062.4897 | 794.6414 | 780 | 200 | 1774.6414 | 44.37% | 95% | 0% | -169.3364 | 893.1533 | -2750 | -200 | -2056.8467 | 51.42% | 44.23% | 95% | 0% | 2032 | -148
[5 empty] | 2019-10-05 | 46 | 6670 | 1782 | -150 | 0 | 0 | 1932 | 905.8533 | 905.8533 | 905.8533 | 794.6414 | 780 | 200 | 1774.6414 | 44.37% | 95% | 0% | -171.6247 | 734.2285 | -2750 | -200 | -2215.7715 | 55.39% | 44.23% | 95% | 0% | 1932 | -150
[5 empty] | 2019-10-05 | 47 | 6670.5 | 1663 | -151 | 0 | 0 | 1814 | 721.0223 | 721.0223 | 721.0223 | 794.6414 | 780 | 200 | 1774.6414 | 44.37% | 95% | 0% | -172.7689 | 548.2534 | -2750 | -200 | -2401.7466 | 60.04% | 44.22% | 95% | 0% | 1814 | -151
[5 empty] | 2019-10-05 | 48 | 6671 | 1557 | -152 | 0 | 0 | 1709 | 556.554 | 556.554 | 556.554 | 794.6414 | 780 | 200 | 1774.6414 | 44.37% | 95% | 0% | -173.913 | 382.641 | -2750 | -200 | -2567.359 | 64.18% | 44.22% | 95% | 0% | 1709 | -152
[5 empty] | 2019-10-06 | 1 | 6671.5 | 1471 | -152 | 0 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 793.075 | 780 | 200 | 1773.075 | 44.33% | 95% | 0% | -173.913 | 247.9336 | -2750 | -200 | -2702.0664 | 67.55% | 44.22% | 95% | 0% | 1623 | -152
[5 empty] | 2019-10-06 | 2 | 6672 | 1418 | -152 | 0 | 0 | 1570 | 338.8293 | 338.8293 | 338.8293 | 793.075 | 780 | 200 | 1773.075 | 44.33% | 95% | 0% | -173.913 | 164.9163 | -2750 | -200 | -2785.0837 | 69.63% | 44.22% | 95% | 0% | 1570 | -152
[5 empty] | 2019-10-06 | 3 | 6672.5 | 1386 | -154 | 0 | 0 | 1540 | 291.8384 | 291.8384 | 291.8384 | 793.075 | 780 | 200 | 1773.075 | 44.33% | 95% | 0% | -176.2014 | 115.637 | -2750 | -200 | -2834.363 | 70.86% | 44.22% | 95% | 0% | 1540 | -154
[5 empty] | 2019-10-06 | 4 | 6673 | 1387 | -155 | 0 | 0 | 1542 | 294.9711 | 294.9711 | 294.9711 | 793.075 | 780 | 200 | 1773.075 | 44.33% | 95% | 0% | -177.3455 | 117.6256 | -2750 | -200 | -2832.3744 | 70.81% | 44.19% | 95% | 0% | 1542 | -155
[5 empty] | 2019-10-06 | 5 | 6673.5 | 1368 | -154 | 0 | 0 | 1522 | 263.6439 | 263.6439 | 263.6439 | 793.075 | 780 | 200 | 1773.075 | 44.33% | 95% | 0% | -176.2014 | 87.4425 | -2750 | -200 | -2862.5575 | 71.56% | 44.19% | 95% | 0% | 1522 | -154
[5 empty] | 2019-10-06 | 6 | 6674 | 1324 | -154 | 0 | 0 | 1478 | 194.7238 | 194.7238 | 194.7238 | 793.075 | 780 | 200 | 1773.075 | 44.33% | 95% | 0% | -176.2014 | 18.5225 | -2750 | -200 | -2931.4775 | 73.29% | 44.19% | 95% | 0% | 1478 | -154
[5 empty] | 2019-10-06 | 7 | 6674.5 | 1287 | -153 | 0 | 0 | 1440 | 135.202 | 135.202 | 135.202 | 793.075 | 780 | 200 | 1773.075 | 44.33% | 95% | 0% | -175.0572 | -39.8552 | -2750 | -200 | -2989.8552 | 74.75% | 44.18% | 95% | 0% | 1440 | -153
[5 empty] | 2019-10-06 | 8 | 6675 | 1270 | -152 | 0 | 0 | 1422 | 107.0074 | 107.0074 | 107.0074 | 793.075 | 780 | 200 | 1773.075 | 44.33% | 95% | 0% | -173.913 | -66.9056 | -2750 | -200 | -3016.9056 | 75.42% | 44.18% | 95% | 0% | 1422 | -152
[5 empty] | 2019-10-06 | 9 | 6675.5 | 1247 | -152 | 0 | 0 | 1399 | 70.981 | 70.981 | 70.981 | 791.5087 | 780 | 200 | 1771.5087 | 44.29% | 95% | 0% | -173.913 | -102.932 | -2750 | -200 | -3052.932 | 76.32% | 44.17% | 95% | 0% | 1399 | -152
[5 empty] | 2019-10-06 | 10 | 6676 | 1240 | -152 | 0 | 0 | 1392 | 60.0165 | 60.0165 | 60.0165 | 791.5087 | 780 | 200 | 1771.5087 | 44.29% | 95% | 0% | -173.913 | -113.8966 | -2750 | -200 | -3063.8966 | 76.6% | 44.17% | 95% | 0% | 1392 | -152
[5 empty] | 2019-10-06 | 11 | 6676.5 | 1261 | -150 | 0 | 0 | 1411 | 89.7774 | 89.7774 | 89.7774 | 791.5087 | 780 | 200 | 1771.5087 | 44.29% | 95% | 0% | -171.6247 | -81.8473 | -2750 | -200 | -3031.8473 | 75.8% | 44.17% | 95% | 0% | 1411 | -150
[5 empty] | 2019-10-06 | 12 | 6677 | 1287 | -148 | 0 | 0 | 1435 | 127.3702 | 127.3702 | 127.3702 | 791.5087 | 780 | 200 | 1771.5087 | 44.29% | 95% | 0% | -169.3364 | -41.9662 | -2750 | -200 | -2991.9662 | 74.8% | 44.16% | 95% | 0% | 1435 | -148
[5 empty] | 2019-10-06 | 13 | 6677.5 | 1370 | -144 | 0 | 0 | 1514 | 251.1129 | 251.1129 | 251.1129 | 791.5087 | 780 | 200 | 1771.5087 | 44.29% | 95% | 0% | -164.7597 | 86.3532 | -2750 | -200 | -2863.6468 | 71.59% | 44.16% | 95% | 0% | 1514 | -144
[5 empty] | 2019-10-06 | 14 | 6678 | 1434 | -140 | 0 | 0 | 1574 | 345.0948 | 345.0948 | 345.0948 | 791.5087 | 780 | 200 | 1771.5087 | 44.29% | 95% | 0% | -160.1831 | 184.9117 | -2750 | -200 | -2765.0883 | 69.13% | 44.15% | 95% | 0% | 1574 | -140
[5 empty] | 2019-10-06 | 15 | 6678.5 | 1527 | -138 | 0 | 0 | 1665 | 487.634 | 487.634 | 487.634 | 791.5087 | 780 | 200 | 1771.5087 | 44.29% | 95% | 0% | -157.8947 | 329.7392 | -2750 | -200 | -2620.2608 | 65.51% | 44.15% | 95% | 0% | 1665 | -138
[5 empty] | 2019-10-06 | 16 | 6679 | 1605 | -142 | 0 | 0 | 1747 | 616.0758 | 616.0758 | 616.0758 | 789.9423 | 780 | 200 | 1769.9423 | 44.25% | 95% | 0% | -162.4714 | 453.6044 | -2750 | -200 | -2496.3956 | 62.41% | 44.15% | 95% | 0% | 1747 | -142
[5 empty] | 2019-10-06 | 17 | 6679.5 | 1697 | -167 | 0 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 789.9423 | 780 | 200 | 1769.9423 | 44.25% | 95% | 0% | -191.0755 | 608.265 | -2750 | -200 | -2341.735 | 58.54% | 44.14% | 95% | 0% | 1864 | -167
[5 empty] | 2019-10-06 | 18 | 6680 | 1734 | -208 | 0 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 789.9423 | 780 | 200 | 1769.9423 | 44.25% | 95% | 0% | -237.9863 | 683.5306 | -2750 | -200 | -2266.4694 | 56.66% | 44.14% | 95% | 0% | 1942 | -208
[5 empty] | 2019-10-06 | 19 | 6680.5 | 1745 | -258 | 1 | 0 | 2003 | 1017.0651 | 1017.0651 | 1017.0651 | 789.9423 | 780 | 200 | 1769.9423 | 44.25% | 95% | 0% | -295.1945 | 721.8706 | -3550 | -400 | -3228.1294 | 80.7% | 44.13% | 95% | 0% | 2003 | -258
[5 empty] | 2019-10-06 | 20 | 6681 | 1714 | -307 | 1 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 789.9423 | 780 | 200 | 1769.9423 | 44.25% | 95% | 0% | -351.2586 | 694.0011 | -3550 | -400 | -3255.9989 | 81.4% | 44.13% | 95% | 0% | 2021 | -307
[5 empty] | 2019-10-06 | 21 | 6681.5 | 1679 | -351 | 1 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 789.9423 | 780 | 200 | 1769.9423 | 44.25% | 95% | 0% | -401.6018 | 657.7551 | -3550 | -400 | -3292.2449 | 82.31% | 44.13% | 95% | 0% | 2030 | -351
[5 empty] | 2019-10-06 | 22 | 6682 | 1620 | -405 | 1 | 0 | 2025 | 1051.5251 | 1051.5251 | 1051.5251 | 789.9423 | 780 | 200 | 1769.9423 | 44.25% | 95% | 0% | -463.3867 | 588.1384 | -3550 | -400 | -3361.8616 | 84.05% | 44.12% | 95% | 0% | 2025 | -405
[5 empty] | 2019-10-06 | 23 | 6682.5 | 1577 | -451 | 1 | 0 | 2028 | 1056.2242 | 1056.2242 | 1056.2242 | 789.9423 | 780 | 200 | 1769.9423 | 44.25% | 95% | 0% | -516.0183 | 540.2059 | -3550 | -400 | -3409.7941 | 85.24% | 44.12% | 95% | 0% | 2028 | -451
[5 empty] | 2019-10-06 | 24 | 6683 | 1531 | -483 | 1 | 0 | 2014 | 1034.2951 | 1034.2951 | 1034.2951 | 789.9423 | 780 | 200 | 1769.9423 | 44.25% | 95% | 0% | -552.6316 | 481.6636 | -3550 | -400 | -3468.3364 | 86.71% | 44.12% | 95% | 0% | 2014 | -483
[5 empty] | 2019-10-06 | 25 | 6683.5 | 1495 | -507 | 1 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 789.9423 | 780 | 200 | 1769.9423 | 44.25% | 95% | 0% | -580.0915 | 435.4072 | -3550 | -400 | -3514.5928 | 87.86% | 44.12% | 95% | 0% | 2002 | -507
[5 empty] | 2019-10-06 | 26 | 6684 | 1494 | -496 | 1 | 0 | 1990 | 996.7024 | 996.7024 | 996.7024 | 789.9423 | 780 | 200 | 1769.9423 | 44.25% | 95% | 0% | -567.5057 | 429.1967 | -3550 | -400 | -3520.8033 | 88.02% | 44.12% | 95% | 0% | 1990 | -496
[5 empty] | 2019-10-06 | 27 | 6684.5 | 1517 | -458 | 1 | 0 | 1975 | 973.2069 | 973.2069 | 973.2069 | 789.9423 | 780 | 200 | 1769.9423 | 44.25% | 95% | 0% | -524.0275 | 449.1795 | -3550 | -400 | -3500.8205 | 87.52% | 44.11% | 95% | 0% | 1975 | -458
[5 empty] | 2019-10-06 | 28 | 6685 | 1502 | -454 | 1 | 0 | 1956 | 943.446 | 943.446 | 943.446 | 788.3759 | 780 | 200 | 1768.3759 | 44.21% | 95% | 0% | -519.4508 | 423.9952 | -3550 | -400 | -3526.0048 | 88.15% | 44.11% | 95% | 0% | 1956 | -454
[5 empty] | 2019-10-06 | 29 | 6685.5 | 1553 | -420 | 1 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 788.3759 | 780 | 200 | 1768.3759 | 44.21% | 95% | 0% | -480.5492 | 489.525 | -3550 | -400 | -3460.475 | 86.51% | 44.11% | 95% | 0% | 1973 | -420
[5 empty] | 2019-10-06 | 30 | 6686 | 1600 | -400 | 1 | 0 | 2000 | 1012.366 | 1012.366 | 1012.366 | 788.3759 | 780 | 200 | 1768.3759 | 44.21% | 95% | 0% | -457.6659 | 554.7001 | -3550 | -400 | -3395.2999 | 84.88% | 44.1% | 95% | 0% | 2000 | -400
[5 empty] | 2019-10-06 | 31 | 6686.5 | 1659 | -379 | 1 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 788.3759 | 780 | 200 | 1768.3759 | 44.21% | 95% | 0% | -433.6384 | 638.2494 | -3550 | -400 | -3311.7506 | 82.79% | 44.09% | 95% | 0% | 2038 | -379
[5 empty] | 2019-10-06 | 32 | 6687 | 1748 | -334 | 1 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 788.3759 | 780 | 200 | 1768.3759 | 44.21% | 95% | 0% | -382.151 | 758.6569 | -3550 | -400 | -3191.3431 | 79.78% | 44.08% | 95% | 0% | 2082 | -334
[5 empty] | 2019-10-06 | 33 | 6687.5 | 1907 | -285 | 1 | 0 | 2192 | 1313.108 | 1313.108 | 1313.108 | 788.3759 | 780 | 200 | 1768.3759 | 44.21% | 95% | 0% | -326.087 | 987.021 | -3550 | -400 | -2962.979 | 74.07% | 44.07% | 95% | 0% | 2192 | -285
[5 empty] | 2019-10-06 | 34 | 6688 | 2050 | -253 | 1 | 0 | 2303 | 1486.9744 | 1486.9744 | 1486.9744 | 788.3759 | 780 | 200 | 1768.3759 | 44.21% | 95% | 0% | -289.4737 | 1197.5008 | -3550 | -400 | -2752.4992 | 68.81% | 44.07% | 95% | 0% | 2303 | -253
[5 empty] | 2019-10-06 | 35 | 6688.5 | 2191 | -208 | 1 | 0 | 2399 | 1637.3454 | 1637.3454 | 1637.3454 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -237.9863 | 1399.3592 | -3550 | -400 | -2550.6408 | 63.77% | 44.05% | 95% | 0% | 2399 | -208
[5 empty] | 2019-10-06 | 36 | 6689 | 2280 | -157 | 1 | 0 | 2437 | 1696.8673 | 1696.8673 | 1696.8673 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -179.6339 | 1517.2334 | -3550 | -400 | -2432.7666 | 60.82% | 44.04% | 95% | 0% | 2437 | -157
[5 empty] | 2019-10-06 | 37 | 6689.5 | 2330 | -125 | 1 | 0 | 2455 | 1725.0618 | 1725.0618 | 1725.0618 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -143.0206 | 1582.0412 | -3550 | -400 | -2367.9588 | 59.2% | 44.04% | 95% | 0% | 2455 | -125
[5 empty] | 2019-10-06 | 38 | 6690 | 2417 | -116 | 1 | 0 | 2533 | 1847.2383 | 1847.2383 | 1847.2383 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -132.7231 | 1714.5151 | -3550 | -400 | -2235.4849 | 55.89% | 44.03% | 95% | 0% | 2533 | -116
[5 empty] | 2019-10-06 | 39 | 6690.5 | 2465 | -115 | 1 | 0 | 2580 | 1920.8574 | 1920.8574 | 1920.8574 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -131.5789 | 1789.2784 | -3550 | -400 | -2160.7216 | 54.02% | 44.02% | 95% | 0% | 2580 | -115
[5 empty] | 2019-10-06 | 40 | 6691 | 2407 | -115 | 0 | 0 | 2522 | 1830.0082 | 1830.0082 | 1830.0082 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -131.5789 | 1698.4293 | -2750 | -200 | -1251.5707 | 31.29% | 44.02% | 95% | 0% | 2522 | -115
[5 empty] | 2019-10-06 | 41 | 6691.5 | 2359 | -115 | 0 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -131.5789 | 1623.2438 | -2750 | -200 | -1326.7562 | 33.17% | 44.01% | 95% | 0% | 2474 | -115
[5 empty] | 2019-10-06 | 42 | 6692 | 2286 | -114 | 0 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -130.4348 | 1508.477 | -2750 | -200 | -1441.523 | 36.04% | 44.01% | 95% | 0% | 2400 | -114
[5 empty] | 2019-10-06 | 43 | 6692.5 | 2191 | -114 | 0 | 0 | 2305 | 1490.1072 | 1490.1072 | 1490.1072 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -130.4348 | 1359.6724 | -2750 | -200 | -1590.3276 | 39.76% | 44.01% | 95% | 0% | 2305 | -114
[5 empty] | 2019-10-06 | 44 | 6693 | 2064 | -115 | 0 | 0 | 2179 | 1292.7453 | 1292.7453 | 1292.7453 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -131.5789 | 1161.1663 | -2750 | -200 | -1788.8337 | 44.72% | 44.01% | 95% | 0% | 2179 | -115
[5 empty] | 2019-10-06 | 45 | 6693.5 | 1952 | -116 | 0 | 0 | 2068 | 1118.8788 | 1118.8788 | 1118.8788 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -132.7231 | 986.1557 | -2750 | -200 | -1963.8443 | 49.1% | 44.01% | 95% | 0% | 2068 | -116
[5 empty] | 2019-10-06 | 46 | 6694 | 1819 | -117 | 0 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -133.8673 | 778.2514 | -2750 | -200 | -2171.7486 | 54.29% | 44% | 95% | 0% | 1936 | -117
[5 empty] | 2019-10-06 | 47 | 6694.5 | 1693 | -118 | 0 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -135.0114 | 581.3117 | -2750 | -200 | -2368.6883 | 59.22% | 44% | 95% | 0% | 1811 | -118
[5 empty] | 2019-10-06 | 48 | 6695 | 1582 | -119 | 0 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 786.8096 | 780 | 200 | 1766.8096 | 44.17% | 95% | 0% | -136.1556 | 407.8675 | -2750 | -200 | -2542.1325 | 63.55% | 44% | 95% | 0% | 1701 | -119
[5 empty] | 2019-10-07 | 1 | 6695.5 | 1499 | -119 | 0 | 0 | 1618 | 414.0148 | 414.0148 | 414.0148 | 785.2432 | 780 | 200 | 1765.2432 | 44.13% | 95% | 0% | -136.1556 | 277.8592 | -2750 | -200 | -2672.1408 | 66.8% | 43.99% | 95% | 0% | 1618 | -119
[5 empty] | 2019-10-07 | 2 | 6696 | 1453 | -120 | 0 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 785.2432 | 780 | 200 | 1765.2432 | 44.13% | 95% | 0% | -137.2998 | 206.2287 | -2750 | -200 | -2743.7713 | 68.59% | 43.99% | 95% | 0% | 1573 | -120
[5 empty] | 2019-10-07 | 3 | 6696.5 | 1440 | -122 | 0 | 0 | 1562 | 326.2984 | 326.2984 | 326.2984 | 785.2432 | 780 | 200 | 1765.2432 | 44.13% | 95% | 0% | -139.5881 | 186.7103 | -2750 | -200 | -2763.2897 | 69.08% | 43.98% | 95% | 0% | 1562 | -122
[5 empty] | 2019-10-07 | 4 | 6697 | 1444 | -123 | 0 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 785.2432 | 780 | 200 | 1765.2432 | 44.13% | 95% | 0% | -140.7323 | 193.398 | -2750 | -200 | -2756.602 | 68.92% | 43.98% | 95% | 0% | 1567 | -123
[5 empty] | 2019-10-07 | 5 | 6697.5 | 1432 | -125 | 0 | 0 | 1557 | 318.4666 | 318.4666 | 318.4666 | 785.2432 | 780 | 200 | 1765.2432 | 44.13% | 95% | 0% | -143.0206 | 175.446 | -2750 | -200 | -2774.554 | 69.36% | 43.97% | 95% | 0% | 1557 | -125
[5 empty] | 2019-10-07 | 6 | 6698 | 1407 | -126 | 0 | 0 | 1533 | 280.8739 | 280.8739 | 280.8739 | 785.2432 | 780 | 200 | 1765.2432 | 44.13% | 95% | 0% | -144.1648 | 136.7091 | -2750 | -200 | -2813.2909 | 70.33% | 43.97% | 95% | 0% | 1533 | -126
[5 empty] | 2019-10-07 | 7 | 6698.5 | 1392 | -127 | 0 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 785.2432 | 780 | 200 | 1765.2432 | 44.13% | 95% | 0% | -145.3089 | 113.6358 | -2750 | -200 | -2836.3642 | 70.91% | 43.96% | 95% | 0% | 1519 | -127
[5 empty] | 2019-10-07 | 8 | 6699 | 1373 | -129 | 1 | 0 | 1502 | 232.3166 | 232.3166 | 232.3166 | 785.2432 | 780 | 200 | 1765.2432 | 44.13% | 95% | 0% | -147.5973 | 84.7193 | -3550 | -400 | -3865.2807 | 96.63% | 43.96% | 95% | 0% | 1502 | -129
[5 empty] | 2019-10-07 | 9 | 6699.5 | 1363 | -129 | 1 | 0 | 1492 | 216.6529 | 216.6529 | 216.6529 | 785.2432 | 780 | 200 | 1765.2432 | 44.13% | 95% | 0% | -147.5973 | 69.0557 | -3550 | -400 | -3880.9443 | 97.02% | 43.95% | 95% | 0% | 1492 | -129
[5 empty] | 2019-10-07 | 10 | 6700 | 1363 | -130 | 1 | 0 | 1493 | 218.2193 | 218.2193 | 218.2193 | 783.6768 | 780 | 200 | 1763.6768 | 44.09% | 95% | 0% | -148.7414 | 69.4779 | -3550 | -400 | -3880.5221 | 97.01% | 43.95% | 95% | 0% | 1493 | -130
[5 empty] | 2019-10-07 | 11 | 6700.5 | 1415 | -132 | 1 | 0 | 1547 | 302.803 | 302.803 | 302.803 | 783.6768 | 780 | 200 | 1763.6768 | 44.09% | 95% | 0% | -151.0297 | 151.7732 | -3550 | -400 | -3798.2268 | 94.96% | 43.95% | 95% | 0% | 1547 | -132
[5 empty] | 2019-10-07 | 12 | 6701 | 1521 | -135 | 1 | 0 | 1656 | 473.5367 | 473.5367 | 473.5367 | 783.6768 | 780 | 200 | 1763.6768 | 44.09% | 95% | 0% | -154.4622 | 319.0744 | -3550 | -400 | -3630.9256 | 90.77% | 43.94% | 95% | 0% | 1656 | -135
[5 empty] | 2019-10-07 | 13 | 6701.5 | 1747 | -137 | 1 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 783.6768 | 780 | 200 | 1763.6768 | 44.09% | 95% | 0% | -156.7506 | 673.9172 | -3550 | -400 | -3276.0828 | 81.9% | 43.94% | 95% | 0% | 1884 | -137
[5 empty] | 2019-10-07 | 14 | 6702 | 1990 | -140 | 1 | 0 | 2130 | 1215.9934 | 1215.9934 | 1215.9934 | 783.6768 | 780 | 200 | 1763.6768 | 44.09% | 95% | 0% | -160.1831 | 1055.8103 | -3550 | -400 | -2894.1897 | 72.35% | 43.94% | 95% | 0% | 2130 | -140
[5 empty] | 2019-10-07 | 15 | 6702.5 | 2252 | -144 | 1 | 0 | 2396 | 1632.6463 | 1632.6463 | 1632.6463 | 783.6768 | 780 | 200 | 1763.6768 | 44.09% | 95% | 0% | -164.7597 | 1467.8866 | -3550 | -400 | -2482.1134 | 62.05% | 43.92% | 95% | 0% | 2396 | -144
[5 empty] | 2019-10-07 | 16 | 6703 | 2381 | -149 | 1 | 0 | 2530 | 1842.5392 | 1842.5392 | 1842.5392 | 783.6768 | 780 | 200 | 1763.6768 | 44.09% | 95% | 0% | -170.4805 | 1672.0586 | -3550 | -400 | -2277.9414 | 56.95% | 43.91% | 95% | 0% | 2530 | -149
[5 empty] | 2019-10-07 | 17 | 6703.5 | 2442 | -162 | 1 | 0 | 2604 | 1958.4501 | 1958.4501 | 1958.4501 | 783.6768 | 780 | 200 | 1763.6768 | 44.09% | 95% | 0% | -185.3547 | 1773.0954 | -3550 | -400 | -2176.9046 | 54.42% | 43.91% | 95% | 0% | 2604 | -162
[5 empty] | 2019-10-07 | 18 | 6704 | 2416 | -181 | 1 | 0 | 2597 | 1947.4856 | 1947.4856 | 1947.4856 | 783.6768 | 780 | 200 | 1763.6768 | 44.09% | 95% | 0% | -207.0938 | 1740.3918 | -3550 | -400 | -2209.6082 | 55.24% | 43.9% | 95% | 0% | 2597 | -181
[5 empty] | 2019-10-07 | 19 | 6704.5 | 2411 | -205 | 1 | 0 | 2616 | 1977.2465 | 1977.2465 | 1977.2465 | 783.6768 | 780 | 200 | 1763.6768 | 44.09% | 95% | 0% | -234.5538 | 1742.6927 | -3550 | -400 | -2207.3073 | 55.18% | 43.9% | 95% | 0% | 2616 | -205
[5 empty] | 2019-10-07 | 20 | 6705 | 2403 | -225 | 1 | 0 | 2628 | 1996.0429 | 1996.0429 | 1996.0429 | 783.6768 | 780 | 200 | 1763.6768 | 44.09% | 95% | 0% | -257.4371 | 1738.6058 | -3550 | -400 | -2211.3942 | 55.28% | 43.9% | 95% | 0% | 2628 | -225
[5 empty] | 2019-10-07 | 21 | 6705.5 | 2384 | -244 | 1 | 0 | 2628 | 1996.0429 | 1996.0429 | 1996.0429 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -279.1762 | 1716.8667 | -3550 | -400 | -2233.1333 | 55.83% | 43.9% | 95% | 0% | 2628 | -244
[5 empty] | 2019-10-07 | 22 | 6706 | 2339 | -267 | 1 | 0 | 2606 | 1961.5829 | 1961.5829 | 1961.5829 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -305.492 | 1656.0909 | -3550 | -400 | -2293.9091 | 57.35% | 43.89% | 95% | 0% | 2606 | -267
[5 empty] | 2019-10-07 | 23 | 6706.5 | 2311 | -289 | 1 | 0 | 2600 | 1952.1847 | 1952.1847 | 1952.1847 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -330.6636 | 1621.5211 | -3550 | -400 | -2328.4789 | 58.21% | 43.88% | 95% | 0% | 2600 | -289
[5 empty] | 2019-10-07 | 24 | 6707 | 2272 | -330 | 1 | 0 | 2602 | 1955.3174 | 1955.3174 | 1955.3174 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -377.5744 | 1577.743 | -3550 | -400 | -2372.257 | 59.31% | 43.88% | 95% | 0% | 2602 | -330
[5 empty] | 2019-10-07 | 25 | 6707.5 | 2320 | -305 | 1 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -348.9703 | 1642.3735 | -3550 | -400 | -2307.6265 | 57.69% | 43.87% | 95% | 0% | 2625 | -305
[5 empty] | 2019-10-07 | 26 | 6708 | 2329 | -285 | 1 | 0 | 2614 | 1974.1138 | 1974.1138 | 1974.1138 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -326.087 | 1648.0268 | -3550 | -400 | -2301.9732 | 57.55% | 43.87% | 95% | 0% | 2614 | -285
[5 empty] | 2019-10-07 | 27 | 6708.5 | 2322 | -273 | 1 | 0 | 2595 | 1944.3528 | 1944.3528 | 1944.3528 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -312.357 | 1631.9959 | -3550 | -400 | -2318.0041 | 57.95% | 43.86% | 95% | 0% | 2595 | -273
[5 empty] | 2019-10-07 | 28 | 6709 | 2327 | -260 | 1 | 0 | 2587 | 1931.8219 | 1931.8219 | 1931.8219 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -297.4828 | 1634.3391 | -3550 | -400 | -2315.6609 | 57.89% | 43.86% | 95% | 0% | 2587 | -260
[5 empty] | 2019-10-07 | 29 | 6709.5 | 2351 | -250 | 1 | 0 | 2601 | 1953.751 | 1953.751 | 1953.751 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -286.0412 | 1667.7098 | -3550 | -400 | -2282.2902 | 57.06% | 43.85% | 95% | 0% | 2601 | -250
[5 empty] | 2019-10-07 | 30 | 6710 | 2331 | -250 | 1 | 0 | 2581 | 1922.4237 | 1922.4237 | 1922.4237 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -286.0412 | 1636.3826 | -3550 | -400 | -2313.6174 | 57.84% | 43.85% | 95% | 0% | 2581 | -250
[5 empty] | 2019-10-07 | 31 | 6710.5 | 2331 | -238 | 1 | 0 | 2569 | 1903.6274 | 1903.6274 | 1903.6274 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -272.3112 | 1631.3162 | -3550 | -400 | -2318.6838 | 57.97% | 43.83% | 95% | 0% | 2569 | -238
[5 empty] | 2019-10-07 | 32 | 6711 | 2409 | -222 | 1 | 0 | 2631 | 2000.742 | 2000.742 | 2000.742 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -254.0046 | 1746.7374 | -3550 | -400 | -2203.2626 | 55.08% | 43.83% | 95% | 0% | 2631 | -222
[5 empty] | 2019-10-07 | 33 | 6711.5 | 2499 | -209 | 1 | 0 | 2708 | 2121.352 | 2121.352 | 2121.352 | 782.1105 | 780 | 200 | 1762.1105 | 44.05% | 95% | 0% | -239.1304 | 1882.2216 | -3550 | -400 | -2067.7784 | 51.69% | 43.83% | 95% | 0% | 2708 | -209
[5 empty] | 2019-10-07 | 34 | 6712 | 2590 | -191 | 1 | 0 | 2781 | 2235.6966 | 2235.6966 | 2235.6966 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -218.5355 | 2017.1612 | -3550 | -400 | -1932.8388 | 48.32% | 43.83% | 95% | 0% | 2781 | -191
[5 empty] | 2019-10-07 | 35 | 6712.5 | 2638 | -176 | 1 | 0 | 2814 | 2287.3866 | 2287.3866 | 2287.3866 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -201.373 | 2086.0136 | -3550 | -400 | -1863.9864 | 46.6% | 43.82% | 95% | 0% | 2814 | -176
[5 empty] | 2019-10-07 | 36 | 6713 | 2685 | -160 | 1 | 0 | 2845 | 2335.9439 | 2335.9439 | 2335.9439 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -183.0664 | 2152.8776 | -3550 | -400 | -1797.1224 | 44.93% | 43.82% | 95% | 0% | 2845 | -160
[5 empty] | 2019-10-07 | 37 | 6713.5 | 2712 | -145 | 1 | 0 | 2857 | 2354.7403 | 2354.7403 | 2354.7403 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -165.9039 | 2188.8364 | -3550 | -400 | -1761.1636 | 44.03% | 43.82% | 95% | 0% | 2857 | -145
[5 empty] | 2019-10-07 | 38 | 6714 | 2738 | -140 | 1 | 0 | 2878 | 2387.634 | 2387.634 | 2387.634 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -160.1831 | 2227.4509 | -3550 | -400 | -1722.5491 | 43.06% | 43.81% | 95% | 0% | 2878 | -140
[5 empty] | 2019-10-07 | 39 | 6714.5 | 2764 | -140 | 0 | 0 | 2904 | 2428.3594 | 2428.3594 | 2428.3594 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -160.1831 | 2268.1764 | -2750 | -200 | -681.8236 | 17.05% | 43.8% | 95% | 0% | 2904 | -140
[5 empty] | 2019-10-07 | 40 | 6715 | 2687 | -140 | 0 | 0 | 2827 | 2307.7494 | 2307.7494 | 2307.7494 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -160.1831 | 2147.5663 | -2750 | -200 | -802.4337 | 20.06% | 43.79% | 95% | 0% | 2827 | -140
[5 empty] | 2019-10-07 | 41 | 6715.5 | 2560 | -141 | 0 | 0 | 2701 | 2110.3875 | 2110.3875 | 2110.3875 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -161.3272 | 1949.0602 | -2750 | -200 | -1000.9398 | 25.02% | 43.79% | 95% | 0% | 2701 | -141
[5 empty] | 2019-10-07 | 42 | 6716 | 2454 | -142 | 0 | 0 | 2596 | 1945.9192 | 1945.9192 | 1945.9192 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -162.4714 | 1783.4478 | -2750 | -200 | -1166.5522 | 29.16% | 43.79% | 95% | 0% | 2596 | -142
[5 empty] | 2019-10-07 | 43 | 6716.5 | 2324 | -144 | 0 | 0 | 2468 | 1745.4246 | 1745.4246 | 1745.4246 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -164.7597 | 1580.6648 | -2750 | -200 | -1369.3352 | 34.23% | 43.78% | 95% | 0% | 2468 | -144
[5 empty] | 2019-10-07 | 44 | 6717 | 2177 | -145 | 0 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -165.9039 | 1350.8315 | -2750 | -200 | -1599.1685 | 39.98% | 43.77% | 95% | 0% | 2322 | -145
[5 empty] | 2019-10-07 | 45 | 6717.5 | 2019 | -146 | 0 | 0 | 2165 | 1270.8162 | 1270.8162 | 1270.8162 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -167.0481 | 1103.7681 | -2750 | -200 | -1846.2319 | 46.16% | 43.77% | 95% | 0% | 2165 | -146
[5 empty] | 2019-10-07 | 46 | 6718 | 1882 | -147 | 0 | 0 | 2029 | 1057.7906 | 1057.7906 | 1057.7906 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -168.1922 | 889.5984 | -2750 | -200 | -2060.4016 | 51.51% | 43.76% | 95% | 0% | 2029 | -147
[5 empty] | 2019-10-07 | 47 | 6718.5 | 1717 | -147 | 0 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -168.1922 | 631.1483 | -2750 | -200 | -2318.8517 | 57.97% | 43.76% | 95% | 0% | 1864 | -147
[5 empty] | 2019-10-07 | 48 | 6719 | 1608 | -147 | 0 | 0 | 1755 | 628.6068 | 628.6068 | 628.6068 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -168.1922 | 460.4145 | -2750 | -200 | -2489.5855 | 62.24% | 43.75% | 95% | 0% | 1755 | -147
[5 empty] | 2019-10-08 | 1 | 6719.5 | 1537 | -145 | 0 | 0 | 1682 | 514.2622 | 514.2622 | 514.2622 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -165.9039 | 348.3583 | -2750 | -200 | -2601.6417 | 65.04% | 43.72% | 95% | 0% | 1682 | -145
[5 empty] | 2019-10-08 | 2 | 6720 | 1493 | -142 | 0 | 0 | 1635 | 440.643 | 440.643 | 440.643 | 780.5441 | 780 | 200 | 1760.5441 | 44.01% | 95% | 0% | -162.4714 | 278.1716 | -2750 | -200 | -2671.8284 | 66.8% | 43.71% | 95% | 0% | 1635 | -142
[5 empty] | 2019-10-08 | 3 | 6720.5 | 1462 | -144 | 0 | 0 | 1606 | 395.2185 | 395.2185 | 395.2185 | 778.9777 | 780 | 200 | 1758.9777 | 43.97% | 95% | 0% | -164.7597 | 230.4587 | -2750 | -200 | -2719.5413 | 67.99% | 43.7% | 95% | 0% | 1606 | -144
[5 empty] | 2019-10-08 | 4 | 6721 | 1471 | -145 | 0 | 0 | 1616 | 410.8821 | 410.8821 | 410.8821 | 778.9777 | 780 | 200 | 1758.9777 | 43.97% | 95% | 0% | -165.9039 | 244.9782 | -2750 | -200 | -2705.0218 | 67.63% | 43.7% | 95% | 0% | 1616 | -145
[5 empty] | 2019-10-08 | 5 | 6721.5 | 1445 | -146 | 0 | 0 | 1591 | 371.723 | 371.723 | 371.723 | 778.9777 | 780 | 200 | 1758.9777 | 43.97% | 95% | 0% | -167.0481 | 204.6749 | -2750 | -200 | -2745.3251 | 68.63% | 43.69% | 95% | 0% | 1591 | -146
[5 empty] | 2019-10-08 | 6 | 6722 | 1424 | -147 | 0 | 0 | 1571 | 340.3957 | 340.3957 | 340.3957 | 777.4114 | 780 | 200 | 1757.4114 | 43.94% | 95% | 0% | -168.1922 | 172.2035 | -2750 | -200 | -2777.7965 | 69.44% | 43.67% | 95% | 0% | 1571 | -147
[5 empty] | 2019-10-08 | 7 | 6722.5 | 1389 | -148 | 0 | 0 | 1537 | 287.1393 | 287.1393 | 287.1393 | 777.4114 | 780 | 200 | 1757.4114 | 43.94% | 95% | 0% | -169.3364 | 117.8029 | -2750 | -200 | -2832.1971 | 70.8% | 43.67% | 95% | 0% | 1537 | -148
[5 empty] | 2019-10-08 | 8 | 6723 | 1370 | -149 | 0 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 777.4114 | 780 | 200 | 1757.4114 | 43.94% | 95% | 0% | -170.4805 | 88.4642 | -2750 | -200 | -2861.5358 | 71.54% | 43.67% | 95% | 0% | 1519 | -149
[5 empty] | 2019-10-08 | 9 | 6723.5 | 1365 | -151 | 0 | 0 | 1516 | 254.2457 | 254.2457 | 254.2457 | 777.4114 | 780 | 200 | 1757.4114 | 43.94% | 95% | 0% | -172.7689 | 81.4768 | -2750 | -200 | -2868.5232 | 71.71% | 43.65% | 95% | 0% | 1516 | -151
[5 empty] | 2019-10-08 | 10 | 6724 | 1365 | -153 | 0 | 0 | 1518 | 257.3784 | 257.3784 | 257.3784 | 777.4114 | 780 | 200 | 1757.4114 | 43.94% | 95% | 0% | -175.0572 | 82.3212 | -2750 | -200 | -2867.6788 | 71.69% | 43.65% | 95% | 0% | 1518 | -153
[5 empty] | 2019-10-08 | 11 | 6724.5 | 1441 | -155 | 0 | 0 | 1596 | 379.5548 | 379.5548 | 379.5548 | 777.4114 | 780 | 200 | 1757.4114 | 43.94% | 95% | 0% | -177.3455 | 202.2093 | -2750 | -200 | -2747.7907 | 68.69% | 43.65% | 95% | 0% | 1596 | -155
[5 empty] | 2019-10-08 | 12 | 6725 | 1531 | -157 | 0 | 0 | 1688 | 523.6603 | 523.6603 | 523.6603 | 777.4114 | 780 | 200 | 1757.4114 | 43.94% | 95% | 0% | -179.6339 | 344.0265 | -2750 | -200 | -2605.9735 | 65.15% | 43.64% | 95% | 0% | 1688 | -157
[5 empty] | 2019-10-08 | 13 | 6725.5 | 1752 | -157 | 0 | 0 | 1909 | 869.8269 | 869.8269 | 869.8269 | 777.4114 | 780 | 200 | 1757.4114 | 43.94% | 95% | 0% | -179.6339 | 690.193 | -2750 | -200 | -2259.807 | 56.5% | 43.63% | 95% | 0% | 1909 | -157
[5 empty] | 2019-10-08 | 14 | 6726 | 1991 | -158 | 1 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 777.4114 | 780 | 200 | 1757.4114 | 43.94% | 95% | 0% | -180.778 | 1064.9763 | -3550 | -400 | -2885.0237 | 72.13% | 43.62% | 95% | 0% | 2149 | -158
[5 empty] | 2019-10-08 | 15 | 6726.5 | 2229 | -158 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 777.4114 | 780 | 200 | 1757.4114 | 43.94% | 95% | 0% | -180.778 | 1437.771 | -3550 | -400 | -2512.229 | 62.81% | 43.62% | 95% | 0% | 2387 | -158
[5 empty] | 2019-10-08 | 16 | 6727 | 2320 | -170 | 1 | 0 | 2490 | 1779.8846 | 1779.8846 | 1779.8846 | 775.845 | 780 | 200 | 1755.845 | 43.9% | 95% | 0% | -194.508 | 1585.3766 | -3550 | -400 | -2364.6234 | 59.12% | 43.62% | 95% | 0% | 2490 | -170
[5 empty] | 2019-10-08 | 17 | 6727.5 | 2315 | -207 | 1 | 0 | 2522 | 1830.0082 | 1830.0082 | 1830.0082 | 775.845 | 780 | 200 | 1755.845 | 43.9% | 95% | 0% | -236.8421 | 1593.1661 | -3550 | -400 | -2356.8339 | 58.92% | 43.62% | 95% | 0% | 2522 | -207
[5 empty] | 2019-10-08 | 18 | 6728 | 2220 | -259 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 775.845 | 780 | 200 | 1755.845 | 43.9% | 95% | 0% | -296.3387 | 1466.3159 | -3550 | -400 | -2483.6841 | 62.09% | 43.62% | 95% | 0% | 2479 | -259
[5 empty] | 2019-10-08 | 19 | 6728.5 | 2114 | -322 | 1 | 0 | 2436 | 1695.3009 | 1695.3009 | 1695.3009 | 775.845 | 780 | 200 | 1755.845 | 43.9% | 95% | 0% | -368.4211 | 1326.8799 | -3550 | -400 | -2623.1201 | 65.58% | 43.61% | 95% | 0% | 2436 | -322
[5 empty] | 2019-10-08 | 20 | 6729 | 2008 | -379 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 775.845 | 780 | 200 | 1755.845 | 43.9% | 95% | 0% | -433.6384 | 1184.9106 | -3550 | -400 | -2765.0894 | 69.13% | 43.61% | 95% | 0% | 2387 | -379
[5 empty] | 2019-10-08 | 21 | 6729.5 | 1930 | -424 | 1 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 775.845 | 780 | 200 | 1755.845 | 43.9% | 95% | 0% | -485.1259 | 1081.7332 | -3550 | -400 | -2868.2668 | 71.71% | 43.61% | 95% | 0% | 2354 | -424
[5 empty] | 2019-10-08 | 22 | 6730 | 1902 | -439 | 1 | 0 | 2341 | 1546.4963 | 1546.4963 | 1546.4963 | 774.2786 | 780 | 200 | 1754.2786 | 43.86% | 95% | 0% | -502.2883 | 1044.208 | -3550 | -400 | -2905.792 | 72.64% | 43.6% | 95% | 0% | 2341 | -439
[5 empty] | 2019-10-08 | 23 | 6730.5 | 1889 | -445 | 1 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 774.2786 | 780 | 200 | 1754.2786 | 43.86% | 95% | 0% | -509.1533 | 1026.3784 | -3550 | -400 | -2923.6216 | 73.09% | 43.6% | 95% | 0% | 2334 | -445
[5 empty] | 2019-10-08 | 24 | 6731 | 1864 | -467 | 1 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 774.2786 | 780 | 200 | 1754.2786 | 43.86% | 95% | 0% | -534.3249 | 996.5077 | -3550 | -400 | -2953.4923 | 73.84% | 43.59% | 95% | 0% | 2331 | -467
[5 empty] | 2019-10-08 | 25 | 6731.5 | 1824 | -490 | 1 | 0 | 2314 | 1504.2045 | 1504.2045 | 1504.2045 | 774.2786 | 780 | 200 | 1754.2786 | 43.86% | 95% | 0% | -560.6407 | 943.5637 | -3550 | -400 | -3006.4363 | 75.16% | 43.59% | 95% | 0% | 2314 | -490
[5 empty] | 2019-10-08 | 26 | 6732 | 1766 | -498 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 774.2786 | 780 | 200 | 1754.2786 | 43.86% | 95% | 0% | -569.7941 | 856.0922 | -3550 | -400 | -3093.9078 | 77.35% | 43.58% | 95% | 0% | 2264 | -498
[5 empty] | 2019-10-08 | 27 | 6732.5 | 1734 | -510 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 774.2786 | 780 | 200 | 1754.2786 | 43.86% | 95% | 0% | -583.524 | 811.0349 | -3550 | -400 | -3138.9651 | 78.47% | 43.58% | 95% | 0% | 2244 | -510
[5 empty] | 2019-10-08 | 28 | 6733 | 1684 | -528 | 1 | 0 | 2212 | 1344.4353 | 1344.4353 | 1344.4353 | 774.2786 | 780 | 200 | 1754.2786 | 43.86% | 95% | 0% | -604.119 | 740.3163 | -3550 | -400 | -3209.6837 | 80.24% | 43.57% | 95% | 0% | 2212 | -528
[5 empty] | 2019-10-08 | 29 | 6733.5 | 1674 | -535 | 1 | 0 | 2209 | 1339.7362 | 1339.7362 | 1339.7362 | 774.2786 | 780 | 200 | 1754.2786 | 43.86% | 95% | 0% | -612.1281 | 727.608 | -3550 | -400 | -3222.392 | 80.56% | 43.57% | 95% | 0% | 2209 | -535
[5 empty] | 2019-10-08 | 30 | 6734 | 1679 | -513 | 1 | 0 | 2192 | 1313.108 | 1313.108 | 1313.108 | 774.2786 | 780 | 200 | 1754.2786 | 43.86% | 95% | 0% | -586.9565 | 726.1515 | -3550 | -400 | -3223.8485 | 80.6% | 43.57% | 95% | 0% | 2192 | -513
[5 empty] | 2019-10-08 | 31 | 6734.5 | 1728 | -468 | 1 | 0 | 2196 | 1319.3735 | 1319.3735 | 1319.3735 | 774.2786 | 780 | 200 | 1754.2786 | 43.86% | 95% | 0% | -535.4691 | 783.9043 | -3550 | -400 | -3166.0957 | 79.15% | 43.57% | 95% | 0% | 2196 | -468
[5 empty] | 2019-10-08 | 32 | 6735 | 1843 | -420 | 1 | 0 | 2263 | 1424.3199 | 1424.3199 | 1424.3199 | 772.7123 | 780 | 200 | 1752.7123 | 43.82% | 95% | 0% | -480.5492 | 943.7707 | -3550 | -400 | -3006.2293 | 75.16% | 43.57% | 95% | 0% | 2263 | -420
[5 empty] | 2019-10-08 | 33 | 6735.5 | 1970 | -384 | 1 | 0 | 2354 | 1566.859 | 1566.859 | 1566.859 | 772.7123 | 780 | 200 | 1752.7123 | 43.82% | 95% | 0% | -439.3593 | 1127.4998 | -3550 | -400 | -2822.5002 | 70.56% | 43.55% | 95% | 0% | 2354 | -384
[5 empty] | 2019-10-08 | 34 | 6736 | 2105 | -335 | 1 | 0 | 2440 | 1701.5664 | 1701.5664 | 1701.5664 | 772.7123 | 780 | 200 | 1752.7123 | 43.82% | 95% | 0% | -383.2952 | 1318.2712 | -3550 | -400 | -2631.7288 | 65.79% | 43.55% | 95% | 0% | 2440 | -335
[5 empty] | 2019-10-08 | 35 | 6736.5 | 2272 | -281 | 1 | 0 | 2553 | 1878.5655 | 1878.5655 | 1878.5655 | 772.7123 | 780 | 200 | 1752.7123 | 43.82% | 95% | 0% | -321.5103 | 1557.0552 | -3550 | -400 | -2392.9448 | 59.82% | 43.54% | 95% | 0% | 2553 | -281
[5 empty] | 2019-10-08 | 36 | 6737 | 2394 | -229 | 1 | 0 | 2623 | 1988.211 | 1988.211 | 1988.211 | 772.7123 | 780 | 200 | 1752.7123 | 43.82% | 95% | 0% | -262.0137 | 1726.1973 | -3550 | -400 | -2223.8027 | 55.6% | 43.54% | 95% | 0% | 2623 | -229
[5 empty] | 2019-10-08 | 37 | 6737.5 | 2468 | -195 | 1 | 0 | 2663 | 2050.8656 | 2050.8656 | 2050.8656 | 772.7123 | 780 | 200 | 1752.7123 | 43.82% | 95% | 0% | -223.1121 | 1827.7535 | -3550 | -400 | -2122.2465 | 53.06% | 43.53% | 95% | 0% | 2663 | -195
[5 empty] | 2019-10-08 | 38 | 6738 | 2561 | -187 | 1 | 0 | 2748 | 2184.0066 | 2184.0066 | 2184.0066 | 772.7123 | 780 | 200 | 1752.7123 | 43.82% | 95% | 0% | -213.9588 | 1970.0478 | -3550 | -400 | -1979.9522 | 49.5% | 43.53% | 95% | 0% | 2748 | -187
[5 empty] | 2019-10-08 | 39 | 6738.5 | 2616 | -185 | 1 | 0 | 2801 | 2267.0239 | 2267.0239 | 2267.0239 | 772.7123 | 780 | 200 | 1752.7123 | 43.82% | 95% | 0% | -211.6705 | 2055.3534 | -3550 | -400 | -1894.6466 | 47.37% | 43.52% | 95% | 0% | 2801 | -185
[5 empty] | 2019-10-08 | 40 | 6739 | 2546 | -184 | 0 | 0 | 2730 | 2155.812 | 2155.812 | 2155.812 | 771.1459 | 780 | 200 | 1751.1459 | 43.78% | 95% | 0% | -210.5263 | 1945.2857 | -2750 | -200 | -1004.7143 | 25.12% | 43.52% | 95% | 0% | 2730 | -184
[5 empty] | 2019-10-08 | 41 | 6739.5 | 2447 | -184 | 0 | 0 | 2631 | 2000.742 | 2000.742 | 2000.742 | 771.1459 | 780 | 200 | 1751.1459 | 43.78% | 95% | 0% | -210.5263 | 1790.2156 | -2750 | -200 | -1159.7844 | 28.99% | 43.51% | 95% | 0% | 2631 | -184
[5 empty] | 2019-10-08 | 42 | 6740 | 2344 | -184 | 0 | 0 | 2528 | 1839.4064 | 1839.4064 | 1839.4064 | 771.1459 | 780 | 200 | 1751.1459 | 43.78% | 95% | 0% | -210.5263 | 1628.8801 | -2750 | -200 | -1321.1199 | 33.03% | 43.5% | 95% | 0% | 2528 | -184
[5 empty] | 2019-10-08 | 43 | 6740.5 | 2227 | -183 | 0 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 771.1459 | 780 | 200 | 1751.1459 | 43.78% | 95% | 0% | -209.3822 | 1445.1933 | -2750 | -200 | -1504.8067 | 37.62% | 43.5% | 95% | 0% | 2410 | -183
[5 empty] | 2019-10-08 | 44 | 6741 | 2085 | -182 | 0 | 0 | 2267 | 1430.5853 | 1430.5853 | 1430.5853 | 771.1459 | 780 | 200 | 1751.1459 | 43.78% | 95% | 0% | -208.238 | 1222.3473 | -2750 | -200 | -1727.6527 | 43.19% | 43.5% | 95% | 0% | 2267 | -182
[5 empty] | 2019-10-08 | 45 | 6741.5 | 1932 | -181 | 0 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 771.1459 | 780 | 200 | 1751.1459 | 43.78% | 95% | 0% | -207.0938 | 982.2714 | -2750 | -200 | -1967.7286 | 49.19% | 43.5% | 95% | 0% | 2113 | -181
[5 empty] | 2019-10-08 | 46 | 6742 | 1786 | -181 | 0 | 0 | 1967 | 960.676 | 960.676 | 960.676 | 771.1459 | 780 | 200 | 1751.1459 | 43.78% | 95% | 0% | -207.0938 | 753.5822 | -2750 | -200 | -2196.4178 | 54.91% | 43.49% | 95% | 0% | 1967 | -181
[5 empty] | 2019-10-08 | 47 | 6742.5 | 1637 | -180 | 0 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 771.1459 | 780 | 200 | 1751.1459 | 43.78% | 95% | 0% | -205.9497 | 519.7717 | -2750 | -200 | -2430.2283 | 60.76% | 43.49% | 95% | 0% | 1817 | -180
[5 empty] | 2019-10-08 | 48 | 6743 | 1522 | -178 | 0 | 0 | 1700 | 542.4567 | 542.4567 | 542.4567 | 771.1459 | 780 | 200 | 1751.1459 | 43.78% | 95% | 0% | -203.6613 | 338.7954 | -2750 | -200 | -2611.2046 | 65.28% | 43.47% | 95% | 0% | 1700 | -178
[5 empty] | 2019-10-09 | 1 | 6743.5 | 1438 | -176 | 0 | 0 | 1614 | 407.7494 | 407.7494 | 407.7494 | 771.1459 | 780 | 200 | 1751.1459 | 43.78% | 95% | 0% | -201.373 | 206.3764 | -2750 | -200 | -2743.6236 | 68.59% | 43.46% | 95% | 0% | 1614 | -176
[5 empty] | 2019-10-09 | 2 | 6744 | 1398 | -173 | 0 | 0 | 1571 | 340.3957 | 340.3957 | 340.3957 | 769.5796 | 780 | 200 | 1749.5796 | 43.74% | 95% | 0% | -197.9405 | 142.4552 | -2750 | -200 | -2807.5448 | 70.19% | 43.46% | 95% | 0% | 1571 | -173
[5 empty] | 2019-10-09 | 3 | 6744.5 | 1385 | -172 | 0 | 0 | 1557 | 318.4666 | 318.4666 | 318.4666 | 769.5796 | 780 | 200 | 1749.5796 | 43.74% | 95% | 0% | -196.7963 | 121.6703 | -2750 | -200 | -2828.3297 | 70.71% | 43.45% | 95% | 0% | 1557 | -172
[5 empty] | 2019-10-09 | 4 | 6745 | 1408 | -171 | 0 | 0 | 1579 | 352.9266 | 352.9266 | 352.9266 | 769.5796 | 780 | 200 | 1749.5796 | 43.74% | 95% | 0% | -195.6522 | 157.2745 | -2750 | -200 | -2792.7255 | 69.82% | 43.45% | 95% | 0% | 1579 | -171
[5 empty] | 2019-10-09 | 5 | 6745.5 | 1410 | -169 | 0 | 0 | 1579 | 352.9266 | 352.9266 | 352.9266 | 769.5796 | 780 | 200 | 1749.5796 | 43.74% | 95% | 0% | -193.3638 | 159.5628 | -2750 | -200 | -2790.4372 | 69.76% | 43.45% | 95% | 0% | 1579 | -169
[5 empty] | 2019-10-09 | 6 | 6746 | 1397 | -167 | 0 | 0 | 1564 | 329.4312 | 329.4312 | 329.4312 | 769.5796 | 780 | 200 | 1749.5796 | 43.74% | 95% | 0% | -191.0755 | 138.3556 | -2750 | -200 | -2811.6444 | 70.29% | 43.45% | 95% | 0% | 1564 | -167
[5 empty] | 2019-10-09 | 7 | 6746.5 | 1379 | -166 | 0 | 0 | 1545 | 299.6702 | 299.6702 | 299.6702 | 769.5796 | 780 | 200 | 1749.5796 | 43.74% | 95% | 0% | -189.9314 | 109.7389 | -2750 | -200 | -2840.2611 | 71.01% | 43.45% | 95% | 0% | 1545 | -166
[5 empty] | 2019-10-09 | 8 | 6747 | 1372 | -165 | 0 | 0 | 1537 | 287.1393 | 287.1393 | 287.1393 | 769.5796 | 780 | 200 | 1749.5796 | 43.74% | 95% | 0% | -188.7872 | 98.3521 | -2750 | -200 | -2851.6479 | 71.29% | 43.45% | 95% | 0% | 1537 | -165
[5 empty] | 2019-10-09 | 9 | 6747.5 | 1379 | -162 | 0 | 0 | 1541 | 293.4048 | 293.4048 | 293.4048 | 769.5796 | 780 | 200 | 1749.5796 | 43.74% | 95% | 0% | -185.3547 | 108.0501 | -2750 | -200 | -2841.9499 | 71.05% | 43.43% | 95% | 0% | 1541 | -162
[5 empty] | 2019-10-09 | 10 | 6748 | 1386 | -158 | 0 | 0 | 1544 | 298.1039 | 298.1039 | 298.1039 | 769.5796 | 780 | 200 | 1749.5796 | 43.74% | 95% | 0% | -180.778 | 117.3258 | -2750 | -200 | -2832.6742 | 70.82% | 43.43% | 95% | 0% | 1544 | -158
[5 empty] | 2019-10-09 | 11 | 6748.5 | 1465 | -158 | 0 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 768.0132 | 780 | 200 | 1748.0132 | 43.7% | 95% | 0% | -180.778 | 241.0686 | -2750 | -200 | -2708.9314 | 67.72% | 43.43% | 95% | 0% | 1623 | -158
[5 empty] | 2019-10-09 | 12 | 6749 | 1564 | -157 | 0 | 0 | 1721 | 575.3504 | 575.3504 | 575.3504 | 768.0132 | 780 | 200 | 1748.0132 | 43.7% | 95% | 0% | -179.6339 | 395.7165 | -2750 | -200 | -2554.2835 | 63.86% | 43.42% | 95% | 0% | 1721 | -157
[5 empty] | 2019-10-09 | 13 | 6749.5 | 1783 | -156 | 0 | 0 | 1939 | 916.8178 | 916.8178 | 916.8178 | 768.0132 | 780 | 200 | 1748.0132 | 43.7% | 95% | 0% | -178.4897 | 738.3281 | -2750 | -200 | -2211.6719 | 55.29% | 43.42% | 95% | 0% | 1939 | -156
[5 empty] | 2019-10-09 | 14 | 6750 | 2016 | -155 | 0 | 0 | 2171 | 1280.2143 | 1280.2143 | 1280.2143 | 768.0132 | 780 | 200 | 1748.0132 | 43.7% | 95% | 0% | -177.3455 | 1102.8688 | -2750 | -200 | -1847.1312 | 46.18% | 43.42% | 95% | 0% | 2171 | -155
[5 empty] | 2019-10-09 | 15 | 6750.5 | 2267 | -155 | 0 | 0 | 2422 | 1673.3718 | 1673.3718 | 1673.3718 | 768.0132 | 780 | 200 | 1748.0132 | 43.7% | 95% | 0% | -177.3455 | 1496.0263 | -2750 | -200 | -1453.9737 | 36.35% | 43.41% | 95% | 0% | 2422 | -155
[5 empty] | 2019-10-09 | 16 | 6751 | 2390 | -159 | 0 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 768.0132 | 780 | 200 | 1748.0132 | 43.7% | 95% | 0% | -181.9222 | 1690.3779 | -2750 | -200 | -1259.6221 | 31.49% | 43.41% | 95% | 0% | 2549 | -159
[5 empty] | 2019-10-09 | 17 | 6751.5 | 2399 | -181 | 0 | 0 | 2580 | 1920.8574 | 1920.8574 | 1920.8574 | 768.0132 | 780 | 200 | 1748.0132 | 43.7% | 95% | 0% | -207.0938 | 1713.7636 | -2750 | -200 | -1236.2364 | 30.91% | 43.41% | 95% | 0% | 2580 | -181
[5 empty] | 2019-10-09 | 18 | 6752 | 2331 | -222 | 1 | 0 | 2553 | 1878.5655 | 1878.5655 | 1878.5655 | 768.0132 | 780 | 200 | 1748.0132 | 43.7% | 95% | 0% | -254.0046 | 1624.561 | -3550 | -400 | -2325.439 | 58.14% | 43.4% | 95% | 0% | 2553 | -222
[5 empty] | 2019-10-09 | 19 | 6752.5 | 2264 | -280 | 1 | 0 | 2544 | 1864.4683 | 1864.4683 | 1864.4683 | 768.0132 | 780 | 200 | 1748.0132 | 43.7% | 95% | 0% | -320.3661 | 1544.1021 | -3550 | -400 | -2405.8979 | 60.15% | 43.4% | 95% | 0% | 2544 | -280
[5 empty] | 2019-10-09 | 20 | 6753 | 2145 | -346 | 1 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 768.0132 | 780 | 200 | 1748.0132 | 43.7% | 95% | 0% | -395.881 | 1385.5699 | -3550 | -400 | -2564.4301 | 64.11% | 43.39% | 95% | 0% | 2491 | -346
[5 empty] | 2019-10-09 | 21 | 6753.5 | 2028 | -405 | 1 | 0 | 2433 | 1690.6018 | 1690.6018 | 1690.6018 | 768.0132 | 780 | 200 | 1748.0132 | 43.7% | 95% | 0% | -463.3867 | 1227.2151 | -3550 | -400 | -2722.7849 | 68.07% | 43.38% | 95% | 0% | 2433 | -405
[5 empty] | 2019-10-09 | 22 | 6754 | 1926 | -454 | 1 | 0 | 2380 | 1607.5845 | 1607.5845 | 1607.5845 | 768.0132 | 780 | 200 | 1748.0132 | 43.7% | 95% | 0% | -519.4508 | 1088.1337 | -3550 | -400 | -2861.8663 | 71.55% | 43.37% | 95% | 0% | 2380 | -454
[5 empty] | 2019-10-09 | 23 | 6754.5 | 1812 | -504 | 1 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 766.4468 | 780 | 200 | 1746.4468 | 43.66% | 95% | 0% | -576.659 | 930.6781 | -3550 | -400 | -3019.3219 | 75.48% | 43.37% | 95% | 0% | 2316 | -504
[5 empty] | 2019-10-09 | 24 | 6755 | 1771 | -526 | 1 | 0 | 2297 | 1477.5763 | 1477.5763 | 1477.5763 | 766.4468 | 780 | 200 | 1746.4468 | 43.66% | 95% | 0% | -601.8307 | 875.7456 | -3550 | -400 | -3074.2544 | 76.86% | 43.36% | 95% | 0% | 2297 | -526
[5 empty] | 2019-10-09 | 25 | 6755.5 | 1744 | -549 | 1 | 0 | 2293 | 1471.3108 | 1471.3108 | 1471.3108 | 766.4468 | 780 | 200 | 1746.4468 | 43.66% | 95% | 0% | -628.1465 | 843.1643 | -3550 | -400 | -3106.8357 | 77.67% | 43.36% | 95% | 0% | 2293 | -549
[5 empty] | 2019-10-09 | 26 | 6756 | 1732 | -538 | 1 | 0 | 2270 | 1435.2844 | 1435.2844 | 1435.2844 | 766.4468 | 780 | 200 | 1746.4468 | 43.66% | 95% | 0% | -615.5606 | 819.7238 | -3550 | -400 | -3130.2762 | 78.26% | 43.36% | 95% | 0% | 2270 | -538
[5 empty] | 2019-10-09 | 27 | 6756.5 | 1734 | -536 | 1 | 0 | 2270 | 1435.2844 | 1435.2844 | 1435.2844 | 766.4468 | 780 | 200 | 1746.4468 | 43.66% | 95% | 0% | -613.2723 | 822.0121 | -3550 | -400 | -3127.9879 | 78.2% | 43.36% | 95% | 0% | 2270 | -536
[5 empty] | 2019-10-09 | 28 | 6757 | 1732 | -523 | 1 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 766.4468 | 780 | 200 | 1746.4468 | 43.66% | 95% | 0% | -598.3982 | 813.3908 | -3550 | -400 | -3136.6092 | 78.42% | 43.35% | 95% | 0% | 2255 | -523
[5 empty] | 2019-10-09 | 29 | 6757.5 | 1768 | -486 | 1 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 766.4468 | 780 | 200 | 1746.4468 | 43.66% | 95% | 0% | -556.0641 | 854.1585 | -3550 | -400 | -3095.8415 | 77.4% | 43.34% | 95% | 0% | 2254 | -486
[5 empty] | 2019-10-09 | 30 | 6758 | 1826 | -448 | 1 | 0 | 2274 | 1441.5499 | 1441.5499 | 1441.5499 | 766.4468 | 780 | 200 | 1746.4468 | 43.66% | 95% | 0% | -512.5858 | 928.9641 | -3550 | -400 | -3021.0359 | 75.53% | 43.34% | 95% | 0% | 2274 | -448
[5 empty] | 2019-10-09 | 31 | 6758.5 | 1882 | -408 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 766.4468 | 780 | 200 | 1746.4468 | 43.66% | 95% | 0% | -466.8192 | 999.7925 | -3550 | -400 | -2950.2075 | 73.76% | 43.34% | 95% | 0% | 2290 | -408
[5 empty] | 2019-10-09 | 32 | 6759 | 1995 | -375 | 1 | 0 | 2370 | 1591.9209 | 1591.9209 | 1591.9209 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -429.0618 | 1162.8591 | -3550 | -400 | -2787.1409 | 69.68% | 43.34% | 95% | 0% | 2370 | -375
[5 empty] | 2019-10-09 | 33 | 6759.5 | 2137 | -320 | 1 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -366.1327 | 1362.0618 | -3550 | -400 | -2587.9382 | 64.7% | 43.33% | 95% | 0% | 2457 | -320
[5 empty] | 2019-10-09 | 34 | 6760 | 2273 | -274 | 1 | 0 | 2547 | 1869.1674 | 1869.1674 | 1869.1674 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -313.5011 | 1555.6662 | -3550 | -400 | -2394.3338 | 59.86% | 43.33% | 95% | 0% | 2547 | -274
[5 empty] | 2019-10-09 | 35 | 6760.5 | 2407 | -234 | 1 | 0 | 2641 | 2016.4056 | 2016.4056 | 2016.4056 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -267.7346 | 1748.6711 | -3550 | -400 | -2201.3289 | 55.03% | 43.33% | 95% | 0% | 2641 | -234
[5 empty] | 2019-10-09 | 36 | 6761 | 2521 | -195 | 1 | 0 | 2716 | 2133.8829 | 2133.8829 | 2133.8829 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -223.1121 | 1910.7708 | -3550 | -400 | -2039.2292 | 50.98% | 43.32% | 95% | 0% | 2716 | -195
[5 empty] | 2019-10-09 | 37 | 6761.5 | 2627 | -173 | 1 | 0 | 2800 | 2265.4575 | 2265.4575 | 2265.4575 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -197.9405 | 2067.517 | -3550 | -400 | -1882.483 | 47.06% | 43.32% | 95% | 0% | 2800 | -173
[5 empty] | 2019-10-09 | 38 | 6762 | 2719 | -166 | 1 | 0 | 2885 | 2398.5985 | 2398.5985 | 2398.5985 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -189.9314 | 2208.6672 | -3550 | -400 | -1741.3328 | 43.53% | 43.31% | 95% | 0% | 2885 | -166
[5 empty] | 2019-10-09 | 39 | 6762.5 | 2726 | -166 | 0 | 0 | 2892 | 2409.5631 | 2409.5631 | 2409.5631 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -189.9314 | 2219.6317 | -2750 | -200 | -730.3683 | 18.26% | 43.31% | 95% | 0% | 2892 | -166
[5 empty] | 2019-10-09 | 40 | 6763 | 2651 | -166 | 0 | 0 | 2817 | 2292.0857 | 2292.0857 | 2292.0857 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -189.9314 | 2102.1544 | -2750 | -200 | -847.8456 | 21.2% | 43.29% | 95% | 0% | 2817 | -166
[5 empty] | 2019-10-09 | 41 | 6763.5 | 2556 | -167 | 0 | 0 | 2723 | 2144.8475 | 2144.8475 | 2144.8475 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -191.0755 | 1953.772 | -2750 | -200 | -996.228 | 24.91% | 43.29% | 95% | 0% | 2723 | -167
[5 empty] | 2019-10-09 | 42 | 6764 | 2447 | -168 | 0 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -192.2197 | 1783.4605 | -2750 | -200 | -1166.5395 | 29.16% | 43.29% | 95% | 0% | 2615 | -168
[5 empty] | 2019-10-09 | 43 | 6764.5 | 2321 | -168 | 0 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -192.2197 | 1586.0985 | -2750 | -200 | -1363.9015 | 34.1% | 43.29% | 95% | 0% | 2489 | -168
[5 empty] | 2019-10-09 | 44 | 6765 | 2166 | -169 | 0 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -193.3638 | 1343.7343 | -2750 | -200 | -1606.2657 | 40.16% | 43.29% | 95% | 0% | 2335 | -169
[5 empty] | 2019-10-09 | 45 | 6765.5 | 1997 | -171 | 0 | 0 | 2168 | 1275.5153 | 1275.5153 | 1275.5153 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -195.6522 | 1079.8631 | -2750 | -200 | -1870.1369 | 46.75% | 43.28% | 95% | 0% | 2168 | -171
[5 empty] | 2019-10-09 | 46 | 6766 | 1854 | -172 | 0 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 764.8805 | 780 | 200 | 1744.8805 | 43.62% | 95% | 0% | -196.7963 | 856.2952 | -2750 | -200 | -2093.7048 | 52.34% | 43.27% | 95% | 0% | 2026 | -172
[5 empty] | 2019-10-09 | 47 | 6766.5 | 1696 | -173 | 0 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -197.9405 | 609.2318 | -2750 | -200 | -2340.7682 | 58.52% | 43.25% | 95% | 0% | 1869 | -173
[5 empty] | 2019-10-09 | 48 | 6767 | 1573 | -174 | 0 | 0 | 1747 | 616.0758 | 616.0758 | 616.0758 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -199.0847 | 416.9912 | -2750 | -200 | -2533.0088 | 63.33% | 43.23% | 95% | 0% | 1747 | -174
[5 empty] | 2019-10-10 | 1 | 6767.5 | 1477 | -174 | 0 | 0 | 1651 | 465.7049 | 465.7049 | 465.7049 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -199.0847 | 266.6202 | -2750 | -200 | -2683.3798 | 67.08% | 43.23% | 95% | 0% | 1651 | -174
[5 empty] | 2019-10-10 | 2 | 6768 | 1425 | -173 | 0 | 0 | 1598 | 382.6876 | 382.6876 | 382.6876 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -197.9405 | 184.747 | -2750 | -200 | -2765.253 | 69.13% | 43.23% | 95% | 0% | 1598 | -173
[5 empty] | 2019-10-10 | 3 | 6768.5 | 1410 | -174 | 0 | 0 | 1584 | 360.7585 | 360.7585 | 360.7585 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -199.0847 | 161.6738 | -2750 | -200 | -2788.3262 | 69.71% | 43.22% | 95% | 0% | 1584 | -174
[5 empty] | 2019-10-10 | 4 | 6769 | 1425 | -175 | 0 | 0 | 1600 | 385.8203 | 385.8203 | 385.8203 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -200.2288 | 185.5914 | -2750 | -200 | -2764.4086 | 69.11% | 43.22% | 95% | 0% | 1600 | -175
[5 empty] | 2019-10-10 | 5 | 6769.5 | 1408 | -176 | 0 | 0 | 1584 | 360.7585 | 360.7585 | 360.7585 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -201.373 | 159.3855 | -2750 | -200 | -2790.6145 | 69.77% | 43.22% | 95% | 0% | 1584 | -176
[5 empty] | 2019-10-10 | 6 | 6770 | 1384 | -176 | 0 | 0 | 1560 | 323.1657 | 323.1657 | 323.1657 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -201.373 | 121.7927 | -2750 | -200 | -2828.2073 | 70.71% | 43.21% | 95% | 0% | 1560 | -176
[5 empty] | 2019-10-10 | 7 | 6770.5 | 1357 | -177 | 0 | 0 | 1534 | 282.4402 | 282.4402 | 282.4402 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -202.5172 | 79.9231 | -2750 | -200 | -2870.0769 | 71.75% | 43.21% | 95% | 0% | 1534 | -177
[5 empty] | 2019-10-10 | 8 | 6771 | 1337 | -177 | 0 | 0 | 1514 | 251.1129 | 251.1129 | 251.1129 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -202.5172 | 48.5958 | -2750 | -200 | -2901.4042 | 72.54% | 43.21% | 95% | 0% | 1514 | -177
[5 empty] | 2019-10-10 | 9 | 6771.5 | 1335 | -175 | 0 | 0 | 1510 | 244.8475 | 244.8475 | 244.8475 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -200.2288 | 44.6187 | -2750 | -200 | -2905.3813 | 72.63% | 43.19% | 95% | 0% | 1510 | -175
[5 empty] | 2019-10-10 | 10 | 6772 | 1347 | -172 | 0 | 0 | 1519 | 258.9448 | 258.9448 | 258.9448 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -196.7963 | 62.1484 | -2750 | -200 | -2887.8516 | 72.2% | 43.19% | 95% | 0% | 1519 | -172
[5 empty] | 2019-10-10 | 11 | 6772.5 | 1414 | -172 | 0 | 0 | 1586 | 363.8912 | 363.8912 | 363.8912 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -196.7963 | 167.0948 | -2750 | -200 | -2782.9052 | 69.57% | 43.19% | 95% | 0% | 1586 | -172
[5 empty] | 2019-10-10 | 12 | 6773 | 1512 | -171 | 1 | 0 | 1683 | 515.8285 | 515.8285 | 515.8285 | 763.3141 | 780 | 200 | 1743.3141 | 43.58% | 95% | 0% | -195.6522 | 320.1764 | -3550 | -400 | -3629.8236 | 90.75% | 43.19% | 95% | 0% | 1683 | -171
[5 empty] | 2019-10-10 | 13 | 6773.5 | 1739 | -168 | 1 | 0 | 1907 | 866.6941 | 866.6941 | 866.6941 | 761.7477 | 780 | 200 | 1741.7477 | 43.54% | 95% | 0% | -192.2197 | 674.4745 | -3550 | -400 | -3275.5255 | 81.89% | 43.17% | 95% | 0% | 1907 | -168
[5 empty] | 2019-10-10 | 14 | 6774 | 1992 | -165 | 1 | 0 | 2157 | 1258.2852 | 1258.2852 | 1258.2852 | 761.7477 | 780 | 200 | 1741.7477 | 43.54% | 95% | 0% | -188.7872 | 1069.4981 | -3550 | -400 | -2880.5019 | 72.01% | 43.17% | 95% | 0% | 2157 | -165
[5 empty] | 2019-10-10 | 15 | 6774.5 | 2242 | -165 | 1 | 0 | 2407 | 1649.8763 | 1649.8763 | 1649.8763 | 761.7477 | 780 | 200 | 1741.7477 | 43.54% | 95% | 0% | -188.7872 | 1461.0892 | -3550 | -400 | -2488.9108 | 62.22% | 43.17% | 95% | 0% | 2407 | -165
[5 empty] | 2019-10-10 | 16 | 6775 | 2338 | -176 | 1 | 0 | 2514 | 1817.4773 | 1817.4773 | 1817.4773 | 761.7477 | 780 | 200 | 1741.7477 | 43.54% | 95% | 0% | -201.373 | 1616.1043 | -3550 | -400 | -2333.8957 | 58.35% | 43.17% | 95% | 0% | 2514 | -176
[5 empty] | 2019-10-10 | 17 | 6775.5 | 2339 | -220 | 1 | 0 | 2559 | 1887.9637 | 1887.9637 | 1887.9637 | 761.7477 | 780 | 200 | 1741.7477 | 43.54% | 95% | 0% | -251.7162 | 1636.2475 | -3550 | -400 | -2313.7525 | 57.84% | 43.17% | 95% | 0% | 2559 | -220
[5 empty] | 2019-10-10 | 18 | 6776 | 2220 | -276 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 761.7477 | 780 | 200 | 1741.7477 | 43.54% | 95% | 0% | -315.7895 | 1473.4933 | -3550 | -400 | -2476.5067 | 61.91% | 43.17% | 95% | 0% | 2496 | -276
[5 empty] | 2019-10-10 | 19 | 6776.5 | 2121 | -336 | 1 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 761.7477 | 780 | 200 | 1741.7477 | 43.54% | 95% | 0% | -384.4394 | 1343.7552 | -3550 | -400 | -2606.2448 | 65.16% | 43.15% | 95% | 0% | 2457 | -336
[5 empty] | 2019-10-10 | 20 | 6777 | 2018 | -394 | 1 | 0 | 2412 | 1657.7082 | 1657.7082 | 1657.7082 | 761.7477 | 780 | 200 | 1741.7477 | 43.54% | 95% | 0% | -450.8009 | 1206.9072 | -3550 | -400 | -2743.0928 | 68.58% | 43.14% | 95% | 0% | 2412 | -394
[5 empty] | 2019-10-10 | 21 | 6777.5 | 1919 | -436 | 1 | 0 | 2355 | 1568.4254 | 1568.4254 | 1568.4254 | 761.7477 | 780 | 200 | 1741.7477 | 43.54% | 95% | 0% | -498.8558 | 1069.5696 | -3550 | -400 | -2880.4304 | 72.01% | 43.13% | 95% | 0% | 2355 | -436
[5 empty] | 2019-10-10 | 22 | 6778 | 1859 | -457 | 1 | 0 | 2316 | 1507.3372 | 1507.3372 | 1507.3372 | 761.7477 | 780 | 200 | 1741.7477 | 43.54% | 95% | 0% | -522.8833 | 984.4539 | -3550 | -400 | -2965.5461 | 74.14% | 43.11% | 95% | 0% | 2316 | -457
[5 empty] | 2019-10-10 | 23 | 6778.5 | 1854 | -472 | 1 | 0 | 2326 | 1523.0008 | 1523.0008 | 1523.0008 | 761.7477 | 780 | 200 | 1741.7477 | 43.54% | 95% | 0% | -540.0458 | 982.9551 | -3550 | -400 | -2967.0449 | 74.18% | 43.1% | 95% | 0% | 2326 | -472
[5 empty] | 2019-10-10 | 24 | 6779 | 1868 | -471 | 1 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 760.1814 | 780 | 200 | 1740.1814 | 43.5% | 95% | 0% | -538.9016 | 1004.462 | -3550 | -400 | -2945.538 | 73.64% | 43.09% | 95% | 0% | 2339 | -471
[5 empty] | 2019-10-10 | 25 | 6779.5 | 1917 | -451 | 1 | 0 | 2368 | 1588.7881 | 1588.7881 | 1588.7881 | 760.1814 | 780 | 200 | 1740.1814 | 43.5% | 95% | 0% | -516.0183 | 1072.7698 | -3550 | -400 | -2877.2302 | 71.93% | 43.09% | 95% | 0% | 2368 | -451
[5 empty] | 2019-10-10 | 26 | 6780 | 1958 | -422 | 1 | 0 | 2380 | 1607.5845 | 1607.5845 | 1607.5845 | 760.1814 | 780 | 200 | 1740.1814 | 43.5% | 95% | 0% | -482.8375 | 1124.747 | -3550 | -400 | -2825.253 | 70.63% | 43.08% | 95% | 0% | 2380 | -422
[5 empty] | 2019-10-10 | 27 | 6780.5 | 1996 | -391 | 1 | 0 | 2387 | 1618.5491 | 1618.5491 | 1618.5491 | 760.1814 | 780 | 200 | 1740.1814 | 43.5% | 95% | 0% | -447.3684 | 1171.1806 | -3550 | -400 | -2778.8194 | 69.47% | 43.08% | 95% | 0% | 2387 | -391
[5 empty] | 2019-10-10 | 28 | 6781 | 2034 | -359 | 1 | 0 | 2393 | 1627.9472 | 1627.9472 | 1627.9472 | 760.1814 | 780 | 200 | 1740.1814 | 43.5% | 95% | 0% | -410.7551 | 1217.1921 | -3550 | -400 | -2732.8079 | 68.32% | 43.08% | 95% | 0% | 2393 | -359
[5 empty] | 2019-10-10 | 29 | 6781.5 | 2084 | -330 | 1 | 0 | 2414 | 1660.8409 | 1660.8409 | 1660.8409 | 760.1814 | 780 | 200 | 1740.1814 | 43.5% | 95% | 0% | -377.5744 | 1283.2665 | -3550 | -400 | -2666.7335 | 66.67% | 43.08% | 95% | 0% | 2414 | -330
[5 empty] | 2019-10-10 | 30 | 6782 | 2115 | -311 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 760.1814 | 780 | 200 | 1740.1814 | 43.5% | 95% | 0% | -355.8352 | 1323.802 | -3550 | -400 | -2626.198 | 65.65% | 43.06% | 95% | 0% | 2426 | -311
[5 empty] | 2019-10-10 | 31 | 6782.5 | 2147 | -282 | 1 | 0 | 2429 | 1684.3364 | 1684.3364 | 1684.3364 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -322.6545 | 1361.6819 | -3550 | -400 | -2588.3181 | 64.71% | 43.06% | 95% | 0% | 2429 | -282
[5 empty] | 2019-10-10 | 32 | 6783 | 2204 | -258 | 1 | 0 | 2462 | 1736.0264 | 1736.0264 | 1736.0264 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -295.1945 | 1440.8319 | -3550 | -400 | -2509.1681 | 62.73% | 43.06% | 95% | 0% | 2462 | -258
[5 empty] | 2019-10-10 | 33 | 6783.5 | 2329 | -235 | 1 | 0 | 2564 | 1895.7955 | 1895.7955 | 1895.7955 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -268.8787 | 1626.9168 | -3550 | -400 | -2323.0832 | 58.08% | 43.05% | 95% | 0% | 2564 | -235
[5 empty] | 2019-10-10 | 34 | 6784 | 2411 | -222 | 1 | 0 | 2633 | 2003.8747 | 2003.8747 | 2003.8747 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -254.0046 | 1749.8701 | -3550 | -400 | -2200.1299 | 55% | 43.04% | 95% | 0% | 2633 | -222
[5 empty] | 2019-10-10 | 35 | 6784.5 | 2498 | -202 | 1 | 0 | 2700 | 2108.8211 | 2108.8211 | 2108.8211 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -231.1213 | 1877.6998 | -3550 | -400 | -2072.3002 | 51.81% | 43.04% | 95% | 0% | 2700 | -202
[5 empty] | 2019-10-10 | 36 | 6785 | 2544 | -186 | 1 | 0 | 2730 | 2155.812 | 2155.812 | 2155.812 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -212.8146 | 1942.9974 | -3550 | -400 | -2007.0026 | 50.18% | 43.03% | 95% | 0% | 2730 | -186
[5 empty] | 2019-10-10 | 37 | 6785.5 | 2588 | -178 | 1 | 0 | 2766 | 2212.2012 | 2212.2012 | 2212.2012 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -203.6613 | 2008.5398 | -3550 | -400 | -1941.4602 | 48.54% | 43.03% | 95% | 0% | 2766 | -178
[5 empty] | 2019-10-10 | 38 | 6786 | 2629 | -179 | 1 | 0 | 2808 | 2277.9885 | 2277.9885 | 2277.9885 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -204.8055 | 2073.183 | -3550 | -400 | -1876.817 | 46.92% | 43.02% | 95% | 0% | 2808 | -179
[5 empty] | 2019-10-10 | 39 | 6786.5 | 2615 | -181 | 1 | 0 | 2796 | 2259.1921 | 2259.1921 | 2259.1921 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -207.0938 | 2052.0983 | -3550 | -400 | -1897.9017 | 47.45% | 43.02% | 95% | 0% | 2796 | -181
[5 empty] | 2019-10-10 | 40 | 6787 | 2515 | -184 | 0 | 0 | 2699 | 2107.2547 | 2107.2547 | 2107.2547 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -210.5263 | 1896.7284 | -2750 | -200 | -1053.2716 | 26.33% | 43.01% | 95% | 0% | 2699 | -184
[5 empty] | 2019-10-10 | 41 | 6787.5 | 2394 | -188 | 0 | 0 | 2582 | 1923.9901 | 1923.9901 | 1923.9901 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -215.103 | 1708.8871 | -2750 | -200 | -1241.1129 | 31.03% | 43% | 95% | 0% | 2582 | -188
[5 empty] | 2019-10-10 | 42 | 6788 | 2288 | -191 | 0 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -218.5355 | 1544.1191 | -2750 | -200 | -1405.8809 | 35.15% | 43% | 95% | 0% | 2479 | -191
[5 empty] | 2019-10-10 | 43 | 6788.5 | 2150 | -193 | 0 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -220.8238 | 1328.8052 | -2750 | -200 | -1621.1948 | 40.53% | 43% | 95% | 0% | 2343 | -193
[5 empty] | 2019-10-10 | 44 | 6789 | 2015 | -195 | 0 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -223.1121 | 1118.1904 | -2750 | -200 | -1831.8096 | 45.8% | 43% | 95% | 0% | 2210 | -195
[5 empty] | 2019-10-10 | 45 | 6789.5 | 1865 | -196 | 0 | 0 | 2061 | 1107.9143 | 1107.9143 | 1107.9143 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -224.2563 | 883.658 | -2750 | -200 | -2066.342 | 51.66% | 43% | 95% | 0% | 2061 | -196
[5 empty] | 2019-10-10 | 46 | 6790 | 1728 | -197 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 758.615 | 780 | 200 | 1738.615 | 43.47% | 95% | 0% | -225.4005 | 669.4882 | -2750 | -200 | -2280.5118 | 57.01% | 42.99% | 95% | 0% | 1925 | -197
[5 empty] | 2019-10-10 | 47 | 6790.5 | 1579 | -196 | 0 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 757.0486 | 780 | 200 | 1737.0486 | 43.43% | 95% | 0% | -224.2563 | 435.6778 | -2750 | -200 | -2514.3222 | 62.86% | 42.98% | 95% | 0% | 1775 | -196
[5 empty] | 2019-10-10 | 48 | 6791 | 1460 | -196 | 0 | 0 | 1656 | 473.5367 | 473.5367 | 473.5367 | 757.0486 | 780 | 200 | 1737.0486 | 43.43% | 95% | 0% | -224.2563 | 249.2804 | -2750 | -200 | -2700.7196 | 67.52% | 42.98% | 95% | 0% | 1656 | -196
[5 empty] | 2019-10-11 | 1 | 6791.5 | 1356 | -196 | 0 | 0 | 1552 | 310.6348 | 310.6348 | 310.6348 | 757.0486 | 780 | 200 | 1737.0486 | 43.43% | 95% | 0% | -224.2563 | 86.3785 | -2750 | -200 | -2863.6215 | 71.59% | 42.96% | 95% | 0% | 1552 | -196
[5 empty] | 2019-10-11 | 2 | 6792 | 1319 | -197 | 0 | 0 | 1516 | 254.2457 | 254.2457 | 254.2457 | 757.0486 | 780 | 200 | 1737.0486 | 43.43% | 95% | 0% | -225.4005 | 28.8452 | -2750 | -200 | -2921.1548 | 73.03% | 42.95% | 95% | 0% | 1516 | -197
[5 empty] | 2019-10-11 | 3 | 6792.5 | 1310 | -197 | 0 | 0 | 1507 | 240.1484 | 240.1484 | 240.1484 | 757.0486 | 780 | 200 | 1737.0486 | 43.43% | 95% | 0% | -225.4005 | 14.7479 | -2750 | -200 | -2935.2521 | 73.38% | 42.94% | 95% | 0% | 1507 | -197
[5 empty] | 2019-10-11 | 4 | 6793 | 1332 | -196 | 0 | 0 | 1528 | 273.042 | 273.042 | 273.042 | 757.0486 | 780 | 200 | 1737.0486 | 43.43% | 95% | 0% | -224.2563 | 48.7858 | -2750 | -200 | -2901.2142 | 72.53% | 42.94% | 95% | 0% | 1528 | -196
[5 empty] | 2019-10-11 | 5 | 6793.5 | 1315 | -195 | 0 | 0 | 1510 | 244.8475 | 244.8475 | 244.8475 | 757.0486 | 780 | 200 | 1737.0486 | 43.43% | 95% | 0% | -223.1121 | 21.7354 | -2750 | -200 | -2928.2646 | 73.21% | 42.92% | 95% | 0% | 1510 | -195
[5 empty] | 2019-10-11 | 6 | 6794 | 1284 | -193 | 0 | 0 | 1477 | 193.1575 | 193.1575 | 193.1575 | 757.0486 | 780 | 200 | 1737.0486 | 43.43% | 95% | 0% | -220.8238 | -27.6663 | -2750 | -200 | -2977.6663 | 74.44% | 42.91% | 95% | 0% | 1477 | -193
[5 empty] | 2019-10-11 | 7 | 6794.5 | 1267 | -192 | 0 | 0 | 1459 | 164.9629 | 164.9629 | 164.9629 | 757.0486 | 780 | 200 | 1737.0486 | 43.43% | 95% | 0% | -219.6796 | -54.7167 | -2750 | -200 | -3004.7167 | 75.12% | 42.91% | 95% | 0% | 1459 | -192
[5 empty] | 2019-10-11 | 8 | 6795 | 1257 | -190 | 0 | 0 | 1447 | 146.1665 | 146.1665 | 146.1665 | 757.0486 | 780 | 200 | 1737.0486 | 43.43% | 95% | 0% | -217.3913 | -71.2248 | -2750 | -200 | -3021.2248 | 75.53% | 42.89% | 95% | 0% | 1447 | -190
[5 empty] | 2019-10-11 | 9 | 6795.5 | 1252 | -190 | 0 | 0 | 1442 | 138.3347 | 138.3347 | 138.3347 | 755.4823 | 780 | 200 | 1735.4823 | 43.39% | 95% | 0% | -217.3913 | -79.0566 | -2750 | -200 | -3029.0566 | 75.73% | 42.88% | 95% | 0% | 1442 | -190
[5 empty] | 2019-10-11 | 10 | 6796 | 1266 | -190 | 0 | 0 | 1456 | 160.2638 | 160.2638 | 160.2638 | 755.4823 | 780 | 200 | 1735.4823 | 43.39% | 95% | 0% | -217.3913 | -57.1275 | -2750 | -200 | -3007.1275 | 75.18% | 42.88% | 95% | 0% | 1456 | -190
[5 empty] | 2019-10-11 | 11 | 6796.5 | 1332 | -189 | 0 | 0 | 1521 | 262.0775 | 262.0775 | 262.0775 | 755.4823 | 780 | 200 | 1735.4823 | 43.39% | 95% | 0% | -216.2471 | 45.8304 | -2750 | -200 | -2904.1696 | 72.6% | 42.87% | 95% | 0% | 1521 | -189
[5 empty] | 2019-10-11 | 12 | 6797 | 1433 | -189 | 1 | 0 | 1622 | 420.2803 | 420.2803 | 420.2803 | 755.4823 | 780 | 200 | 1735.4823 | 43.39% | 95% | 0% | -216.2471 | 204.0332 | -3550 | -400 | -3745.9668 | 93.65% | 42.87% | 95% | 0% | 1622 | -189
[5 empty] | 2019-10-11 | 13 | 6797.5 | 1644 | -187 | 1 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 755.4823 | 780 | 200 | 1735.4823 | 43.39% | 95% | 0% | -213.9588 | 533.6916 | -3550 | -400 | -3416.3084 | 85.41% | 42.87% | 95% | 0% | 1831 | -187
[5 empty] | 2019-10-11 | 14 | 6798 | 1874 | -185 | 1 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 755.4823 | 780 | 200 | 1735.4823 | 43.39% | 95% | 0% | -211.6705 | 893.1111 | -3550 | -400 | -3056.8889 | 76.42% | 42.87% | 95% | 0% | 2059 | -185
[5 empty] | 2019-10-11 | 15 | 6798.5 | 2146 | -185 | 1 | 0 | 2331 | 1530.8326 | 1530.8326 | 1530.8326 | 755.4823 | 780 | 200 | 1735.4823 | 43.39% | 95% | 0% | -211.6705 | 1319.1622 | -3550 | -400 | -2630.8378 | 65.77% | 42.85% | 95% | 0% | 2331 | -185
[5 empty] | 2019-10-11 | 16 | 6799 | 2306 | -185 | 1 | 0 | 2491 | 1781.4509 | 1781.4509 | 1781.4509 | 755.4823 | 780 | 200 | 1735.4823 | 43.39% | 95% | 0% | -211.6705 | 1569.7805 | -3550 | -400 | -2380.2195 | 59.51% | 42.85% | 95% | 0% | 2491 | -185
[5 empty] | 2019-10-11 | 17 | 6799.5 | 2371 | -192 | 1 | 0 | 2563 | 1894.2292 | 1894.2292 | 1894.2292 | 755.4823 | 780 | 200 | 1735.4823 | 43.39% | 95% | 0% | -219.6796 | 1674.5495 | -3550 | -400 | -2275.4505 | 56.89% | 42.85% | 95% | 0% | 2563 | -192
[5 empty] | 2019-10-11 | 18 | 6800 | 2336 | -207 | 1 | 0 | 2543 | 1862.9019 | 1862.9019 | 1862.9019 | 755.4823 | 780 | 200 | 1735.4823 | 43.39% | 95% | 0% | -236.8421 | 1626.0598 | -3550 | -400 | -2323.9402 | 58.1% | 42.84% | 95% | 0% | 2543 | -207
[5 empty] | 2019-10-11 | 19 | 6800.5 | 2337 | -212 | 1 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 755.4823 | 780 | 200 | 1735.4823 | 43.39% | 95% | 0% | -242.5629 | 1629.7372 | -3550 | -400 | -2320.2628 | 58.01% | 42.84% | 95% | 0% | 2549 | -212
[5 empty] | 2019-10-11 | 20 | 6801 | 2301 | -247 | 1 | 0 | 2548 | 1870.7337 | 1870.7337 | 1870.7337 | 753.9159 | 780 | 200 | 1733.9159 | 43.35% | 95% | 0% | -282.6087 | 1588.125 | -3550 | -400 | -2361.875 | 59.05% | 42.84% | 95% | 0% | 2548 | -247
[5 empty] | 2019-10-11 | 21 | 6801.5 | 2277 | -277 | 1 | 0 | 2554 | 1880.1319 | 1880.1319 | 1880.1319 | 753.9159 | 780 | 200 | 1733.9159 | 43.35% | 95% | 0% | -316.9336 | 1563.1983 | -3550 | -400 | -2386.8017 | 59.67% | 42.84% | 95% | 0% | 2554 | -277
[5 empty] | 2019-10-11 | 22 | 6802 | 2244 | -303 | 1 | 0 | 2547 | 1869.1674 | 1869.1674 | 1869.1674 | 753.9159 | 780 | 200 | 1733.9159 | 43.35% | 95% | 0% | -346.6819 | 1522.4854 | -3550 | -400 | -2427.5146 | 60.69% | 42.83% | 95% | 0% | 2547 | -303
[5 empty] | 2019-10-11 | 23 | 6802.5 | 2248 | -312 | 1 | 0 | 2560 | 1889.5301 | 1889.5301 | 1889.5301 | 753.9159 | 780 | 200 | 1733.9159 | 43.35% | 95% | 0% | -356.9794 | 1532.5507 | -3550 | -400 | -2417.4493 | 60.44% | 42.83% | 95% | 0% | 2560 | -312
[5 empty] | 2019-10-11 | 24 | 6803 | 2238 | -321 | 1 | 0 | 2559 | 1887.9637 | 1887.9637 | 1887.9637 | 753.9159 | 780 | 200 | 1733.9159 | 43.35% | 95% | 0% | -367.2769 | 1520.6868 | -3550 | -400 | -2429.3132 | 60.73% | 42.82% | 95% | 0% | 2559 | -321
[5 empty] | 2019-10-11 | 25 | 6803.5 | 2231 | -333 | 1 | 0 | 2564 | 1895.7955 | 1895.7955 | 1895.7955 | 753.9159 | 780 | 200 | 1733.9159 | 43.35% | 95% | 0% | -381.0069 | 1514.7887 | -3550 | -400 | -2435.2113 | 60.88% | 42.82% | 95% | 0% | 2564 | -333
[5 empty] | 2019-10-11 | 26 | 6804 | 2190 | -345 | 1 | 0 | 2535 | 1850.371 | 1850.371 | 1850.371 | 753.9159 | 780 | 200 | 1733.9159 | 43.35% | 95% | 0% | -394.7368 | 1455.6341 | -3550 | -400 | -2494.3659 | 62.36% | 42.82% | 95% | 0% | 2535 | -345
[5 empty] | 2019-10-11 | 27 | 6804.5 | 2131 | -361 | 1 | 0 | 2492 | 1783.0173 | 1783.0173 | 1783.0173 | 753.9159 | 780 | 200 | 1733.9159 | 43.35% | 95% | 0% | -413.0435 | 1369.9738 | -3550 | -400 | -2580.0262 | 64.5% | 42.82% | 95% | 0% | 2492 | -361
[5 empty] | 2019-10-11 | 28 | 6805 | 2092 | -365 | 1 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 753.9159 | 780 | 200 | 1733.9159 | 43.35% | 95% | 0% | -417.6201 | 1310.5744 | -3550 | -400 | -2639.4256 | 65.99% | 42.81% | 95% | 0% | 2457 | -365
[5 empty] | 2019-10-11 | 29 | 6805.5 | 2074 | -360 | 1 | 0 | 2434 | 1692.1682 | 1692.1682 | 1692.1682 | 753.9159 | 780 | 200 | 1733.9159 | 43.35% | 95% | 0% | -411.8993 | 1280.2689 | -3550 | -400 | -2669.7311 | 66.74% | 42.8% | 95% | 0% | 2434 | -360
[5 empty] | 2019-10-11 | 30 | 6806 | 2054 | -352 | 1 | 0 | 2406 | 1648.31 | 1648.31 | 1648.31 | 753.9159 | 780 | 200 | 1733.9159 | 43.35% | 95% | 0% | -402.746 | 1245.564 | -3550 | -400 | -2704.436 | 67.61% | 42.8% | 95% | 0% | 2406 | -352
[5 empty] | 2019-10-11 | 31 | 6806.5 | 2066 | -324 | 1 | 0 | 2390 | 1623.2481 | 1623.2481 | 1623.2481 | 752.3495 | 780 | 200 | 1732.3495 | 43.31% | 95% | 0% | -370.7094 | 1252.5388 | -3550 | -400 | -2697.4612 | 67.44% | 42.8% | 95% | 0% | 2390 | -324
[5 empty] | 2019-10-11 | 32 | 6807 | 2149 | -288 | 1 | 0 | 2437 | 1696.8673 | 1696.8673 | 1696.8673 | 752.3495 | 780 | 200 | 1732.3495 | 43.31% | 95% | 0% | -329.5195 | 1367.3478 | -3550 | -400 | -2582.6522 | 64.57% | 42.8% | 95% | 0% | 2437 | -288
[5 empty] | 2019-10-11 | 33 | 6807.5 | 2261 | -254 | 1 | 0 | 2515 | 1819.0437 | 1819.0437 | 1819.0437 | 752.3495 | 780 | 200 | 1732.3495 | 43.31% | 95% | 0% | -290.6178 | 1528.4258 | -3550 | -400 | -2421.5742 | 60.54% | 42.8% | 95% | 0% | 2515 | -254
[5 empty] | 2019-10-11 | 34 | 6808 | 2353 | -228 | 1 | 0 | 2581 | 1922.4237 | 1922.4237 | 1922.4237 | 752.3495 | 780 | 200 | 1732.3495 | 43.31% | 95% | 0% | -260.8696 | 1661.5542 | -3550 | -400 | -2288.4458 | 57.21% | 42.79% | 95% | 0% | 2581 | -228
[5 empty] | 2019-10-11 | 35 | 6808.5 | 2441 | -204 | 1 | 0 | 2645 | 2022.6711 | 2022.6711 | 2022.6711 | 752.3495 | 780 | 200 | 1732.3495 | 43.31% | 95% | 0% | -233.4096 | 1789.2615 | -3550 | -400 | -2160.7385 | 54.02% | 42.79% | 95% | 0% | 2645 | -204
[5 empty] | 2019-10-11 | 36 | 6809 | 2493 | -182 | 1 | 0 | 2675 | 2069.662 | 2069.662 | 2069.662 | 752.3495 | 780 | 200 | 1732.3495 | 43.31% | 95% | 0% | -208.238 | 1861.424 | -3550 | -400 | -2088.576 | 52.21% | 42.79% | 95% | 0% | 2675 | -182
[5 empty] | 2019-10-11 | 37 | 6809.5 | 2534 | -174 | 1 | 0 | 2708 | 2121.352 | 2121.352 | 2121.352 | 752.3495 | 780 | 200 | 1732.3495 | 43.31% | 95% | 0% | -199.0847 | 1922.2674 | -3550 | -400 | -2027.7326 | 50.69% | 42.79% | 95% | 0% | 2708 | -174
[5 empty] | 2019-10-11 | 38 | 6810 | 2586 | -170 | 1 | 0 | 2756 | 2196.5375 | 2196.5375 | 2196.5375 | 752.3495 | 780 | 200 | 1732.3495 | 43.31% | 95% | 0% | -194.508 | 2002.0295 | -3550 | -400 | -1947.9705 | 48.7% | 42.79% | 95% | 0% | 2756 | -170
[5 empty] | 2019-10-11 | 39 | 6810.5 | 2562 | -168 | 0 | 0 | 2730 | 2155.812 | 2155.812 | 2155.812 | 752.3495 | 780 | 200 | 1732.3495 | 43.31% | 95% | 0% | -192.2197 | 1963.5924 | -2750 | -200 | -986.4076 | 24.66% | 42.78% | 95% | 0% | 2730 | -168
[5 empty] | 2019-10-11 | 40 | 6811 | 2470 | -166 | 0 | 0 | 2636 | 2008.5738 | 2008.5738 | 2008.5738 | 752.3495 | 780 | 200 | 1732.3495 | 43.31% | 95% | 0% | -189.9314 | 1818.6424 | -2750 | -200 | -1131.3576 | 28.28% | 42.78% | 95% | 0% | 2636 | -166
[5 empty] | 2019-10-11 | 41 | 6811.5 | 2384 | -163 | 0 | 0 | 2547 | 1869.1674 | 1869.1674 | 1869.1674 | 752.3495 | 780 | 200 | 1732.3495 | 43.31% | 95% | 0% | -186.4989 | 1682.6685 | -2750 | -200 | -1267.3315 | 31.68% | 42.78% | 95% | 0% | 2547 | -163
[5 empty] | 2019-10-11 | 42 | 6812 | 2285 | -160 | 0 | 0 | 2445 | 1709.3982 | 1709.3982 | 1709.3982 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -183.0664 | 1526.3318 | -2750 | -200 | -1423.6682 | 35.59% | 42.77% | 95% | 0% | 2445 | -160
[5 empty] | 2019-10-11 | 43 | 6812.5 | 2195 | -157 | 0 | 0 | 2352 | 1563.7263 | 1563.7263 | 1563.7263 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -179.6339 | 1384.0924 | -2750 | -200 | -1565.9076 | 39.15% | 42.76% | 95% | 0% | 2352 | -157
[5 empty] | 2019-10-11 | 44 | 6813 | 2071 | -153 | 0 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -175.0572 | 1188.1744 | -2750 | -200 | -1761.8256 | 44.05% | 42.75% | 95% | 0% | 2224 | -153
[5 empty] | 2019-10-11 | 45 | 6813.5 | 1947 | -150 | 0 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -171.6247 | 992.6787 | -2750 | -200 | -1957.3213 | 48.93% | 42.75% | 95% | 0% | 2097 | -150
[5 empty] | 2019-10-11 | 46 | 6814 | 1834 | -147 | 0 | 0 | 1981 | 982.6051 | 982.6051 | 982.6051 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -168.1922 | 814.4129 | -2750 | -200 | -2135.5871 | 53.39% | 42.74% | 95% | 0% | 1981 | -147
[5 empty] | 2019-10-11 | 47 | 6814.5 | 1727 | -142 | 0 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -162.4714 | 644.7009 | -2750 | -200 | -2305.2991 | 57.63% | 42.73% | 95% | 0% | 1869 | -142
[5 empty] | 2019-10-11 | 48 | 6815 | 1630 | -137 | 1 | 0 | 1767 | 647.4031 | 647.4031 | 647.4031 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -156.7506 | 490.6526 | -3550 | -400 | -3459.3474 | 86.48% | 42.73% | 95% | 0% | 1767 | -137
[5 empty] | 2019-10-12 | 1 | 6815.5 | 1552 | -133 | 1 | 0 | 1685 | 518.9613 | 518.9613 | 518.9613 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -152.1739 | 366.7873 | -3550 | -400 | -3583.2127 | 89.58% | 42.71% | 95% | 0% | 1685 | -133
[5 empty] | 2019-10-12 | 2 | 6816 | 1511 | -129 | 1 | 0 | 1640 | 448.4749 | 448.4749 | 448.4749 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -147.5973 | 300.8776 | -3550 | -400 | -3649.1224 | 91.23% | 42.71% | 95% | 0% | 1640 | -129
[5 empty] | 2019-10-12 | 3 | 6816.5 | 1498 | -125 | 1 | 0 | 1623 | 421.8467 | 421.8467 | 421.8467 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -143.0206 | 278.8261 | -3550 | -400 | -3671.1739 | 91.78% | 42.71% | 95% | 0% | 1623 | -125
[5 empty] | 2019-10-12 | 4 | 6817 | 1516 | -120 | 1 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -137.2998 | 304.9096 | -3550 | -400 | -3645.0904 | 91.13% | 42.71% | 95% | 0% | 1636 | -120
[5 empty] | 2019-10-12 | 5 | 6817.5 | 1510 | -116 | 1 | 0 | 1626 | 426.5458 | 426.5458 | 426.5458 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -132.7231 | 293.8226 | -3550 | -400 | -3656.1774 | 91.4% | 42.7% | 95% | 0% | 1626 | -116
[5 empty] | 2019-10-12 | 6 | 6818 | 1497 | -112 | 1 | 0 | 1609 | 399.9176 | 399.9176 | 399.9176 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -128.1465 | 271.7711 | -3550 | -400 | -3678.2289 | 91.96% | 42.68% | 95% | 0% | 1609 | -112
[5 empty] | 2019-10-12 | 7 | 6818.5 | 1472 | -109 | 1 | 0 | 1581 | 356.0594 | 356.0594 | 356.0594 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -124.714 | 231.3454 | -3550 | -400 | -3718.6546 | 92.97% | 42.68% | 95% | 0% | 1581 | -109
[5 empty] | 2019-10-12 | 8 | 6819 | 1454 | -105 | 1 | 0 | 1559 | 321.5993 | 321.5993 | 321.5993 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -120.1373 | 201.462 | -3550 | -400 | -3748.538 | 93.71% | 42.68% | 95% | 0% | 1559 | -105
[5 empty] | 2019-10-12 | 9 | 6819.5 | 1456 | -102 | 1 | 0 | 1558 | 320.033 | 320.033 | 320.033 | 750.7832 | 780 | 200 | 1730.7832 | 43.27% | 95% | 0% | -116.7048 | 203.3282 | -3550 | -400 | -3746.6718 | 93.67% | 42.67% | 95% | 0% | 1558 | -102
[5 empty] | 2019-10-12 | 10 | 6820 | 1468 | -99 | 1 | 0 | 1567 | 334.1303 | 334.1303 | 334.1303 | 749.2168 | 780 | 200 | 1729.2168 | 43.23% | 95% | 0% | -113.2723 | 220.8579 | -3550 | -400 | -3729.1421 | 93.23% | 42.67% | 95% | 0% | 1567 | -99
[5 empty] | 2019-10-12 | 11 | 6820.5 | 1497 | -97 | 1 | 0 | 1594 | 376.4221 | 376.4221 | 376.4221 | 749.2168 | 780 | 200 | 1729.2168 | 43.23% | 95% | 0% | -110.984 | 265.4381 | -3550 | -400 | -3684.5619 | 92.11% | 42.67% | 95% | 0% | 1594 | -97
[5 empty] | 2019-10-12 | 12 | 6821 | 1544 | -95 | 1 | 0 | 1639 | 446.9085 | 446.9085 | 446.9085 | 749.2168 | 780 | 200 | 1729.2168 | 43.23% | 95% | 0% | -108.6957 | 338.2128 | -3550 | -400 | -3611.7872 | 90.29% | 42.67% | 95% | 0% | 1639 | -95
[5 empty] | 2019-10-12 | 13 | 6821.5 | 1658 | -93 | 1 | 0 | 1751 | 622.3413 | 622.3413 | 622.3413 | 749.2168 | 780 | 200 | 1729.2168 | 43.23% | 95% | 0% | -106.4073 | 515.934 | -3550 | -400 | -3434.066 | 85.85% | 42.66% | 95% | 0% | 1751 | -93
[5 empty] | 2019-10-12 | 14 | 6822 | 1754 | -91 | 1 | 0 | 1845 | 769.5796 | 769.5796 | 769.5796 | 749.2168 | 780 | 200 | 1729.2168 | 43.23% | 95% | 0% | -104.119 | 665.4606 | -3550 | -400 | -3284.5394 | 82.11% | 42.66% | 95% | 0% | 1845 | -91
[5 empty] | 2019-10-12 | 15 | 6822.5 | 1888 | -89 | 1 | 0 | 1977 | 976.3397 | 976.3397 | 976.3397 | 749.2168 | 780 | 200 | 1729.2168 | 43.23% | 95% | 0% | -101.8307 | 874.509 | -3550 | -400 | -3075.491 | 76.89% | 42.65% | 95% | 0% | 1977 | -89
[5 empty] | 2019-10-12 | 16 | 6823 | 2000 | -89 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 749.2168 | 780 | 200 | 1729.2168 | 43.23% | 95% | 0% | -101.8307 | 1049.9418 | -3550 | -400 | -2900.0582 | 72.5% | 42.64% | 95% | 0% | 2089 | -89
[5 empty] | 2019-10-12 | 17 | 6823.5 | 2131 | -98 | 1 | 0 | 2229 | 1371.0635 | 1371.0635 | 1371.0635 | 749.2168 | 780 | 200 | 1729.2168 | 43.23% | 95% | 0% | -112.1281 | 1258.9353 | -3550 | -400 | -2691.0647 | 67.28% | 42.64% | 95% | 0% | 2229 | -98
[5 empty] | 2019-10-12 | 18 | 6824 | 2190 | -117 | 1 | 0 | 2307 | 1493.2399 | 1493.2399 | 1493.2399 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -133.8673 | 1359.3726 | -3550 | -400 | -2590.6274 | 64.77% | 42.64% | 95% | 0% | 2307 | -117
[5 empty] | 2019-10-12 | 19 | 6824.5 | 2198 | -151 | 1 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -172.7689 | 1386.2583 | -3550 | -400 | -2563.7417 | 64.09% | 42.62% | 95% | 0% | 2349 | -151
[5 empty] | 2019-10-12 | 20 | 6825 | 2158 | -182 | 1 | 0 | 2340 | 1544.9299 | 1544.9299 | 1544.9299 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -208.238 | 1336.6919 | -3550 | -400 | -2613.3081 | 65.33% | 42.62% | 95% | 0% | 2340 | -182
[5 empty] | 2019-10-12 | 21 | 6825.5 | 2133 | -212 | 1 | 0 | 2345 | 1552.7617 | 1552.7617 | 1552.7617 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -242.5629 | 1310.1988 | -3550 | -400 | -2639.8012 | 66% | 42.61% | 95% | 0% | 2345 | -212
[5 empty] | 2019-10-12 | 22 | 6826 | 2084 | -250 | 1 | 0 | 2334 | 1535.5317 | 1535.5317 | 1535.5317 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -286.0412 | 1249.4905 | -3550 | -400 | -2700.5095 | 67.51% | 42.61% | 95% | 0% | 2334 | -250
[5 empty] | 2019-10-12 | 23 | 6826.5 | 2045 | -282 | 1 | 0 | 2327 | 1524.5672 | 1524.5672 | 1524.5672 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -322.6545 | 1201.9127 | -3550 | -400 | -2748.0873 | 68.7% | 42.61% | 95% | 0% | 2327 | -282
[5 empty] | 2019-10-12 | 24 | 6827 | 2022 | -301 | 1 | 0 | 2323 | 1518.3017 | 1518.3017 | 1518.3017 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -344.3936 | 1173.9081 | -3550 | -400 | -2776.0919 | 69.4% | 42.6% | 95% | 0% | 2323 | -301
[5 empty] | 2019-10-12 | 25 | 6827.5 | 2002 | -302 | 1 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -345.5378 | 1143.0031 | -3550 | -400 | -2806.9969 | 70.17% | 42.6% | 95% | 0% | 2304 | -302
[5 empty] | 2019-10-12 | 26 | 6828 | 1987 | -303 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -346.6819 | 1119.9298 | -3550 | -400 | -2830.0702 | 70.75% | 42.6% | 95% | 0% | 2290 | -303
[5 empty] | 2019-10-12 | 27 | 6828.5 | 1954 | -305 | 1 | 0 | 2259 | 1418.0544 | 1418.0544 | 1418.0544 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -348.9703 | 1069.0842 | -3550 | -400 | -2880.9158 | 72.02% | 42.59% | 95% | 0% | 2259 | -305
[5 empty] | 2019-10-12 | 28 | 6829 | 1962 | -279 | 1 | 0 | 2241 | 1389.8599 | 1389.8599 | 1389.8599 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -319.222 | 1070.6379 | -3550 | -400 | -2879.3621 | 71.98% | 42.59% | 95% | 0% | 2241 | -279
[5 empty] | 2019-10-12 | 29 | 6829.5 | 1984 | -251 | 1 | 0 | 2235 | 1380.4617 | 1380.4617 | 1380.4617 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -287.1854 | 1093.2763 | -3550 | -400 | -2856.7237 | 71.42% | 42.59% | 95% | 0% | 2235 | -251
[5 empty] | 2019-10-12 | 30 | 6830 | 1998 | -228 | 1 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 747.6505 | 780 | 200 | 1727.6505 | 43.19% | 95% | 0% | -260.8696 | 1105.4948 | -3550 | -400 | -2844.5052 | 71.11% | 42.59% | 95% | 0% | 2226 | -228
[5 empty] | 2019-10-12 | 31 | 6830.5 | 2012 | -202 | 1 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -231.1213 | 1116.4467 | -3550 | -400 | -2833.5533 | 70.84% | 42.59% | 95% | 0% | 2214 | -202
[5 empty] | 2019-10-12 | 32 | 6831 | 2074 | -177 | 1 | 0 | 2251 | 1405.5235 | 1405.5235 | 1405.5235 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -202.5172 | 1203.0063 | -3550 | -400 | -2746.9937 | 68.67% | 42.58% | 95% | 0% | 2251 | -177
[5 empty] | 2019-10-12 | 33 | 6831.5 | 2198 | -144 | 1 | 0 | 2342 | 1548.0627 | 1548.0627 | 1548.0627 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -164.7597 | 1383.3029 | -3550 | -400 | -2566.6971 | 64.17% | 42.58% | 95% | 0% | 2342 | -144
[5 empty] | 2019-10-12 | 34 | 6832 | 2314 | -112 | 1 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -128.1465 | 1551.4908 | -3550 | -400 | -2398.5092 | 59.96% | 42.58% | 95% | 0% | 2426 | -112
[5 empty] | 2019-10-12 | 35 | 6832.5 | 2469 | -88 | 1 | 0 | 2557 | 1884.831 | 1884.831 | 1884.831 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -100.6865 | 1784.1445 | -3550 | -400 | -2165.8555 | 54.15% | 42.58% | 95% | 0% | 2557 | -88
[5 empty] | 2019-10-12 | 36 | 6833 | 2557 | -68 | 1 | 0 | 2625 | 1991.3438 | 1991.3438 | 1991.3438 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -77.8032 | 1913.5406 | -3550 | -400 | -2036.4594 | 50.91% | 42.57% | 95% | 0% | 2625 | -68
[5 empty] | 2019-10-12 | 37 | 6833.5 | 2603 | -62 | 1 | 0 | 2665 | 2053.9984 | 2053.9984 | 2053.9984 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -70.9382 | 1983.0601 | -3550 | -400 | -1966.9399 | 49.17% | 42.57% | 95% | 0% | 2665 | -62
[5 empty] | 2019-10-12 | 38 | 6834 | 2634 | -61 | 1 | 0 | 2695 | 2100.9893 | 2100.9893 | 2100.9893 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -69.7941 | 2031.1952 | -3550 | -400 | -1918.8048 | 47.97% | 42.57% | 95% | 0% | 2695 | -61
[5 empty] | 2019-10-12 | 39 | 6834.5 | 2585 | -61 | 1 | 0 | 2646 | 2024.2374 | 2024.2374 | 2024.2374 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -69.7941 | 1954.4434 | -3550 | -400 | -1995.5566 | 49.89% | 42.57% | 95% | 0% | 2646 | -61
[5 empty] | 2019-10-12 | 40 | 6835 | 2539 | -60 | 0 | 0 | 2599 | 1950.6183 | 1950.6183 | 1950.6183 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -68.6499 | 1881.9684 | -2750 | -200 | -1068.0316 | 26.7% | 42.56% | 95% | 0% | 2599 | -60
[5 empty] | 2019-10-12 | 41 | 6835.5 | 2463 | -59 | 0 | 0 | 2522 | 1830.0082 | 1830.0082 | 1830.0082 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -67.5057 | 1762.5025 | -2750 | -200 | -1187.4975 | 29.69% | 42.56% | 95% | 0% | 2522 | -59
[5 empty] | 2019-10-12 | 42 | 6836 | 2371 | -59 | 0 | 0 | 2430 | 1685.9027 | 1685.9027 | 1685.9027 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -67.5057 | 1618.397 | -2750 | -200 | -1331.603 | 33.29% | 42.56% | 95% | 0% | 2430 | -59
[5 empty] | 2019-10-12 | 43 | 6836.5 | 2290 | -58 | 0 | 0 | 2348 | 1557.4608 | 1557.4608 | 1557.4608 | 746.0841 | 780 | 200 | 1726.0841 | 43.15% | 95% | 0% | -66.3616 | 1491.0993 | -2750 | -200 | -1458.9007 | 36.47% | 42.56% | 95% | 0% | 2348 | -58
[5 empty] | 2019-10-12 | 44 | 6837 | 2200 | -57 | 0 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 744.5177 | 780 | 200 | 1724.5177 | 43.11% | 95% | 0% | -65.2174 | 1349.7043 | -2750 | -200 | -1600.2957 | 40.01% | 42.55% | 95% | 0% | 2257 | -57
[5 empty] | 2019-10-12 | 45 | 6837.5 | 2089 | -55 | 0 | 0 | 2144 | 1237.9225 | 1237.9225 | 1237.9225 | 744.5177 | 780 | 200 | 1724.5177 | 43.11% | 95% | 0% | -62.9291 | 1174.9934 | -2750 | -200 | -1775.0066 | 44.38% | 42.54% | 95% | 0% | 2144 | -55
[5 empty] | 2019-10-12 | 46 | 6838 | 2002 | -53 | 0 | 0 | 2055 | 1098.5161 | 1098.5161 | 1098.5161 | 744.5177 | 780 | 200 | 1724.5177 | 43.11% | 95% | 0% | -60.6407 | 1037.8753 | -2750 | -200 | -1912.1247 | 47.8% | 42.54% | 95% | 0% | 2055 | -53
[5 empty] | 2019-10-12 | 47 | 6838.5 | 1894 | -52 | 0 | 0 | 1946 | 927.7824 | 927.7824 | 927.7824 | 744.5177 | 780 | 200 | 1724.5177 | 43.11% | 95% | 0% | -59.4966 | 868.2858 | -2750 | -200 | -2081.7142 | 52.04% | 42.54% | 95% | 0% | 1946 | -52
[5 empty] | 2019-10-12 | 48 | 6839 | 1800 | -50 | 0 | 0 | 1850 | 777.4114 | 777.4114 | 777.4114 | 744.5177 | 780 | 200 | 1724.5177 | 43.11% | 95% | 0% | -57.2082 | 720.2031 | -2750 | -200 | -2229.7969 | 55.74% | 42.53% | 95% | 0% | 1850 | -50
[5 empty] | 2019-10-13 | 1 | 6839.5 | 1717 | -50 | 0 | 0 | 1767 | 647.4031 | 647.4031 | 647.4031 | 744.5177 | 780 | 200 | 1724.5177 | 43.11% | 95% | 0% | -57.2082 | 590.1949 | -2750 | -200 | -2359.8051 | 59% | 42.52% | 95% | 0% | 1767 | -50
[5 empty] | 2019-10-13 | 2 | 6840 | 1677 | -49 | 0 | 0 | 1726 | 583.1822 | 583.1822 | 583.1822 | 744.5177 | 780 | 200 | 1724.5177 | 43.11% | 95% | 0% | -56.0641 | 527.1181 | -2750 | -200 | -2422.8819 | 60.57% | 42.5% | 95% | 0% | 1726 | -49
[5 empty] | 2019-10-13 | 3 | 6840.5 | 1666 | -48 | 0 | 0 | 1714 | 564.3858 | 564.3858 | 564.3858 | 744.5177 | 780 | 200 | 1724.5177 | 43.11% | 95% | 0% | -54.9199 | 509.4659 | -2750 | -200 | -2440.5341 | 61.01% | 42.5% | 95% | 0% | 1714 | -48
[5 empty] | 2019-10-13 | 4 | 6841 | 1665 | -46 | 0 | 0 | 1711 | 559.6867 | 559.6867 | 559.6867 | 744.5177 | 780 | 200 | 1724.5177 | 43.11% | 95% | 0% | -52.6316 | 507.0551 | -2750 | -200 | -2442.9449 | 61.07% | 42.5% | 95% | 0% | 1711 | -46
[5 empty] | 2019-10-13 | 5 | 6841.5 | 1647 | -46 | 0 | 0 | 1693 | 531.4922 | 531.4922 | 531.4922 | 744.5177 | 780 | 200 | 1724.5177 | 43.11% | 95% | 0% | -52.6316 | 478.8606 | -2750 | -200 | -2471.1394 | 61.78% | 42.48% | 95% | 0% | 1693 | -46
[5 empty] | 2019-10-13 | 6 | 6842 | 1614 | -45 | 0 | 0 | 1659 | 478.2358 | 478.2358 | 478.2358 | 742.9514 | 780 | 200 | 1722.9514 | 43.07% | 95% | 0% | -51.4874 | 426.7484 | -2750 | -200 | -2523.2516 | 63.08% | 42.48% | 95% | 0% | 1659 | -45
[5 empty] | 2019-10-13 | 7 | 6842.5 | 1584 | -45 | 0 | 0 | 1629 | 431.2448 | 431.2448 | 431.2448 | 742.9514 | 780 | 200 | 1722.9514 | 43.07% | 95% | 0% | -51.4874 | 379.7574 | -2750 | -200 | -2570.2426 | 64.26% | 42.47% | 95% | 0% | 1629 | -45
[5 empty] | 2019-10-13 | 8 | 6843 | 1567 | -45 | 0 | 0 | 1612 | 404.6167 | 404.6167 | 404.6167 | 742.9514 | 780 | 200 | 1722.9514 | 43.07% | 95% | 0% | -51.4874 | 353.1292 | -2750 | -200 | -2596.8708 | 64.92% | 42.46% | 95% | 0% | 1612 | -45
[5 empty] | 2019-10-13 | 9 | 6843.5 | 1531 | -47 | 0 | 0 | 1578 | 351.3603 | 351.3603 | 351.3603 | 742.9514 | 780 | 200 | 1722.9514 | 43.07% | 95% | 0% | -53.7757 | 297.5845 | -2750 | -200 | -2652.4155 | 66.31% | 42.46% | 95% | 0% | 1578 | -47
[5 empty] | 2019-10-13 | 10 | 6844 | 1520 | -48 | 0 | 0 | 1568 | 335.6966 | 335.6966 | 335.6966 | 742.9514 | 780 | 200 | 1722.9514 | 43.07% | 95% | 0% | -54.9199 | 280.7767 | -2750 | -200 | -2669.2233 | 66.73% | 42.45% | 95% | 0% | 1568 | -48
[5 empty] | 2019-10-13 | 11 | 6844.5 | 1544 | -50 | 0 | 0 | 1594 | 376.4221 | 376.4221 | 376.4221 | 742.9514 | 780 | 200 | 1722.9514 | 43.07% | 95% | 0% | -57.2082 | 319.2139 | -2750 | -200 | -2630.7861 | 65.77% | 42.43% | 95% | 0% | 1594 | -50
[5 empty] | 2019-10-13 | 12 | 6845 | 1559 | -52 | 0 | 0 | 1611 | 403.0503 | 403.0503 | 403.0503 | 742.9514 | 780 | 200 | 1722.9514 | 43.07% | 95% | 0% | -59.4966 | 343.5537 | -2750 | -200 | -2606.4463 | 65.16% | 42.43% | 95% | 0% | 1611 | -52
[5 empty] | 2019-10-13 | 13 | 6845.5 | 1625 | -53 | 1 | 0 | 1678 | 507.9967 | 507.9967 | 507.9967 | 742.9514 | 780 | 200 | 1722.9514 | 43.07% | 95% | 0% | -60.6407 | 447.356 | -3550 | -400 | -3502.644 | 87.57% | 42.42% | 95% | 0% | 1678 | -53
[5 empty] | 2019-10-13 | 14 | 6846 | 1688 | -54 | 1 | 0 | 1742 | 608.244 | 608.244 | 608.244 | 742.9514 | 780 | 200 | 1722.9514 | 43.07% | 95% | 0% | -61.7849 | 546.4591 | -3550 | -400 | -3403.5409 | 85.09% | 42.42% | 95% | 0% | 1742 | -54
[5 empty] | 2019-10-13 | 15 | 6846.5 | 1774 | -56 | 1 | 0 | 1830 | 746.0841 | 746.0841 | 746.0841 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -64.0732 | 682.0109 | -3550 | -400 | -3267.9891 | 81.7% | 42.42% | 95% | 0% | 1830 | -56
[5 empty] | 2019-10-13 | 16 | 6847 | 1835 | -57 | 1 | 0 | 1892 | 843.1987 | 843.1987 | 843.1987 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -65.2174 | 777.9813 | -3550 | -400 | -3172.0187 | 79.3% | 42.42% | 95% | 0% | 1892 | -57
[5 empty] | 2019-10-13 | 17 | 6847.5 | 1959 | -62 | 1 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -70.9382 | 974.3215 | -3550 | -400 | -2975.6785 | 74.39% | 42.41% | 95% | 0% | 2021 | -62
[5 empty] | 2019-10-13 | 18 | 6848 | 2056 | -73 | 1 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -83.524 | 1130.903 | -3550 | -400 | -2819.097 | 70.48% | 42.41% | 95% | 0% | 2129 | -73
[5 empty] | 2019-10-13 | 19 | 6848.5 | 2174 | -86 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -98.3982 | 1321.2226 | -3550 | -400 | -2628.7774 | 65.72% | 42.4% | 95% | 0% | 2260 | -86
[5 empty] | 2019-10-13 | 20 | 6849 | 2247 | -99 | 1 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -113.2723 | 1441.0558 | -3550 | -400 | -2508.9442 | 62.72% | 42.4% | 95% | 0% | 2346 | -99
[5 empty] | 2019-10-13 | 21 | 6849.5 | 2296 | -110 | 1 | 0 | 2406 | 1648.31 | 1648.31 | 1648.31 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -125.8581 | 1522.4519 | -3550 | -400 | -2427.5481 | 60.69% | 42.4% | 95% | 0% | 2406 | -110
[5 empty] | 2019-10-13 | 22 | 6850 | 2293 | -122 | 1 | 0 | 2415 | 1662.4073 | 1662.4073 | 1662.4073 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -139.5881 | 1522.8192 | -3550 | -400 | -2427.1808 | 60.68% | 42.38% | 95% | 0% | 2415 | -122
[5 empty] | 2019-10-13 | 23 | 6850.5 | 2315 | -136 | 1 | 0 | 2451 | 1718.7964 | 1718.7964 | 1718.7964 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -155.6064 | 1563.19 | -3550 | -400 | -2386.81 | 59.67% | 42.38% | 95% | 0% | 2451 | -136
[5 empty] | 2019-10-13 | 24 | 6851 | 2317 | -151 | 1 | 0 | 2468 | 1745.4246 | 1745.4246 | 1745.4246 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -172.7689 | 1572.6557 | -3550 | -400 | -2377.3443 | 59.43% | 42.37% | 95% | 0% | 2468 | -151
[5 empty] | 2019-10-13 | 25 | 6851.5 | 2284 | -169 | 1 | 0 | 2453 | 1721.9291 | 1721.9291 | 1721.9291 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -193.3638 | 1528.5653 | -3550 | -400 | -2421.4347 | 60.54% | 42.37% | 95% | 0% | 2453 | -169
[5 empty] | 2019-10-13 | 26 | 6852 | 2271 | -187 | 1 | 0 | 2458 | 1729.7609 | 1729.7609 | 1729.7609 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -213.9588 | 1515.8021 | -3550 | -400 | -2434.1979 | 60.85% | 42.36% | 95% | 0% | 2458 | -187
[5 empty] | 2019-10-13 | 27 | 6852.5 | 2213 | -203 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 741.385 | 780 | 200 | 1721.385 | 43.03% | 95% | 0% | -232.2654 | 1431.7082 | -3550 | -400 | -2518.2918 | 62.96% | 42.35% | 95% | 0% | 2416 | -203
[5 empty] | 2019-10-13 | 28 | 6853 | 2140 | -224 | 1 | 0 | 2364 | 1582.5227 | 1582.5227 | 1582.5227 | 739.8186 | 780 | 200 | 1719.8186 | 43% | 95% | 0% | -256.2929 | 1326.2298 | -3550 | -400 | -2623.7702 | 65.59% | 42.35% | 95% | 0% | 2364 | -224
[5 empty] | 2019-10-13 | 29 | 6853.5 | 2099 | -244 | 1 | 0 | 2343 | 1549.629 | 1549.629 | 1549.629 | 739.8186 | 780 | 200 | 1719.8186 | 43% | 95% | 0% | -279.1762 | 1270.4528 | -3550 | -400 | -2679.5472 | 66.99% | 42.34% | 95% | 0% | 2343 | -244
[5 empty] | 2019-10-13 | 30 | 6854 | 2057 | -246 | 1 | 0 | 2303 | 1486.9744 | 1486.9744 | 1486.9744 | 739.8186 | 780 | 200 | 1719.8186 | 43% | 95% | 0% | -281.4645 | 1205.5099 | -3550 | -400 | -2744.4901 | 68.61% | 42.34% | 95% | 0% | 2303 | -246
[5 empty] | 2019-10-13 | 31 | 6854.5 | 2053 | -242 | 1 | 0 | 2295 | 1474.4435 | 1474.4435 | 1474.4435 | 739.8186 | 780 | 200 | 1719.8186 | 43% | 95% | 0% | -276.8879 | 1197.5557 | -3550 | -400 | -2752.4443 | 68.81% | 42.34% | 95% | 0% | 2295 | -242
[5 empty] | 2019-10-13 | 32 | 6855 | 2073 | -244 | 1 | 0 | 2317 | 1508.9035 | 1508.9035 | 1508.9035 | 739.8186 | 780 | 200 | 1719.8186 | 43% | 95% | 0% | -279.1762 | 1229.7273 | -3550 | -400 | -2720.2727 | 68.01% | 42.32% | 95% | 0% | 2317 | -244
[5 empty] | 2019-10-13 | 33 | 6855.5 | 2144 | -227 | 1 | 0 | 2371 | 1593.4872 | 1593.4872 | 1593.4872 | 739.8186 | 780 | 200 | 1719.8186 | 43% | 95% | 0% | -259.7254 | 1333.7618 | -3550 | -400 | -2616.2382 | 65.41% | 42.3% | 95% | 0% | 2371 | -227
[5 empty] | 2019-10-13 | 34 | 6856 | 2249 | -205 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 739.8186 | 780 | 200 | 1719.8186 | 43% | 95% | 0% | -234.5538 | 1488.9417 | -3550 | -400 | -2461.0583 | 61.53% | 42.3% | 95% | 0% | 2454 | -205
[5 empty] | 2019-10-13 | 35 | 6856.5 | 2388 | -155 | 1 | 0 | 2543 | 1862.9019 | 1862.9019 | 1862.9019 | 738.2523 | 780 | 200 | 1718.2523 | 42.96% | 95% | 0% | -177.3455 | 1685.5564 | -3550 | -400 | -2264.4436 | 56.61% | 42.29% | 95% | 0% | 2543 | -155
[5 empty] | 2019-10-13 | 36 | 6857 | 2518 | -110 | 1 | 0 | 2628 | 1996.0429 | 1996.0429 | 1996.0429 | 738.2523 | 780 | 200 | 1718.2523 | 42.96% | 95% | 0% | -125.8581 | 1870.1847 | -3550 | -400 | -2079.8153 | 52% | 42.29% | 95% | 0% | 2628 | -110
[5 empty] | 2019-10-13 | 37 | 6857.5 | 2595 | -89 | 1 | 0 | 2684 | 2083.7593 | 2083.7593 | 2083.7593 | 738.2523 | 780 | 200 | 1718.2523 | 42.96% | 95% | 0% | -101.8307 | 1981.9286 | -3550 | -400 | -1968.0714 | 49.2% | 42.29% | 95% | 0% | 2684 | -89
[5 empty] | 2019-10-13 | 38 | 6858 | 2674 | -86 | 1 | 0 | 2760 | 2202.803 | 2202.803 | 2202.803 | 738.2523 | 780 | 200 | 1718.2523 | 42.96% | 95% | 0% | -98.3982 | 2104.4048 | -3550 | -400 | -1845.5952 | 46.14% | 42.29% | 95% | 0% | 2760 | -86
[5 empty] | 2019-10-13 | 39 | 6858.5 | 2640 | -86 | 0 | 0 | 2726 | 2149.5466 | 2149.5466 | 2149.5466 | 738.2523 | 780 | 200 | 1718.2523 | 42.96% | 95% | 0% | -98.3982 | 2051.1484 | -2750 | -200 | -898.8516 | 22.47% | 42.28% | 95% | 0% | 2726 | -86
[5 empty] | 2019-10-13 | 40 | 6859 | 2543 | -86 | 0 | 0 | 2629 | 1997.6092 | 1997.6092 | 1997.6092 | 738.2523 | 780 | 200 | 1718.2523 | 42.96% | 95% | 0% | -98.3982 | 1899.2111 | -2750 | -200 | -1050.7889 | 26.27% | 42.28% | 95% | 0% | 2629 | -86
[5 empty] | 2019-10-13 | 41 | 6859.5 | 2458 | -85 | 0 | 0 | 2543 | 1862.9019 | 1862.9019 | 1862.9019 | 738.2523 | 780 | 200 | 1718.2523 | 42.96% | 95% | 0% | -97.254 | 1765.6479 | -2750 | -200 | -1184.3521 | 29.61% | 42.27% | 95% | 0% | 2543 | -85
[5 empty] | 2019-10-13 | 42 | 6860 | 2357 | -83 | 0 | 0 | 2440 | 1701.5664 | 1701.5664 | 1701.5664 | 738.2523 | 780 | 200 | 1718.2523 | 42.96% | 95% | 0% | -94.9657 | 1606.6007 | -2750 | -200 | -1343.3993 | 33.58% | 42.27% | 95% | 0% | 2440 | -83
[5 empty] | 2019-10-13 | 43 | 6860.5 | 2271 | -81 | 0 | 0 | 2352 | 1563.7263 | 1563.7263 | 1563.7263 | 738.2523 | 780 | 200 | 1718.2523 | 42.96% | 95% | 0% | -92.6773 | 1471.049 | -2750 | -200 | -1478.951 | 36.97% | 42.26% | 95% | 0% | 2352 | -81
[5 empty] | 2019-10-13 | 44 | 6861 | 2148 | -79 | 0 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 738.2523 | 780 | 200 | 1718.2523 | 42.96% | 95% | 0% | -90.389 | 1277.5417 | -2750 | -200 | -1672.4583 | 41.81% | 42.25% | 95% | 0% | 2227 | -79
[5 empty] | 2019-10-13 | 45 | 6861.5 | 2027 | -76 | 0 | 0 | 2103 | 1173.7016 | 1173.7016 | 1173.7016 | 738.2523 | 780 | 200 | 1718.2523 | 42.96% | 95% | 0% | -86.9565 | 1086.745 | -2750 | -200 | -1863.255 | 46.58% | 42.25% | 95% | 0% | 2103 | -76
[5 empty] | 2019-10-13 | 46 | 6862 | 1924 | -72 | 0 | 0 | 1996 | 1006.1006 | 1006.1006 | 1006.1006 | 738.2523 | 780 | 200 | 1718.2523 | 42.96% | 95% | 0% | -82.3799 | 923.7207 | -2750 | -200 | -2026.2793 | 50.66% | 42.25% | 95% | 0% | 1996 | -72
[5 empty] | 2019-10-13 | 47 | 6862.5 | 1812 | -67 | 0 | 0 | 1879 | 822.8359 | 822.8359 | 822.8359 | 736.6859 | 780 | 200 | 1716.6859 | 42.92% | 95% | 0% | -76.659 | 746.1769 | -2750 | -200 | -2203.8231 | 55.1% | 42.25% | 95% | 0% | 1879 | -67
[5 empty] | 2019-10-13 | 48 | 6863 | 1727 | -63 | 0 | 0 | 1790 | 683.4295 | 683.4295 | 683.4295 | 736.6859 | 780 | 200 | 1716.6859 | 42.92% | 95% | 0% | -72.0824 | 611.3471 | -2750 | -200 | -2338.6529 | 58.47% | 42.25% | 95% | 0% | 1790 | -63
[5 empty] | 2019-10-14 | 1 | 6863.5 | 1657 | -58 | 0 | 0 | 1715 | 565.9522 | 565.9522 | 565.9522 | 736.6859 | 780 | 200 | 1716.6859 | 42.92% | 95% | 0% | -66.3616 | 499.5906 | -2750 | -200 | -2450.4094 | 61.26% | 42.23% | 95% | 0% | 1715 | -58
[5 empty] | 2019-10-14 | 2 | 6864 | 1626 | -53 | 0 | 0 | 1679 | 509.5631 | 509.5631 | 509.5631 | 736.6859 | 780 | 200 | 1716.6859 | 42.92% | 95% | 0% | -60.6407 | 448.9223 | -2750 | -200 | -2501.0777 | 62.53% | 42.22% | 95% | 0% | 1679 | -53
[5 empty] | 2019-10-14 | 3 | 6864.5 | 1623 | -51 | 0 | 0 | 1674 | 501.7312 | 501.7312 | 501.7312 | 736.6859 | 780 | 200 | 1716.6859 | 42.92% | 95% | 0% | -58.3524 | 443.3788 | -2750 | -200 | -2506.6212 | 62.67% | 42.22% | 95% | 0% | 1674 | -51
[5 empty] | 2019-10-14 | 4 | 6865 | 1648 | -48 | 0 | 0 | 1696 | 536.1913 | 536.1913 | 536.1913 | 736.6859 | 780 | 200 | 1716.6859 | 42.92% | 95% | 0% | -54.9199 | 481.2714 | -2750 | -200 | -2468.7286 | 61.72% | 42.22% | 95% | 0% | 1696 | -48
[5 empty] | 2019-10-14 | 5 | 6865.5 | 1643 | -48 | 0 | 0 | 1691 | 528.3594 | 528.3594 | 528.3594 | 736.6859 | 780 | 200 | 1716.6859 | 42.92% | 95% | 0% | -54.9199 | 473.4395 | -2750 | -200 | -2476.5605 | 61.91% | 42.21% | 95% | 0% | 1691 | -48
[5 empty] | 2019-10-14 | 6 | 6866 | 1619 | -47 | 0 | 0 | 1666 | 489.2003 | 489.2003 | 489.2003 | 736.6859 | 780 | 200 | 1716.6859 | 42.92% | 95% | 0% | -53.7757 | 435.4246 | -2750 | -200 | -2514.5754 | 62.86% | 42.19% | 95% | 0% | 1666 | -47
[5 empty] | 2019-10-14 | 7 | 6866.5 | 1601 | -46 | 0 | 0 | 1647 | 459.4394 | 459.4394 | 459.4394 | 736.6859 | 780 | 200 | 1716.6859 | 42.92% | 95% | 0% | -52.6316 | 406.8078 | -2750 | -200 | -2543.1922 | 63.58% | 42.19% | 95% | 0% | 1647 | -46
[5 empty] | 2019-10-14 | 8 | 6867 | 1596 | -45 | 0 | 0 | 1641 | 450.0412 | 450.0412 | 450.0412 | 736.6859 | 780 | 200 | 1716.6859 | 42.92% | 95% | 0% | -51.4874 | 398.5538 | -2750 | -200 | -2551.4462 | 63.79% | 42.19% | 95% | 0% | 1641 | -45
[5 empty] | 2019-10-14 | 9 | 6867.5 | 1599 | -45 | 0 | 0 | 1644 | 454.7403 | 454.7403 | 454.7403 | 736.6859 | 780 | 200 | 1716.6859 | 42.92% | 95% | 0% | -51.4874 | 403.2529 | -2750 | -200 | -2546.7471 | 63.67% | 42.17% | 95% | 0% | 1644 | -45
[5 empty] | 2019-10-14 | 10 | 6868 | 1611 | -44 | 0 | 0 | 1655 | 471.9703 | 471.9703 | 471.9703 | 735.1195 | 780 | 200 | 1715.1195 | 42.88% | 95% | 0% | -50.3432 | 421.6271 | -2750 | -200 | -2528.3729 | 63.21% | 42.17% | 95% | 0% | 1655 | -44
[5 empty] | 2019-10-14 | 11 | 6868.5 | 1656 | -45 | 0 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 735.1195 | 780 | 200 | 1715.1195 | 42.88% | 95% | 0% | -51.4874 | 492.5357 | -2750 | -200 | -2457.4643 | 61.44% | 42.15% | 95% | 0% | 1701 | -45
[5 empty] | 2019-10-14 | 12 | 6869 | 1759 | -46 | 0 | 0 | 1805 | 706.925 | 706.925 | 706.925 | 735.1195 | 780 | 200 | 1715.1195 | 42.88% | 95% | 0% | -52.6316 | 654.2934 | -2750 | -200 | -2295.7066 | 57.39% | 42.15% | 95% | 0% | 1805 | -46
[5 empty] | 2019-10-14 | 13 | 6869.5 | 1984 | -46 | 0 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 735.1195 | 780 | 200 | 1715.1195 | 42.88% | 95% | 0% | -52.6316 | 1006.7254 | -2750 | -200 | -1943.2746 | 48.58% | 42.13% | 95% | 0% | 2030 | -46
[5 empty] | 2019-10-14 | 14 | 6870 | 2218 | -47 | 0 | 0 | 2265 | 1427.4526 | 1427.4526 | 1427.4526 | 735.1195 | 780 | 200 | 1715.1195 | 42.88% | 95% | 0% | -53.7757 | 1373.6769 | -2750 | -200 | -1576.3231 | 39.41% | 42.12% | 95% | 0% | 2265 | -47
[5 empty] | 2019-10-14 | 15 | 6870.5 | 2500 | -48 | 0 | 0 | 2548 | 1870.7337 | 1870.7337 | 1870.7337 | 735.1195 | 780 | 200 | 1715.1195 | 42.88% | 95% | 0% | -54.9199 | 1815.8138 | -2750 | -200 | -1134.1862 | 28.35% | 42.11% | 95% | 0% | 2548 | -48
[5 empty] | 2019-10-14 | 16 | 6871 | 2621 | -49 | 0 | 0 | 2670 | 2061.8302 | 2061.8302 | 2061.8302 | 735.1195 | 780 | 200 | 1715.1195 | 42.88% | 95% | 0% | -56.0641 | 2005.7661 | -2750 | -200 | -944.2339 | 23.61% | 42.1% | 95% | 0% | 2670 | -49
[5 empty] | 2019-10-14 | 17 | 6871.5 | 2689 | -59 | 1 | 0 | 2748 | 2184.0066 | 2184.0066 | 2184.0066 | 733.5532 | 780 | 200 | 1713.5532 | 42.84% | 95% | 0% | -67.5057 | 2116.5009 | -3550 | -400 | -1833.4991 | 45.84% | 42.1% | 95% | 0% | 2748 | -59
[5 empty] | 2019-10-14 | 18 | 6872 | 2673 | -79 | 1 | 0 | 2752 | 2190.2721 | 2190.2721 | 2190.2721 | 733.5532 | 780 | 200 | 1713.5532 | 42.84% | 95% | 0% | -90.389 | 2099.883 | -3550 | -400 | -1850.117 | 46.25% | 42.1% | 95% | 0% | 2752 | -79
[5 empty] | 2019-10-14 | 19 | 6872.5 | 2677 | -109 | 1 | 0 | 2786 | 2243.5284 | 2243.5284 | 2243.5284 | 733.5532 | 780 | 200 | 1713.5532 | 42.84% | 95% | 0% | -124.714 | 2118.8145 | -3550 | -400 | -1831.1855 | 45.78% | 42.09% | 95% | 0% | 2786 | -109
[5 empty] | 2019-10-14 | 20 | 6873 | 2669 | -136 | 1 | 0 | 2805 | 2273.2894 | 2273.2894 | 2273.2894 | 733.5532 | 780 | 200 | 1713.5532 | 42.84% | 95% | 0% | -155.6064 | 2117.683 | -3550 | -400 | -1832.317 | 45.81% | 42.09% | 95% | 0% | 2805 | -136
[5 empty] | 2019-10-14 | 21 | 6873.5 | 2639 | -158 | 1 | 0 | 2797 | 2260.7585 | 2260.7585 | 2260.7585 | 733.5532 | 780 | 200 | 1713.5532 | 42.84% | 95% | 0% | -180.778 | 2079.9804 | -3550 | -400 | -1870.0196 | 46.75% | 42.09% | 95% | 0% | 2797 | -158
[5 empty] | 2019-10-14 | 22 | 6874 | 2613 | -176 | 1 | 0 | 2789 | 2248.2275 | 2248.2275 | 2248.2275 | 733.5532 | 780 | 200 | 1713.5532 | 42.84% | 95% | 0% | -201.373 | 2046.8545 | -3550 | -400 | -1903.1455 | 47.58% | 42.08% | 95% | 0% | 2789 | -176
[5 empty] | 2019-10-14 | 23 | 6874.5 | 2621 | -188 | 1 | 0 | 2809 | 2279.5548 | 2279.5548 | 2279.5548 | 733.5532 | 780 | 200 | 1713.5532 | 42.84% | 95% | 0% | -215.103 | 2064.4518 | -3550 | -400 | -1885.5482 | 47.14% | 42.08% | 95% | 0% | 2809 | -188
[5 empty] | 2019-10-14 | 24 | 6875 | 2633 | -187 | 1 | 0 | 2820 | 2296.7848 | 2296.7848 | 2296.7848 | 733.5532 | 780 | 200 | 1713.5532 | 42.84% | 95% | 0% | -213.9588 | 2082.826 | -3550 | -400 | -1867.174 | 46.68% | 42.07% | 95% | 0% | 2820 | -187
[5 empty] | 2019-10-14 | 25 | 6875.5 | 2654 | -185 | 1 | 0 | 2839 | 2326.5458 | 2326.5458 | 2326.5458 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -211.6705 | 2114.8753 | -3550 | -400 | -1835.1247 | 45.88% | 42.07% | 95% | 0% | 2839 | -185
[5 empty] | 2019-10-14 | 26 | 6876 | 2630 | -176 | 1 | 0 | 2806 | 2274.8557 | 2274.8557 | 2274.8557 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -201.373 | 2073.4827 | -3550 | -400 | -1876.5173 | 46.91% | 42.07% | 95% | 0% | 2806 | -176
[5 empty] | 2019-10-14 | 27 | 6876.5 | 2620 | -169 | 1 | 0 | 2789 | 2248.2275 | 2248.2275 | 2248.2275 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -193.3638 | 2054.8637 | -3550 | -400 | -1895.1363 | 47.38% | 42.07% | 95% | 0% | 2789 | -169
[5 empty] | 2019-10-14 | 28 | 6877 | 2607 | -168 | 1 | 0 | 2775 | 2226.2984 | 2226.2984 | 2226.2984 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -192.2197 | 2034.0788 | -3550 | -400 | -1915.9212 | 47.9% | 42.05% | 95% | 0% | 2775 | -168
[5 empty] | 2019-10-14 | 29 | 6877.5 | 2624 | -161 | 1 | 0 | 2785 | 2241.9621 | 2241.9621 | 2241.9621 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -184.2105 | 2057.7516 | -3550 | -400 | -1892.2484 | 47.31% | 42.05% | 95% | 0% | 2785 | -161
[5 empty] | 2019-10-14 | 30 | 6878 | 2632 | -149 | 1 | 0 | 2781 | 2235.6966 | 2235.6966 | 2235.6966 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -170.4805 | 2065.2161 | -3550 | -400 | -1884.7839 | 47.12% | 42.03% | 95% | 0% | 2781 | -149
[5 empty] | 2019-10-14 | 31 | 6878.5 | 2637 | -138 | 1 | 0 | 2775 | 2226.2984 | 2226.2984 | 2226.2984 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -157.8947 | 2068.4037 | -3550 | -400 | -1881.5963 | 47.04% | 42.03% | 95% | 0% | 2775 | -138
[5 empty] | 2019-10-14 | 32 | 6879 | 2675 | -126 | 1 | 0 | 2801 | 2267.0239 | 2267.0239 | 2267.0239 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -144.1648 | 2122.8591 | -3550 | -400 | -1827.1409 | 45.68% | 42.03% | 95% | 0% | 2801 | -126
[5 empty] | 2019-10-14 | 33 | 6879.5 | 2740 | -111 | 1 | 0 | 2851 | 2345.3421 | 2345.3421 | 2345.3421 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -127.0023 | 2218.3398 | -3550 | -400 | -1731.6602 | 43.29% | 42.02% | 95% | 0% | 2851 | -111
[5 empty] | 2019-10-14 | 34 | 6880 | 2837 | -96 | 1 | 0 | 2933 | 2473.784 | 2473.784 | 2473.784 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -109.8398 | 2363.9442 | -3550 | -400 | -1586.0558 | 39.65% | 42.01% | 95% | 0% | 2933 | -96
[5 empty] | 2019-10-14 | 35 | 6880.5 | 2919 | -88 | 1 | 0 | 3007 | 2589.695 | 2589.695 | 2589.695 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -100.6865 | 2489.0085 | -3550 | -400 | -1460.9915 | 36.52% | 42% | 95% | 0% | 3007 | -88
[5 empty] | 2019-10-14 | 36 | 6881 | 2962 | -83 | 1 | 0 | 3045 | 2649.2168 | 2649.2168 | 2649.2168 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -94.9657 | 2554.2511 | -3550 | -400 | -1395.7489 | 34.89% | 41.99% | 95% | 0% | 3045 | -83
[5 empty] | 2019-10-14 | 37 | 6881.5 | 2990 | -83 | 1 | 0 | 3073 | 2693.075 | 2693.075 | 2693.075 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -94.9657 | 2598.1093 | -3550 | -400 | -1351.8907 | 33.8% | 41.99% | 95% | 0% | 3073 | -83
[5 empty] | 2019-10-14 | 38 | 6882 | 3025 | -85 | 1 | 0 | 3110 | 2751.0305 | 2751.0305 | 2751.0305 | 731.9868 | 780 | 200 | 1711.9868 | 42.8% | 95% | 0% | -97.254 | 2653.7765 | -3550 | -400 | -1296.2235 | 32.41% | 41.97% | 95% | 0% | 3110 | -85
[5 empty] | 2019-10-14 | 39 | 6882.5 | 2969 | -84 | 0 | 0 | 3053 | 2661.7477 | 2661.7477 | 2661.7477 | 730.4204 | 780 | 200 | 1710.4204 | 42.76% | 95% | 0% | -96.1098 | 2565.6379 | -2750 | -200 | -384.3621 | 9.609% | 41.96% | 95% | 0% | 3053 | -84
[5 empty] | 2019-10-14 | 40 | 6883 | 2888 | -84 | 0 | 0 | 2972 | 2534.8722 | 2534.8722 | 2534.8722 | 730.4204 | 780 | 200 | 1710.4204 | 42.76% | 95% | 0% | -96.1098 | 2438.7624 | -2750 | -200 | -511.2376 | 12.78% | 41.95% | 95% | 0% | 2972 | -84
[5 empty] | 2019-10-14 | 41 | 6883.5 | 2786 | -83 | 0 | 0 | 2869 | 2373.5367 | 2373.5367 | 2373.5367 | 730.4204 | 780 | 200 | 1710.4204 | 42.76% | 95% | 0% | -94.9657 | 2278.571 | -2750 | -200 | -671.429 | 16.79% | 41.94% | 95% | 0% | 2869 | -83
[5 empty] | 2019-10-14 | 42 | 6884 | 2664 | -83 | 0 | 0 | 2747 | 2182.4402 | 2182.4402 | 2182.4402 | 730.4204 | 780 | 200 | 1710.4204 | 42.76% | 95% | 0% | -94.9657 | 2087.4746 | -2750 | -200 | -862.5254 | 21.56% | 41.94% | 95% | 0% | 2747 | -83
[5 empty] | 2019-10-14 | 43 | 6884.5 | 2528 | -82 | 0 | 0 | 2610 | 1967.8483 | 1967.8483 | 1967.8483 | 730.4204 | 780 | 200 | 1710.4204 | 42.76% | 95% | 0% | -93.8215 | 1874.0268 | -2750 | -200 | -1075.9732 | 26.9% | 41.94% | 95% | 0% | 2610 | -82
[5 empty] | 2019-10-14 | 44 | 6885 | 2393 | -82 | 0 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 730.4204 | 780 | 200 | 1710.4204 | 42.76% | 95% | 0% | -93.8215 | 1662.5676 | -2750 | -200 | -1287.4324 | 32.19% | 41.93% | 95% | 0% | 2475 | -82
[5 empty] | 2019-10-14 | 45 | 6885.5 | 2237 | -81 | 0 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 730.4204 | 780 | 200 | 1710.4204 | 42.76% | 95% | 0% | -92.6773 | 1417.7926 | -2750 | -200 | -1532.2074 | 38.31% | 41.93% | 95% | 0% | 2318 | -81
[5 empty] | 2019-10-14 | 46 | 6886 | 2084 | -80 | 0 | 0 | 2164 | 1269.2498 | 1269.2498 | 1269.2498 | 730.4204 | 780 | 200 | 1710.4204 | 42.76% | 95% | 0% | -91.5332 | 1177.7166 | -2750 | -200 | -1772.2834 | 44.31% | 41.93% | 95% | 0% | 2164 | -80
[5 empty] | 2019-10-14 | 47 | 6886.5 | 1927 | -78 | 0 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 730.4204 | 780 | 200 | 1710.4204 | 42.76% | 95% | 0% | -89.2449 | 930.953 | -2750 | -200 | -2019.047 | 50.48% | 41.91% | 95% | 0% | 2005 | -78
[5 empty] | 2019-10-14 | 48 | 6887 | 1814 | -75 | 0 | 0 | 1889 | 838.4996 | 838.4996 | 838.4996 | 730.4204 | 780 | 200 | 1710.4204 | 42.76% | 95% | 0% | -85.8124 | 752.6872 | -2750 | -200 | -2197.3128 | 54.93% | 41.9% | 95% | 0% | 1889 | -75
[5 empty] | 2019-10-15 | 1 | 6887.5 | 1728 | -73 | 0 | 0 | 1801 | 700.6595 | 700.6595 | 700.6595 | 730.4204 | 780 | 200 | 1710.4204 | 42.76% | 95% | 0% | -83.524 | 617.1355 | -2750 | -200 | -2332.8645 | 58.32% | 41.9% | 95% | 0% | 1801 | -73
[5 empty] | 2019-10-15 | 2 | 6888 | 1685 | -70 | 0 | 0 | 1755 | 628.6068 | 628.6068 | 628.6068 | 728.8541 | 780 | 200 | 1708.8541 | 42.72% | 95% | 0% | -80.0915 | 548.5152 | -2750 | -200 | -2401.4848 | 60.04% | 41.9% | 95% | 0% | 1755 | -70
[5 empty] | 2019-10-15 | 3 | 6888.5 | 1678 | -69 | 0 | 0 | 1747 | 616.0758 | 616.0758 | 616.0758 | 728.8541 | 780 | 200 | 1708.8541 | 42.72% | 95% | 0% | -78.9474 | 537.1285 | -2750 | -200 | -2412.8715 | 60.32% | 41.89% | 95% | 0% | 1747 | -69
[5 empty] | 2019-10-15 | 4 | 6889 | 1696 | -67 | 0 | 0 | 1763 | 641.1377 | 641.1377 | 641.1377 | 728.8541 | 780 | 200 | 1708.8541 | 42.72% | 95% | 0% | -76.659 | 564.4786 | -2750 | -200 | -2385.5214 | 59.64% | 41.86% | 95% | 0% | 1763 | -67
[5 empty] | 2019-10-15 | 5 | 6889.5 | 1698 | -66 | 0 | 0 | 1764 | 642.704 | 642.704 | 642.704 | 728.8541 | 780 | 200 | 1708.8541 | 42.72% | 95% | 0% | -75.5149 | 567.1892 | -2750 | -200 | -2382.8108 | 59.57% | 41.86% | 95% | 0% | 1764 | -66
[5 empty] | 2019-10-15 | 6 | 6890 | 1671 | -65 | 0 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 728.8541 | 780 | 200 | 1708.8541 | 42.72% | 95% | 0% | -74.3707 | 524.4751 | -2750 | -200 | -2425.5249 | 60.64% | 41.85% | 95% | 0% | 1736 | -65
[5 empty] | 2019-10-15 | 7 | 6890.5 | 1650 | -62 | 0 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 728.8541 | 780 | 200 | 1708.8541 | 42.72% | 95% | 0% | -70.9382 | 490.3149 | -2750 | -200 | -2459.6851 | 61.49% | 41.85% | 95% | 0% | 1712 | -62
[5 empty] | 2019-10-15 | 8 | 6891 | 1638 | -60 | 0 | 0 | 1698 | 539.324 | 539.324 | 539.324 | 728.8541 | 780 | 200 | 1708.8541 | 42.72% | 95% | 0% | -68.6499 | 470.6741 | -2750 | -200 | -2479.3259 | 61.98% | 41.84% | 95% | 0% | 1698 | -60
[5 empty] | 2019-10-15 | 9 | 6891.5 | 1643 | -60 | 0 | 0 | 1703 | 547.1558 | 547.1558 | 547.1558 | 728.8541 | 780 | 200 | 1708.8541 | 42.72% | 95% | 0% | -68.6499 | 478.5059 | -2750 | -200 | -2471.4941 | 61.79% | 41.83% | 95% | 0% | 1703 | -60
[5 empty] | 2019-10-15 | 10 | 6892 | 1659 | -59 | 0 | 0 | 1718 | 570.6513 | 570.6513 | 570.6513 | 728.8541 | 780 | 200 | 1708.8541 | 42.72% | 95% | 0% | -67.5057 | 503.1456 | -2750 | -200 | -2446.8544 | 61.17% | 41.83% | 95% | 0% | 1718 | -59
[5 empty] | 2019-10-15 | 11 | 6892.5 | 1727 | -57 | 0 | 0 | 1784 | 674.0313 | 674.0313 | 674.0313 | 728.8541 | 780 | 200 | 1708.8541 | 42.72% | 95% | 0% | -65.2174 | 608.8139 | -2750 | -200 | -2341.1861 | 58.53% | 41.83% | 95% | 0% | 1784 | -57
[5 empty] | 2019-10-15 | 12 | 6893 | 1832 | -54 | 1 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 727.2877 | 780 | 200 | 1707.2877 | 42.68% | 95% | 0% | -61.7849 | 772.0156 | -3550 | -400 | -3177.9844 | 79.45% | 41.83% | 95% | 0% | 1886 | -54
[5 empty] | 2019-10-15 | 13 | 6893.5 | 2048 | -53 | 1 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 727.2877 | 780 | 200 | 1707.2877 | 42.68% | 95% | 0% | -60.6407 | 1109.9281 | -3550 | -400 | -2840.0719 | 71% | 41.83% | 95% | 0% | 2101 | -53
[5 empty] | 2019-10-15 | 14 | 6894 | 2295 | -51 | 1 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 727.2877 | 780 | 200 | 1707.2877 | 42.68% | 95% | 0% | -58.3524 | 1495.9757 | -3550 | -400 | -2454.0243 | 61.35% | 41.82% | 95% | 0% | 2346 | -51
[5 empty] | 2019-10-15 | 15 | 6894.5 | 2574 | -48 | 1 | 0 | 2622 | 1986.6447 | 1986.6447 | 1986.6447 | 727.2877 | 780 | 200 | 1707.2877 | 42.68% | 95% | 0% | -54.9199 | 1931.7248 | -3550 | -400 | -2018.2752 | 50.46% | 41.81% | 95% | 0% | 2622 | -48
[5 empty] | 2019-10-15 | 16 | 6895 | 2691 | -46 | 1 | 0 | 2737 | 2166.7766 | 2166.7766 | 2166.7766 | 727.2877 | 780 | 200 | 1707.2877 | 42.68% | 95% | 0% | -52.6316 | 2114.145 | -3550 | -400 | -1835.855 | 45.9% | 41.81% | 95% | 0% | 2737 | -46
[5 empty] | 2019-10-15 | 17 | 6895.5 | 2729 | -56 | 1 | 0 | 2785 | 2241.9621 | 2241.9621 | 2241.9621 | 727.2877 | 780 | 200 | 1707.2877 | 42.68% | 95% | 0% | -64.0732 | 2177.8889 | -3550 | -400 | -1772.1111 | 44.3% | 41.8% | 95% | 0% | 2785 | -56
[5 empty] | 2019-10-15 | 18 | 6896 | 2690 | -75 | 1 | 0 | 2765 | 2210.6348 | 2210.6348 | 2210.6348 | 727.2877 | 780 | 200 | 1707.2877 | 42.68% | 95% | 0% | -85.8124 | 2124.8224 | -3550 | -400 | -1825.1776 | 45.63% | 41.8% | 95% | 0% | 2765 | -75
[5 empty] | 2019-10-15 | 19 | 6896.5 | 2700 | -96 | 1 | 0 | 2796 | 2259.1921 | 2259.1921 | 2259.1921 | 727.2877 | 780 | 200 | 1707.2877 | 42.68% | 95% | 0% | -109.8398 | 2149.3523 | -3550 | -400 | -1800.6477 | 45.02% | 41.79% | 95% | 0% | 2796 | -96
[5 empty] | 2019-10-15 | 20 | 6897 | 2650 | -119 | 1 | 0 | 2769 | 2216.9002 | 2216.9002 | 2216.9002 | 727.2877 | 780 | 200 | 1707.2877 | 42.68% | 95% | 0% | -136.1556 | 2080.7446 | -3550 | -400 | -1869.2554 | 46.73% | 41.79% | 95% | 0% | 2769 | -119
[5 empty] | 2019-10-15 | 21 | 6897.5 | 2573 | -145 | 1 | 0 | 2718 | 2137.0157 | 2137.0157 | 2137.0157 | 727.2877 | 780 | 200 | 1707.2877 | 42.68% | 95% | 0% | -165.9039 | 1971.1118 | -3550 | -400 | -1978.8882 | 49.47% | 41.79% | 95% | 0% | 2718 | -145
[5 empty] | 2019-10-15 | 22 | 6898 | 2524 | -166 | 1 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -189.9314 | 1903.2261 | -3550 | -400 | -2046.7739 | 51.17% | 41.79% | 95% | 0% | 2690 | -166
[5 empty] | 2019-10-15 | 23 | 6898.5 | 2482 | -190 | 1 | 0 | 2672 | 2064.9629 | 2064.9629 | 2064.9629 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -217.3913 | 1847.5716 | -3550 | -400 | -2102.4284 | 52.56% | 41.77% | 95% | 0% | 2672 | -190
[5 empty] | 2019-10-15 | 24 | 6899 | 2451 | -220 | 1 | 0 | 2671 | 2063.3965 | 2063.3965 | 2063.3965 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -251.7162 | 1811.6803 | -3550 | -400 | -2138.3197 | 53.46% | 41.77% | 95% | 0% | 2671 | -220
[5 empty] | 2019-10-15 | 25 | 6899.5 | 2421 | -242 | 1 | 0 | 2663 | 2050.8656 | 2050.8656 | 2050.8656 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -276.8879 | 1773.9778 | -3550 | -400 | -2176.0222 | 54.4% | 41.76% | 95% | 0% | 2663 | -242
[5 empty] | 2019-10-15 | 26 | 6900 | 2395 | -260 | 1 | 0 | 2655 | 2038.3347 | 2038.3347 | 2038.3347 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -297.4828 | 1740.8519 | -3550 | -400 | -2209.1481 | 55.23% | 41.76% | 95% | 0% | 2655 | -260
[5 empty] | 2019-10-15 | 27 | 6900.5 | 2342 | -299 | 1 | 0 | 2641 | 2016.4056 | 2016.4056 | 2016.4056 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -342.1053 | 1674.3003 | -3550 | -400 | -2275.6997 | 56.89% | 41.75% | 95% | 0% | 2641 | -299
[5 empty] | 2019-10-15 | 28 | 6901 | 2325 | -288 | 1 | 0 | 2613 | 1972.5474 | 1972.5474 | 1972.5474 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -329.5195 | 1643.028 | -3550 | -400 | -2306.972 | 57.67% | 41.75% | 95% | 0% | 2613 | -288
[5 empty] | 2019-10-15 | 29 | 6901.5 | 2305 | -302 | 1 | 0 | 2607 | 1963.1492 | 1963.1492 | 1963.1492 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -345.5378 | 1617.6115 | -3550 | -400 | -2332.3885 | 58.31% | 41.74% | 95% | 0% | 2607 | -302
[5 empty] | 2019-10-15 | 30 | 6902 | 2294 | -294 | 1 | 0 | 2588 | 1933.3883 | 1933.3883 | 1933.3883 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -336.3844 | 1597.0039 | -3550 | -400 | -2352.9961 | 58.82% | 41.74% | 95% | 0% | 2588 | -294
[5 empty] | 2019-10-15 | 31 | 6902.5 | 2336 | -252 | 1 | 0 | 2588 | 1933.3883 | 1933.3883 | 1933.3883 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -288.3295 | 1645.0588 | -3550 | -400 | -2304.9412 | 57.62% | 41.72% | 95% | 0% | 2588 | -252
[5 empty] | 2019-10-15 | 32 | 6903 | 2411 | -223 | 1 | 0 | 2634 | 2005.4411 | 2005.4411 | 2005.4411 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -255.1487 | 1750.2923 | -3550 | -400 | -2199.7077 | 54.99% | 41.72% | 95% | 0% | 2634 | -223
[5 empty] | 2019-10-15 | 33 | 6903.5 | 2528 | -174 | 1 | 0 | 2702 | 2111.9538 | 2111.9538 | 2111.9538 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -199.0847 | 1912.8692 | -3550 | -400 | -2037.1308 | 50.93% | 41.7% | 95% | 0% | 2702 | -174
[5 empty] | 2019-10-15 | 34 | 6904 | 2639 | -135 | 1 | 0 | 2774 | 2224.7321 | 2224.7321 | 2224.7321 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -154.4622 | 2070.2698 | -3550 | -400 | -1879.7302 | 46.99% | 41.7% | 95% | 0% | 2774 | -135
[5 empty] | 2019-10-15 | 35 | 6904.5 | 2761 | -100 | 1 | 0 | 2861 | 2361.0058 | 2361.0058 | 2361.0058 | 725.7214 | 780 | 200 | 1705.7214 | 42.64% | 95% | 0% | -114.4165 | 2246.5893 | -3550 | -400 | -1703.4107 | 42.59% | 41.7% | 95% | 0% | 2861 | -100
[5 empty] | 2019-10-15 | 36 | 6905 | 2843 | -70 | 1 | 0 | 2913 | 2442.4567 | 2442.4567 | 2442.4567 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -80.0915 | 2362.3652 | -3550 | -400 | -1587.6348 | 39.69% | 41.69% | 95% | 0% | 2913 | -70
[5 empty] | 2019-10-15 | 37 | 6905.5 | 2933 | -64 | 1 | 0 | 2997 | 2574.0313 | 2574.0313 | 2574.0313 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -73.2265 | 2500.8048 | -3550 | -400 | -1449.1952 | 36.23% | 41.69% | 95% | 0% | 2997 | -64
[5 empty] | 2019-10-15 | 38 | 6906 | 2993 | -67 | 1 | 0 | 3060 | 2672.7123 | 2672.7123 | 2672.7123 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -76.659 | 2596.0532 | -3550 | -400 | -1353.9468 | 33.85% | 41.68% | 95% | 0% | 3060 | -67
[5 empty] | 2019-10-15 | 39 | 6906.5 | 2953 | -71 | 0 | 0 | 3024 | 2616.3232 | 2616.3232 | 2616.3232 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -81.2357 | 2535.0875 | -2750 | -200 | -414.9125 | 10.37% | 41.68% | 95% | 0% | 3024 | -71
[5 empty] | 2019-10-15 | 40 | 6907 | 2897 | -75 | 0 | 0 | 2972 | 2534.8722 | 2534.8722 | 2534.8722 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -85.8124 | 2449.0599 | -2750 | -200 | -500.9401 | 12.52% | 41.66% | 95% | 0% | 2972 | -75
[5 empty] | 2019-10-15 | 41 | 6907.5 | 2773 | -79 | 0 | 0 | 2852 | 2346.9085 | 2346.9085 | 2346.9085 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -90.389 | 2256.5195 | -2750 | -200 | -693.4805 | 17.34% | 41.65% | 95% | 0% | 2852 | -79
[5 empty] | 2019-10-15 | 42 | 6908 | 2666 | -82 | 0 | 0 | 2748 | 2184.0066 | 2184.0066 | 2184.0066 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -93.8215 | 2090.1851 | -2750 | -200 | -859.8149 | 21.5% | 41.64% | 95% | 0% | 2748 | -82
[5 empty] | 2019-10-15 | 43 | 6908.5 | 2536 | -86 | 0 | 0 | 2622 | 1986.6447 | 1986.6447 | 1986.6447 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -98.3982 | 1888.2465 | -2750 | -200 | -1061.7535 | 26.54% | 41.63% | 95% | 0% | 2622 | -86
[5 empty] | 2019-10-15 | 44 | 6909 | 2383 | -89 | 0 | 0 | 2472 | 1751.69 | 1751.69 | 1751.69 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -101.8307 | 1649.8594 | -2750 | -200 | -1300.1406 | 32.5% | 41.63% | 95% | 0% | 2472 | -89
[5 empty] | 2019-10-15 | 45 | 6909.5 | 2212 | -92 | 0 | 0 | 2304 | 1488.5408 | 1488.5408 | 1488.5408 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -105.2632 | 1383.2777 | -2750 | -200 | -1566.7223 | 39.17% | 41.63% | 95% | 0% | 2304 | -92
[5 empty] | 2019-10-15 | 46 | 6910 | 2043 | -96 | 0 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -109.8398 | 1120.2509 | -2750 | -200 | -1829.7491 | 45.74% | 41.61% | 95% | 0% | 2139 | -96
[5 empty] | 2019-10-15 | 47 | 6910.5 | 1887 | -99 | 1 | 0 | 1986 | 990.4369 | 990.4369 | 990.4369 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -113.2723 | 877.1646 | -3550 | -400 | -3072.8354 | 76.82% | 41.61% | 95% | 0% | 1986 | -99
[5 empty] | 2019-10-15 | 48 | 6911 | 1751 | -101 | 1 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 724.155 | 780 | 200 | 1704.155 | 42.6% | 95% | 0% | -115.5606 | 664.9835 | -3550 | -400 | -3285.0165 | 82.13% | 41.61% | 95% | 0% | 1852 | -101
[5 empty] | 2019-10-16 | 1 | 6911.5 | 1665 | -104 | 1 | 0 | 1769 | 650.5359 | 650.5359 | 650.5359 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -118.9931 | 531.5427 | -3550 | -400 | -3418.4573 | 85.46% | 41.6% | 95% | 0% | 1769 | -104
[5 empty] | 2019-10-16 | 2 | 6912 | 1611 | -107 | 1 | 0 | 1718 | 570.6513 | 570.6513 | 570.6513 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -122.4256 | 448.2256 | -3550 | -400 | -3501.7744 | 87.54% | 41.6% | 95% | 0% | 1718 | -107
[5 empty] | 2019-10-16 | 3 | 6912.5 | 1595 | -110 | 1 | 0 | 1705 | 550.2885 | 550.2885 | 550.2885 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -125.8581 | 424.4304 | -3550 | -400 | -3525.5696 | 88.14% | 41.59% | 95% | 0% | 1705 | -110
[5 empty] | 2019-10-16 | 4 | 6913 | 1612 | -112 | 1 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -128.1465 | 451.903 | -3550 | -400 | -3498.097 | 87.45% | 41.59% | 95% | 0% | 1724 | -112
[5 empty] | 2019-10-16 | 5 | 6913.5 | 1597 | -114 | 1 | 0 | 1711 | 559.6867 | 559.6867 | 559.6867 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -130.4348 | 429.2519 | -3550 | -400 | -3520.7481 | 88.02% | 41.58% | 95% | 0% | 1711 | -114
[5 empty] | 2019-10-16 | 6 | 6914 | 1561 | -116 | 1 | 0 | 1677 | 506.4303 | 506.4303 | 506.4303 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -132.7231 | 373.7072 | -3550 | -400 | -3576.2928 | 89.41% | 41.58% | 95% | 0% | 1677 | -116
[5 empty] | 2019-10-16 | 7 | 6914.5 | 1534 | -119 | 1 | 0 | 1653 | 468.8376 | 468.8376 | 468.8376 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -136.1556 | 332.682 | -3550 | -400 | -3617.318 | 90.43% | 41.58% | 95% | 0% | 1653 | -119
[5 empty] | 2019-10-16 | 8 | 6915 | 1505 | -122 | 1 | 0 | 1627 | 428.1121 | 428.1121 | 428.1121 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -139.5881 | 288.524 | -3550 | -400 | -3661.476 | 91.54% | 41.58% | 95% | 0% | 1627 | -122
[5 empty] | 2019-10-16 | 9 | 6915.5 | 1494 | -126 | 1 | 0 | 1620 | 417.1476 | 417.1476 | 417.1476 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -144.1648 | 272.9828 | -3550 | -400 | -3677.0172 | 91.93% | 41.58% | 95% | 0% | 1620 | -126
[5 empty] | 2019-10-16 | 10 | 6916 | 1506 | -129 | 1 | 0 | 1635 | 440.643 | 440.643 | 440.643 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -147.5973 | 293.0458 | -3550 | -400 | -3656.9542 | 91.42% | 41.57% | 95% | 0% | 1635 | -129
[5 empty] | 2019-10-16 | 11 | 6916.5 | 1549 | -133 | 1 | 0 | 1682 | 514.2622 | 514.2622 | 514.2622 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -152.1739 | 362.0882 | -3550 | -400 | -3587.9118 | 89.7% | 41.56% | 95% | 0% | 1682 | -133
[5 empty] | 2019-10-16 | 12 | 6917 | 1632 | -136 | 1 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -155.6064 | 493.3631 | -3550 | -400 | -3456.6369 | 86.42% | 41.56% | 95% | 0% | 1768 | -136
[5 empty] | 2019-10-16 | 13 | 6917.5 | 1849 | -138 | 1 | 0 | 1987 | 992.0033 | 992.0033 | 992.0033 | 722.5886 | 780 | 200 | 1702.5886 | 42.56% | 95% | 0% | -157.8947 | 834.1086 | -3550 | -400 | -3115.8914 | 77.9% | 41.56% | 95% | 0% | 1987 | -138
[5 empty] | 2019-10-16 | 14 | 6918 | 2082 | -139 | 1 | 0 | 2221 | 1358.5326 | 1358.5326 | 1358.5326 | 721.0223 | 780 | 200 | 1701.0223 | 42.53% | 95% | 0% | -159.0389 | 1199.4937 | -3550 | -400 | -2750.5063 | 68.76% | 41.55% | 95% | 0% | 2221 | -139
[5 empty] | 2019-10-16 | 15 | 6918.5 | 2352 | -137 | 1 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 721.0223 | 780 | 200 | 1701.0223 | 42.53% | 95% | 0% | -156.7506 | 1621.5676 | -3550 | -400 | -2328.4324 | 58.21% | 41.54% | 95% | 0% | 2489 | -137
[5 empty] | 2019-10-16 | 16 | 6919 | 2475 | -135 | 1 | 0 | 2610 | 1967.8483 | 1967.8483 | 1967.8483 | 721.0223 | 780 | 200 | 1701.0223 | 42.53% | 95% | 0% | -154.4622 | 1813.3861 | -3550 | -400 | -2136.6139 | 53.42% | 41.54% | 95% | 0% | 2610 | -135
[5 empty] | 2019-10-16 | 17 | 6919.5 | 2525 | -140 | 1 | 0 | 2665 | 2053.9984 | 2053.9984 | 2053.9984 | 721.0223 | 780 | 200 | 1701.0223 | 42.53% | 95% | 0% | -160.1831 | 1893.8153 | -3550 | -400 | -2056.1847 | 51.4% | 41.54% | 95% | 0% | 2665 | -140
[5 empty] | 2019-10-16 | 18 | 6920 | 2520 | -156 | 1 | 0 | 2676 | 2071.2284 | 2071.2284 | 2071.2284 | 721.0223 | 780 | 200 | 1701.0223 | 42.53% | 95% | 0% | -178.4897 | 1892.7387 | -3550 | -400 | -2057.2613 | 51.43% | 41.53% | 95% | 0% | 2676 | -156
[5 empty] | 2019-10-16 | 19 | 6920.5 | 2509 | -181 | 1 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 721.0223 | 780 | 200 | 1701.0223 | 42.53% | 95% | 0% | -207.0938 | 1886.0636 | -3550 | -400 | -2063.9364 | 51.6% | 41.53% | 95% | 0% | 2690 | -181
[5 empty] | 2019-10-16 | 20 | 6921 | 2456 | -223 | 1 | 0 | 2679 | 2075.9275 | 2075.9275 | 2075.9275 | 721.0223 | 780 | 200 | 1701.0223 | 42.53% | 95% | 0% | -255.1487 | 1820.7787 | -3550 | -400 | -2129.2213 | 53.23% | 41.53% | 95% | 0% | 2679 | -223
[5 empty] | 2019-10-16 | 21 | 6921.5 | 2373 | -269 | 1 | 0 | 2642 | 2017.972 | 2017.972 | 2017.972 | 721.0223 | 780 | 200 | 1701.0223 | 42.53% | 95% | 0% | -307.7803 | 1710.1916 | -3550 | -400 | -2239.8084 | 56% | 41.52% | 95% | 0% | 2642 | -269
[5 empty] | 2019-10-16 | 22 | 6922 | 2291 | -305 | 1 | 0 | 2596 | 1945.9192 | 1945.9192 | 1945.9192 | 721.0223 | 780 | 200 | 1701.0223 | 42.53% | 95% | 0% | -348.9703 | 1596.949 | -3550 | -400 | -2353.051 | 58.83% | 41.51% | 95% | 0% | 2596 | -305
[5 empty] | 2019-10-16 | 23 | 6922.5 | 2244 | -335 | 1 | 0 | 2579 | 1919.291 | 1919.291 | 1919.291 | 721.0223 | 780 | 200 | 1701.0223 | 42.53% | 95% | 0% | -383.2952 | 1535.9958 | -3550 | -400 | -2414.0042 | 60.35% | 41.5% | 95% | 0% | 2579 | -335
[5 empty] | 2019-10-16 | 24 | 6923 | 2182 | -376 | 1 | 0 | 2558 | 1886.3974 | 1886.3974 | 1886.3974 | 721.0223 | 780 | 200 | 1701.0223 | 42.53% | 95% | 0% | -430.2059 | 1456.1914 | -3550 | -400 | -2493.8086 | 62.35% | 41.5% | 95% | 0% | 2558 | -376
[5 empty] | 2019-10-16 | 25 | 6923.5 | 2171 | -385 | 1 | 0 | 2556 | 1883.2646 | 1883.2646 | 1883.2646 | 719.4559 | 780 | 200 | 1699.4559 | 42.49% | 95% | 0% | -440.5034 | 1442.7612 | -3550 | -400 | -2507.2388 | 62.68% | 41.49% | 95% | 0% | 2556 | -385
[5 empty] | 2019-10-16 | 26 | 6924 | 2111 | -401 | 1 | 0 | 2512 | 1814.3446 | 1814.3446 | 1814.3446 | 719.4559 | 780 | 200 | 1699.4559 | 42.49% | 95% | 0% | -458.8101 | 1355.5345 | -3550 | -400 | -2594.4655 | 64.86% | 41.49% | 95% | 0% | 2512 | -401
[5 empty] | 2019-10-16 | 27 | 6924.5 | 2047 | -423 | 1 | 0 | 2470 | 1748.5573 | 1748.5573 | 1748.5573 | 719.4559 | 780 | 200 | 1699.4559 | 42.49% | 95% | 0% | -483.9817 | 1264.5756 | -3550 | -400 | -2685.4244 | 67.14% | 41.49% | 95% | 0% | 2470 | -423
[5 empty] | 2019-10-16 | 28 | 6925 | 2029 | -414 | 1 | 0 | 2443 | 1706.2655 | 1706.2655 | 1706.2655 | 719.4559 | 780 | 200 | 1699.4559 | 42.49% | 95% | 0% | -473.6842 | 1232.5812 | -3550 | -400 | -2717.4188 | 67.94% | 41.49% | 95% | 0% | 2443 | -414
[5 empty] | 2019-10-16 | 29 | 6925.5 | 2005 | -413 | 1 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 719.4559 | 780 | 200 | 1699.4559 | 42.49% | 95% | 0% | -472.54 | 1194.5663 | -3550 | -400 | -2755.4337 | 68.89% | 41.48% | 95% | 0% | 2418 | -413
[5 empty] | 2019-10-16 | 30 | 6926 | 2001 | -396 | 1 | 0 | 2397 | 1634.2127 | 1634.2127 | 1634.2127 | 719.4559 | 780 | 200 | 1699.4559 | 42.49% | 95% | 0% | -453.0892 | 1181.1235 | -3550 | -400 | -2768.8765 | 69.22% | 41.48% | 95% | 0% | 2397 | -396
[5 empty] | 2019-10-16 | 31 | 6926.5 | 2060 | -354 | 1 | 0 | 2414 | 1660.8409 | 1660.8409 | 1660.8409 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -405.0343 | 1255.8066 | -3550 | -400 | -2694.1934 | 67.35% | 41.47% | 95% | 0% | 2414 | -354
[5 empty] | 2019-10-16 | 32 | 6927 | 2153 | -316 | 1 | 0 | 2469 | 1746.9909 | 1746.9909 | 1746.9909 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -361.5561 | 1385.4349 | -3550 | -400 | -2564.5651 | 64.11% | 41.47% | 95% | 0% | 2469 | -316
[5 empty] | 2019-10-16 | 33 | 6927.5 | 2290 | -259 | 1 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -296.3387 | 1575.9614 | -3550 | -400 | -2374.0386 | 59.35% | 41.47% | 95% | 0% | 2549 | -259
[5 empty] | 2019-10-16 | 34 | 6928 | 2439 | -199 | 1 | 0 | 2638 | 2011.7065 | 2011.7065 | 2011.7065 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -227.6888 | 1784.0177 | -3550 | -400 | -2165.9823 | 54.15% | 41.46% | 95% | 0% | 2638 | -199
[5 empty] | 2019-10-16 | 35 | 6928.5 | 2613 | -144 | 1 | 0 | 2757 | 2198.1039 | 2198.1039 | 2198.1039 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -164.7597 | 2033.3441 | -3550 | -400 | -1916.6559 | 47.92% | 41.46% | 95% | 0% | 2757 | -144
[5 empty] | 2019-10-16 | 36 | 6929 | 2735 | -92 | 1 | 0 | 2827 | 2307.7494 | 2307.7494 | 2307.7494 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -105.2632 | 2202.4862 | -3550 | -400 | -1747.5138 | 43.69% | 41.45% | 95% | 0% | 2827 | -92
[5 empty] | 2019-10-16 | 37 | 6929.5 | 2846 | -72 | 1 | 0 | 2918 | 2450.2885 | 2450.2885 | 2450.2885 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -82.3799 | 2367.9087 | -3550 | -400 | -1582.0913 | 39.55% | 41.45% | 95% | 0% | 2918 | -72
[5 empty] | 2019-10-16 | 38 | 6930 | 2951 | -69 | 1 | 0 | 3020 | 2610.0577 | 2610.0577 | 2610.0577 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -78.9474 | 2531.1103 | -3550 | -400 | -1418.8897 | 35.47% | 41.44% | 95% | 0% | 3020 | -69
[5 empty] | 2019-10-16 | 39 | 6930.5 | 2908 | -69 | 0 | 0 | 2977 | 2542.704 | 2542.704 | 2542.704 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -78.9474 | 2463.7567 | -2750 | -200 | -486.2433 | 12.16% | 41.43% | 95% | 0% | 2977 | -69
[5 empty] | 2019-10-16 | 40 | 6931 | 2846 | -69 | 0 | 0 | 2915 | 2445.5894 | 2445.5894 | 2445.5894 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -78.9474 | 2366.6421 | -2750 | -200 | -583.3579 | 14.58% | 41.41% | 95% | 0% | 2915 | -69
[5 empty] | 2019-10-16 | 41 | 6931.5 | 2774 | -69 | 0 | 0 | 2843 | 2332.8112 | 2332.8112 | 2332.8112 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -78.9474 | 2253.8638 | -2750 | -200 | -696.1362 | 17.4% | 41.4% | 95% | 0% | 2843 | -69
[5 empty] | 2019-10-16 | 42 | 6932 | 2686 | -68 | 0 | 0 | 2754 | 2193.4048 | 2193.4048 | 2193.4048 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -77.8032 | 2115.6016 | -2750 | -200 | -834.3984 | 20.86% | 41.4% | 95% | 0% | 2754 | -68
[5 empty] | 2019-10-16 | 43 | 6932.5 | 2547 | -68 | 1 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 717.8895 | 780 | 200 | 1697.8895 | 42.45% | 95% | 0% | -77.8032 | 1897.8769 | -3550 | -400 | -2052.1231 | 51.3% | 41.39% | 95% | 0% | 2615 | -68
[5 empty] | 2019-10-16 | 44 | 6933 | 2398 | -68 | 1 | 0 | 2466 | 1742.2918 | 1742.2918 | 1742.2918 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -77.8032 | 1664.4886 | -3550 | -400 | -2285.5114 | 57.14% | 41.39% | 95% | 0% | 2466 | -68
[5 empty] | 2019-10-16 | 45 | 6933.5 | 2271 | -67 | 1 | 0 | 2338 | 1541.7972 | 1541.7972 | 1541.7972 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -76.659 | 1465.1382 | -3550 | -400 | -2484.8618 | 62.12% | 41.38% | 95% | 0% | 2338 | -67
[5 empty] | 2019-10-16 | 46 | 6934 | 2118 | -67 | 1 | 0 | 2185 | 1302.1434 | 1302.1434 | 1302.1434 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -76.659 | 1225.4844 | -3550 | -400 | -2724.5156 | 68.11% | 41.37% | 95% | 0% | 2185 | -67
[5 empty] | 2019-10-16 | 47 | 6934.5 | 1976 | -67 | 1 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -76.659 | 1003.0607 | -3550 | -400 | -2946.9393 | 73.67% | 41.36% | 95% | 0% | 2043 | -67
[5 empty] | 2019-10-16 | 48 | 6935 | 1860 | -67 | 1 | 0 | 1927 | 898.0214 | 898.0214 | 898.0214 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -76.659 | 821.3624 | -3550 | -400 | -3128.6376 | 78.22% | 41.36% | 95% | 0% | 1927 | -67
[5 empty] | 2019-10-17 | 1 | 6935.5 | 1769 | -67 | 1 | 0 | 1836 | 755.4823 | 755.4823 | 755.4823 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -76.659 | 678.8232 | -3550 | -400 | -3271.1768 | 81.78% | 41.35% | 95% | 0% | 1836 | -67
[5 empty] | 2019-10-17 | 2 | 6936 | 1715 | -66 | 1 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -75.5149 | 593.8174 | -3550 | -400 | -3356.1826 | 83.9% | 41.35% | 95% | 0% | 1781 | -66
[5 empty] | 2019-10-17 | 3 | 6936.5 | 1705 | -67 | 1 | 0 | 1772 | 655.235 | 655.235 | 655.235 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -76.659 | 578.5759 | -3550 | -400 | -3371.4241 | 84.29% | 41.35% | 95% | 0% | 1772 | -67
[5 empty] | 2019-10-17 | 4 | 6937 | 1729 | -68 | 1 | 0 | 1797 | 694.3941 | 694.3941 | 694.3941 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -77.8032 | 616.5909 | -3550 | -400 | -3333.4091 | 83.34% | 41.35% | 95% | 0% | 1797 | -68
[5 empty] | 2019-10-17 | 5 | 6937.5 | 1720 | -69 | 1 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -78.9474 | 602.9158 | -3550 | -400 | -3347.0842 | 83.68% | 41.33% | 95% | 0% | 1789 | -69
[5 empty] | 2019-10-17 | 6 | 6938 | 1695 | -70 | 1 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -80.0915 | 564.1789 | -3550 | -400 | -3385.8211 | 84.65% | 41.32% | 95% | 0% | 1765 | -70
[5 empty] | 2019-10-17 | 7 | 6938.5 | 1663 | -70 | 1 | 0 | 1733 | 594.1467 | 594.1467 | 594.1467 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -80.0915 | 514.0552 | -3550 | -400 | -3435.9448 | 85.9% | 41.32% | 95% | 0% | 1733 | -70
[5 empty] | 2019-10-17 | 8 | 6939 | 1656 | -70 | 1 | 0 | 1726 | 583.1822 | 583.1822 | 583.1822 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -80.0915 | 503.0907 | -3550 | -400 | -3446.9093 | 86.17% | 41.32% | 95% | 0% | 1726 | -70
[5 empty] | 2019-10-17 | 9 | 6939.5 | 1646 | -71 | 1 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -81.2357 | 487.8492 | -3550 | -400 | -3462.1508 | 86.55% | 41.31% | 95% | 0% | 1717 | -71
[5 empty] | 2019-10-17 | 10 | 6940 | 1653 | -72 | 1 | 0 | 1725 | 581.6158 | 581.6158 | 581.6158 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -82.3799 | 499.236 | -3550 | -400 | -3450.764 | 86.27% | 41.31% | 95% | 0% | 1725 | -72
[5 empty] | 2019-10-17 | 11 | 6940.5 | 1708 | -73 | 1 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -83.524 | 585.8082 | -3550 | -400 | -3364.1918 | 84.1% | 41.31% | 95% | 0% | 1781 | -73
[5 empty] | 2019-10-17 | 12 | 6941 | 1813 | -74 | 1 | 0 | 1887 | 835.3669 | 835.3669 | 835.3669 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -84.6682 | 750.6987 | -3550 | -400 | -3199.3013 | 79.98% | 41.3% | 95% | 0% | 1887 | -74
[5 empty] | 2019-10-17 | 13 | 6941.5 | 2030 | -76 | 1 | 0 | 2106 | 1178.4007 | 1178.4007 | 1178.4007 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -86.9565 | 1091.4441 | -3550 | -400 | -2858.5559 | 71.46% | 41.3% | 95% | 0% | 2106 | -76
[5 empty] | 2019-10-17 | 14 | 6942 | 2253 | -77 | 1 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -88.1007 | 1441.1656 | -3550 | -400 | -2508.8344 | 62.72% | 41.29% | 95% | 0% | 2330 | -77
[5 empty] | 2019-10-17 | 15 | 6942.5 | 2518 | -79 | 1 | 0 | 2597 | 1947.4856 | 1947.4856 | 1947.4856 | 716.3232 | 780 | 200 | 1696.3232 | 42.41% | 95% | 0% | -90.389 | 1857.0966 | -3550 | -400 | -2092.9034 | 52.32% | 41.27% | 95% | 0% | 2597 | -79
[5 empty] | 2019-10-17 | 16 | 6943 | 2624 | -86 | 1 | 0 | 2710 | 2124.4847 | 2124.4847 | 2124.4847 | 714.7568 | 780 | 200 | 1694.7568 | 42.37% | 95% | 0% | -98.3982 | 2026.0866 | -3550 | -400 | -1923.9134 | 48.1% | 41.26% | 95% | 0% | 2710 | -86
[5 empty] | 2019-10-17 | 17 | 6943.5 | 2651 | -124 | 1 | 0 | 2775 | 2226.2984 | 2226.2984 | 2226.2984 | 714.7568 | 780 | 200 | 1694.7568 | 42.37% | 95% | 0% | -141.8764 | 2084.422 | -3550 | -400 | -1865.578 | 46.64% | 41.26% | 95% | 0% | 2775 | -124
[5 empty] | 2019-10-17 | 18 | 6944 | 2551 | -188 | 1 | 0 | 2739 | 2169.9093 | 2169.9093 | 2169.9093 | 714.7568 | 780 | 200 | 1694.7568 | 42.37% | 95% | 0% | -215.103 | 1954.8063 | -3550 | -400 | -1995.1937 | 49.88% | 41.25% | 95% | 0% | 2739 | -188
[5 empty] | 2019-10-17 | 19 | 6944.5 | 2457 | -251 | 1 | 0 | 2708 | 2121.352 | 2121.352 | 2121.352 | 714.7568 | 780 | 200 | 1694.7568 | 42.37% | 95% | 0% | -287.1854 | 1834.1667 | -3550 | -400 | -2115.8333 | 52.9% | 41.24% | 95% | 0% | 2708 | -251
[5 empty] | 2019-10-17 | 20 | 6945 | 2364 | -319 | 1 | 0 | 2683 | 2082.1929 | 2082.1929 | 2082.1929 | 714.7568 | 780 | 200 | 1694.7568 | 42.37% | 95% | 0% | -364.9886 | 1717.2044 | -3550 | -400 | -2232.7956 | 55.82% | 41.23% | 95% | 0% | 2683 | -319
[5 empty] | 2019-10-17 | 21 | 6945.5 | 2242 | -372 | 1 | 0 | 2614 | 1974.1138 | 1974.1138 | 1974.1138 | 714.7568 | 780 | 200 | 1694.7568 | 42.37% | 95% | 0% | -425.6293 | 1548.4845 | -3550 | -400 | -2401.5155 | 60.04% | 41.23% | 95% | 0% | 2614 | -372
[5 empty] | 2019-10-17 | 22 | 6946 | 2145 | -419 | 1 | 0 | 2564 | 1895.7955 | 1895.7955 | 1895.7955 | 713.1904 | 780 | 200 | 1693.1904 | 42.33% | 95% | 0% | -479.405 | 1416.3905 | -3550 | -400 | -2533.6095 | 63.34% | 41.23% | 95% | 0% | 2564 | -419
[5 empty] | 2019-10-17 | 23 | 6946.5 | 2076 | -448 | 1 | 0 | 2524 | 1833.141 | 1833.141 | 1833.141 | 713.1904 | 780 | 200 | 1693.1904 | 42.33% | 95% | 0% | -512.5858 | 1320.5552 | -3550 | -400 | -2629.4448 | 65.74% | 41.22% | 95% | 0% | 2524 | -448
[5 empty] | 2019-10-17 | 24 | 6947 | 2026 | -463 | 1 | 0 | 2489 | 1778.3182 | 1778.3182 | 1778.3182 | 713.1904 | 780 | 200 | 1693.1904 | 42.33% | 95% | 0% | -529.7483 | 1248.5699 | -3550 | -400 | -2701.4301 | 67.54% | 41.2% | 95% | 0% | 2489 | -463
[5 empty] | 2019-10-17 | 25 | 6947.5 | 2030 | -457 | 1 | 0 | 2487 | 1775.1855 | 1775.1855 | 1775.1855 | 713.1904 | 780 | 200 | 1693.1904 | 42.33% | 95% | 0% | -522.8833 | 1252.3022 | -3550 | -400 | -2697.6978 | 67.44% | 41.2% | 95% | 0% | 2487 | -457
[5 empty] | 2019-10-17 | 26 | 6948 | 2045 | -440 | 1 | 0 | 2485 | 1772.0528 | 1772.0528 | 1772.0528 | 713.1904 | 780 | 200 | 1693.1904 | 42.33% | 95% | 0% | -503.4325 | 1268.6203 | -3550 | -400 | -2681.3797 | 67.03% | 41.2% | 95% | 0% | 2485 | -440
[5 empty] | 2019-10-17 | 27 | 6948.5 | 2048 | -425 | 1 | 0 | 2473 | 1753.2564 | 1753.2564 | 1753.2564 | 713.1904 | 780 | 200 | 1693.1904 | 42.33% | 95% | 0% | -486.27 | 1266.9864 | -3550 | -400 | -2683.0136 | 67.08% | 41.2% | 95% | 0% | 2473 | -425
[5 empty] | 2019-10-17 | 28 | 6949 | 2058 | -394 | 1 | 0 | 2452 | 1720.3627 | 1720.3627 | 1720.3627 | 713.1904 | 780 | 200 | 1693.1904 | 42.33% | 95% | 0% | -450.8009 | 1269.5618 | -3550 | -400 | -2680.4382 | 67.01% | 41.18% | 95% | 0% | 2452 | -394
[5 empty] | 2019-10-17 | 29 | 6949.5 | 2099 | -373 | 1 | 0 | 2472 | 1751.69 | 1751.69 | 1751.69 | 713.1904 | 780 | 200 | 1693.1904 | 42.33% | 95% | 0% | -426.7735 | 1324.9166 | -3550 | -400 | -2625.0834 | 65.63% | 41.18% | 95% | 0% | 2472 | -373
[5 empty] | 2019-10-17 | 30 | 6950 | 2137 | -353 | 1 | 0 | 2490 | 1779.8846 | 1779.8846 | 1779.8846 | 713.1904 | 780 | 200 | 1693.1904 | 42.33% | 95% | 0% | -403.8902 | 1375.9944 | -3550 | -400 | -2574.0056 | 64.35% | 41.18% | 95% | 0% | 2490 | -353
[5 empty] | 2019-10-17 | 31 | 6950.5 | 2169 | -326 | 1 | 0 | 2495 | 1787.7164 | 1787.7164 | 1787.7164 | 711.6241 | 780 | 200 | 1691.6241 | 42.29% | 95% | 0% | -372.9977 | 1414.7187 | -3550 | -400 | -2535.2813 | 63.38% | 41.16% | 95% | 0% | 2495 | -326
[5 empty] | 2019-10-17 | 32 | 6951 | 2270 | -297 | 1 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 711.6241 | 780 | 200 | 1691.6241 | 42.29% | 95% | 0% | -339.8169 | 1560.6777 | -3550 | -400 | -2389.3223 | 59.73% | 41.16% | 95% | 0% | 2567 | -297
[5 empty] | 2019-10-17 | 33 | 6951.5 | 2408 | -252 | 1 | 0 | 2660 | 2046.1665 | 2046.1665 | 2046.1665 | 711.6241 | 780 | 200 | 1691.6241 | 42.29% | 95% | 0% | -288.3295 | 1757.837 | -3550 | -400 | -2192.163 | 54.8% | 41.16% | 95% | 0% | 2660 | -252
[5 empty] | 2019-10-17 | 34 | 6952 | 2530 | -211 | 1 | 0 | 2741 | 2173.042 | 2173.042 | 2173.042 | 711.6241 | 780 | 200 | 1691.6241 | 42.29% | 95% | 0% | -241.4188 | 1931.6233 | -3550 | -400 | -2018.3767 | 50.46% | 41.15% | 95% | 0% | 2741 | -211
[5 empty] | 2019-10-17 | 35 | 6952.5 | 2675 | -153 | 1 | 0 | 2828 | 2309.3157 | 2309.3157 | 2309.3157 | 711.6241 | 780 | 200 | 1691.6241 | 42.29% | 95% | 0% | -175.0572 | 2134.2585 | -3550 | -400 | -1815.7415 | 45.39% | 41.14% | 95% | 0% | 2828 | -153
[5 empty] | 2019-10-17 | 36 | 6953 | 2762 | -128 | 1 | 0 | 2890 | 2406.4303 | 2406.4303 | 2406.4303 | 711.6241 | 780 | 200 | 1691.6241 | 42.29% | 95% | 0% | -146.4531 | 2259.9772 | -3550 | -400 | -1690.0228 | 42.25% | 41.13% | 95% | 0% | 2890 | -128
[5 empty] | 2019-10-17 | 37 | 6953.5 | 2854 | -125 | 1 | 0 | 2979 | 2545.8368 | 2545.8368 | 2545.8368 | 711.6241 | 780 | 200 | 1691.6241 | 42.29% | 95% | 0% | -143.0206 | 2402.8162 | -3550 | -400 | -1547.1838 | 38.68% | 41.11% | 95% | 0% | 2979 | -125
[5 empty] | 2019-10-17 | 38 | 6954 | 2919 | -126 | 1 | 0 | 3045 | 2649.2168 | 2649.2168 | 2649.2168 | 711.6241 | 780 | 200 | 1691.6241 | 42.29% | 95% | 0% | -144.1648 | 2505.0521 | -3550 | -400 | -1444.9479 | 36.12% | 41.11% | 95% | 0% | 3045 | -126
[5 empty] | 2019-10-17 | 39 | 6954.5 | 2891 | -126 | 0 | 0 | 3017 | 2605.3586 | 2605.3586 | 2605.3586 | 711.6241 | 780 | 200 | 1691.6241 | 42.29% | 95% | 0% | -144.1648 | 2461.1939 | -2750 | -200 | -488.8061 | 12.22% | 41.1% | 95% | 0% | 3017 | -126
[5 empty] | 2019-10-17 | 40 | 6955 | 2807 | -126 | 0 | 0 | 2933 | 2473.784 | 2473.784 | 2473.784 | 711.6241 | 780 | 200 | 1691.6241 | 42.29% | 95% | 0% | -144.1648 | 2329.6192 | -2750 | -200 | -620.3808 | 15.51% | 41.08% | 95% | 0% | 2933 | -126
[5 empty] | 2019-10-17 | 41 | 6955.5 | 2701 | -125 | 0 | 0 | 2826 | 2306.183 | 2306.183 | 2306.183 | 711.6241 | 780 | 200 | 1691.6241 | 42.29% | 95% | 0% | -143.0206 | 2163.1624 | -2750 | -200 | -786.8376 | 19.67% | 41.07% | 95% | 0% | 2826 | -125
[5 empty] | 2019-10-17 | 42 | 6956 | 2590 | -123 | 0 | 0 | 2713 | 2129.1838 | 2129.1838 | 2129.1838 | 711.6241 | 780 | 200 | 1691.6241 | 42.29% | 95% | 0% | -140.7323 | 1988.4516 | -2750 | -200 | -961.5484 | 24.04% | 41.06% | 95% | 0% | 2713 | -123
[5 empty] | 2019-10-17 | 43 | 6956.5 | 2470 | -123 | 0 | 0 | 2593 | 1941.2201 | 1941.2201 | 1941.2201 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -140.7323 | 1800.4878 | -2750 | -200 | -1149.5122 | 28.74% | 41.06% | 95% | 0% | 2593 | -123
[5 empty] | 2019-10-17 | 44 | 6957 | 2319 | -122 | 0 | 0 | 2441 | 1703.1327 | 1703.1327 | 1703.1327 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -139.5881 | 1563.5446 | -2750 | -200 | -1386.4554 | 34.66% | 41.06% | 95% | 0% | 2441 | -122
[5 empty] | 2019-10-17 | 45 | 6957.5 | 2169 | -120 | 0 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -137.2998 | 1327.7456 | -2750 | -200 | -1622.2544 | 40.56% | 41.06% | 95% | 0% | 2289 | -120
[5 empty] | 2019-10-17 | 46 | 6958 | 2043 | -118 | 0 | 0 | 2161 | 1264.5507 | 1264.5507 | 1264.5507 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -135.0114 | 1129.5393 | -2750 | -200 | -1820.4607 | 45.51% | 41.05% | 95% | 0% | 2161 | -118
[5 empty] | 2019-10-17 | 47 | 6958.5 | 1907 | -115 | 0 | 0 | 2022 | 1046.8261 | 1046.8261 | 1046.8261 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -131.5789 | 915.2471 | -2750 | -200 | -2034.7529 | 50.87% | 41.04% | 95% | 0% | 2022 | -115
[5 empty] | 2019-10-17 | 48 | 6959 | 1798 | -113 | 0 | 0 | 1911 | 872.9596 | 872.9596 | 872.9596 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -129.2906 | 743.669 | -2750 | -200 | -2206.331 | 55.16% | 41.03% | 95% | 0% | 1911 | -113
[5 empty] | 2019-10-18 | 1 | 6959.5 | 1709 | -106 | 0 | 0 | 1815 | 722.5886 | 722.5886 | 722.5886 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -121.2815 | 601.3072 | -2750 | -200 | -2348.6928 | 58.72% | 41.03% | 95% | 0% | 1815 | -106
[5 empty] | 2019-10-18 | 2 | 6960 | 1655 | -100 | 0 | 0 | 1755 | 628.6068 | 628.6068 | 628.6068 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -114.4165 | 514.1903 | -2750 | -200 | -2435.8097 | 60.9% | 41.02% | 95% | 0% | 1755 | -100
[5 empty] | 2019-10-18 | 3 | 6960.5 | 1650 | -97 | 0 | 0 | 1747 | 616.0758 | 616.0758 | 616.0758 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -110.984 | 505.0919 | -2750 | -200 | -2444.9081 | 61.12% | 41.02% | 95% | 0% | 1747 | -97
[5 empty] | 2019-10-18 | 4 | 6961 | 1682 | -94 | 0 | 0 | 1776 | 661.5004 | 661.5004 | 661.5004 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -107.5515 | 553.9489 | -2750 | -200 | -2396.0511 | 59.9% | 41.02% | 95% | 0% | 1776 | -94
[5 empty] | 2019-10-18 | 5 | 6961.5 | 1676 | -92 | 0 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -105.2632 | 543.7063 | -2750 | -200 | -2406.2937 | 60.16% | 41% | 95% | 0% | 1768 | -92
[5 empty] | 2019-10-18 | 6 | 6962 | 1658 | -90 | 0 | 0 | 1748 | 617.6422 | 617.6422 | 617.6422 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -102.9748 | 514.6674 | -2750 | -200 | -2435.3326 | 60.88% | 41% | 95% | 0% | 1748 | -90
[5 empty] | 2019-10-18 | 7 | 6962.5 | 1635 | -89 | 0 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -101.8307 | 478.2188 | -2750 | -200 | -2471.7812 | 61.79% | 40.98% | 95% | 0% | 1724 | -89
[5 empty] | 2019-10-18 | 8 | 6963 | 1624 | -88 | 0 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -100.6865 | 460.5666 | -2750 | -200 | -2489.4334 | 62.24% | 40.97% | 95% | 0% | 1712 | -88
[5 empty] | 2019-10-18 | 9 | 6963.5 | 1625 | -89 | 0 | 0 | 1714 | 564.3858 | 564.3858 | 564.3858 | 710.0577 | 780 | 200 | 1690.0577 | 42.25% | 95% | 0% | -101.8307 | 462.5552 | -2750 | -200 | -2487.4448 | 62.19% | 40.97% | 95% | 0% | 1714 | -89
[5 empty] | 2019-10-18 | 10 | 6964 | 1639 | -89 | 0 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 708.4913 | 780 | 200 | 1688.4913 | 42.21% | 95% | 0% | -101.8307 | 484.4843 | -2750 | -200 | -2465.5157 | 61.64% | 40.96% | 95% | 0% | 1728 | -89
[5 empty] | 2019-10-18 | 11 | 6964.5 | 1698 | -89 | 0 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 708.4913 | 780 | 200 | 1688.4913 | 42.21% | 95% | 0% | -101.8307 | 576.8998 | -2750 | -200 | -2373.1002 | 59.33% | 40.96% | 95% | 0% | 1787 | -89
[5 empty] | 2019-10-18 | 12 | 6965 | 1792 | -88 | 0 | 0 | 1880 | 824.4023 | 824.4023 | 824.4023 | 708.4913 | 780 | 200 | 1688.4913 | 42.21% | 95% | 0% | -100.6865 | 723.7158 | -2750 | -200 | -2226.2842 | 55.66% | 40.95% | 95% | 0% | 1880 | -88
[5 empty] | 2019-10-18 | 13 | 6965.5 | 1992 | -88 | 0 | 0 | 2080 | 1137.6752 | 1137.6752 | 1137.6752 | 708.4913 | 780 | 200 | 1688.4913 | 42.21% | 95% | 0% | -100.6865 | 1036.9887 | -2750 | -200 | -1913.0113 | 47.83% | 40.95% | 95% | 0% | 2080 | -88
[5 empty] | 2019-10-18 | 14 | 6966 | 2215 | -87 | 0 | 0 | 2302 | 1485.4081 | 1485.4081 | 1485.4081 | 708.4913 | 780 | 200 | 1688.4913 | 42.21% | 95% | 0% | -99.5423 | 1385.8657 | -2750 | -200 | -1564.1343 | 39.1% | 40.94% | 95% | 0% | 2302 | -87
[5 empty] | 2019-10-18 | 15 | 6966.5 | 2498 | -87 | 0 | 0 | 2585 | 1928.6892 | 1928.6892 | 1928.6892 | 708.4913 | 780 | 200 | 1688.4913 | 42.21% | 95% | 0% | -99.5423 | 1829.1469 | -2750 | -200 | -1120.8531 | 28.02% | 40.94% | 95% | 0% | 2585 | -87
[5 empty] | 2019-10-18 | 16 | 6967 | 2631 | -88 | 0 | 0 | 2719 | 2138.582 | 2138.582 | 2138.582 | 708.4913 | 780 | 200 | 1688.4913 | 42.21% | 95% | 0% | -100.6865 | 2037.8955 | -2750 | -200 | -912.1045 | 22.8% | 40.93% | 95% | 0% | 2719 | -88
[5 empty] | 2019-10-18 | 17 | 6967.5 | 2677 | -103 | 0 | 0 | 2780 | 2234.1303 | 2234.1303 | 2234.1303 | 708.4913 | 780 | 200 | 1688.4913 | 42.21% | 95% | 0% | -117.849 | 2116.2813 | -2750 | -200 | -833.7187 | 20.84% | 40.93% | 95% | 0% | 2780 | -103
[5 empty] | 2019-10-18 | 18 | 6968 | 2624 | -147 | 0 | 0 | 2771 | 2220.033 | 2220.033 | 2220.033 | 708.4913 | 780 | 200 | 1688.4913 | 42.21% | 95% | 0% | -168.1922 | 2051.8408 | -2750 | -200 | -898.1592 | 22.45% | 40.93% | 95% | 0% | 2771 | -147
[5 empty] | 2019-10-18 | 19 | 6968.5 | 2548 | -212 | 0 | 0 | 2760 | 2202.803 | 2202.803 | 2202.803 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -242.5629 | 1960.24 | -2750 | -200 | -989.76 | 24.74% | 40.93% | 95% | 0% | 2760 | -212
[5 empty] | 2019-10-18 | 20 | 6969 | 2421 | -264 | 1 | 0 | 2685 | 2085.3256 | 2085.3256 | 2085.3256 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -302.0595 | 1783.2661 | -3550 | -400 | -2166.7339 | 54.17% | 40.93% | 95% | 0% | 2685 | -264
[5 empty] | 2019-10-18 | 21 | 6969.5 | 2304 | -337 | 1 | 0 | 2641 | 2016.4056 | 2016.4056 | 2016.4056 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -385.5835 | 1630.8221 | -3550 | -400 | -2319.1779 | 57.98% | 40.91% | 95% | 0% | 2641 | -337
[5 empty] | 2019-10-18 | 22 | 6970 | 2201 | -396 | 1 | 0 | 2597 | 1947.4856 | 1947.4856 | 1947.4856 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -453.0892 | 1494.3963 | -3550 | -400 | -2455.6037 | 61.39% | 40.91% | 95% | 0% | 2597 | -396
[5 empty] | 2019-10-18 | 23 | 6970.5 | 2163 | -413 | 1 | 0 | 2576 | 1914.5919 | 1914.5919 | 1914.5919 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -472.54 | 1442.0519 | -3550 | -400 | -2507.9481 | 62.7% | 40.91% | 95% | 0% | 2576 | -413
[5 empty] | 2019-10-18 | 24 | 6971 | 2136 | -414 | 1 | 0 | 2550 | 1873.8664 | 1873.8664 | 1873.8664 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -473.6842 | 1400.1822 | -3550 | -400 | -2549.8178 | 63.75% | 40.91% | 95% | 0% | 2550 | -414
[5 empty] | 2019-10-18 | 25 | 6971.5 | 2087 | -448 | 1 | 0 | 2535 | 1850.371 | 1850.371 | 1850.371 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -512.5858 | 1337.7852 | -3550 | -400 | -2612.2148 | 65.31% | 40.9% | 95% | 0% | 2535 | -448
[5 empty] | 2019-10-18 | 26 | 6972 | 2089 | -439 | 1 | 0 | 2528 | 1839.4064 | 1839.4064 | 1839.4064 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -502.2883 | 1337.1181 | -3550 | -400 | -2612.8819 | 65.32% | 40.9% | 95% | 0% | 2528 | -439
[5 empty] | 2019-10-18 | 27 | 6972.5 | 2113 | -388 | 1 | 0 | 2501 | 1797.1146 | 1797.1146 | 1797.1146 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -443.9359 | 1353.1787 | -3550 | -400 | -2596.8213 | 64.92% | 40.89% | 95% | 0% | 2501 | -388
[5 empty] | 2019-10-18 | 28 | 6973 | 2059 | -382 | 1 | 0 | 2441 | 1703.1327 | 1703.1327 | 1703.1327 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -437.0709 | 1266.0618 | -3550 | -400 | -2683.9382 | 67.1% | 40.89% | 95% | 0% | 2441 | -382
[5 empty] | 2019-10-18 | 29 | 6973.5 | 2114 | -336 | 1 | 0 | 2450 | 1717.23 | 1717.23 | 1717.23 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -384.4394 | 1332.7906 | -3550 | -400 | -2617.2094 | 65.43% | 40.89% | 95% | 0% | 2450 | -336
[5 empty] | 2019-10-18 | 30 | 6974 | 2129 | -330 | 1 | 0 | 2459 | 1731.3273 | 1731.3273 | 1731.3273 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -377.5744 | 1353.7529 | -3550 | -400 | -2596.2471 | 64.91% | 40.88% | 95% | 0% | 2459 | -330
[5 empty] | 2019-10-18 | 31 | 6974.5 | 2156 | -294 | 1 | 0 | 2450 | 1717.23 | 1717.23 | 1717.23 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -336.3844 | 1380.8456 | -3550 | -400 | -2569.1544 | 64.23% | 40.86% | 95% | 0% | 2450 | -294
[5 empty] | 2019-10-18 | 32 | 6975 | 2242 | -254 | 1 | 0 | 2496 | 1789.2828 | 1789.2828 | 1789.2828 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -290.6178 | 1498.6649 | -3550 | -400 | -2451.3351 | 61.28% | 40.85% | 95% | 0% | 2496 | -254
[5 empty] | 2019-10-18 | 33 | 6975.5 | 2369 | -217 | 1 | 0 | 2586 | 1930.2556 | 1930.2556 | 1930.2556 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -248.2838 | 1681.9718 | -3550 | -400 | -2268.0282 | 56.7% | 40.85% | 95% | 0% | 2586 | -217
[5 empty] | 2019-10-18 | 34 | 6976 | 2499 | -180 | 1 | 0 | 2679 | 2075.9275 | 2075.9275 | 2075.9275 | 706.925 | 780 | 200 | 1686.925 | 42.17% | 95% | 0% | -205.9497 | 1869.9778 | -3550 | -400 | -2080.0222 | 52% | 40.82% | 95% | 0% | 2679 | -180
[5 empty] | 2019-10-18 | 35 | 6976.5 | 2619 | -140 | 1 | 0 | 2759 | 2201.2366 | 2201.2366 | 2201.2366 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -160.1831 | 2041.0535 | -3550 | -400 | -1908.9465 | 47.72% | 40.81% | 95% | 0% | 2759 | -140
[5 empty] | 2019-10-18 | 36 | 6977 | 2679 | -115 | 1 | 0 | 2794 | 2256.0594 | 2256.0594 | 2256.0594 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -131.5789 | 2124.4804 | -3550 | -400 | -1825.5196 | 45.64% | 40.81% | 95% | 0% | 2794 | -115
[5 empty] | 2019-10-18 | 37 | 6977.5 | 2756 | -110 | 1 | 0 | 2866 | 2368.8376 | 2368.8376 | 2368.8376 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -125.8581 | 2242.9795 | -3550 | -400 | -1707.0205 | 42.68% | 40.8% | 95% | 0% | 2866 | -110
[5 empty] | 2019-10-18 | 38 | 6978 | 2803 | -109 | 1 | 0 | 2912 | 2440.8904 | 2440.8904 | 2440.8904 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -124.714 | 2316.1764 | -3550 | -400 | -1633.8236 | 40.85% | 40.8% | 95% | 0% | 2912 | -109
[5 empty] | 2019-10-18 | 39 | 6978.5 | 2752 | -109 | 0 | 0 | 2861 | 2361.0058 | 2361.0058 | 2361.0058 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -124.714 | 2236.2918 | -2750 | -200 | -713.7082 | 17.84% | 40.77% | 95% | 0% | 2861 | -109
[5 empty] | 2019-10-18 | 40 | 6979 | 2698 | -109 | 0 | 0 | 2807 | 2276.4221 | 2276.4221 | 2276.4221 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -124.714 | 2151.7081 | -2750 | -200 | -798.2919 | 19.96% | 40.77% | 95% | 0% | 2807 | -109
[5 empty] | 2019-10-18 | 41 | 6979.5 | 2600 | -108 | 0 | 0 | 2708 | 2121.352 | 2121.352 | 2121.352 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -123.5698 | 1997.7822 | -2750 | -200 | -952.2178 | 23.81% | 40.77% | 95% | 0% | 2708 | -108
[5 empty] | 2019-10-18 | 42 | 6980 | 2490 | -108 | 0 | 0 | 2598 | 1949.0519 | 1949.0519 | 1949.0519 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -123.5698 | 1825.4821 | -2750 | -200 | -1124.5179 | 28.11% | 40.76% | 95% | 0% | 2598 | -108
[5 empty] | 2019-10-18 | 43 | 6980.5 | 2369 | -107 | 0 | 0 | 2476 | 1757.9555 | 1757.9555 | 1757.9555 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -122.4256 | 1635.5299 | -2750 | -200 | -1314.4701 | 32.86% | 40.76% | 95% | 0% | 2476 | -107
[5 empty] | 2019-10-18 | 44 | 6981 | 2249 | -106 | 0 | 0 | 2355 | 1568.4254 | 1568.4254 | 1568.4254 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -121.2815 | 1447.1439 | -2750 | -200 | -1502.8561 | 37.57% | 40.75% | 95% | 0% | 2355 | -106
[5 empty] | 2019-10-18 | 45 | 6981.5 | 2133 | -105 | 0 | 0 | 2238 | 1385.1608 | 1385.1608 | 1385.1608 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -120.1373 | 1265.0235 | -2750 | -200 | -1684.9765 | 42.12% | 40.75% | 95% | 0% | 2238 | -105
[5 empty] | 2019-10-18 | 46 | 6982 | 2005 | -105 | 0 | 0 | 2110 | 1184.6661 | 1184.6661 | 1184.6661 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -120.1373 | 1064.5288 | -2750 | -200 | -1885.4712 | 47.14% | 40.74% | 95% | 0% | 2110 | -105
[5 empty] | 2019-10-18 | 47 | 6982.5 | 1889 | -104 | 0 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -118.9931 | 882.4083 | -2750 | -200 | -2067.5917 | 51.69% | 40.74% | 95% | 0% | 1993 | -104
[5 empty] | 2019-10-18 | 48 | 6983 | 1779 | -104 | 0 | 0 | 1883 | 829.1014 | 829.1014 | 829.1014 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -118.9931 | 710.1083 | -2750 | -200 | -2239.8917 | 56% | 40.73% | 95% | 0% | 1883 | -104
[5 empty] | 2019-10-19 | 1 | 6983.5 | 1691 | -103 | 0 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 705.3586 | 780 | 200 | 1685.3586 | 42.13% | 95% | 0% | -117.849 | 571.846 | -2750 | -200 | -2378.154 | 59.45% | 40.72% | 95% | 0% | 1794 | -103
[5 empty] | 2019-10-19 | 2 | 6984 | 1643 | -102 | 0 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 703.7923 | 780 | 200 | 1683.7923 | 42.09% | 95% | 0% | -116.7048 | 496.2383 | -2750 | -200 | -2453.7617 | 61.34% | 40.72% | 95% | 0% | 1745 | -102
[5 empty] | 2019-10-19 | 3 | 6984.5 | 1620 | -102 | 0 | 0 | 1722 | 576.9167 | 576.9167 | 576.9167 | 703.7923 | 780 | 200 | 1683.7923 | 42.09% | 95% | 0% | -116.7048 | 460.2119 | -2750 | -200 | -2489.7881 | 62.24% | 40.71% | 95% | 0% | 1722 | -102
[5 empty] | 2019-10-19 | 4 | 6985 | 1640 | -102 | 0 | 0 | 1742 | 608.244 | 608.244 | 608.244 | 703.7923 | 780 | 200 | 1683.7923 | 42.09% | 95% | 0% | -116.7048 | 491.5392 | -2750 | -200 | -2458.4608 | 61.46% | 40.71% | 95% | 0% | 1742 | -102
[5 empty] | 2019-10-19 | 5 | 6985.5 | 1621 | -101 | 0 | 0 | 1722 | 576.9167 | 576.9167 | 576.9167 | 703.7923 | 780 | 200 | 1683.7923 | 42.09% | 95% | 0% | -115.5606 | 461.3561 | -2750 | -200 | -2488.6439 | 62.22% | 40.71% | 95% | 0% | 1722 | -101
[5 empty] | 2019-10-19 | 6 | 6986 | 1582 | -100 | 0 | 0 | 1682 | 514.2622 | 514.2622 | 514.2622 | 702.2259 | 780 | 200 | 1682.2259 | 42.06% | 95% | 0% | -114.4165 | 399.8457 | -2750 | -200 | -2550.1543 | 63.75% | 40.7% | 95% | 0% | 1682 | -100
[5 empty] | 2019-10-19 | 7 | 6986.5 | 1549 | -100 | 0 | 0 | 1649 | 462.5721 | 462.5721 | 462.5721 | 702.2259 | 780 | 200 | 1682.2259 | 42.06% | 95% | 0% | -114.4165 | 348.1557 | -2750 | -200 | -2601.8443 | 65.05% | 40.69% | 95% | 0% | 1649 | -100
[5 empty] | 2019-10-19 | 8 | 6987 | 1525 | -100 | 0 | 0 | 1625 | 424.9794 | 424.9794 | 424.9794 | 702.2259 | 780 | 200 | 1682.2259 | 42.06% | 95% | 0% | -114.4165 | 310.5629 | -2750 | -200 | -2639.4371 | 65.99% | 40.69% | 95% | 0% | 1625 | -100
[5 empty] | 2019-10-19 | 9 | 6987.5 | 1517 | -98 | 0 | 0 | 1615 | 409.3157 | 409.3157 | 409.3157 | 702.2259 | 780 | 200 | 1682.2259 | 42.06% | 95% | 0% | -112.1281 | 297.1876 | -2750 | -200 | -2652.8124 | 66.32% | 40.68% | 95% | 0% | 1615 | -98
[5 empty] | 2019-10-19 | 10 | 6988 | 1521 | -97 | 0 | 0 | 1618 | 414.0148 | 414.0148 | 414.0148 | 702.2259 | 780 | 200 | 1682.2259 | 42.06% | 95% | 0% | -110.984 | 303.0309 | -2750 | -200 | -2646.9691 | 66.17% | 40.68% | 95% | 0% | 1618 | -97
[5 empty] | 2019-10-19 | 11 | 6988.5 | 1552 | -97 | 0 | 0 | 1649 | 462.5721 | 462.5721 | 462.5721 | 702.2259 | 780 | 200 | 1682.2259 | 42.06% | 95% | 0% | -110.984 | 351.5882 | -2750 | -200 | -2598.4118 | 64.96% | 40.67% | 95% | 0% | 1649 | -97
[5 empty] | 2019-10-19 | 12 | 6989 | 1591 | -96 | 0 | 0 | 1687 | 522.094 | 522.094 | 522.094 | 702.2259 | 780 | 200 | 1682.2259 | 42.06% | 95% | 0% | -109.8398 | 412.2542 | -2750 | -200 | -2537.7458 | 63.44% | 40.66% | 95% | 0% | 1687 | -96
[5 empty] | 2019-10-19 | 13 | 6989.5 | 1701 | -96 | 0 | 0 | 1797 | 694.3941 | 694.3941 | 694.3941 | 702.2259 | 780 | 200 | 1682.2259 | 42.06% | 95% | 0% | -109.8398 | 584.5542 | -2750 | -200 | -2365.4458 | 59.14% | 40.66% | 95% | 0% | 1797 | -96
[5 empty] | 2019-10-19 | 14 | 6990 | 1797 | -96 | 0 | 0 | 1893 | 844.765 | 844.765 | 844.765 | 702.2259 | 780 | 200 | 1682.2259 | 42.06% | 95% | 0% | -109.8398 | 734.9252 | -2750 | -200 | -2215.0748 | 55.38% | 40.66% | 95% | 0% | 1893 | -96
[5 empty] | 2019-10-19 | 15 | 6990.5 | 1945 | -97 | 0 | 0 | 2042 | 1078.1533 | 1078.1533 | 1078.1533 | 702.2259 | 780 | 200 | 1682.2259 | 42.06% | 95% | 0% | -110.984 | 967.1694 | -2750 | -200 | -1982.8306 | 49.57% | 40.65% | 95% | 0% | 2042 | -97
[5 empty] | 2019-10-19 | 16 | 6991 | 2055 | -101 | 0 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 702.2259 | 780 | 200 | 1682.2259 | 42.06% | 95% | 0% | -115.5606 | 1141.1582 | -2750 | -200 | -1808.8418 | 45.22% | 40.64% | 95% | 0% | 2156 | -101
[5 empty] | 2019-10-19 | 17 | 6991.5 | 2171 | -129 | 0 | 0 | 2300 | 1482.2754 | 1482.2754 | 1482.2754 | 702.2259 | 780 | 200 | 1682.2259 | 42.06% | 95% | 0% | -147.5973 | 1334.6781 | -2750 | -200 | -1615.3219 | 40.38% | 40.64% | 95% | 0% | 2300 | -129
[5 empty] | 2019-10-19 | 18 | 6992 | 2156 | -179 | 0 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -204.8055 | 1332.2926 | -2750 | -200 | -1617.7074 | 40.44% | 40.62% | 95% | 0% | 2335 | -179
[5 empty] | 2019-10-19 | 19 | 6992.5 | 2145 | -233 | 1 | 0 | 2378 | 1604.4518 | 1604.4518 | 1604.4518 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -266.5904 | 1337.8614 | -3550 | -400 | -2612.1386 | 65.3% | 40.6% | 95% | 0% | 2378 | -233
[5 empty] | 2019-10-19 | 20 | 6993 | 2032 | -315 | 1 | 0 | 2347 | 1555.8945 | 1555.8945 | 1555.8945 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -360.4119 | 1195.4826 | -3550 | -400 | -2754.5174 | 68.86% | 40.6% | 95% | 0% | 2347 | -315
[5 empty] | 2019-10-19 | 21 | 6993.5 | 1945 | -378 | 1 | 0 | 2323 | 1518.3017 | 1518.3017 | 1518.3017 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -432.4943 | 1085.8075 | -3550 | -400 | -2864.1925 | 71.6% | 40.6% | 95% | 0% | 2323 | -378
[5 empty] | 2019-10-19 | 22 | 6994 | 1891 | -400 | 1 | 0 | 2291 | 1468.1781 | 1468.1781 | 1468.1781 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -457.6659 | 1010.5122 | -3550 | -400 | -2939.4878 | 73.49% | 40.59% | 95% | 0% | 2291 | -400
[5 empty] | 2019-10-19 | 23 | 6994.5 | 1790 | -436 | 1 | 0 | 2226 | 1366.3644 | 1366.3644 | 1366.3644 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -498.8558 | 867.5086 | -3550 | -400 | -3082.4914 | 77.06% | 40.59% | 95% | 0% | 2226 | -436
[5 empty] | 2019-10-19 | 24 | 6995 | 1710 | -488 | 1 | 0 | 2198 | 1322.5062 | 1322.5062 | 1322.5062 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -558.3524 | 764.1538 | -3550 | -400 | -3185.8462 | 79.65% | 40.59% | 95% | 0% | 2198 | -488
[5 empty] | 2019-10-19 | 25 | 6995.5 | 1674 | -516 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -590.389 | 719.5863 | -3550 | -400 | -3230.4137 | 80.76% | 40.58% | 95% | 0% | 2190 | -516
[5 empty] | 2019-10-19 | 26 | 6996 | 1686 | -488 | 1 | 0 | 2174 | 1284.9134 | 1284.9134 | 1284.9134 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -558.3524 | 726.561 | -3550 | -400 | -3223.439 | 80.59% | 40.57% | 95% | 0% | 2174 | -488
[5 empty] | 2019-10-19 | 27 | 6996.5 | 1716 | -439 | 1 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -502.2883 | 752.8642 | -3550 | -400 | -3197.1358 | 79.93% | 40.57% | 95% | 0% | 2155 | -439
[5 empty] | 2019-10-19 | 28 | 6997 | 1756 | -389 | 1 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -445.0801 | 794.4088 | -3550 | -400 | -3155.5912 | 78.89% | 40.56% | 95% | 0% | 2145 | -389
[5 empty] | 2019-10-19 | 29 | 6997.5 | 1751 | -392 | 1 | 0 | 2143 | 1236.3561 | 1236.3561 | 1236.3561 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -448.5126 | 787.8436 | -3550 | -400 | -3162.1564 | 79.05% | 40.56% | 95% | 0% | 2143 | -392
[5 empty] | 2019-10-19 | 30 | 6998 | 1763 | -363 | 1 | 0 | 2126 | 1209.7279 | 1209.7279 | 1209.7279 | 700.6595 | 780 | 200 | 1680.6595 | 42.02% | 95% | 0% | -415.3318 | 794.3961 | -3550 | -400 | -3155.6039 | 78.89% | 40.56% | 95% | 0% | 2126 | -363
[5 empty] | 2019-10-19 | 31 | 6998.5 | 1811 | -328 | 1 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 699.0932 | 780 | 200 | 1679.0932 | 41.98% | 95% | 0% | -375.286 | 854.8046 | -3550 | -400 | -3095.1954 | 77.38% | 40.55% | 95% | 0% | 2139 | -328
[5 empty] | 2019-10-19 | 32 | 6999 | 1870 | -293 | 1 | 0 | 2163 | 1267.6834 | 1267.6834 | 1267.6834 | 699.0932 | 780 | 200 | 1679.0932 | 41.98% | 95% | 0% | -335.2403 | 932.4432 | -3550 | -400 | -3017.5568 | 75.44% | 40.55% | 95% | 0% | 2163 | -293
[5 empty] | 2019-10-19 | 33 | 6999.5 | 1996 | -248 | 1 | 0 | 2244 | 1394.5589 | 1394.5589 | 1394.5589 | 699.0932 | 780 | 200 | 1679.0932 | 41.98% | 95% | 0% | -283.7529 | 1110.8061 | -3550 | -400 | -2839.1939 | 70.98% | 40.55% | 95% | 0% | 2244 | -248
[5 empty] | 2019-10-19 | 34 | 7000 | 2147 | -192 | 1 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 699.0932 | 780 | 200 | 1679.0932 | 41.98% | 95% | 0% | -219.6796 | 1323.6839 | -3550 | -400 | -2626.3161 | 65.66% | 40.55% | 95% | 0% | 2339 | -192
[5 empty] | 2019-10-19 | 35 | 7000.5 | 2322 | -143 | 1 | 0 | 2465 | 1740.7255 | 1740.7255 | 1740.7255 | 699.0932 | 780 | 200 | 1679.0932 | 41.98% | 95% | 0% | -163.6156 | 1577.1099 | -3550 | -400 | -2372.8901 | 59.32% | 40.54% | 95% | 0% | 2465 | -143
[5 empty] | 2019-10-19 | 36 | 7001 | 2435 | -110 | 1 | 0 | 2545 | 1866.0346 | 1866.0346 | 1866.0346 | 699.0932 | 780 | 200 | 1679.0932 | 41.98% | 95% | 0% | -125.8581 | 1740.1765 | -3550 | -400 | -2209.8235 | 55.25% | 40.54% | 95% | 0% | 2545 | -110
[5 empty] | 2019-10-19 | 37 | 7001.5 | 2527 | -102 | 1 | 0 | 2629 | 1997.6092 | 1997.6092 | 1997.6092 | 699.0932 | 780 | 200 | 1679.0932 | 41.98% | 95% | 0% | -116.7048 | 1880.9044 | -3550 | -400 | -2069.0956 | 51.73% | 40.54% | 95% | 0% | 2629 | -102
[5 empty] | 2019-10-19 | 38 | 7002 | 2560 | -102 | 1 | 0 | 2662 | 2049.2993 | 2049.2993 | 2049.2993 | 699.0932 | 780 | 200 | 1679.0932 | 41.98% | 95% | 0% | -116.7048 | 1932.5945 | -3550 | -400 | -2017.4055 | 50.44% | 40.53% | 95% | 0% | 2662 | -102
[5 empty] | 2019-10-19 | 39 | 7002.5 | 2588 | -102 | 0 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 699.0932 | 780 | 200 | 1679.0932 | 41.98% | 95% | 0% | -116.7048 | 1976.4527 | -2750 | -200 | -973.5473 | 24.34% | 40.53% | 95% | 0% | 2690 | -102
[5 empty] | 2019-10-19 | 40 | 7003 | 2447 | -102 | 0 | 0 | 2549 | 1872.3001 | 1872.3001 | 1872.3001 | 699.0932 | 780 | 200 | 1679.0932 | 41.98% | 95% | 0% | -116.7048 | 1755.5953 | -2750 | -200 | -1194.4047 | 29.86% | 40.52% | 95% | 0% | 2549 | -102
[5 empty] | 2019-10-19 | 41 | 7003.5 | 2374 | -101 | 0 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 697.5268 | 780 | 200 | 1677.5268 | 41.94% | 95% | 0% | -115.5606 | 1640.8285 | -2750 | -200 | -1309.1715 | 32.73% | 40.51% | 95% | 0% | 2475 | -101
[5 empty] | 2019-10-19 | 42 | 7004 | 2316 | -101 | 0 | 0 | 2417 | 1665.54 | 1665.54 | 1665.54 | 697.5268 | 780 | 200 | 1677.5268 | 41.94% | 95% | 0% | -115.5606 | 1549.9793 | -2750 | -200 | -1400.0207 | 35% | 40.51% | 95% | 0% | 2417 | -101
[5 empty] | 2019-10-19 | 43 | 7004.5 | 2244 | -102 | 0 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 697.5268 | 780 | 200 | 1677.5268 | 41.94% | 95% | 0% | -116.7048 | 1437.6233 | -2750 | -200 | -1512.3767 | 37.81% | 40.5% | 95% | 0% | 2346 | -102
[5 empty] | 2019-10-19 | 44 | 7005 | 2148 | -103 | 0 | 0 | 2251 | 1405.5235 | 1405.5235 | 1405.5235 | 697.5268 | 780 | 200 | 1677.5268 | 41.94% | 95% | 0% | -117.849 | 1287.6745 | -2750 | -200 | -1662.3255 | 41.56% | 40.49% | 95% | 0% | 2251 | -103
[5 empty] | 2019-10-19 | 45 | 7005.5 | 2046 | -103 | 0 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 697.5268 | 780 | 200 | 1677.5268 | 41.94% | 95% | 0% | -117.849 | 1127.9054 | -2750 | -200 | -1822.0946 | 45.55% | 40.48% | 95% | 0% | 2149 | -103
[5 empty] | 2019-10-19 | 46 | 7006 | 1938 | -104 | 0 | 0 | 2042 | 1078.1533 | 1078.1533 | 1078.1533 | 697.5268 | 780 | 200 | 1677.5268 | 41.94% | 95% | 0% | -118.9931 | 959.1602 | -2750 | -200 | -1990.8398 | 49.77% | 40.46% | 95% | 0% | 2042 | -104
[5 empty] | 2019-10-19 | 47 | 7006.5 | 1814 | -104 | 0 | 0 | 1918 | 883.9242 | 883.9242 | 883.9242 | 697.5268 | 780 | 200 | 1677.5268 | 41.94% | 95% | 0% | -118.9931 | 764.931 | -2750 | -200 | -2185.069 | 54.63% | 40.46% | 95% | 0% | 1918 | -104
[5 empty] | 2019-10-19 | 48 | 7007 | 1714 | -105 | 0 | 0 | 1819 | 728.8541 | 728.8541 | 728.8541 | 697.5268 | 780 | 200 | 1677.5268 | 41.94% | 95% | 0% | -120.1373 | 608.7168 | -2750 | -200 | -2341.2832 | 58.53% | 40.46% | 95% | 0% | 1819 | -105
[5 empty] | 2019-10-20 | 1 | 7007.5 | 1631 | -106 | 0 | 0 | 1737 | 600.4122 | 600.4122 | 600.4122 | 697.5268 | 780 | 200 | 1677.5268 | 41.94% | 95% | 0% | -121.2815 | 479.1307 | -2750 | -200 | -2470.8693 | 61.77% | 40.46% | 95% | 0% | 1737 | -106
[5 empty] | 2019-10-20 | 2 | 7008 | 1571 | -106 | 0 | 0 | 1677 | 506.4303 | 506.4303 | 506.4303 | 697.5268 | 780 | 200 | 1677.5268 | 41.94% | 95% | 0% | -121.2815 | 385.1489 | -2750 | -200 | -2564.8511 | 64.12% | 40.45% | 95% | 0% | 1677 | -106
[5 empty] | 2019-10-20 | 3 | 7008.5 | 1575 | -108 | 0 | 0 | 1683 | 515.8285 | 515.8285 | 515.8285 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -123.5698 | 392.2587 | -2750 | -200 | -2557.7413 | 63.94% | 40.44% | 95% | 0% | 1683 | -108
[5 empty] | 2019-10-20 | 4 | 7009 | 1567 | -109 | 0 | 0 | 1676 | 504.864 | 504.864 | 504.864 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -124.714 | 380.15 | -2750 | -200 | -2569.85 | 64.25% | 40.44% | 95% | 0% | 1676 | -109
[5 empty] | 2019-10-20 | 5 | 7009.5 | 1555 | -110 | 0 | 0 | 1665 | 487.634 | 487.634 | 487.634 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -125.8581 | 361.7758 | -2750 | -200 | -2588.2242 | 64.71% | 40.44% | 95% | 0% | 1665 | -110
[5 empty] | 2019-10-20 | 6 | 7010 | 1522 | -112 | 0 | 0 | 1634 | 439.0767 | 439.0767 | 439.0767 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -128.1465 | 310.9302 | -2750 | -200 | -2639.0698 | 65.98% | 40.43% | 95% | 0% | 1634 | -112
[5 empty] | 2019-10-20 | 7 | 7010.5 | 1482 | -114 | 0 | 0 | 1596 | 379.5548 | 379.5548 | 379.5548 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -130.4348 | 249.12 | -2750 | -200 | -2700.88 | 67.52% | 40.42% | 95% | 0% | 1596 | -114
[5 empty] | 2019-10-20 | 8 | 7011 | 1453 | -115 | 0 | 0 | 1568 | 335.6966 | 335.6966 | 335.6966 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -131.5789 | 204.1177 | -2750 | -200 | -2745.8823 | 68.65% | 40.41% | 95% | 0% | 1568 | -115
[5 empty] | 2019-10-20 | 9 | 7011.5 | 1423 | -116 | 0 | 0 | 1539 | 290.2721 | 290.2721 | 290.2721 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -132.7231 | 157.5489 | -2750 | -200 | -2792.4511 | 69.81% | 40.4% | 95% | 0% | 1539 | -116
[5 empty] | 2019-10-20 | 10 | 7012 | 1418 | -116 | 0 | 0 | 1534 | 282.4402 | 282.4402 | 282.4402 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -132.7231 | 149.7171 | -2750 | -200 | -2800.2829 | 70.01% | 40.4% | 95% | 0% | 1534 | -116
[5 empty] | 2019-10-20 | 11 | 7012.5 | 1429 | -118 | 0 | 0 | 1547 | 302.803 | 302.803 | 302.803 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -135.0114 | 167.7915 | -2750 | -200 | -2782.2085 | 69.56% | 40.4% | 95% | 0% | 1547 | -118
[5 empty] | 2019-10-20 | 12 | 7013 | 1458 | -120 | 0 | 0 | 1578 | 351.3603 | 351.3603 | 351.3603 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -137.2998 | 214.0605 | -2750 | -200 | -2735.9395 | 68.4% | 40.4% | 95% | 0% | 1578 | -120
[5 empty] | 2019-10-20 | 13 | 7013.5 | 1532 | -120 | 0 | 0 | 1652 | 467.2712 | 467.2712 | 467.2712 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -137.2998 | 329.9715 | -2750 | -200 | -2620.0285 | 65.5% | 40.39% | 95% | 0% | 1652 | -120
[5 empty] | 2019-10-20 | 14 | 7014 | 1590 | -121 | 1 | 0 | 1711 | 559.6867 | 559.6867 | 559.6867 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -138.4439 | 421.2428 | -3550 | -400 | -3528.7572 | 88.22% | 40.38% | 95% | 0% | 1711 | -121
[5 empty] | 2019-10-20 | 15 | 7014.5 | 1702 | -120 | 1 | 0 | 1822 | 733.5532 | 733.5532 | 733.5532 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -137.2998 | 596.2534 | -3550 | -400 | -3353.7466 | 83.84% | 40.37% | 95% | 0% | 1822 | -120
[5 empty] | 2019-10-20 | 16 | 7015 | 1793 | -121 | 1 | 0 | 1914 | 877.6587 | 877.6587 | 877.6587 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -138.4439 | 739.2148 | -3550 | -400 | -3210.7852 | 80.27% | 40.37% | 95% | 0% | 1914 | -121
[5 empty] | 2019-10-20 | 17 | 7015.5 | 1916 | -135 | 1 | 0 | 2051 | 1092.2506 | 1092.2506 | 1092.2506 | 695.9604 | 780 | 200 | 1675.9604 | 41.9% | 95% | 0% | -154.4622 | 937.7884 | -3550 | -400 | -3012.2116 | 75.31% | 40.36% | 95% | 0% | 2051 | -135
[5 empty] | 2019-10-20 | 18 | 7016 | 1938 | -170 | 1 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 694.3941 | 780 | 200 | 1674.3941 | 41.86% | 95% | 0% | -194.508 | 987.0254 | -3550 | -400 | -2962.9746 | 74.07% | 40.36% | 95% | 0% | 2108 | -170
[5 empty] | 2019-10-20 | 19 | 7016.5 | 1955 | -226 | 1 | 0 | 2181 | 1295.878 | 1295.878 | 1295.878 | 694.3941 | 780 | 200 | 1674.3941 | 41.86% | 95% | 0% | -258.5812 | 1037.2968 | -3550 | -400 | -2912.7032 | 72.82% | 40.35% | 95% | 0% | 2181 | -226
[5 empty] | 2019-10-20 | 20 | 7017 | 1903 | -270 | 1 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 694.3941 | 780 | 200 | 1674.3941 | 41.86% | 95% | 0% | -308.9245 | 974.4226 | -3550 | -400 | -2975.5774 | 74.39% | 40.35% | 95% | 0% | 2173 | -270
[5 empty] | 2019-10-20 | 21 | 7017.5 | 1893 | -311 | 1 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 694.3941 | 780 | 200 | 1674.3941 | 41.86% | 95% | 0% | -355.8352 | 976.0691 | -3550 | -400 | -2973.9309 | 74.35% | 40.34% | 95% | 0% | 2204 | -311
[5 empty] | 2019-10-20 | 22 | 7018 | 1860 | -354 | 1 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 694.3941 | 780 | 200 | 1674.3941 | 41.86% | 95% | 0% | -405.0343 | 942.5337 | -3550 | -400 | -3007.4663 | 75.19% | 40.34% | 95% | 0% | 2214 | -354
[5 empty] | 2019-10-20 | 23 | 7018.5 | 1827 | -387 | 1 | 0 | 2214 | 1347.568 | 1347.568 | 1347.568 | 694.3941 | 780 | 200 | 1674.3941 | 41.86% | 95% | 0% | -442.7918 | 904.7763 | -3550 | -400 | -3045.2237 | 76.13% | 40.34% | 95% | 0% | 2214 | -387
[5 empty] | 2019-10-20 | 24 | 7019 | 1805 | -400 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 694.3941 | 780 | 200 | 1674.3941 | 41.86% | 95% | 0% | -457.6659 | 875.8048 | -3550 | -400 | -3074.1952 | 76.85% | 40.34% | 95% | 0% | 2205 | -400
[5 empty] | 2019-10-20 | 25 | 7019.5 | 1813 | -397 | 1 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 694.3941 | 780 | 200 | 1674.3941 | 41.86% | 95% | 0% | -454.2334 | 887.0691 | -3550 | -400 | -3062.9309 | 76.57% | 40.32% | 95% | 0% | 2210 | -397
[5 empty] | 2019-10-20 | 26 | 7020 | 1845 | -383 | 1 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 692.8277 | 780 | 200 | 1672.8277 | 41.82% | 95% | 0% | -438.2151 | 931.282 | -3550 | -400 | -3018.718 | 75.47% | 40.32% | 95% | 0% | 2228 | -383
[5 empty] | 2019-10-20 | 27 | 7020.5 | 1832 | -373 | 1 | 0 | 2205 | 1333.4707 | 1333.4707 | 1333.4707 | 692.8277 | 780 | 200 | 1672.8277 | 41.82% | 95% | 0% | -426.7735 | 906.6973 | -3550 | -400 | -3043.3027 | 76.08% | 40.32% | 95% | 0% | 2205 | -373
[5 empty] | 2019-10-20 | 28 | 7021 | 1834 | -369 | 1 | 0 | 2203 | 1330.338 | 1330.338 | 1330.338 | 692.8277 | 780 | 200 | 1672.8277 | 41.82% | 95% | 0% | -422.1968 | 908.1412 | -3550 | -400 | -3041.8588 | 76.05% | 40.31% | 95% | 0% | 2203 | -369
[5 empty] | 2019-10-20 | 29 | 7021.5 | 1860 | -351 | 1 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 692.8277 | 780 | 200 | 1672.8277 | 41.82% | 95% | 0% | -401.6018 | 941.2671 | -3550 | -400 | -3008.7329 | 75.22% | 40.31% | 95% | 0% | 2211 | -351
[5 empty] | 2019-10-20 | 30 | 7022 | 1911 | -320 | 1 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 692.8277 | 780 | 200 | 1672.8277 | 41.82% | 95% | 0% | -366.1327 | 1008.0635 | -3550 | -400 | -2941.9365 | 73.55% | 40.31% | 95% | 0% | 2231 | -320
[5 empty] | 2019-10-20 | 31 | 7022.5 | 2015 | -274 | 1 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 692.8277 | 780 | 200 | 1672.8277 | 41.82% | 95% | 0% | -313.5011 | 1151.5442 | -3550 | -400 | -2798.4558 | 69.96% | 40.31% | 95% | 0% | 2289 | -274
[5 empty] | 2019-10-20 | 32 | 7023 | 2130 | -230 | 1 | 0 | 2360 | 1576.2572 | 1576.2572 | 1576.2572 | 692.8277 | 780 | 200 | 1672.8277 | 41.82% | 95% | 0% | -263.1579 | 1313.0993 | -3550 | -400 | -2636.9007 | 65.92% | 40.31% | 95% | 0% | 2360 | -230
[5 empty] | 2019-10-20 | 33 | 7023.5 | 2256 | -199 | 1 | 0 | 2455 | 1725.0618 | 1725.0618 | 1725.0618 | 692.8277 | 780 | 200 | 1672.8277 | 41.82% | 95% | 0% | -227.6888 | 1497.373 | -3550 | -400 | -2452.627 | 61.32% | 40.29% | 95% | 0% | 2455 | -199
[5 empty] | 2019-10-20 | 34 | 7024 | 2383 | -171 | 1 | 0 | 2554 | 1880.1319 | 1880.1319 | 1880.1319 | 692.8277 | 780 | 200 | 1672.8277 | 41.82% | 95% | 0% | -195.6522 | 1684.4797 | -3550 | -400 | -2265.5203 | 56.64% | 40.28% | 95% | 0% | 2554 | -171
[5 empty] | 2019-10-20 | 35 | 7024.5 | 2499 | -147 | 1 | 0 | 2646 | 2024.2374 | 2024.2374 | 2024.2374 | 692.8277 | 780 | 200 | 1672.8277 | 41.82% | 95% | 0% | -168.1922 | 1856.0452 | -3550 | -400 | -2093.9548 | 52.35% | 40.28% | 95% | 0% | 2646 | -147
[5 empty] | 2019-10-20 | 36 | 7025 | 2587 | -130 | 1 | 0 | 2717 | 2135.4493 | 2135.4493 | 2135.4493 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -148.7414 | 1986.7079 | -3550 | -400 | -1963.2921 | 49.08% | 40.27% | 95% | 0% | 2717 | -130
[5 empty] | 2019-10-20 | 37 | 7025.5 | 2631 | -126 | 1 | 0 | 2757 | 2198.1039 | 2198.1039 | 2198.1039 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -144.1648 | 2053.9391 | -3550 | -400 | -1896.0609 | 47.4% | 40.27% | 95% | 0% | 2757 | -126
[5 empty] | 2019-10-20 | 38 | 7026 | 2677 | -124 | 0 | 0 | 2801 | 2267.0239 | 2267.0239 | 2267.0239 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -141.8764 | 2125.1475 | -2750 | -200 | -824.8525 | 20.62% | 40.27% | 95% | 0% | 2801 | -124
[5 empty] | 2019-10-20 | 39 | 7026.5 | 2630 | -122 | 0 | 0 | 2752 | 2190.2721 | 2190.2721 | 2190.2721 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -139.5881 | 2050.684 | -2750 | -200 | -899.316 | 22.48% | 40.26% | 95% | 0% | 2752 | -122
[5 empty] | 2019-10-20 | 40 | 7027 | 2526 | -121 | 0 | 0 | 2647 | 2025.8038 | 2025.8038 | 2025.8038 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -138.4439 | 1887.3599 | -2750 | -200 | -1062.6401 | 26.57% | 40.24% | 95% | 0% | 2647 | -121
[5 empty] | 2019-10-20 | 41 | 7027.5 | 2447 | -119 | 0 | 0 | 2566 | 1898.9283 | 1898.9283 | 1898.9283 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -136.1556 | 1762.7727 | -2750 | -200 | -1187.2273 | 29.68% | 40.24% | 95% | 0% | 2566 | -119
[5 empty] | 2019-10-20 | 42 | 7028 | 2340 | -117 | 0 | 0 | 2457 | 1728.1946 | 1728.1946 | 1728.1946 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -133.8673 | 1594.3273 | -2750 | -200 | -1355.6727 | 33.89% | 40.23% | 95% | 0% | 2457 | -117
[5 empty] | 2019-10-20 | 43 | 7028.5 | 2236 | -115 | 0 | 0 | 2351 | 1562.1599 | 1562.1599 | 1562.1599 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -131.5789 | 1430.581 | -2750 | -200 | -1519.419 | 37.99% | 40.23% | 95% | 0% | 2351 | -115
[5 empty] | 2019-10-20 | 44 | 7029 | 2115 | -113 | 0 | 0 | 2228 | 1369.4971 | 1369.4971 | 1369.4971 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -129.2906 | 1240.2065 | -2750 | -200 | -1709.7935 | 42.74% | 40.23% | 95% | 0% | 2228 | -113
[5 empty] | 2019-10-20 | 45 | 7029.5 | 1997 | -110 | 0 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -125.8581 | 1054.1089 | -2750 | -200 | -1895.8911 | 47.4% | 40.21% | 95% | 0% | 2107 | -110
[5 empty] | 2019-10-20 | 46 | 7030 | 1870 | -108 | 0 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -123.5698 | 854.3362 | -2750 | -200 | -2095.6638 | 52.39% | 40.21% | 95% | 0% | 1978 | -108
[5 empty] | 2019-10-20 | 47 | 7030.5 | 1731 | -106 | 0 | 0 | 1837 | 757.0486 | 757.0486 | 757.0486 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -121.2815 | 635.7672 | -2750 | -200 | -2314.2328 | 57.86% | 40.21% | 95% | 0% | 1837 | -106
[5 empty] | 2019-10-20 | 48 | 7031 | 1653 | -104 | 0 | 0 | 1757 | 631.7395 | 631.7395 | 631.7395 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -118.9931 | 512.7464 | -2750 | -200 | -2437.2536 | 60.93% | 40.21% | 95% | 0% | 1757 | -104
[5 empty] | 2019-10-21 | 1 | 7031.5 | 1580 | -101 | 0 | 0 | 1681 | 512.6958 | 512.6958 | 512.6958 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -115.5606 | 397.1352 | -2750 | -200 | -2552.8648 | 63.82% | 40.2% | 95% | 0% | 1681 | -101
[5 empty] | 2019-10-21 | 2 | 7032 | 1537 | -98 | 0 | 0 | 1635 | 440.643 | 440.643 | 440.643 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -112.1281 | 328.5149 | -2750 | -200 | -2621.4851 | 65.54% | 40.2% | 95% | 0% | 1635 | -98
[5 empty] | 2019-10-21 | 3 | 7032.5 | 1539 | -97 | 0 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -110.984 | 331.2254 | -2750 | -200 | -2618.7746 | 65.47% | 40.19% | 95% | 0% | 1636 | -97
[5 empty] | 2019-10-21 | 4 | 7033 | 1577 | -97 | 0 | 0 | 1674 | 501.7312 | 501.7312 | 501.7312 | 691.2613 | 780 | 200 | 1671.2613 | 41.78% | 95% | 0% | -110.984 | 390.7473 | -2750 | -200 | -2559.2527 | 63.98% | 40.17% | 95% | 0% | 1674 | -97
[5 empty] | 2019-10-21 | 5 | 7033.5 | 1579 | -96 | 0 | 0 | 1675 | 503.2976 | 503.2976 | 503.2976 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -109.8398 | 393.4578 | -2750 | -200 | -2556.5422 | 63.91% | 40.16% | 95% | 0% | 1675 | -96
[5 empty] | 2019-10-21 | 6 | 7034 | 1552 | -95 | 0 | 0 | 1647 | 459.4394 | 459.4394 | 459.4394 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -108.6957 | 350.7438 | -2750 | -200 | -2599.2562 | 64.98% | 40.16% | 95% | 0% | 1647 | -95
[5 empty] | 2019-10-21 | 7 | 7034.5 | 1535 | -95 | 0 | 0 | 1630 | 432.8112 | 432.8112 | 432.8112 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -108.6957 | 324.1156 | -2750 | -200 | -2625.8844 | 65.65% | 40.15% | 95% | 0% | 1630 | -95
[5 empty] | 2019-10-21 | 8 | 7035 | 1530 | -94 | 0 | 0 | 1624 | 423.413 | 423.413 | 423.413 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -107.5515 | 315.8615 | -2750 | -200 | -2634.1385 | 65.85% | 40.15% | 95% | 0% | 1624 | -94
[5 empty] | 2019-10-21 | 9 | 7035.5 | 1531 | -93 | 0 | 0 | 1624 | 423.413 | 423.413 | 423.413 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -106.4073 | 317.0057 | -2750 | -200 | -2632.9943 | 65.82% | 40.14% | 95% | 0% | 1624 | -93
[5 empty] | 2019-10-21 | 10 | 7036 | 1543 | -93 | 0 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -106.4073 | 335.8021 | -2750 | -200 | -2614.1979 | 65.35% | 40.12% | 95% | 0% | 1636 | -93
[5 empty] | 2019-10-21 | 11 | 7036.5 | 1606 | -91 | 1 | 0 | 1697 | 537.7576 | 537.7576 | 537.7576 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -104.119 | 433.6386 | -3550 | -400 | -3516.3614 | 87.91% | 40.11% | 95% | 0% | 1697 | -91
[5 empty] | 2019-10-21 | 12 | 7037 | 1710 | -89 | 1 | 0 | 1799 | 697.5268 | 697.5268 | 697.5268 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -101.8307 | 595.6961 | -3550 | -400 | -3354.3039 | 83.86% | 40.1% | 95% | 0% | 1799 | -89
[5 empty] | 2019-10-21 | 13 | 7037.5 | 1944 | -87 | 1 | 0 | 2031 | 1060.9233 | 1060.9233 | 1060.9233 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -99.5423 | 961.381 | -3550 | -400 | -2988.619 | 74.72% | 40.1% | 95% | 0% | 2031 | -87
[5 empty] | 2019-10-21 | 14 | 7038 | 2199 | -84 | 1 | 0 | 2283 | 1455.6472 | 1455.6472 | 1455.6472 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -96.1098 | 1359.5373 | -3550 | -400 | -2590.4627 | 64.76% | 40.09% | 95% | 0% | 2283 | -84
[5 empty] | 2019-10-21 | 15 | 7038.5 | 2485 | -82 | 1 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -93.8215 | 1806.6731 | -3550 | -400 | -2143.3269 | 53.58% | 40.09% | 95% | 0% | 2567 | -82
[5 empty] | 2019-10-21 | 16 | 7039 | 2612 | -80 | 1 | 0 | 2692 | 2096.2902 | 2096.2902 | 2096.2902 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -91.5332 | 2004.757 | -3550 | -400 | -1945.243 | 48.63% | 40.09% | 95% | 0% | 2692 | -80
[5 empty] | 2019-10-21 | 17 | 7039.5 | 2726 | -85 | 1 | 0 | 2811 | 2282.6876 | 2282.6876 | 2282.6876 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -97.254 | 2185.4335 | -3550 | -400 | -1764.5665 | 44.11% | 40.08% | 95% | 0% | 2811 | -85
[5 empty] | 2019-10-21 | 18 | 7040 | 2730 | -102 | 1 | 0 | 2832 | 2315.5812 | 2315.5812 | 2315.5812 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -116.7048 | 2198.8764 | -3550 | -400 | -1751.1236 | 43.78% | 40.08% | 95% | 0% | 2832 | -102
[5 empty] | 2019-10-21 | 19 | 7040.5 | 2747 | -124 | 1 | 0 | 2871 | 2376.6694 | 2376.6694 | 2376.6694 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -141.8764 | 2234.793 | -3550 | -400 | -1715.207 | 42.88% | 40.07% | 95% | 0% | 2871 | -124
[5 empty] | 2019-10-21 | 20 | 7041 | 2712 | -148 | 1 | 0 | 2860 | 2359.4394 | 2359.4394 | 2359.4394 | 689.695 | 780 | 200 | 1669.695 | 41.74% | 95% | 0% | -169.3364 | 2190.103 | -3550 | -400 | -1759.897 | 44% | 40.05% | 95% | 0% | 2860 | -148
[5 empty] | 2019-10-21 | 21 | 7041.5 | 2642 | -187 | 1 | 0 | 2829 | 2310.8821 | 2310.8821 | 2310.8821 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -213.9588 | 2096.9233 | -3550 | -400 | -1853.0767 | 46.33% | 40.05% | 95% | 0% | 2829 | -187
[5 empty] | 2019-10-21 | 22 | 7042 | 2600 | -216 | 1 | 0 | 2816 | 2290.5194 | 2290.5194 | 2290.5194 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -247.1396 | 2043.3798 | -3550 | -400 | -1906.6202 | 47.67% | 40.04% | 95% | 0% | 2816 | -216
[5 empty] | 2019-10-21 | 23 | 7042.5 | 2588 | -221 | 1 | 0 | 2809 | 2279.5548 | 2279.5548 | 2279.5548 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -252.8604 | 2026.6944 | -3550 | -400 | -1923.3056 | 48.08% | 40.04% | 95% | 0% | 2809 | -221
[5 empty] | 2019-10-21 | 24 | 7043 | 2550 | -243 | 1 | 0 | 2793 | 2254.493 | 2254.493 | 2254.493 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -278.032 | 1976.461 | -3550 | -400 | -1973.539 | 49.34% | 40.04% | 95% | 0% | 2793 | -243
[5 empty] | 2019-10-21 | 25 | 7043.5 | 2523 | -258 | 1 | 0 | 2781 | 2235.6966 | 2235.6966 | 2235.6966 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -295.1945 | 1940.5021 | -3550 | -400 | -2009.4979 | 50.24% | 40.01% | 95% | 0% | 2781 | -258
[5 empty] | 2019-10-21 | 26 | 7044 | 2479 | -279 | 1 | 0 | 2758 | 2199.6702 | 2199.6702 | 2199.6702 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -319.222 | 1880.4483 | -3550 | -400 | -2069.5517 | 51.74% | 40.01% | 95% | 0% | 2758 | -279
[5 empty] | 2019-10-21 | 27 | 7044.5 | 2464 | -272 | 1 | 0 | 2736 | 2165.2102 | 2165.2102 | 2165.2102 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -311.2128 | 1853.9974 | -3550 | -400 | -2096.0026 | 52.4% | 40% | 95% | 0% | 2736 | -272
[5 empty] | 2019-10-21 | 28 | 7045 | 2468 | -266 | 1 | 0 | 2734 | 2162.0775 | 2162.0775 | 2162.0775 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -304.3478 | 1857.7297 | -3550 | -400 | -2092.2703 | 52.31% | 40% | 95% | 0% | 2734 | -266
[5 empty] | 2019-10-21 | 29 | 7045.5 | 2501 | -241 | 1 | 0 | 2742 | 2174.6084 | 2174.6084 | 2174.6084 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -275.7437 | 1898.8647 | -3550 | -400 | -2051.1353 | 51.28% | 39.99% | 95% | 0% | 2742 | -241
[5 empty] | 2019-10-21 | 30 | 7046 | 2533 | -216 | 1 | 0 | 2749 | 2185.573 | 2185.573 | 2185.573 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -247.1396 | 1938.4334 | -3550 | -400 | -2011.5666 | 50.29% | 39.99% | 95% | 0% | 2749 | -216
[5 empty] | 2019-10-21 | 31 | 7046.5 | 2601 | -175 | 1 | 0 | 2776 | 2227.8648 | 2227.8648 | 2227.8648 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -200.2288 | 2027.636 | -3550 | -400 | -1922.364 | 48.06% | 39.98% | 95% | 0% | 2776 | -175
[5 empty] | 2019-10-21 | 32 | 7047 | 2675 | -151 | 1 | 0 | 2826 | 2306.183 | 2306.183 | 2306.183 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -172.7689 | 2133.4141 | -3550 | -400 | -1816.5859 | 45.41% | 39.98% | 95% | 0% | 2826 | -151
[5 empty] | 2019-10-21 | 33 | 7047.5 | 2780 | -125 | 1 | 0 | 2905 | 2429.9258 | 2429.9258 | 2429.9258 | 688.1286 | 780 | 200 | 1668.1286 | 41.7% | 95% | 0% | -143.0206 | 2286.9052 | -3550 | -400 | -1663.0948 | 41.58% | 39.97% | 95% | 0% | 2905 | -125
[5 empty] | 2019-10-21 | 34 | 7048 | 2869 | -105 | 1 | 0 | 2974 | 2538.0049 | 2538.0049 | 2538.0049 | 686.5622 | 780 | 200 | 1666.5622 | 41.66% | 95% | 0% | -120.1373 | 2417.8676 | -3550 | -400 | -1532.1324 | 38.3% | 39.97% | 95% | 0% | 2974 | -105
[5 empty] | 2019-10-21 | 35 | 7048.5 | 2961 | -87 | 1 | 0 | 3048 | 2653.9159 | 2653.9159 | 2653.9159 | 686.5622 | 780 | 200 | 1666.5622 | 41.66% | 95% | 0% | -99.5423 | 2554.3736 | -3550 | -400 | -1395.6264 | 34.89% | 39.95% | 95% | 0% | 3048 | -87
[5 empty] | 2019-10-21 | 36 | 7049 | 3007 | -73 | 1 | 0 | 3080 | 2704.0396 | 2704.0396 | 2704.0396 | 686.5622 | 780 | 200 | 1666.5622 | 41.66% | 95% | 0% | -83.524 | 2620.5155 | -3550 | -400 | -1329.4845 | 33.24% | 39.95% | 95% | 0% | 3080 | -73
[5 empty] | 2019-10-21 | 37 | 7049.5 | 3078 | -72 | 1 | 0 | 3150 | 2813.6851 | 2813.6851 | 2813.6851 | 686.5622 | 780 | 200 | 1666.5622 | 41.66% | 95% | 0% | -82.3799 | 2731.3052 | -3550 | -400 | -1218.6948 | 30.47% | 39.95% | 95% | 0% | 3150 | -72
[5 empty] | 2019-10-21 | 38 | 7050 | 3109 | -72 | 1 | 0 | 3181 | 2862.2424 | 2862.2424 | 2862.2424 | 686.5622 | 780 | 200 | 1666.5622 | 41.66% | 95% | 0% | -82.3799 | 2779.8625 | -3550 | -400 | -1170.1375 | 29.25% | 39.95% | 95% | 0% | 3181 | -72
[5 empty] | 2019-10-21 | 39 | 7050.5 | 3075 | -73 | 0 | 0 | 3148 | 2810.5523 | 2810.5523 | 2810.5523 | 686.5622 | 780 | 200 | 1666.5622 | 41.66% | 95% | 0% | -83.524 | 2727.0283 | -2750 | -200 | -222.9717 | 5.574% | 39.92% | 95% | 0% | 3148 | -73
[5 empty] | 2019-10-21 | 40 | 7051 | 2988 | -73 | 0 | 0 | 3061 | 2674.2786 | 2674.2786 | 2674.2786 | 686.5622 | 780 | 200 | 1666.5622 | 41.66% | 95% | 0% | -83.524 | 2590.7546 | -2750 | -200 | -359.2454 | 8.981% | 39.92% | 95% | 0% | 3061 | -73
[5 empty] | 2019-10-21 | 41 | 7051.5 | 2878 | -73 | 0 | 0 | 2951 | 2501.9786 | 2501.9786 | 2501.9786 | 686.5622 | 780 | 200 | 1666.5622 | 41.66% | 95% | 0% | -83.524 | 2418.4545 | -2750 | -200 | -531.5455 | 13.29% | 39.92% | 95% | 0% | 2951 | -73
[5 empty] | 2019-10-21 | 42 | 7052 | 2764 | -72 | 0 | 0 | 2836 | 2321.8467 | 2321.8467 | 2321.8467 | 684.9959 | 780 | 200 | 1664.9959 | 41.62% | 95% | 0% | -82.3799 | 2239.4668 | -2750 | -200 | -710.5332 | 17.76% | 39.92% | 95% | 0% | 2836 | -72
[5 empty] | 2019-10-21 | 43 | 7052.5 | 2633 | -73 | 0 | 0 | 2706 | 2118.2193 | 2118.2193 | 2118.2193 | 684.9959 | 780 | 200 | 1664.9959 | 41.62% | 95% | 0% | -83.524 | 2034.6953 | -2750 | -200 | -915.3047 | 22.88% | 39.92% | 95% | 0% | 2706 | -73
[5 empty] | 2019-10-21 | 44 | 7053 | 2471 | -73 | 0 | 0 | 2544 | 1864.4683 | 1864.4683 | 1864.4683 | 684.9959 | 780 | 200 | 1664.9959 | 41.62% | 95% | 0% | -83.524 | 1780.9442 | -2750 | -200 | -1169.0558 | 29.23% | 39.91% | 95% | 0% | 2544 | -73
[5 empty] | 2019-10-21 | 45 | 7053.5 | 2308 | -75 | 0 | 0 | 2383 | 1612.2836 | 1612.2836 | 1612.2836 | 684.9959 | 780 | 200 | 1664.9959 | 41.62% | 95% | 0% | -85.8124 | 1526.4712 | -2750 | -200 | -1423.5288 | 35.59% | 39.89% | 95% | 0% | 2383 | -75
[5 empty] | 2019-10-21 | 46 | 7054 | 2148 | -77 | 0 | 0 | 2225 | 1364.798 | 1364.798 | 1364.798 | 684.9959 | 780 | 200 | 1664.9959 | 41.62% | 95% | 0% | -88.1007 | 1276.6973 | -2750 | -200 | -1673.3027 | 41.83% | 39.88% | 95% | 0% | 2225 | -77
[5 empty] | 2019-10-21 | 47 | 7054.5 | 1984 | -78 | 0 | 0 | 2062 | 1109.4806 | 1109.4806 | 1109.4806 | 684.9959 | 780 | 200 | 1664.9959 | 41.62% | 95% | 0% | -89.2449 | 1020.2358 | -2750 | -200 | -1929.7642 | 48.24% | 39.88% | 95% | 0% | 2062 | -78
[5 empty] | 2019-10-21 | 48 | 7055 | 1869 | -79 | 0 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 684.9959 | 780 | 200 | 1664.9959 | 41.62% | 95% | 0% | -90.389 | 840.5261 | -2750 | -200 | -2109.4739 | 52.74% | 39.87% | 95% | 0% | 1948 | -79
[5 empty] | 2019-10-22 | 1 | 7055.5 | 1787 | -81 | 0 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 684.9959 | 780 | 200 | 1664.9959 | 41.62% | 95% | 0% | -92.6773 | 712.9286 | -2750 | -200 | -2237.0714 | 55.93% | 39.87% | 95% | 0% | 1868 | -81
[5 empty] | 2019-10-22 | 2 | 7056 | 1740 | -84 | 0 | 0 | 1824 | 736.6859 | 736.6859 | 736.6859 | 684.9959 | 780 | 200 | 1664.9959 | 41.62% | 95% | 0% | -96.1098 | 640.5761 | -2750 | -200 | -2309.4239 | 57.74% | 39.86% | 95% | 0% | 1824 | -84
[5 empty] | 2019-10-22 | 3 | 7056.5 | 1736 | -84 | 0 | 0 | 1820 | 730.4204 | 730.4204 | 730.4204 | 684.9959 | 780 | 200 | 1664.9959 | 41.62% | 95% | 0% | -96.1098 | 634.3106 | -2750 | -200 | -2315.6894 | 57.89% | 39.86% | 95% | 0% | 1820 | -84
[5 empty] | 2019-10-22 | 4 | 7057 | 1769 | -85 | 0 | 0 | 1854 | 783.6768 | 783.6768 | 783.6768 | 684.9959 | 780 | 200 | 1664.9959 | 41.62% | 95% | 0% | -97.254 | 686.4228 | -2750 | -200 | -2263.5772 | 56.59% | 39.86% | 95% | 0% | 1854 | -85
[5 empty] | 2019-10-22 | 5 | 7057.5 | 1746 | -87 | 0 | 0 | 1833 | 750.7832 | 750.7832 | 750.7832 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -99.5423 | 651.2408 | -2750 | -200 | -2298.7592 | 57.47% | 39.85% | 95% | 0% | 1833 | -87
[5 empty] | 2019-10-22 | 6 | 7058 | 1719 | -88 | 0 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -100.6865 | 609.3712 | -2750 | -200 | -2340.6288 | 58.52% | 39.85% | 95% | 0% | 1807 | -88
[5 empty] | 2019-10-22 | 7 | 7058.5 | 1694 | -89 | 0 | 0 | 1783 | 672.465 | 672.465 | 672.465 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -101.8307 | 570.6343 | -2750 | -200 | -2379.3657 | 59.48% | 39.85% | 95% | 0% | 1783 | -89
[5 empty] | 2019-10-22 | 8 | 7059 | 1678 | -90 | 0 | 0 | 1768 | 648.9695 | 648.9695 | 648.9695 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -102.9748 | 545.9947 | -2750 | -200 | -2404.0053 | 60.1% | 39.85% | 95% | 0% | 1768 | -90
[5 empty] | 2019-10-22 | 9 | 7059.5 | 1668 | -90 | 0 | 0 | 1758 | 633.3059 | 633.3059 | 633.3059 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -102.9748 | 530.331 | -2750 | -200 | -2419.669 | 60.49% | 39.84% | 95% | 0% | 1758 | -90
[5 empty] | 2019-10-22 | 10 | 7060 | 1681 | -91 | 1 | 0 | 1772 | 655.235 | 655.235 | 655.235 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -104.119 | 551.116 | -3550 | -400 | -3398.884 | 84.97% | 39.84% | 95% | 0% | 1772 | -91
[5 empty] | 2019-10-22 | 11 | 7060.5 | 1744 | -92 | 1 | 0 | 1836 | 755.4823 | 755.4823 | 755.4823 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -105.2632 | 650.2191 | -3550 | -400 | -3299.7809 | 82.49% | 39.83% | 95% | 0% | 1836 | -92
[5 empty] | 2019-10-22 | 12 | 7061 | 1841 | -93 | 1 | 0 | 1934 | 908.986 | 908.986 | 908.986 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -106.4073 | 802.5787 | -3550 | -400 | -3147.4213 | 78.69% | 39.83% | 95% | 0% | 1934 | -93
[5 empty] | 2019-10-22 | 13 | 7061.5 | 2061 | -94 | 1 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -107.5515 | 1147.601 | -3550 | -400 | -2802.399 | 70.06% | 39.82% | 95% | 0% | 2155 | -94
[5 empty] | 2019-10-22 | 14 | 7062 | 2288 | -95 | 1 | 0 | 2383 | 1612.2836 | 1612.2836 | 1612.2836 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -108.6957 | 1503.5879 | -3550 | -400 | -2446.4121 | 61.16% | 39.82% | 95% | 0% | 2383 | -95
[5 empty] | 2019-10-22 | 15 | 7062.5 | 2535 | -94 | 1 | 0 | 2629 | 1997.6092 | 1997.6092 | 1997.6092 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -107.5515 | 1890.0577 | -3550 | -400 | -2059.9423 | 51.5% | 39.82% | 95% | 0% | 2629 | -94
[5 empty] | 2019-10-22 | 16 | 7063 | 2660 | -95 | 1 | 0 | 2755 | 2194.9711 | 2194.9711 | 2194.9711 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -108.6957 | 2086.2755 | -3550 | -400 | -1863.7245 | 46.59% | 39.82% | 95% | 0% | 2755 | -95
[5 empty] | 2019-10-22 | 17 | 7063.5 | 2719 | -108 | 1 | 0 | 2827 | 2307.7494 | 2307.7494 | 2307.7494 | 683.4295 | 780 | 200 | 1663.4295 | 41.59% | 95% | 0% | -123.5698 | 2184.1796 | -3550 | -400 | -1765.8204 | 44.15% | 39.81% | 95% | 0% | 2827 | -108
[5 empty] | 2019-10-22 | 18 | 7064 | 2694 | -137 | 1 | 0 | 2831 | 2314.0148 | 2314.0148 | 2314.0148 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -156.7506 | 2157.2643 | -3550 | -400 | -1792.7357 | 44.82% | 39.81% | 95% | 0% | 2831 | -137
[5 empty] | 2019-10-22 | 19 | 7064.5 | 2658 | -177 | 1 | 0 | 2835 | 2320.2803 | 2320.2803 | 2320.2803 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -202.5172 | 2117.7631 | -3550 | -400 | -1832.2369 | 45.81% | 39.8% | 95% | 0% | 2835 | -177
[5 empty] | 2019-10-22 | 20 | 7065 | 2568 | -225 | 1 | 0 | 2793 | 2254.493 | 2254.493 | 2254.493 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -257.4371 | 1997.0559 | -3550 | -400 | -1952.9441 | 48.82% | 39.77% | 95% | 0% | 2793 | -225
[5 empty] | 2019-10-22 | 21 | 7065.5 | 2450 | -284 | 1 | 0 | 2734 | 2162.0775 | 2162.0775 | 2162.0775 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -324.9428 | 1837.1347 | -3550 | -400 | -2112.8653 | 52.82% | 39.77% | 95% | 0% | 2734 | -284
[5 empty] | 2019-10-22 | 22 | 7066 | 2312 | -368 | 1 | 0 | 2680 | 2077.4938 | 2077.4938 | 2077.4938 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -421.0526 | 1656.4412 | -3550 | -400 | -2293.5588 | 57.34% | 39.76% | 95% | 0% | 2680 | -368
[5 empty] | 2019-10-22 | 23 | 7066.5 | 2198 | -440 | 1 | 0 | 2638 | 2011.7065 | 2011.7065 | 2011.7065 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -503.4325 | 1508.274 | -3550 | -400 | -2441.726 | 61.04% | 39.74% | 95% | 0% | 2638 | -440
[5 empty] | 2019-10-22 | 24 | 7067 | 2108 | -485 | 1 | 0 | 2593 | 1941.2201 | 1941.2201 | 1941.2201 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -554.9199 | 1386.3002 | -3550 | -400 | -2563.6998 | 64.09% | 39.74% | 95% | 0% | 2593 | -485
[5 empty] | 2019-10-22 | 25 | 7067.5 | 2046 | -511 | 1 | 0 | 2557 | 1884.831 | 1884.831 | 1884.831 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -584.6682 | 1300.1628 | -3550 | -400 | -2649.8372 | 66.25% | 39.74% | 95% | 0% | 2557 | -511
[5 empty] | 2019-10-22 | 26 | 7068 | 2015 | -507 | 1 | 0 | 2522 | 1830.0082 | 1830.0082 | 1830.0082 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -580.0915 | 1249.9167 | -3550 | -400 | -2700.0833 | 67.5% | 39.74% | 95% | 0% | 2522 | -507
[5 empty] | 2019-10-22 | 27 | 7068.5 | 2015 | -492 | 1 | 0 | 2507 | 1806.5128 | 1806.5128 | 1806.5128 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -562.9291 | 1243.5837 | -3550 | -400 | -2706.4163 | 67.66% | 39.73% | 95% | 0% | 2507 | -492
[5 empty] | 2019-10-22 | 28 | 7069 | 2037 | -455 | 1 | 0 | 2492 | 1783.0173 | 1783.0173 | 1783.0173 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -520.595 | 1262.4223 | -3550 | -400 | -2687.5777 | 67.19% | 39.73% | 95% | 0% | 2492 | -455
[5 empty] | 2019-10-22 | 29 | 7069.5 | 2072 | -432 | 1 | 0 | 2504 | 1801.8137 | 1801.8137 | 1801.8137 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -494.2792 | 1307.5345 | -3550 | -400 | -2642.4655 | 66.06% | 39.73% | 95% | 0% | 2504 | -432
[5 empty] | 2019-10-22 | 30 | 7070 | 2135 | -387 | 1 | 0 | 2522 | 1830.0082 | 1830.0082 | 1830.0082 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -442.7918 | 1387.2165 | -3550 | -400 | -2562.7835 | 64.07% | 39.73% | 95% | 0% | 2522 | -387
[5 empty] | 2019-10-22 | 31 | 7070.5 | 2199 | -352 | 1 | 0 | 2551 | 1875.4328 | 1875.4328 | 1875.4328 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -402.746 | 1472.6868 | -3550 | -400 | -2477.3132 | 61.93% | 39.72% | 95% | 0% | 2551 | -352
[5 empty] | 2019-10-22 | 32 | 7071 | 2342 | -280 | 1 | 0 | 2622 | 1986.6447 | 1986.6447 | 1986.6447 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -320.3661 | 1666.2785 | -3550 | -400 | -2283.7215 | 57.09% | 39.72% | 95% | 0% | 2622 | -280
[5 empty] | 2019-10-22 | 33 | 7071.5 | 2477 | -231 | 1 | 0 | 2708 | 2121.352 | 2121.352 | 2121.352 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -264.3021 | 1857.05 | -3550 | -400 | -2092.95 | 52.32% | 39.72% | 95% | 0% | 2708 | -231
[5 empty] | 2019-10-22 | 34 | 7072 | 2648 | -177 | 1 | 0 | 2825 | 2304.6167 | 2304.6167 | 2304.6167 | 681.8631 | 780 | 200 | 1661.8631 | 41.55% | 95% | 0% | -202.5172 | 2102.0995 | -3550 | -400 | -1847.9005 | 46.2% | 39.71% | 95% | 0% | 2825 | -177
[5 empty] | 2019-10-22 | 35 | 7072.5 | 2779 | -127 | 1 | 0 | 2906 | 2431.4922 | 2431.4922 | 2431.4922 | 680.2968 | 780 | 200 | 1660.2968 | 41.51% | 95% | 0% | -145.3089 | 2286.1832 | -3550 | -400 | -1663.8168 | 41.6% | 39.71% | 95% | 0% | 2906 | -127
[5 empty] | 2019-10-22 | 36 | 7073 | 2880 | -101 | 1 | 0 | 2981 | 2548.9695 | 2548.9695 | 2548.9695 | 680.2968 | 780 | 200 | 1660.2968 | 41.51% | 95% | 0% | -115.5606 | 2433.4089 | -3550 | -400 | -1516.5911 | 37.91% | 39.71% | 95% | 0% | 2981 | -101
[5 empty] | 2019-10-22 | 37 | 7073.5 | 3023 | -99 | 1 | 0 | 3122 | 2769.8269 | 2769.8269 | 2769.8269 | 680.2968 | 780 | 200 | 1660.2968 | 41.51% | 95% | 0% | -113.2723 | 2656.5546 | -3550 | -400 | -1293.4454 | 32.34% | 39.71% | 95% | 0% | 3122 | -99
[5 empty] | 2019-10-22 | 38 | 7074 | 3069 | -100 | 1 | 0 | 3169 | 2843.446 | 2843.446 | 2843.446 | 680.2968 | 780 | 200 | 1660.2968 | 41.51% | 95% | 0% | -114.4165 | 2729.0295 | -3550 | -400 | -1220.9705 | 30.52% | 39.71% | 95% | 0% | 3169 | -100
[5 empty] | 2019-10-22 | 39 | 7074.5 | 3003 | -101 | 0 | 0 | 3104 | 2741.6323 | 2741.6323 | 2741.6323 | 680.2968 | 780 | 200 | 1660.2968 | 41.51% | 95% | 0% | -115.5606 | 2626.0717 | -2750 | -200 | -323.9283 | 8.098% | 39.71% | 95% | 0% | 3104 | -101
[5 empty] | 2019-10-22 | 40 | 7075 | 2892 | -102 | 0 | 0 | 2994 | 2569.3322 | 2569.3322 | 2569.3322 | 680.2968 | 780 | 200 | 1660.2968 | 41.51% | 95% | 0% | -116.7048 | 2452.6274 | -2750 | -200 | -497.3726 | 12.43% | 39.7% | 95% | 0% | 2994 | -102
[5 empty] | 2019-10-22 | 41 | 7075.5 | 2784 | -103 | 0 | 0 | 2887 | 2401.7312 | 2401.7312 | 2401.7312 | 680.2968 | 780 | 200 | 1660.2968 | 41.51% | 95% | 0% | -117.849 | 2283.8823 | -2750 | -200 | -666.1177 | 16.65% | 39.69% | 95% | 0% | 2887 | -103
[5 empty] | 2019-10-22 | 42 | 7076 | 2674 | -103 | 0 | 0 | 2777 | 2229.4312 | 2229.4312 | 2229.4312 | 680.2968 | 780 | 200 | 1660.2968 | 41.51% | 95% | 0% | -117.849 | 2111.5822 | -2750 | -200 | -838.4178 | 20.96% | 39.69% | 95% | 0% | 2777 | -103
[5 empty] | 2019-10-22 | 43 | 7076.5 | 2564 | -104 | 0 | 0 | 2668 | 2058.6974 | 2058.6974 | 2058.6974 | 680.2968 | 780 | 200 | 1660.2968 | 41.51% | 95% | 0% | -118.9931 | 1939.7043 | -2750 | -200 | -1010.2957 | 25.26% | 39.69% | 95% | 0% | 2668 | -104
[5 empty] | 2019-10-22 | 44 | 7077 | 2405 | -105 | 0 | 0 | 2510 | 1811.2119 | 1811.2119 | 1811.2119 | 680.2968 | 780 | 200 | 1660.2968 | 41.51% | 95% | 0% | -120.1373 | 1691.0746 | -2750 | -200 | -1258.9254 | 31.47% | 39.68% | 95% | 0% | 2510 | -105
[5 empty] | 2019-10-22 | 45 | 7077.5 | 2252 | -106 | 0 | 0 | 2358 | 1573.1245 | 1573.1245 | 1573.1245 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -121.2815 | 1451.843 | -2750 | -200 | -1498.157 | 37.45% | 39.68% | 95% | 0% | 2358 | -106
[5 empty] | 2019-10-22 | 46 | 7078 | 2095 | -107 | 0 | 0 | 2202 | 1328.7716 | 1328.7716 | 1328.7716 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -122.4256 | 1206.346 | -2750 | -200 | -1743.654 | 43.59% | 39.67% | 95% | 0% | 2202 | -107
[5 empty] | 2019-10-22 | 47 | 7078.5 | 1933 | -107 | 0 | 0 | 2040 | 1075.0206 | 1075.0206 | 1075.0206 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -122.4256 | 952.595 | -2750 | -200 | -1997.405 | 49.94% | 39.67% | 95% | 0% | 2040 | -107
[5 empty] | 2019-10-22 | 48 | 7079 | 1817 | -107 | 0 | 0 | 1924 | 893.3223 | 893.3223 | 893.3223 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -122.4256 | 770.8967 | -2750 | -200 | -2179.1033 | 54.48% | 39.66% | 95% | 0% | 1924 | -107
[5 empty] | 2019-10-23 | 1 | 7079.5 | 1718 | -106 | 0 | 0 | 1824 | 736.6859 | 736.6859 | 736.6859 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -121.2815 | 615.4044 | -2750 | -200 | -2334.5956 | 58.36% | 39.66% | 95% | 0% | 1824 | -106
[5 empty] | 2019-10-23 | 2 | 7080 | 1685 | -104 | 0 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -118.9931 | 562.87 | -2750 | -200 | -2387.13 | 59.68% | 39.65% | 95% | 0% | 1789 | -104
[5 empty] | 2019-10-23 | 3 | 7080.5 | 1680 | -104 | 0 | 0 | 1784 | 674.0313 | 674.0313 | 674.0313 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -118.9931 | 555.0382 | -2750 | -200 | -2394.9618 | 59.87% | 39.65% | 95% | 0% | 1784 | -104
[5 empty] | 2019-10-23 | 4 | 7081 | 1712 | -104 | 0 | 0 | 1816 | 724.155 | 724.155 | 724.155 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -118.9931 | 605.1619 | -2750 | -200 | -2344.8381 | 58.62% | 39.64% | 95% | 0% | 1816 | -104
[5 empty] | 2019-10-23 | 5 | 7081.5 | 1711 | -104 | 0 | 0 | 1815 | 722.5886 | 722.5886 | 722.5886 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -118.9931 | 603.5955 | -2750 | -200 | -2346.4045 | 58.66% | 39.62% | 95% | 0% | 1815 | -104
[5 empty] | 2019-10-23 | 6 | 7082 | 1688 | -104 | 0 | 0 | 1792 | 686.5622 | 686.5622 | 686.5622 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -118.9931 | 567.5691 | -2750 | -200 | -2382.4309 | 59.56% | 39.62% | 95% | 0% | 1792 | -104
[5 empty] | 2019-10-23 | 7 | 7082.5 | 1668 | -103 | 0 | 0 | 1771 | 653.6686 | 653.6686 | 653.6686 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -117.849 | 535.8196 | -2750 | -200 | -2414.1804 | 60.35% | 39.62% | 95% | 0% | 1771 | -103
[5 empty] | 2019-10-23 | 8 | 7083 | 1655 | -101 | 0 | 0 | 1756 | 630.1731 | 630.1731 | 630.1731 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -115.5606 | 514.6125 | -2750 | -200 | -2435.3875 | 60.88% | 39.61% | 95% | 0% | 1756 | -101
[5 empty] | 2019-10-23 | 9 | 7083.5 | 1653 | -102 | 0 | 0 | 1755 | 628.6068 | 628.6068 | 628.6068 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -116.7048 | 511.902 | -2750 | -200 | -2438.098 | 60.95% | 39.61% | 95% | 0% | 1755 | -102
[5 empty] | 2019-10-23 | 10 | 7084 | 1672 | -103 | 0 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 678.7304 | 780 | 200 | 1658.7304 | 41.47% | 95% | 0% | -117.849 | 542.0851 | -2750 | -200 | -2407.9149 | 60.2% | 39.61% | 95% | 0% | 1775 | -103
[5 empty] | 2019-10-23 | 11 | 7084.5 | 1740 | -104 | 0 | 0 | 1844 | 768.0132 | 768.0132 | 768.0132 | 677.1641 | 780 | 200 | 1657.1641 | 41.43% | 95% | 0% | -118.9931 | 649.0201 | -2750 | -200 | -2300.9799 | 57.52% | 39.6% | 95% | 0% | 1844 | -104
[5 empty] | 2019-10-23 | 12 | 7085 | 1835 | -105 | 0 | 0 | 1940 | 918.3842 | 918.3842 | 918.3842 | 677.1641 | 780 | 200 | 1657.1641 | 41.43% | 95% | 0% | -120.1373 | 798.2469 | -2750 | -200 | -2151.7531 | 53.79% | 39.6% | 95% | 0% | 1940 | -105
[5 empty] | 2019-10-23 | 13 | 7085.5 | 2041 | -105 | 0 | 0 | 2146 | 1241.0552 | 1241.0552 | 1241.0552 | 677.1641 | 780 | 200 | 1657.1641 | 41.43% | 95% | 0% | -120.1373 | 1120.9179 | -2750 | -200 | -1829.0821 | 45.73% | 39.59% | 95% | 0% | 2146 | -105
[5 empty] | 2019-10-23 | 14 | 7086 | 2275 | -106 | 0 | 0 | 2381 | 1609.1509 | 1609.1509 | 1609.1509 | 677.1641 | 780 | 200 | 1657.1641 | 41.43% | 95% | 0% | -121.2815 | 1487.8694 | -2750 | -200 | -1462.1306 | 36.55% | 39.58% | 95% | 0% | 2381 | -106
[5 empty] | 2019-10-23 | 15 | 7086.5 | 2529 | -106 | 0 | 0 | 2635 | 2007.0074 | 2007.0074 | 2007.0074 | 677.1641 | 780 | 200 | 1657.1641 | 41.43% | 95% | 0% | -121.2815 | 1885.726 | -2750 | -200 | -1064.274 | 26.61% | 39.58% | 95% | 0% | 2635 | -106
[5 empty] | 2019-10-23 | 16 | 7087 | 2651 | -107 | 0 | 0 | 2758 | 2199.6702 | 2199.6702 | 2199.6702 | 677.1641 | 780 | 200 | 1657.1641 | 41.43% | 95% | 0% | -122.4256 | 2077.2446 | -2750 | -200 | -872.7554 | 21.82% | 39.57% | 95% | 0% | 2758 | -107
[5 empty] | 2019-10-23 | 17 | 7087.5 | 2729 | -125 | 0 | 0 | 2854 | 2350.0412 | 2350.0412 | 2350.0412 | 677.1641 | 780 | 200 | 1657.1641 | 41.43% | 95% | 0% | -143.0206 | 2207.0206 | -2750 | -200 | -742.9794 | 18.57% | 39.56% | 95% | 0% | 2854 | -125
[5 empty] | 2019-10-23 | 18 | 7088 | 2681 | -172 | 0 | 0 | 2853 | 2348.4749 | 2348.4749 | 2348.4749 | 677.1641 | 780 | 200 | 1657.1641 | 41.43% | 95% | 0% | -196.7963 | 2151.6785 | -2750 | -200 | -798.3215 | 19.96% | 39.55% | 95% | 0% | 2853 | -172
[5 empty] | 2019-10-23 | 19 | 7088.5 | 2642 | -203 | 1 | 0 | 2845 | 2335.9439 | 2335.9439 | 2335.9439 | 677.1641 | 780 | 200 | 1657.1641 | 41.43% | 95% | 0% | -232.2654 | 2103.6785 | -3550 | -400 | -1846.3215 | 46.16% | 39.55% | 95% | 0% | 2845 | -203
[5 empty] | 2019-10-23 | 20 | 7089 | 2570 | -235 | 1 | 0 | 2805 | 2273.2894 | 2273.2894 | 2273.2894 | 677.1641 | 780 | 200 | 1657.1641 | 41.43% | 95% | 0% | -268.8787 | 2004.4106 | -3550 | -400 | -1945.5894 | 48.64% | 39.55% | 95% | 0% | 2805 | -235
[5 empty] | 2019-10-23 | 21 | 7089.5 | 2452 | -315 | 1 | 0 | 2767 | 2213.7675 | 2213.7675 | 2213.7675 | 677.1641 | 780 | 200 | 1657.1641 | 41.43% | 95% | 0% | -360.4119 | 1853.3556 | -3550 | -400 | -2096.6444 | 52.42% | 39.54% | 95% | 0% | 2767 | -315
[5 empty] | 2019-10-23 | 22 | 7090 | 2365 | -359 | 1 | 0 | 2724 | 2146.4138 | 2146.4138 | 2146.4138 | 677.1641 | 780 | 200 | 1657.1641 | 41.43% | 95% | 0% | -410.7551 | 1735.6587 | -3550 | -400 | -2214.3413 | 55.36% | 39.53% | 95% | 0% | 2724 | -359
[5 empty] | 2019-10-23 | 23 | 7090.5 | 2293 | -396 | 1 | 0 | 2689 | 2091.5911 | 2091.5911 | 2091.5911 | 675.5977 | 780 | 200 | 1655.5977 | 41.39% | 95% | 0% | -453.0892 | 1638.5019 | -3550 | -400 | -2311.4981 | 57.79% | 39.53% | 95% | 0% | 2689 | -396
[5 empty] | 2019-10-23 | 24 | 7091 | 2204 | -444 | 1 | 0 | 2648 | 2027.3702 | 2027.3702 | 2027.3702 | 675.5977 | 780 | 200 | 1655.5977 | 41.39% | 95% | 0% | -508.0092 | 1519.361 | -3550 | -400 | -2430.639 | 60.77% | 39.52% | 95% | 0% | 2648 | -444
[5 empty] | 2019-10-23 | 25 | 7091.5 | 2171 | -458 | 1 | 0 | 2629 | 1997.6092 | 1997.6092 | 1997.6092 | 675.5977 | 780 | 200 | 1655.5977 | 41.39% | 95% | 0% | -524.0275 | 1473.5818 | -3550 | -400 | -2476.4182 | 61.91% | 39.5% | 95% | 0% | 2629 | -458
[5 empty] | 2019-10-23 | 26 | 7092 | 2167 | -444 | 1 | 0 | 2611 | 1969.4147 | 1969.4147 | 1969.4147 | 675.5977 | 780 | 200 | 1655.5977 | 41.39% | 95% | 0% | -508.0092 | 1461.4055 | -3550 | -400 | -2488.5945 | 62.21% | 39.5% | 95% | 0% | 2611 | -444
[5 empty] | 2019-10-23 | 27 | 7092.5 | 2117 | -467 | 1 | 0 | 2584 | 1927.1228 | 1927.1228 | 1927.1228 | 675.5977 | 780 | 200 | 1655.5977 | 41.39% | 95% | 0% | -534.3249 | 1392.7979 | -3550 | -400 | -2557.2021 | 63.93% | 39.49% | 95% | 0% | 2584 | -467
[5 empty] | 2019-10-23 | 28 | 7093 | 2137 | -426 | 1 | 0 | 2563 | 1894.2292 | 1894.2292 | 1894.2292 | 675.5977 | 780 | 200 | 1655.5977 | 41.39% | 95% | 0% | -487.4142 | 1406.815 | -3550 | -400 | -2543.185 | 63.58% | 39.47% | 95% | 0% | 2563 | -426
[5 empty] | 2019-10-23 | 29 | 7093.5 | 2210 | -361 | 1 | 0 | 2571 | 1906.7601 | 1906.7601 | 1906.7601 | 675.5977 | 780 | 200 | 1655.5977 | 41.39% | 95% | 0% | -413.0435 | 1493.7166 | -3550 | -400 | -2456.2834 | 61.41% | 39.47% | 95% | 0% | 2571 | -361
[5 empty] | 2019-10-23 | 30 | 7094 | 2286 | -315 | 1 | 0 | 2601 | 1953.751 | 1953.751 | 1953.751 | 675.5977 | 780 | 200 | 1655.5977 | 41.39% | 95% | 0% | -360.4119 | 1593.3391 | -3550 | -400 | -2356.6609 | 58.92% | 39.47% | 95% | 0% | 2601 | -315
[5 empty] | 2019-10-23 | 31 | 7094.5 | 2366 | -268 | 1 | 0 | 2634 | 2005.4411 | 2005.4411 | 2005.4411 | 675.5977 | 780 | 200 | 1655.5977 | 41.39% | 95% | 0% | -306.6362 | 1698.8049 | -3550 | -400 | -2251.1951 | 56.28% | 39.47% | 95% | 0% | 2634 | -268
[5 empty] | 2019-10-23 | 32 | 7095 | 2475 | -236 | 1 | 0 | 2711 | 2126.0511 | 2126.0511 | 2126.0511 | 674.0313 | 780 | 200 | 1654.0313 | 41.35% | 95% | 0% | -270.0229 | 1856.0282 | -3550 | -400 | -2093.9718 | 52.35% | 39.46% | 95% | 0% | 2711 | -236
[5 empty] | 2019-10-23 | 33 | 7095.5 | 2587 | -197 | 1 | 0 | 2784 | 2240.3957 | 2240.3957 | 2240.3957 | 674.0313 | 780 | 200 | 1654.0313 | 41.35% | 95% | 0% | -225.4005 | 2014.9953 | -3550 | -400 | -1935.0047 | 48.38% | 39.45% | 95% | 0% | 2784 | -197
[5 empty] | 2019-10-23 | 34 | 7096 | 2707 | -167 | 1 | 0 | 2874 | 2381.3685 | 2381.3685 | 2381.3685 | 674.0313 | 780 | 200 | 1654.0313 | 41.35% | 95% | 0% | -191.0755 | 2190.293 | -3550 | -400 | -1759.707 | 43.99% | 39.45% | 95% | 0% | 2874 | -167
[5 empty] | 2019-10-23 | 35 | 7096.5 | 2811 | -140 | 1 | 0 | 2951 | 2501.9786 | 2501.9786 | 2501.9786 | 674.0313 | 780 | 200 | 1654.0313 | 41.35% | 95% | 0% | -160.1831 | 2341.7955 | -3550 | -400 | -1608.2045 | 40.21% | 39.45% | 95% | 0% | 2951 | -140
[5 empty] | 2019-10-23 | 36 | 7097 | 2903 | -130 | 1 | 0 | 3033 | 2630.4204 | 2630.4204 | 2630.4204 | 674.0313 | 780 | 200 | 1654.0313 | 41.35% | 95% | 0% | -148.7414 | 2481.679 | -3550 | -400 | -1468.321 | 36.71% | 39.44% | 95% | 0% | 3033 | -130
[5 empty] | 2019-10-23 | 37 | 7097.5 | 3002 | -128 | 1 | 0 | 3130 | 2782.3578 | 2782.3578 | 2782.3578 | 674.0313 | 780 | 200 | 1654.0313 | 41.35% | 95% | 0% | -146.4531 | 2635.9047 | -3550 | -400 | -1314.0953 | 32.85% | 39.44% | 95% | 0% | 3130 | -128
[5 empty] | 2019-10-23 | 38 | 7098 | 3004 | -128 | 1 | 0 | 3132 | 2785.4905 | 2785.4905 | 2785.4905 | 674.0313 | 780 | 200 | 1654.0313 | 41.35% | 95% | 0% | -146.4531 | 2639.0374 | -3550 | -400 | -1310.9626 | 32.77% | 39.44% | 95% | 0% | 3132 | -128
[5 empty] | 2019-10-23 | 39 | 7098.5 | 2935 | -128 | 0 | 0 | 3063 | 2677.4114 | 2677.4114 | 2677.4114 | 674.0313 | 780 | 200 | 1654.0313 | 41.35% | 95% | 0% | -146.4531 | 2530.9583 | -2750 | -200 | -419.0417 | 10.48% | 39.44% | 95% | 0% | 3063 | -128
[5 empty] | 2019-10-23 | 40 | 7099 | 2840 | -128 | 0 | 0 | 2968 | 2528.6068 | 2528.6068 | 2528.6068 | 674.0313 | 780 | 200 | 1654.0313 | 41.35% | 95% | 0% | -146.4531 | 2382.1537 | -2750 | -200 | -567.8463 | 14.2% | 39.42% | 95% | 0% | 2968 | -128
[5 empty] | 2019-10-23 | 41 | 7099.5 | 2736 | -127 | 0 | 0 | 2863 | 2364.1385 | 2364.1385 | 2364.1385 | 674.0313 | 780 | 200 | 1654.0313 | 41.35% | 95% | 0% | -145.3089 | 2218.8296 | -2750 | -200 | -731.1704 | 18.28% | 39.42% | 95% | 0% | 2863 | -127
[5 empty] | 2019-10-23 | 42 | 7100 | 2614 | -127 | 0 | 0 | 2741 | 2173.042 | 2173.042 | 2173.042 | 672.465 | 780 | 200 | 1652.465 | 41.31% | 95% | 0% | -145.3089 | 2027.7331 | -2750 | -200 | -922.2669 | 23.06% | 39.41% | 95% | 0% | 2741 | -127
[5 empty] | 2019-10-23 | 43 | 7100.5 | 2495 | -127 | 0 | 0 | 2622 | 1986.6447 | 1986.6447 | 1986.6447 | 672.465 | 780 | 200 | 1652.465 | 41.31% | 95% | 0% | -145.3089 | 1841.3358 | -2750 | -200 | -1108.6642 | 27.72% | 39.41% | 95% | 0% | 2622 | -127
[5 empty] | 2019-10-23 | 44 | 7101 | 2340 | -127 | 0 | 0 | 2467 | 1743.8582 | 1743.8582 | 1743.8582 | 672.465 | 780 | 200 | 1652.465 | 41.31% | 95% | 0% | -145.3089 | 1598.5493 | -2750 | -200 | -1351.4507 | 33.79% | 39.41% | 95% | 0% | 2467 | -127
[5 empty] | 2019-10-23 | 45 | 7101.5 | 2192 | -126 | 0 | 0 | 2318 | 1510.4699 | 1510.4699 | 1510.4699 | 672.465 | 780 | 200 | 1652.465 | 41.31% | 95% | 0% | -144.1648 | 1366.3051 | -2750 | -200 | -1583.6949 | 39.59% | 39.4% | 95% | 0% | 2318 | -126
[5 empty] | 2019-10-23 | 46 | 7102 | 2031 | -124 | 0 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 672.465 | 780 | 200 | 1652.465 | 41.31% | 95% | 0% | -141.8764 | 1113.2761 | -2750 | -200 | -1836.7239 | 45.92% | 39.38% | 95% | 0% | 2155 | -124
[5 empty] | 2019-10-23 | 47 | 7102.5 | 1859 | -122 | 0 | 0 | 1981 | 982.6051 | 982.6051 | 982.6051 | 672.465 | 780 | 200 | 1652.465 | 41.31% | 95% | 0% | -139.5881 | 843.017 | -2750 | -200 | -2106.983 | 52.67% | 39.37% | 95% | 0% | 1981 | -122
[5 empty] | 2019-10-23 | 48 | 7103 | 1746 | -121 | 0 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -138.4439 | 665.5956 | -2750 | -200 | -2284.4044 | 57.11% | 39.37% | 95% | 0% | 1867 | -121
[5 empty] | 2019-10-24 | 1 | 7103.5 | 1665 | -117 | 0 | 0 | 1782 | 670.8986 | 670.8986 | 670.8986 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -133.8673 | 537.0313 | -2750 | -200 | -2412.9687 | 60.32% | 39.37% | 95% | 0% | 1782 | -117
[5 empty] | 2019-10-24 | 2 | 7104 | 1631 | -114 | 0 | 0 | 1745 | 612.9431 | 612.9431 | 612.9431 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -130.4348 | 482.5083 | -2750 | -200 | -2467.4917 | 61.69% | 39.36% | 95% | 0% | 1745 | -114
[5 empty] | 2019-10-24 | 3 | 7104.5 | 1633 | -111 | 0 | 0 | 1744 | 611.3768 | 611.3768 | 611.3768 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -127.0023 | 484.3745 | -2750 | -200 | -2465.6255 | 61.64% | 39.35% | 95% | 0% | 1744 | -111
[5 empty] | 2019-10-24 | 4 | 7105 | 1680 | -107 | 0 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -122.4256 | 556.3048 | -2750 | -200 | -2393.6952 | 59.84% | 39.34% | 95% | 0% | 1787 | -107
[5 empty] | 2019-10-24 | 5 | 7105.5 | 1685 | -104 | 0 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -118.9931 | 562.87 | -2750 | -200 | -2387.13 | 59.68% | 39.33% | 95% | 0% | 1789 | -104
[5 empty] | 2019-10-24 | 6 | 7106 | 1656 | -100 | 0 | 0 | 1756 | 630.1731 | 630.1731 | 630.1731 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -114.4165 | 515.7566 | -2750 | -200 | -2434.2434 | 60.86% | 39.32% | 95% | 0% | 1756 | -100
[5 empty] | 2019-10-24 | 7 | 7106.5 | 1637 | -97 | 0 | 0 | 1734 | 595.7131 | 595.7131 | 595.7131 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -110.984 | 484.7291 | -2750 | -200 | -2465.2709 | 61.63% | 39.31% | 95% | 0% | 1734 | -97
[5 empty] | 2019-10-24 | 8 | 7107 | 1624 | -94 | 0 | 0 | 1718 | 570.6513 | 570.6513 | 570.6513 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -107.5515 | 463.0998 | -2750 | -200 | -2486.9002 | 62.17% | 39.31% | 95% | 0% | 1718 | -94
[5 empty] | 2019-10-24 | 9 | 7107.5 | 1615 | -92 | 0 | 0 | 1707 | 553.4213 | 553.4213 | 553.4213 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -105.2632 | 448.1581 | -2750 | -200 | -2501.8419 | 62.55% | 39.31% | 95% | 0% | 1707 | -92
[5 empty] | 2019-10-24 | 10 | 7108 | 1627 | -90 | 0 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -102.9748 | 466.1101 | -2750 | -200 | -2483.8899 | 62.1% | 39.29% | 95% | 0% | 1717 | -90
[5 empty] | 2019-10-24 | 11 | 7108.5 | 1699 | -88 | 0 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -100.6865 | 578.0439 | -2750 | -200 | -2371.9561 | 59.3% | 39.29% | 95% | 0% | 1787 | -88
[5 empty] | 2019-10-24 | 12 | 7109 | 1799 | -85 | 0 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -97.254 | 733.4138 | -2750 | -200 | -2216.5862 | 55.41% | 39.29% | 95% | 0% | 1884 | -85
[5 empty] | 2019-10-24 | 13 | 7109.5 | 2014 | -83 | 0 | 0 | 2097 | 1164.3034 | 1164.3034 | 1164.3034 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -94.9657 | 1069.3377 | -2750 | -200 | -1880.6623 | 47.02% | 39.27% | 95% | 0% | 2097 | -83
[5 empty] | 2019-10-24 | 14 | 7110 | 2232 | -81 | 0 | 0 | 2313 | 1502.6381 | 1502.6381 | 1502.6381 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -92.6773 | 1409.9607 | -2750 | -200 | -1540.0393 | 38.5% | 39.26% | 95% | 0% | 2313 | -81
[5 empty] | 2019-10-24 | 15 | 7110.5 | 2491 | -79 | 0 | 0 | 2570 | 1905.1937 | 1905.1937 | 1905.1937 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -90.389 | 1814.8047 | -2750 | -200 | -1135.1953 | 28.38% | 39.24% | 95% | 0% | 2570 | -79
[5 empty] | 2019-10-24 | 16 | 7111 | 2627 | -78 | 0 | 0 | 2705 | 2116.6529 | 2116.6529 | 2116.6529 | 670.8986 | 780 | 200 | 1650.8986 | 41.27% | 95% | 0% | -89.2449 | 2027.4081 | -2750 | -200 | -922.5919 | 23.06% | 39.23% | 95% | 0% | 2705 | -78
[5 empty] | 2019-10-24 | 17 | 7111.5 | 2739 | -79 | 0 | 0 | 2818 | 2293.6521 | 2293.6521 | 2293.6521 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -90.389 | 2203.2631 | -2750 | -200 | -746.7369 | 18.67% | 39.23% | 95% | 0% | 2818 | -79
[5 empty] | 2019-10-24 | 18 | 7112 | 2729 | -86 | 0 | 0 | 2815 | 2288.953 | 2288.953 | 2288.953 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -98.3982 | 2190.5548 | -2750 | -200 | -759.4452 | 18.99% | 39.22% | 95% | 0% | 2815 | -86
[5 empty] | 2019-10-24 | 19 | 7112.5 | 2752 | -102 | 0 | 0 | 2854 | 2350.0412 | 2350.0412 | 2350.0412 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -116.7048 | 2233.3364 | -2750 | -200 | -716.6636 | 17.92% | 39.22% | 95% | 0% | 2854 | -102
[5 empty] | 2019-10-24 | 20 | 7113 | 2746 | -118 | 1 | 0 | 2864 | 2365.7049 | 2365.7049 | 2365.7049 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -135.0114 | 2230.6934 | -3550 | -400 | -1719.3066 | 42.98% | 39.21% | 95% | 0% | 2864 | -118
[5 empty] | 2019-10-24 | 21 | 7113.5 | 2728 | -140 | 1 | 0 | 2868 | 2371.9703 | 2371.9703 | 2371.9703 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -160.1831 | 2211.7873 | -3550 | -400 | -1738.2127 | 43.46% | 39.2% | 95% | 0% | 2868 | -140
[5 empty] | 2019-10-24 | 22 | 7114 | 2704 | -160 | 1 | 0 | 2864 | 2365.7049 | 2365.7049 | 2365.7049 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -183.0664 | 2182.6385 | -3550 | -400 | -1767.3615 | 44.18% | 39.19% | 95% | 0% | 2864 | -160
[5 empty] | 2019-10-24 | 23 | 7114.5 | 2665 | -189 | 1 | 0 | 2854 | 2350.0412 | 2350.0412 | 2350.0412 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -216.2471 | 2133.7941 | -3550 | -400 | -1816.2059 | 45.41% | 39.19% | 95% | 0% | 2854 | -189
[5 empty] | 2019-10-24 | 24 | 7115 | 2634 | -212 | 1 | 0 | 2846 | 2337.5103 | 2337.5103 | 2337.5103 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -242.5629 | 2094.9474 | -3550 | -400 | -1855.0526 | 46.38% | 39.17% | 95% | 0% | 2846 | -212
[5 empty] | 2019-10-24 | 25 | 7115.5 | 2589 | -239 | 1 | 0 | 2828 | 2309.3157 | 2309.3157 | 2309.3157 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -273.4554 | 2035.8604 | -3550 | -400 | -1914.1396 | 47.85% | 39.17% | 95% | 0% | 2828 | -239
[5 empty] | 2019-10-24 | 26 | 7116 | 2557 | -250 | 1 | 0 | 2807 | 2276.4221 | 2276.4221 | 2276.4221 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -286.0412 | 1990.3809 | -3550 | -400 | -1959.6191 | 48.99% | 39.17% | 95% | 0% | 2807 | -250
[5 empty] | 2019-10-24 | 27 | 7116.5 | 2516 | -261 | 1 | 0 | 2777 | 2229.4312 | 2229.4312 | 2229.4312 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -298.627 | 1930.8042 | -3550 | -400 | -2019.1958 | 50.48% | 39.16% | 95% | 0% | 2777 | -261
[5 empty] | 2019-10-24 | 28 | 7117 | 2487 | -269 | 1 | 0 | 2756 | 2196.5375 | 2196.5375 | 2196.5375 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -307.7803 | 1888.7572 | -3550 | -400 | -2061.2428 | 51.53% | 39.16% | 95% | 0% | 2756 | -269
[5 empty] | 2019-10-24 | 29 | 7117.5 | 2459 | -268 | 1 | 0 | 2727 | 2151.1129 | 2151.1129 | 2151.1129 | 669.3322 | 780 | 200 | 1649.3322 | 41.23% | 95% | 0% | -306.6362 | 1844.4768 | -3550 | -400 | -2105.5232 | 52.64% | 39.15% | 95% | 0% | 2727 | -268
[5 empty] | 2019-10-24 | 30 | 7118 | 2412 | -278 | 1 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -318.0778 | 1775.0797 | -3550 | -400 | -2174.9203 | 54.37% | 39.15% | 95% | 0% | 2690 | -278
[5 empty] | 2019-10-24 | 31 | 7118.5 | 2380 | -283 | 1 | 0 | 2663 | 2050.8656 | 2050.8656 | 2050.8656 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -323.7986 | 1727.067 | -3550 | -400 | -2222.933 | 55.57% | 39.14% | 95% | 0% | 2663 | -283
[5 empty] | 2019-10-24 | 32 | 7119 | 2430 | -264 | 1 | 0 | 2694 | 2099.4229 | 2099.4229 | 2099.4229 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -302.0595 | 1797.3634 | -3550 | -400 | -2152.6366 | 53.82% | 39.13% | 95% | 0% | 2694 | -264
[5 empty] | 2019-10-24 | 33 | 7119.5 | 2523 | -228 | 1 | 0 | 2751 | 2188.7057 | 2188.7057 | 2188.7057 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -260.8696 | 1927.8361 | -3550 | -400 | -2022.1639 | 50.55% | 39.13% | 95% | 0% | 2751 | -228
[5 empty] | 2019-10-24 | 34 | 7120 | 2623 | -194 | 1 | 0 | 2817 | 2292.0857 | 2292.0857 | 2292.0857 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -221.968 | 2070.1178 | -3550 | -400 | -1879.8822 | 47% | 39.13% | 95% | 0% | 2817 | -194
[5 empty] | 2019-10-24 | 35 | 7120.5 | 2762 | -145 | 1 | 0 | 2907 | 2433.0585 | 2433.0585 | 2433.0585 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -165.9039 | 2267.1546 | -3550 | -400 | -1682.8454 | 42.07% | 39.12% | 95% | 0% | 2907 | -145
[5 empty] | 2019-10-24 | 36 | 7121 | 2834 | -124 | 1 | 0 | 2958 | 2512.9431 | 2512.9431 | 2512.9431 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -141.8764 | 2371.0667 | -3550 | -400 | -1578.9333 | 39.47% | 39.12% | 95% | 0% | 2958 | -124
[5 empty] | 2019-10-24 | 37 | 7121.5 | 2938 | -121 | 1 | 0 | 3059 | 2671.1459 | 2671.1459 | 2671.1459 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -138.4439 | 2532.702 | -3550 | -400 | -1417.298 | 35.43% | 39.11% | 95% | 0% | 3059 | -121
[5 empty] | 2019-10-24 | 38 | 7122 | 2958 | -121 | 1 | 0 | 3079 | 2702.4732 | 2702.4732 | 2702.4732 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -138.4439 | 2564.0293 | -3550 | -400 | -1385.9707 | 34.65% | 39.1% | 95% | 0% | 3079 | -121
[5 empty] | 2019-10-24 | 39 | 7122.5 | 2884 | -119 | 0 | 0 | 3003 | 2583.4295 | 2583.4295 | 2583.4295 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -136.1556 | 2447.2739 | -2750 | -200 | -502.7261 | 12.57% | 39.1% | 95% | 0% | 3003 | -119
[5 empty] | 2019-10-24 | 40 | 7123 | 2803 | -118 | 0 | 0 | 2921 | 2454.9876 | 2454.9876 | 2454.9876 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -135.0114 | 2319.9762 | -2750 | -200 | -630.0238 | 15.75% | 39.1% | 95% | 0% | 2921 | -118
[5 empty] | 2019-10-24 | 41 | 7123.5 | 2704 | -117 | 0 | 0 | 2821 | 2298.3512 | 2298.3512 | 2298.3512 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -133.8673 | 2164.4839 | -2750 | -200 | -785.5161 | 19.64% | 39.1% | 95% | 0% | 2821 | -117
[5 empty] | 2019-10-24 | 42 | 7124 | 2587 | -115 | 0 | 0 | 2702 | 2111.9538 | 2111.9538 | 2111.9538 | 667.7659 | 780 | 200 | 1647.7659 | 41.19% | 95% | 0% | -131.5789 | 1980.3749 | -2750 | -200 | -969.6251 | 24.24% | 39.09% | 95% | 0% | 2702 | -115
[5 empty] | 2019-10-24 | 43 | 7124.5 | 2494 | -114 | 0 | 0 | 2608 | 1964.7156 | 1964.7156 | 1964.7156 | 666.1995 | 780 | 200 | 1646.1995 | 41.15% | 95% | 0% | -130.4348 | 1834.2808 | -2750 | -200 | -1115.7192 | 27.89% | 39.07% | 95% | 0% | 2608 | -114
[5 empty] | 2019-10-24 | 44 | 7125 | 2365 | -112 | 0 | 0 | 2477 | 1759.5218 | 1759.5218 | 1759.5218 | 666.1995 | 780 | 200 | 1646.1995 | 41.15% | 95% | 0% | -128.1465 | 1631.3754 | -2750 | -200 | -1318.6246 | 32.97% | 39.06% | 95% | 0% | 2477 | -112
[5 empty] | 2019-10-24 | 45 | 7125.5 | 2219 | -111 | 0 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 666.1995 | 780 | 200 | 1646.1995 | 41.15% | 95% | 0% | -127.0023 | 1402.264 | -2750 | -200 | -1547.736 | 38.69% | 39.06% | 95% | 0% | 2330 | -111
[5 empty] | 2019-10-24 | 46 | 7126 | 2063 | -110 | 0 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 666.1995 | 780 | 200 | 1646.1995 | 41.15% | 95% | 0% | -125.8581 | 1157.4889 | -2750 | -200 | -1792.5111 | 44.81% | 39.06% | 95% | 0% | 2173 | -110
[5 empty] | 2019-10-24 | 47 | 7126.5 | 1910 | -109 | 0 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 666.1995 | 780 | 200 | 1646.1995 | 41.15% | 95% | 0% | -124.714 | 917.413 | -2750 | -200 | -2032.587 | 50.81% | 39.06% | 95% | 0% | 2019 | -109
[5 empty] | 2019-10-24 | 48 | 7127 | 1806 | -109 | 0 | 0 | 1915 | 879.2251 | 879.2251 | 879.2251 | 666.1995 | 780 | 200 | 1646.1995 | 41.15% | 95% | 0% | -124.714 | 754.5111 | -2750 | -200 | -2195.4889 | 54.89% | 39.05% | 95% | 0% | 1915 | -109
[5 empty] | 2019-10-25 | 1 | 7127.5 | 1727 | -104 | 0 | 0 | 1831 | 747.6505 | 747.6505 | 747.6505 | 664.6331 | 780 | 200 | 1644.6331 | 41.12% | 95% | 0% | -118.9931 | 628.6573 | -2750 | -200 | -2321.3427 | 58.03% | 39.05% | 95% | 0% | 1831 | -104
[5 empty] | 2019-10-25 | 2 | 7128 | 1685 | -99 | 0 | 0 | 1784 | 674.0313 | 674.0313 | 674.0313 | 664.6331 | 780 | 200 | 1644.6331 | 41.12% | 95% | 0% | -113.2723 | 560.759 | -2750 | -200 | -2389.241 | 59.73% | 39.04% | 95% | 0% | 1784 | -99
[5 empty] | 2019-10-25 | 3 | 7128.5 | 1682 | -99 | 0 | 0 | 1781 | 669.3322 | 669.3322 | 669.3322 | 664.6331 | 780 | 200 | 1644.6331 | 41.12% | 95% | 0% | -113.2723 | 556.0599 | -2750 | -200 | -2393.9401 | 59.85% | 39.04% | 95% | 0% | 1781 | -99
[5 empty] | 2019-10-25 | 4 | 7129 | 1722 | -99 | 0 | 0 | 1821 | 731.9868 | 731.9868 | 731.9868 | 664.6331 | 780 | 200 | 1644.6331 | 41.12% | 95% | 0% | -113.2723 | 618.7145 | -2750 | -200 | -2331.2855 | 58.28% | 39.04% | 95% | 0% | 1821 | -99
[5 empty] | 2019-10-25 | 5 | 7129.5 | 1710 | -97 | 0 | 0 | 1807 | 710.0577 | 710.0577 | 710.0577 | 664.6331 | 780 | 200 | 1644.6331 | 41.12% | 95% | 0% | -110.984 | 599.0737 | -2750 | -200 | -2350.9263 | 58.77% | 39.03% | 95% | 0% | 1807 | -97
[5 empty] | 2019-10-25 | 6 | 7130 | 1679 | -96 | 0 | 0 | 1775 | 659.934 | 659.934 | 659.934 | 664.6331 | 780 | 200 | 1644.6331 | 41.12% | 95% | 0% | -109.8398 | 550.0942 | -2750 | -200 | -2399.9058 | 60% | 39.03% | 95% | 0% | 1775 | -96
[5 empty] | 2019-10-25 | 7 | 7130.5 | 1655 | -95 | 0 | 0 | 1750 | 620.7749 | 620.7749 | 620.7749 | 664.6331 | 780 | 200 | 1644.6331 | 41.12% | 95% | 0% | -108.6957 | 512.0793 | -2750 | -200 | -2437.9207 | 60.95% | 39.03% | 95% | 0% | 1750 | -95
[5 empty] | 2019-10-25 | 8 | 7131 | 1631 | -95 | 0 | 0 | 1726 | 583.1822 | 583.1822 | 583.1822 | 663.0668 | 780 | 200 | 1643.0668 | 41.08% | 95% | 0% | -108.6957 | 474.4865 | -2750 | -200 | -2475.5135 | 61.89% | 39.03% | 95% | 0% | 1726 | -95
[5 empty] | 2019-10-25 | 9 | 7131.5 | 1629 | -95 | 0 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 663.0668 | 780 | 200 | 1643.0668 | 41.08% | 95% | 0% | -108.6957 | 471.3538 | -2750 | -200 | -2478.6462 | 61.97% | 39.01% | 95% | 0% | 1724 | -95
[5 empty] | 2019-10-25 | 10 | 7132 | 1641 | -95 | 0 | 0 | 1736 | 598.8458 | 598.8458 | 598.8458 | 663.0668 | 780 | 200 | 1643.0668 | 41.08% | 95% | 0% | -108.6957 | 490.1502 | -2750 | -200 | -2459.8498 | 61.5% | 39.01% | 95% | 0% | 1736 | -95
[5 empty] | 2019-10-25 | 11 | 7132.5 | 1709 | -95 | 0 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 663.0668 | 780 | 200 | 1643.0668 | 41.08% | 95% | 0% | -108.6957 | 596.663 | -2750 | -200 | -2353.337 | 58.83% | 39% | 95% | 0% | 1804 | -95
[5 empty] | 2019-10-25 | 12 | 7133 | 1801 | -96 | 0 | 0 | 1897 | 851.0305 | 851.0305 | 851.0305 | 663.0668 | 780 | 200 | 1643.0668 | 41.08% | 95% | 0% | -109.8398 | 741.1907 | -2750 | -200 | -2208.8093 | 55.22% | 39% | 95% | 0% | 1897 | -96
[5 empty] | 2019-10-25 | 13 | 7133.5 | 1994 | -97 | 0 | 0 | 2091 | 1154.9052 | 1154.9052 | 1154.9052 | 663.0668 | 780 | 200 | 1643.0668 | 41.08% | 95% | 0% | -110.984 | 1043.9212 | -2750 | -200 | -1906.0788 | 47.65% | 38.99% | 95% | 0% | 2091 | -97
[5 empty] | 2019-10-25 | 14 | 7134 | 2200 | -99 | 0 | 0 | 2299 | 1480.709 | 1480.709 | 1480.709 | 663.0668 | 780 | 200 | 1643.0668 | 41.08% | 95% | 0% | -113.2723 | 1367.4367 | -2750 | -200 | -1582.5633 | 39.56% | 38.99% | 95% | 0% | 2299 | -99
[5 empty] | 2019-10-25 | 15 | 7134.5 | 2467 | -99 | 0 | 0 | 2566 | 1898.9283 | 1898.9283 | 1898.9283 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -113.2723 | 1785.656 | -2750 | -200 | -1164.344 | 29.11% | 38.97% | 95% | 0% | 2566 | -99
[5 empty] | 2019-10-25 | 16 | 7135 | 2577 | -99 | 0 | 0 | 2676 | 2071.2284 | 2071.2284 | 2071.2284 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -113.2723 | 1957.956 | -2750 | -200 | -992.044 | 24.8% | 38.97% | 95% | 0% | 2676 | -99
[5 empty] | 2019-10-25 | 17 | 7135.5 | 2669 | -108 | 0 | 0 | 2777 | 2229.4312 | 2229.4312 | 2229.4312 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -123.5698 | 2105.8614 | -2750 | -200 | -844.1386 | 21.1% | 38.96% | 95% | 0% | 2777 | -108
[5 empty] | 2019-10-25 | 18 | 7136 | 2659 | -121 | 0 | 0 | 2780 | 2234.1303 | 2234.1303 | 2234.1303 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -138.4439 | 2095.6863 | -2750 | -200 | -854.3137 | 21.36% | 38.96% | 95% | 0% | 2780 | -121
[5 empty] | 2019-10-25 | 19 | 7136.5 | 2650 | -140 | 1 | 0 | 2790 | 2249.7939 | 2249.7939 | 2249.7939 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -160.1831 | 2089.6108 | -3550 | -400 | -1860.3892 | 46.51% | 38.96% | 95% | 0% | 2790 | -140
[5 empty] | 2019-10-25 | 20 | 7137 | 2639 | -162 | 1 | 0 | 2801 | 2267.0239 | 2267.0239 | 2267.0239 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -185.3547 | 2081.6692 | -3550 | -400 | -1868.3308 | 46.71% | 38.95% | 95% | 0% | 2801 | -162
[5 empty] | 2019-10-25 | 21 | 7137.5 | 2608 | -185 | 1 | 0 | 2793 | 2254.493 | 2254.493 | 2254.493 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -211.6705 | 2042.8225 | -3550 | -400 | -1907.1775 | 47.68% | 38.95% | 95% | 0% | 2793 | -185
[5 empty] | 2019-10-25 | 22 | 7138 | 2605 | -183 | 1 | 0 | 2788 | 2246.6612 | 2246.6612 | 2246.6612 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -209.3822 | 2037.279 | -3550 | -400 | -1912.721 | 47.82% | 38.94% | 95% | 0% | 2788 | -183
[5 empty] | 2019-10-25 | 23 | 7138.5 | 2619 | -196 | 1 | 0 | 2815 | 2288.953 | 2288.953 | 2288.953 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -224.2563 | 2064.6967 | -3550 | -400 | -1885.3033 | 47.13% | 38.94% | 95% | 0% | 2815 | -196
[5 empty] | 2019-10-25 | 24 | 7139 | 2612 | -206 | 1 | 0 | 2818 | 2293.6521 | 2293.6521 | 2293.6521 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -235.6979 | 2057.9542 | -3550 | -400 | -1892.0458 | 47.3% | 38.94% | 95% | 0% | 2818 | -206
[5 empty] | 2019-10-25 | 25 | 7139.5 | 2647 | -195 | 1 | 0 | 2842 | 2331.2448 | 2331.2448 | 2331.2448 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -223.1121 | 2108.1327 | -3550 | -400 | -1841.8673 | 46.05% | 38.94% | 95% | 0% | 2842 | -195
[5 empty] | 2019-10-25 | 26 | 7140 | 2657 | -190 | 1 | 0 | 2847 | 2339.0767 | 2339.0767 | 2339.0767 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -217.3913 | 2121.6854 | -3550 | -400 | -1828.3146 | 45.71% | 38.93% | 95% | 0% | 2847 | -190
[5 empty] | 2019-10-25 | 27 | 7140.5 | 2626 | -191 | 1 | 0 | 2817 | 2292.0857 | 2292.0857 | 2292.0857 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -218.5355 | 2073.5503 | -3550 | -400 | -1876.4497 | 46.91% | 38.91% | 95% | 0% | 2817 | -191
[5 empty] | 2019-10-25 | 28 | 7141 | 2593 | -193 | 1 | 0 | 2786 | 2243.5284 | 2243.5284 | 2243.5284 | 661.5004 | 780 | 200 | 1641.5004 | 41.04% | 95% | 0% | -220.8238 | 2022.7046 | -3550 | -400 | -1927.2954 | 48.18% | 38.91% | 95% | 0% | 2786 | -193
[5 empty] | 2019-10-25 | 29 | 7141.5 | 2582 | -184 | 1 | 0 | 2766 | 2212.2012 | 2212.2012 | 2212.2012 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -210.5263 | 2001.6748 | -3550 | -400 | -1948.3252 | 48.71% | 38.9% | 95% | 0% | 2766 | -184
[5 empty] | 2019-10-25 | 30 | 7142 | 2571 | -177 | 1 | 0 | 2748 | 2184.0066 | 2184.0066 | 2184.0066 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -202.5172 | 1981.4894 | -3550 | -400 | -1968.5106 | 49.21% | 38.89% | 95% | 0% | 2748 | -177
[5 empty] | 2019-10-25 | 31 | 7142.5 | 2571 | -165 | 1 | 0 | 2736 | 2165.2102 | 2165.2102 | 2165.2102 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -188.7872 | 1976.423 | -3550 | -400 | -1973.577 | 49.34% | 38.88% | 95% | 0% | 2736 | -165
[5 empty] | 2019-10-25 | 32 | 7143 | 2589 | -157 | 1 | 0 | 2746 | 2180.8739 | 2180.8739 | 2180.8739 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -179.6339 | 2001.24 | -3550 | -400 | -1948.76 | 48.72% | 38.88% | 95% | 0% | 2746 | -157
[5 empty] | 2019-10-25 | 33 | 7143.5 | 2608 | -159 | 1 | 0 | 2767 | 2213.7675 | 2213.7675 | 2213.7675 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -181.9222 | 2031.8453 | -3550 | -400 | -1918.1547 | 47.95% | 38.87% | 95% | 0% | 2767 | -159
[5 empty] | 2019-10-25 | 34 | 7144 | 2649 | -155 | 1 | 0 | 2804 | 2271.723 | 2271.723 | 2271.723 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -177.3455 | 2094.3775 | -3550 | -400 | -1855.6225 | 46.39% | 38.87% | 95% | 0% | 2804 | -155
[5 empty] | 2019-10-25 | 35 | 7144.5 | 2720 | -149 | 1 | 0 | 2869 | 2373.5367 | 2373.5367 | 2373.5367 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -170.4805 | 2203.0561 | -3550 | -400 | -1746.9439 | 43.67% | 38.86% | 95% | 0% | 2869 | -149
[5 empty] | 2019-10-25 | 36 | 7145 | 2787 | -148 | 1 | 0 | 2935 | 2476.9167 | 2476.9167 | 2476.9167 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -169.3364 | 2307.5804 | -3550 | -400 | -1642.4196 | 41.06% | 38.86% | 95% | 0% | 2935 | -148
[5 empty] | 2019-10-25 | 37 | 7145.5 | 2847 | -150 | 1 | 0 | 2997 | 2574.0313 | 2574.0313 | 2574.0313 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -171.6247 | 2402.4066 | -3550 | -400 | -1547.5934 | 38.69% | 38.85% | 95% | 0% | 2997 | -150
[5 empty] | 2019-10-25 | 38 | 7146 | 2805 | -152 | 1 | 0 | 2957 | 2511.3768 | 2511.3768 | 2511.3768 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -173.913 | 2337.4637 | -3550 | -400 | -1612.5363 | 40.31% | 38.84% | 95% | 0% | 2957 | -152
[5 empty] | 2019-10-25 | 39 | 7146.5 | 2743 | -152 | 0 | 0 | 2895 | 2414.2622 | 2414.2622 | 2414.2622 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -173.913 | 2240.3491 | -2750 | -200 | -709.6509 | 17.74% | 38.83% | 95% | 0% | 2895 | -152
[5 empty] | 2019-10-25 | 40 | 7147 | 2654 | -151 | 0 | 0 | 2805 | 2273.2894 | 2273.2894 | 2273.2894 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -172.7689 | 2100.5205 | -2750 | -200 | -849.4795 | 21.24% | 38.83% | 95% | 0% | 2805 | -151
[5 empty] | 2019-10-25 | 41 | 7147.5 | 2528 | -148 | 0 | 0 | 2676 | 2071.2284 | 2071.2284 | 2071.2284 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -169.3364 | 1901.892 | -2750 | -200 | -1048.108 | 26.2% | 38.82% | 95% | 0% | 2676 | -148
[5 empty] | 2019-10-25 | 42 | 7148 | 2429 | -144 | 0 | 0 | 2573 | 1909.8928 | 1909.8928 | 1909.8928 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -164.7597 | 1745.1331 | -2750 | -200 | -1204.8669 | 30.12% | 38.81% | 95% | 0% | 2573 | -144
[5 empty] | 2019-10-25 | 43 | 7148.5 | 2335 | -140 | 0 | 0 | 2475 | 1756.3891 | 1756.3891 | 1756.3891 | 659.934 | 780 | 200 | 1639.934 | 41% | 95% | 0% | -160.1831 | 1596.2061 | -2750 | -200 | -1353.7939 | 33.84% | 38.81% | 95% | 0% | 2475 | -140
[5 empty] | 2019-10-25 | 44 | 7149 | 2227 | -136 | 0 | 0 | 2363 | 1580.9563 | 1580.9563 | 1580.9563 | 658.3677 | 780 | 200 | 1638.3677 | 40.96% | 95% | 0% | -155.6064 | 1425.3499 | -2750 | -200 | -1524.6501 | 38.12% | 38.79% | 95% | 0% | 2363 | -136
[5 empty] | 2019-10-25 | 45 | 7149.5 | 2108 | -132 | 0 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 658.3677 | 780 | 200 | 1638.3677 | 40.96% | 95% | 0% | -151.0297 | 1237.2637 | -2750 | -200 | -1712.7363 | 42.82% | 38.79% | 95% | 0% | 2240 | -132
[5 empty] | 2019-10-25 | 46 | 7150 | 1986 | -127 | 0 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 658.3677 | 780 | 200 | 1638.3677 | 40.96% | 95% | 0% | -145.3089 | 1044.0563 | -2750 | -200 | -1905.9437 | 47.65% | 38.78% | 95% | 0% | 2113 | -127
[5 empty] | 2019-10-25 | 47 | 7150.5 | 1864 | -123 | 0 | 0 | 1987 | 992.0033 | 992.0033 | 992.0033 | 658.3677 | 780 | 200 | 1638.3677 | 40.96% | 95% | 0% | -140.7323 | 851.271 | -2750 | -200 | -2098.729 | 52.47% | 38.77% | 95% | 0% | 1987 | -123
[5 empty] | 2019-10-25 | 48 | 7151 | 1770 | -120 | 0 | 0 | 1890 | 840.066 | 840.066 | 840.066 | 658.3677 | 780 | 200 | 1638.3677 | 40.96% | 95% | 0% | -137.2998 | 702.7662 | -2750 | -200 | -2247.2338 | 56.18% | 38.76% | 95% | 0% | 1890 | -120
[5 empty] | 2019-10-26 | 1 | 7151.5 | 1680 | -114 | 0 | 0 | 1794 | 689.695 | 689.695 | 689.695 | 658.3677 | 780 | 200 | 1638.3677 | 40.96% | 95% | 0% | -130.4348 | 559.2602 | -2750 | -200 | -2390.7398 | 59.77% | 38.75% | 95% | 0% | 1794 | -114
[5 empty] | 2019-10-26 | 2 | 7152 | 1640 | -109 | 0 | 0 | 1749 | 619.2086 | 619.2086 | 619.2086 | 658.3677 | 780 | 200 | 1638.3677 | 40.96% | 95% | 0% | -124.714 | 494.4946 | -2750 | -200 | -2455.5054 | 61.39% | 38.74% | 95% | 0% | 1749 | -109
[5 empty] | 2019-10-26 | 3 | 7152.5 | 1615 | -109 | 0 | 0 | 1724 | 580.0495 | 580.0495 | 580.0495 | 658.3677 | 780 | 200 | 1638.3677 | 40.96% | 95% | 0% | -124.714 | 455.3355 | -2750 | -200 | -2494.6645 | 62.37% | 38.73% | 95% | 0% | 1724 | -109
[5 empty] | 2019-10-26 | 4 | 7153 | 1651 | -108 | 0 | 0 | 1759 | 634.8722 | 634.8722 | 634.8722 | 658.3677 | 780 | 200 | 1638.3677 | 40.96% | 95% | 0% | -123.5698 | 511.3024 | -2750 | -200 | -2438.6976 | 60.97% | 38.72% | 95% | 0% | 1759 | -108
[5 empty] | 2019-10-26 | 5 | 7153.5 | 1626 | -109 | 0 | 0 | 1735 | 597.2795 | 597.2795 | 597.2795 | 658.3677 | 780 | 200 | 1638.3677 | 40.96% | 95% | 0% | -124.714 | 472.5655 | -2750 | -200 | -2477.4345 | 61.94% | 38.71% | 95% | 0% | 1735 | -109
[5 empty] | 2019-10-26 | 6 | 7154 | 1592 | -109 | 0 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 658.3677 | 780 | 200 | 1638.3677 | 40.96% | 95% | 0% | -124.714 | 419.3091 | -2750 | -200 | -2530.6909 | 63.27% | 38.7% | 95% | 0% | 1701 | -109
[5 empty] | 2019-10-26 | 7 | 7154.5 | 1560 | -108 | 0 | 0 | 1668 | 492.3331 | 492.3331 | 492.3331 | 658.3677 | 780 | 200 | 1638.3677 | 40.96% | 95% | 0% | -123.5698 | 368.7633 | -2750 | -200 | -2581.2367 | 64.53% | 38.69% | 95% | 0% | 1668 | -108
[5 empty] | 2019-10-26 | 8 | 7155 | 1536 | -107 | 0 | 0 | 1643 | 453.1739 | 453.1739 | 453.1739 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -122.4256 | 330.7483 | -2750 | -200 | -2619.2517 | 65.48% | 38.69% | 95% | 0% | 1643 | -107
[5 empty] | 2019-10-26 | 9 | 7155.5 | 1519 | -107 | 0 | 0 | 1626 | 426.5458 | 426.5458 | 426.5458 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -122.4256 | 304.1201 | -2750 | -200 | -2645.8799 | 66.15% | 38.69% | 95% | 0% | 1626 | -107
[5 empty] | 2019-10-26 | 10 | 7156 | 1504 | -106 | 0 | 0 | 1610 | 401.4839 | 401.4839 | 401.4839 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -121.2815 | 280.2025 | -2750 | -200 | -2669.7975 | 66.74% | 38.68% | 95% | 0% | 1610 | -106
[5 empty] | 2019-10-26 | 11 | 7156.5 | 1529 | -107 | 0 | 0 | 1636 | 442.2094 | 442.2094 | 442.2094 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -122.4256 | 319.7838 | -2750 | -200 | -2630.2162 | 65.76% | 38.68% | 95% | 0% | 1636 | -107
[5 empty] | 2019-10-26 | 12 | 7157 | 1564 | -108 | 0 | 0 | 1672 | 498.5985 | 498.5985 | 498.5985 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -123.5698 | 375.0287 | -2750 | -200 | -2574.9713 | 64.37% | 38.67% | 95% | 0% | 1672 | -108
[5 empty] | 2019-10-26 | 13 | 7157.5 | 1659 | -108 | 0 | 0 | 1767 | 647.4031 | 647.4031 | 647.4031 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -123.5698 | 523.8333 | -2750 | -200 | -2426.1667 | 60.65% | 38.66% | 95% | 0% | 1767 | -108
[5 empty] | 2019-10-26 | 14 | 7158 | 1761 | -107 | 0 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -122.4256 | 683.1803 | -2750 | -200 | -2266.8197 | 56.67% | 38.66% | 95% | 0% | 1868 | -107
[5 empty] | 2019-10-26 | 15 | 7158.5 | 1906 | -108 | 0 | 0 | 2014 | 1034.2951 | 1034.2951 | 1034.2951 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -123.5698 | 910.7253 | -2750 | -200 | -2039.2747 | 50.98% | 38.64% | 95% | 0% | 2014 | -108
[5 empty] | 2019-10-26 | 16 | 7159 | 2031 | -109 | 1 | 0 | 2140 | 1231.657 | 1231.657 | 1231.657 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -124.714 | 1106.9431 | -3550 | -400 | -2843.0569 | 71.08% | 38.64% | 95% | 0% | 2140 | -109
[5 empty] | 2019-10-26 | 17 | 7159.5 | 2166 | -110 | 1 | 0 | 2276 | 1444.6826 | 1444.6826 | 1444.6826 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -125.8581 | 1318.8245 | -3550 | -400 | -2631.1755 | 65.78% | 38.63% | 95% | 0% | 2276 | -110
[5 empty] | 2019-10-26 | 18 | 7160 | 2278 | -112 | 1 | 0 | 2390 | 1623.2481 | 1623.2481 | 1623.2481 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -128.1465 | 1495.1017 | -3550 | -400 | -2454.8983 | 61.37% | 38.63% | 95% | 0% | 2390 | -112
[5 empty] | 2019-10-26 | 19 | 7160.5 | 2343 | -121 | 1 | 0 | 2464 | 1739.1591 | 1739.1591 | 1739.1591 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -138.4439 | 1600.7152 | -3550 | -400 | -2349.2848 | 58.73% | 38.63% | 95% | 0% | 2464 | -121
[5 empty] | 2019-10-26 | 20 | 7161 | 2387 | -134 | 1 | 0 | 2521 | 1828.4419 | 1828.4419 | 1828.4419 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -153.3181 | 1675.1238 | -3550 | -400 | -2274.8762 | 56.87% | 38.63% | 95% | 0% | 2521 | -134
[5 empty] | 2019-10-26 | 21 | 7161.5 | 2408 | -143 | 1 | 0 | 2551 | 1875.4328 | 1875.4328 | 1875.4328 | 656.8013 | 780 | 200 | 1636.8013 | 40.92% | 95% | 0% | -163.6156 | 1711.8173 | -3550 | -400 | -2238.1827 | 55.95% | 38.62% | 95% | 0% | 2551 | -143
[5 empty] | 2019-10-26 | 22 | 7162 | 2393 | -147 | 1 | 0 | 2540 | 1858.2028 | 1858.2028 | 1858.2028 | 655.235 | 780 | 200 | 1635.235 | 40.88% | 95% | 0% | -168.1922 | 1690.0106 | -3550 | -400 | -2259.9894 | 56.5% | 38.62% | 95% | 0% | 2540 | -147
[5 empty] | 2019-10-26 | 23 | 7162.5 | 2387 | -161 | 1 | 0 | 2548 | 1870.7337 | 1870.7337 | 1870.7337 | 655.235 | 780 | 200 | 1635.235 | 40.88% | 95% | 0% | -184.2105 | 1686.5232 | -3550 | -400 | -2263.4768 | 56.59% | 38.62% | 95% | 0% | 2548 | -161
[5 empty] | 2019-10-26 | 24 | 7163 | 2399 | -172 | 1 | 0 | 2571 | 1906.7601 | 1906.7601 | 1906.7601 | 655.235 | 780 | 200 | 1635.235 | 40.88% | 95% | 0% | -196.7963 | 1709.9638 | -3550 | -400 | -2240.0362 | 56% | 38.61% | 95% | 0% | 2571 | -172
[5 empty] | 2019-10-26 | 25 | 7163.5 | 2368 | -180 | 1 | 0 | 2548 | 1870.7337 | 1870.7337 | 1870.7337 | 655.235 | 780 | 200 | 1635.235 | 40.88% | 95% | 0% | -205.9497 | 1664.7841 | -3550 | -400 | -2285.2159 | 57.13% | 38.59% | 95% | 0% | 2548 | -180
[5 empty] | 2019-10-26 | 26 | 7164 | 2340 | -186 | 1 | 0 | 2526 | 1836.2737 | 1836.2737 | 1836.2737 | 655.235 | 780 | 200 | 1635.235 | 40.88% | 95% | 0% | -212.8146 | 1623.4591 | -3550 | -400 | -2326.5409 | 58.16% | 38.57% | 95% | 0% | 2526 | -186
[5 empty] | 2019-10-26 | 27 | 7164.5 | 2313 | -188 | 1 | 0 | 2501 | 1797.1146 | 1797.1146 | 1797.1146 | 655.235 | 780 | 200 | 1635.235 | 40.88% | 95% | 0% | -215.103 | 1582.0116 | -3550 | -400 | -2367.9884 | 59.2% | 38.56% | 95% | 0% | 2501 | -188
[5 empty] | 2019-10-26 | 28 | 7165 | 2292 | -188 | 1 | 0 | 2480 | 1764.2209 | 1764.2209 | 1764.2209 | 655.235 | 780 | 200 | 1635.235 | 40.88% | 95% | 0% | -215.103 | 1549.118 | -3550 | -400 | -2400.882 | 60.02% | 38.56% | 95% | 0% | 2480 | -188
[5 empty] | 2019-10-26 | 29 | 7165.5 | 2277 | -191 | 1 | 0 | 2468 | 1745.4246 | 1745.4246 | 1745.4246 | 655.235 | 780 | 200 | 1635.235 | 40.88% | 95% | 0% | -218.5355 | 1526.8891 | -3550 | -400 | -2423.1109 | 60.58% | 38.56% | 95% | 0% | 2468 | -191
[5 empty] | 2019-10-26 | 30 | 7166 | 2250 | -193 | 1 | 0 | 2443 | 1706.2655 | 1706.2655 | 1706.2655 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -220.8238 | 1485.4417 | -3550 | -400 | -2464.5583 | 61.61% | 38.56% | 95% | 0% | 2443 | -193
[5 empty] | 2019-10-26 | 31 | 7166.5 | 2243 | -186 | 1 | 0 | 2429 | 1684.3364 | 1684.3364 | 1684.3364 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -212.8146 | 1471.5217 | -3550 | -400 | -2478.4783 | 61.96% | 38.55% | 95% | 0% | 2429 | -186
[5 empty] | 2019-10-26 | 32 | 7167 | 2256 | -183 | 1 | 0 | 2439 | 1700 | 1700 | 1700 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -209.3822 | 1490.6178 | -3550 | -400 | -2459.3822 | 61.48% | 38.55% | 95% | 0% | 2439 | -183
[5 empty] | 2019-10-26 | 33 | 7167.5 | 2304 | -175 | 1 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -200.2288 | 1562.4257 | -3550 | -400 | -2387.5743 | 59.69% | 38.54% | 95% | 0% | 2479 | -175
[5 empty] | 2019-10-26 | 34 | 7168 | 2389 | -158 | 1 | 0 | 2547 | 1869.1674 | 1869.1674 | 1869.1674 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -180.778 | 1688.3893 | -3550 | -400 | -2261.6107 | 56.54% | 38.54% | 95% | 0% | 2547 | -158
[5 empty] | 2019-10-26 | 35 | 7168.5 | 2507 | -138 | 1 | 0 | 2645 | 2022.6711 | 2022.6711 | 2022.6711 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -157.8947 | 1864.7763 | -3550 | -400 | -2085.2237 | 52.13% | 38.54% | 95% | 0% | 2645 | -138
[5 empty] | 2019-10-26 | 36 | 7169 | 2604 | -131 | 1 | 0 | 2735 | 2163.6439 | 2163.6439 | 2163.6439 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -149.8856 | 2013.7583 | -3550 | -400 | -1936.2417 | 48.41% | 38.54% | 95% | 0% | 2735 | -131
[5 empty] | 2019-10-26 | 37 | 7169.5 | 2675 | -133 | 1 | 0 | 2808 | 2277.9885 | 2277.9885 | 2277.9885 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -152.1739 | 2125.8145 | -3550 | -400 | -1824.1855 | 45.6% | 38.54% | 95% | 0% | 2808 | -133
[5 empty] | 2019-10-26 | 38 | 7170 | 2633 | -135 | 1 | 0 | 2768 | 2215.3339 | 2215.3339 | 2215.3339 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -154.4622 | 2060.8716 | -3550 | -400 | -1889.1284 | 47.23% | 38.54% | 95% | 0% | 2768 | -135
[5 empty] | 2019-10-26 | 39 | 7170.5 | 2546 | -140 | 0 | 0 | 2686 | 2086.892 | 2086.892 | 2086.892 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -160.1831 | 1926.7089 | -2750 | -200 | -1023.2911 | 25.58% | 38.53% | 95% | 0% | 2686 | -140
[5 empty] | 2019-10-26 | 40 | 7171 | 2430 | -144 | 0 | 0 | 2574 | 1911.4592 | 1911.4592 | 1911.4592 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -164.7597 | 1746.6995 | -2750 | -200 | -1203.3005 | 30.08% | 38.53% | 95% | 0% | 2574 | -144
[5 empty] | 2019-10-26 | 41 | 7171.5 | 2327 | -146 | 0 | 0 | 2473 | 1753.2564 | 1753.2564 | 1753.2564 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -167.0481 | 1586.2083 | -2750 | -200 | -1363.7917 | 34.09% | 38.53% | 95% | 0% | 2473 | -146
[5 empty] | 2019-10-26 | 42 | 7172 | 2251 | -147 | 0 | 0 | 2398 | 1635.7791 | 1635.7791 | 1635.7791 | 653.6686 | 780 | 200 | 1633.6686 | 40.84% | 95% | 0% | -168.1922 | 1467.5868 | -2750 | -200 | -1482.4132 | 37.06% | 38.52% | 95% | 0% | 2398 | -147
[5 empty] | 2019-10-26 | 43 | 7172.5 | 2176 | -149 | 0 | 0 | 2325 | 1521.4345 | 1521.4345 | 1521.4345 | 652.1022 | 780 | 200 | 1632.1022 | 40.8% | 95% | 0% | -170.4805 | 1350.9539 | -2750 | -200 | -1599.0461 | 39.98% | 38.51% | 95% | 0% | 2325 | -149
[5 empty] | 2019-10-26 | 44 | 7173 | 2083 | -150 | 0 | 0 | 2233 | 1377.3289 | 1377.3289 | 1377.3289 | 652.1022 | 780 | 200 | 1632.1022 | 40.8% | 95% | 0% | -171.6247 | 1205.7042 | -2750 | -200 | -1744.2958 | 43.61% | 38.5% | 95% | 0% | 2233 | -150
[5 empty] | 2019-10-26 | 45 | 7173.5 | 1970 | -152 | 0 | 0 | 2122 | 1203.4625 | 1203.4625 | 1203.4625 | 652.1022 | 780 | 200 | 1632.1022 | 40.8% | 95% | 0% | -173.913 | 1029.5494 | -2750 | -200 | -1920.4506 | 48.01% | 38.49% | 95% | 0% | 2122 | -152
[5 empty] | 2019-10-26 | 46 | 7174 | 1867 | -154 | 0 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 652.1022 | 780 | 200 | 1632.1022 | 40.8% | 95% | 0% | -176.2014 | 869.0583 | -2750 | -200 | -2080.9417 | 52.02% | 38.48% | 95% | 0% | 2021 | -154
[5 empty] | 2019-10-26 | 47 | 7174.5 | 1743 | -156 | 0 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 652.1022 | 780 | 200 | 1632.1022 | 40.8% | 95% | 0% | -178.4897 | 675.6735 | -2750 | -200 | -2274.3265 | 56.86% | 38.48% | 95% | 0% | 1899 | -156
[5 empty] | 2019-10-26 | 48 | 7175 | 1642 | -158 | 0 | 0 | 1800 | 699.0932 | 699.0932 | 699.0932 | 652.1022 | 780 | 200 | 1632.1022 | 40.8% | 95% | 0% | -180.778 | 518.3151 | -2750 | -200 | -2431.6849 | 60.79% | 38.48% | 95% | 0% | 1800 | -158
[5 empty] | 2019-10-27 | 1 | 7175.5 | 1562 | -160 | 0 | 0 | 1722 | 576.9167 | 576.9167 | 576.9167 | 652.1022 | 780 | 200 | 1632.1022 | 40.8% | 95% | 0% | -183.0664 | 393.8504 | -2750 | -200 | -2556.1496 | 63.9% | 38.47% | 95% | 0% | 1722 | -160
[5 empty] | 2019-10-27 | 2 | 7176 | 1507 | -162 | 0 | 0 | 1669 | 493.8994 | 493.8994 | 493.8994 | 652.1022 | 780 | 200 | 1632.1022 | 40.8% | 95% | 0% | -185.3547 | 308.5447 | -2750 | -200 | -2641.4553 | 66.04% | 38.44% | 95% | 0% | 1669 | -162
[5 empty] | 2019-10-27 | 3 | 7176.5 | 1485 | -164 | 0 | 0 | 1649 | 462.5721 | 462.5721 | 462.5721 | 652.1022 | 780 | 200 | 1632.1022 | 40.8% | 95% | 0% | -187.643 | 274.9291 | -2750 | -200 | -2675.0709 | 66.88% | 38.43% | 95% | 0% | 1649 | -164
[5 empty] | 2019-10-27 | 4 | 7177 | 1508 | -166 | 0 | 0 | 1674 | 501.7312 | 501.7312 | 501.7312 | 652.1022 | 780 | 200 | 1632.1022 | 40.8% | 95% | 0% | -189.9314 | 311.7999 | -2750 | -200 | -2638.2001 | 65.96% | 38.42% | 95% | 0% | 1674 | -166
[5 empty] | 2019-10-27 | 5 | 7177.5 | 1484 | -166 | 0 | 0 | 1650 | 464.1385 | 464.1385 | 464.1385 | 652.1022 | 780 | 200 | 1632.1022 | 40.8% | 95% | 0% | -189.9314 | 274.2071 | -2750 | -200 | -2675.7929 | 66.89% | 38.42% | 95% | 0% | 1650 | -166
[5 empty] | 2019-10-27 | 6 | 7178 | 1454 | -166 | 0 | 0 | 1620 | 417.1476 | 417.1476 | 417.1476 | 652.1022 | 780 | 200 | 1632.1022 | 40.8% | 95% | 0% | -189.9314 | 227.2162 | -2750 | -200 | -2722.7838 | 68.07% | 38.41% | 95% | 0% | 1620 | -166
[5 empty] | 2019-10-27 | 7 | 7178.5 | 1420 | -166 | 0 | 0 | 1586 | 363.8912 | 363.8912 | 363.8912 | 650.5359 | 780 | 200 | 1630.5359 | 40.76% | 95% | 0% | -189.9314 | 173.9598 | -2750 | -200 | -2776.0402 | 69.4% | 38.41% | 95% | 0% | 1586 | -166
[5 empty] | 2019-10-27 | 8 | 7179 | 1407 | -166 | 0 | 0 | 1573 | 343.5284 | 343.5284 | 343.5284 | 650.5359 | 780 | 200 | 1630.5359 | 40.76% | 95% | 0% | -189.9314 | 153.5971 | -2750 | -200 | -2796.4029 | 69.91% | 38.4% | 95% | 0% | 1573 | -166
[5 empty] | 2019-10-27 | 9 | 7179.5 | 1390 | -161 | 0 | 0 | 1551 | 309.0684 | 309.0684 | 309.0684 | 650.5359 | 780 | 200 | 1630.5359 | 40.76% | 95% | 0% | -184.2105 | 124.8579 | -2750 | -200 | -2825.1421 | 70.63% | 38.4% | 95% | 0% | 1551 | -161
[5 empty] | 2019-10-27 | 10 | 7180 | 1363 | -157 | 0 | 0 | 1520 | 260.5111 | 260.5111 | 260.5111 | 650.5359 | 780 | 200 | 1630.5359 | 40.76% | 95% | 0% | -179.6339 | 80.8773 | -2750 | -200 | -2869.1227 | 71.73% | 38.4% | 95% | 0% | 1520 | -157
[5 empty] | 2019-10-27 | 11 | 7180.5 | 1355 | -157 | 0 | 0 | 1512 | 247.9802 | 247.9802 | 247.9802 | 650.5359 | 780 | 200 | 1630.5359 | 40.76% | 95% | 0% | -179.6339 | 68.3463 | -2750 | -200 | -2881.6537 | 72.04% | 38.39% | 95% | 0% | 1512 | -157
[5 empty] | 2019-10-27 | 12 | 7181 | 1356 | -157 | 0 | 0 | 1513 | 249.5466 | 249.5466 | 249.5466 | 650.5359 | 780 | 200 | 1630.5359 | 40.76% | 95% | 0% | -179.6339 | 69.9127 | -2750 | -200 | -2880.0873 | 72% | 38.34% | 95% | 0% | 1513 | -157
[5 empty] | 2019-10-27 | 13 | 7181.5 | 1387 | -155 | 0 | 0 | 1542 | 294.9711 | 294.9711 | 294.9711 | 650.5359 | 780 | 200 | 1630.5359 | 40.76% | 95% | 0% | -177.3455 | 117.6256 | -2750 | -200 | -2832.3744 | 70.81% | 38.34% | 95% | 0% | 1542 | -155
[5 empty] | 2019-10-27 | 14 | 7182 | 1436 | -154 | 0 | 0 | 1590 | 370.1566 | 370.1566 | 370.1566 | 650.5359 | 780 | 200 | 1630.5359 | 40.76% | 95% | 0% | -176.2014 | 193.9553 | -2750 | -200 | -2756.0447 | 68.9% | 38.34% | 95% | 0% | 1590 | -154
[5 empty] | 2019-10-27 | 15 | 7182.5 | 1529 | -153 | 0 | 0 | 1682 | 514.2622 | 514.2622 | 514.2622 | 650.5359 | 780 | 200 | 1630.5359 | 40.76% | 95% | 0% | -175.0572 | 339.205 | -2750 | -200 | -2610.795 | 65.27% | 38.33% | 95% | 0% | 1682 | -153
[5 empty] | 2019-10-27 | 16 | 7183 | 1600 | -152 | 0 | 0 | 1752 | 623.9077 | 623.9077 | 623.9077 | 650.5359 | 780 | 200 | 1630.5359 | 40.76% | 95% | 0% | -173.913 | 449.9946 | -2750 | -200 | -2500.0054 | 62.5% | 38.33% | 95% | 0% | 1752 | -152
[5 empty] | 2019-10-27 | 17 | 7183.5 | 1698 | -163 | 0 | 0 | 1861 | 794.6414 | 794.6414 | 794.6414 | 650.5359 | 780 | 200 | 1630.5359 | 40.76% | 95% | 0% | -186.4989 | 608.1425 | -2750 | -200 | -2341.8575 | 58.55% | 38.33% | 95% | 0% | 1861 | -163
[5 empty] | 2019-10-27 | 18 | 7184 | 1736 | -207 | 0 | 0 | 1943 | 923.0833 | 923.0833 | 923.0833 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -236.8421 | 686.2412 | -2750 | -200 | -2263.7588 | 56.59% | 38.31% | 95% | 0% | 1943 | -207
[5 empty] | 2019-10-27 | 19 | 7184.5 | 1768 | -285 | 1 | 0 | 2053 | 1095.3833 | 1095.3833 | 1095.3833 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -326.087 | 769.2964 | -3550 | -400 | -3180.7036 | 79.52% | 38.3% | 95% | 0% | 2053 | -285
[5 empty] | 2019-10-27 | 20 | 7185 | 1711 | -373 | 1 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -426.7735 | 717.1672 | -3550 | -400 | -3232.8328 | 80.82% | 38.29% | 95% | 0% | 2084 | -373
[5 empty] | 2019-10-27 | 21 | 7185.5 | 1640 | -450 | 1 | 0 | 2090 | 1153.3388 | 1153.3388 | 1153.3388 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -514.8741 | 638.4647 | -3550 | -400 | -3311.5353 | 82.79% | 38.28% | 95% | 0% | 2090 | -450
[5 empty] | 2019-10-27 | 22 | 7186 | 1547 | -515 | 1 | 0 | 2062 | 1109.4806 | 1109.4806 | 1109.4806 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -589.2449 | 520.2358 | -3550 | -400 | -3429.7642 | 85.74% | 38.28% | 95% | 0% | 2062 | -515
[5 empty] | 2019-10-27 | 23 | 7186.5 | 1462 | -578 | 1 | 0 | 2040 | 1075.0206 | 1075.0206 | 1075.0206 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -661.3272 | 413.6934 | -3550 | -400 | -3536.3066 | 88.41% | 38.28% | 95% | 0% | 2040 | -578
[5 empty] | 2019-10-27 | 24 | 7187 | 1353 | -629 | 1 | 0 | 1982 | 984.1715 | 984.1715 | 984.1715 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -719.6796 | 264.4918 | -3550 | -400 | -3685.5082 | 92.14% | 38.25% | 95% | 0% | 1982 | -629
[5 empty] | 2019-10-27 | 25 | 7187.5 | 1311 | -671 | 1 | 0 | 1982 | 984.1715 | 984.1715 | 984.1715 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -767.7346 | 216.4369 | -3550 | -400 | -3733.5631 | 93.34% | 38.24% | 95% | 0% | 1982 | -671
[5 empty] | 2019-10-27 | 26 | 7188 | 1321 | -674 | 1 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -771.167 | 233.3672 | -3550 | -400 | -3716.6328 | 92.92% | 38.24% | 95% | 0% | 1995 | -674
[5 empty] | 2019-10-27 | 27 | 7188.5 | 1347 | -663 | 1 | 0 | 2010 | 1028.0297 | 1028.0297 | 1028.0297 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -758.5812 | 269.4484 | -3550 | -400 | -3680.5516 | 92.01% | 38.23% | 95% | 0% | 2010 | -663
[5 empty] | 2019-10-27 | 28 | 7189 | 1402 | -625 | 1 | 0 | 2027 | 1054.6579 | 1054.6579 | 1054.6579 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -715.103 | 339.5549 | -3550 | -400 | -3610.4451 | 90.26% | 38.23% | 95% | 0% | 2027 | -625
[5 empty] | 2019-10-27 | 29 | 7189.5 | 1468 | -576 | 1 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -659.0389 | 422.2472 | -3550 | -400 | -3527.7528 | 88.19% | 38.23% | 95% | 0% | 2044 | -576
[5 empty] | 2019-10-27 | 30 | 7190 | 1549 | -511 | 1 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -584.6682 | 521.6797 | -3550 | -400 | -3428.3203 | 85.71% | 38.22% | 95% | 0% | 2060 | -511
[5 empty] | 2019-10-27 | 31 | 7190.5 | 1674 | -441 | 1 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -504.5767 | 687.9213 | -3550 | -400 | -3262.0787 | 81.55% | 38.22% | 95% | 0% | 2115 | -441
[5 empty] | 2019-10-27 | 32 | 7191 | 1833 | -360 | 1 | 0 | 2193 | 1314.6744 | 1314.6744 | 1314.6744 | 648.9695 | 780 | 200 | 1628.9695 | 40.72% | 95% | 0% | -411.8993 | 902.775 | -3550 | -400 | -3047.225 | 76.18% | 38.21% | 95% | 0% | 2193 | -360
[5 empty] | 2019-10-27 | 33 | 7191.5 | 2016 | -274 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -313.5011 | 1153.1106 | -3550 | -400 | -2796.8894 | 69.92% | 38.2% | 95% | 0% | 2290 | -274
[5 empty] | 2019-10-27 | 34 | 7192 | 2224 | -190 | 1 | 0 | 2414 | 1660.8409 | 1660.8409 | 1660.8409 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -217.3913 | 1443.4496 | -3550 | -400 | -2506.5504 | 62.66% | 38.18% | 95% | 0% | 2414 | -190
[5 empty] | 2019-10-27 | 35 | 7192.5 | 2439 | -128 | 1 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -146.4531 | 1754.0416 | -3550 | -400 | -2195.9584 | 54.9% | 38.18% | 95% | 0% | 2567 | -128
[5 empty] | 2019-10-27 | 36 | 7193 | 2607 | -101 | 1 | 0 | 2708 | 2121.352 | 2121.352 | 2121.352 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -115.5606 | 2005.7914 | -3550 | -400 | -1944.2086 | 48.61% | 38.17% | 95% | 0% | 2708 | -101
[5 empty] | 2019-10-27 | 37 | 7193.5 | 2818 | -96 | 1 | 0 | 2914 | 2444.0231 | 2444.0231 | 2444.0231 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -109.8398 | 2334.1833 | -3550 | -400 | -1615.8167 | 40.4% | 38.14% | 95% | 0% | 2914 | -96
[5 empty] | 2019-10-27 | 38 | 7194 | 2856 | -93 | 1 | 0 | 2949 | 2498.8458 | 2498.8458 | 2498.8458 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -106.4073 | 2392.4385 | -3550 | -400 | -1557.5615 | 38.94% | 38.14% | 95% | 0% | 2949 | -93
[5 empty] | 2019-10-27 | 39 | 7194.5 | 2796 | -92 | 0 | 0 | 2888 | 2403.2976 | 2403.2976 | 2403.2976 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -105.2632 | 2298.0345 | -2750 | -200 | -651.9655 | 16.3% | 38.13% | 95% | 0% | 2888 | -92
[5 empty] | 2019-10-27 | 40 | 7195 | 2767 | -90 | 0 | 0 | 2857 | 2354.7403 | 2354.7403 | 2354.7403 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -102.9748 | 2251.7655 | -2750 | -200 | -698.2345 | 17.46% | 38.13% | 95% | 0% | 2857 | -90
[5 empty] | 2019-10-27 | 41 | 7195.5 | 2698 | -88 | 0 | 0 | 2786 | 2243.5284 | 2243.5284 | 2243.5284 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -100.6865 | 2142.8419 | -2750 | -200 | -807.1581 | 20.18% | 38.12% | 95% | 0% | 2786 | -88
[5 empty] | 2019-10-27 | 42 | 7196 | 2632 | -86 | 0 | 0 | 2718 | 2137.0157 | 2137.0157 | 2137.0157 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -98.3982 | 2038.6175 | -2750 | -200 | -911.3825 | 22.78% | 38.1% | 95% | 0% | 2718 | -86
[5 empty] | 2019-10-27 | 43 | 7196.5 | 2566 | -85 | 0 | 0 | 2651 | 2032.0692 | 2032.0692 | 2032.0692 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -97.254 | 1934.8152 | -2750 | -200 | -1015.1848 | 25.38% | 38.1% | 95% | 0% | 2651 | -85
[5 empty] | 2019-10-27 | 44 | 7197 | 2481 | -83 | 0 | 0 | 2564 | 1895.7955 | 1895.7955 | 1895.7955 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -94.9657 | 1800.8299 | -2750 | -200 | -1149.1701 | 28.73% | 38.09% | 95% | 0% | 2564 | -83
[5 empty] | 2019-10-27 | 45 | 7197.5 | 2379 | -81 | 0 | 0 | 2460 | 1732.8937 | 1732.8937 | 1732.8937 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -92.6773 | 1640.2163 | -2750 | -200 | -1309.7837 | 32.74% | 38.09% | 95% | 0% | 2460 | -81
[5 empty] | 2019-10-27 | 46 | 7198 | 2254 | -79 | 0 | 0 | 2333 | 1533.9654 | 1533.9654 | 1533.9654 | 647.4031 | 780 | 200 | 1627.4031 | 40.69% | 95% | 0% | -90.389 | 1443.5764 | -2750 | -200 | -1506.4236 | 37.66% | 38.09% | 95% | 0% | 2333 | -79
[5 empty] | 2019-10-27 | 47 | 7198.5 | 2150 | -77 | 0 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 645.8368 | 780 | 200 | 1625.8368 | 40.65% | 95% | 0% | -88.1007 | 1279.8301 | -2750 | -200 | -1670.1699 | 41.75% | 38.09% | 95% | 0% | 2227 | -77
[5 empty] | 2019-10-27 | 48 | 7199 | 2032 | -75 | 0 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 645.8368 | 780 | 200 | 1625.8368 | 40.65% | 95% | 0% | -85.8124 | 1094.1547 | -2750 | -200 | -1855.8453 | 46.4% | 38.09% | 95% | 0% | 2107 | -75
[5 empty] | 2019-10-27 | 49 | 7199.5 | 1932 | -71 | 0 | 0 | 2003 | 1017.0651 | 1017.0651 | 1017.0651 | 645.8368 | 780 | 200 | 1625.8368 | 40.65% | 95% | 0% | -81.2357 | 935.8294 | -2750 | -200 | -2014.1706 | 50.35% | 38.09% | 95% | 0% | 2003 | -71
[5 empty] | 2019-10-27 | 50 | 7200 | 1860 | -67 | 0 | 0 | 1927 | 898.0214 | 898.0214 | 898.0214 | 645.8368 | 780 | 200 | 1625.8368 | 40.65% | 95% | 0% | -76.659 | 821.3624 | -2750 | -200 | -2128.6376 | 53.22% | 38.08% | 95% | 0% | 1927 | -67
[5 empty] | 2019-10-28 | 1 | 7200.5 | 1839 | -66 | 0 | 0 | 1905 | 863.5614 | 863.5614 | 863.5614 | 645.8368 | 780 | 200 | 1625.8368 | 40.65% | 95% | 0% | -75.5149 | 788.0465 | -2750 | -200 | -2161.9535 | 54.05% | 38.08% | 95% | 0% | 1905 | -66
[5 empty] | 2019-10-28 | 2 | 7201 | 1854 | -65 | 0 | 0 | 1919 | 885.4905 | 885.4905 | 885.4905 | 645.8368 | 780 | 200 | 1625.8368 | 40.65% | 95% | 0% | -74.3707 | 811.1198 | -2750 | -200 | -2138.8802 | 53.47% | 38.08% | 95% | 0% | 1919 | -65
[5 empty] | 2019-10-28 | 3 | 7201.5 | 1829 | -65 | 0 | 0 | 1894 | 846.3314 | 846.3314 | 846.3314 | 645.8368 | 780 | 200 | 1625.8368 | 40.65% | 95% | 0% | -74.3707 | 771.9607 | -2750 | -200 | -2178.0393 | 54.45% | 38.07% | 95% | 0% | 1894 | -65
[5 empty] | 2019-10-28 | 4 | 7202 | 1793 | -64 | 0 | 0 | 1857 | 788.3759 | 788.3759 | 788.3759 | 645.8368 | 780 | 200 | 1625.8368 | 40.65% | 95% | 0% | -73.2265 | 715.1494 | -2750 | -200 | -2234.8506 | 55.87% | 38.06% | 95% | 0% | 1857 | -64
[5 empty] | 2019-10-28 | 5 | 7202.5 | 1765 | -62 | 0 | 0 | 1827 | 741.385 | 741.385 | 741.385 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -70.9382 | 670.4468 | -2750 | -200 | -2279.5532 | 56.99% | 38.05% | 95% | 0% | 1827 | -62
[5 empty] | 2019-10-28 | 6 | 7203 | 1760 | -61 | 0 | 0 | 1821 | 731.9868 | 731.9868 | 731.9868 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -69.7941 | 662.1928 | -2750 | -200 | -2287.8072 | 57.2% | 38.04% | 95% | 0% | 1821 | -61
[5 empty] | 2019-10-28 | 7 | 7203.5 | 1753 | -61 | 0 | 0 | 1814 | 721.0223 | 721.0223 | 721.0223 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -69.7941 | 651.2282 | -2750 | -200 | -2298.7718 | 57.47% | 38.03% | 95% | 0% | 1814 | -61
[5 empty] | 2019-10-28 | 8 | 7204 | 1742 | -60 | 0 | 0 | 1802 | 702.2259 | 702.2259 | 702.2259 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -68.6499 | 633.576 | -2750 | -200 | -2316.424 | 57.91% | 38.03% | 95% | 0% | 1802 | -60
[5 empty] | 2019-10-28 | 9 | 7204.5 | 1750 | -61 | 0 | 0 | 1811 | 716.3232 | 716.3232 | 716.3232 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -69.7941 | 646.5291 | -2750 | -200 | -2303.4709 | 57.59% | 38.01% | 95% | 0% | 1811 | -61
[5 empty] | 2019-10-28 | 10 | 7205 | 1777 | -61 | 1 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -69.7941 | 688.821 | -3550 | -400 | -3261.179 | 81.53% | 38.01% | 95% | 0% | 1838 | -61
[5 empty] | 2019-10-28 | 11 | 7205.5 | 1849 | -61 | 1 | 0 | 1910 | 871.3932 | 871.3932 | 871.3932 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -69.7941 | 801.5992 | -3550 | -400 | -3148.4008 | 78.71% | 38.01% | 95% | 0% | 1910 | -61
[5 empty] | 2019-10-28 | 12 | 7206 | 1968 | -61 | 1 | 0 | 2029 | 1057.7906 | 1057.7906 | 1057.7906 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -69.7941 | 987.9966 | -3550 | -400 | -2962.0034 | 74.05% | 38% | 95% | 0% | 2029 | -61
[5 empty] | 2019-10-28 | 13 | 7206.5 | 2219 | -60 | 1 | 0 | 2279 | 1449.3817 | 1449.3817 | 1449.3817 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -68.6499 | 1380.7318 | -3550 | -400 | -2569.2682 | 64.23% | 38% | 95% | 0% | 2279 | -60
[5 empty] | 2019-10-28 | 14 | 7207 | 2412 | -59 | 1 | 0 | 2471 | 1750.1237 | 1750.1237 | 1750.1237 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -67.5057 | 1682.6179 | -3550 | -400 | -2267.3821 | 56.68% | 37.99% | 95% | 0% | 2471 | -59
[5 empty] | 2019-10-28 | 15 | 7207.5 | 2608 | -80 | 1 | 0 | 2688 | 2090.0247 | 2090.0247 | 2090.0247 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -91.5332 | 1998.4916 | -3550 | -400 | -1951.5084 | 48.79% | 37.99% | 95% | 0% | 2688 | -80
[5 empty] | 2019-10-28 | 16 | 7208 | 2637 | -141 | 1 | 0 | 2778 | 2230.9975 | 2230.9975 | 2230.9975 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -161.3272 | 2069.6703 | -3550 | -400 | -1880.3297 | 47.01% | 37.99% | 95% | 0% | 2778 | -141
[5 empty] | 2019-10-28 | 17 | 7208.5 | 2648 | -209 | 1 | 0 | 2857 | 2354.7403 | 2354.7403 | 2354.7403 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -239.1304 | 2115.6099 | -3550 | -400 | -1834.3901 | 45.86% | 37.98% | 95% | 0% | 2857 | -209
[5 empty] | 2019-10-28 | 18 | 7209 | 2587 | -277 | 1 | 0 | 2864 | 2365.7049 | 2365.7049 | 2365.7049 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -316.9336 | 2048.7712 | -3550 | -400 | -1901.2288 | 47.53% | 37.98% | 95% | 0% | 2864 | -277
[5 empty] | 2019-10-28 | 19 | 7209.5 | 2517 | -339 | 1 | 0 | 2856 | 2353.1739 | 2353.1739 | 2353.1739 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -387.8719 | 1965.3021 | -3550 | -400 | -1984.6979 | 49.62% | 37.98% | 95% | 0% | 2856 | -339
[5 empty] | 2019-10-28 | 20 | 7210 | 2440 | -385 | 1 | 0 | 2825 | 2304.6167 | 2304.6167 | 2304.6167 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -440.5034 | 1864.1132 | -3550 | -400 | -2085.8868 | 52.15% | 37.96% | 95% | 0% | 2825 | -385
[5 empty] | 2019-10-28 | 21 | 7210.5 | 2358 | -424 | 1 | 0 | 2782 | 2237.263 | 2237.263 | 2237.263 | 644.2704 | 780 | 200 | 1624.2704 | 40.61% | 95% | 0% | -485.1259 | 1752.1371 | -3550 | -400 | -2197.8629 | 54.95% | 37.95% | 95% | 0% | 2782 | -424
[5 empty] | 2019-10-28 | 22 | 7211 | 2314 | -444 | 1 | 0 | 2758 | 2199.6702 | 2199.6702 | 2199.6702 | 642.704 | 780 | 200 | 1622.704 | 40.57% | 95% | 0% | -508.0092 | 1691.6611 | -3550 | -400 | -2258.3389 | 56.46% | 37.95% | 95% | 0% | 2758 | -444
[5 empty] | 2019-10-28 | 23 | 7211.5 | 2303 | -437 | 1 | 0 | 2740 | 2171.4757 | 2171.4757 | 2171.4757 | 642.704 | 780 | 200 | 1622.704 | 40.57% | 95% | 0% | -500 | 1671.4757 | -3550 | -400 | -2278.5243 | 56.96% | 37.93% | 95% | 0% | 2740 | -437
[5 empty] | 2019-10-28 | 24 | 7212 | 2316 | -429 | 1 | 0 | 2745 | 2179.3075 | 2179.3075 | 2179.3075 | 642.704 | 780 | 200 | 1622.704 | 40.57% | 95% | 0% | -490.8467 | 1688.4608 | -3550 | -400 | -2261.5392 | 56.54% | 37.92% | 95% | 0% | 2745 | -429
[5 empty] | 2019-10-28 | 25 | 7212.5 | 2368 | -395 | 1 | 0 | 2763 | 2207.5021 | 2207.5021 | 2207.5021 | 642.704 | 780 | 200 | 1622.704 | 40.57% | 95% | 0% | -451.9451 | 1755.557 | -3550 | -400 | -2194.443 | 54.86% | 37.91% | 95% | 0% | 2763 | -395
[5 empty] | 2019-10-28 | 26 | 7213 | 2432 | -336 | 1 | 0 | 2768 | 2215.3339 | 2215.3339 | 2215.3339 | 642.704 | 780 | 200 | 1622.704 | 40.57% | 95% | 0% | -384.4394 | 1830.8945 | -3550 | -400 | -2119.1055 | 52.98% | 37.91% | 95% | 0% | 2768 | -336
[5 empty] | 2019-10-28 | 27 | 7213.5 | 2484 | -300 | 1 | 0 | 2784 | 2240.3957 | 2240.3957 | 2240.3957 | 642.704 | 780 | 200 | 1622.704 | 40.57% | 95% | 0% | -343.2494 | 1897.1463 | -3550 | -400 | -2052.8537 | 51.32% | 37.91% | 95% | 0% | 2784 | -300
[5 empty] | 2019-10-28 | 28 | 7214 | 2550 | -260 | 1 | 0 | 2810 | 2281.1212 | 2281.1212 | 2281.1212 | 642.704 | 780 | 200 | 1622.704 | 40.57% | 95% | 0% | -297.4828 | 1983.6383 | -3550 | -400 | -1966.3617 | 49.16% | 37.9% | 95% | 0% | 2810 | -260
[5 empty] | 2019-10-28 | 29 | 7214.5 | 2605 | -232 | 1 | 0 | 2837 | 2323.413 | 2323.413 | 2323.413 | 642.704 | 780 | 200 | 1622.704 | 40.57% | 95% | 0% | -265.4462 | 2057.9668 | -3550 | -400 | -1892.0332 | 47.3% | 37.88% | 95% | 0% | 2837 | -232
[5 empty] | 2019-10-28 | 30 | 7215 | 2685 | -192 | 1 | 0 | 2877 | 2386.0676 | 2386.0676 | 2386.0676 | 642.704 | 780 | 200 | 1622.704 | 40.57% | 95% | 0% | -219.6796 | 2166.388 | -3550 | -400 | -1783.612 | 44.59% | 37.87% | 95% | 0% | 2877 | -192
[5 empty] | 2019-10-28 | 31 | 7215.5 | 2783 | -147 | 1 | 0 | 2930 | 2469.0849 | 2469.0849 | 2469.0849 | 642.704 | 780 | 200 | 1622.704 | 40.57% | 95% | 0% | -168.1922 | 2300.8927 | -3550 | -400 | -1649.1073 | 41.23% | 37.87% | 95% | 0% | 2930 | -147
[5 empty] | 2019-10-28 | 32 | 7216 | 2899 | -104 | 1 | 0 | 3003 | 2583.4295 | 2583.4295 | 2583.4295 | 641.1377 | 780 | 200 | 1621.1377 | 40.53% | 95% | 0% | -118.9931 | 2464.4364 | -3550 | -400 | -1485.5636 | 37.14% | 37.85% | 95% | 0% | 3003 | -104
[5 empty] | 2019-10-28 | 33 | 7216.5 | 3027 | -85 | 1 | 0 | 3112 | 2754.1632 | 2754.1632 | 2754.1632 | 641.1377 | 780 | 200 | 1621.1377 | 40.53% | 95% | 0% | -97.254 | 2656.9092 | -3550 | -400 | -1293.0908 | 32.33% | 37.83% | 95% | 0% | 3112 | -85
[5 empty] | 2019-10-28 | 34 | 7217 | 3173 | -81 | 1 | 0 | 3254 | 2976.587 | 2976.587 | 2976.587 | 641.1377 | 780 | 200 | 1621.1377 | 40.53% | 95% | 0% | -92.6773 | 2883.9096 | -3550 | -400 | -1066.0904 | 26.65% | 37.83% | 95% | 0% | 3254 | -81
[5 empty] | 2019-10-28 | 35 | 7217.5 | 3301 | -83 | 1 | 0 | 3384 | 3180.2143 | 3180.2143 | 3180.2143 | 641.1377 | 780 | 200 | 1621.1377 | 40.53% | 95% | 0% | -94.9657 | 3085.2487 | -3550 | -400 | -864.7513 | 21.62% | 37.82% | 95% | 0% | 3384 | -83
[5 empty] | 2019-10-28 | 36 | 7218 | 3299 | -85 | 1 | 0 | 3384 | 3180.2143 | 3180.2143 | 3180.2143 | 641.1377 | 780 | 200 | 1621.1377 | 40.53% | 95% | 0% | -97.254 | 3082.9603 | -3550 | -400 | -867.0397 | 21.68% | 37.82% | 95% | 0% | 3384 | -85
[5 empty] | 2019-10-28 | 37 | 7218.5 | 3278 | -86 | 0 | 0 | 3364 | 3148.8871 | 3148.8871 | 3148.8871 | 641.1377 | 780 | 200 | 1621.1377 | 40.53% | 95% | 0% | -98.3982 | 3050.4889 | -2750 | -200 | 100.4889 | -2.512% | 37.81% | 95% | 0% | 3364 | -86
[5 empty] | 2019-10-28 | 38 | 7219 | 3233 | -87 | 0 | 0 | 3320 | 3079.967 | 3079.967 | 3079.967 | 641.1377 | 780 | 200 | 1621.1377 | 40.53% | 95% | 0% | -99.5423 | 2980.4247 | -2750 | -200 | 30.4247 | -0.7606% | 37.8% | 95% | 0% | 3320 | -87
[5 empty] | 2019-10-28 | 39 | 7219.5 | 3121 | -87 | 0 | 0 | 3208 | 2904.5342 | 2904.5342 | 2904.5342 | 641.1377 | 780 | 200 | 1621.1377 | 40.53% | 95% | 0% | -99.5423 | 2804.9919 | -2750 | -200 | -145.0081 | 3.625% | 37.79% | 95% | 0% | 3208 | -87
[5 empty] | 2019-10-28 | 40 | 7220 | 3017 | -87 | 0 | 0 | 3104 | 2741.6323 | 2741.6323 | 2741.6323 | 641.1377 | 780 | 200 | 1621.1377 | 40.53% | 95% | 0% | -99.5423 | 2642.09 | -2750 | -200 | -307.91 | 7.698% | 37.79% | 95% | 0% | 3104 | -87
[5 empty] | 2019-10-28 | 41 | 7220.5 | 2902 | -87 | 0 | 0 | 2989 | 2561.5004 | 2561.5004 | 2561.5004 | 639.5713 | 780 | 200 | 1619.5713 | 40.49% | 95% | 0% | -99.5423 | 2461.9581 | -2750 | -200 | -488.0419 | 12.2% | 37.78% | 95% | 0% | 2989 | -87
[5 empty] | 2019-10-28 | 42 | 7221 | 2774 | -87 | 0 | 0 | 2861 | 2361.0058 | 2361.0058 | 2361.0058 | 639.5713 | 780 | 200 | 1619.5713 | 40.49% | 95% | 0% | -99.5423 | 2261.4634 | -2750 | -200 | -688.5366 | 17.21% | 37.78% | 95% | 0% | 2861 | -87
[5 empty] | 2019-10-28 | 43 | 7221.5 | 2636 | -87 | 0 | 0 | 2723 | 2144.8475 | 2144.8475 | 2144.8475 | 639.5713 | 780 | 200 | 1619.5713 | 40.49% | 95% | 0% | -99.5423 | 2045.3052 | -2750 | -200 | -904.6948 | 22.62% | 37.78% | 95% | 0% | 2723 | -87
[5 empty] | 2019-10-28 | 44 | 7222 | 2474 | -86 | 0 | 0 | 2560 | 1889.5301 | 1889.5301 | 1889.5301 | 639.5713 | 780 | 200 | 1619.5713 | 40.49% | 95% | 0% | -98.3982 | 1791.1319 | -2750 | -200 | -1158.8681 | 28.97% | 37.77% | 95% | 0% | 2560 | -86
[5 empty] | 2019-10-28 | 45 | 7222.5 | 2313 | -87 | 0 | 0 | 2400 | 1638.9118 | 1638.9118 | 1638.9118 | 639.5713 | 780 | 200 | 1619.5713 | 40.49% | 95% | 0% | -99.5423 | 1539.3695 | -2750 | -200 | -1410.6305 | 35.27% | 37.76% | 95% | 0% | 2400 | -87
[5 empty] | 2019-10-28 | 46 | 7223 | 2166 | -87 | 0 | 0 | 2253 | 1408.6562 | 1408.6562 | 1408.6562 | 639.5713 | 780 | 200 | 1619.5713 | 40.49% | 95% | 0% | -99.5423 | 1309.1139 | -2750 | -200 | -1640.8861 | 41.02% | 37.76% | 95% | 0% | 2253 | -87
[5 empty] | 2019-10-28 | 47 | 7223.5 | 2023 | -86 | 0 | 0 | 2109 | 1183.0998 | 1183.0998 | 1183.0998 | 639.5713 | 780 | 200 | 1619.5713 | 40.49% | 95% | 0% | -98.3982 | 1084.7016 | -2750 | -200 | -1865.2984 | 46.63% | 37.76% | 95% | 0% | 2109 | -86
[5 empty] | 2019-10-28 | 48 | 7224 | 1932 | -84 | 0 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 638.0049 | 780 | 200 | 1618.0049 | 40.45% | 95% | 0% | -96.1098 | 941.318 | -2750 | -200 | -2008.682 | 50.22% | 37.75% | 95% | 0% | 2016 | -84
[5 empty] | 2019-10-29 | 1 | 7224.5 | 1900 | -86 | 0 | 0 | 1986 | 990.4369 | 990.4369 | 990.4369 | 638.0049 | 780 | 200 | 1618.0049 | 40.45% | 95% | 0% | -98.3982 | 892.0388 | -2750 | -200 | -2057.9612 | 51.45% | 37.75% | 95% | 0% | 1986 | -86
[5 empty] | 2019-10-29 | 2 | 7225 | 1915 | -87 | 0 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 638.0049 | 780 | 200 | 1618.0049 | 40.45% | 95% | 0% | -99.5423 | 915.9564 | -2750 | -200 | -2034.0436 | 50.85% | 37.74% | 95% | 0% | 2002 | -87
[5 empty] | 2019-10-29 | 3 | 7225.5 | 1889 | -88 | 0 | 0 | 1977 | 976.3397 | 976.3397 | 976.3397 | 638.0049 | 780 | 200 | 1618.0049 | 40.45% | 95% | 0% | -100.6865 | 875.6532 | -2750 | -200 | -2074.3468 | 51.86% | 37.74% | 95% | 0% | 1977 | -88
[5 empty] | 2019-10-29 | 4 | 7226 | 1839 | -89 | 0 | 0 | 1928 | 899.5878 | 899.5878 | 899.5878 | 638.0049 | 780 | 200 | 1618.0049 | 40.45% | 95% | 0% | -101.8307 | 797.7571 | -2750 | -200 | -2152.2429 | 53.81% | 37.73% | 95% | 0% | 1928 | -89
[5 empty] | 2019-10-29 | 5 | 7226.5 | 1791 | -89 | 0 | 0 | 1880 | 824.4023 | 824.4023 | 824.4023 | 638.0049 | 780 | 200 | 1618.0049 | 40.45% | 95% | 0% | -101.8307 | 722.5716 | -2750 | -200 | -2227.4284 | 55.69% | 37.72% | 95% | 0% | 1880 | -89
[5 empty] | 2019-10-29 | 6 | 7227 | 1775 | -89 | 1 | 0 | 1864 | 799.3405 | 799.3405 | 799.3405 | 638.0049 | 780 | 200 | 1618.0049 | 40.45% | 95% | 0% | -101.8307 | 697.5098 | -3550 | -400 | -3252.4902 | 81.31% | 37.71% | 95% | 0% | 1864 | -89
[5 empty] | 2019-10-29 | 7 | 7227.5 | 1749 | -90 | 1 | 0 | 1839 | 760.1814 | 760.1814 | 760.1814 | 638.0049 | 780 | 200 | 1618.0049 | 40.45% | 95% | 0% | -102.9748 | 657.2065 | -3550 | -400 | -3292.7935 | 82.32% | 37.7% | 95% | 0% | 1839 | -90
[5 empty] | 2019-10-29 | 8 | 7228 | 1727 | -91 | 1 | 0 | 1818 | 727.2877 | 727.2877 | 727.2877 | 638.0049 | 780 | 200 | 1618.0049 | 40.45% | 95% | 0% | -104.119 | 623.1687 | -3550 | -400 | -3326.8313 | 83.17% | 37.7% | 95% | 0% | 1818 | -91
[5 empty] | 2019-10-29 | 9 | 7228.5 | 1714 | -92 | 1 | 0 | 1806 | 708.4913 | 708.4913 | 708.4913 | 638.0049 | 780 | 200 | 1618.0049 | 40.45% | 95% | 0% | -105.2632 | 603.2282 | -3550 | -400 | -3346.7718 | 83.67% | 37.7% | 95% | 0% | 1806 | -92
[5 empty] | 2019-10-29 | 10 | 7229 | 1732 | -93 | 1 | 0 | 1825 | 738.2523 | 738.2523 | 738.2523 | 636.4386 | 780 | 200 | 1616.4386 | 40.41% | 95% | 0% | -106.4073 | 631.8449 | -3550 | -400 | -3318.1551 | 82.95% | 37.69% | 95% | 0% | 1825 | -93
[5 empty] | 2019-10-29 | 11 | 7229.5 | 1808 | -93 | 1 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 636.4386 | 780 | 200 | 1616.4386 | 40.41% | 95% | 0% | -106.4073 | 750.8886 | -3550 | -400 | -3199.1114 | 79.98% | 37.66% | 95% | 0% | 1901 | -93
[5 empty] | 2019-10-29 | 12 | 7230 | 1928 | -94 | 1 | 0 | 2022 | 1046.8261 | 1046.8261 | 1046.8261 | 636.4386 | 780 | 200 | 1616.4386 | 40.41% | 95% | 0% | -107.5515 | 939.2746 | -3550 | -400 | -3010.7254 | 75.27% | 37.66% | 95% | 0% | 2022 | -94
[5 empty] | 2019-10-29 | 13 | 7230.5 | 2167 | -93 | 1 | 0 | 2260 | 1419.6208 | 1419.6208 | 1419.6208 | 636.4386 | 780 | 200 | 1616.4386 | 40.41% | 95% | 0% | -106.4073 | 1313.2135 | -3550 | -400 | -2636.7865 | 65.92% | 37.66% | 95% | 0% | 2260 | -93
[5 empty] | 2019-10-29 | 14 | 7231 | 2365 | -93 | 1 | 0 | 2458 | 1729.7609 | 1729.7609 | 1729.7609 | 636.4386 | 780 | 200 | 1616.4386 | 40.41% | 95% | 0% | -106.4073 | 1623.3536 | -3550 | -400 | -2326.6464 | 58.17% | 37.66% | 95% | 0% | 2458 | -93
[5 empty] | 2019-10-29 | 15 | 7231.5 | 2553 | -101 | 1 | 0 | 2654 | 2036.7683 | 2036.7683 | 2036.7683 | 636.4386 | 780 | 200 | 1616.4386 | 40.41% | 95% | 0% | -115.5606 | 1921.2077 | -3550 | -400 | -2028.7923 | 50.72% | 37.65% | 95% | 0% | 2654 | -101
[5 empty] | 2019-10-29 | 16 | 7232 | 2623 | -135 | 1 | 0 | 2758 | 2199.6702 | 2199.6702 | 2199.6702 | 636.4386 | 780 | 200 | 1616.4386 | 40.41% | 95% | 0% | -154.4622 | 2045.208 | -3550 | -400 | -1904.792 | 47.62% | 37.64% | 95% | 0% | 2758 | -135
[5 empty] | 2019-10-29 | 17 | 7232.5 | 2675 | -180 | 1 | 0 | 2855 | 2351.6076 | 2351.6076 | 2351.6076 | 634.8722 | 780 | 200 | 1614.8722 | 40.37% | 95% | 0% | -205.9497 | 2145.6579 | -3550 | -400 | -1804.3421 | 45.11% | 37.64% | 95% | 0% | 2855 | -180
[5 empty] | 2019-10-29 | 18 | 7233 | 2642 | -228 | 1 | 0 | 2870 | 2375.1031 | 2375.1031 | 2375.1031 | 634.8722 | 780 | 200 | 1614.8722 | 40.37% | 95% | 0% | -260.8696 | 2114.2335 | -3550 | -400 | -1835.7665 | 45.89% | 37.64% | 95% | 0% | 2870 | -228
[5 empty] | 2019-10-29 | 19 | 7233.5 | 2621 | -266 | 1 | 0 | 2887 | 2401.7312 | 2401.7312 | 2401.7312 | 634.8722 | 780 | 200 | 1614.8722 | 40.37% | 95% | 0% | -304.3478 | 2097.3834 | -3550 | -400 | -1852.6166 | 46.32% | 37.64% | 95% | 0% | 2887 | -266
[5 empty] | 2019-10-29 | 20 | 7234 | 2555 | -305 | 1 | 0 | 2860 | 2359.4394 | 2359.4394 | 2359.4394 | 634.8722 | 780 | 200 | 1614.8722 | 40.37% | 95% | 0% | -348.9703 | 2010.4692 | -3550 | -400 | -1939.5308 | 48.49% | 37.64% | 95% | 0% | 2860 | -305
[5 empty] | 2019-10-29 | 21 | 7234.5 | 2464 | -347 | 1 | 0 | 2811 | 2282.6876 | 2282.6876 | 2282.6876 | 634.8722 | 780 | 200 | 1614.8722 | 40.37% | 95% | 0% | -397.0252 | 1885.6624 | -3550 | -400 | -2064.3376 | 51.61% | 37.63% | 95% | 0% | 2811 | -347
[5 empty] | 2019-10-29 | 22 | 7235 | 2400 | -374 | 1 | 0 | 2774 | 2224.7321 | 2224.7321 | 2224.7321 | 634.8722 | 780 | 200 | 1614.8722 | 40.37% | 95% | 0% | -427.9176 | 1796.8144 | -3550 | -400 | -2153.1856 | 53.83% | 37.63% | 95% | 0% | 2774 | -374
[5 empty] | 2019-10-29 | 23 | 7235.5 | 2379 | -381 | 1 | 0 | 2760 | 2202.803 | 2202.803 | 2202.803 | 634.8722 | 780 | 200 | 1614.8722 | 40.37% | 95% | 0% | -435.9268 | 1766.8762 | -3550 | -400 | -2183.1238 | 54.58% | 37.63% | 95% | 0% | 2760 | -381
[5 empty] | 2019-10-29 | 24 | 7236 | 2378 | -373 | 1 | 0 | 2751 | 2188.7057 | 2188.7057 | 2188.7057 | 634.8722 | 780 | 200 | 1614.8722 | 40.37% | 95% | 0% | -426.7735 | 1761.9322 | -3550 | -400 | -2188.0678 | 54.7% | 37.62% | 95% | 0% | 2751 | -373
[5 empty] | 2019-10-29 | 25 | 7236.5 | 2413 | -357 | 1 | 0 | 2770 | 2218.4666 | 2218.4666 | 2218.4666 | 634.8722 | 780 | 200 | 1614.8722 | 40.37% | 95% | 0% | -408.4668 | 1809.9998 | -3550 | -400 | -2140.0002 | 53.5% | 37.61% | 95% | 0% | 2770 | -357
[5 empty] | 2019-10-29 | 26 | 7237 | 2421 | -347 | 1 | 0 | 2768 | 2215.3339 | 2215.3339 | 2215.3339 | 634.8722 | 780 | 200 | 1614.8722 | 40.37% | 95% | 0% | -397.0252 | 1818.3087 | -3550 | -400 | -2131.6913 | 53.29% | 37.61% | 95% | 0% | 2768 | -347
[5 empty] | 2019-10-29 | 27 | 7237.5 | 2443 | -323 | 1 | 0 | 2766 | 2212.2012 | 2212.2012 | 2212.2012 | 634.8722 | 780 | 200 | 1614.8722 | 40.37% | 95% | 0% | -369.5652 | 1842.6359 | -3550 | -400 | -2107.3641 | 52.68% | 37.6% | 95% | 0% | 2766 | -323
[5 empty] | 2019-10-29 | 28 | 7238 | 2463 | -302 | 1 | 0 | 2765 | 2210.6348 | 2210.6348 | 2210.6348 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -345.5378 | 1865.097 | -3550 | -400 | -2084.903 | 52.12% | 37.59% | 95% | 0% | 2765 | -302
[5 empty] | 2019-10-29 | 29 | 7238.5 | 2530 | -254 | 1 | 0 | 2784 | 2240.3957 | 2240.3957 | 2240.3957 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -290.6178 | 1949.7779 | -3550 | -400 | -2000.2221 | 50.01% | 37.59% | 95% | 0% | 2784 | -254
[5 empty] | 2019-10-29 | 30 | 7239 | 2596 | -218 | 1 | 0 | 2814 | 2287.3866 | 2287.3866 | 2287.3866 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -249.4279 | 2037.9587 | -3550 | -400 | -1912.0413 | 47.8% | 37.58% | 95% | 0% | 2814 | -218
[5 empty] | 2019-10-29 | 31 | 7239.5 | 2681 | -174 | 1 | 0 | 2855 | 2351.6076 | 2351.6076 | 2351.6076 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -199.0847 | 2152.5229 | -3550 | -400 | -1797.4771 | 44.94% | 37.58% | 95% | 0% | 2855 | -174
[5 empty] | 2019-10-29 | 32 | 7240 | 2803 | -130 | 1 | 0 | 2933 | 2473.784 | 2473.784 | 2473.784 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -148.7414 | 2325.0426 | -3550 | -400 | -1624.9574 | 40.62% | 37.57% | 95% | 0% | 2933 | -130
[5 empty] | 2019-10-29 | 33 | 7240.5 | 2922 | -103 | 1 | 0 | 3025 | 2617.8895 | 2617.8895 | 2617.8895 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -117.849 | 2500.0406 | -3550 | -400 | -1449.9594 | 36.25% | 37.57% | 95% | 0% | 3025 | -103
[5 empty] | 2019-10-29 | 34 | 7241 | 3064 | -96 | 1 | 0 | 3160 | 2829.3487 | 2829.3487 | 2829.3487 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -109.8398 | 2719.5089 | -3550 | -400 | -1230.4911 | 30.76% | 37.57% | 95% | 0% | 3160 | -96
[5 empty] | 2019-10-29 | 35 | 7241.5 | 3234 | -96 | 1 | 0 | 3330 | 3095.6307 | 3095.6307 | 3095.6307 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -109.8398 | 2985.7909 | -3550 | -400 | -964.2091 | 24.11% | 37.57% | 95% | 0% | 3330 | -96
[5 empty] | 2019-10-29 | 36 | 7242 | 3269 | -97 | 1 | 0 | 3366 | 3152.0198 | 3152.0198 | 3152.0198 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -110.984 | 3041.0358 | -3550 | -400 | -908.9642 | 22.72% | 37.56% | 95% | 0% | 3366 | -97
[5 empty] | 2019-10-29 | 37 | 7242.5 | 3235 | -97 | 0 | 0 | 3332 | 3098.7634 | 3098.7634 | 3098.7634 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -110.984 | 2987.7794 | -2750 | -200 | 37.7794 | -0.9445% | 37.56% | 95% | 0% | 3332 | -97
[5 empty] | 2019-10-29 | 38 | 7243 | 3167 | -98 | 0 | 0 | 3265 | 2993.817 | 2993.817 | 2993.817 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -112.1281 | 2881.6888 | -2750 | -200 | -68.3112 | 1.708% | 37.56% | 95% | 0% | 3265 | -98
[5 empty] | 2019-10-29 | 39 | 7243.5 | 3066 | -98 | 0 | 0 | 3164 | 2835.6142 | 2835.6142 | 2835.6142 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -112.1281 | 2723.486 | -2750 | -200 | -226.514 | 5.663% | 37.56% | 95% | 0% | 3164 | -98
[5 empty] | 2019-10-29 | 40 | 7244 | 2979 | -97 | 0 | 0 | 3076 | 2697.7741 | 2697.7741 | 2697.7741 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -110.984 | 2586.7901 | -2750 | -200 | -363.2099 | 9.08% | 37.54% | 95% | 0% | 3076 | -97
[5 empty] | 2019-10-29 | 41 | 7244.5 | 2873 | -97 | 0 | 0 | 2970 | 2531.7395 | 2531.7395 | 2531.7395 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -110.984 | 2420.7555 | -2750 | -200 | -529.2445 | 13.23% | 37.54% | 95% | 0% | 2970 | -97
[5 empty] | 2019-10-29 | 42 | 7245 | 2733 | -97 | 0 | 0 | 2830 | 2312.4485 | 2312.4485 | 2312.4485 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -110.984 | 2201.4645 | -2750 | -200 | -748.5355 | 18.71% | 37.54% | 95% | 0% | 2830 | -97
[5 empty] | 2019-10-29 | 43 | 7245.5 | 2600 | -97 | 0 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 633.3059 | 780 | 200 | 1613.3059 | 40.33% | 95% | 0% | -110.984 | 1993.138 | -2750 | -200 | -956.862 | 23.92% | 37.53% | 95% | 0% | 2697 | -97
[5 empty] | 2019-10-29 | 44 | 7246 | 2455 | -96 | 0 | 0 | 2551 | 1875.4328 | 1875.4328 | 1875.4328 | 631.7395 | 780 | 200 | 1611.7395 | 40.29% | 95% | 0% | -109.8398 | 1765.593 | -2750 | -200 | -1184.407 | 29.61% | 37.53% | 95% | 0% | 2551 | -96
[5 empty] | 2019-10-29 | 45 | 7246.5 | 2294 | -95 | 0 | 0 | 2389 | 1621.6818 | 1621.6818 | 1621.6818 | 631.7395 | 780 | 200 | 1611.7395 | 40.29% | 95% | 0% | -108.6957 | 1512.9861 | -2750 | -200 | -1437.0139 | 35.93% | 37.51% | 95% | 0% | 2389 | -95
[5 empty] | 2019-10-29 | 46 | 7247 | 2147 | -94 | 0 | 0 | 2241 | 1389.8599 | 1389.8599 | 1389.8599 | 631.7395 | 780 | 200 | 1611.7395 | 40.29% | 95% | 0% | -107.5515 | 1282.3084 | -2750 | -200 | -1667.6916 | 41.69% | 37.51% | 95% | 0% | 2241 | -94
[5 empty] | 2019-10-29 | 47 | 7247.5 | 2005 | -93 | 0 | 0 | 2098 | 1165.8697 | 1165.8697 | 1165.8697 | 631.7395 | 780 | 200 | 1611.7395 | 40.29% | 95% | 0% | -106.4073 | 1059.4624 | -2750 | -200 | -1890.5376 | 47.26% | 37.51% | 95% | 0% | 2098 | -93
[5 empty] | 2019-10-29 | 48 | 7248 | 1913 | -92 | 0 | 0 | 2005 | 1020.1979 | 1020.1979 | 1020.1979 | 631.7395 | 780 | 200 | 1611.7395 | 40.29% | 95% | 0% | -105.2632 | 914.9347 | -2750 | -200 | -2035.0653 | 50.88% | 37.5% | 95% | 0% | 2005 | -92
[5 empty] | 2019-10-30 | 1 | 7248.5 | 1881 | -92 | 0 | 0 | 1973 | 970.0742 | 970.0742 | 970.0742 | 631.7395 | 780 | 200 | 1611.7395 | 40.29% | 95% | 0% | -105.2632 | 864.811 | -2750 | -200 | -2085.189 | 52.13% | 37.5% | 95% | 0% | 1973 | -92
[5 empty] | 2019-10-30 | 2 | 7249 | 1884 | -92 | 0 | 0 | 1976 | 974.7733 | 974.7733 | 974.7733 | 631.7395 | 780 | 200 | 1611.7395 | 40.29% | 95% | 0% | -105.2632 | 869.5101 | -2750 | -200 | -2080.4899 | 52.01% | 37.5% | 95% | 0% | 1976 | -92
[5 empty] | 2019-10-30 | 3 | 7249.5 | 1859 | -91 | 0 | 0 | 1950 | 934.0478 | 934.0478 | 934.0478 | 631.7395 | 780 | 200 | 1611.7395 | 40.29% | 95% | 0% | -104.119 | 829.9288 | -2750 | -200 | -2120.0712 | 53% | 37.49% | 95% | 0% | 1950 | -91
[5 empty] | 2019-10-30 | 4 | 7250 | 1809 | -90 | 0 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 630.1731 | 780 | 200 | 1610.1731 | 40.25% | 95% | 0% | -102.9748 | 751.1884 | -2750 | -200 | -2198.8116 | 54.97% | 37.48% | 95% | 0% | 1899 | -90
[5 empty] | 2019-10-30 | 5 | 7250.5 | 1759 | -90 | 0 | 0 | 1849 | 775.845 | 775.845 | 775.845 | 630.1731 | 780 | 200 | 1610.1731 | 40.25% | 95% | 0% | -102.9748 | 672.8702 | -2750 | -200 | -2277.1298 | 56.93% | 37.45% | 95% | 0% | 1849 | -90
[5 empty] | 2019-10-30 | 6 | 7251 | 1749 | -89 | 0 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 630.1731 | 780 | 200 | 1610.1731 | 40.25% | 95% | 0% | -101.8307 | 656.7843 | -2750 | -200 | -2293.2157 | 57.33% | 37.44% | 95% | 0% | 1838 | -89
[5 empty] | 2019-10-30 | 7 | 7251.5 | 1726 | -90 | 0 | 0 | 1816 | 724.155 | 724.155 | 724.155 | 630.1731 | 780 | 200 | 1610.1731 | 40.25% | 95% | 0% | -102.9748 | 621.1802 | -2750 | -200 | -2328.8198 | 58.22% | 37.44% | 95% | 0% | 1816 | -90
[5 empty] | 2019-10-30 | 8 | 7252 | 1710 | -91 | 0 | 0 | 1801 | 700.6595 | 700.6595 | 700.6595 | 630.1731 | 780 | 200 | 1610.1731 | 40.25% | 95% | 0% | -104.119 | 596.5405 | -2750 | -200 | -2353.4595 | 58.84% | 37.44% | 95% | 0% | 1801 | -91
[5 empty] | 2019-10-30 | 9 | 7252.5 | 1706 | -92 | 0 | 0 | 1798 | 695.9604 | 695.9604 | 695.9604 | 630.1731 | 780 | 200 | 1610.1731 | 40.25% | 95% | 0% | -105.2632 | 590.6973 | -2750 | -200 | -2359.3027 | 58.98% | 37.43% | 95% | 0% | 1798 | -92
[5 empty] | 2019-10-30 | 10 | 7253 | 1727 | -94 | 0 | 0 | 1821 | 731.9868 | 731.9868 | 731.9868 | 630.1731 | 780 | 200 | 1610.1731 | 40.25% | 95% | 0% | -107.5515 | 624.4353 | -2750 | -200 | -2325.5647 | 58.14% | 37.43% | 95% | 0% | 1821 | -94
[5 empty] | 2019-10-30 | 11 | 7253.5 | 1795 | -95 | 0 | 0 | 1890 | 840.066 | 840.066 | 840.066 | 630.1731 | 780 | 200 | 1610.1731 | 40.25% | 95% | 0% | -108.6957 | 731.3703 | -2750 | -200 | -2218.6297 | 55.47% | 37.41% | 95% | 0% | 1890 | -95
[5 empty] | 2019-10-30 | 12 | 7254 | 1902 | -95 | 0 | 0 | 1997 | 1007.6669 | 1007.6669 | 1007.6669 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -108.6957 | 898.9713 | -2750 | -200 | -2051.0287 | 51.28% | 37.41% | 95% | 0% | 1997 | -95
[5 empty] | 2019-10-30 | 13 | 7254.5 | 2144 | -96 | 0 | 0 | 2240 | 1388.2935 | 1388.2935 | 1388.2935 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -109.8398 | 1278.4537 | -2750 | -200 | -1671.5463 | 41.79% | 37.41% | 95% | 0% | 2240 | -96
[5 empty] | 2019-10-30 | 14 | 7255 | 2349 | -96 | 0 | 0 | 2445 | 1709.3982 | 1709.3982 | 1709.3982 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -109.8398 | 1599.5584 | -2750 | -200 | -1350.4416 | 33.76% | 37.39% | 95% | 0% | 2445 | -96
[5 empty] | 2019-10-30 | 15 | 7255.5 | 2530 | -105 | 0 | 0 | 2635 | 2007.0074 | 2007.0074 | 2007.0074 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -120.1373 | 1886.8701 | -2750 | -200 | -1063.1299 | 26.58% | 37.38% | 95% | 0% | 2635 | -105
[5 empty] | 2019-10-30 | 16 | 7256 | 2583 | -146 | 0 | 0 | 2729 | 2154.2457 | 2154.2457 | 2154.2457 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -167.0481 | 1987.1976 | -2750 | -200 | -962.8024 | 24.07% | 37.38% | 95% | 0% | 2729 | -146
[5 empty] | 2019-10-30 | 17 | 7256.5 | 2587 | -207 | 1 | 0 | 2794 | 2256.0594 | 2256.0594 | 2256.0594 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -236.8421 | 2019.2173 | -3550 | -400 | -1930.7827 | 48.27% | 37.37% | 95% | 0% | 2794 | -207
[5 empty] | 2019-10-30 | 18 | 7257 | 2529 | -268 | 1 | 0 | 2797 | 2260.7585 | 2260.7585 | 2260.7585 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -306.6362 | 1954.1223 | -3550 | -400 | -1995.8777 | 49.9% | 37.36% | 95% | 0% | 2797 | -268
[5 empty] | 2019-10-30 | 19 | 7257.5 | 2477 | -330 | 1 | 0 | 2807 | 2276.4221 | 2276.4221 | 2276.4221 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -377.5744 | 1898.8477 | -3550 | -400 | -2051.1523 | 51.28% | 37.36% | 95% | 0% | 2807 | -330
[5 empty] | 2019-10-30 | 20 | 7258 | 2399 | -374 | 1 | 0 | 2773 | 2223.1657 | 2223.1657 | 2223.1657 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -427.9176 | 1795.2481 | -3550 | -400 | -2154.7519 | 53.87% | 37.36% | 95% | 0% | 2773 | -374
[5 empty] | 2019-10-30 | 21 | 7258.5 | 2328 | -398 | 1 | 0 | 2726 | 2149.5466 | 2149.5466 | 2149.5466 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -455.3776 | 1694.169 | -3550 | -400 | -2255.831 | 56.4% | 37.36% | 95% | 0% | 2726 | -398
[5 empty] | 2019-10-30 | 22 | 7259 | 2246 | -445 | 1 | 0 | 2691 | 2094.7238 | 2094.7238 | 2094.7238 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -509.1533 | 1585.5705 | -3550 | -400 | -2364.4295 | 59.11% | 37.34% | 95% | 0% | 2691 | -445
[5 empty] | 2019-10-30 | 23 | 7259.5 | 2223 | -457 | 1 | 0 | 2680 | 2077.4938 | 2077.4938 | 2077.4938 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -522.8833 | 1554.6105 | -3550 | -400 | -2395.3895 | 59.88% | 37.34% | 95% | 0% | 2680 | -457
[5 empty] | 2019-10-30 | 24 | 7260 | 2244 | -447 | 1 | 0 | 2691 | 2094.7238 | 2094.7238 | 2094.7238 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -511.4416 | 1583.2822 | -3550 | -400 | -2366.7178 | 59.17% | 37.32% | 95% | 0% | 2691 | -447
[5 empty] | 2019-10-30 | 25 | 7260.5 | 2321 | -410 | 1 | 0 | 2731 | 2157.3784 | 2157.3784 | 2157.3784 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -469.1076 | 1688.2708 | -3550 | -400 | -2261.7292 | 56.54% | 37.31% | 95% | 0% | 2731 | -410
[5 empty] | 2019-10-30 | 26 | 7261 | 2394 | -336 | 1 | 0 | 2730 | 2155.812 | 2155.812 | 2155.812 | 628.6068 | 780 | 200 | 1608.6068 | 40.22% | 95% | 0% | -384.4394 | 1771.3727 | -3550 | -400 | -2178.6273 | 54.47% | 37.31% | 95% | 0% | 2730 | -336
[5 empty] | 2019-10-30 | 27 | 7261.5 | 2432 | -310 | 1 | 0 | 2742 | 2174.6084 | 2174.6084 | 2174.6084 | 627.0404 | 780 | 200 | 1607.0404 | 40.18% | 95% | 0% | -354.6911 | 1819.9173 | -3550 | -400 | -2130.0827 | 53.25% | 37.31% | 95% | 0% | 2742 | -310
[5 empty] | 2019-10-30 | 28 | 7262 | 2455 | -304 | 1 | 0 | 2759 | 2201.2366 | 2201.2366 | 2201.2366 | 627.0404 | 780 | 200 | 1607.0404 | 40.18% | 95% | 0% | -347.8261 | 1853.4105 | -3550 | -400 | -2096.5895 | 52.41% | 37.27% | 95% | 0% | 2759 | -304
[5 empty] | 2019-10-30 | 29 | 7262.5 | 2537 | -251 | 1 | 0 | 2788 | 2246.6612 | 2246.6612 | 2246.6612 | 627.0404 | 780 | 200 | 1607.0404 | 40.18% | 95% | 0% | -287.1854 | 1959.4758 | -3550 | -400 | -1990.5242 | 49.76% | 37.26% | 95% | 0% | 2788 | -251
[5 empty] | 2019-10-30 | 30 | 7263 | 2577 | -213 | 1 | 0 | 2790 | 2249.7939 | 2249.7939 | 2249.7939 | 627.0404 | 780 | 200 | 1607.0404 | 40.18% | 95% | 0% | -243.7071 | 2006.0868 | -3550 | -400 | -1943.9132 | 48.6% | 37.25% | 95% | 0% | 2790 | -213
[5 empty] | 2019-10-30 | 31 | 7263.5 | 2651 | -176 | 1 | 0 | 2827 | 2307.7494 | 2307.7494 | 2307.7494 | 627.0404 | 780 | 200 | 1607.0404 | 40.18% | 95% | 0% | -201.373 | 2106.3764 | -3550 | -400 | -1843.6236 | 46.09% | 37.25% | 95% | 0% | 2827 | -176
[5 empty] | 2019-10-30 | 32 | 7264 | 2744 | -141 | 1 | 0 | 2885 | 2398.5985 | 2398.5985 | 2398.5985 | 627.0404 | 780 | 200 | 1607.0404 | 40.18% | 95% | 0% | -161.3272 | 2237.2713 | -3550 | -400 | -1712.7287 | 42.82% | 37.25% | 95% | 0% | 2885 | -141
[5 empty] | 2019-10-30 | 33 | 7264.5 | 2848 | -121 | 1 | 0 | 2969 | 2530.1731 | 2530.1731 | 2530.1731 | 627.0404 | 780 | 200 | 1607.0404 | 40.18% | 95% | 0% | -138.4439 | 2391.7292 | -3550 | -400 | -1558.2708 | 38.96% | 37.24% | 95% | 0% | 2969 | -121
[5 empty] | 2019-10-30 | 34 | 7265 | 3013 | -116 | 1 | 0 | 3129 | 2780.7914 | 2780.7914 | 2780.7914 | 627.0404 | 780 | 200 | 1607.0404 | 40.18% | 95% | 0% | -132.7231 | 2648.0683 | -3550 | -400 | -1301.9317 | 32.55% | 37.24% | 95% | 0% | 3129 | -116
[5 empty] | 2019-10-30 | 35 | 7265.5 | 3152 | -117 | 1 | 0 | 3269 | 3000.0824 | 3000.0824 | 3000.0824 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -133.8673 | 2866.2152 | -3550 | -400 | -1083.7848 | 27.09% | 37.24% | 95% | 0% | 3269 | -117
[5 empty] | 2019-10-30 | 36 | 7266 | 3138 | -117 | 0 | 0 | 3255 | 2978.1533 | 2978.1533 | 2978.1533 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -133.8673 | 2844.2861 | -2750 | -200 | -105.7139 | 2.643% | 37.24% | 95% | 0% | 3255 | -117
[5 empty] | 2019-10-30 | 37 | 7266.5 | 3098 | -117 | 0 | 0 | 3215 | 2915.4988 | 2915.4988 | 2915.4988 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -133.8673 | 2781.6315 | -2750 | -200 | -168.3685 | 4.209% | 37.18% | 95% | 0% | 3215 | -117
[5 empty] | 2019-10-30 | 38 | 7267 | 3074 | -117 | 0 | 0 | 3191 | 2877.906 | 2877.906 | 2877.906 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -133.8673 | 2744.0387 | -2750 | -200 | -205.9613 | 5.149% | 37.18% | 95% | 0% | 3191 | -117
[5 empty] | 2019-10-30 | 39 | 7267.5 | 2992 | -117 | 0 | 0 | 3109 | 2749.4641 | 2749.4641 | 2749.4641 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -133.8673 | 2615.5969 | -2750 | -200 | -334.4031 | 8.36% | 37.17% | 95% | 0% | 3109 | -117
[5 empty] | 2019-10-30 | 40 | 7268 | 2907 | -117 | 0 | 0 | 3024 | 2616.3232 | 2616.3232 | 2616.3232 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -133.8673 | 2482.4559 | -2750 | -200 | -467.5441 | 11.69% | 37.17% | 95% | 0% | 3024 | -117
[5 empty] | 2019-10-30 | 41 | 7268.5 | 2824 | -117 | 0 | 0 | 2941 | 2486.3149 | 2486.3149 | 2486.3149 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -133.8673 | 2352.4476 | -2750 | -200 | -597.5524 | 14.94% | 37.17% | 95% | 0% | 2941 | -117
[5 empty] | 2019-10-30 | 42 | 7269 | 2695 | -116 | 0 | 0 | 2811 | 2282.6876 | 2282.6876 | 2282.6876 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -132.7231 | 2149.9644 | -2750 | -200 | -800.0356 | 20% | 37.17% | 95% | 0% | 2811 | -116
[5 empty] | 2019-10-30 | 43 | 7269.5 | 2564 | -115 | 0 | 0 | 2679 | 2075.9275 | 2075.9275 | 2075.9275 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -131.5789 | 1944.3485 | -2750 | -200 | -1005.6515 | 25.14% | 37.16% | 95% | 0% | 2679 | -115
[5 empty] | 2019-10-30 | 44 | 7270 | 2419 | -113 | 0 | 0 | 2532 | 1845.6719 | 1845.6719 | 1845.6719 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -129.2906 | 1716.3813 | -2750 | -200 | -1233.6187 | 30.84% | 37.15% | 95% | 0% | 2532 | -113
[5 empty] | 2019-10-30 | 45 | 7270.5 | 2275 | -111 | 0 | 0 | 2386 | 1616.9827 | 1616.9827 | 1616.9827 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -127.0023 | 1489.9804 | -2750 | -200 | -1460.0196 | 36.5% | 37.15% | 95% | 0% | 2386 | -111
[5 empty] | 2019-10-30 | 46 | 7271 | 2142 | -110 | 0 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -125.8581 | 1281.2317 | -2750 | -200 | -1668.7683 | 41.72% | 37.15% | 95% | 0% | 2252 | -110
[5 empty] | 2019-10-30 | 47 | 7271.5 | 1999 | -109 | 0 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 625.474 | 780 | 200 | 1605.474 | 40.14% | 95% | 0% | -124.714 | 1056.8194 | -2750 | -200 | -1893.1806 | 47.33% | 37.14% | 95% | 0% | 2108 | -109
[5 empty] | 2019-10-30 | 48 | 7272 | 1894 | -109 | 1 | 0 | 2003 | 1017.0651 | 1017.0651 | 1017.0651 | 623.9077 | 780 | 200 | 1603.9077 | 40.1% | 95% | 0% | -124.714 | 892.3512 | -3550 | -400 | -3057.6488 | 76.44% | 37.14% | 95% | 0% | 2003 | -109
[5 empty] | 2019-10-31 | 1 | 7272.5 | 1872 | -107 | 1 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 623.9077 | 780 | 200 | 1603.9077 | 40.1% | 95% | 0% | -122.4256 | 857.0468 | -3550 | -400 | -3092.9532 | 77.32% | 37.14% | 95% | 0% | 1979 | -107
[5 empty] | 2019-10-31 | 2 | 7273 | 1887 | -106 | 1 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 623.9077 | 780 | 200 | 1603.9077 | 40.1% | 95% | 0% | -121.2815 | 880.12 | -3550 | -400 | -3069.88 | 76.75% | 37.14% | 95% | 0% | 1993 | -106
[5 empty] | 2019-10-31 | 3 | 7273.5 | 1862 | -104 | 1 | 0 | 1966 | 959.1096 | 959.1096 | 959.1096 | 623.9077 | 780 | 200 | 1603.9077 | 40.1% | 95% | 0% | -118.9931 | 840.1165 | -3550 | -400 | -3109.8835 | 77.75% | 37.13% | 95% | 0% | 1966 | -104
[5 empty] | 2019-10-31 | 4 | 7274 | 1820 | -103 | 1 | 0 | 1923 | 891.756 | 891.756 | 891.756 | 623.9077 | 780 | 200 | 1603.9077 | 40.1% | 95% | 0% | -117.849 | 773.907 | -3550 | -400 | -3176.093 | 79.4% | 37.13% | 95% | 0% | 1923 | -103
[5 empty] | 2019-10-31 | 5 | 7274.5 | 1785 | -102 | 1 | 0 | 1887 | 835.3669 | 835.3669 | 835.3669 | 623.9077 | 780 | 200 | 1603.9077 | 40.1% | 95% | 0% | -116.7048 | 718.6621 | -3550 | -400 | -3231.3379 | 80.78% | 37.13% | 95% | 0% | 1887 | -102
[5 empty] | 2019-10-31 | 6 | 7275 | 1776 | -100 | 1 | 0 | 1876 | 818.1369 | 818.1369 | 818.1369 | 623.9077 | 780 | 200 | 1603.9077 | 40.1% | 95% | 0% | -114.4165 | 703.7204 | -3550 | -400 | -3246.2796 | 81.16% | 37.13% | 95% | 0% | 1876 | -100
[5 empty] | 2019-10-31 | 7 | 7275.5 | 1749 | -101 | 1 | 0 | 1850 | 777.4114 | 777.4114 | 777.4114 | 623.9077 | 780 | 200 | 1603.9077 | 40.1% | 95% | 0% | -115.5606 | 661.8507 | -3550 | -400 | -3288.1493 | 82.2% | 37.12% | 95% | 0% | 1850 | -101
[5 empty] | 2019-10-31 | 8 | 7276 | 1722 | -102 | 1 | 0 | 1824 | 736.6859 | 736.6859 | 736.6859 | 623.9077 | 780 | 200 | 1603.9077 | 40.1% | 95% | 0% | -116.7048 | 619.9811 | -3550 | -400 | -3330.0189 | 83.25% | 37.11% | 95% | 0% | 1824 | -102
[5 empty] | 2019-10-31 | 9 | 7276.5 | 1716 | -103 | 1 | 0 | 1819 | 728.8541 | 728.8541 | 728.8541 | 622.3413 | 780 | 200 | 1602.3413 | 40.06% | 95% | 0% | -117.849 | 611.0051 | -3550 | -400 | -3338.9949 | 83.47% | 37.11% | 95% | 0% | 1819 | -103
[5 empty] | 2019-10-31 | 10 | 7277 | 1734 | -104 | 1 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 622.3413 | 780 | 200 | 1602.3413 | 40.06% | 95% | 0% | -118.9931 | 639.6219 | -3550 | -400 | -3310.3781 | 82.76% | 37.11% | 95% | 0% | 1838 | -104
[5 empty] | 2019-10-31 | 11 | 7277.5 | 1811 | -104 | 1 | 0 | 1915 | 879.2251 | 879.2251 | 879.2251 | 622.3413 | 780 | 200 | 1602.3413 | 40.06% | 95% | 0% | -118.9931 | 760.2319 | -3550 | -400 | -3189.7681 | 79.74% | 37.1% | 95% | 0% | 1915 | -104
[5 empty] | 2019-10-31 | 12 | 7278 | 1916 | -104 | 1 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 622.3413 | 780 | 200 | 1602.3413 | 40.06% | 95% | 0% | -118.9931 | 924.7002 | -3550 | -400 | -3025.2998 | 75.63% | 37.1% | 95% | 0% | 2020 | -104
[5 empty] | 2019-10-31 | 13 | 7278.5 | 2146 | -103 | 1 | 0 | 2249 | 1402.3908 | 1402.3908 | 1402.3908 | 622.3413 | 780 | 200 | 1602.3413 | 40.06% | 95% | 0% | -117.849 | 1284.5418 | -3550 | -400 | -2665.4582 | 66.64% | 37.09% | 95% | 0% | 2249 | -103
[5 empty] | 2019-10-31 | 14 | 7279 | 2342 | -102 | 1 | 0 | 2444 | 1707.8318 | 1707.8318 | 1707.8318 | 622.3413 | 780 | 200 | 1602.3413 | 40.06% | 95% | 0% | -116.7048 | 1591.127 | -3550 | -400 | -2358.873 | 58.97% | 37.07% | 95% | 0% | 2444 | -102
[5 empty] | 2019-10-31 | 15 | 7279.5 | 2541 | -108 | 1 | 0 | 2649 | 2028.9365 | 2028.9365 | 2028.9365 | 622.3413 | 780 | 200 | 1602.3413 | 40.06% | 95% | 0% | -123.5698 | 1905.3667 | -3550 | -400 | -2044.6333 | 51.12% | 37.06% | 95% | 0% | 2649 | -108
[5 empty] | 2019-10-31 | 16 | 7280 | 2632 | -129 | 1 | 0 | 2761 | 2204.3693 | 2204.3693 | 2204.3693 | 622.3413 | 780 | 200 | 1602.3413 | 40.06% | 95% | 0% | -147.5973 | 2056.7721 | -3550 | -400 | -1893.2279 | 47.33% | 37.06% | 95% | 0% | 2761 | -129
[5 empty] | 2019-10-31 | 17 | 7280.5 | 2689 | -165 | 1 | 0 | 2854 | 2350.0412 | 2350.0412 | 2350.0412 | 622.3413 | 780 | 200 | 1602.3413 | 40.06% | 95% | 0% | -188.7872 | 2161.254 | -3550 | -400 | -1788.746 | 44.72% | 37.06% | 95% | 0% | 2854 | -165
[5 empty] | 2019-10-31 | 18 | 7281 | 2665 | -210 | 1 | 0 | 2875 | 2382.9349 | 2382.9349 | 2382.9349 | 622.3413 | 780 | 200 | 1602.3413 | 40.06% | 95% | 0% | -240.2746 | 2142.6603 | -3550 | -400 | -1807.3397 | 45.18% | 37.05% | 95% | 0% | 2875 | -210
[5 empty] | 2019-10-31 | 19 | 7281.5 | 2633 | -255 | 1 | 0 | 2888 | 2403.2976 | 2403.2976 | 2403.2976 | 622.3413 | 780 | 200 | 1602.3413 | 40.06% | 95% | 0% | -291.762 | 2111.5356 | -3550 | -400 | -1838.4644 | 45.96% | 37.04% | 95% | 0% | 2888 | -255
[5 empty] | 2019-10-31 | 20 | 7282 | 2577 | -303 | 1 | 0 | 2880 | 2390.7667 | 2390.7667 | 2390.7667 | 622.3413 | 780 | 200 | 1602.3413 | 40.06% | 95% | 0% | -346.6819 | 2044.0848 | -3550 | -400 | -1905.9152 | 47.65% | 37.04% | 95% | 0% | 2880 | -303
[5 empty] | 2019-10-31 | 21 | 7282.5 | 2527 | -329 | 1 | 0 | 2856 | 2353.1739 | 2353.1739 | 2353.1739 | 620.7749 | 780 | 200 | 1600.7749 | 40.02% | 95% | 0% | -376.4302 | 1976.7437 | -3550 | -400 | -1973.2563 | 49.33% | 37.04% | 95% | 0% | 2856 | -329
[5 empty] | 2019-10-31 | 22 | 7283 | 2498 | -350 | 1 | 0 | 2848 | 2340.643 | 2340.643 | 2340.643 | 620.7749 | 780 | 200 | 1600.7749 | 40.02% | 95% | 0% | -400.4577 | 1940.1854 | -3550 | -400 | -2009.8146 | 50.25% | 37.02% | 95% | 0% | 2848 | -350
[5 empty] | 2019-10-31 | 23 | 7283.5 | 2507 | -339 | 1 | 0 | 2846 | 2337.5103 | 2337.5103 | 2337.5103 | 620.7749 | 780 | 200 | 1600.7749 | 40.02% | 95% | 0% | -387.8719 | 1949.6385 | -3550 | -400 | -2000.3615 | 50.01% | 37% | 95% | 0% | 2846 | -339
[5 empty] | 2019-10-31 | 24 | 7284 | 2507 | -333 | 1 | 0 | 2840 | 2328.1121 | 2328.1121 | 2328.1121 | 620.7749 | 780 | 200 | 1600.7749 | 40.02% | 95% | 0% | -381.0069 | 1947.1053 | -3550 | -400 | -2002.8947 | 50.07% | 36.99% | 95% | 0% | 2840 | -333
[5 empty] | 2019-10-31 | 25 | 7284.5 | 2521 | -331 | 1 | 0 | 2852 | 2346.9085 | 2346.9085 | 2346.9085 | 620.7749 | 780 | 200 | 1600.7749 | 40.02% | 95% | 0% | -378.7185 | 1968.19 | -3550 | -400 | -1981.81 | 49.55% | 36.99% | 95% | 0% | 2852 | -331
[5 empty] | 2019-10-31 | 26 | 7285 | 2541 | -305 | 1 | 0 | 2846 | 2337.5103 | 2337.5103 | 2337.5103 | 620.7749 | 780 | 200 | 1600.7749 | 40.02% | 95% | 0% | -348.9703 | 1988.5401 | -3550 | -400 | -1961.4599 | 49.04% | 36.99% | 95% | 0% | 2846 | -305
[5 empty] | 2019-10-31 | 27 | 7285.5 | 2565 | -291 | 1 | 0 | 2856 | 2353.1739 | 2353.1739 | 2353.1739 | 620.7749 | 780 | 200 | 1600.7749 | 40.02% | 95% | 0% | -332.9519 | 2020.222 | -3550 | -400 | -1929.778 | 48.24% | 36.98% | 95% | 0% | 2856 | -291
[5 empty] | 2019-10-31 | 28 | 7286 | 2603 | -253 | 1 | 0 | 2856 | 2353.1739 | 2353.1739 | 2353.1739 | 620.7749 | 780 | 200 | 1600.7749 | 40.02% | 95% | 0% | -289.4737 | 2063.7003 | -3550 | -400 | -1886.2997 | 47.16% | 36.98% | 95% | 0% | 2856 | -253
[5 empty] | 2019-10-31 | 29 | 7286.5 | 2643 | -224 | 1 | 0 | 2867 | 2370.404 | 2370.404 | 2370.404 | 620.7749 | 780 | 200 | 1600.7749 | 40.02% | 95% | 0% | -256.2929 | 2114.1111 | -3550 | -400 | -1835.8889 | 45.9% | 36.97% | 95% | 0% | 2867 | -224
[5 empty] | 2019-10-31 | 30 | 7287 | 2707 | -185 | 1 | 0 | 2892 | 2409.5631 | 2409.5631 | 2409.5631 | 620.7749 | 780 | 200 | 1600.7749 | 40.02% | 95% | 0% | -211.6705 | 2197.8926 | -3550 | -400 | -1752.1074 | 43.8% | 36.96% | 95% | 0% | 2892 | -185
[5 empty] | 2019-10-31 | 31 | 7287.5 | 2778 | -149 | 1 | 0 | 2927 | 2464.3858 | 2464.3858 | 2464.3858 | 620.7749 | 780 | 200 | 1600.7749 | 40.02% | 95% | 0% | -170.4805 | 2293.9053 | -3550 | -400 | -1656.0947 | 41.4% | 36.96% | 95% | 0% | 2927 | -149
[5 empty] | 2019-10-31 | 32 | 7288 | 2867 | -118 | 1 | 0 | 2985 | 2555.235 | 2555.235 | 2555.235 | 620.7749 | 780 | 200 | 1600.7749 | 40.02% | 95% | 0% | -135.0114 | 2420.2235 | -3550 | -400 | -1529.7765 | 38.24% | 36.95% | 95% | 0% | 2985 | -118
[5 empty] | 2019-10-31 | 33 | 7288.5 | 2997 | -102 | 1 | 0 | 3099 | 2733.8005 | 2733.8005 | 2733.8005 | 619.2086 | 780 | 200 | 1599.2086 | 39.98% | 95% | 0% | -116.7048 | 2617.0957 | -3550 | -400 | -1332.9043 | 33.32% | 36.95% | 95% | 0% | 3099 | -102
[5 empty] | 2019-10-31 | 34 | 7289 | 3110 | -101 | 1 | 0 | 3211 | 2909.2333 | 2909.2333 | 2909.2333 | 619.2086 | 780 | 200 | 1599.2086 | 39.98% | 95% | 0% | -115.5606 | 2793.6727 | -3550 | -400 | -1156.3273 | 28.91% | 36.95% | 95% | 0% | 3211 | -101
[5 empty] | 2019-10-31 | 35 | 7289.5 | 3223 | -104 | 1 | 0 | 3327 | 3090.9316 | 3090.9316 | 3090.9316 | 619.2086 | 780 | 200 | 1599.2086 | 39.98% | 95% | 0% | -118.9931 | 2971.9384 | -3550 | -400 | -978.0616 | 24.45% | 36.95% | 95% | 0% | 3327 | -104
[5 empty] | 2019-10-31 | 36 | 7290 | 3186 | -106 | 0 | 0 | 3292 | 3036.1088 | 3036.1088 | 3036.1088 | 619.2086 | 780 | 200 | 1599.2086 | 39.98% | 95% | 0% | -121.2815 | 2914.8274 | -2750 | -200 | -35.1726 | 0.8793% | 36.95% | 95% | 0% | 3292 | -106
[5 empty] | 2019-10-31 | 37 | 7290.5 | 3121 | -106 | 0 | 0 | 3227 | 2934.2951 | 2934.2951 | 2934.2951 | 619.2086 | 780 | 200 | 1599.2086 | 39.98% | 95% | 0% | -121.2815 | 2813.0137 | -2750 | -200 | -136.9863 | 3.425% | 36.92% | 95% | 0% | 3227 | -106
[5 empty] | 2019-10-31 | 38 | 7291 | 3066 | -107 | 0 | 0 | 3173 | 2849.7115 | 2849.7115 | 2849.7115 | 619.2086 | 780 | 200 | 1599.2086 | 39.98% | 95% | 0% | -122.4256 | 2727.2858 | -2750 | -200 | -222.7142 | 5.568% | 36.92% | 95% | 0% | 3173 | -107
[5 empty] | 2019-10-31 | 39 | 7291.5 | 2974 | -107 | 0 | 0 | 3081 | 2705.6059 | 2705.6059 | 2705.6059 | 619.2086 | 780 | 200 | 1599.2086 | 39.98% | 95% | 0% | -122.4256 | 2583.1803 | -2750 | -200 | -366.8197 | 9.17% | 36.89% | 95% | 0% | 3081 | -107
[5 empty] | 2019-10-31 | 40 | 7292 | 2909 | -107 | 0 | 0 | 3016 | 2603.7923 | 2603.7923 | 2603.7923 | 619.2086 | 780 | 200 | 1599.2086 | 39.98% | 95% | 0% | -122.4256 | 2481.3666 | -2750 | -200 | -468.6334 | 11.72% | 36.87% | 95% | 0% | 3016 | -107
[5 empty] | 2019-10-31 | 41 | 7292.5 | 2837 | -108 | 0 | 0 | 2945 | 2492.5804 | 2492.5804 | 2492.5804 | 619.2086 | 780 | 200 | 1599.2086 | 39.98% | 95% | 0% | -123.5698 | 2369.0106 | -2750 | -200 | -580.9894 | 14.52% | 36.87% | 95% | 0% | 2945 | -108
[5 empty] | 2019-10-31 | 42 | 7293 | 2731 | -108 | 0 | 0 | 2839 | 2326.5458 | 2326.5458 | 2326.5458 | 619.2086 | 780 | 200 | 1599.2086 | 39.98% | 95% | 0% | -123.5698 | 2202.976 | -2750 | -200 | -747.024 | 18.68% | 36.85% | 95% | 0% | 2839 | -108
[5 empty] | 2019-10-31 | 43 | 7293.5 | 2613 | -108 | 0 | 0 | 2721 | 2141.7148 | 2141.7148 | 2141.7148 | 619.2086 | 780 | 200 | 1599.2086 | 39.98% | 95% | 0% | -123.5698 | 2018.145 | -2750 | -200 | -931.855 | 23.3% | 36.85% | 95% | 0% | 2721 | -108
[5 empty] | 2019-10-31 | 44 | 7294 | 2461 | -108 | 0 | 0 | 2569 | 1903.6274 | 1903.6274 | 1903.6274 | 617.6422 | 780 | 200 | 1597.6422 | 39.94% | 95% | 0% | -123.5698 | 1780.0576 | -2750 | -200 | -1169.9424 | 29.25% | 36.85% | 95% | 0% | 2569 | -108
[5 empty] | 2019-10-31 | 45 | 7294.5 | 2318 | -108 | 0 | 0 | 2426 | 1679.6373 | 1679.6373 | 1679.6373 | 617.6422 | 780 | 200 | 1597.6422 | 39.94% | 95% | 0% | -123.5698 | 1556.0675 | -2750 | -200 | -1393.9325 | 34.85% | 36.84% | 95% | 0% | 2426 | -108
[5 empty] | 2019-10-31 | 46 | 7295 | 2181 | -108 | 0 | 0 | 2289 | 1465.0453 | 1465.0453 | 1465.0453 | 617.6422 | 780 | 200 | 1597.6422 | 39.94% | 95% | 0% | -123.5698 | 1341.4755 | -2750 | -200 | -1608.5245 | 40.21% | 36.84% | 95% | 0% | 2289 | -108
[5 empty] | 2019-10-31 | 47 | 7295.5 | 2033 | -107 | 0 | 0 | 2140 | 1231.657 | 1231.657 | 1231.657 | 617.6422 | 780 | 200 | 1597.6422 | 39.94% | 95% | 0% | -122.4256 | 1109.2314 | -2750 | -200 | -1840.7686 | 46.02% | 36.84% | 95% | 0% | 2140 | -107
[5 empty] | 2019-10-31 | 48 | 7296 | 1947 | -105 | 0 | 0 | 2052 | 1093.817 | 1093.817 | 1093.817 | 617.6422 | 780 | 200 | 1597.6422 | 39.94% | 95% | 0% | -120.1373 | 973.6797 | -2750 | -200 | -1976.3203 | 49.41% | 36.83% | 95% | 0% | 2052 | -105
[5 empty] | 2019-11-01 | 1 | 7296.5 | 1911 | -106 | 0 | 0 | 2017 | 1038.9942 | 1038.9942 | 1038.9942 | 617.6422 | 780 | 200 | 1597.6422 | 39.94% | 95% | 0% | -121.2815 | 917.7128 | -2750 | -200 | -2032.2872 | 50.81% | 36.83% | 95% | 0% | 2017 | -106
[5 empty] | 2019-11-01 | 2 | 7297 | 1919 | -106 | 0 | 0 | 2025 | 1051.5251 | 1051.5251 | 1051.5251 | 617.6422 | 780 | 200 | 1597.6422 | 39.94% | 95% | 0% | -121.2815 | 930.2437 | -2750 | -200 | -2019.7563 | 50.49% | 36.82% | 95% | 0% | 2025 | -106
[5 empty] | 2019-11-01 | 3 | 7297.5 | 1884 | -106 | 0 | 0 | 1990 | 996.7024 | 996.7024 | 996.7024 | 616.0758 | 780 | 200 | 1596.0758 | 39.9% | 95% | 0% | -121.2815 | 875.4209 | -2750 | -200 | -2074.5791 | 51.86% | 36.81% | 95% | 0% | 1990 | -106
[5 empty] | 2019-11-01 | 4 | 7298 | 1832 | -106 | 0 | 0 | 1938 | 915.2514 | 915.2514 | 915.2514 | 616.0758 | 780 | 200 | 1596.0758 | 39.9% | 95% | 0% | -121.2815 | 793.97 | -2750 | -200 | -2156.03 | 53.9% | 36.8% | 95% | 0% | 1938 | -106
[5 empty] | 2019-11-01 | 5 | 7298.5 | 1794 | -105 | 0 | 0 | 1899 | 854.1632 | 854.1632 | 854.1632 | 616.0758 | 780 | 200 | 1596.0758 | 39.9% | 95% | 0% | -120.1373 | 734.0259 | -2750 | -200 | -2215.9741 | 55.4% | 36.78% | 95% | 0% | 1899 | -105
[5 empty] | 2019-11-01 | 6 | 7299 | 1771 | -104 | 0 | 0 | 1875 | 816.5705 | 816.5705 | 816.5705 | 616.0758 | 780 | 200 | 1596.0758 | 39.9% | 95% | 0% | -118.9931 | 697.5774 | -2750 | -200 | -2252.4226 | 56.31% | 36.77% | 95% | 0% | 1875 | -104
[5 empty] | 2019-11-01 | 7 | 7299.5 | 1740 | -105 | 0 | 0 | 1845 | 769.5796 | 769.5796 | 769.5796 | 616.0758 | 780 | 200 | 1596.0758 | 39.9% | 95% | 0% | -120.1373 | 649.4423 | -2750 | -200 | -2300.5577 | 57.51% | 36.77% | 95% | 0% | 1845 | -105
[5 empty] | 2019-11-01 | 8 | 7300 | 1698 | -105 | 0 | 0 | 1803 | 703.7923 | 703.7923 | 703.7923 | 616.0758 | 780 | 200 | 1596.0758 | 39.9% | 95% | 0% | -120.1373 | 583.655 | -2750 | -200 | -2366.345 | 59.16% | 36.76% | 95% | 0% | 1803 | -105
[5 empty] | 2019-11-01 | 9 | 7300.5 | 1689 | -107 | 0 | 0 | 1796 | 692.8277 | 692.8277 | 692.8277 | 616.0758 | 780 | 200 | 1596.0758 | 39.9% | 95% | 0% | -122.4256 | 570.4021 | -2750 | -200 | -2379.5979 | 59.49% | 36.76% | 95% | 0% | 1796 | -107
[5 empty] | 2019-11-01 | 10 | 7301 | 1698 | -108 | 1 | 0 | 1806 | 708.4913 | 708.4913 | 708.4913 | 616.0758 | 780 | 200 | 1596.0758 | 39.9% | 95% | 0% | -123.5698 | 584.9215 | -3550 | -400 | -3365.0785 | 84.13% | 36.76% | 95% | 0% | 1806 | -108
[5 empty] | 2019-11-01 | 11 | 7301.5 | 1759 | -109 | 1 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 616.0758 | 780 | 200 | 1596.0758 | 39.9% | 95% | 0% | -124.714 | 680.892 | -3550 | -400 | -3269.108 | 81.73% | 36.75% | 95% | 0% | 1868 | -109
[5 empty] | 2019-11-01 | 12 | 7302 | 1851 | -110 | 1 | 0 | 1961 | 951.2778 | 951.2778 | 951.2778 | 616.0758 | 780 | 200 | 1596.0758 | 39.9% | 95% | 0% | -125.8581 | 825.4197 | -3550 | -400 | -3124.5803 | 78.11% | 36.74% | 95% | 0% | 1961 | -110
[5 empty] | 2019-11-01 | 13 | 7302.5 | 2066 | -110 | 1 | 0 | 2176 | 1288.0462 | 1288.0462 | 1288.0462 | 614.5095 | 780 | 200 | 1594.5095 | 39.86% | 95% | 0% | -125.8581 | 1162.188 | -3550 | -400 | -2787.812 | 69.7% | 36.74% | 95% | 0% | 2176 | -110
[5 empty] | 2019-11-01 | 14 | 7303 | 2259 | -110 | 1 | 0 | 2369 | 1590.3545 | 1590.3545 | 1590.3545 | 614.5095 | 780 | 200 | 1594.5095 | 39.86% | 95% | 0% | -125.8581 | 1464.4964 | -3550 | -400 | -2485.5036 | 62.14% | 36.73% | 95% | 0% | 2369 | -110
[5 empty] | 2019-11-01 | 15 | 7303.5 | 2455 | -112 | 1 | 0 | 2567 | 1900.4946 | 1900.4946 | 1900.4946 | 614.5095 | 780 | 200 | 1594.5095 | 39.86% | 95% | 0% | -128.1465 | 1772.3482 | -3550 | -400 | -2177.6518 | 54.44% | 36.73% | 95% | 0% | 2567 | -112
[5 empty] | 2019-11-01 | 16 | 7304 | 2552 | -116 | 1 | 0 | 2668 | 2058.6974 | 2058.6974 | 2058.6974 | 614.5095 | 780 | 200 | 1594.5095 | 39.86% | 95% | 0% | -132.7231 | 1925.9743 | -3550 | -400 | -2024.0257 | 50.6% | 36.71% | 95% | 0% | 2668 | -116
[5 empty] | 2019-11-01 | 17 | 7304.5 | 2655 | -130 | 1 | 0 | 2785 | 2241.9621 | 2241.9621 | 2241.9621 | 614.5095 | 780 | 200 | 1594.5095 | 39.86% | 95% | 0% | -148.7414 | 2093.2207 | -3550 | -400 | -1856.7793 | 46.42% | 36.71% | 95% | 0% | 2785 | -130
[5 empty] | 2019-11-01 | 18 | 7305 | 2695 | -141 | 1 | 0 | 2836 | 2321.8467 | 2321.8467 | 2321.8467 | 614.5095 | 780 | 200 | 1594.5095 | 39.86% | 95% | 0% | -161.3272 | 2160.5194 | -3550 | -400 | -1789.4806 | 44.74% | 36.71% | 95% | 0% | 2836 | -141
[5 empty] | 2019-11-01 | 19 | 7305.5 | 2723 | -154 | 1 | 0 | 2877 | 2386.0676 | 2386.0676 | 2386.0676 | 614.5095 | 780 | 200 | 1594.5095 | 39.86% | 95% | 0% | -176.2014 | 2209.8662 | -3550 | -400 | -1740.1338 | 43.5% | 36.7% | 95% | 0% | 2877 | -154
[5 empty] | 2019-11-01 | 20 | 7306 | 2711 | -171 | 1 | 0 | 2882 | 2393.8994 | 2393.8994 | 2393.8994 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -195.6522 | 2198.2472 | -3550 | -400 | -1751.7528 | 43.79% | 36.7% | 95% | 0% | 2882 | -171
[5 empty] | 2019-11-01 | 21 | 7306.5 | 2700 | -175 | 1 | 0 | 2875 | 2382.9349 | 2382.9349 | 2382.9349 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -200.2288 | 2182.706 | -3550 | -400 | -1767.294 | 44.18% | 36.69% | 95% | 0% | 2875 | -175
[5 empty] | 2019-11-01 | 22 | 7307 | 2675 | -186 | 1 | 0 | 2861 | 2361.0058 | 2361.0058 | 2361.0058 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -212.8146 | 2148.1911 | -3550 | -400 | -1801.8089 | 45.05% | 36.66% | 95% | 0% | 2861 | -186
[5 empty] | 2019-11-01 | 23 | 7307.5 | 2667 | -197 | 1 | 0 | 2864 | 2365.7049 | 2365.7049 | 2365.7049 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -225.4005 | 2140.3044 | -3550 | -400 | -1809.6956 | 45.24% | 36.65% | 95% | 0% | 2864 | -197
[5 empty] | 2019-11-01 | 24 | 7308 | 2680 | -204 | 1 | 0 | 2884 | 2397.0322 | 2397.0322 | 2397.0322 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -233.4096 | 2163.6225 | -3550 | -400 | -1786.3775 | 44.66% | 36.64% | 95% | 0% | 2884 | -204
[5 empty] | 2019-11-01 | 25 | 7308.5 | 2697 | -185 | 1 | 0 | 2882 | 2393.8994 | 2393.8994 | 2393.8994 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -211.6705 | 2182.2289 | -3550 | -400 | -1767.7711 | 44.19% | 36.64% | 95% | 0% | 2882 | -185
[5 empty] | 2019-11-01 | 26 | 7309 | 2680 | -183 | 1 | 0 | 2863 | 2364.1385 | 2364.1385 | 2364.1385 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -209.3822 | 2154.7563 | -3550 | -400 | -1795.2437 | 44.88% | 36.61% | 95% | 0% | 2863 | -183
[5 empty] | 2019-11-01 | 27 | 7309.5 | 2675 | -181 | 1 | 0 | 2856 | 2353.1739 | 2353.1739 | 2353.1739 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -207.0938 | 2146.0801 | -3550 | -400 | -1803.9199 | 45.1% | 36.6% | 95% | 0% | 2856 | -181
[5 empty] | 2019-11-01 | 28 | 7310 | 2667 | -171 | 1 | 0 | 2838 | 2324.9794 | 2324.9794 | 2324.9794 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -195.6522 | 2129.3272 | -3550 | -400 | -1820.6728 | 45.52% | 36.6% | 95% | 0% | 2838 | -171
[5 empty] | 2019-11-01 | 29 | 7310.5 | 2665 | -159 | 1 | 0 | 2824 | 2303.0503 | 2303.0503 | 2303.0503 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -181.9222 | 2121.1281 | -3550 | -400 | -1828.8719 | 45.72% | 36.58% | 95% | 0% | 2824 | -159
[5 empty] | 2019-11-01 | 30 | 7311 | 2683 | -135 | 1 | 0 | 2818 | 2293.6521 | 2293.6521 | 2293.6521 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -154.4622 | 2139.1899 | -3550 | -400 | -1810.8101 | 45.27% | 36.58% | 95% | 0% | 2818 | -135
[5 empty] | 2019-11-01 | 31 | 7311.5 | 2703 | -129 | 1 | 0 | 2832 | 2315.5812 | 2315.5812 | 2315.5812 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -147.5973 | 2167.9839 | -3550 | -400 | -1782.0161 | 44.55% | 36.58% | 95% | 0% | 2832 | -129
[5 empty] | 2019-11-01 | 32 | 7312 | 2754 | -118 | 1 | 0 | 2872 | 2378.2358 | 2378.2358 | 2378.2358 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -135.0114 | 2243.2243 | -3550 | -400 | -1706.7757 | 42.67% | 36.57% | 95% | 0% | 2872 | -118
[5 empty] | 2019-11-01 | 33 | 7312.5 | 2816 | -108 | 1 | 0 | 2924 | 2459.6867 | 2459.6867 | 2459.6867 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -123.5698 | 2336.1169 | -3550 | -400 | -1613.8831 | 40.35% | 36.56% | 95% | 0% | 2924 | -108
[5 empty] | 2019-11-01 | 34 | 7313 | 2913 | -106 | 1 | 0 | 3019 | 2608.4913 | 2608.4913 | 2608.4913 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -121.2815 | 2487.2099 | -3550 | -400 | -1462.7901 | 36.57% | 36.56% | 95% | 0% | 3019 | -106
[5 empty] | 2019-11-01 | 35 | 7313.5 | 3005 | -106 | 0 | 0 | 3111 | 2752.5969 | 2752.5969 | 2752.5969 | 612.9431 | 780 | 200 | 1592.9431 | 39.82% | 95% | 0% | -121.2815 | 2631.3154 | -2750 | -200 | -318.6846 | 7.967% | 36.55% | 95% | 0% | 3111 | -106
[5 empty] | 2019-11-01 | 36 | 7314 | 2992 | -107 | 0 | 0 | 3099 | 2733.8005 | 2733.8005 | 2733.8005 | 611.3768 | 780 | 200 | 1591.3768 | 39.78% | 95% | 0% | -122.4256 | 2611.3749 | -2750 | -200 | -338.6251 | 8.466% | 36.52% | 95% | 0% | 3099 | -107
[5 empty] | 2019-11-01 | 37 | 7314.5 | 2944 | -109 | 0 | 0 | 3053 | 2661.7477 | 2661.7477 | 2661.7477 | 611.3768 | 780 | 200 | 1591.3768 | 39.78% | 95% | 0% | -124.714 | 2537.0338 | -2750 | -200 | -412.9662 | 10.32% | 36.52% | 95% | 0% | 3053 | -109
[5 empty] | 2019-11-01 | 38 | 7315 | 2887 | -112 | 0 | 0 | 2999 | 2577.1641 | 2577.1641 | 2577.1641 | 611.3768 | 780 | 200 | 1591.3768 | 39.78% | 95% | 0% | -128.1465 | 2449.0176 | -2750 | -200 | -500.9824 | 12.52% | 36.52% | 95% | 0% | 2999 | -112
[5 empty] | 2019-11-01 | 39 | 7315.5 | 2782 | -115 | 0 | 0 | 2897 | 2417.3949 | 2417.3949 | 2417.3949 | 611.3768 | 780 | 200 | 1591.3768 | 39.78% | 95% | 0% | -131.5789 | 2285.8159 | -2750 | -200 | -664.1841 | 16.6% | 36.51% | 95% | 0% | 2897 | -115
[5 empty] | 2019-11-01 | 40 | 7316 | 2680 | -119 | 0 | 0 | 2799 | 2263.8912 | 2263.8912 | 2263.8912 | 611.3768 | 780 | 200 | 1591.3768 | 39.78% | 95% | 0% | -136.1556 | 2127.7356 | -2750 | -200 | -822.2644 | 20.56% | 36.51% | 95% | 0% | 2799 | -119
[5 empty] | 2019-11-01 | 41 | 7316.5 | 2581 | -125 | 0 | 0 | 2706 | 2118.2193 | 2118.2193 | 2118.2193 | 611.3768 | 780 | 200 | 1591.3768 | 39.78% | 95% | 0% | -143.0206 | 1975.1987 | -2750 | -200 | -974.8013 | 24.37% | 36.5% | 95% | 0% | 2706 | -125
[5 empty] | 2019-11-01 | 42 | 7317 | 2451 | -132 | 0 | 0 | 2583 | 1925.5565 | 1925.5565 | 1925.5565 | 611.3768 | 780 | 200 | 1591.3768 | 39.78% | 95% | 0% | -151.0297 | 1774.5267 | -2750 | -200 | -1175.4733 | 29.39% | 36.5% | 95% | 0% | 2583 | -132
[5 empty] | 2019-11-01 | 43 | 7317.5 | 2313 | -137 | 0 | 0 | 2450 | 1717.23 | 1717.23 | 1717.23 | 611.3768 | 780 | 200 | 1591.3768 | 39.78% | 95% | 0% | -156.7506 | 1560.4794 | -2750 | -200 | -1389.5206 | 34.74% | 36.5% | 95% | 0% | 2450 | -137
[5 empty] | 2019-11-01 | 44 | 7318 | 2188 | -142 | 0 | 0 | 2330 | 1529.2663 | 1529.2663 | 1529.2663 | 611.3768 | 780 | 200 | 1591.3768 | 39.78% | 95% | 0% | -162.4714 | 1366.7949 | -2750 | -200 | -1583.2051 | 39.58% | 36.49% | 95% | 0% | 2330 | -142
[5 empty] | 2019-11-01 | 45 | 7318.5 | 2053 | -146 | 0 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 611.3768 | 780 | 200 | 1591.3768 | 39.78% | 95% | 0% | -167.0481 | 1157.0245 | -2750 | -200 | -1792.9755 | 44.82% | 36.49% | 95% | 0% | 2199 | -146
[5 empty] | 2019-11-01 | 46 | 7319 | 1926 | -150 | 0 | 0 | 2076 | 1131.4097 | 1131.4097 | 1131.4097 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -171.6247 | 959.785 | -2750 | -200 | -1990.215 | 49.76% | 36.48% | 95% | 0% | 2076 | -150
[5 empty] | 2019-11-01 | 47 | 7319.5 | 1791 | -154 | 0 | 0 | 1945 | 926.216 | 926.216 | 926.216 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -176.2014 | 750.0146 | -2750 | -200 | -2199.9854 | 55% | 36.47% | 95% | 0% | 1945 | -154
[5 empty] | 2019-11-01 | 48 | 7320 | 1704 | -159 | 0 | 0 | 1863 | 797.7741 | 797.7741 | 797.7741 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -181.9222 | 615.8519 | -2750 | -200 | -2334.1481 | 58.35% | 36.47% | 95% | 0% | 1863 | -159
[5 empty] | 2019-11-02 | 1 | 7320.5 | 1663 | -161 | 0 | 0 | 1824 | 736.6859 | 736.6859 | 736.6859 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -184.2105 | 552.4754 | -2750 | -200 | -2397.5246 | 59.94% | 36.46% | 95% | 0% | 1824 | -161
[5 empty] | 2019-11-02 | 2 | 7321 | 1655 | -163 | 0 | 0 | 1818 | 727.2877 | 727.2877 | 727.2877 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -186.4989 | 540.7889 | -2750 | -200 | -2409.2111 | 60.23% | 36.46% | 95% | 0% | 1818 | -163
[5 empty] | 2019-11-02 | 3 | 7321.5 | 1608 | -162 | 0 | 0 | 1770 | 652.1022 | 652.1022 | 652.1022 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -185.3547 | 466.7475 | -2750 | -200 | -2483.2525 | 62.08% | 36.45% | 95% | 0% | 1770 | -162
[5 empty] | 2019-11-02 | 4 | 7322 | 1542 | -162 | 0 | 0 | 1704 | 548.7222 | 548.7222 | 548.7222 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -185.3547 | 363.3675 | -2750 | -200 | -2586.6325 | 64.67% | 36.43% | 95% | 0% | 1704 | -162
[5 empty] | 2019-11-02 | 5 | 7322.5 | 1481 | -161 | 0 | 0 | 1642 | 451.6076 | 451.6076 | 451.6076 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -184.2105 | 267.3971 | -2750 | -200 | -2682.6029 | 67.07% | 36.43% | 95% | 0% | 1642 | -161
[5 empty] | 2019-11-02 | 6 | 7323 | 1461 | -160 | 0 | 0 | 1621 | 418.7139 | 418.7139 | 418.7139 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -183.0664 | 235.6476 | -2750 | -200 | -2714.3524 | 67.86% | 36.43% | 95% | 0% | 1621 | -160
[5 empty] | 2019-11-02 | 7 | 7323.5 | 1439 | -158 | 0 | 0 | 1597 | 381.1212 | 381.1212 | 381.1212 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -180.778 | 200.3432 | -2750 | -200 | -2749.6568 | 68.74% | 36.42% | 95% | 0% | 1597 | -158
[5 empty] | 2019-11-02 | 8 | 7324 | 1407 | -156 | 0 | 0 | 1563 | 327.8648 | 327.8648 | 327.8648 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -178.4897 | 149.3751 | -2750 | -200 | -2800.6249 | 70.02% | 36.42% | 95% | 0% | 1563 | -156
[5 empty] | 2019-11-02 | 9 | 7324.5 | 1391 | -154 | 0 | 0 | 1545 | 299.6702 | 299.6702 | 299.6702 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -176.2014 | 123.4689 | -2750 | -200 | -2826.5311 | 70.66% | 36.37% | 95% | 0% | 1545 | -154
[5 empty] | 2019-11-02 | 10 | 7325 | 1398 | -153 | 0 | 0 | 1551 | 309.0684 | 309.0684 | 309.0684 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -175.0572 | 134.0112 | -2750 | -200 | -2815.9888 | 70.4% | 36.36% | 95% | 0% | 1551 | -153
[5 empty] | 2019-11-02 | 11 | 7325.5 | 1432 | -152 | 0 | 0 | 1584 | 360.7585 | 360.7585 | 360.7585 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -173.913 | 186.8454 | -2750 | -200 | -2763.1546 | 69.08% | 36.36% | 95% | 0% | 1584 | -152
[5 empty] | 2019-11-02 | 12 | 7326 | 1495 | -150 | 0 | 0 | 1645 | 456.3067 | 456.3067 | 456.3067 | 609.8104 | 780 | 200 | 1589.8104 | 39.75% | 95% | 0% | -171.6247 | 284.682 | -2750 | -200 | -2665.318 | 66.63% | 36.36% | 95% | 0% | 1645 | -150
[5 empty] | 2019-11-02 | 13 | 7326.5 | 1617 | -148 | 0 | 0 | 1765 | 644.2704 | 644.2704 | 644.2704 | 608.244 | 780 | 200 | 1588.244 | 39.71% | 95% | 0% | -169.3364 | 474.934 | -2750 | -200 | -2475.066 | 61.88% | 36.35% | 95% | 0% | 1765 | -148
[5 empty] | 2019-11-02 | 14 | 7327 | 1733 | -145 | 0 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 608.244 | 780 | 200 | 1588.244 | 39.71% | 95% | 0% | -165.9039 | 655.3657 | -2750 | -200 | -2294.6343 | 57.37% | 36.35% | 95% | 0% | 1878 | -145
[5 empty] | 2019-11-02 | 15 | 7327.5 | 1838 | -146 | 0 | 0 | 1984 | 987.3042 | 987.3042 | 987.3042 | 608.244 | 780 | 200 | 1588.244 | 39.71% | 95% | 0% | -167.0481 | 820.2561 | -2750 | -200 | -2129.7439 | 53.24% | 36.35% | 95% | 0% | 1984 | -146
[5 empty] | 2019-11-02 | 16 | 7328 | 1932 | -163 | 0 | 0 | 2095 | 1161.1707 | 1161.1707 | 1161.1707 | 608.244 | 780 | 200 | 1588.244 | 39.71% | 95% | 0% | -186.4989 | 974.6718 | -2750 | -200 | -1975.3282 | 49.38% | 36.35% | 95% | 0% | 2095 | -163
[5 empty] | 2019-11-02 | 17 | 7328.5 | 2077 | -195 | 0 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 608.244 | 780 | 200 | 1588.244 | 39.71% | 95% | 0% | -223.1121 | 1215.305 | -2750 | -200 | -1734.695 | 43.37% | 36.35% | 95% | 0% | 2272 | -195
[5 empty] | 2019-11-02 | 18 | 7329 | 2177 | -198 | 1 | 0 | 2375 | 1599.7527 | 1599.7527 | 1599.7527 | 608.244 | 780 | 200 | 1588.244 | 39.71% | 95% | 0% | -226.5446 | 1373.2081 | -3550 | -400 | -2576.7919 | 64.42% | 36.33% | 95% | 0% | 2375 | -198
[5 empty] | 2019-11-02 | 19 | 7329.5 | 2216 | -212 | 1 | 0 | 2428 | 1682.77 | 1682.77 | 1682.77 | 608.244 | 780 | 200 | 1588.244 | 39.71% | 95% | 0% | -242.5629 | 1440.2071 | -3550 | -400 | -2509.7929 | 62.74% | 36.33% | 95% | 0% | 2428 | -212
[5 empty] | 2019-11-02 | 20 | 7330 | 2223 | -237 | 1 | 0 | 2460 | 1732.8937 | 1732.8937 | 1732.8937 | 608.244 | 780 | 200 | 1588.244 | 39.71% | 95% | 0% | -271.167 | 1461.7266 | -3550 | -400 | -2488.2734 | 62.21% | 36.31% | 95% | 0% | 2460 | -237
[5 empty] | 2019-11-02 | 21 | 7330.5 | 2268 | -249 | 1 | 0 | 2517 | 1822.1764 | 1822.1764 | 1822.1764 | 608.244 | 780 | 200 | 1588.244 | 39.71% | 95% | 0% | -284.897 | 1537.2794 | -3550 | -400 | -2412.7206 | 60.32% | 36.3% | 95% | 0% | 2517 | -249
[5 empty] | 2019-11-02 | 22 | 7331 | 2228 | -252 | 1 | 0 | 2480 | 1764.2209 | 1764.2209 | 1764.2209 | 608.244 | 780 | 200 | 1588.244 | 39.71% | 95% | 0% | -288.3295 | 1475.8914 | -3550 | -400 | -2474.1086 | 61.85% | 36.3% | 95% | 0% | 2480 | -252
[5 empty] | 2019-11-02 | 23 | 7331.5 | 2248 | -265 | 1 | 0 | 2513 | 1815.911 | 1815.911 | 1815.911 | 608.244 | 780 | 200 | 1588.244 | 39.71% | 95% | 0% | -303.2037 | 1512.7073 | -3550 | -400 | -2437.2927 | 60.93% | 36.29% | 95% | 0% | 2513 | -265
[5 empty] | 2019-11-02 | 24 | 7332 | 2240 | -267 | 1 | 0 | 2507 | 1806.5128 | 1806.5128 | 1806.5128 | 608.244 | 780 | 200 | 1588.244 | 39.71% | 95% | 0% | -305.492 | 1501.0208 | -3550 | -400 | -2448.9792 | 61.22% | 36.29% | 95% | 0% | 2507 | -267
[5 empty] | 2019-11-02 | 25 | 7332.5 | 2259 | -246 | 1 | 0 | 2505 | 1803.38 | 1803.38 | 1803.38 | 606.6777 | 780 | 200 | 1586.6777 | 39.67% | 95% | 0% | -281.4645 | 1521.9155 | -3550 | -400 | -2428.0845 | 60.7% | 36.28% | 95% | 0% | 2505 | -246
[5 empty] | 2019-11-02 | 26 | 7333 | 2250 | -234 | 1 | 0 | 2484 | 1770.4864 | 1770.4864 | 1770.4864 | 606.6777 | 780 | 200 | 1586.6777 | 39.67% | 95% | 0% | -267.7346 | 1502.7518 | -3550 | -400 | -2447.2482 | 61.18% | 36.28% | 95% | 0% | 2484 | -234
[5 empty] | 2019-11-02 | 27 | 7333.5 | 2249 | -232 | 1 | 0 | 2481 | 1765.7873 | 1765.7873 | 1765.7873 | 606.6777 | 780 | 200 | 1586.6777 | 39.67% | 95% | 0% | -265.4462 | 1500.3411 | -3550 | -400 | -2449.6589 | 61.24% | 36.25% | 95% | 0% | 2481 | -232
[5 empty] | 2019-11-02 | 28 | 7334 | 2261 | -213 | 1 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 606.6777 | 780 | 200 | 1586.6777 | 39.67% | 95% | 0% | -243.7071 | 1511.1157 | -3550 | -400 | -2438.8843 | 60.97% | 36.25% | 95% | 0% | 2474 | -213
[5 empty] | 2019-11-02 | 29 | 7334.5 | 2283 | -185 | 1 | 0 | 2468 | 1745.4246 | 1745.4246 | 1745.4246 | 606.6777 | 780 | 200 | 1586.6777 | 39.67% | 95% | 0% | -211.6705 | 1533.7541 | -3550 | -400 | -2416.2459 | 60.41% | 36.25% | 95% | 0% | 2468 | -185
[5 empty] | 2019-11-02 | 30 | 7335 | 2311 | -158 | 1 | 0 | 2469 | 1746.9909 | 1746.9909 | 1746.9909 | 606.6777 | 780 | 200 | 1586.6777 | 39.67% | 95% | 0% | -180.778 | 1566.2129 | -3550 | -400 | -2383.7871 | 59.59% | 36.24% | 95% | 0% | 2469 | -158
[5 empty] | 2019-11-02 | 31 | 7335.5 | 2358 | -150 | 1 | 0 | 2508 | 1808.0791 | 1808.0791 | 1808.0791 | 606.6777 | 780 | 200 | 1586.6777 | 39.67% | 95% | 0% | -171.6247 | 1636.4544 | -3550 | -400 | -2313.5456 | 57.84% | 36.23% | 95% | 0% | 2508 | -150
[5 empty] | 2019-11-02 | 32 | 7336 | 2412 | -134 | 1 | 0 | 2546 | 1867.601 | 1867.601 | 1867.601 | 605.1113 | 780 | 200 | 1585.1113 | 39.63% | 95% | 0% | -153.3181 | 1714.2829 | -3550 | -400 | -2235.7171 | 55.89% | 36.23% | 95% | 0% | 2546 | -134
[5 empty] | 2019-11-02 | 33 | 7336.5 | 2507 | -124 | 1 | 0 | 2631 | 2000.742 | 2000.742 | 2000.742 | 605.1113 | 780 | 200 | 1585.1113 | 39.63% | 95% | 0% | -141.8764 | 1858.8655 | -3550 | -400 | -2091.1345 | 52.28% | 36.22% | 95% | 0% | 2631 | -124
[5 empty] | 2019-11-02 | 34 | 7337 | 2668 | -122 | 1 | 0 | 2790 | 2249.7939 | 2249.7939 | 2249.7939 | 605.1113 | 780 | 200 | 1585.1113 | 39.63% | 95% | 0% | -139.5881 | 2110.2058 | -3550 | -400 | -1839.7942 | 45.99% | 36.22% | 95% | 0% | 2790 | -122
[5 empty] | 2019-11-02 | 35 | 7337.5 | 2746 | -120 | 1 | 0 | 2866 | 2368.8376 | 2368.8376 | 2368.8376 | 605.1113 | 780 | 200 | 1585.1113 | 39.63% | 95% | 0% | -137.2998 | 2231.5378 | -3550 | -400 | -1718.4622 | 42.96% | 36.22% | 95% | 0% | 2866 | -120
[5 empty] | 2019-11-02 | 36 | 7338 | 2739 | -118 | 0 | 0 | 2857 | 2354.7403 | 2354.7403 | 2354.7403 | 605.1113 | 780 | 200 | 1585.1113 | 39.63% | 95% | 0% | -135.0114 | 2219.7289 | -2750 | -200 | -730.2711 | 18.26% | 36.22% | 95% | 0% | 2857 | -118
[5 empty] | 2019-11-02 | 37 | 7338.5 | 2719 | -117 | 0 | 0 | 2836 | 2321.8467 | 2321.8467 | 2321.8467 | 605.1113 | 780 | 200 | 1585.1113 | 39.63% | 95% | 0% | -133.8673 | 2187.9794 | -2750 | -200 | -762.0206 | 19.05% | 36.21% | 95% | 0% | 2836 | -117
[5 empty] | 2019-11-02 | 38 | 7339 | 2650 | -115 | 0 | 0 | 2765 | 2210.6348 | 2210.6348 | 2210.6348 | 605.1113 | 780 | 200 | 1585.1113 | 39.63% | 95% | 0% | -131.5789 | 2079.0558 | -2750 | -200 | -870.9442 | 21.77% | 36.21% | 95% | 0% | 2765 | -115
[5 empty] | 2019-11-02 | 39 | 7339.5 | 2553 | -115 | 0 | 0 | 2668 | 2058.6974 | 2058.6974 | 2058.6974 | 605.1113 | 780 | 200 | 1585.1113 | 39.63% | 95% | 0% | -131.5789 | 1927.1185 | -2750 | -200 | -1022.8815 | 25.57% | 36.2% | 95% | 0% | 2668 | -115
[5 empty] | 2019-11-02 | 40 | 7340 | 2458 | -114 | 0 | 0 | 2572 | 1908.3265 | 1908.3265 | 1908.3265 | 605.1113 | 780 | 200 | 1585.1113 | 39.63% | 95% | 0% | -130.4348 | 1777.8917 | -2750 | -200 | -1172.1083 | 29.3% | 36.2% | 95% | 0% | 2572 | -114
[5 empty] | 2019-11-02 | 41 | 7340.5 | 2384 | -115 | 0 | 0 | 2499 | 1793.9819 | 1793.9819 | 1793.9819 | 605.1113 | 780 | 200 | 1585.1113 | 39.63% | 95% | 0% | -131.5789 | 1662.4029 | -2750 | -200 | -1287.5971 | 32.19% | 36.19% | 95% | 0% | 2499 | -115
[5 empty] | 2019-11-02 | 42 | 7341 | 2312 | -115 | 0 | 0 | 2427 | 1681.2036 | 1681.2036 | 1681.2036 | 605.1113 | 780 | 200 | 1585.1113 | 39.63% | 95% | 0% | -131.5789 | 1549.6247 | -2750 | -200 | -1400.3753 | 35.01% | 36.19% | 95% | 0% | 2427 | -115
[5 empty] | 2019-11-02 | 43 | 7341.5 | 2233 | -116 | 0 | 0 | 2349 | 1559.0272 | 1559.0272 | 1559.0272 | 603.5449 | 780 | 200 | 1583.5449 | 39.59% | 95% | 0% | -132.7231 | 1426.3041 | -2750 | -200 | -1523.6959 | 38.09% | 36.17% | 95% | 0% | 2349 | -116
[5 empty] | 2019-11-02 | 44 | 7342 | 2148 | -116 | 1 | 0 | 2264 | 1425.8862 | 1425.8862 | 1425.8862 | 603.5449 | 780 | 200 | 1583.5449 | 39.59% | 95% | 0% | -132.7231 | 1293.1631 | -3550 | -400 | -2656.8369 | 66.42% | 36.15% | 95% | 0% | 2264 | -116
[5 empty] | 2019-11-02 | 45 | 7342.5 | 2055 | -117 | 1 | 0 | 2172 | 1281.7807 | 1281.7807 | 1281.7807 | 603.5449 | 780 | 200 | 1583.5449 | 39.59% | 95% | 0% | -133.8673 | 1147.9134 | -3550 | -400 | -2802.0866 | 70.05% | 36.14% | 95% | 0% | 2172 | -117
[5 empty] | 2019-11-02 | 46 | 7343 | 1972 | -117 | 1 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 603.5449 | 780 | 200 | 1583.5449 | 39.59% | 95% | 0% | -133.8673 | 1017.9052 | -3550 | -400 | -2932.0948 | 73.3% | 36.14% | 95% | 0% | 2089 | -117
[5 empty] | 2019-11-02 | 47 | 7343.5 | 1864 | -110 | 1 | 0 | 1974 | 971.6406 | 971.6406 | 971.6406 | 603.5449 | 780 | 200 | 1583.5449 | 39.59% | 95% | 0% | -125.8581 | 845.7824 | -3550 | -400 | -3104.2176 | 77.61% | 36.14% | 95% | 0% | 1974 | -110
[5 empty] | 2019-11-02 | 48 | 7344 | 1799 | -103 | 1 | 0 | 1902 | 858.8623 | 858.8623 | 858.8623 | 603.5449 | 780 | 200 | 1583.5449 | 39.59% | 95% | 0% | -117.849 | 741.0134 | -3550 | -400 | -3208.9866 | 80.22% | 36.14% | 95% | 0% | 1902 | -103
[5 empty] | 2019-11-03 | 1 | 7344.5 | 1777 | -102 | 1 | 0 | 1879 | 822.8359 | 822.8359 | 822.8359 | 603.5449 | 780 | 200 | 1583.5449 | 39.59% | 95% | 0% | -116.7048 | 706.1311 | -3550 | -400 | -3243.8689 | 81.1% | 36.13% | 95% | 0% | 1879 | -102
[5 empty] | 2019-11-03 | 2 | 7345 | 1783 | -101 | 1 | 0 | 1884 | 830.6678 | 830.6678 | 830.6678 | 603.5449 | 780 | 200 | 1583.5449 | 39.59% | 95% | 0% | -115.5606 | 715.1071 | -3550 | -400 | -3234.8929 | 80.87% | 36.12% | 95% | 0% | 1884 | -101
[5 empty] | 2019-11-03 | 3 | 7345.5 | 1744 | -100 | 1 | 0 | 1844 | 768.0132 | 768.0132 | 768.0132 | 603.5449 | 780 | 200 | 1583.5449 | 39.59% | 95% | 0% | -114.4165 | 653.5967 | -3550 | -400 | -3296.4033 | 82.41% | 36.11% | 95% | 0% | 1844 | -100
[5 empty] | 2019-11-03 | 4 | 7346 | 1688 | -99 | 1 | 0 | 1787 | 678.7304 | 678.7304 | 678.7304 | 603.5449 | 780 | 200 | 1583.5449 | 39.59% | 95% | 0% | -113.2723 | 565.4581 | -3550 | -400 | -3384.5419 | 84.61% | 36.1% | 95% | 0% | 1787 | -99
[5 empty] | 2019-11-03 | 5 | 7346.5 | 1641 | -98 | 1 | 0 | 1739 | 603.5449 | 603.5449 | 603.5449 | 603.5449 | 780 | 200 | 1583.5449 | 39.59% | 95% | 0% | -112.1281 | 491.4168 | -3550 | -400 | -3458.5832 | 86.46% | 36.09% | 95% | 0% | 1739 | -98
[5 empty] | 2019-11-03 | 6 | 7347 | 1611 | -96 | 1 | 0 | 1707 | 553.4213 | 553.4213 | 553.4213 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -109.8398 | 443.5815 | -3550 | -400 | -3506.4185 | 87.66% | 36.09% | 95% | 0% | 1707 | -96
[5 empty] | 2019-11-03 | 7 | 7347.5 | 1575 | -95 | 1 | 0 | 1670 | 495.4658 | 495.4658 | 495.4658 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -108.6957 | 386.7701 | -3550 | -400 | -3563.2299 | 89.08% | 36.09% | 95% | 0% | 1670 | -95
[5 empty] | 2019-11-03 | 8 | 7348 | 1539 | -93 | 1 | 0 | 1632 | 435.9439 | 435.9439 | 435.9439 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -106.4073 | 329.5366 | -3550 | -400 | -3620.4634 | 90.51% | 36.08% | 95% | 0% | 1632 | -93
[5 empty] | 2019-11-03 | 9 | 7348.5 | 1515 | -95 | 1 | 0 | 1610 | 401.4839 | 401.4839 | 401.4839 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -108.6957 | 292.7883 | -3550 | -400 | -3657.2117 | 91.43% | 36.08% | 95% | 0% | 1610 | -95
[5 empty] | 2019-11-03 | 10 | 7349 | 1477 | -97 | 1 | 0 | 1574 | 345.0948 | 345.0948 | 345.0948 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -110.984 | 234.1108 | -3550 | -400 | -3715.8892 | 92.9% | 36.07% | 95% | 0% | 1574 | -97
[5 empty] | 2019-11-03 | 11 | 7349.5 | 1489 | -97 | 1 | 0 | 1586 | 363.8912 | 363.8912 | 363.8912 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -110.984 | 252.9072 | -3550 | -400 | -3697.0928 | 92.43% | 36.05% | 95% | 0% | 1586 | -97
[5 empty] | 2019-11-03 | 12 | 7350 | 1522 | -98 | 1 | 0 | 1620 | 417.1476 | 417.1476 | 417.1476 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -112.1281 | 305.0194 | -3550 | -400 | -3644.9806 | 91.12% | 36.05% | 95% | 0% | 1620 | -98
[5 empty] | 2019-11-03 | 13 | 7350.5 | 1621 | -96 | 1 | 0 | 1717 | 569.0849 | 569.0849 | 569.0849 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -109.8398 | 459.2451 | -3550 | -400 | -3490.7549 | 87.27% | 36.05% | 95% | 0% | 1717 | -96
[5 empty] | 2019-11-03 | 14 | 7351 | 1690 | -94 | 1 | 0 | 1784 | 674.0313 | 674.0313 | 674.0313 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -107.5515 | 566.4798 | -3550 | -400 | -3383.5202 | 84.59% | 36.05% | 95% | 0% | 1784 | -94
[5 empty] | 2019-11-03 | 15 | 7351.5 | 1761 | -95 | 1 | 0 | 1856 | 786.8096 | 786.8096 | 786.8096 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -108.6957 | 678.1139 | -3550 | -400 | -3271.8861 | 81.8% | 36.05% | 95% | 0% | 1856 | -95
[5 empty] | 2019-11-03 | 16 | 7352 | 1806 | -108 | 1 | 0 | 1914 | 877.6587 | 877.6587 | 877.6587 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -123.5698 | 754.0889 | -3550 | -400 | -3195.9111 | 79.9% | 36.04% | 95% | 0% | 1914 | -108
[5 empty] | 2019-11-03 | 17 | 7352.5 | 1905 | -132 | 1 | 0 | 2037 | 1070.3215 | 1070.3215 | 1070.3215 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -151.0297 | 919.2918 | -3550 | -400 | -3030.7082 | 75.77% | 36.04% | 95% | 0% | 2037 | -132
[5 empty] | 2019-11-03 | 18 | 7353 | 1952 | -176 | 1 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -201.373 | 1011.4877 | -3550 | -400 | -2938.5123 | 73.46% | 36.01% | 95% | 0% | 2128 | -176
[5 empty] | 2019-11-03 | 19 | 7353.5 | 1992 | -219 | 1 | 0 | 2211 | 1342.8689 | 1342.8689 | 1342.8689 | 601.9786 | 780 | 200 | 1581.9786 | 39.55% | 95% | 0% | -250.5721 | 1092.2968 | -3550 | -400 | -2857.7032 | 71.44% | 36.01% | 95% | 0% | 2211 | -219
[5 empty] | 2019-11-03 | 20 | 7354 | 1977 | -275 | 1 | 0 | 2252 | 1407.0899 | 1407.0899 | 1407.0899 | 600.4122 | 780 | 200 | 1580.4122 | 39.51% | 95% | 0% | -314.6453 | 1092.4446 | -3550 | -400 | -2857.5554 | 71.44% | 36% | 95% | 0% | 2252 | -275
[5 empty] | 2019-11-03 | 21 | 7354.5 | 2008 | -282 | 1 | 0 | 2290 | 1466.6117 | 1466.6117 | 1466.6117 | 600.4122 | 780 | 200 | 1580.4122 | 39.51% | 95% | 0% | -322.6545 | 1143.9572 | -3550 | -400 | -2806.0428 | 70.15% | 36% | 95% | 0% | 2290 | -282
[5 empty] | 2019-11-03 | 22 | 7355 | 2025 | -300 | 1 | 0 | 2325 | 1521.4345 | 1521.4345 | 1521.4345 | 600.4122 | 780 | 200 | 1580.4122 | 39.51% | 95% | 0% | -343.2494 | 1178.185 | -3550 | -400 | -2771.815 | 69.3% | 36% | 95% | 0% | 2325 | -300
[5 empty] | 2019-11-03 | 23 | 7355.5 | 2052 | -307 | 1 | 0 | 2359 | 1574.6908 | 1574.6908 | 1574.6908 | 600.4122 | 780 | 200 | 1580.4122 | 39.51% | 95% | 0% | -351.2586 | 1223.4323 | -3550 | -400 | -2726.5677 | 68.16% | 35.99% | 95% | 0% | 2359 | -307
[5 empty] | 2019-11-03 | 24 | 7356 | 2070 | -306 | 1 | 0 | 2376 | 1601.319 | 1601.319 | 1601.319 | 600.4122 | 780 | 200 | 1580.4122 | 39.51% | 95% | 0% | -350.1144 | 1251.2046 | -3550 | -400 | -2698.7954 | 67.47% | 35.98% | 95% | 0% | 2376 | -306
[5 empty] | 2019-11-03 | 25 | 7356.5 | 2109 | -285 | 1 | 0 | 2394 | 1629.5136 | 1629.5136 | 1629.5136 | 600.4122 | 780 | 200 | 1580.4122 | 39.51% | 95% | 0% | -326.087 | 1303.4266 | -3550 | -400 | -2646.5734 | 66.16% | 35.96% | 95% | 0% | 2394 | -285
[5 empty] | 2019-11-03 | 26 | 7357 | 2135 | -279 | 1 | 0 | 2414 | 1660.8409 | 1660.8409 | 1660.8409 | 600.4122 | 780 | 200 | 1580.4122 | 39.51% | 95% | 0% | -319.222 | 1341.6189 | -3550 | -400 | -2608.3811 | 65.21% | 35.96% | 95% | 0% | 2414 | -279
[5 empty] | 2019-11-03 | 27 | 7357.5 | 2153 | -263 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 600.4122 | 780 | 200 | 1580.4122 | 39.51% | 95% | 0% | -300.9153 | 1363.0583 | -3550 | -400 | -2586.9417 | 64.67% | 35.96% | 95% | 0% | 2416 | -263
[5 empty] | 2019-11-03 | 28 | 7358 | 2175 | -248 | 1 | 0 | 2423 | 1674.9382 | 1674.9382 | 1674.9382 | 600.4122 | 780 | 200 | 1580.4122 | 39.51% | 95% | 0% | -283.7529 | 1391.1853 | -3550 | -400 | -2558.8147 | 63.97% | 35.96% | 95% | 0% | 2423 | -248
[5 empty] | 2019-11-03 | 29 | 7358.5 | 2230 | -224 | 1 | 0 | 2454 | 1723.4955 | 1723.4955 | 1723.4955 | 600.4122 | 780 | 200 | 1580.4122 | 39.51% | 95% | 0% | -256.2929 | 1467.2026 | -3550 | -400 | -2482.7974 | 62.07% | 35.95% | 95% | 0% | 2454 | -224
[5 empty] | 2019-11-03 | 30 | 7359 | 2297 | -190 | 1 | 0 | 2487 | 1775.1855 | 1775.1855 | 1775.1855 | 600.4122 | 780 | 200 | 1580.4122 | 39.51% | 95% | 0% | -217.3913 | 1557.7942 | -3550 | -400 | -2392.2058 | 59.81% | 35.95% | 95% | 0% | 2487 | -190
[5 empty] | 2019-11-03 | 31 | 7359.5 | 2417 | -140 | 1 | 0 | 2557 | 1884.831 | 1884.831 | 1884.831 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -160.1831 | 1724.6479 | -3550 | -400 | -2225.3521 | 55.63% | 35.93% | 95% | 0% | 2557 | -140
[5 empty] | 2019-11-03 | 32 | 7360 | 2539 | -108 | 1 | 0 | 2647 | 2025.8038 | 2025.8038 | 2025.8038 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -123.5698 | 1902.234 | -3550 | -400 | -2047.766 | 51.19% | 35.93% | 95% | 0% | 2647 | -108
[5 empty] | 2019-11-03 | 33 | 7360.5 | 2683 | -85 | 1 | 0 | 2768 | 2215.3339 | 2215.3339 | 2215.3339 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -97.254 | 2118.0799 | -3550 | -400 | -1831.9201 | 45.8% | 35.93% | 95% | 0% | 2768 | -85
[5 empty] | 2019-11-03 | 34 | 7361 | 2825 | -82 | 1 | 0 | 2907 | 2433.0585 | 2433.0585 | 2433.0585 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -93.8215 | 2339.237 | -3550 | -400 | -1610.763 | 40.27% | 35.93% | 95% | 0% | 2907 | -82
[5 empty] | 2019-11-03 | 35 | 7361.5 | 2923 | -82 | 1 | 0 | 3005 | 2586.5622 | 2586.5622 | 2586.5622 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -93.8215 | 2492.7407 | -3550 | -400 | -1457.2593 | 36.43% | 35.92% | 95% | 0% | 3005 | -82
[5 empty] | 2019-11-03 | 36 | 7362 | 2905 | -83 | 0 | 0 | 2988 | 2559.934 | 2559.934 | 2559.934 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -94.9657 | 2464.9684 | -2750 | -200 | -485.0316 | 12.13% | 35.92% | 95% | 0% | 2988 | -83
[5 empty] | 2019-11-03 | 37 | 7362.5 | 2841 | -85 | 0 | 0 | 2926 | 2462.8195 | 2462.8195 | 2462.8195 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -97.254 | 2365.5655 | -2750 | -200 | -584.4345 | 14.61% | 35.91% | 95% | 0% | 2926 | -85
[5 empty] | 2019-11-03 | 38 | 7363 | 2797 | -88 | 0 | 0 | 2885 | 2398.5985 | 2398.5985 | 2398.5985 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -100.6865 | 2297.912 | -2750 | -200 | -652.088 | 16.3% | 35.91% | 95% | 0% | 2885 | -88
[5 empty] | 2019-11-03 | 39 | 7363.5 | 2719 | -88 | 0 | 0 | 2807 | 2276.4221 | 2276.4221 | 2276.4221 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -100.6865 | 2175.7356 | -2750 | -200 | -774.2644 | 19.36% | 35.9% | 95% | 0% | 2807 | -88
[5 empty] | 2019-11-03 | 40 | 7364 | 2636 | -89 | 0 | 0 | 2725 | 2147.9802 | 2147.9802 | 2147.9802 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -101.8307 | 2046.1496 | -2750 | -200 | -903.8504 | 22.6% | 35.87% | 95% | 0% | 2725 | -89
[5 empty] | 2019-11-03 | 41 | 7364.5 | 2559 | -89 | 0 | 0 | 2648 | 2027.3702 | 2027.3702 | 2027.3702 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -101.8307 | 1925.5395 | -2750 | -200 | -1024.4605 | 25.61% | 35.85% | 95% | 0% | 2648 | -89
[5 empty] | 2019-11-03 | 42 | 7365 | 2463 | -89 | 0 | 0 | 2552 | 1876.9992 | 1876.9992 | 1876.9992 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -101.8307 | 1775.1685 | -2750 | -200 | -1174.8315 | 29.37% | 35.85% | 95% | 0% | 2552 | -89
[5 empty] | 2019-11-03 | 43 | 7365.5 | 2363 | -90 | 0 | 0 | 2453 | 1721.9291 | 1721.9291 | 1721.9291 | 598.8458 | 780 | 200 | 1578.8458 | 39.47% | 95% | 0% | -102.9748 | 1618.9543 | -2750 | -200 | -1331.0457 | 33.28% | 35.84% | 95% | 0% | 2453 | -90
[5 empty] | 2019-11-03 | 44 | 7366 | 2245 | -90 | 0 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 597.2795 | 780 | 200 | 1577.2795 | 39.43% | 95% | 0% | -102.9748 | 1434.1233 | -2750 | -200 | -1515.8767 | 37.9% | 35.84% | 95% | 0% | 2335 | -90
[5 empty] | 2019-11-03 | 45 | 7366.5 | 2120 | -90 | 0 | 0 | 2210 | 1341.3026 | 1341.3026 | 1341.3026 | 597.2795 | 780 | 200 | 1577.2795 | 39.43% | 95% | 0% | -102.9748 | 1238.3277 | -2750 | -200 | -1711.6723 | 42.79% | 35.81% | 95% | 0% | 2210 | -90
[5 empty] | 2019-11-03 | 46 | 7367 | 2004 | -90 | 0 | 0 | 2094 | 1159.6043 | 1159.6043 | 1159.6043 | 597.2795 | 780 | 200 | 1577.2795 | 39.43% | 95% | 0% | -102.9748 | 1056.6295 | -2750 | -200 | -1893.3705 | 47.33% | 35.8% | 95% | 0% | 2094 | -90
[5 empty] | 2019-11-03 | 47 | 7367.5 | 1887 | -89 | 0 | 0 | 1976 | 974.7733 | 974.7733 | 974.7733 | 597.2795 | 780 | 200 | 1577.2795 | 39.43% | 95% | 0% | -101.8307 | 872.9426 | -2750 | -200 | -2077.0574 | 51.93% | 35.8% | 95% | 0% | 1976 | -89
[5 empty] | 2019-11-03 | 48 | 7368 | 1813 | -87 | 0 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 597.2795 | 780 | 200 | 1577.2795 | 39.43% | 95% | 0% | -99.5423 | 756.1873 | -2750 | -200 | -2193.8127 | 54.85% | 35.77% | 95% | 0% | 1900 | -87
[5 empty] | 2019-11-04 | 1 | 7368.5 | 1781 | -90 | 0 | 0 | 1871 | 810.305 | 810.305 | 810.305 | 597.2795 | 780 | 200 | 1577.2795 | 39.43% | 95% | 0% | -102.9748 | 707.3302 | -2750 | -200 | -2242.6698 | 56.07% | 35.76% | 95% | 0% | 1871 | -90
[5 empty] | 2019-11-04 | 2 | 7369 | 1798 | -93 | 1 | 0 | 1891 | 841.6323 | 841.6323 | 841.6323 | 597.2795 | 780 | 200 | 1577.2795 | 39.43% | 95% | 0% | -106.4073 | 735.225 | -3550 | -400 | -3214.775 | 80.37% | 35.76% | 95% | 0% | 1891 | -93
[5 empty] | 2019-11-04 | 3 | 7369.5 | 1767 | -94 | 1 | 0 | 1861 | 794.6414 | 794.6414 | 794.6414 | 597.2795 | 780 | 200 | 1577.2795 | 39.43% | 95% | 0% | -107.5515 | 687.0899 | -3550 | -400 | -3262.9101 | 81.57% | 35.73% | 95% | 0% | 1861 | -94
[5 empty] | 2019-11-04 | 4 | 7370 | 1714 | -95 | 1 | 0 | 1809 | 713.1904 | 713.1904 | 713.1904 | 595.7131 | 780 | 200 | 1575.7131 | 39.39% | 95% | 0% | -108.6957 | 604.4948 | -3550 | -400 | -3345.5052 | 83.64% | 35.72% | 95% | 0% | 1809 | -95
[5 empty] | 2019-11-04 | 5 | 7370.5 | 1682 | -95 | 1 | 0 | 1777 | 663.0668 | 663.0668 | 663.0668 | 595.7131 | 780 | 200 | 1575.7131 | 39.39% | 95% | 0% | -108.6957 | 554.3711 | -3550 | -400 | -3395.6289 | 84.89% | 35.71% | 95% | 0% | 1777 | -95
[5 empty] | 2019-11-04 | 6 | 7371 | 1656 | -96 | 1 | 0 | 1752 | 623.9077 | 623.9077 | 623.9077 | 595.7131 | 780 | 200 | 1575.7131 | 39.39% | 95% | 0% | -109.8398 | 514.0679 | -3550 | -400 | -3435.9321 | 85.9% | 35.71% | 95% | 0% | 1752 | -96
[5 empty] | 2019-11-04 | 7 | 7371.5 | 1636 | -92 | 1 | 0 | 1728 | 586.3149 | 586.3149 | 586.3149 | 595.7131 | 780 | 200 | 1575.7131 | 39.39% | 95% | 0% | -105.2632 | 481.0518 | -3550 | -400 | -3468.9482 | 86.72% | 35.7% | 95% | 0% | 1728 | -92
[5 empty] | 2019-11-04 | 8 | 7372 | 1613 | -88 | 1 | 0 | 1701 | 544.0231 | 544.0231 | 544.0231 | 595.7131 | 780 | 200 | 1575.7131 | 39.39% | 95% | 0% | -100.6865 | 443.3366 | -3550 | -400 | -3506.6634 | 87.67% | 35.69% | 95% | 0% | 1701 | -88
[5 empty] | 2019-11-04 | 9 | 7372.5 | 1624 | -88 | 1 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 595.7131 | 780 | 200 | 1575.7131 | 39.39% | 95% | 0% | -100.6865 | 460.5666 | -3550 | -400 | -3489.4334 | 87.24% | 35.68% | 95% | 0% | 1712 | -88
[5 empty] | 2019-11-04 | 10 | 7373 | 1652 | -87 | 1 | 0 | 1739 | 603.5449 | 603.5449 | 603.5449 | 595.7131 | 780 | 200 | 1575.7131 | 39.39% | 95% | 0% | -99.5423 | 504.0026 | -3550 | -400 | -3445.9974 | 86.15% | 35.68% | 95% | 0% | 1739 | -87
[5 empty] | 2019-11-04 | 11 | 7373.5 | 1731 | -86 | 1 | 0 | 1817 | 725.7214 | 725.7214 | 725.7214 | 595.7131 | 780 | 200 | 1575.7131 | 39.39% | 95% | 0% | -98.3982 | 627.3232 | -3550 | -400 | -3322.6768 | 83.07% | 35.68% | 95% | 0% | 1817 | -86
[5 empty] | 2019-11-04 | 12 | 7374 | 1857 | -85 | 1 | 0 | 1942 | 921.5169 | 921.5169 | 921.5169 | 595.7131 | 780 | 200 | 1575.7131 | 39.39% | 95% | 0% | -97.254 | 824.2629 | -3550 | -400 | -3125.7371 | 78.14% | 35.68% | 95% | 0% | 1942 | -85
[5 empty] | 2019-11-04 | 13 | 7374.5 | 2097 | -86 | 1 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 595.7131 | 780 | 200 | 1575.7131 | 39.39% | 95% | 0% | -98.3982 | 1200.6125 | -3550 | -400 | -2749.3875 | 68.73% | 35.67% | 95% | 0% | 2183 | -86
[5 empty] | 2019-11-04 | 14 | 7375 | 2330 | -86 | 1 | 0 | 2416 | 1663.9736 | 1663.9736 | 1663.9736 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -98.3982 | 1565.5754 | -3550 | -400 | -2384.4246 | 59.61% | 35.65% | 95% | 0% | 2416 | -86
[5 empty] | 2019-11-04 | 15 | 7375.5 | 2553 | -88 | 1 | 0 | 2641 | 2016.4056 | 2016.4056 | 2016.4056 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -100.6865 | 1915.7191 | -3550 | -400 | -2034.2809 | 50.86% | 35.64% | 95% | 0% | 2641 | -88
[5 empty] | 2019-11-04 | 16 | 7376 | 2655 | -103 | 1 | 0 | 2758 | 2199.6702 | 2199.6702 | 2199.6702 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -117.849 | 2081.8213 | -3550 | -400 | -1868.1787 | 46.7% | 35.64% | 95% | 0% | 2758 | -103
[5 empty] | 2019-11-04 | 17 | 7376.5 | 2692 | -131 | 1 | 0 | 2823 | 2301.4839 | 2301.4839 | 2301.4839 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -149.8856 | 2151.5983 | -3550 | -400 | -1798.4017 | 44.96% | 35.64% | 95% | 0% | 2823 | -131
[5 empty] | 2019-11-04 | 18 | 7377 | 2654 | -173 | 1 | 0 | 2827 | 2307.7494 | 2307.7494 | 2307.7494 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -197.9405 | 2109.8089 | -3550 | -400 | -1840.1911 | 46% | 35.64% | 95% | 0% | 2827 | -173
[5 empty] | 2019-11-04 | 19 | 7377.5 | 2644 | -208 | 1 | 0 | 2852 | 2346.9085 | 2346.9085 | 2346.9085 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -237.9863 | 2108.9222 | -3550 | -400 | -1841.0778 | 46.03% | 35.63% | 95% | 0% | 2852 | -208
[5 empty] | 2019-11-04 | 20 | 7378 | 2605 | -244 | 1 | 0 | 2849 | 2342.2094 | 2342.2094 | 2342.2094 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -279.1762 | 2063.0332 | -3550 | -400 | -1886.9668 | 47.17% | 35.63% | 95% | 0% | 2849 | -244
[5 empty] | 2019-11-04 | 21 | 7378.5 | 2514 | -289 | 1 | 0 | 2803 | 2270.1566 | 2270.1566 | 2270.1566 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -330.6636 | 1939.493 | -3550 | -400 | -2010.507 | 50.26% | 35.62% | 95% | 0% | 2803 | -289
[5 empty] | 2019-11-04 | 22 | 7379 | 2504 | -291 | 1 | 0 | 2795 | 2257.6257 | 2257.6257 | 2257.6257 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -332.9519 | 1924.6738 | -3550 | -400 | -2025.3262 | 50.63% | 35.62% | 95% | 0% | 2795 | -291
[5 empty] | 2019-11-04 | 23 | 7379.5 | 2506 | -288 | 1 | 0 | 2794 | 2256.0594 | 2256.0594 | 2256.0594 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -329.5195 | 1926.5399 | -3550 | -400 | -2023.4601 | 50.59% | 35.61% | 95% | 0% | 2794 | -288
[5 empty] | 2019-11-04 | 24 | 7380 | 2515 | -296 | 1 | 0 | 2811 | 2282.6876 | 2282.6876 | 2282.6876 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -338.6728 | 1944.0148 | -3550 | -400 | -2005.9852 | 50.15% | 35.61% | 95% | 0% | 2811 | -296
[5 empty] | 2019-11-04 | 25 | 7380.5 | 2521 | -307 | 1 | 0 | 2828 | 2309.3157 | 2309.3157 | 2309.3157 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -351.2586 | 1958.0572 | -3550 | -400 | -1991.9428 | 49.8% | 35.6% | 95% | 0% | 2828 | -307
[5 empty] | 2019-11-04 | 26 | 7381 | 2534 | -306 | 1 | 0 | 2840 | 2328.1121 | 2328.1121 | 2328.1121 | 594.1467 | 780 | 200 | 1574.1467 | 39.35% | 95% | 0% | -350.1144 | 1977.9977 | -3550 | -400 | -1972.0023 | 49.3% | 35.6% | 95% | 0% | 2840 | -306
[5 empty] | 2019-11-04 | 27 | 7381.5 | 2548 | -279 | 1 | 0 | 2827 | 2307.7494 | 2307.7494 | 2307.7494 | 592.5804 | 780 | 200 | 1572.5804 | 39.31% | 95% | 0% | -319.222 | 1988.5274 | -3550 | -400 | -1961.4726 | 49.04% | 35.6% | 95% | 0% | 2827 | -279
[5 empty] | 2019-11-04 | 28 | 7382 | 2565 | -253 | 1 | 0 | 2818 | 2293.6521 | 2293.6521 | 2293.6521 | 592.5804 | 780 | 200 | 1572.5804 | 39.31% | 95% | 0% | -289.4737 | 2004.1784 | -3550 | -400 | -1945.8216 | 48.65% | 35.59% | 95% | 0% | 2818 | -253
[5 empty] | 2019-11-04 | 29 | 7382.5 | 2589 | -240 | 1 | 0 | 2829 | 2310.8821 | 2310.8821 | 2310.8821 | 592.5804 | 780 | 200 | 1572.5804 | 39.31% | 95% | 0% | -274.5995 | 2036.2826 | -3550 | -400 | -1913.7174 | 47.84% | 35.59% | 95% | 0% | 2829 | -240
[5 empty] | 2019-11-04 | 30 | 7383 | 2640 | -199 | 1 | 0 | 2839 | 2326.5458 | 2326.5458 | 2326.5458 | 592.5804 | 780 | 200 | 1572.5804 | 39.31% | 95% | 0% | -227.6888 | 2098.857 | -3550 | -400 | -1851.143 | 46.28% | 35.59% | 95% | 0% | 2839 | -199
[5 empty] | 2019-11-04 | 31 | 7383.5 | 2713 | -160 | 1 | 0 | 2873 | 2379.8021 | 2379.8021 | 2379.8021 | 592.5804 | 780 | 200 | 1572.5804 | 39.31% | 95% | 0% | -183.0664 | 2196.7358 | -3550 | -400 | -1753.2642 | 43.83% | 35.59% | 95% | 0% | 2873 | -160
[5 empty] | 2019-11-04 | 32 | 7384 | 2811 | -134 | 1 | 0 | 2945 | 2492.5804 | 2492.5804 | 2492.5804 | 592.5804 | 780 | 200 | 1572.5804 | 39.31% | 95% | 0% | -153.3181 | 2339.2623 | -3550 | -400 | -1610.7377 | 40.27% | 35.57% | 95% | 0% | 2945 | -134
[5 empty] | 2019-11-04 | 33 | 7384.5 | 2932 | -120 | 1 | 0 | 3052 | 2660.1814 | 2660.1814 | 2660.1814 | 591.014 | 780 | 200 | 1571.014 | 39.28% | 95% | 0% | -137.2998 | 2522.8816 | -3550 | -400 | -1427.1184 | 35.68% | 35.56% | 95% | 0% | 3052 | -120
[5 empty] | 2019-11-04 | 34 | 7385 | 3073 | -121 | 1 | 0 | 3194 | 2882.6051 | 2882.6051 | 2882.6051 | 591.014 | 780 | 200 | 1571.014 | 39.28% | 95% | 0% | -138.4439 | 2744.1612 | -3550 | -400 | -1205.8388 | 30.15% | 35.56% | 95% | 0% | 3194 | -121
[5 empty] | 2019-11-04 | 35 | 7385.5 | 3194 | -122 | 0 | 0 | 3316 | 3073.7016 | 3073.7016 | 3073.7016 | 591.014 | 780 | 200 | 1571.014 | 39.28% | 95% | 0% | -139.5881 | 2934.1135 | -2750 | -200 | -15.8865 | 0.3972% | 35.56% | 95% | 0% | 3316 | -122
[5 empty] | 2019-11-04 | 36 | 7386 | 3194 | -124 | 0 | 0 | 3318 | 3076.8343 | 3076.8343 | 3076.8343 | 591.014 | 780 | 200 | 1571.014 | 39.28% | 95% | 0% | -141.8764 | 2934.9579 | -2750 | -200 | -15.0421 | 0.3761% | 35.55% | 95% | 0% | 3318 | -124
[5 empty] | 2019-11-04 | 37 | 7386.5 | 3151 | -125 | 0 | 0 | 3276 | 3011.047 | 3011.047 | 3011.047 | 591.014 | 780 | 200 | 1571.014 | 39.28% | 95% | 0% | -143.0206 | 2868.0264 | -2750 | -200 | -81.9736 | 2.049% | 35.55% | 95% | 0% | 3276 | -125
[5 empty] | 2019-11-04 | 38 | 7387 | 3084 | -127 | 0 | 0 | 3211 | 2909.2333 | 2909.2333 | 2909.2333 | 591.014 | 780 | 200 | 1571.014 | 39.28% | 95% | 0% | -145.3089 | 2763.9244 | -2750 | -200 | -186.0756 | 4.652% | 35.55% | 95% | 0% | 3211 | -127
[5 empty] | 2019-11-04 | 39 | 7387.5 | 2998 | -128 | 0 | 0 | 3126 | 2776.0923 | 2776.0923 | 2776.0923 | 591.014 | 780 | 200 | 1571.014 | 39.28% | 95% | 0% | -146.4531 | 2629.6392 | -2750 | -200 | -320.3608 | 8.009% | 35.54% | 95% | 0% | 3126 | -128
[5 empty] | 2019-11-04 | 40 | 7388 | 2899 | -129 | 0 | 0 | 3028 | 2622.5886 | 2622.5886 | 2622.5886 | 589.4477 | 780 | 200 | 1569.4477 | 39.24% | 95% | 0% | -147.5973 | 2474.9914 | -2750 | -200 | -475.0086 | 11.88% | 35.52% | 95% | 0% | 3028 | -129
[5 empty] | 2019-11-04 | 41 | 7388.5 | 2786 | -130 | 0 | 0 | 2916 | 2447.1558 | 2447.1558 | 2447.1558 | 589.4477 | 780 | 200 | 1569.4477 | 39.24% | 95% | 0% | -148.7414 | 2298.4144 | -2750 | -200 | -651.5856 | 16.29% | 35.5% | 95% | 0% | 2916 | -130
[5 empty] | 2019-11-04 | 42 | 7389 | 2667 | -131 | 0 | 0 | 2798 | 2262.3248 | 2262.3248 | 2262.3248 | 589.4477 | 780 | 200 | 1569.4477 | 39.24% | 95% | 0% | -149.8856 | 2112.4392 | -2750 | -200 | -837.5608 | 20.94% | 35.5% | 95% | 0% | 2798 | -131
[5 empty] | 2019-11-04 | 43 | 7389.5 | 2523 | -132 | 0 | 0 | 2655 | 2038.3347 | 2038.3347 | 2038.3347 | 589.4477 | 780 | 200 | 1569.4477 | 39.24% | 95% | 0% | -151.0297 | 1887.305 | -2750 | -200 | -1062.695 | 26.57% | 35.5% | 95% | 0% | 2655 | -132
[5 empty] | 2019-11-04 | 44 | 7390 | 2348 | -132 | 0 | 0 | 2480 | 1764.2209 | 1764.2209 | 1764.2209 | 589.4477 | 780 | 200 | 1569.4477 | 39.24% | 95% | 0% | -151.0297 | 1613.1912 | -2750 | -200 | -1336.8088 | 33.42% | 35.49% | 95% | 0% | 2480 | -132
[5 empty] | 2019-11-04 | 45 | 7390.5 | 2195 | -133 | 0 | 0 | 2328 | 1526.1336 | 1526.1336 | 1526.1336 | 589.4477 | 780 | 200 | 1569.4477 | 39.24% | 95% | 0% | -152.1739 | 1373.9596 | -2750 | -200 | -1576.0404 | 39.4% | 35.48% | 95% | 0% | 2328 | -133
[5 empty] | 2019-11-04 | 46 | 7391 | 2026 | -134 | 0 | 0 | 2160 | 1262.9843 | 1262.9843 | 1262.9843 | 589.4477 | 780 | 200 | 1569.4477 | 39.24% | 95% | 0% | -153.3181 | 1109.6663 | -2750 | -200 | -1840.3337 | 46.01% | 35.47% | 95% | 0% | 2160 | -134
[5 empty] | 2019-11-04 | 47 | 7391.5 | 1884 | -134 | 0 | 0 | 2018 | 1040.5606 | 1040.5606 | 1040.5606 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -153.3181 | 887.2425 | -2750 | -200 | -2062.7575 | 51.57% | 35.46% | 95% | 0% | 2018 | -134
[5 empty] | 2019-11-04 | 48 | 7392 | 1791 | -134 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -153.3181 | 741.5706 | -2750 | -200 | -2208.4294 | 55.21% | 35.46% | 95% | 0% | 1925 | -134
[5 empty] | 2019-11-05 | 1 | 7392.5 | 1759 | -136 | 0 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -155.6064 | 692.2914 | -2750 | -200 | -2257.7086 | 56.44% | 35.45% | 95% | 0% | 1895 | -136
[5 empty] | 2019-11-05 | 2 | 7393 | 1760 | -137 | 0 | 0 | 1897 | 851.0305 | 851.0305 | 851.0305 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -156.7506 | 694.2799 | -2750 | -200 | -2255.7201 | 56.39% | 35.44% | 95% | 0% | 1897 | -137
[5 empty] | 2019-11-05 | 3 | 7393.5 | 1720 | -138 | 0 | 0 | 1858 | 789.9423 | 789.9423 | 789.9423 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -157.8947 | 632.0476 | -2750 | -200 | -2317.9524 | 57.95% | 35.43% | 95% | 0% | 1858 | -138
[5 empty] | 2019-11-05 | 4 | 7394 | 1673 | -139 | 0 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -159.0389 | 558.8506 | -2750 | -200 | -2391.1494 | 59.78% | 35.43% | 95% | 0% | 1812 | -139
[5 empty] | 2019-11-05 | 5 | 7394.5 | 1634 | -139 | 0 | 0 | 1773 | 656.8013 | 656.8013 | 656.8013 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -159.0389 | 497.7624 | -2750 | -200 | -2452.2376 | 61.31% | 35.43% | 95% | 0% | 1773 | -139
[5 empty] | 2019-11-05 | 6 | 7395 | 1616 | -140 | 0 | 0 | 1756 | 630.1731 | 630.1731 | 630.1731 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -160.1831 | 469.9901 | -2750 | -200 | -2480.0099 | 62% | 35.42% | 95% | 0% | 1756 | -140
[5 empty] | 2019-11-05 | 7 | 7395.5 | 1588 | -139 | 0 | 0 | 1727 | 584.7486 | 584.7486 | 584.7486 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -159.0389 | 425.7097 | -2750 | -200 | -2524.2903 | 63.11% | 35.42% | 95% | 0% | 1727 | -139
[5 empty] | 2019-11-05 | 8 | 7396 | 1565 | -138 | 0 | 0 | 1703 | 547.1558 | 547.1558 | 547.1558 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -157.8947 | 389.2611 | -2750 | -200 | -2560.7389 | 64.02% | 35.42% | 95% | 0% | 1703 | -138
[5 empty] | 2019-11-05 | 9 | 7396.5 | 1572 | -138 | 0 | 0 | 1710 | 558.1204 | 558.1204 | 558.1204 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -157.8947 | 400.2256 | -2750 | -200 | -2549.7744 | 63.74% | 35.42% | 95% | 0% | 1710 | -138
[5 empty] | 2019-11-05 | 10 | 7397 | 1591 | -138 | 0 | 0 | 1729 | 587.8813 | 587.8813 | 587.8813 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -157.8947 | 429.9865 | -2750 | -200 | -2520.0135 | 63% | 35.39% | 95% | 0% | 1729 | -138
[5 empty] | 2019-11-05 | 11 | 7397.5 | 1667 | -137 | 0 | 0 | 1804 | 705.3586 | 705.3586 | 705.3586 | 587.8813 | 780 | 200 | 1567.8813 | 39.2% | 95% | 0% | -156.7506 | 548.608 | -2750 | -200 | -2401.392 | 60.03% | 35.39% | 95% | 0% | 1804 | -137
[5 empty] | 2019-11-05 | 12 | 7398 | 1774 | -136 | 0 | 0 | 1910 | 871.3932 | 871.3932 | 871.3932 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -155.6064 | 715.7868 | -2750 | -200 | -2234.2132 | 55.86% | 35.38% | 95% | 0% | 1910 | -136
[5 empty] | 2019-11-05 | 13 | 7398.5 | 2018 | -136 | 0 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -155.6064 | 1097.9797 | -2750 | -200 | -1852.0203 | 46.3% | 35.36% | 95% | 0% | 2154 | -136
[5 empty] | 2019-11-05 | 14 | 7399 | 2268 | -135 | 0 | 0 | 2403 | 1643.6109 | 1643.6109 | 1643.6109 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -154.4622 | 1489.1486 | -2750 | -200 | -1460.8514 | 36.52% | 35.36% | 95% | 0% | 2403 | -135
[5 empty] | 2019-11-05 | 15 | 7399.5 | 2509 | -135 | 0 | 0 | 2644 | 2021.1047 | 2021.1047 | 2021.1047 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -154.4622 | 1866.6425 | -2750 | -200 | -1083.3575 | 27.08% | 35.34% | 95% | 0% | 2644 | -135
[5 empty] | 2019-11-05 | 16 | 7400 | 2602 | -141 | 0 | 0 | 2743 | 2176.1748 | 2176.1748 | 2176.1748 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -161.3272 | 2014.8475 | -2750 | -200 | -935.1525 | 23.38% | 35.33% | 95% | 0% | 2743 | -141
[5 empty] | 2019-11-05 | 17 | 7400.5 | 2638 | -154 | 0 | 0 | 2792 | 2252.9266 | 2252.9266 | 2252.9266 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -176.2014 | 2076.7253 | -2750 | -200 | -873.2747 | 21.83% | 35.33% | 95% | 0% | 2792 | -154
[5 empty] | 2019-11-05 | 18 | 7401 | 2616 | -172 | 0 | 0 | 2788 | 2246.6612 | 2246.6612 | 2246.6612 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -196.7963 | 2049.8648 | -2750 | -200 | -900.1352 | 22.5% | 35.33% | 95% | 0% | 2788 | -172
[5 empty] | 2019-11-05 | 19 | 7401.5 | 2638 | -195 | 1 | 0 | 2833 | 2317.1476 | 2317.1476 | 2317.1476 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -223.1121 | 2094.0354 | -3550 | -400 | -1855.9646 | 46.4% | 35.32% | 95% | 0% | 2833 | -195
[5 empty] | 2019-11-05 | 20 | 7402 | 2613 | -213 | 1 | 0 | 2826 | 2306.183 | 2306.183 | 2306.183 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -243.7071 | 2062.4759 | -3550 | -400 | -1887.5241 | 47.19% | 35.32% | 95% | 0% | 2826 | -213
[5 empty] | 2019-11-05 | 21 | 7402.5 | 2602 | -222 | 1 | 0 | 2824 | 2303.0503 | 2303.0503 | 2303.0503 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -254.0046 | 2049.0457 | -3550 | -400 | -1900.9543 | 47.52% | 35.29% | 95% | 0% | 2824 | -222
[5 empty] | 2019-11-05 | 22 | 7403 | 2579 | -236 | 1 | 0 | 2815 | 2288.953 | 2288.953 | 2288.953 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -270.0229 | 2018.9301 | -3550 | -400 | -1931.0699 | 48.28% | 35.29% | 95% | 0% | 2815 | -236
[5 empty] | 2019-11-05 | 23 | 7403.5 | 2566 | -257 | 1 | 0 | 2823 | 2301.4839 | 2301.4839 | 2301.4839 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -294.0503 | 2007.4336 | -3550 | -400 | -1942.5664 | 48.56% | 35.29% | 95% | 0% | 2823 | -257
[5 empty] | 2019-11-05 | 24 | 7404 | 2530 | -291 | 1 | 0 | 2821 | 2298.3512 | 2298.3512 | 2298.3512 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -332.9519 | 1965.3993 | -3550 | -400 | -1984.6007 | 49.62% | 35.29% | 95% | 0% | 2821 | -291
[5 empty] | 2019-11-05 | 25 | 7404.5 | 2540 | -291 | 1 | 0 | 2831 | 2314.0148 | 2314.0148 | 2314.0148 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -332.9519 | 1981.0629 | -3550 | -400 | -1968.9371 | 49.22% | 35.28% | 95% | 0% | 2831 | -291
[5 empty] | 2019-11-05 | 26 | 7405 | 2517 | -312 | 1 | 0 | 2829 | 2310.8821 | 2310.8821 | 2310.8821 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -356.9794 | 1953.9027 | -3550 | -400 | -1996.0973 | 49.9% | 35.27% | 95% | 0% | 2829 | -312
[5 empty] | 2019-11-05 | 27 | 7405.5 | 2536 | -288 | 1 | 0 | 2824 | 2303.0503 | 2303.0503 | 2303.0503 | 586.3149 | 780 | 200 | 1566.3149 | 39.16% | 95% | 0% | -329.5195 | 1973.5308 | -3550 | -400 | -1976.4692 | 49.41% | 35.27% | 95% | 0% | 2824 | -288
[5 empty] | 2019-11-05 | 28 | 7406 | 2566 | -259 | 1 | 0 | 2825 | 2304.6167 | 2304.6167 | 2304.6167 | 584.7486 | 780 | 200 | 1564.7486 | 39.12% | 95% | 0% | -296.3387 | 2008.278 | -3550 | -400 | -1941.722 | 48.54% | 35.26% | 95% | 0% | 2825 | -259
[5 empty] | 2019-11-05 | 29 | 7406.5 | 2646 | -208 | 1 | 0 | 2854 | 2350.0412 | 2350.0412 | 2350.0412 | 584.7486 | 780 | 200 | 1564.7486 | 39.12% | 95% | 0% | -237.9863 | 2112.055 | -3550 | -400 | -1837.945 | 45.95% | 35.26% | 95% | 0% | 2854 | -208
[5 empty] | 2019-11-05 | 30 | 7407 | 2695 | -170 | 1 | 0 | 2865 | 2367.2712 | 2367.2712 | 2367.2712 | 584.7486 | 780 | 200 | 1564.7486 | 39.12% | 95% | 0% | -194.508 | 2172.7632 | -3550 | -400 | -1777.2368 | 44.43% | 35.26% | 95% | 0% | 2865 | -170
[5 empty] | 2019-11-05 | 31 | 7407.5 | 2752 | -140 | 1 | 0 | 2892 | 2409.5631 | 2409.5631 | 2409.5631 | 584.7486 | 780 | 200 | 1564.7486 | 39.12% | 95% | 0% | -160.1831 | 2249.38 | -3550 | -400 | -1700.62 | 42.52% | 35.25% | 95% | 0% | 2892 | -140
[5 empty] | 2019-11-05 | 32 | 7408 | 2849 | -113 | 1 | 0 | 2962 | 2519.2086 | 2519.2086 | 2519.2086 | 584.7486 | 780 | 200 | 1564.7486 | 39.12% | 95% | 0% | -129.2906 | 2389.918 | -3550 | -400 | -1560.082 | 39% | 35.25% | 95% | 0% | 2962 | -113
[5 empty] | 2019-11-05 | 33 | 7408.5 | 2974 | -101 | 1 | 0 | 3075 | 2696.2077 | 2696.2077 | 2696.2077 | 584.7486 | 780 | 200 | 1564.7486 | 39.12% | 95% | 0% | -115.5606 | 2580.6471 | -3550 | -400 | -1369.3529 | 34.23% | 35.24% | 95% | 0% | 3075 | -101
[5 empty] | 2019-11-05 | 34 | 7409 | 3109 | -97 | 1 | 0 | 3206 | 2901.4015 | 2901.4015 | 2901.4015 | 584.7486 | 780 | 200 | 1564.7486 | 39.12% | 95% | 0% | -110.984 | 2790.4175 | -3550 | -400 | -1159.5825 | 28.99% | 35.23% | 95% | 0% | 3206 | -97
[5 empty] | 2019-11-05 | 35 | 7409.5 | 3206 | -95 | 1 | 0 | 3301 | 3050.2061 | 3050.2061 | 3050.2061 | 584.7486 | 780 | 200 | 1564.7486 | 39.12% | 95% | 0% | -108.6957 | 2941.5104 | -3550 | -400 | -1008.4896 | 25.21% | 35.22% | 95% | 0% | 3301 | -95
[5 empty] | 2019-11-05 | 36 | 7410 | 3204 | -92 | 0 | 0 | 3296 | 3042.3743 | 3042.3743 | 3042.3743 | 584.7486 | 780 | 200 | 1564.7486 | 39.12% | 95% | 0% | -105.2632 | 2937.1111 | -2750 | -200 | -12.8889 | 0.3222% | 35.22% | 95% | 0% | 3296 | -92
[5 empty] | 2019-11-05 | 37 | 7410.5 | 3186 | -90 | 0 | 0 | 3276 | 3011.047 | 3011.047 | 3011.047 | 584.7486 | 780 | 200 | 1564.7486 | 39.12% | 95% | 0% | -102.9748 | 2908.0722 | -2750 | -200 | -41.9278 | 1.048% | 35.22% | 95% | 0% | 3276 | -90
[5 empty] | 2019-11-05 | 38 | 7411 | 3138 | -87 | 0 | 0 | 3225 | 2931.1624 | 2931.1624 | 2931.1624 | 584.7486 | 780 | 200 | 1564.7486 | 39.12% | 95% | 0% | -99.5423 | 2831.6201 | -2750 | -200 | -118.3799 | 2.959% | 35.22% | 95% | 0% | 3225 | -87
[5 empty] | 2019-11-05 | 39 | 7411.5 | 3076 | -85 | 0 | 0 | 3161 | 2830.9151 | 2830.9151 | 2830.9151 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -97.254 | 2733.6611 | -2750 | -200 | -216.3389 | 5.408% | 35.21% | 95% | 0% | 3161 | -85
[5 empty] | 2019-11-05 | 40 | 7412 | 2990 | -82 | 0 | 0 | 3072 | 2691.5087 | 2691.5087 | 2691.5087 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -93.8215 | 2597.6871 | -2750 | -200 | -352.3129 | 8.808% | 35.2% | 95% | 0% | 3072 | -82
[5 empty] | 2019-11-05 | 41 | 7412.5 | 2908 | -80 | 0 | 0 | 2988 | 2559.934 | 2559.934 | 2559.934 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -91.5332 | 2468.4009 | -2750 | -200 | -481.5991 | 12.04% | 35.2% | 95% | 0% | 2988 | -80
[5 empty] | 2019-11-05 | 42 | 7413 | 2803 | -77 | 0 | 0 | 2880 | 2390.7667 | 2390.7667 | 2390.7667 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -88.1007 | 2302.666 | -2750 | -200 | -647.334 | 16.18% | 35.19% | 95% | 0% | 2880 | -77
[5 empty] | 2019-11-05 | 43 | 7413.5 | 2683 | -74 | 0 | 0 | 2757 | 2198.1039 | 2198.1039 | 2198.1039 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -84.6682 | 2113.4357 | -2750 | -200 | -836.5643 | 20.91% | 35.17% | 95% | 0% | 2757 | -74
[5 empty] | 2019-11-05 | 44 | 7414 | 2535 | -70 | 0 | 0 | 2605 | 1960.0165 | 1960.0165 | 1960.0165 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -80.0915 | 1879.925 | -2750 | -200 | -1070.075 | 26.75% | 35.15% | 95% | 0% | 2605 | -70
[5 empty] | 2019-11-05 | 45 | 7414.5 | 2393 | -67 | 0 | 0 | 2460 | 1732.8937 | 1732.8937 | 1732.8937 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -76.659 | 1656.2346 | -2750 | -200 | -1293.7654 | 32.34% | 35.15% | 95% | 0% | 2460 | -67
[5 empty] | 2019-11-05 | 46 | 7415 | 2246 | -64 | 0 | 0 | 2310 | 1497.939 | 1497.939 | 1497.939 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -73.2265 | 1424.7124 | -2750 | -200 | -1525.2876 | 38.13% | 35.14% | 95% | 0% | 2310 | -64
[5 empty] | 2019-11-05 | 47 | 7415.5 | 2119 | -58 | 0 | 0 | 2177 | 1289.6125 | 1289.6125 | 1289.6125 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -66.3616 | 1223.251 | -2750 | -200 | -1726.749 | 43.17% | 35.14% | 95% | 0% | 2177 | -58
[5 empty] | 2019-11-05 | 48 | 7416 | 2024 | -53 | 0 | 0 | 2077 | 1132.9761 | 1132.9761 | 1132.9761 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -60.6407 | 1072.3354 | -2750 | -200 | -1877.6646 | 46.94% | 35.14% | 95% | 0% | 2077 | -53
[5 empty] | 2019-11-06 | 1 | 7416.5 | 1997 | -51 | 0 | 0 | 2048 | 1087.5515 | 1087.5515 | 1087.5515 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -58.3524 | 1029.1991 | -2750 | -200 | -1920.8009 | 48.02% | 35.13% | 95% | 0% | 2048 | -51
[5 empty] | 2019-11-06 | 2 | 7417 | 2019 | -48 | 0 | 0 | 2067 | 1117.3124 | 1117.3124 | 1117.3124 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -54.9199 | 1062.3925 | -2750 | -200 | -1887.6075 | 47.19% | 35.1% | 95% | 0% | 2067 | -48
[5 empty] | 2019-11-06 | 3 | 7417.5 | 1989 | -47 | 0 | 0 | 2036 | 1068.7552 | 1068.7552 | 1068.7552 | 583.1822 | 780 | 200 | 1563.1822 | 39.08% | 95% | 0% | -53.7757 | 1014.9794 | -2750 | -200 | -1935.0206 | 48.38% | 35.08% | 95% | 0% | 2036 | -47
[5 empty] | 2019-11-06 | 4 | 7418 | 1948 | -45 | 0 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 581.6158 | 780 | 200 | 1561.6158 | 39.04% | 95% | 0% | -51.4874 | 949.9141 | -2750 | -200 | -2000.0859 | 50% | 35.07% | 95% | 0% | 1993 | -45
[5 empty] | 2019-11-06 | 5 | 7418.5 | 1916 | -44 | 0 | 0 | 1960 | 949.7115 | 949.7115 | 949.7115 | 581.6158 | 780 | 200 | 1561.6158 | 39.04% | 95% | 0% | -50.3432 | 899.3682 | -2750 | -200 | -2050.6318 | 51.27% | 35.07% | 95% | 0% | 1960 | -44
[5 empty] | 2019-11-06 | 6 | 7419 | 1870 | -42 | 0 | 0 | 1912 | 874.526 | 874.526 | 874.526 | 581.6158 | 780 | 200 | 1561.6158 | 39.04% | 95% | 0% | -48.0549 | 826.471 | -2750 | -200 | -2123.529 | 53.09% | 35.07% | 95% | 0% | 1912 | -42
[5 empty] | 2019-11-06 | 7 | 7419.5 | 1869 | -42 | 0 | 0 | 1911 | 872.9596 | 872.9596 | 872.9596 | 581.6158 | 780 | 200 | 1561.6158 | 39.04% | 95% | 0% | -48.0549 | 824.9047 | -2750 | -200 | -2125.0953 | 53.13% | 35.07% | 95% | 0% | 1911 | -42
[5 empty] | 2019-11-06 | 8 | 7420 | 1836 | -42 | 0 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 581.6158 | 780 | 200 | 1561.6158 | 39.04% | 95% | 0% | -48.0549 | 773.2147 | -2750 | -200 | -2176.7853 | 54.42% | 35.06% | 95% | 0% | 1878 | -42
[5 empty] | 2019-11-06 | 9 | 7420.5 | 1837 | -42 | 0 | 0 | 1879 | 822.8359 | 822.8359 | 822.8359 | 581.6158 | 780 | 200 | 1561.6158 | 39.04% | 95% | 0% | -48.0549 | 774.781 | -2750 | -200 | -2175.219 | 54.38% | 35.06% | 95% | 0% | 1879 | -42
[5 empty] | 2019-11-06 | 10 | 7421 | 1876 | -42 | 0 | 0 | 1918 | 883.9242 | 883.9242 | 883.9242 | 581.6158 | 780 | 200 | 1561.6158 | 39.04% | 95% | 0% | -48.0549 | 835.8692 | -2750 | -200 | -2114.1308 | 52.85% | 35.05% | 95% | 0% | 1918 | -42
[5 empty] | 2019-11-06 | 11 | 7421.5 | 1956 | -41 | 0 | 0 | 1997 | 1007.6669 | 1007.6669 | 1007.6669 | 581.6158 | 780 | 200 | 1561.6158 | 39.04% | 95% | 0% | -46.9108 | 960.7562 | -2750 | -200 | -1989.2438 | 49.73% | 35.04% | 95% | 0% | 1997 | -41
[5 empty] | 2019-11-06 | 12 | 7422 | 2073 | -41 | 0 | 0 | 2114 | 1190.9316 | 1190.9316 | 1190.9316 | 581.6158 | 780 | 200 | 1561.6158 | 39.04% | 95% | 0% | -46.9108 | 1144.0208 | -2750 | -200 | -1805.9792 | 45.15% | 35.04% | 95% | 0% | 2114 | -41
[5 empty] | 2019-11-06 | 13 | 7422.5 | 2296 | -40 | 0 | 0 | 2336 | 1538.6645 | 1538.6645 | 1538.6645 | 581.6158 | 780 | 200 | 1561.6158 | 39.04% | 95% | 0% | -45.7666 | 1492.8979 | -2750 | -200 | -1457.1021 | 36.43% | 35.03% | 95% | 0% | 2336 | -40
[5 empty] | 2019-11-06 | 14 | 7423 | 2537 | -39 | 0 | 0 | 2576 | 1914.5919 | 1914.5919 | 1914.5919 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -44.6224 | 1869.9695 | -2750 | -200 | -1080.0305 | 27% | 35.02% | 95% | 0% | 2576 | -39
[5 empty] | 2019-11-06 | 15 | 7423.5 | 2786 | -42 | 0 | 0 | 2828 | 2309.3157 | 2309.3157 | 2309.3157 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -48.0549 | 2261.2608 | -2750 | -200 | -688.7392 | 17.22% | 35.01% | 95% | 0% | 2828 | -42
[5 empty] | 2019-11-06 | 16 | 7424 | 2837 | -72 | 0 | 0 | 2909 | 2436.1913 | 2436.1913 | 2436.1913 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -82.3799 | 2353.8114 | -2750 | -200 | -596.1886 | 14.9% | 35% | 95% | 0% | 2909 | -72
[5 empty] | 2019-11-06 | 17 | 7424.5 | 2839 | -125 | 0 | 0 | 2964 | 2522.3413 | 2522.3413 | 2522.3413 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -143.0206 | 2379.3207 | -2750 | -200 | -570.6793 | 14.27% | 35% | 95% | 0% | 2964 | -125
[5 empty] | 2019-11-06 | 18 | 7425 | 2783 | -175 | 1 | 0 | 2958 | 2512.9431 | 2512.9431 | 2512.9431 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -200.2288 | 2312.7143 | -3550 | -400 | -1637.2857 | 40.93% | 34.99% | 95% | 0% | 2958 | -175
[5 empty] | 2019-11-06 | 19 | 7425.5 | 2792 | -210 | 1 | 0 | 3002 | 2581.8631 | 2581.8631 | 2581.8631 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -240.2746 | 2341.5885 | -3550 | -400 | -1608.4115 | 40.21% | 34.98% | 95% | 0% | 3002 | -210
[5 empty] | 2019-11-06 | 20 | 7426 | 2762 | -236 | 1 | 0 | 2998 | 2575.5977 | 2575.5977 | 2575.5977 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -270.0229 | 2305.5748 | -3550 | -400 | -1644.4252 | 41.11% | 34.97% | 95% | 0% | 2998 | -236
[5 empty] | 2019-11-06 | 21 | 7426.5 | 2721 | -254 | 1 | 0 | 2975 | 2539.5713 | 2539.5713 | 2539.5713 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -290.6178 | 2248.9535 | -3550 | -400 | -1701.0465 | 42.53% | 34.97% | 95% | 0% | 2975 | -254
[5 empty] | 2019-11-06 | 22 | 7427 | 2680 | -280 | 1 | 0 | 2960 | 2516.0758 | 2516.0758 | 2516.0758 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -320.3661 | 2195.7097 | -3550 | -400 | -1754.2903 | 43.86% | 34.97% | 95% | 0% | 2960 | -280
[5 empty] | 2019-11-06 | 23 | 7427.5 | 2662 | -295 | 1 | 0 | 2957 | 2511.3768 | 2511.3768 | 2511.3768 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -337.5286 | 2173.8481 | -3550 | -400 | -1776.1519 | 44.4% | 34.95% | 95% | 0% | 2957 | -295
[5 empty] | 2019-11-06 | 24 | 7428 | 2713 | -247 | 1 | 0 | 2960 | 2516.0758 | 2516.0758 | 2516.0758 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -282.6087 | 2233.4671 | -3550 | -400 | -1716.5329 | 42.91% | 34.94% | 95% | 0% | 2960 | -247
[5 empty] | 2019-11-06 | 25 | 7428.5 | 2764 | -204 | 1 | 0 | 2968 | 2528.6068 | 2528.6068 | 2528.6068 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -233.4096 | 2295.1971 | -3550 | -400 | -1654.8029 | 41.37% | 34.93% | 95% | 0% | 2968 | -204
[5 empty] | 2019-11-06 | 26 | 7429 | 2783 | -182 | 1 | 0 | 2965 | 2523.9077 | 2523.9077 | 2523.9077 | 580.0495 | 780 | 200 | 1560.0495 | 39% | 95% | 0% | -208.238 | 2315.6697 | -3550 | -400 | -1634.3303 | 40.86% | 34.93% | 95% | 0% | 2965 | -182
[5 empty] | 2019-11-06 | 27 | 7429.5 | 2834 | -154 | 1 | 0 | 2988 | 2559.934 | 2559.934 | 2559.934 | 578.4831 | 780 | 200 | 1558.4831 | 38.96% | 95% | 0% | -176.2014 | 2383.7327 | -3550 | -400 | -1566.2673 | 39.16% | 34.92% | 95% | 0% | 2988 | -154
[5 empty] | 2019-11-06 | 28 | 7430 | 2885 | -119 | 1 | 0 | 3004 | 2584.9959 | 2584.9959 | 2584.9959 | 578.4831 | 780 | 200 | 1558.4831 | 38.96% | 95% | 0% | -136.1556 | 2448.8403 | -3550 | -400 | -1501.1597 | 37.53% | 34.92% | 95% | 0% | 3004 | -119
[5 empty] | 2019-11-06 | 29 | 7430.5 | 2907 | -102 | 1 | 0 | 3009 | 2592.8277 | 2592.8277 | 2592.8277 | 578.4831 | 780 | 200 | 1558.4831 | 38.96% | 95% | 0% | -116.7048 | 2476.1229 | -3550 | -400 | -1473.8771 | 36.85% | 34.92% | 95% | 0% | 3009 | -102
[5 empty] | 2019-11-06 | 30 | 7431 | 2938 | -81 | 1 | 0 | 3019 | 2608.4913 | 2608.4913 | 2608.4913 | 578.4831 | 780 | 200 | 1558.4831 | 38.96% | 95% | 0% | -92.6773 | 2515.814 | -3550 | -400 | -1434.186 | 35.85% | 34.91% | 95% | 0% | 3019 | -81
[5 empty] | 2019-11-06 | 31 | 7431.5 | 2986 | -65 | 1 | 0 | 3051 | 2658.615 | 2658.615 | 2658.615 | 576.9167 | 780 | 200 | 1556.9167 | 38.92% | 95% | 0% | -74.3707 | 2584.2443 | -3550 | -400 | -1365.7557 | 34.14% | 34.91% | 95% | 0% | 3051 | -65
[5 empty] | 2019-11-06 | 32 | 7432 | 3081 | -55 | 1 | 0 | 3136 | 2791.756 | 2791.756 | 2791.756 | 576.9167 | 780 | 200 | 1556.9167 | 38.92% | 95% | 0% | -62.9291 | 2728.8269 | -3550 | -400 | -1221.1731 | 30.53% | 34.9% | 95% | 0% | 3136 | -55
[5 empty] | 2019-11-06 | 33 | 7432.5 | 3179 | -52 | 1 | 0 | 3231 | 2940.5606 | 2940.5606 | 2940.5606 | 576.9167 | 780 | 200 | 1556.9167 | 38.92% | 95% | 0% | -59.4966 | 2881.064 | -3550 | -400 | -1068.936 | 26.72% | 34.9% | 95% | 0% | 3231 | -52
[5 empty] | 2019-11-06 | 34 | 7433 | 3297 | -53 | 1 | 0 | 3350 | 3126.958 | 3126.958 | 3126.958 | 576.9167 | 780 | 200 | 1556.9167 | 38.92% | 95% | 0% | -60.6407 | 3066.3172 | -3550 | -400 | -883.6828 | 22.09% | 34.89% | 95% | 0% | 3350 | -53
[5 empty] | 2019-11-06 | 35 | 7433.5 | 3338 | -56 | 1 | 0 | 3394 | 3195.878 | 3195.878 | 3195.878 | 576.9167 | 780 | 200 | 1556.9167 | 38.92% | 95% | 0% | -64.0732 | 3131.8048 | -3550 | -400 | -818.1952 | 20.45% | 34.89% | 95% | 0% | 3394 | -56
[5 empty] | 2019-11-06 | 36 | 7434 | 3319 | -59 | 0 | 0 | 3378 | 3170.8162 | 3170.8162 | 3170.8162 | 576.9167 | 780 | 200 | 1556.9167 | 38.92% | 95% | 0% | -67.5057 | 3103.3104 | -2750 | -200 | 153.3104 | -3.833% | 34.89% | 95% | 0% | 3378 | -59
[5 empty] | 2019-11-06 | 37 | 7434.5 | 3295 | -61 | 0 | 0 | 3356 | 3136.3561 | 3136.3561 | 3136.3561 | 576.9167 | 780 | 200 | 1556.9167 | 38.92% | 95% | 0% | -69.7941 | 3066.5621 | -2750 | -200 | 116.5621 | -2.914% | 34.88% | 95% | 0% | 3356 | -61
[5 empty] | 2019-11-06 | 38 | 7435 | 3273 | -64 | 0 | 0 | 3337 | 3106.5952 | 3106.5952 | 3106.5952 | 576.9167 | 780 | 200 | 1556.9167 | 38.92% | 95% | 0% | -73.2265 | 3033.3687 | -2750 | -200 | 83.3687 | -2.084% | 34.86% | 95% | 0% | 3337 | -64
[5 empty] | 2019-11-06 | 39 | 7435.5 | 3228 | -67 | 0 | 0 | 3295 | 3040.8079 | 3040.8079 | 3040.8079 | 576.9167 | 780 | 200 | 1556.9167 | 38.92% | 95% | 0% | -76.659 | 2964.1489 | -2750 | -200 | 14.1489 | -0.3537% | 34.85% | 95% | 0% | 3295 | -67
[5 empty] | 2019-11-06 | 40 | 7436 | 3147 | -70 | 0 | 0 | 3217 | 2918.6315 | 2918.6315 | 2918.6315 | 575.3504 | 780 | 200 | 1555.3504 | 38.88% | 95% | 0% | -80.0915 | 2838.54 | -2750 | -200 | -111.46 | 2.787% | 34.85% | 95% | 0% | 3217 | -70
[5 empty] | 2019-11-06 | 41 | 7436.5 | 3045 | -74 | 0 | 0 | 3119 | 2765.1278 | 2765.1278 | 2765.1278 | 575.3504 | 780 | 200 | 1555.3504 | 38.88% | 95% | 0% | -84.6682 | 2680.4596 | -2750 | -200 | -269.5404 | 6.739% | 34.84% | 95% | 0% | 3119 | -74
[5 empty] | 2019-11-06 | 42 | 7437 | 2912 | -77 | 0 | 0 | 2989 | 2561.5004 | 2561.5004 | 2561.5004 | 575.3504 | 780 | 200 | 1555.3504 | 38.88% | 95% | 0% | -88.1007 | 2473.3997 | -2750 | -200 | -476.6003 | 11.92% | 34.84% | 95% | 0% | 2989 | -77
[5 empty] | 2019-11-06 | 43 | 7437.5 | 2755 | -79 | 0 | 0 | 2834 | 2318.7139 | 2318.7139 | 2318.7139 | 575.3504 | 780 | 200 | 1555.3504 | 38.88% | 95% | 0% | -90.389 | 2228.3249 | -2750 | -200 | -721.6751 | 18.04% | 34.84% | 95% | 0% | 2834 | -79
[5 empty] | 2019-11-06 | 44 | 7438 | 2583 | -82 | 1 | 0 | 2665 | 2053.9984 | 2053.9984 | 2053.9984 | 575.3504 | 780 | 200 | 1555.3504 | 38.88% | 95% | 0% | -93.8215 | 1960.1768 | -3550 | -400 | -1989.8232 | 49.75% | 34.83% | 95% | 0% | 2665 | -82
[5 empty] | 2019-11-06 | 45 | 7438.5 | 2402 | -84 | 1 | 0 | 2486 | 1773.6191 | 1773.6191 | 1773.6191 | 575.3504 | 780 | 200 | 1555.3504 | 38.88% | 95% | 0% | -96.1098 | 1677.5093 | -3550 | -400 | -2272.4907 | 56.81% | 34.83% | 95% | 0% | 2486 | -84
[5 empty] | 2019-11-06 | 46 | 7439 | 2251 | -86 | 1 | 0 | 2337 | 1540.2308 | 1540.2308 | 1540.2308 | 575.3504 | 780 | 200 | 1555.3504 | 38.88% | 95% | 0% | -98.3982 | 1441.8327 | -3550 | -400 | -2508.1673 | 62.7% | 34.82% | 95% | 0% | 2337 | -86
[5 empty] | 2019-11-06 | 47 | 7439.5 | 2100 | -87 | 1 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 575.3504 | 780 | 200 | 1555.3504 | 38.88% | 95% | 0% | -99.5423 | 1205.7338 | -3550 | -400 | -2744.2662 | 68.61% | 34.82% | 95% | 0% | 2187 | -87
[5 empty] | 2019-11-06 | 48 | 7440 | 1996 | -89 | 1 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 575.3504 | 780 | 200 | 1555.3504 | 38.88% | 95% | 0% | -101.8307 | 1043.6763 | -3550 | -400 | -2906.3237 | 72.66% | 34.82% | 95% | 0% | 2085 | -89
[5 empty] | 2019-11-07 | 1 | 7440.5 | 1955 | -91 | 1 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 575.3504 | 780 | 200 | 1555.3504 | 38.88% | 95% | 0% | -104.119 | 980.2998 | -3550 | -400 | -2969.7002 | 74.24% | 34.8% | 95% | 0% | 2046 | -91
[5 empty] | 2019-11-07 | 2 | 7441 | 1967 | -92 | 1 | 0 | 2059 | 1104.7815 | 1104.7815 | 1104.7815 | 573.784 | 780 | 200 | 1553.784 | 38.84% | 95% | 0% | -105.2632 | 999.5184 | -3550 | -400 | -2950.4816 | 73.76% | 34.79% | 95% | 0% | 2059 | -92
[5 empty] | 2019-11-07 | 3 | 7441.5 | 1925 | -94 | 1 | 0 | 2019 | 1042.127 | 1042.127 | 1042.127 | 573.784 | 780 | 200 | 1553.784 | 38.84% | 95% | 0% | -107.5515 | 934.5755 | -3550 | -400 | -3015.4245 | 75.39% | 34.77% | 95% | 0% | 2019 | -94
[5 empty] | 2019-11-07 | 4 | 7442 | 1865 | -96 | 1 | 0 | 1961 | 951.2778 | 951.2778 | 951.2778 | 573.784 | 780 | 200 | 1553.784 | 38.84% | 95% | 0% | -109.8398 | 841.438 | -3550 | -400 | -3108.562 | 77.71% | 34.76% | 95% | 0% | 1961 | -96
[5 empty] | 2019-11-07 | 5 | 7442.5 | 1826 | -98 | 1 | 0 | 1924 | 893.3223 | 893.3223 | 893.3223 | 573.784 | 780 | 200 | 1553.784 | 38.84% | 95% | 0% | -112.1281 | 781.1942 | -3550 | -400 | -3168.8058 | 79.22% | 34.76% | 95% | 0% | 1924 | -98
[5 empty] | 2019-11-07 | 6 | 7443 | 1805 | -100 | 1 | 0 | 1905 | 863.5614 | 863.5614 | 863.5614 | 573.784 | 780 | 200 | 1553.784 | 38.84% | 95% | 0% | -114.4165 | 749.1449 | -3550 | -400 | -3200.8551 | 80.02% | 34.76% | 95% | 0% | 1905 | -100
[5 empty] | 2019-11-07 | 7 | 7443.5 | 1765 | -103 | 1 | 0 | 1868 | 805.6059 | 805.6059 | 805.6059 | 573.784 | 780 | 200 | 1553.784 | 38.84% | 95% | 0% | -117.849 | 687.757 | -3550 | -400 | -3262.243 | 81.56% | 34.76% | 95% | 0% | 1868 | -103
[5 empty] | 2019-11-07 | 8 | 7444 | 1734 | -106 | 1 | 0 | 1840 | 761.7477 | 761.7477 | 761.7477 | 572.2176 | 780 | 200 | 1552.2176 | 38.81% | 95% | 0% | -121.2815 | 640.4663 | -3550 | -400 | -3309.5337 | 82.74% | 34.75% | 95% | 0% | 1840 | -106
[5 empty] | 2019-11-07 | 9 | 7444.5 | 1715 | -108 | 1 | 0 | 1823 | 735.1195 | 735.1195 | 735.1195 | 572.2176 | 780 | 200 | 1552.2176 | 38.81% | 95% | 0% | -123.5698 | 611.5497 | -3550 | -400 | -3338.4503 | 83.46% | 34.74% | 95% | 0% | 1823 | -108
[5 empty] | 2019-11-07 | 10 | 7445 | 1733 | -110 | 1 | 0 | 1843 | 766.4468 | 766.4468 | 766.4468 | 572.2176 | 780 | 200 | 1552.2176 | 38.81% | 95% | 0% | -125.8581 | 640.5887 | -3550 | -400 | -3309.4113 | 82.74% | 34.74% | 95% | 0% | 1843 | -110
[5 empty] | 2019-11-07 | 11 | 7445.5 | 1809 | -111 | 1 | 0 | 1920 | 887.0569 | 887.0569 | 887.0569 | 572.2176 | 780 | 200 | 1552.2176 | 38.81% | 95% | 0% | -127.0023 | 760.0546 | -3550 | -400 | -3189.9454 | 79.75% | 34.72% | 95% | 0% | 1920 | -111
[5 empty] | 2019-11-07 | 12 | 7446 | 1918 | -113 | 1 | 0 | 2031 | 1060.9233 | 1060.9233 | 1060.9233 | 572.2176 | 780 | 200 | 1552.2176 | 38.81% | 95% | 0% | -129.2906 | 931.6327 | -3550 | -400 | -3018.3673 | 75.46% | 34.69% | 95% | 0% | 2031 | -113
[5 empty] | 2019-11-07 | 13 | 7446.5 | 2154 | -114 | 1 | 0 | 2268 | 1432.1517 | 1432.1517 | 1432.1517 | 570.6513 | 780 | 200 | 1550.6513 | 38.77% | 95% | 0% | -130.4348 | 1301.7169 | -3550 | -400 | -2648.2831 | 66.21% | 34.69% | 95% | 0% | 2268 | -114
[5 empty] | 2019-11-07 | 14 | 7447 | 2392 | -116 | 1 | 0 | 2508 | 1808.0791 | 1808.0791 | 1808.0791 | 570.6513 | 780 | 200 | 1550.6513 | 38.77% | 95% | 0% | -132.7231 | 1675.356 | -3550 | -400 | -2274.644 | 56.87% | 34.68% | 95% | 0% | 2508 | -116
[5 empty] | 2019-11-07 | 15 | 7447.5 | 2644 | -117 | 1 | 0 | 2761 | 2204.3693 | 2204.3693 | 2204.3693 | 570.6513 | 780 | 200 | 1550.6513 | 38.77% | 95% | 0% | -133.8673 | 2070.5021 | -3550 | -400 | -1879.4979 | 46.99% | 34.67% | 95% | 0% | 2761 | -117
[5 empty] | 2019-11-07 | 16 | 7448 | 2740 | -128 | 1 | 0 | 2868 | 2371.9703 | 2371.9703 | 2371.9703 | 570.6513 | 780 | 200 | 1550.6513 | 38.77% | 95% | 0% | -146.4531 | 2225.5172 | -3550 | -400 | -1724.4828 | 43.11% | 34.67% | 95% | 0% | 2868 | -128
[5 empty] | 2019-11-07 | 17 | 7448.5 | 2766 | -157 | 1 | 0 | 2923 | 2458.1204 | 2458.1204 | 2458.1204 | 570.6513 | 780 | 200 | 1550.6513 | 38.77% | 95% | 0% | -179.6339 | 2278.4865 | -3550 | -400 | -1671.5135 | 41.79% | 34.66% | 95% | 0% | 2923 | -157
[5 empty] | 2019-11-07 | 18 | 7449 | 2703 | -201 | 1 | 0 | 2904 | 2428.3594 | 2428.3594 | 2428.3594 | 570.6513 | 780 | 200 | 1550.6513 | 38.77% | 95% | 0% | -229.9771 | 2198.3823 | -3550 | -400 | -1751.6177 | 43.79% | 34.65% | 95% | 0% | 2904 | -201
[5 empty] | 2019-11-07 | 19 | 7449.5 | 2679 | -241 | 1 | 0 | 2920 | 2453.4213 | 2453.4213 | 2453.4213 | 570.6513 | 780 | 200 | 1550.6513 | 38.77% | 95% | 0% | -275.7437 | 2177.6776 | -3550 | -400 | -1772.3224 | 44.31% | 34.65% | 95% | 0% | 2920 | -241
[5 empty] | 2019-11-07 | 20 | 7450 | 2628 | -279 | 1 | 0 | 2907 | 2433.0585 | 2433.0585 | 2433.0585 | 570.6513 | 780 | 200 | 1550.6513 | 38.77% | 95% | 0% | -319.222 | 2113.8366 | -3550 | -400 | -1836.1634 | 45.9% | 34.63% | 95% | 0% | 2907 | -279
[5 empty] | 2019-11-07 | 21 | 7450.5 | 2552 | -328 | 1 | 0 | 2880 | 2390.7667 | 2390.7667 | 2390.7667 | 570.6513 | 780 | 200 | 1550.6513 | 38.77% | 95% | 0% | -375.286 | 2015.4807 | -3550 | -400 | -1934.5193 | 48.36% | 34.62% | 95% | 0% | 2880 | -328
[5 empty] | 2019-11-07 | 22 | 7451 | 2493 | -352 | 1 | 0 | 2845 | 2335.9439 | 2335.9439 | 2335.9439 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -402.746 | 1933.1979 | -3550 | -400 | -2016.8021 | 50.42% | 34.62% | 95% | 0% | 2845 | -352
[5 empty] | 2019-11-07 | 23 | 7451.5 | 2463 | -363 | 1 | 0 | 2826 | 2306.183 | 2306.183 | 2306.183 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -415.3318 | 1890.8512 | -3550 | -400 | -2059.1488 | 51.48% | 34.62% | 95% | 0% | 2826 | -363
[5 empty] | 2019-11-07 | 24 | 7452 | 2483 | -348 | 1 | 0 | 2831 | 2314.0148 | 2314.0148 | 2314.0148 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -398.1693 | 1915.8455 | -3550 | -400 | -2034.1545 | 50.85% | 34.62% | 95% | 0% | 2831 | -348
[5 empty] | 2019-11-07 | 25 | 7452.5 | 2501 | -339 | 1 | 0 | 2840 | 2328.1121 | 2328.1121 | 2328.1121 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -387.8719 | 1940.2403 | -3550 | -400 | -2009.7597 | 50.24% | 34.58% | 95% | 0% | 2840 | -339
[5 empty] | 2019-11-07 | 26 | 7453 | 2511 | -335 | 1 | 0 | 2846 | 2337.5103 | 2337.5103 | 2337.5103 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -383.2952 | 1954.2151 | -3550 | -400 | -1995.7849 | 49.89% | 34.58% | 95% | 0% | 2846 | -335
[5 empty] | 2019-11-07 | 27 | 7453.5 | 2519 | -325 | 1 | 0 | 2844 | 2334.3776 | 2334.3776 | 2334.3776 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -371.8535 | 1962.524 | -3550 | -400 | -1987.476 | 49.69% | 34.57% | 95% | 0% | 2844 | -325
[5 empty] | 2019-11-07 | 28 | 7454 | 2539 | -304 | 1 | 0 | 2843 | 2332.8112 | 2332.8112 | 2332.8112 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -347.8261 | 1984.9851 | -3550 | -400 | -1965.0149 | 49.13% | 34.57% | 95% | 0% | 2843 | -304
[5 empty] | 2019-11-07 | 29 | 7454.5 | 2586 | -277 | 1 | 0 | 2863 | 2364.1385 | 2364.1385 | 2364.1385 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -316.9336 | 2047.2049 | -3550 | -400 | -1902.7951 | 47.57% | 34.54% | 95% | 0% | 2863 | -277
[5 empty] | 2019-11-07 | 30 | 7455 | 2609 | -253 | 1 | 0 | 2862 | 2362.5721 | 2362.5721 | 2362.5721 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -289.4737 | 2073.0985 | -3550 | -400 | -1876.9015 | 46.92% | 34.52% | 95% | 0% | 2862 | -253
[5 empty] | 2019-11-07 | 31 | 7455.5 | 2698 | -211 | 1 | 0 | 2909 | 2436.1913 | 2436.1913 | 2436.1913 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -241.4188 | 2194.7725 | -3550 | -400 | -1755.2275 | 43.88% | 34.48% | 95% | 0% | 2909 | -211
[5 empty] | 2019-11-07 | 32 | 7456 | 2839 | -173 | 1 | 0 | 3012 | 2597.5268 | 2597.5268 | 2597.5268 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -197.9405 | 2399.5863 | -3550 | -400 | -1550.4137 | 38.76% | 34.48% | 95% | 0% | 3012 | -173
[5 empty] | 2019-11-07 | 33 | 7456.5 | 2980 | -151 | 1 | 0 | 3131 | 2783.9242 | 2783.9242 | 2783.9242 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -172.7689 | 2611.1553 | -3550 | -400 | -1338.8447 | 33.47% | 34.46% | 95% | 0% | 3131 | -151
[5 empty] | 2019-11-07 | 34 | 7457 | 3141 | -146 | 1 | 0 | 3287 | 3028.277 | 3028.277 | 3028.277 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -167.0481 | 2861.2289 | -3550 | -400 | -1088.7711 | 27.22% | 34.46% | 95% | 0% | 3287 | -146
[5 empty] | 2019-11-07 | 35 | 7457.5 | 3211 | -146 | 1 | 0 | 3357 | 3137.9225 | 3137.9225 | 3137.9225 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -167.0481 | 2970.8745 | -3550 | -400 | -979.1255 | 24.48% | 34.45% | 95% | 0% | 3357 | -146
[5 empty] | 2019-11-07 | 36 | 7458 | 3204 | -145 | 0 | 0 | 3349 | 3125.3916 | 3125.3916 | 3125.3916 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -165.9039 | 2959.4877 | -2750 | -200 | 9.4877 | -0.2372% | 34.44% | 95% | 0% | 3349 | -145
[5 empty] | 2019-11-07 | 37 | 7458.5 | 3168 | -146 | 0 | 0 | 3314 | 3070.5688 | 3070.5688 | 3070.5688 | 569.0849 | 780 | 200 | 1549.0849 | 38.73% | 95% | 0% | -167.0481 | 2903.5208 | -2750 | -200 | -46.4792 | 1.162% | 34.43% | 95% | 0% | 3314 | -146
[5 empty] | 2019-11-07 | 38 | 7459 | 3114 | -146 | 0 | 0 | 3260 | 2985.9852 | 2985.9852 | 2985.9852 | 567.5185 | 780 | 200 | 1547.5185 | 38.69% | 95% | 0% | -167.0481 | 2818.9371 | -2750 | -200 | -131.0629 | 3.277% | 34.43% | 95% | 0% | 3260 | -146
[5 empty] | 2019-11-07 | 39 | 7459.5 | 3040 | -147 | 0 | 0 | 3187 | 2871.6406 | 2871.6406 | 2871.6406 | 567.5185 | 780 | 200 | 1547.5185 | 38.69% | 95% | 0% | -168.1922 | 2703.4483 | -2750 | -200 | -246.5517 | 6.164% | 34.42% | 95% | 0% | 3187 | -147
[5 empty] | 2019-11-07 | 40 | 7460 | 2944 | -148 | 0 | 0 | 3092 | 2722.8359 | 2722.8359 | 2722.8359 | 567.5185 | 780 | 200 | 1547.5185 | 38.69% | 95% | 0% | -169.3364 | 2553.4996 | -2750 | -200 | -396.5004 | 9.913% | 34.42% | 95% | 0% | 3092 | -148
[5 empty] | 2019-11-07 | 41 | 7460.5 | 2846 | -150 | 0 | 0 | 2996 | 2572.465 | 2572.465 | 2572.465 | 567.5185 | 780 | 200 | 1547.5185 | 38.69% | 95% | 0% | -171.6247 | 2400.8402 | -2750 | -200 | -549.1598 | 13.73% | 34.42% | 95% | 0% | 2996 | -150
[5 empty] | 2019-11-07 | 42 | 7461 | 2715 | -151 | 0 | 0 | 2866 | 2368.8376 | 2368.8376 | 2368.8376 | 567.5185 | 780 | 200 | 1547.5185 | 38.69% | 95% | 0% | -172.7689 | 2196.0687 | -2750 | -200 | -753.9313 | 18.85% | 34.41% | 95% | 0% | 2866 | -151
[5 empty] | 2019-11-07 | 43 | 7461.5 | 2591 | -152 | 0 | 0 | 2743 | 2176.1748 | 2176.1748 | 2176.1748 | 567.5185 | 780 | 200 | 1547.5185 | 38.69% | 95% | 0% | -173.913 | 2002.2617 | -2750 | -200 | -947.7383 | 23.69% | 34.4% | 95% | 0% | 2743 | -152
[5 empty] | 2019-11-07 | 44 | 7462 | 2419 | -154 | 0 | 0 | 2573 | 1909.8928 | 1909.8928 | 1909.8928 | 567.5185 | 780 | 200 | 1547.5185 | 38.69% | 95% | 0% | -176.2014 | 1733.6915 | -2750 | -200 | -1216.3085 | 30.41% | 34.39% | 95% | 0% | 2573 | -154
[5 empty] | 2019-11-07 | 45 | 7462.5 | 2248 | -153 | 0 | 0 | 2401 | 1640.4782 | 1640.4782 | 1640.4782 | 565.9522 | 780 | 200 | 1545.9522 | 38.65% | 95% | 0% | -175.0572 | 1465.4209 | -2750 | -200 | -1484.5791 | 37.11% | 34.39% | 95% | 0% | 2401 | -153
[5 empty] | 2019-11-07 | 46 | 7463 | 2104 | -153 | 0 | 0 | 2257 | 1414.9217 | 1414.9217 | 1414.9217 | 565.9522 | 780 | 200 | 1545.9522 | 38.65% | 95% | 0% | -175.0572 | 1239.8645 | -2750 | -200 | -1710.1355 | 42.75% | 34.39% | 95% | 0% | 2257 | -153
[5 empty] | 2019-11-07 | 47 | 7463.5 | 1968 | -149 | 0 | 0 | 2117 | 1195.6307 | 1195.6307 | 1195.6307 | 565.9522 | 780 | 200 | 1545.9522 | 38.65% | 95% | 0% | -170.4805 | 1025.1501 | -2750 | -200 | -1924.8499 | 48.12% | 34.38% | 95% | 0% | 2117 | -149
[5 empty] | 2019-11-07 | 48 | 7464 | 1869 | -145 | 0 | 0 | 2014 | 1034.2951 | 1034.2951 | 1034.2951 | 565.9522 | 780 | 200 | 1545.9522 | 38.65% | 95% | 0% | -165.9039 | 868.3912 | -2750 | -200 | -2081.6088 | 52.04% | 34.37% | 95% | 0% | 2014 | -145
[5 empty] | 2019-11-08 | 1 | 7464.5 | 1846 | -143 | 0 | 0 | 1989 | 995.136 | 995.136 | 995.136 | 565.9522 | 780 | 200 | 1545.9522 | 38.65% | 95% | 0% | -163.6156 | 831.5205 | -2750 | -200 | -2118.4795 | 52.96% | 34.35% | 95% | 0% | 1989 | -143
[5 empty] | 2019-11-08 | 2 | 7465 | 1862 | -140 | 0 | 0 | 2002 | 1015.4988 | 1015.4988 | 1015.4988 | 565.9522 | 780 | 200 | 1545.9522 | 38.65% | 95% | 0% | -160.1831 | 855.3157 | -2750 | -200 | -2094.6843 | 52.37% | 34.35% | 95% | 0% | 2002 | -140
[5 empty] | 2019-11-08 | 3 | 7465.5 | 1827 | -137 | 0 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 565.9522 | 780 | 200 | 1545.9522 | 38.65% | 95% | 0% | -156.7506 | 799.2263 | -2750 | -200 | -2150.7737 | 53.77% | 34.35% | 95% | 0% | 1964 | -137
[5 empty] | 2019-11-08 | 4 | 7466 | 1791 | -134 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 564.3858 | 780 | 200 | 1544.3858 | 38.61% | 95% | 0% | -153.3181 | 741.5706 | -2750 | -200 | -2208.4294 | 55.21% | 34.35% | 95% | 0% | 1925 | -134
[5 empty] | 2019-11-08 | 5 | 7466.5 | 1748 | -131 | 0 | 0 | 1879 | 822.8359 | 822.8359 | 822.8359 | 564.3858 | 780 | 200 | 1544.3858 | 38.61% | 95% | 0% | -149.8856 | 672.9504 | -2750 | -200 | -2277.0496 | 56.93% | 34.33% | 95% | 0% | 1879 | -131
[5 empty] | 2019-11-08 | 6 | 7467 | 1742 | -129 | 0 | 0 | 1871 | 810.305 | 810.305 | 810.305 | 564.3858 | 780 | 200 | 1544.3858 | 38.61% | 95% | 0% | -147.5973 | 662.7078 | -2750 | -200 | -2287.2922 | 57.18% | 34.33% | 95% | 0% | 1871 | -129
[5 empty] | 2019-11-08 | 7 | 7467.5 | 1713 | -125 | 0 | 0 | 1838 | 758.615 | 758.615 | 758.615 | 564.3858 | 780 | 200 | 1544.3858 | 38.61% | 95% | 0% | -143.0206 | 615.5944 | -2750 | -200 | -2334.4056 | 58.36% | 34.31% | 95% | 0% | 1838 | -125
[5 empty] | 2019-11-08 | 8 | 7468 | 1691 | -121 | 0 | 0 | 1812 | 717.8895 | 717.8895 | 717.8895 | 564.3858 | 780 | 200 | 1544.3858 | 38.61% | 95% | 0% | -138.4439 | 579.4456 | -2750 | -200 | -2370.5544 | 59.26% | 34.31% | 95% | 0% | 1812 | -121
[5 empty] | 2019-11-08 | 9 | 7468.5 | 1699 | -119 | 0 | 0 | 1818 | 727.2877 | 727.2877 | 727.2877 | 564.3858 | 780 | 200 | 1544.3858 | 38.61% | 95% | 0% | -136.1556 | 591.1321 | -2750 | -200 | -2358.8679 | 58.97% | 34.3% | 95% | 0% | 1818 | -119
[5 empty] | 2019-11-08 | 10 | 7469 | 1735 | -117 | 0 | 0 | 1852 | 780.5441 | 780.5441 | 780.5441 | 564.3858 | 780 | 200 | 1544.3858 | 38.61% | 95% | 0% | -133.8673 | 646.6768 | -2750 | -200 | -2303.3232 | 57.58% | 34.3% | 95% | 0% | 1852 | -117
[5 empty] | 2019-11-08 | 11 | 7469.5 | 1812 | -113 | 0 | 0 | 1925 | 894.8887 | 894.8887 | 894.8887 | 564.3858 | 780 | 200 | 1544.3858 | 38.61% | 95% | 0% | -129.2906 | 765.5981 | -2750 | -200 | -2184.4019 | 54.61% | 34.3% | 95% | 0% | 1925 | -113
[5 empty] | 2019-11-08 | 12 | 7470 | 1921 | -110 | 0 | 0 | 2031 | 1060.9233 | 1060.9233 | 1060.9233 | 564.3858 | 780 | 200 | 1544.3858 | 38.61% | 95% | 0% | -125.8581 | 935.0652 | -2750 | -200 | -2014.9348 | 50.37% | 34.29% | 95% | 0% | 2031 | -110
[5 empty] | 2019-11-08 | 13 | 7470.5 | 2146 | -108 | 0 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 562.8195 | 780 | 200 | 1542.8195 | 38.57% | 95% | 0% | -123.5698 | 1286.6528 | -2750 | -200 | -1663.3472 | 41.58% | 34.28% | 95% | 0% | 2254 | -108
[5 empty] | 2019-11-08 | 14 | 7471 | 2413 | -106 | 0 | 0 | 2519 | 1825.3092 | 1825.3092 | 1825.3092 | 562.8195 | 780 | 200 | 1542.8195 | 38.57% | 95% | 0% | -121.2815 | 1704.0277 | -2750 | -200 | -1245.9723 | 31.15% | 34.28% | 95% | 0% | 2519 | -106
[5 empty] | 2019-11-08 | 15 | 7471.5 | 2668 | -104 | 0 | 0 | 2772 | 2221.5993 | 2221.5993 | 2221.5993 | 562.8195 | 780 | 200 | 1542.8195 | 38.57% | 95% | 0% | -118.9931 | 2102.6062 | -2750 | -200 | -847.3938 | 21.18% | 34.27% | 95% | 0% | 2772 | -104
[5 empty] | 2019-11-08 | 16 | 7472 | 2771 | -114 | 0 | 0 | 2885 | 2398.5985 | 2398.5985 | 2398.5985 | 562.8195 | 780 | 200 | 1542.8195 | 38.57% | 95% | 0% | -130.4348 | 2268.1637 | -2750 | -200 | -681.8363 | 17.05% | 34.26% | 95% | 0% | 2885 | -114
[5 empty] | 2019-11-08 | 17 | 7472.5 | 2817 | -148 | 0 | 0 | 2965 | 2523.9077 | 2523.9077 | 2523.9077 | 562.8195 | 780 | 200 | 1542.8195 | 38.57% | 95% | 0% | -169.3364 | 2354.5713 | -2750 | -200 | -595.4287 | 14.89% | 34.25% | 95% | 0% | 2965 | -148
[5 empty] | 2019-11-08 | 18 | 7473 | 2750 | -188 | 1 | 0 | 2938 | 2481.6158 | 2481.6158 | 2481.6158 | 562.8195 | 780 | 200 | 1542.8195 | 38.57% | 95% | 0% | -215.103 | 2266.5129 | -3550 | -400 | -1683.4871 | 42.09% | 34.23% | 95% | 0% | 2938 | -188
[5 empty] | 2019-11-08 | 19 | 7473.5 | 2761 | -228 | 1 | 0 | 2989 | 2561.5004 | 2561.5004 | 2561.5004 | 562.8195 | 780 | 200 | 1542.8195 | 38.57% | 95% | 0% | -260.8696 | 2300.6308 | -3550 | -400 | -1649.3692 | 41.23% | 34.23% | 95% | 0% | 2989 | -228
[5 empty] | 2019-11-08 | 20 | 7474 | 2706 | -270 | 1 | 0 | 2976 | 2541.1377 | 2541.1377 | 2541.1377 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -308.9245 | 2232.2132 | -3550 | -400 | -1717.7868 | 42.94% | 34.23% | 95% | 0% | 2976 | -270
[5 empty] | 2019-11-08 | 21 | 7474.5 | 2625 | -302 | 1 | 0 | 2927 | 2464.3858 | 2464.3858 | 2464.3858 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -345.5378 | 2118.8481 | -3550 | -400 | -1831.1519 | 45.78% | 34.23% | 95% | 0% | 2927 | -302
[5 empty] | 2019-11-08 | 22 | 7475 | 2529 | -354 | 1 | 0 | 2883 | 2395.4658 | 2395.4658 | 2395.4658 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -405.0343 | 1990.4315 | -3550 | -400 | -1959.5685 | 48.99% | 34.22% | 95% | 0% | 2883 | -354
[5 empty] | 2019-11-08 | 23 | 7475.5 | 2483 | -367 | 1 | 0 | 2850 | 2343.7758 | 2343.7758 | 2343.7758 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -419.9085 | 1923.8673 | -3550 | -400 | -2026.1327 | 50.65% | 34.21% | 95% | 0% | 2850 | -367
[5 empty] | 2019-11-08 | 24 | 7476 | 2501 | -340 | 1 | 0 | 2841 | 2329.6785 | 2329.6785 | 2329.6785 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -389.016 | 1940.6625 | -3550 | -400 | -2009.3375 | 50.23% | 34.21% | 95% | 0% | 2841 | -340
[5 empty] | 2019-11-08 | 25 | 7476.5 | 2557 | -312 | 1 | 0 | 2869 | 2373.5367 | 2373.5367 | 2373.5367 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -356.9794 | 2016.5573 | -3550 | -400 | -1933.4427 | 48.34% | 34.19% | 95% | 0% | 2869 | -312
[5 empty] | 2019-11-08 | 26 | 7477 | 2610 | -282 | 1 | 0 | 2892 | 2409.5631 | 2409.5631 | 2409.5631 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -322.6545 | 2086.9086 | -3550 | -400 | -1863.0914 | 46.58% | 34.19% | 95% | 0% | 2892 | -282
[5 empty] | 2019-11-08 | 27 | 7477.5 | 2653 | -261 | 1 | 0 | 2914 | 2444.0231 | 2444.0231 | 2444.0231 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -298.627 | 2145.3961 | -3550 | -400 | -1804.6039 | 45.12% | 34.16% | 95% | 0% | 2914 | -261
[5 empty] | 2019-11-08 | 28 | 7478 | 2672 | -229 | 1 | 0 | 2901 | 2423.6603 | 2423.6603 | 2423.6603 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -262.0137 | 2161.6466 | -3550 | -400 | -1788.3534 | 44.71% | 34.15% | 95% | 0% | 2901 | -229
[5 empty] | 2019-11-08 | 29 | 7478.5 | 2714 | -209 | 1 | 0 | 2923 | 2458.1204 | 2458.1204 | 2458.1204 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -239.1304 | 2218.9899 | -3550 | -400 | -1731.0101 | 43.28% | 34.15% | 95% | 0% | 2923 | -209
[5 empty] | 2019-11-08 | 30 | 7479 | 2753 | -176 | 1 | 0 | 2929 | 2467.5185 | 2467.5185 | 2467.5185 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -201.373 | 2266.1456 | -3550 | -400 | -1683.8544 | 42.1% | 34.15% | 95% | 0% | 2929 | -176
[5 empty] | 2019-11-08 | 31 | 7479.5 | 2841 | -130 | 1 | 0 | 2971 | 2533.3059 | 2533.3059 | 2533.3059 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -148.7414 | 2384.5644 | -3550 | -400 | -1565.4356 | 39.14% | 34.15% | 95% | 0% | 2971 | -130
[5 empty] | 2019-11-08 | 32 | 7480 | 2956 | -91 | 1 | 0 | 3047 | 2652.3495 | 2652.3495 | 2652.3495 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -104.119 | 2548.2306 | -3550 | -400 | -1401.7694 | 35.04% | 34.14% | 95% | 0% | 3047 | -91
[5 empty] | 2019-11-08 | 33 | 7480.5 | 3071 | -72 | 1 | 0 | 3143 | 2802.7205 | 2802.7205 | 2802.7205 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -82.3799 | 2720.3407 | -3550 | -400 | -1229.6593 | 30.74% | 34.14% | 95% | 0% | 3143 | -72
[5 empty] | 2019-11-08 | 34 | 7481 | 3207 | -68 | 1 | 0 | 3275 | 3009.4806 | 3009.4806 | 3009.4806 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -77.8032 | 2931.6774 | -3550 | -400 | -1018.3226 | 25.46% | 34.13% | 95% | 0% | 3275 | -68
[5 empty] | 2019-11-08 | 35 | 7481.5 | 3283 | -68 | 1 | 0 | 3351 | 3128.5243 | 3128.5243 | 3128.5243 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -77.8032 | 3050.7211 | -3550 | -400 | -899.2789 | 22.48% | 34.13% | 95% | 0% | 3351 | -68
[5 empty] | 2019-11-08 | 36 | 7482 | 3272 | -67 | 0 | 0 | 3339 | 3109.7279 | 3109.7279 | 3109.7279 | 561.2531 | 780 | 200 | 1541.2531 | 38.53% | 95% | 0% | -76.659 | 3033.0689 | -2750 | -200 | 83.0689 | -2.077% | 34.13% | 95% | 0% | 3339 | -67
[5 empty] | 2019-11-08 | 37 | 7482.5 | 3239 | -66 | 0 | 0 | 3305 | 3056.4716 | 3056.4716 | 3056.4716 | 559.6867 | 780 | 200 | 1539.6867 | 38.49% | 95% | 0% | -75.5149 | 2980.9567 | -2750 | -200 | 30.9567 | -0.7739% | 34.1% | 95% | 0% | 3305 | -66
[5 empty] | 2019-11-08 | 38 | 7483 | 3173 | -65 | 0 | 0 | 3238 | 2951.5251 | 2951.5251 | 2951.5251 | 559.6867 | 780 | 200 | 1539.6867 | 38.49% | 95% | 0% | -74.3707 | 2877.1544 | -2750 | -200 | -72.8456 | 1.821% | 34.1% | 95% | 0% | 3238 | -65
[5 empty] | 2019-11-08 | 39 | 7483.5 | 3146 | -64 | 0 | 0 | 3210 | 2907.6669 | 2907.6669 | 2907.6669 | 559.6867 | 780 | 200 | 1539.6867 | 38.49% | 95% | 0% | -73.2265 | 2834.4404 | -2750 | -200 | -115.5596 | 2.889% | 34.1% | 95% | 0% | 3210 | -64
[5 empty] | 2019-11-08 | 40 | 7484 | 3059 | -63 | 0 | 0 | 3122 | 2769.8269 | 2769.8269 | 2769.8269 | 559.6867 | 780 | 200 | 1539.6867 | 38.49% | 95% | 0% | -72.0824 | 2697.7445 | -2750 | -200 | -252.2555 | 6.306% | 34.09% | 95% | 0% | 3122 | -63
[5 empty] | 2019-11-08 | 41 | 7484.5 | 2952 | -63 | 0 | 0 | 3015 | 2602.2259 | 2602.2259 | 2602.2259 | 559.6867 | 780 | 200 | 1539.6867 | 38.49% | 95% | 0% | -72.0824 | 2530.1435 | -2750 | -200 | -419.8565 | 10.5% | 34.09% | 95% | 0% | 3015 | -63
[5 empty] | 2019-11-08 | 42 | 7485 | 2841 | -62 | 0 | 0 | 2903 | 2426.7931 | 2426.7931 | 2426.7931 | 559.6867 | 780 | 200 | 1539.6867 | 38.49% | 95% | 0% | -70.9382 | 2355.8549 | -2750 | -200 | -594.1451 | 14.85% | 34.09% | 95% | 0% | 2903 | -62
[5 empty] | 2019-11-08 | 43 | 7485.5 | 2738 | -62 | 0 | 0 | 2800 | 2265.4575 | 2265.4575 | 2265.4575 | 559.6867 | 780 | 200 | 1539.6867 | 38.49% | 95% | 0% | -70.9382 | 2194.5193 | -2750 | -200 | -755.4807 | 18.89% | 34.08% | 95% | 0% | 2800 | -62
[5 empty] | 2019-11-08 | 44 | 7486 | 2616 | -62 | 0 | 0 | 2678 | 2074.3611 | 2074.3611 | 2074.3611 | 559.6867 | 780 | 200 | 1539.6867 | 38.49% | 95% | 0% | -70.9382 | 2003.4229 | -2750 | -200 | -946.5771 | 23.66% | 34.08% | 95% | 0% | 2678 | -62
[5 empty] | 2019-11-08 | 45 | 7486.5 | 2478 | -61 | 0 | 0 | 2539 | 1856.6364 | 1856.6364 | 1856.6364 | 559.6867 | 780 | 200 | 1539.6867 | 38.49% | 95% | 0% | -69.7941 | 1786.8424 | -2750 | -200 | -1163.1576 | 29.08% | 34.06% | 95% | 0% | 2539 | -61
[5 empty] | 2019-11-08 | 46 | 7487 | 2349 | -61 | 0 | 0 | 2410 | 1654.5754 | 1654.5754 | 1654.5754 | 559.6867 | 780 | 200 | 1539.6867 | 38.49% | 95% | 0% | -69.7941 | 1584.7814 | -2750 | -200 | -1365.2186 | 34.13% | 34.01% | 95% | 0% | 2410 | -61
[5 empty] | 2019-11-08 | 47 | 7487.5 | 2235 | -63 | 0 | 0 | 2298 | 1479.1426 | 1479.1426 | 1479.1426 | 559.6867 | 780 | 200 | 1539.6867 | 38.49% | 95% | 0% | -72.0824 | 1407.0602 | -2750 | -200 | -1542.9398 | 38.57% | 34% | 95% | 0% | 2298 | -63
[5 empty] | 2019-11-08 | 48 | 7488 | 2143 | -64 | 0 | 0 | 2207 | 1336.6035 | 1336.6035 | 1336.6035 | 559.6867 | 780 | 200 | 1539.6867 | 38.49% | 95% | 0% | -73.2265 | 1263.3769 | -2750 | -200 | -1686.6231 | 42.17% | 34% | 95% | 0% | 2207 | -64
[5 empty] | 2019-11-09 | 1 | 7488.5 | 2107 | -66 | 0 | 0 | 2173 | 1283.3471 | 1283.3471 | 1283.3471 | 558.1204 | 780 | 200 | 1538.1204 | 38.45% | 95% | 0% | -75.5149 | 1207.8322 | -2750 | -200 | -1742.1678 | 43.55% | 33.99% | 95% | 0% | 2173 | -66
[5 empty] | 2019-11-09 | 2 | 7489 | 2121 | -67 | 0 | 0 | 2188 | 1306.8425 | 1306.8425 | 1306.8425 | 558.1204 | 780 | 200 | 1538.1204 | 38.45% | 95% | 0% | -76.659 | 1230.1835 | -2750 | -200 | -1719.8165 | 43% | 33.98% | 95% | 0% | 2188 | -67
[5 empty] | 2019-11-09 | 3 | 7489.5 | 2078 | -70 | 0 | 0 | 2148 | 1244.188 | 1244.188 | 1244.188 | 558.1204 | 780 | 200 | 1538.1204 | 38.45% | 95% | 0% | -80.0915 | 1164.0964 | -2750 | -200 | -1785.9036 | 44.65% | 33.96% | 95% | 0% | 2148 | -70
[5 empty] | 2019-11-09 | 4 | 7490 | 2009 | -73 | 0 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 558.1204 | 780 | 200 | 1538.1204 | 38.45% | 95% | 0% | -83.524 | 1057.2839 | -2750 | -200 | -1892.7161 | 47.32% | 33.96% | 95% | 0% | 2082 | -73
[5 empty] | 2019-11-09 | 5 | 7490.5 | 1965 | -75 | 0 | 0 | 2040 | 1075.0206 | 1075.0206 | 1075.0206 | 558.1204 | 780 | 200 | 1538.1204 | 38.45% | 95% | 0% | -85.8124 | 989.2083 | -2750 | -200 | -1960.7917 | 49.02% | 33.95% | 95% | 0% | 2040 | -75
[5 empty] | 2019-11-09 | 6 | 7491 | 1936 | -78 | 0 | 0 | 2014 | 1034.2951 | 1034.2951 | 1034.2951 | 558.1204 | 780 | 200 | 1538.1204 | 38.45% | 95% | 0% | -89.2449 | 945.0503 | -2750 | -200 | -2004.9497 | 50.12% | 33.94% | 95% | 0% | 2014 | -78
[5 empty] | 2019-11-09 | 7 | 7491.5 | 1886 | -83 | 0 | 0 | 1969 | 963.8087 | 963.8087 | 963.8087 | 558.1204 | 780 | 200 | 1538.1204 | 38.45% | 95% | 0% | -94.9657 | 868.8431 | -2750 | -200 | -2081.1569 | 52.03% | 33.92% | 95% | 0% | 1969 | -83
[5 empty] | 2019-11-09 | 8 | 7492 | 1853 | -87 | 0 | 0 | 1940 | 918.3842 | 918.3842 | 918.3842 | 558.1204 | 780 | 200 | 1538.1204 | 38.45% | 95% | 0% | -99.5423 | 818.8418 | -2750 | -200 | -2131.1582 | 53.28% | 33.91% | 95% | 0% | 1940 | -87
[5 empty] | 2019-11-09 | 9 | 7492.5 | 1829 | -90 | 0 | 0 | 1919 | 885.4905 | 885.4905 | 885.4905 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -102.9748 | 782.5157 | -2750 | -200 | -2167.4843 | 54.19% | 33.9% | 95% | 0% | 1919 | -90
[5 empty] | 2019-11-09 | 10 | 7493 | 1816 | -93 | 0 | 0 | 1909 | 869.8269 | 869.8269 | 869.8269 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -106.4073 | 763.4196 | -2750 | -200 | -2186.5804 | 54.66% | 33.89% | 95% | 0% | 1909 | -93
[5 empty] | 2019-11-09 | 11 | 7493.5 | 1842 | -95 | 0 | 0 | 1937 | 913.6851 | 913.6851 | 913.6851 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -108.6957 | 804.9894 | -2750 | -200 | -2145.0106 | 53.63% | 33.89% | 95% | 0% | 1937 | -95
[5 empty] | 2019-11-09 | 12 | 7494 | 1877 | -97 | 0 | 0 | 1974 | 971.6406 | 971.6406 | 971.6406 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -110.984 | 860.6566 | -2750 | -200 | -2089.3434 | 52.23% | 33.86% | 95% | 0% | 1974 | -97
[5 empty] | 2019-11-09 | 13 | 7494.5 | 1998 | -96 | 0 | 0 | 2094 | 1159.6043 | 1159.6043 | 1159.6043 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -109.8398 | 1049.7645 | -2750 | -200 | -1900.2355 | 47.51% | 33.85% | 95% | 0% | 2094 | -96
[5 empty] | 2019-11-09 | 14 | 7495 | 2094 | -96 | 1 | 0 | 2190 | 1309.9753 | 1309.9753 | 1309.9753 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -109.8398 | 1200.1355 | -3550 | -400 | -2749.8645 | 68.75% | 33.84% | 95% | 0% | 2190 | -96
[5 empty] | 2019-11-09 | 15 | 7495.5 | 2198 | -99 | 1 | 0 | 2297 | 1477.5763 | 1477.5763 | 1477.5763 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -113.2723 | 1364.3039 | -3550 | -400 | -2585.6961 | 64.64% | 33.84% | 95% | 0% | 2297 | -99
[5 empty] | 2019-11-09 | 16 | 7496 | 2264 | -126 | 1 | 0 | 2390 | 1623.2481 | 1623.2481 | 1623.2481 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -144.1648 | 1479.0834 | -3550 | -400 | -2470.9166 | 61.77% | 33.84% | 95% | 0% | 2390 | -126
[5 empty] | 2019-11-09 | 17 | 7496.5 | 2357 | -167 | 1 | 0 | 2524 | 1833.141 | 1833.141 | 1833.141 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -191.0755 | 1642.0655 | -3550 | -400 | -2307.9345 | 57.7% | 33.82% | 95% | 0% | 2524 | -167
[5 empty] | 2019-11-09 | 18 | 7497 | 2417 | -212 | 1 | 0 | 2629 | 1997.6092 | 1997.6092 | 1997.6092 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -242.5629 | 1755.0463 | -3550 | -400 | -2194.9537 | 54.87% | 33.81% | 95% | 0% | 2629 | -212
[5 empty] | 2019-11-09 | 19 | 7497.5 | 2470 | -239 | 1 | 0 | 2709 | 2122.9184 | 2122.9184 | 2122.9184 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -273.4554 | 1849.463 | -3550 | -400 | -2100.537 | 52.51% | 33.8% | 95% | 0% | 2709 | -239
[5 empty] | 2019-11-09 | 20 | 7498 | 2477 | -264 | 1 | 0 | 2741 | 2173.042 | 2173.042 | 2173.042 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -302.0595 | 1870.9825 | -3550 | -400 | -2079.0175 | 51.98% | 33.8% | 95% | 0% | 2741 | -264
[5 empty] | 2019-11-09 | 21 | 7498.5 | 2498 | -271 | 1 | 0 | 2769 | 2216.9002 | 2216.9002 | 2216.9002 | 556.554 | 780 | 200 | 1536.554 | 38.41% | 95% | 0% | -310.0686 | 1906.8316 | -3550 | -400 | -2043.1684 | 51.08% | 33.8% | 95% | 0% | 2769 | -271
[5 empty] | 2019-11-09 | 22 | 7499 | 2510 | -274 | 1 | 0 | 2784 | 2240.3957 | 2240.3957 | 2240.3957 | 554.9876 | 780 | 200 | 1534.9876 | 38.37% | 95% | 0% | -313.5011 | 1926.8946 | -3550 | -400 | -2023.1054 | 50.58% | 33.79% | 95% | 0% | 2784 | -274
[5 empty] | 2019-11-09 | 23 | 7499.5 | 2520 | -279 | 1 | 0 | 2799 | 2263.8912 | 2263.8912 | 2263.8912 | 554.9876 | 780 | 200 | 1534.9876 | 38.37% | 95% | 0% | -319.222 | 1944.6692 | -3550 | -400 | -2005.3308 | 50.13% | 33.79% | 95% | 0% | 2799 | -279
[5 empty] | 2019-11-09 | 24 | 7500 | 2557 | -251 | 1 | 0 | 2808 | 2277.9885 | 2277.9885 | 2277.9885 | 554.9876 | 780 | 200 | 1534.9876 | 38.37% | 95% | 0% | -287.1854 | 1990.8031 | -3550 | -400 | -1959.1969 | 48.98% | 33.78% | 95% | 0% | 2808 | -251
[5 empty] | 2019-11-09 | 25 | 7500.5 | 2607 | -225 | 1 | 0 | 2832 | 2315.5812 | 2315.5812 | 2315.5812 | 554.9876 | 780 | 200 | 1534.9876 | 38.37% | 95% | 0% | -257.4371 | 2058.1441 | -3550 | -400 | -1891.8559 | 47.3% | 33.76% | 95% | 0% | 2832 | -225
[5 empty] | 2019-11-09 | 26 | 7501 | 2605 | -213 | 1 | 0 | 2818 | 2293.6521 | 2293.6521 | 2293.6521 | 554.9876 | 780 | 200 | 1534.9876 | 38.37% | 95% | 0% | -243.7071 | 2049.945 | -3550 | -400 | -1900.055 | 47.5% | 33.73% | 95% | 0% | 2818 | -213
[5 empty] | 2019-11-09 | 27 | 7501.5 | 2613 | -200 | 1 | 0 | 2813 | 2285.8203 | 2285.8203 | 2285.8203 | 553.4213 | 780 | 200 | 1533.4213 | 38.34% | 95% | 0% | -228.833 | 2056.9873 | -3550 | -400 | -1893.0127 | 47.33% | 33.72% | 95% | 0% | 2813 | -200
[5 empty] | 2019-11-09 | 28 | 7502 | 2619 | -190 | 1 | 0 | 2809 | 2279.5548 | 2279.5548 | 2279.5548 | 553.4213 | 780 | 200 | 1533.4213 | 38.34% | 95% | 0% | -217.3913 | 2062.1635 | -3550 | -400 | -1887.8365 | 47.2% | 33.72% | 95% | 0% | 2809 | -190
[5 empty] | 2019-11-09 | 29 | 7502.5 | 2657 | -151 | 1 | 0 | 2808 | 2277.9885 | 2277.9885 | 2277.9885 | 553.4213 | 780 | 200 | 1533.4213 | 38.34% | 95% | 0% | -172.7689 | 2105.2196 | -3550 | -400 | -1844.7804 | 46.12% | 33.71% | 95% | 0% | 2808 | -151
[5 empty] | 2019-11-09 | 30 | 7503 | 2717 | -113 | 1 | 0 | 2830 | 2312.4485 | 2312.4485 | 2312.4485 | 553.4213 | 780 | 200 | 1533.4213 | 38.34% | 95% | 0% | -129.2906 | 2183.1579 | -3550 | -400 | -1766.8421 | 44.17% | 33.71% | 95% | 0% | 2830 | -113
[5 empty] | 2019-11-09 | 31 | 7503.5 | 2772 | -95 | 1 | 0 | 2867 | 2370.404 | 2370.404 | 2370.404 | 553.4213 | 780 | 200 | 1533.4213 | 38.34% | 95% | 0% | -108.6957 | 2261.7083 | -3550 | -400 | -1688.2917 | 42.21% | 33.7% | 95% | 0% | 2867 | -95
[5 empty] | 2019-11-09 | 32 | 7504 | 2824 | -85 | 1 | 0 | 2909 | 2436.1913 | 2436.1913 | 2436.1913 | 553.4213 | 780 | 200 | 1533.4213 | 38.34% | 95% | 0% | -97.254 | 2338.9373 | -3550 | -400 | -1611.0627 | 40.28% | 33.7% | 95% | 0% | 2909 | -85
[5 empty] | 2019-11-09 | 33 | 7504.5 | 2915 | -82 | 1 | 0 | 2997 | 2574.0313 | 2574.0313 | 2574.0313 | 551.8549 | 780 | 200 | 1531.8549 | 38.3% | 95% | 0% | -93.8215 | 2480.2098 | -3550 | -400 | -1469.7902 | 36.74% | 33.69% | 95% | 0% | 2997 | -82
[5 empty] | 2019-11-09 | 34 | 7505 | 3048 | -83 | 1 | 0 | 3131 | 2783.9242 | 2783.9242 | 2783.9242 | 551.8549 | 780 | 200 | 1531.8549 | 38.3% | 95% | 0% | -94.9657 | 2688.9585 | -3550 | -400 | -1261.0415 | 31.53% | 33.69% | 95% | 0% | 3131 | -83
[5 empty] | 2019-11-09 | 35 | 7505.5 | 3080 | -84 | 0 | 0 | 3164 | 2835.6142 | 2835.6142 | 2835.6142 | 551.8549 | 780 | 200 | 1531.8549 | 38.3% | 95% | 0% | -96.1098 | 2739.5043 | -2750 | -200 | -210.4957 | 5.262% | 33.67% | 95% | 0% | 3164 | -84
[5 empty] | 2019-11-09 | 36 | 7506 | 3064 | -86 | 0 | 0 | 3150 | 2813.6851 | 2813.6851 | 2813.6851 | 551.8549 | 780 | 200 | 1531.8549 | 38.3% | 95% | 0% | -98.3982 | 2715.2869 | -2750 | -200 | -234.7131 | 5.868% | 33.67% | 95% | 0% | 3150 | -86
[5 empty] | 2019-11-09 | 37 | 7506.5 | 3047 | -87 | 0 | 0 | 3134 | 2788.6232 | 2788.6232 | 2788.6232 | 551.8549 | 780 | 200 | 1531.8549 | 38.3% | 95% | 0% | -99.5423 | 2689.0809 | -2750 | -200 | -260.9191 | 6.523% | 33.66% | 95% | 0% | 3134 | -87
[5 empty] | 2019-11-09 | 38 | 7507 | 2999 | -88 | 0 | 0 | 3087 | 2715.0041 | 2715.0041 | 2715.0041 | 550.2885 | 780 | 200 | 1530.2885 | 38.26% | 95% | 0% | -100.6865 | 2614.3176 | -2750 | -200 | -335.6824 | 8.392% | 33.65% | 95% | 0% | 3087 | -88
[5 empty] | 2019-11-09 | 39 | 7507.5 | 2898 | -89 | 0 | 0 | 2987 | 2558.3677 | 2558.3677 | 2558.3677 | 550.2885 | 780 | 200 | 1530.2885 | 38.26% | 95% | 0% | -101.8307 | 2456.537 | -2750 | -200 | -493.463 | 12.34% | 33.65% | 95% | 0% | 2987 | -89
[5 empty] | 2019-11-09 | 40 | 7508 | 2795 | -90 | 0 | 0 | 2885 | 2398.5985 | 2398.5985 | 2398.5985 | 550.2885 | 780 | 200 | 1530.2885 | 38.26% | 95% | 0% | -102.9748 | 2295.6237 | -2750 | -200 | -654.3763 | 16.36% | 33.64% | 95% | 0% | 2885 | -90
[5 empty] | 2019-11-09 | 41 | 7508.5 | 2706 | -93 | 0 | 0 | 2799 | 2263.8912 | 2263.8912 | 2263.8912 | 550.2885 | 780 | 200 | 1530.2885 | 38.26% | 95% | 0% | -106.4073 | 2157.4839 | -2750 | -200 | -792.5161 | 19.81% | 33.64% | 95% | 0% | 2799 | -93
[5 empty] | 2019-11-09 | 42 | 7509 | 2589 | -96 | 0 | 0 | 2685 | 2085.3256 | 2085.3256 | 2085.3256 | 550.2885 | 780 | 200 | 1530.2885 | 38.26% | 95% | 0% | -109.8398 | 1975.4858 | -2750 | -200 | -974.5142 | 24.36% | 33.63% | 95% | 0% | 2685 | -96
[5 empty] | 2019-11-09 | 43 | 7509.5 | 2484 | -98 | 0 | 0 | 2582 | 1923.9901 | 1923.9901 | 1923.9901 | 550.2885 | 780 | 200 | 1530.2885 | 38.26% | 95% | 0% | -112.1281 | 1811.862 | -2750 | -200 | -1138.138 | 28.45% | 33.63% | 95% | 0% | 2582 | -98
[5 empty] | 2019-11-09 | 44 | 7510 | 2379 | -100 | 0 | 0 | 2479 | 1762.6546 | 1762.6546 | 1762.6546 | 550.2885 | 780 | 200 | 1530.2885 | 38.26% | 95% | 0% | -114.4165 | 1648.2381 | -2750 | -200 | -1301.7619 | 32.54% | 33.62% | 95% | 0% | 2479 | -100
[5 empty] | 2019-11-09 | 45 | 7510.5 | 2252 | -101 | 0 | 0 | 2353 | 1565.2927 | 1565.2927 | 1565.2927 | 550.2885 | 780 | 200 | 1530.2885 | 38.26% | 95% | 0% | -115.5606 | 1449.732 | -2750 | -200 | -1500.268 | 37.51% | 33.61% | 95% | 0% | 2353 | -101
[5 empty] | 2019-11-09 | 46 | 7511 | 2146 | -102 | 0 | 0 | 2248 | 1400.8244 | 1400.8244 | 1400.8244 | 548.7222 | 780 | 200 | 1528.7222 | 38.22% | 95% | 0% | -116.7048 | 1284.1196 | -2750 | -200 | -1665.8804 | 41.65% | 33.61% | 95% | 0% | 2248 | -102
[5 empty] | 2019-11-09 | 47 | 7511.5 | 2028 | -103 | 0 | 0 | 2131 | 1217.5598 | 1217.5598 | 1217.5598 | 548.7222 | 780 | 200 | 1528.7222 | 38.22% | 95% | 0% | -117.849 | 1099.7108 | -2750 | -200 | -1850.2892 | 46.26% | 33.58% | 95% | 0% | 2131 | -103
[5 empty] | 2019-11-09 | 48 | 7512 | 1935 | -104 | 0 | 0 | 2039 | 1073.4542 | 1073.4542 | 1073.4542 | 548.7222 | 780 | 200 | 1528.7222 | 38.22% | 95% | 0% | -118.9931 | 954.4611 | -2750 | -200 | -1995.5389 | 49.89% | 33.58% | 95% | 0% | 2039 | -104
[5 empty] | 2019-11-10 | 1 | 7512.5 | 1896 | -103 | 0 | 0 | 1999 | 1010.7997 | 1010.7997 | 1010.7997 | 548.7222 | 780 | 200 | 1528.7222 | 38.22% | 95% | 0% | -117.849 | 892.9507 | -2750 | -200 | -2057.0493 | 51.43% | 33.57% | 95% | 0% | 1999 | -103
[5 empty] | 2019-11-10 | 2 | 7513 | 1913 | -103 | 0 | 0 | 2016 | 1037.4279 | 1037.4279 | 1037.4279 | 548.7222 | 780 | 200 | 1528.7222 | 38.22% | 95% | 0% | -117.849 | 919.5789 | -2750 | -200 | -2030.4211 | 50.76% | 33.57% | 95% | 0% | 2016 | -103
[5 empty] | 2019-11-10 | 3 | 7513.5 | 1877 | -102 | 0 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 548.7222 | 780 | 200 | 1528.7222 | 38.22% | 95% | 0% | -116.7048 | 862.7676 | -2750 | -200 | -2087.2324 | 52.18% | 33.56% | 95% | 0% | 1979 | -102
[5 empty] | 2019-11-10 | 4 | 7514 | 1833 | -100 | 0 | 0 | 1933 | 907.4196 | 907.4196 | 907.4196 | 548.7222 | 780 | 200 | 1528.7222 | 38.22% | 95% | 0% | -114.4165 | 793.0031 | -2750 | -200 | -2156.9969 | 53.92% | 33.55% | 95% | 0% | 1933 | -100
[5 empty] | 2019-11-10 | 5 | 7514.5 | 1773 | -98 | 0 | 0 | 1871 | 810.305 | 810.305 | 810.305 | 548.7222 | 780 | 200 | 1528.7222 | 38.22% | 95% | 0% | -112.1281 | 698.1769 | -2750 | -200 | -2251.8231 | 56.3% | 33.54% | 95% | 0% | 1871 | -98
[5 empty] | 2019-11-10 | 6 | 7515 | 1745 | -96 | 0 | 0 | 1841 | 763.3141 | 763.3141 | 763.3141 | 548.7222 | 780 | 200 | 1528.7222 | 38.22% | 95% | 0% | -109.8398 | 653.4743 | -2750 | -200 | -2296.5257 | 57.41% | 33.53% | 95% | 0% | 1841 | -96
[5 empty] | 2019-11-10 | 7 | 7515.5 | 1712 | -94 | 0 | 0 | 1806 | 708.4913 | 708.4913 | 708.4913 | 547.1558 | 780 | 200 | 1527.1558 | 38.18% | 95% | 0% | -107.5515 | 600.9399 | -2750 | -200 | -2349.0601 | 58.73% | 33.53% | 95% | 0% | 1806 | -94
[5 empty] | 2019-11-10 | 8 | 7516 | 1685 | -93 | 0 | 0 | 1778 | 664.6331 | 664.6331 | 664.6331 | 547.1558 | 780 | 200 | 1527.1558 | 38.18% | 95% | 0% | -106.4073 | 558.2258 | -2750 | -200 | -2391.7742 | 59.79% | 33.51% | 95% | 0% | 1778 | -93
[5 empty] | 2019-11-10 | 9 | 7516.5 | 1663 | -92 | 0 | 0 | 1755 | 628.6068 | 628.6068 | 628.6068 | 547.1558 | 780 | 200 | 1527.1558 | 38.18% | 95% | 0% | -105.2632 | 523.3436 | -2750 | -200 | -2426.6564 | 60.67% | 33.5% | 95% | 0% | 1755 | -92
[5 empty] | 2019-11-10 | 10 | 7517 | 1662 | -91 | 0 | 0 | 1753 | 625.474 | 625.474 | 625.474 | 547.1558 | 780 | 200 | 1527.1558 | 38.18% | 95% | 0% | -104.119 | 521.355 | -2750 | -200 | -2428.645 | 60.72% | 33.48% | 95% | 0% | 1753 | -91
[5 empty] | 2019-11-10 | 11 | 7517.5 | 1677 | -89 | 0 | 0 | 1766 | 645.8368 | 645.8368 | 645.8368 | 547.1558 | 780 | 200 | 1527.1558 | 38.18% | 95% | 0% | -101.8307 | 544.0061 | -2750 | -200 | -2405.9939 | 60.15% | 33.48% | 95% | 0% | 1766 | -89
[5 empty] | 2019-11-10 | 12 | 7518 | 1706 | -87 | 0 | 0 | 1793 | 688.1286 | 688.1286 | 688.1286 | 547.1558 | 780 | 200 | 1527.1558 | 38.18% | 95% | 0% | -99.5423 | 588.5863 | -2750 | -200 | -2361.4137 | 59.04% | 33.47% | 95% | 0% | 1793 | -87
[5 empty] | 2019-11-10 | 13 | 7518.5 | 1796 | -83 | 0 | 0 | 1879 | 822.8359 | 822.8359 | 822.8359 | 547.1558 | 780 | 200 | 1527.1558 | 38.18% | 95% | 0% | -94.9657 | 727.8703 | -2750 | -200 | -2222.1297 | 55.55% | 33.47% | 95% | 0% | 1879 | -83
[5 empty] | 2019-11-10 | 14 | 7519 | 1878 | -79 | 0 | 0 | 1957 | 945.0124 | 945.0124 | 945.0124 | 547.1558 | 780 | 200 | 1527.1558 | 38.18% | 95% | 0% | -90.389 | 854.6234 | -2750 | -200 | -2095.3766 | 52.38% | 33.47% | 95% | 0% | 1957 | -79
[5 empty] | 2019-11-10 | 15 | 7519.5 | 1950 | -76 | 0 | 0 | 2026 | 1053.0915 | 1053.0915 | 1053.0915 | 547.1558 | 780 | 200 | 1527.1558 | 38.18% | 95% | 0% | -86.9565 | 966.135 | -2750 | -200 | -1983.865 | 49.6% | 33.46% | 95% | 0% | 2026 | -76
[5 empty] | 2019-11-10 | 16 | 7520 | 2015 | -89 | 0 | 0 | 2104 | 1175.2679 | 1175.2679 | 1175.2679 | 547.1558 | 780 | 200 | 1527.1558 | 38.18% | 95% | 0% | -101.8307 | 1073.4373 | -2750 | -200 | -1876.5627 | 46.91% | 33.44% | 95% | 0% | 2104 | -89
[5 empty] | 2019-11-10 | 17 | 7520.5 | 2101 | -130 | 1 | 0 | 2231 | 1374.1962 | 1374.1962 | 1374.1962 | 547.1558 | 780 | 200 | 1527.1558 | 38.18% | 95% | 0% | -148.7414 | 1225.4548 | -3550 | -400 | -2724.5452 | 68.11% | 33.44% | 95% | 0% | 2231 | -130
[5 empty] | 2019-11-10 | 18 | 7521 | 2165 | -181 | 1 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 547.1558 | 780 | 200 | 1527.1558 | 38.18% | 95% | 0% | -207.0938 | 1347.2343 | -3550 | -400 | -2602.7657 | 65.07% | 33.43% | 95% | 0% | 2346 | -181
[5 empty] | 2019-11-10 | 19 | 7521.5 | 2202 | -227 | 1 | 0 | 2429 | 1684.3364 | 1684.3364 | 1684.3364 | 545.5894 | 780 | 200 | 1525.5894 | 38.14% | 95% | 0% | -259.7254 | 1424.611 | -3550 | -400 | -2525.389 | 63.13% | 33.42% | 95% | 0% | 2429 | -227
[5 empty] | 2019-11-10 | 20 | 7522 | 2171 | -284 | 1 | 0 | 2455 | 1725.0618 | 1725.0618 | 1725.0618 | 545.5894 | 780 | 200 | 1525.5894 | 38.14% | 95% | 0% | -324.9428 | 1400.119 | -3550 | -400 | -2549.881 | 63.75% | 33.41% | 95% | 0% | 2455 | -284
[5 empty] | 2019-11-10 | 21 | 7522.5 | 2114 | -348 | 1 | 0 | 2462 | 1736.0264 | 1736.0264 | 1736.0264 | 545.5894 | 780 | 200 | 1525.5894 | 38.14% | 95% | 0% | -398.1693 | 1337.857 | -3550 | -400 | -2612.143 | 65.3% | 33.4% | 95% | 0% | 2462 | -348
[5 empty] | 2019-11-10 | 22 | 7523 | 2054 | -398 | 1 | 0 | 2452 | 1720.3627 | 1720.3627 | 1720.3627 | 545.5894 | 780 | 200 | 1525.5894 | 38.14% | 95% | 0% | -455.3776 | 1264.9852 | -3550 | -400 | -2685.0148 | 67.13% | 33.4% | 95% | 0% | 2452 | -398
[5 empty] | 2019-11-10 | 23 | 7523.5 | 2022 | -414 | 1 | 0 | 2436 | 1695.3009 | 1695.3009 | 1695.3009 | 545.5894 | 780 | 200 | 1525.5894 | 38.14% | 95% | 0% | -473.6842 | 1221.6167 | -3550 | -400 | -2728.3833 | 68.21% | 33.39% | 95% | 0% | 2436 | -414
[5 empty] | 2019-11-10 | 24 | 7524 | 2032 | -433 | 1 | 0 | 2465 | 1740.7255 | 1740.7255 | 1740.7255 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -495.4233 | 1245.3021 | -3550 | -400 | -2704.6979 | 67.62% | 33.39% | 95% | 0% | 2465 | -433
[5 empty] | 2019-11-10 | 25 | 7524.5 | 2078 | -425 | 1 | 0 | 2503 | 1800.2473 | 1800.2473 | 1800.2473 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -486.27 | 1313.9773 | -3550 | -400 | -2636.0227 | 65.9% | 33.36% | 95% | 0% | 2503 | -425
[5 empty] | 2019-11-10 | 26 | 7525 | 2145 | -385 | 1 | 0 | 2530 | 1842.5392 | 1842.5392 | 1842.5392 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -440.5034 | 1402.0357 | -3550 | -400 | -2547.9643 | 63.7% | 33.36% | 95% | 0% | 2530 | -385
[5 empty] | 2019-11-10 | 27 | 7525.5 | 2202 | -346 | 1 | 0 | 2548 | 1870.7337 | 1870.7337 | 1870.7337 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -395.881 | 1474.8527 | -3550 | -400 | -2475.1473 | 61.88% | 33.35% | 95% | 0% | 2548 | -346
[5 empty] | 2019-11-10 | 28 | 7526 | 2266 | -296 | 1 | 0 | 2562 | 1892.6628 | 1892.6628 | 1892.6628 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -338.6728 | 1553.9901 | -3550 | -400 | -2396.0099 | 59.9% | 33.32% | 95% | 0% | 2562 | -296
[5 empty] | 2019-11-10 | 29 | 7526.5 | 2384 | -232 | 1 | 0 | 2616 | 1977.2465 | 1977.2465 | 1977.2465 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -265.4462 | 1711.8003 | -3550 | -400 | -2238.1997 | 55.95% | 33.32% | 95% | 0% | 2616 | -232
[5 empty] | 2019-11-10 | 30 | 7527 | 2524 | -166 | 1 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -189.9314 | 1903.2261 | -3550 | -400 | -2046.7739 | 51.17% | 33.32% | 95% | 0% | 2690 | -166
[5 empty] | 2019-11-10 | 31 | 7527.5 | 2658 | -103 | 1 | 0 | 2761 | 2204.3693 | 2204.3693 | 2204.3693 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -117.849 | 2086.5204 | -3550 | -400 | -1863.4796 | 46.59% | 33.29% | 95% | 0% | 2761 | -103
[5 empty] | 2019-11-10 | 32 | 7528 | 2780 | -64 | 1 | 0 | 2844 | 2334.3776 | 2334.3776 | 2334.3776 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -73.2265 | 2261.151 | -3550 | -400 | -1688.849 | 42.22% | 33.29% | 95% | 0% | 2844 | -64
[5 empty] | 2019-11-10 | 33 | 7528.5 | 2961 | -53 | 1 | 0 | 3014 | 2600.6595 | 2600.6595 | 2600.6595 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -60.6407 | 2540.0188 | -3550 | -400 | -1409.9812 | 35.25% | 33.28% | 95% | 0% | 3014 | -53
[5 empty] | 2019-11-10 | 34 | 7529 | 3084 | -57 | 1 | 0 | 3141 | 2799.5878 | 2799.5878 | 2799.5878 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -65.2174 | 2734.3704 | -3550 | -400 | -1215.6296 | 30.39% | 33.27% | 95% | 0% | 3141 | -57
[5 empty] | 2019-11-10 | 35 | 7529.5 | 3154 | -60 | 1 | 0 | 3214 | 2913.9324 | 2913.9324 | 2913.9324 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -68.6499 | 2845.2825 | -3550 | -400 | -1104.7175 | 27.62% | 33.26% | 95% | 0% | 3214 | -60
[5 empty] | 2019-11-10 | 36 | 7530 | 3145 | -63 | 0 | 0 | 3208 | 2904.5342 | 2904.5342 | 2904.5342 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -72.0824 | 2832.4518 | -2750 | -200 | -117.5482 | 2.939% | 33.26% | 95% | 0% | 3208 | -63
[5 empty] | 2019-11-10 | 37 | 7530.5 | 3110 | -69 | 0 | 0 | 3179 | 2859.1096 | 2859.1096 | 2859.1096 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -78.9474 | 2780.1623 | -2750 | -200 | -169.8377 | 4.246% | 33.26% | 95% | 0% | 3179 | -69
[5 empty] | 2019-11-10 | 38 | 7531 | 3049 | -75 | 0 | 0 | 3124 | 2772.9596 | 2772.9596 | 2772.9596 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -85.8124 | 2687.1472 | -2750 | -200 | -262.8528 | 6.571% | 33.24% | 95% | 0% | 3124 | -75
[5 empty] | 2019-11-10 | 39 | 7531.5 | 2965 | -81 | 0 | 0 | 3046 | 2650.7832 | 2650.7832 | 2650.7832 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -92.6773 | 2558.1058 | -2750 | -200 | -391.8942 | 9.797% | 33.24% | 95% | 0% | 3046 | -81
[5 empty] | 2019-11-10 | 40 | 7532 | 2851 | -87 | 0 | 0 | 2938 | 2481.6158 | 2481.6158 | 2481.6158 | 544.0231 | 780 | 200 | 1524.0231 | 38.1% | 95% | 0% | -99.5423 | 2382.0735 | -2750 | -200 | -567.9265 | 14.2% | 33.24% | 95% | 0% | 2938 | -87
[5 empty] | 2019-11-10 | 41 | 7532.5 | 2756 | -94 | 0 | 0 | 2850 | 2343.7758 | 2343.7758 | 2343.7758 | 542.4567 | 780 | 200 | 1522.4567 | 38.06% | 95% | 0% | -107.5515 | 2236.2243 | -2750 | -200 | -713.7757 | 17.84% | 33.23% | 95% | 0% | 2850 | -94
[5 empty] | 2019-11-10 | 42 | 7533 | 2625 | -101 | 0 | 0 | 2726 | 2149.5466 | 2149.5466 | 2149.5466 | 542.4567 | 780 | 200 | 1522.4567 | 38.06% | 95% | 0% | -115.5606 | 2033.9859 | -2750 | -200 | -916.0141 | 22.9% | 33.19% | 95% | 0% | 2726 | -101
[5 empty] | 2019-11-10 | 43 | 7533.5 | 2492 | -108 | 0 | 0 | 2600 | 1952.1847 | 1952.1847 | 1952.1847 | 542.4567 | 780 | 200 | 1522.4567 | 38.06% | 95% | 0% | -123.5698 | 1828.6149 | -2750 | -200 | -1121.3851 | 28.03% | 33.17% | 95% | 0% | 2600 | -108
[5 empty] | 2019-11-10 | 44 | 7534 | 2328 | -114 | 0 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 542.4567 | 780 | 200 | 1522.4567 | 38.06% | 95% | 0% | -130.4348 | 1574.2643 | -2750 | -200 | -1375.7357 | 34.39% | 33.17% | 95% | 0% | 2442 | -114
[5 empty] | 2019-11-10 | 45 | 7534.5 | 2177 | -121 | 0 | 0 | 2298 | 1479.1426 | 1479.1426 | 1479.1426 | 542.4567 | 780 | 200 | 1522.4567 | 38.06% | 95% | 0% | -138.4439 | 1340.6987 | -2750 | -200 | -1609.3013 | 40.23% | 33.16% | 95% | 0% | 2298 | -121
[5 empty] | 2019-11-10 | 46 | 7535 | 2028 | -127 | 0 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 542.4567 | 780 | 200 | 1522.4567 | 38.06% | 95% | 0% | -145.3089 | 1109.8436 | -2750 | -200 | -1840.1564 | 46% | 33.15% | 95% | 0% | 2155 | -127
[5 empty] | 2019-11-10 | 47 | 7535.5 | 1865 | -136 | 0 | 0 | 2001 | 1013.9324 | 1013.9324 | 1013.9324 | 542.4567 | 780 | 200 | 1522.4567 | 38.06% | 95% | 0% | -155.6064 | 858.326 | -2750 | -200 | -2091.674 | 52.29% | 33.15% | 95% | 0% | 2001 | -136
[5 empty] | 2019-11-10 | 48 | 7536 | 1766 | -144 | 0 | 0 | 1910 | 871.3932 | 871.3932 | 871.3932 | 542.4567 | 780 | 200 | 1522.4567 | 38.06% | 95% | 0% | -164.7597 | 706.6335 | -2750 | -200 | -2243.3665 | 56.08% | 33.14% | 95% | 0% | 1910 | -144
[5 empty] | 2019-11-11 | 1 | 7536.5 | 1726 | -149 | 0 | 0 | 1875 | 816.5705 | 816.5705 | 816.5705 | 542.4567 | 780 | 200 | 1522.4567 | 38.06% | 95% | 0% | -170.4805 | 646.0899 | -2750 | -200 | -2303.9101 | 57.6% | 33.14% | 95% | 0% | 1875 | -149
[5 empty] | 2019-11-11 | 2 | 7537 | 1734 | -154 | 0 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 542.4567 | 780 | 200 | 1522.4567 | 38.06% | 95% | 0% | -176.2014 | 660.7319 | -2750 | -200 | -2289.2681 | 57.23% | 33.13% | 95% | 0% | 1888 | -154
[5 empty] | 2019-11-11 | 3 | 7537.5 | 1699 | -160 | 0 | 0 | 1859 | 791.5087 | 791.5087 | 791.5087 | 542.4567 | 780 | 200 | 1522.4567 | 38.06% | 95% | 0% | -183.0664 | 608.4423 | -2750 | -200 | -2341.5577 | 58.54% | 33.11% | 95% | 0% | 1859 | -160
[5 empty] | 2019-11-11 | 4 | 7538 | 1662 | -165 | 0 | 0 | 1827 | 741.385 | 741.385 | 741.385 | 542.4567 | 780 | 200 | 1522.4567 | 38.06% | 95% | 0% | -188.7872 | 552.5978 | -2750 | -200 | -2397.4022 | 59.94% | 33.1% | 95% | 0% | 1827 | -165
[5 empty] | 2019-11-11 | 5 | 7538.5 | 1622 | -167 | 0 | 0 | 1789 | 681.8631 | 681.8631 | 681.8631 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -191.0755 | 490.7876 | -2750 | -200 | -2459.2124 | 61.48% | 33.09% | 95% | 0% | 1789 | -167
[5 empty] | 2019-11-11 | 6 | 7539 | 1606 | -168 | 0 | 0 | 1774 | 658.3677 | 658.3677 | 658.3677 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -192.2197 | 466.148 | -2750 | -200 | -2483.852 | 62.1% | 33.07% | 95% | 0% | 1774 | -168
[5 empty] | 2019-11-11 | 7 | 7539.5 | 1575 | -168 | 0 | 0 | 1743 | 609.8104 | 609.8104 | 609.8104 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -192.2197 | 417.5907 | -2750 | -200 | -2532.4093 | 63.31% | 33.07% | 95% | 0% | 1743 | -168
[5 empty] | 2019-11-11 | 8 | 7540 | 1552 | -168 | 0 | 0 | 1720 | 573.784 | 573.784 | 573.784 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -192.2197 | 381.5643 | -2750 | -200 | -2568.4357 | 64.21% | 33.05% | 95% | 0% | 1720 | -168
[5 empty] | 2019-11-11 | 9 | 7540.5 | 1546 | -166 | 0 | 0 | 1712 | 561.2531 | 561.2531 | 561.2531 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -189.9314 | 371.3217 | -2750 | -200 | -2578.6783 | 64.47% | 33.05% | 95% | 0% | 1712 | -166
[5 empty] | 2019-11-11 | 10 | 7541 | 1574 | -164 | 0 | 0 | 1738 | 601.9786 | 601.9786 | 601.9786 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -187.643 | 414.3355 | -2750 | -200 | -2535.6645 | 63.39% | 33.04% | 95% | 0% | 1738 | -164
[5 empty] | 2019-11-11 | 11 | 7541.5 | 1659 | -162 | 0 | 0 | 1821 | 731.9868 | 731.9868 | 731.9868 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -185.3547 | 546.6321 | -2750 | -200 | -2403.3679 | 60.08% | 33.04% | 95% | 0% | 1821 | -162
[5 empty] | 2019-11-11 | 12 | 7542 | 1777 | -159 | 0 | 0 | 1936 | 912.1187 | 912.1187 | 912.1187 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -181.9222 | 730.1965 | -2750 | -200 | -2219.8035 | 55.5% | 33.04% | 95% | 0% | 1936 | -159
[5 empty] | 2019-11-11 | 13 | 7542.5 | 2032 | -157 | 0 | 0 | 2189 | 1308.4089 | 1308.4089 | 1308.4089 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -179.6339 | 1128.775 | -2750 | -200 | -1821.225 | 45.53% | 33.03% | 95% | 0% | 2189 | -157
[5 empty] | 2019-11-11 | 14 | 7543 | 2287 | -155 | 1 | 0 | 2442 | 1704.6991 | 1704.6991 | 1704.6991 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -177.3455 | 1527.3536 | -3550 | -400 | -2422.6464 | 60.57% | 33.02% | 95% | 0% | 2442 | -155
[5 empty] | 2019-11-11 | 15 | 7543.5 | 2542 | -155 | 1 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -177.3455 | 1926.7765 | -3550 | -400 | -2023.2235 | 50.58% | 33.01% | 95% | 0% | 2697 | -155
[5 empty] | 2019-11-11 | 16 | 7544 | 2655 | -161 | 1 | 0 | 2816 | 2290.5194 | 2290.5194 | 2290.5194 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -184.2105 | 2106.3088 | -3550 | -400 | -1843.6912 | 46.09% | 32.99% | 95% | 0% | 2816 | -161
[5 empty] | 2019-11-11 | 17 | 7544.5 | 2681 | -187 | 1 | 0 | 2868 | 2371.9703 | 2371.9703 | 2371.9703 | 540.8904 | 780 | 200 | 1520.8904 | 38.02% | 95% | 0% | -213.9588 | 2158.0115 | -3550 | -400 | -1791.9885 | 44.8% | 32.99% | 95% | 0% | 2868 | -187
[5 empty] | 2019-11-11 | 18 | 7545 | 2618 | -241 | 1 | 0 | 2859 | 2357.873 | 2357.873 | 2357.873 | 539.324 | 780 | 200 | 1519.324 | 37.98% | 95% | 0% | -275.7437 | 2082.1293 | -3550 | -400 | -1867.8707 | 46.7% | 32.98% | 95% | 0% | 2859 | -241
[5 empty] | 2019-11-11 | 19 | 7545.5 | 2603 | -289 | 1 | 0 | 2892 | 2409.5631 | 2409.5631 | 2409.5631 | 539.324 | 780 | 200 | 1519.324 | 37.98% | 95% | 0% | -330.6636 | 2078.8995 | -3550 | -400 | -1871.1005 | 46.78% | 32.97% | 95% | 0% | 2892 | -289
[5 empty] | 2019-11-11 | 20 | 7546 | 2548 | -332 | 1 | 0 | 2880 | 2390.7667 | 2390.7667 | 2390.7667 | 539.324 | 780 | 200 | 1519.324 | 37.98% | 95% | 0% | -379.8627 | 2010.904 | -3550 | -400 | -1939.096 | 48.48% | 32.97% | 95% | 0% | 2880 | -332
[5 empty] | 2019-11-11 | 21 | 7546.5 | 2459 | -376 | 1 | 0 | 2835 | 2320.2803 | 2320.2803 | 2320.2803 | 539.324 | 780 | 200 | 1519.324 | 37.98% | 95% | 0% | -430.2059 | 1890.0743 | -3550 | -400 | -2059.9257 | 51.5% | 32.97% | 95% | 0% | 2835 | -376
[5 empty] | 2019-11-11 | 22 | 7547 | 2382 | -413 | 1 | 0 | 2795 | 2257.6257 | 2257.6257 | 2257.6257 | 539.324 | 780 | 200 | 1519.324 | 37.98% | 95% | 0% | -472.54 | 1785.0857 | -3550 | -400 | -2164.9143 | 54.12% | 32.96% | 95% | 0% | 2795 | -413
[5 empty] | 2019-11-11 | 23 | 7547.5 | 2346 | -418 | 1 | 0 | 2764 | 2209.0684 | 2209.0684 | 2209.0684 | 539.324 | 780 | 200 | 1519.324 | 37.98% | 95% | 0% | -478.2609 | 1730.8076 | -3550 | -400 | -2219.1924 | 55.48% | 32.95% | 95% | 0% | 2764 | -418
[5 empty] | 2019-11-11 | 24 | 7548 | 2309 | -450 | 1 | 0 | 2759 | 2201.2366 | 2201.2366 | 2201.2366 | 539.324 | 780 | 200 | 1519.324 | 37.98% | 95% | 0% | -514.8741 | 1686.3625 | -3550 | -400 | -2263.6375 | 56.59% | 32.95% | 95% | 0% | 2759 | -450
[5 empty] | 2019-11-11 | 25 | 7548.5 | 2328 | -461 | 1 | 0 | 2789 | 2248.2275 | 2248.2275 | 2248.2275 | 537.7576 | 780 | 200 | 1517.7576 | 37.94% | 95% | 0% | -527.46 | 1720.7676 | -3550 | -400 | -2229.2324 | 55.73% | 32.94% | 95% | 0% | 2789 | -461
[5 empty] | 2019-11-11 | 26 | 7549 | 2340 | -453 | 1 | 0 | 2793 | 2254.493 | 2254.493 | 2254.493 | 537.7576 | 780 | 200 | 1517.7576 | 37.94% | 95% | 0% | -518.3066 | 1736.1864 | -3550 | -400 | -2213.8136 | 55.35% | 32.92% | 95% | 0% | 2793 | -453
[5 empty] | 2019-11-11 | 27 | 7549.5 | 2382 | -401 | 1 | 0 | 2783 | 2238.8293 | 2238.8293 | 2238.8293 | 537.7576 | 780 | 200 | 1517.7576 | 37.94% | 95% | 0% | -458.8101 | 1780.0193 | -3550 | -400 | -2169.9807 | 54.25% | 32.9% | 95% | 0% | 2783 | -401
[5 empty] | 2019-11-11 | 28 | 7550 | 2423 | -375 | 1 | 0 | 2798 | 2262.3248 | 2262.3248 | 2262.3248 | 537.7576 | 780 | 200 | 1517.7576 | 37.94% | 95% | 0% | -429.0618 | 1833.263 | -3550 | -400 | -2116.737 | 52.92% | 32.88% | 95% | 0% | 2798 | -375
[5 empty] | 2019-11-11 | 29 | 7550.5 | 2488 | -324 | 1 | 0 | 2812 | 2284.2539 | 2284.2539 | 2284.2539 | 537.7576 | 780 | 200 | 1517.7576 | 37.94% | 95% | 0% | -370.7094 | 1913.5445 | -3550 | -400 | -2036.4555 | 50.91% | 32.86% | 95% | 0% | 2812 | -324
[5 empty] | 2019-11-11 | 30 | 7551 | 2565 | -282 | 1 | 0 | 2847 | 2339.0767 | 2339.0767 | 2339.0767 | 536.1913 | 780 | 200 | 1516.1913 | 37.9% | 95% | 0% | -322.6545 | 2016.4222 | -3550 | -400 | -1933.5778 | 48.34% | 32.86% | 95% | 0% | 2847 | -282
[5 empty] | 2019-11-11 | 31 | 7551.5 | 2676 | -233 | 1 | 0 | 2909 | 2436.1913 | 2436.1913 | 2436.1913 | 536.1913 | 780 | 200 | 1516.1913 | 37.9% | 95% | 0% | -266.5904 | 2169.6009 | -3550 | -400 | -1780.3991 | 44.51% | 32.85% | 95% | 0% | 2909 | -233
[5 empty] | 2019-11-11 | 32 | 7552 | 2827 | -194 | 1 | 0 | 3021 | 2611.6241 | 2611.6241 | 2611.6241 | 536.1913 | 780 | 200 | 1516.1913 | 37.9% | 95% | 0% | -221.968 | 2389.6561 | -3550 | -400 | -1560.3439 | 39.01% | 32.84% | 95% | 0% | 3021 | -194
[5 empty] | 2019-11-11 | 33 | 7552.5 | 2984 | -177 | 1 | 0 | 3161 | 2830.9151 | 2830.9151 | 2830.9151 | 536.1913 | 780 | 200 | 1516.1913 | 37.9% | 95% | 0% | -202.5172 | 2628.3979 | -3550 | -400 | -1321.6021 | 33.04% | 32.81% | 95% | 0% | 3161 | -177
[5 empty] | 2019-11-11 | 34 | 7553 | 3147 | -173 | 1 | 0 | 3320 | 3079.967 | 3079.967 | 3079.967 | 534.6249 | 780 | 200 | 1514.6249 | 37.87% | 95% | 0% | -197.9405 | 2882.0265 | -3550 | -400 | -1067.9735 | 26.7% | 32.79% | 95% | 0% | 3320 | -173
[5 empty] | 2019-11-11 | 35 | 7553.5 | 3170 | -172 | 1 | 0 | 3342 | 3114.427 | 3114.427 | 3114.427 | 534.6249 | 780 | 200 | 1514.6249 | 37.87% | 95% | 0% | -196.7963 | 2917.6307 | -3550 | -400 | -1032.3693 | 25.81% | 32.77% | 95% | 0% | 3342 | -172
[5 empty] | 2019-11-11 | 36 | 7554 | 3143 | -171 | 0 | 0 | 3314 | 3070.5688 | 3070.5688 | 3070.5688 | 534.6249 | 780 | 200 | 1514.6249 | 37.87% | 95% | 0% | -195.6522 | 2874.9167 | -2750 | -200 | -75.0833 | 1.877% | 32.75% | 95% | 0% | 3314 | -171
[5 empty] | 2019-11-11 | 37 | 7554.5 | 3129 | -171 | 0 | 0 | 3300 | 3048.6397 | 3048.6397 | 3048.6397 | 534.6249 | 780 | 200 | 1514.6249 | 37.87% | 95% | 0% | -195.6522 | 2852.9876 | -2750 | -200 | -97.0124 | 2.425% | 32.74% | 95% | 0% | 3300 | -171
[5 empty] | 2019-11-11 | 38 | 7555 | 3105 | -170 | 0 | 0 | 3275 | 3009.4806 | 3009.4806 | 3009.4806 | 534.6249 | 780 | 200 | 1514.6249 | 37.87% | 95% | 0% | -194.508 | 2814.9726 | -2750 | -200 | -135.0274 | 3.376% | 32.74% | 95% | 0% | 3275 | -170
[5 empty] | 2019-11-11 | 39 | 7555.5 | 3033 | -170 | 0 | 0 | 3203 | 2896.7024 | 2896.7024 | 2896.7024 | 534.6249 | 780 | 200 | 1514.6249 | 37.87% | 95% | 0% | -194.508 | 2702.1944 | -2750 | -200 | -247.8056 | 6.195% | 32.73% | 95% | 0% | 3203 | -170
[5 empty] | 2019-11-11 | 40 | 7556 | 2940 | -169 | 0 | 0 | 3109 | 2749.4641 | 2749.4641 | 2749.4641 | 534.6249 | 780 | 200 | 1514.6249 | 37.87% | 95% | 0% | -193.3638 | 2556.1003 | -2750 | -200 | -393.8997 | 9.847% | 32.73% | 95% | 0% | 3109 | -169
[5 empty] | 2019-11-11 | 41 | 7556.5 | 2830 | -170 | 0 | 0 | 3000 | 2578.7304 | 2578.7304 | 2578.7304 | 534.6249 | 780 | 200 | 1514.6249 | 37.87% | 95% | 0% | -194.508 | 2384.2224 | -2750 | -200 | -565.7776 | 14.14% | 32.73% | 95% | 0% | 3000 | -170
[5 empty] | 2019-11-11 | 42 | 7557 | 2687 | -170 | 0 | 0 | 2857 | 2354.7403 | 2354.7403 | 2354.7403 | 534.6249 | 780 | 200 | 1514.6249 | 37.87% | 95% | 0% | -194.508 | 2160.2323 | -2750 | -200 | -789.7677 | 19.74% | 32.72% | 95% | 0% | 2857 | -170
[5 empty] | 2019-11-11 | 43 | 7557.5 | 2544 | -170 | 0 | 0 | 2714 | 2130.7502 | 2130.7502 | 2130.7502 | 533.0585 | 780 | 200 | 1513.0585 | 37.83% | 95% | 0% | -194.508 | 1936.2422 | -2750 | -200 | -1013.7578 | 25.34% | 32.71% | 95% | 0% | 2714 | -170
[5 empty] | 2019-11-11 | 44 | 7558 | 2389 | -170 | 0 | 0 | 2559 | 1887.9637 | 1887.9637 | 1887.9637 | 533.0585 | 780 | 200 | 1513.0585 | 37.83% | 95% | 0% | -194.508 | 1693.4557 | -2750 | -200 | -1256.5443 | 31.41% | 32.71% | 95% | 0% | 2559 | -170
[5 empty] | 2019-11-11 | 45 | 7558.5 | 2210 | -169 | 0 | 0 | 2379 | 1606.0181 | 1606.0181 | 1606.0181 | 533.0585 | 780 | 200 | 1513.0585 | 37.83% | 95% | 0% | -193.3638 | 1412.6543 | -2750 | -200 | -1537.3457 | 38.43% | 32.71% | 95% | 0% | 2379 | -169
[5 empty] | 2019-11-11 | 46 | 7559 | 2059 | -168 | 0 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 533.0585 | 780 | 200 | 1513.0585 | 37.83% | 95% | 0% | -192.2197 | 1175.7111 | -2750 | -200 | -1774.2889 | 44.36% | 32.71% | 95% | 0% | 2227 | -168
[5 empty] | 2019-11-11 | 47 | 7559.5 | 1917 | -168 | 0 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 533.0585 | 780 | 200 | 1513.0585 | 37.83% | 95% | 0% | -192.2197 | 953.2873 | -2750 | -200 | -1996.7127 | 49.92% | 32.71% | 95% | 0% | 2085 | -168
[5 empty] | 2019-11-11 | 48 | 7560 | 1809 | -169 | 0 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 533.0585 | 780 | 200 | 1513.0585 | 37.83% | 95% | 0% | -193.3638 | 784.5422 | -2750 | -200 | -2165.4578 | 54.14% | 32.69% | 95% | 0% | 1978 | -169
[5 empty] | 2019-11-12 | 1 | 7560.5 | 1769 | -169 | 0 | 0 | 1938 | 915.2514 | 915.2514 | 915.2514 | 533.0585 | 780 | 200 | 1513.0585 | 37.83% | 95% | 0% | -193.3638 | 721.8876 | -2750 | -200 | -2228.1124 | 55.7% | 32.68% | 95% | 0% | 1938 | -169
[5 empty] | 2019-11-12 | 2 | 7561 | 1791 | -169 | 0 | 0 | 1960 | 949.7115 | 949.7115 | 949.7115 | 531.4922 | 780 | 200 | 1511.4922 | 37.79% | 95% | 0% | -193.3638 | 756.3476 | -2750 | -200 | -2193.6524 | 54.84% | 32.68% | 95% | 0% | 1960 | -169
[5 empty] | 2019-11-12 | 3 | 7561.5 | 1779 | -168 | 0 | 0 | 1947 | 929.3487 | 929.3487 | 929.3487 | 531.4922 | 780 | 200 | 1511.4922 | 37.79% | 95% | 0% | -192.2197 | 737.129 | -2750 | -200 | -2212.871 | 55.32% | 32.67% | 95% | 0% | 1947 | -168
[5 empty] | 2019-11-12 | 4 | 7562 | 1761 | -168 | 0 | 0 | 1929 | 901.1542 | 901.1542 | 901.1542 | 531.4922 | 780 | 200 | 1511.4922 | 37.79% | 95% | 0% | -192.2197 | 708.9345 | -2750 | -200 | -2241.0655 | 56.03% | 32.65% | 95% | 0% | 1929 | -168
[5 empty] | 2019-11-12 | 5 | 7562.5 | 1721 | -166 | 0 | 0 | 1887 | 835.3669 | 835.3669 | 835.3669 | 531.4922 | 780 | 200 | 1511.4922 | 37.79% | 95% | 0% | -189.9314 | 645.4355 | -2750 | -200 | -2304.5645 | 57.61% | 32.64% | 95% | 0% | 1887 | -166
[5 empty] | 2019-11-12 | 6 | 7563 | 1702 | -165 | 0 | 0 | 1867 | 804.0396 | 804.0396 | 804.0396 | 531.4922 | 780 | 200 | 1511.4922 | 37.79% | 95% | 0% | -188.7872 | 615.2524 | -2750 | -200 | -2334.7476 | 58.37% | 32.62% | 95% | 0% | 1867 | -165
[5 empty] | 2019-11-12 | 7 | 7563.5 | 1679 | -163 | 0 | 0 | 1842 | 764.8805 | 764.8805 | 764.8805 | 531.4922 | 780 | 200 | 1511.4922 | 37.79% | 95% | 0% | -186.4989 | 578.3816 | -2750 | -200 | -2371.6184 | 59.29% | 32.61% | 95% | 0% | 1842 | -163
[5 empty] | 2019-11-12 | 8 | 7564 | 1656 | -162 | 0 | 0 | 1818 | 727.2877 | 727.2877 | 727.2877 | 531.4922 | 780 | 200 | 1511.4922 | 37.79% | 95% | 0% | -185.3547 | 541.933 | -2750 | -200 | -2408.067 | 60.2% | 32.61% | 95% | 0% | 1818 | -162
[5 empty] | 2019-11-12 | 9 | 7564.5 | 1628 | -164 | 0 | 0 | 1792 | 686.5622 | 686.5622 | 686.5622 | 529.9258 | 780 | 200 | 1509.9258 | 37.75% | 95% | 0% | -187.643 | 498.9192 | -2750 | -200 | -2451.0808 | 61.28% | 32.61% | 95% | 0% | 1792 | -164
[5 empty] | 2019-11-12 | 10 | 7565 | 1648 | -167 | 0 | 0 | 1815 | 722.5886 | 722.5886 | 722.5886 | 529.9258 | 780 | 200 | 1509.9258 | 37.75% | 95% | 0% | -191.0755 | 531.5131 | -2750 | -200 | -2418.4869 | 60.46% | 32.58% | 95% | 0% | 1815 | -167
[5 empty] | 2019-11-12 | 11 | 7565.5 | 1721 | -169 | 0 | 0 | 1890 | 840.066 | 840.066 | 840.066 | 529.9258 | 780 | 200 | 1509.9258 | 37.75% | 95% | 0% | -193.3638 | 646.7021 | -2750 | -200 | -2303.2979 | 57.58% | 32.57% | 95% | 0% | 1890 | -169
[5 empty] | 2019-11-12 | 12 | 7566 | 1814 | -172 | 1 | 0 | 1986 | 990.4369 | 990.4369 | 990.4369 | 529.9258 | 780 | 200 | 1509.9258 | 37.75% | 95% | 0% | -196.7963 | 793.6406 | -3550 | -400 | -3156.3594 | 78.91% | 32.56% | 95% | 0% | 1986 | -172
[5 empty] | 2019-11-12 | 13 | 7566.5 | 2067 | -174 | 1 | 0 | 2241 | 1389.8599 | 1389.8599 | 1389.8599 | 529.9258 | 780 | 200 | 1509.9258 | 37.75% | 95% | 0% | -199.0847 | 1190.7752 | -3550 | -400 | -2759.2248 | 68.98% | 32.56% | 95% | 0% | 2241 | -174
[5 empty] | 2019-11-12 | 14 | 7567 | 2311 | -175 | 1 | 0 | 2486 | 1773.6191 | 1773.6191 | 1773.6191 | 529.9258 | 780 | 200 | 1509.9258 | 37.75% | 95% | 0% | -200.2288 | 1573.3903 | -3550 | -400 | -2376.6097 | 59.42% | 32.56% | 95% | 0% | 2486 | -175
[5 empty] | 2019-11-12 | 15 | 7567.5 | 2581 | -177 | 1 | 0 | 2758 | 2199.6702 | 2199.6702 | 2199.6702 | 529.9258 | 780 | 200 | 1509.9258 | 37.75% | 95% | 0% | -202.5172 | 1997.1531 | -3550 | -400 | -1952.8469 | 48.82% | 32.55% | 95% | 0% | 2758 | -177
[5 empty] | 2019-11-12 | 16 | 7568 | 2664 | -198 | 1 | 0 | 2862 | 2362.5721 | 2362.5721 | 2362.5721 | 528.3594 | 780 | 200 | 1508.3594 | 37.71% | 95% | 0% | -226.5446 | 2136.0275 | -3550 | -400 | -1813.9725 | 45.35% | 32.54% | 95% | 0% | 2862 | -198
[5 empty] | 2019-11-12 | 17 | 7568.5 | 2650 | -253 | 1 | 0 | 2903 | 2426.7931 | 2426.7931 | 2426.7931 | 528.3594 | 780 | 200 | 1508.3594 | 37.71% | 95% | 0% | -289.4737 | 2137.3194 | -3550 | -400 | -1812.6806 | 45.32% | 32.53% | 95% | 0% | 2903 | -253
[5 empty] | 2019-11-12 | 18 | 7569 | 2560 | -316 | 1 | 0 | 2876 | 2384.5012 | 2384.5012 | 2384.5012 | 528.3594 | 780 | 200 | 1508.3594 | 37.71% | 95% | 0% | -361.5561 | 2022.9452 | -3550 | -400 | -1927.0548 | 48.18% | 32.53% | 95% | 0% | 2876 | -316
[5 empty] | 2019-11-12 | 19 | 7569.5 | 2515 | -360 | 1 | 0 | 2875 | 2382.9349 | 2382.9349 | 2382.9349 | 528.3594 | 780 | 200 | 1508.3594 | 37.71% | 95% | 0% | -411.8993 | 1971.0356 | -3550 | -400 | -1978.9644 | 49.47% | 32.53% | 95% | 0% | 2875 | -360
[5 empty] | 2019-11-12 | 20 | 7570 | 2460 | -397 | 1 | 0 | 2857 | 2354.7403 | 2354.7403 | 2354.7403 | 528.3594 | 780 | 200 | 1508.3594 | 37.71% | 95% | 0% | -454.2334 | 1900.5069 | -3550 | -400 | -2049.4931 | 51.24% | 32.52% | 95% | 0% | 2857 | -397
[5 empty] | 2019-11-12 | 21 | 7570.5 | 2416 | -424 | 1 | 0 | 2840 | 2328.1121 | 2328.1121 | 2328.1121 | 528.3594 | 780 | 200 | 1508.3594 | 37.71% | 95% | 0% | -485.1259 | 1842.9863 | -3550 | -400 | -2107.0137 | 52.68% | 32.5% | 95% | 0% | 2840 | -424
[5 empty] | 2019-11-12 | 22 | 7571 | 2418 | -410 | 1 | 0 | 2828 | 2309.3157 | 2309.3157 | 2309.3157 | 528.3594 | 780 | 200 | 1508.3594 | 37.71% | 95% | 0% | -469.1076 | 1840.2082 | -3550 | -400 | -2109.7918 | 52.74% | 32.5% | 95% | 0% | 2828 | -410
[5 empty] | 2019-11-12 | 23 | 7571.5 | 2467 | -380 | 1 | 0 | 2847 | 2339.0767 | 2339.0767 | 2339.0767 | 528.3594 | 780 | 200 | 1508.3594 | 37.71% | 95% | 0% | -434.7826 | 1904.2941 | -3550 | -400 | -2045.7059 | 51.14% | 32.48% | 95% | 0% | 2847 | -380
[5 empty] | 2019-11-12 | 24 | 7572 | 2481 | -378 | 1 | 0 | 2859 | 2357.873 | 2357.873 | 2357.873 | 526.7931 | 780 | 200 | 1506.7931 | 37.67% | 95% | 0% | -432.4943 | 1925.3788 | -3550 | -400 | -2024.6212 | 50.62% | 32.48% | 95% | 0% | 2859 | -378
[5 empty] | 2019-11-12 | 25 | 7572.5 | 2550 | -350 | 1 | 0 | 2900 | 2422.094 | 2422.094 | 2422.094 | 526.7931 | 780 | 200 | 1506.7931 | 37.67% | 95% | 0% | -400.4577 | 2021.6363 | -3550 | -400 | -1928.3637 | 48.21% | 32.46% | 95% | 0% | 2900 | -350
[5 empty] | 2019-11-12 | 26 | 7573 | 2600 | -322 | 1 | 0 | 2922 | 2456.554 | 2456.554 | 2456.554 | 526.7931 | 780 | 200 | 1506.7931 | 37.67% | 95% | 0% | -368.4211 | 2088.1329 | -3550 | -400 | -1861.8671 | 46.55% | 32.43% | 95% | 0% | 2922 | -322
[5 empty] | 2019-11-12 | 27 | 7573.5 | 2644 | -306 | 1 | 0 | 2950 | 2500.4122 | 2500.4122 | 2500.4122 | 526.7931 | 780 | 200 | 1506.7931 | 37.67% | 95% | 0% | -350.1144 | 2150.2978 | -3550 | -400 | -1799.7022 | 44.99% | 32.41% | 95% | 0% | 2950 | -306
[5 empty] | 2019-11-12 | 28 | 7574 | 2661 | -289 | 1 | 0 | 2950 | 2500.4122 | 2500.4122 | 2500.4122 | 526.7931 | 780 | 200 | 1506.7931 | 37.67% | 95% | 0% | -330.6636 | 2169.7486 | -3550 | -400 | -1780.2514 | 44.51% | 32.39% | 95% | 0% | 2950 | -289
[5 empty] | 2019-11-12 | 29 | 7574.5 | 2684 | -251 | 1 | 0 | 2935 | 2476.9167 | 2476.9167 | 2476.9167 | 526.7931 | 780 | 200 | 1506.7931 | 37.67% | 95% | 0% | -287.1854 | 2189.7314 | -3550 | -400 | -1760.2686 | 44.01% | 32.39% | 95% | 0% | 2935 | -251
[5 empty] | 2019-11-12 | 30 | 7575 | 2727 | -227 | 1 | 0 | 2954 | 2506.6777 | 2506.6777 | 2506.6777 | 525.2267 | 780 | 200 | 1505.2267 | 37.63% | 95% | 0% | -259.7254 | 2246.9523 | -3550 | -400 | -1703.0477 | 42.58% | 32.39% | 95% | 0% | 2954 | -227
[5 empty] | 2019-11-12 | 31 | 7575.5 | 2780 | -202 | 1 | 0 | 2982 | 2550.5359 | 2550.5359 | 2550.5359 | 525.2267 | 780 | 200 | 1505.2267 | 37.63% | 95% | 0% | -231.1213 | 2319.4146 | -3550 | -400 | -1630.5854 | 40.76% | 32.34% | 95% | 0% | 2982 | -202
[5 empty] | 2019-11-12 | 32 | 7576 | 2908 | -183 | 1 | 0 | 3091 | 2721.2696 | 2721.2696 | 2721.2696 | 525.2267 | 780 | 200 | 1505.2267 | 37.63% | 95% | 0% | -209.3822 | 2511.8874 | -3550 | -400 | -1438.1126 | 35.95% | 32.34% | 95% | 0% | 3091 | -183
[5 empty] | 2019-11-12 | 33 | 7576.5 | 3046 | -173 | 1 | 0 | 3219 | 2921.7642 | 2921.7642 | 2921.7642 | 525.2267 | 780 | 200 | 1505.2267 | 37.63% | 95% | 0% | -197.9405 | 2723.8237 | -3550 | -400 | -1226.1763 | 30.65% | 32.34% | 95% | 0% | 3219 | -173
[5 empty] | 2019-11-12 | 34 | 7577 | 3142 | -167 | 1 | 0 | 3309 | 3062.737 | 3062.737 | 3062.737 | 525.2267 | 780 | 200 | 1505.2267 | 37.63% | 95% | 0% | -191.0755 | 2871.6615 | -3550 | -400 | -1078.3385 | 26.96% | 32.34% | 95% | 0% | 3309 | -167
[5 empty] | 2019-11-12 | 35 | 7577.5 | 3200 | -162 | 0 | 0 | 3362 | 3145.7543 | 3145.7543 | 3145.7543 | 523.6603 | 780 | 200 | 1503.6603 | 37.59% | 95% | 0% | -185.3547 | 2960.3996 | -2750 | -200 | 10.3996 | -0.26% | 32.33% | 95% | 0% | 3362 | -162
[5 empty] | 2019-11-12 | 36 | 7578 | 3195 | -156 | 0 | 0 | 3351 | 3128.5243 | 3128.5243 | 3128.5243 | 523.6603 | 780 | 200 | 1503.6603 | 37.59% | 95% | 0% | -178.4897 | 2950.0346 | -2750 | -200 | 0.034617 | -0.0008654% | 32.33% | 95% | 0% | 3351 | -156
[5 empty] | 2019-11-12 | 37 | 7578.5 | 3155 | -152 | 0 | 0 | 3307 | 3059.6043 | 3059.6043 | 3059.6043 | 523.6603 | 780 | 200 | 1503.6603 | 37.59% | 95% | 0% | -173.913 | 2885.6912 | -2750 | -200 | -64.3088 | 1.608% | 32.33% | 95% | 0% | 3307 | -152
[5 empty] | 2019-11-12 | 38 | 7579 | 3115 | -148 | 0 | 0 | 3263 | 2990.6843 | 2990.6843 | 2990.6843 | 523.6603 | 780 | 200 | 1503.6603 | 37.59% | 95% | 0% | -169.3364 | 2821.3479 | -2750 | -200 | -128.6521 | 3.216% | 32.32% | 95% | 0% | 3263 | -148
[5 empty] | 2019-11-12 | 39 | 7579.5 | 3071 | -145 | 0 | 0 | 3216 | 2917.0651 | 2917.0651 | 2917.0651 | 523.6603 | 780 | 200 | 1503.6603 | 37.59% | 95% | 0% | -165.9039 | 2751.1612 | -2750 | -200 | -198.8388 | 4.971% | 32.31% | 95% | 0% | 3216 | -145
[5 empty] | 2019-11-12 | 40 | 7580 | 2998 | -141 | 0 | 0 | 3139 | 2796.4551 | 2796.4551 | 2796.4551 | 523.6603 | 780 | 200 | 1503.6603 | 37.59% | 95% | 0% | -161.3272 | 2635.1278 | -2750 | -200 | -314.8722 | 7.872% | 32.3% | 95% | 0% | 3139 | -141
[5 empty] | 2019-11-12 | 41 | 7580.5 | 2917 | -139 | 0 | 0 | 3056 | 2666.4468 | 2666.4468 | 2666.4468 | 523.6603 | 780 | 200 | 1503.6603 | 37.59% | 95% | 0% | -159.0389 | 2507.4079 | -2750 | -200 | -442.5921 | 11.06% | 32.27% | 95% | 0% | 3056 | -139
[5 empty] | 2019-11-12 | 42 | 7581 | 2810 | -136 | 0 | 0 | 2946 | 2494.1467 | 2494.1467 | 2494.1467 | 523.6603 | 780 | 200 | 1503.6603 | 37.59% | 95% | 0% | -155.6064 | 2338.5403 | -2750 | -200 | -611.4597 | 15.29% | 32.26% | 95% | 0% | 2946 | -136
[5 empty] | 2019-11-12 | 43 | 7581.5 | 2683 | -133 | 0 | 0 | 2816 | 2290.5194 | 2290.5194 | 2290.5194 | 522.094 | 780 | 200 | 1502.094 | 37.55% | 95% | 0% | -152.1739 | 2138.3455 | -2750 | -200 | -811.6545 | 20.29% | 32.25% | 95% | 0% | 2816 | -133
[5 empty] | 2019-11-12 | 44 | 7582 | 2513 | -130 | 0 | 0 | 2643 | 2019.5383 | 2019.5383 | 2019.5383 | 522.094 | 780 | 200 | 1502.094 | 37.55% | 95% | 0% | -148.7414 | 1870.7969 | -2750 | -200 | -1079.2031 | 26.98% | 32.24% | 95% | 0% | 2643 | -130
[5 empty] | 2019-11-12 | 45 | 7582.5 | 2348 | -126 | 0 | 0 | 2474 | 1754.8228 | 1754.8228 | 1754.8228 | 522.094 | 780 | 200 | 1502.094 | 37.55% | 95% | 0% | -144.1648 | 1610.658 | -2750 | -200 | -1339.342 | 33.48% | 32.24% | 95% | 0% | 2474 | -126
[5 empty] | 2019-11-12 | 46 | 7583 | 2217 | -122 | 0 | 0 | 2339 | 1543.3636 | 1543.3636 | 1543.3636 | 522.094 | 780 | 200 | 1502.094 | 37.55% | 95% | 0% | -139.5881 | 1403.7755 | -2750 | -200 | -1546.2245 | 38.66% | 32.22% | 95% | 0% | 2339 | -122
[5 empty] | 2019-11-12 | 47 | 7583.5 | 2073 | -114 | 0 | 0 | 2187 | 1305.2762 | 1305.2762 | 1305.2762 | 522.094 | 780 | 200 | 1502.094 | 37.55% | 95% | 0% | -130.4348 | 1174.8414 | -2750 | -200 | -1775.1586 | 44.38% | 32.22% | 95% | 0% | 2187 | -114
[5 empty] | 2019-11-12 | 48 | 7584 | 1982 | -106 | 0 | 0 | 2088 | 1150.2061 | 1150.2061 | 1150.2061 | 522.094 | 780 | 200 | 1502.094 | 37.55% | 95% | 0% | -121.2815 | 1028.9246 | -2750 | -200 | -1921.0754 | 48.03% | 32.21% | 95% | 0% | 2088 | -106
[5 empty] | 2019-11-13 | 1 | 7584.5 | 1976 | -102 | 0 | 0 | 2078 | 1134.5425 | 1134.5425 | 1134.5425 | 522.094 | 780 | 200 | 1502.094 | 37.55% | 95% | 0% | -116.7048 | 1017.8377 | -2750 | -200 | -1932.1623 | 48.3% | 32.21% | 95% | 0% | 2078 | -102
[5 empty] | 2019-11-13 | 2 | 7585 | 2023 | -97 | 0 | 0 | 2120 | 1200.3298 | 1200.3298 | 1200.3298 | 522.094 | 780 | 200 | 1502.094 | 37.55% | 95% | 0% | -110.984 | 1089.3458 | -2750 | -200 | -1860.6542 | 46.52% | 32.19% | 95% | 0% | 2120 | -97
[5 empty] | 2019-11-13 | 3 | 7585.5 | 2001 | -93 | 0 | 0 | 2094 | 1159.6043 | 1159.6043 | 1159.6043 | 522.094 | 780 | 200 | 1502.094 | 37.55% | 95% | 0% | -106.4073 | 1053.197 | -2750 | -200 | -1896.803 | 47.42% | 32.19% | 95% | 0% | 2094 | -93
[5 empty] | 2019-11-13 | 4 | 7586 | 1965 | -89 | 0 | 0 | 2054 | 1096.9497 | 1096.9497 | 1096.9497 | 522.094 | 780 | 200 | 1502.094 | 37.55% | 95% | 0% | -101.8307 | 995.119 | -2750 | -200 | -1954.881 | 48.87% | 32.16% | 95% | 0% | 2054 | -89
[5 empty] | 2019-11-13 | 5 | 7586.5 | 1941 | -86 | 0 | 0 | 2027 | 1054.6579 | 1054.6579 | 1054.6579 | 520.5276 | 780 | 200 | 1500.5276 | 37.51% | 95% | 0% | -98.3982 | 956.2597 | -2750 | -200 | -1993.7403 | 49.84% | 32.15% | 95% | 0% | 2027 | -86
[5 empty] | 2019-11-13 | 6 | 7587 | 1939 | -83 | 0 | 0 | 2022 | 1046.8261 | 1046.8261 | 1046.8261 | 520.5276 | 780 | 200 | 1500.5276 | 37.51% | 95% | 0% | -94.9657 | 951.8604 | -2750 | -200 | -1998.1396 | 49.95% | 32.12% | 95% | 0% | 2022 | -83
[5 empty] | 2019-11-13 | 7 | 7587.5 | 1925 | -79 | 0 | 0 | 2004 | 1018.6315 | 1018.6315 | 1018.6315 | 520.5276 | 780 | 200 | 1500.5276 | 37.51% | 95% | 0% | -90.389 | 928.2425 | -2750 | -200 | -2021.7575 | 50.54% | 32.11% | 95% | 0% | 2004 | -79
[5 empty] | 2019-11-13 | 8 | 7588 | 1907 | -75 | 0 | 0 | 1982 | 984.1715 | 984.1715 | 984.1715 | 520.5276 | 780 | 200 | 1500.5276 | 37.51% | 95% | 0% | -85.8124 | 898.3591 | -2750 | -200 | -2051.6409 | 51.29% | 32.09% | 95% | 0% | 1982 | -75
[5 empty] | 2019-11-13 | 9 | 7588.5 | 1904 | -72 | 0 | 0 | 1976 | 974.7733 | 974.7733 | 974.7733 | 520.5276 | 780 | 200 | 1500.5276 | 37.51% | 95% | 0% | -82.3799 | 892.3934 | -2750 | -200 | -2057.6066 | 51.44% | 32.06% | 95% | 0% | 1976 | -72
[5 empty] | 2019-11-13 | 10 | 7589 | 1927 | -68 | 0 | 0 | 1995 | 1004.5342 | 1004.5342 | 1004.5342 | 520.5276 | 780 | 200 | 1500.5276 | 37.51% | 95% | 0% | -77.8032 | 926.731 | -2750 | -200 | -2023.269 | 50.58% | 32.06% | 95% | 0% | 1995 | -68
[5 empty] | 2019-11-13 | 11 | 7589.5 | 2008 | -65 | 0 | 0 | 2073 | 1126.7106 | 1126.7106 | 1126.7106 | 520.5276 | 780 | 200 | 1500.5276 | 37.51% | 95% | 0% | -74.3707 | 1052.3399 | -2750 | -200 | -1897.6601 | 47.44% | 32.06% | 95% | 0% | 2073 | -65
[5 empty] | 2019-11-13 | 12 | 7590 | 2121 | -62 | 0 | 0 | 2183 | 1299.0107 | 1299.0107 | 1299.0107 | 520.5276 | 780 | 200 | 1500.5276 | 37.51% | 95% | 0% | -70.9382 | 1228.0725 | -2750 | -200 | -1721.9275 | 43.05% | 32.06% | 95% | 0% | 2183 | -62
[5 empty] | 2019-11-13 | 13 | 7590.5 | 2362 | -59 | 0 | 0 | 2421 | 1671.8054 | 1671.8054 | 1671.8054 | 520.5276 | 780 | 200 | 1500.5276 | 37.51% | 95% | 0% | -67.5057 | 1604.2997 | -2750 | -200 | -1345.7003 | 33.64% | 32.04% | 95% | 0% | 2421 | -59
[5 empty] | 2019-11-13 | 14 | 7591 | 2619 | -55 | 0 | 0 | 2674 | 2068.0956 | 2068.0956 | 2068.0956 | 518.9613 | 780 | 200 | 1498.9613 | 37.47% | 95% | 0% | -62.9291 | 2005.1666 | -2750 | -200 | -944.8334 | 23.62% | 32.02% | 95% | 0% | 2674 | -55
[5 empty] | 2019-11-13 | 15 | 7591.5 | 2879 | -53 | 0 | 0 | 2932 | 2472.2176 | 2472.2176 | 2472.2176 | 518.9613 | 780 | 200 | 1498.9613 | 37.47% | 95% | 0% | -60.6407 | 2411.5769 | -2750 | -200 | -538.4231 | 13.46% | 32.01% | 95% | 0% | 2932 | -53
[5 empty] | 2019-11-13 | 16 | 7592 | 2937 | -64 | 0 | 0 | 3001 | 2580.2968 | 2580.2968 | 2580.2968 | 518.9613 | 780 | 200 | 1498.9613 | 37.47% | 95% | 0% | -73.2265 | 2507.0702 | -2750 | -200 | -442.9298 | 11.07% | 31.97% | 95% | 0% | 3001 | -64
[5 empty] | 2019-11-13 | 17 | 7592.5 | 2937 | -103 | 0 | 0 | 3040 | 2641.385 | 2641.385 | 2641.385 | 518.9613 | 780 | 200 | 1498.9613 | 37.47% | 95% | 0% | -117.849 | 2523.536 | -2750 | -200 | -426.464 | 10.66% | 31.94% | 95% | 0% | 3040 | -103
[5 empty] | 2019-11-13 | 18 | 7593 | 2871 | -150 | 1 | 0 | 3021 | 2611.6241 | 2611.6241 | 2611.6241 | 518.9613 | 780 | 200 | 1498.9613 | 37.47% | 95% | 0% | -171.6247 | 2439.9994 | -3550 | -400 | -1510.0006 | 37.75% | 31.93% | 95% | 0% | 3021 | -150
[5 empty] | 2019-11-13 | 19 | 7593.5 | 2852 | -189 | 1 | 0 | 3041 | 2642.9514 | 2642.9514 | 2642.9514 | 518.9613 | 780 | 200 | 1498.9613 | 37.47% | 95% | 0% | -216.2471 | 2426.7042 | -3550 | -400 | -1523.2958 | 38.08% | 31.92% | 95% | 0% | 3041 | -189
[5 empty] | 2019-11-13 | 20 | 7594 | 2785 | -224 | 1 | 0 | 3009 | 2592.8277 | 2592.8277 | 2592.8277 | 518.9613 | 780 | 200 | 1498.9613 | 37.47% | 95% | 0% | -256.2929 | 2336.5348 | -3550 | -400 | -1613.4652 | 40.34% | 31.91% | 95% | 0% | 3009 | -224
[5 empty] | 2019-11-13 | 21 | 7594.5 | 2734 | -264 | 1 | 0 | 2998 | 2575.5977 | 2575.5977 | 2575.5977 | 518.9613 | 780 | 200 | 1498.9613 | 37.47% | 95% | 0% | -302.0595 | 2273.5382 | -3550 | -400 | -1676.4618 | 41.91% | 31.9% | 95% | 0% | 2998 | -264
[5 empty] | 2019-11-13 | 22 | 7595 | 2670 | -302 | 1 | 0 | 2972 | 2534.8722 | 2534.8722 | 2534.8722 | 518.9613 | 780 | 200 | 1498.9613 | 37.47% | 95% | 0% | -345.5378 | 2189.3345 | -3550 | -400 | -1760.6655 | 44.02% | 31.88% | 95% | 0% | 2972 | -302
[5 empty] | 2019-11-13 | 23 | 7595.5 | 2654 | -310 | 1 | 0 | 2964 | 2522.3413 | 2522.3413 | 2522.3413 | 518.9613 | 780 | 200 | 1498.9613 | 37.47% | 95% | 0% | -354.6911 | 2167.6502 | -3550 | -400 | -1782.3498 | 44.56% | 31.88% | 95% | 0% | 2964 | -310
[5 empty] | 2019-11-13 | 24 | 7596 | 2661 | -283 | 1 | 0 | 2944 | 2491.014 | 2491.014 | 2491.014 | 517.3949 | 780 | 200 | 1497.3949 | 37.43% | 95% | 0% | -323.7986 | 2167.2154 | -3550 | -400 | -1782.7846 | 44.57% | 31.84% | 95% | 0% | 2944 | -283
[5 empty] | 2019-11-13 | 25 | 7596.5 | 2723 | -276 | 1 | 0 | 2999 | 2577.1641 | 2577.1641 | 2577.1641 | 517.3949 | 780 | 200 | 1497.3949 | 37.43% | 95% | 0% | -315.7895 | 2261.3746 | -3550 | -400 | -1688.6254 | 42.22% | 31.83% | 95% | 0% | 2999 | -276
[5 empty] | 2019-11-13 | 26 | 7597 | 2758 | -265 | 1 | 0 | 3023 | 2614.7568 | 2614.7568 | 2614.7568 | 517.3949 | 780 | 200 | 1497.3949 | 37.43% | 95% | 0% | -303.2037 | 2311.5531 | -3550 | -400 | -1638.4469 | 40.96% | 31.83% | 95% | 0% | 3023 | -265
[5 empty] | 2019-11-13 | 27 | 7597.5 | 2769 | -262 | 1 | 0 | 3031 | 2627.2877 | 2627.2877 | 2627.2877 | 517.3949 | 780 | 200 | 1497.3949 | 37.43% | 95% | 0% | -299.7712 | 2327.5165 | -3550 | -400 | -1622.4835 | 40.56% | 31.83% | 95% | 0% | 3031 | -262
[5 empty] | 2019-11-13 | 28 | 7598 | 2795 | -243 | 1 | 0 | 3038 | 2638.2523 | 2638.2523 | 2638.2523 | 517.3949 | 780 | 200 | 1497.3949 | 37.43% | 95% | 0% | -278.032 | 2360.2202 | -3550 | -400 | -1589.7798 | 39.74% | 31.81% | 95% | 0% | 3038 | -243
[5 empty] | 2019-11-13 | 29 | 7598.5 | 2855 | -203 | 1 | 0 | 3058 | 2669.5796 | 2669.5796 | 2669.5796 | 517.3949 | 780 | 200 | 1497.3949 | 37.43% | 95% | 0% | -232.2654 | 2437.3141 | -3550 | -400 | -1512.6859 | 37.82% | 31.8% | 95% | 0% | 3058 | -203
[5 empty] | 2019-11-13 | 30 | 7599 | 2923 | -160 | 1 | 0 | 3083 | 2708.7387 | 2708.7387 | 2708.7387 | 517.3949 | 780 | 200 | 1497.3949 | 37.43% | 95% | 0% | -183.0664 | 2525.6723 | -3550 | -400 | -1424.3277 | 35.61% | 31.8% | 95% | 0% | 3083 | -160
[5 empty] | 2019-11-13 | 31 | 7599.5 | 3001 | -111 | 1 | 0 | 3112 | 2754.1632 | 2754.1632 | 2754.1632 | 515.8285 | 780 | 200 | 1495.8285 | 37.4% | 95% | 0% | -127.0023 | 2627.1609 | -3550 | -400 | -1322.8391 | 33.07% | 31.77% | 95% | 0% | 3112 | -111
[5 empty] | 2019-11-13 | 32 | 7600 | 3096 | -77 | 1 | 0 | 3173 | 2849.7115 | 2849.7115 | 2849.7115 | 515.8285 | 780 | 200 | 1495.8285 | 37.4% | 95% | 0% | -88.1007 | 2761.6108 | -3550 | -400 | -1188.3892 | 29.71% | 31.76% | 95% | 0% | 3173 | -77
[5 empty] | 2019-11-13 | 33 | 7600.5 | 3240 | -72 | 1 | 0 | 3312 | 3067.4361 | 3067.4361 | 3067.4361 | 515.8285 | 780 | 200 | 1495.8285 | 37.4% | 95% | 0% | -82.3799 | 2985.0562 | -3550 | -400 | -964.9438 | 24.12% | 31.76% | 95% | 0% | 3312 | -72
[5 empty] | 2019-11-13 | 34 | 7601 | 3349 | -75 | 1 | 0 | 3424 | 3242.8689 | 3242.8689 | 3242.8689 | 515.8285 | 780 | 200 | 1495.8285 | 37.4% | 95% | 0% | -85.8124 | 3157.0566 | -3550 | -400 | -792.9434 | 19.82% | 31.74% | 95% | 0% | 3424 | -75
[5 empty] | 2019-11-13 | 35 | 7601.5 | 3344 | -76 | 0 | 0 | 3420 | 3236.6035 | 3236.6035 | 3236.6035 | 515.8285 | 780 | 200 | 1495.8285 | 37.4% | 95% | 0% | -86.9565 | 3149.6469 | -2750 | -200 | 199.6469 | -4.991% | 31.73% | 95% | 0% | 3420 | -76
[5 empty] | 2019-11-13 | 36 | 7602 | 3323 | -78 | 0 | 0 | 3401 | 3206.8425 | 3206.8425 | 3206.8425 | 515.8285 | 780 | 200 | 1495.8285 | 37.4% | 95% | 0% | -89.2449 | 3117.5977 | -2750 | -200 | 167.5977 | -4.19% | 31.72% | 95% | 0% | 3401 | -78
[5 empty] | 2019-11-13 | 37 | 7602.5 | 3325 | -80 | 0 | 0 | 3405 | 3213.108 | 3213.108 | 3213.108 | 515.8285 | 780 | 200 | 1495.8285 | 37.4% | 95% | 0% | -91.5332 | 3121.5748 | -2750 | -200 | 171.5748 | -4.289% | 31.72% | 95% | 0% | 3405 | -80
[5 empty] | 2019-11-13 | 38 | 7603 | 3308 | -82 | 0 | 0 | 3390 | 3189.6125 | 3189.6125 | 3189.6125 | 514.2622 | 780 | 200 | 1494.2622 | 37.36% | 95% | 0% | -93.8215 | 3095.791 | -2750 | -200 | 145.791 | -3.645% | 31.71% | 95% | 0% | 3390 | -82
[5 empty] | 2019-11-13 | 39 | 7603.5 | 3250 | -84 | 0 | 0 | 3334 | 3101.8961 | 3101.8961 | 3101.8961 | 514.2622 | 780 | 200 | 1494.2622 | 37.36% | 95% | 0% | -96.1098 | 3005.7863 | -2750 | -200 | 55.7863 | -1.395% | 31.68% | 95% | 0% | 3334 | -84
[5 empty] | 2019-11-13 | 40 | 7604 | 3183 | -87 | 0 | 0 | 3270 | 3001.6488 | 3001.6488 | 3001.6488 | 514.2622 | 780 | 200 | 1494.2622 | 37.36% | 95% | 0% | -99.5423 | 2902.1065 | -2750 | -200 | -47.8935 | 1.197% | 31.67% | 95% | 0% | 3270 | -87
[5 empty] | 2019-11-13 | 41 | 7604.5 | 3097 | -90 | 0 | 0 | 3187 | 2871.6406 | 2871.6406 | 2871.6406 | 514.2622 | 780 | 200 | 1494.2622 | 37.36% | 95% | 0% | -102.9748 | 2768.6657 | -2750 | -200 | -181.3343 | 4.533% | 31.65% | 95% | 0% | 3187 | -90
[5 empty] | 2019-11-13 | 42 | 7605 | 2952 | -92 | 0 | 0 | 3044 | 2647.6505 | 2647.6505 | 2647.6505 | 514.2622 | 780 | 200 | 1494.2622 | 37.36% | 95% | 0% | -105.2632 | 2542.3873 | -2750 | -200 | -407.6127 | 10.19% | 31.65% | 95% | 0% | 3044 | -92
[5 empty] | 2019-11-13 | 43 | 7605.5 | 2784 | -95 | 0 | 0 | 2879 | 2389.2003 | 2389.2003 | 2389.2003 | 514.2622 | 780 | 200 | 1494.2622 | 37.36% | 95% | 0% | -108.6957 | 2280.5047 | -2750 | -200 | -669.4953 | 16.74% | 31.65% | 95% | 0% | 2879 | -95
[5 empty] | 2019-11-13 | 44 | 7606 | 2608 | -99 | 0 | 0 | 2707 | 2119.7857 | 2119.7857 | 2119.7857 | 514.2622 | 780 | 200 | 1494.2622 | 37.36% | 95% | 0% | -113.2723 | 2006.5133 | -2750 | -200 | -943.4867 | 23.59% | 31.64% | 95% | 0% | 2707 | -99
[5 empty] | 2019-11-13 | 45 | 7606.5 | 2433 | -102 | 0 | 0 | 2535 | 1850.371 | 1850.371 | 1850.371 | 514.2622 | 780 | 200 | 1494.2622 | 37.36% | 95% | 0% | -116.7048 | 1733.6662 | -2750 | -200 | -1216.3338 | 30.41% | 31.64% | 95% | 0% | 2535 | -102
[5 empty] | 2019-11-13 | 46 | 7607 | 2288 | -105 | 0 | 0 | 2393 | 1627.9472 | 1627.9472 | 1627.9472 | 514.2622 | 780 | 200 | 1494.2622 | 37.36% | 95% | 0% | -120.1373 | 1507.8099 | -2750 | -200 | -1442.1901 | 36.05% | 31.63% | 95% | 0% | 2393 | -105
[5 empty] | 2019-11-13 | 47 | 7607.5 | 2117 | -110 | 0 | 0 | 2227 | 1367.9308 | 1367.9308 | 1367.9308 | 512.6958 | 780 | 200 | 1492.6958 | 37.32% | 95% | 0% | -125.8581 | 1242.0726 | -2750 | -200 | -1707.9274 | 42.7% | 31.63% | 95% | 0% | 2227 | -110
[5 empty] | 2019-11-13 | 48 | 7608 | 2013 | -114 | 0 | 0 | 2127 | 1211.2943 | 1211.2943 | 1211.2943 | 512.6958 | 780 | 200 | 1492.6958 | 37.32% | 95% | 0% | -130.4348 | 1080.8595 | -2750 | -200 | -1869.1405 | 46.73% | 31.62% | 95% | 0% | 2127 | -114
[5 empty] | 2019-11-14 | 1 | 7608.5 | 1962 | -116 | 0 | 0 | 2078 | 1134.5425 | 1134.5425 | 1134.5425 | 512.6958 | 780 | 200 | 1492.6958 | 37.32% | 95% | 0% | -132.7231 | 1001.8193 | -2750 | -200 | -1948.1807 | 48.7% | 31.62% | 95% | 0% | 2078 | -116
[5 empty] | 2019-11-14 | 2 | 7609 | 1973 | -118 | 0 | 0 | 2091 | 1154.9052 | 1154.9052 | 1154.9052 | 512.6958 | 780 | 200 | 1492.6958 | 37.32% | 95% | 0% | -135.0114 | 1019.8938 | -2750 | -200 | -1930.1062 | 48.25% | 31.6% | 95% | 0% | 2091 | -118
[5 empty] | 2019-11-14 | 3 | 7609.5 | 1948 | -120 | 0 | 0 | 2068 | 1118.8788 | 1118.8788 | 1118.8788 | 512.6958 | 780 | 200 | 1492.6958 | 37.32% | 95% | 0% | -137.2998 | 981.579 | -2750 | -200 | -1968.421 | 49.21% | 31.6% | 95% | 0% | 2068 | -120
[5 empty] | 2019-11-14 | 4 | 7610 | 1900 | -122 | 0 | 0 | 2022 | 1046.8261 | 1046.8261 | 1046.8261 | 512.6958 | 780 | 200 | 1492.6958 | 37.32% | 95% | 0% | -139.5881 | 907.238 | -2750 | -200 | -2042.762 | 51.07% | 31.59% | 95% | 0% | 2022 | -122
[5 empty] | 2019-11-14 | 5 | 7610.5 | 1859 | -124 | 0 | 0 | 1983 | 985.7378 | 985.7378 | 985.7378 | 512.6958 | 780 | 200 | 1492.6958 | 37.32% | 95% | 0% | -141.8764 | 843.8614 | -2750 | -200 | -2106.1386 | 52.65% | 31.56% | 95% | 0% | 1983 | -124
[5 empty] | 2019-11-14 | 6 | 7611 | 1839 | -127 | 0 | 0 | 1966 | 959.1096 | 959.1096 | 959.1096 | 511.1294 | 780 | 200 | 1491.1294 | 37.28% | 95% | 0% | -145.3089 | 813.8007 | -2750 | -200 | -2136.1993 | 53.4% | 31.56% | 95% | 0% | 1966 | -127
[5 empty] | 2019-11-14 | 7 | 7611.5 | 1809 | -129 | 0 | 0 | 1938 | 915.2514 | 915.2514 | 915.2514 | 511.1294 | 780 | 200 | 1491.1294 | 37.28% | 95% | 0% | -147.5973 | 767.6542 | -2750 | -200 | -2182.3458 | 54.56% | 31.56% | 95% | 0% | 1938 | -129
[5 empty] | 2019-11-14 | 8 | 7612 | 1775 | -132 | 0 | 0 | 1907 | 866.6941 | 866.6941 | 866.6941 | 511.1294 | 780 | 200 | 1491.1294 | 37.28% | 95% | 0% | -151.0297 | 715.6644 | -2750 | -200 | -2234.3356 | 55.86% | 31.54% | 95% | 0% | 1907 | -132
[5 empty] | 2019-11-14 | 9 | 7612.5 | 1754 | -134 | 0 | 0 | 1888 | 836.9332 | 836.9332 | 836.9332 | 511.1294 | 780 | 200 | 1491.1294 | 37.28% | 95% | 0% | -153.3181 | 683.6151 | -2750 | -200 | -2266.3849 | 56.66% | 31.54% | 95% | 0% | 1888 | -134
[5 empty] | 2019-11-14 | 10 | 7613 | 1762 | -135 | 0 | 0 | 1897 | 851.0305 | 851.0305 | 851.0305 | 511.1294 | 780 | 200 | 1491.1294 | 37.28% | 95% | 0% | -154.4622 | 696.5683 | -2750 | -200 | -2253.4317 | 56.34% | 31.54% | 95% | 0% | 1897 | -135
[5 empty] | 2019-11-14 | 11 | 7613.5 | 1821 | -136 | 0 | 0 | 1957 | 945.0124 | 945.0124 | 945.0124 | 511.1294 | 780 | 200 | 1491.1294 | 37.28% | 95% | 0% | -155.6064 | 789.406 | -2750 | -200 | -2160.594 | 54.01% | 31.53% | 95% | 0% | 1957 | -136
[5 empty] | 2019-11-14 | 12 | 7614 | 1937 | -136 | 0 | 0 | 2073 | 1126.7106 | 1126.7106 | 1126.7106 | 511.1294 | 780 | 200 | 1491.1294 | 37.28% | 95% | 0% | -155.6064 | 971.1042 | -2750 | -200 | -1978.8958 | 49.47% | 31.53% | 95% | 0% | 2073 | -136
[5 empty] | 2019-11-14 | 13 | 7614.5 | 2150 | -138 | 0 | 0 | 2288 | 1463.479 | 1463.479 | 1463.479 | 511.1294 | 780 | 200 | 1491.1294 | 37.28% | 95% | 0% | -157.8947 | 1305.5842 | -2750 | -200 | -1644.4158 | 41.11% | 31.53% | 95% | 0% | 2288 | -138
[5 empty] | 2019-11-14 | 14 | 7615 | 2416 | -139 | 0 | 0 | 2555 | 1881.6983 | 1881.6983 | 1881.6983 | 511.1294 | 780 | 200 | 1491.1294 | 37.28% | 95% | 0% | -159.0389 | 1722.6594 | -2750 | -200 | -1227.3406 | 30.68% | 31.53% | 95% | 0% | 2555 | -139
[5 empty] | 2019-11-14 | 15 | 7615.5 | 2685 | -140 | 0 | 0 | 2825 | 2304.6167 | 2304.6167 | 2304.6167 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -160.1831 | 2144.4336 | -2750 | -200 | -805.5664 | 20.14% | 31.52% | 95% | 0% | 2825 | -140
[5 empty] | 2019-11-14 | 16 | 7616 | 2800 | -142 | 0 | 0 | 2942 | 2487.8813 | 2487.8813 | 2487.8813 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -162.4714 | 2325.4099 | -2750 | -200 | -624.5901 | 15.61% | 31.51% | 95% | 0% | 2942 | -142
[5 empty] | 2019-11-14 | 17 | 7616.5 | 2867 | -153 | 0 | 0 | 3020 | 2610.0577 | 2610.0577 | 2610.0577 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -175.0572 | 2435.0005 | -2750 | -200 | -514.9995 | 12.87% | 31.5% | 95% | 0% | 3020 | -153
[5 empty] | 2019-11-14 | 18 | 7617 | 2861 | -168 | 0 | 0 | 3029 | 2624.155 | 2624.155 | 2624.155 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -192.2197 | 2431.9353 | -2750 | -200 | -518.0647 | 12.95% | 31.49% | 95% | 0% | 3029 | -168
[5 empty] | 2019-11-14 | 19 | 7617.5 | 2901 | -185 | 1 | 0 | 3086 | 2713.4378 | 2713.4378 | 2713.4378 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -211.6705 | 2501.7673 | -3550 | -400 | -1448.2327 | 36.21% | 31.49% | 95% | 0% | 3086 | -185
[5 empty] | 2019-11-14 | 20 | 7618 | 2896 | -210 | 1 | 0 | 3106 | 2744.765 | 2744.765 | 2744.765 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -240.2746 | 2504.4904 | -3550 | -400 | -1445.5096 | 36.14% | 31.47% | 95% | 0% | 3106 | -210
[5 empty] | 2019-11-14 | 21 | 7618.5 | 2850 | -243 | 1 | 0 | 3093 | 2724.4023 | 2724.4023 | 2724.4023 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -278.032 | 2446.3703 | -3550 | -400 | -1503.6297 | 37.59% | 31.47% | 95% | 0% | 3093 | -243
[5 empty] | 2019-11-14 | 22 | 7619 | 2844 | -248 | 1 | 0 | 3092 | 2722.8359 | 2722.8359 | 2722.8359 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -283.7529 | 2439.0831 | -3550 | -400 | -1510.9169 | 37.77% | 31.47% | 95% | 0% | 3092 | -248
[5 empty] | 2019-11-14 | 23 | 7619.5 | 2841 | -254 | 1 | 0 | 3095 | 2727.535 | 2727.535 | 2727.535 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -290.6178 | 2436.9172 | -3550 | -400 | -1513.0828 | 37.83% | 31.47% | 95% | 0% | 3095 | -254
[5 empty] | 2019-11-14 | 24 | 7620 | 2820 | -270 | 1 | 0 | 3090 | 2719.7032 | 2719.7032 | 2719.7032 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -308.9245 | 2410.7787 | -3550 | -400 | -1539.2213 | 38.48% | 31.45% | 95% | 0% | 3090 | -270
[5 empty] | 2019-11-14 | 25 | 7620.5 | 2844 | -267 | 1 | 0 | 3111 | 2752.5969 | 2752.5969 | 2752.5969 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -305.492 | 2447.1049 | -3550 | -400 | -1502.8951 | 37.57% | 31.44% | 95% | 0% | 3111 | -267
[5 empty] | 2019-11-14 | 26 | 7621 | 2818 | -270 | 1 | 0 | 3088 | 2716.5705 | 2716.5705 | 2716.5705 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -308.9245 | 2407.646 | -3550 | -400 | -1542.354 | 38.56% | 31.44% | 95% | 0% | 3088 | -270
[5 empty] | 2019-11-14 | 27 | 7621.5 | 2817 | -268 | 1 | 0 | 3085 | 2711.8714 | 2711.8714 | 2711.8714 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -306.6362 | 2405.2352 | -3550 | -400 | -1544.7648 | 38.62% | 31.44% | 95% | 0% | 3085 | -268
[5 empty] | 2019-11-14 | 28 | 7622 | 2814 | -254 | 1 | 0 | 3068 | 2685.2432 | 2685.2432 | 2685.2432 | 509.5631 | 780 | 200 | 1489.5631 | 37.24% | 95% | 0% | -290.6178 | 2394.6253 | -3550 | -400 | -1555.3747 | 38.88% | 31.44% | 95% | 0% | 3068 | -254
[5 empty] | 2019-11-14 | 29 | 7622.5 | 2828 | -236 | 1 | 0 | 3064 | 2678.9777 | 2678.9777 | 2678.9777 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -270.0229 | 2408.9549 | -3550 | -400 | -1541.0451 | 38.53% | 31.43% | 95% | 0% | 3064 | -236
[5 empty] | 2019-11-14 | 30 | 7623 | 2869 | -215 | 1 | 0 | 3084 | 2710.305 | 2710.305 | 2710.305 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -245.9954 | 2464.3096 | -3550 | -400 | -1485.6904 | 37.14% | 31.41% | 95% | 0% | 3084 | -215
[5 empty] | 2019-11-14 | 31 | 7623.5 | 2916 | -186 | 1 | 0 | 3102 | 2738.4996 | 2738.4996 | 2738.4996 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -212.8146 | 2525.6849 | -3550 | -400 | -1424.3151 | 35.61% | 31.41% | 95% | 0% | 3102 | -186
[5 empty] | 2019-11-14 | 32 | 7624 | 2999 | -167 | 1 | 0 | 3166 | 2838.7469 | 2838.7469 | 2838.7469 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -191.0755 | 2647.6714 | -3550 | -400 | -1302.3286 | 32.56% | 31.41% | 95% | 0% | 3166 | -167
[5 empty] | 2019-11-14 | 33 | 7624.5 | 3123 | -160 | 1 | 0 | 3283 | 3022.0115 | 3022.0115 | 3022.0115 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -183.0664 | 2838.9452 | -3550 | -400 | -1111.0548 | 27.78% | 31.41% | 95% | 0% | 3283 | -160
[5 empty] | 2019-11-14 | 34 | 7625 | 3212 | -158 | 1 | 0 | 3370 | 3158.2852 | 3158.2852 | 3158.2852 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -180.778 | 2977.5072 | -3550 | -400 | -972.4928 | 24.31% | 31.4% | 95% | 0% | 3370 | -158
[5 empty] | 2019-11-14 | 35 | 7625.5 | 3240 | -156 | 1 | 0 | 3396 | 3199.0107 | 3199.0107 | 3199.0107 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -178.4897 | 3020.521 | -3550 | -400 | -929.479 | 23.24% | 31.37% | 95% | 0% | 3396 | -156
[5 empty] | 2019-11-14 | 36 | 7626 | 3229 | -153 | 0 | 0 | 3382 | 3177.0816 | 3177.0816 | 3177.0816 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -175.0572 | 3002.0244 | -2750 | -200 | 52.0244 | -1.301% | 31.37% | 95% | 0% | 3382 | -153
[5 empty] | 2019-11-14 | 37 | 7626.5 | 3216 | -151 | 0 | 0 | 3367 | 3153.5862 | 3153.5862 | 3153.5862 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -172.7689 | 2980.8173 | -2750 | -200 | 30.8173 | -0.7704% | 31.36% | 95% | 0% | 3367 | -151
[5 empty] | 2019-11-14 | 38 | 7627 | 3183 | -150 | 0 | 0 | 3333 | 3100.3298 | 3100.3298 | 3100.3298 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -171.6247 | 2928.705 | -2750 | -200 | -21.295 | 0.5324% | 31.33% | 95% | 0% | 3333 | -150
[5 empty] | 2019-11-14 | 39 | 7627.5 | 3162 | -147 | 0 | 0 | 3309 | 3062.737 | 3062.737 | 3062.737 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -168.1922 | 2894.5448 | -2750 | -200 | -55.4552 | 1.386% | 31.32% | 95% | 0% | 3309 | -147
[5 empty] | 2019-11-14 | 40 | 7628 | 3074 | -144 | 0 | 0 | 3218 | 2920.1979 | 2920.1979 | 2920.1979 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -164.7597 | 2755.4381 | -2750 | -200 | -194.5619 | 4.864% | 31.3% | 95% | 0% | 3218 | -144
[5 empty] | 2019-11-14 | 41 | 7628.5 | 2968 | -142 | 0 | 0 | 3110 | 2751.0305 | 2751.0305 | 2751.0305 | 507.9967 | 780 | 200 | 1487.9967 | 37.2% | 95% | 0% | -162.4714 | 2588.5591 | -2750 | -200 | -361.4409 | 9.036% | 31.29% | 95% | 0% | 3110 | -142
[5 empty] | 2019-11-14 | 42 | 7629 | 2854 | -141 | 0 | 0 | 2995 | 2570.8986 | 2570.8986 | 2570.8986 | 506.4303 | 780 | 200 | 1486.4303 | 37.16% | 95% | 0% | -161.3272 | 2409.5714 | -2750 | -200 | -540.4286 | 13.51% | 31.29% | 95% | 0% | 2995 | -141
[5 empty] | 2019-11-14 | 43 | 7629.5 | 2721 | -138 | 0 | 0 | 2859 | 2357.873 | 2357.873 | 2357.873 | 506.4303 | 780 | 200 | 1486.4303 | 37.16% | 95% | 0% | -157.8947 | 2199.9783 | -2750 | -200 | -750.0217 | 18.75% | 31.25% | 95% | 0% | 2859 | -138
[5 empty] | 2019-11-14 | 44 | 7630 | 2567 | -136 | 0 | 0 | 2703 | 2113.5202 | 2113.5202 | 2113.5202 | 506.4303 | 780 | 200 | 1486.4303 | 37.16% | 95% | 0% | -155.6064 | 1957.9138 | -2750 | -200 | -992.0862 | 24.8% | 31.24% | 95% | 0% | 2703 | -136
[5 empty] | 2019-11-14 | 45 | 7630.5 | 2398 | -134 | 0 | 0 | 2532 | 1845.6719 | 1845.6719 | 1845.6719 | 506.4303 | 780 | 200 | 1486.4303 | 37.16% | 95% | 0% | -153.3181 | 1692.3538 | -2750 | -200 | -1257.6462 | 31.44% | 31.23% | 95% | 0% | 2532 | -134
[5 empty] | 2019-11-14 | 46 | 7631 | 2241 | -132 | 0 | 0 | 2373 | 1596.62 | 1596.62 | 1596.62 | 506.4303 | 780 | 200 | 1486.4303 | 37.16% | 95% | 0% | -151.0297 | 1445.5902 | -2750 | -200 | -1504.4098 | 37.61% | 31.22% | 95% | 0% | 2373 | -132
[5 empty] | 2019-11-14 | 47 | 7631.5 | 2090 | -128 | 0 | 0 | 2218 | 1353.8335 | 1353.8335 | 1353.8335 | 506.4303 | 780 | 200 | 1486.4303 | 37.16% | 95% | 0% | -146.4531 | 1207.3804 | -2750 | -200 | -1742.6196 | 43.57% | 31.21% | 95% | 0% | 2218 | -128
[5 empty] | 2019-11-14 | 48 | 7632 | 2005 | -124 | 0 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 506.4303 | 780 | 200 | 1486.4303 | 37.16% | 95% | 0% | -141.8764 | 1072.5506 | -2750 | -200 | -1877.4494 | 46.94% | 31.2% | 95% | 0% | 2129 | -124
[5 empty] | 2019-11-15 | 1 | 7632.5 | 1977 | -125 | 0 | 0 | 2102 | 1172.1352 | 1172.1352 | 1172.1352 | 506.4303 | 780 | 200 | 1486.4303 | 37.16% | 95% | 0% | -143.0206 | 1029.1146 | -2750 | -200 | -1920.8854 | 48.02% | 31.18% | 95% | 0% | 2102 | -125
[5 empty] | 2019-11-15 | 2 | 7633 | 2000 | -125 | 0 | 0 | 2125 | 1208.1616 | 1208.1616 | 1208.1616 | 506.4303 | 780 | 200 | 1486.4303 | 37.16% | 95% | 0% | -143.0206 | 1065.141 | -2750 | -200 | -1884.859 | 47.12% | 31.18% | 95% | 0% | 2125 | -125
[5 empty] | 2019-11-15 | 3 | 7633.5 | 1968 | -124 | 0 | 0 | 2092 | 1156.4716 | 1156.4716 | 1156.4716 | 506.4303 | 780 | 200 | 1486.4303 | 37.16% | 95% | 0% | -141.8764 | 1014.5951 | -2750 | -200 | -1935.4049 | 48.39% | 31.18% | 95% | 0% | 2092 | -124
[5 empty] | 2019-11-15 | 4 | 7634 | 1915 | -123 | 0 | 0 | 2038 | 1071.8879 | 1071.8879 | 1071.8879 | 504.864 | 780 | 200 | 1484.864 | 37.12% | 95% | 0% | -140.7323 | 931.1556 | -2750 | -200 | -2018.8444 | 50.47% | 31.18% | 95% | 0% | 2038 | -123
[5 empty] | 2019-11-15 | 5 | 7634.5 | 1859 | -125 | 0 | 0 | 1984 | 987.3042 | 987.3042 | 987.3042 | 504.864 | 780 | 200 | 1484.864 | 37.12% | 95% | 0% | -143.0206 | 844.2836 | -2750 | -200 | -2105.7164 | 52.64% | 31.17% | 95% | 0% | 1984 | -125
[5 empty] | 2019-11-15 | 6 | 7635 | 1854 | -127 | 0 | 0 | 1981 | 982.6051 | 982.6051 | 982.6051 | 504.864 | 780 | 200 | 1484.864 | 37.12% | 95% | 0% | -145.3089 | 837.2962 | -2750 | -200 | -2112.7038 | 52.82% | 31.16% | 95% | 0% | 1981 | -127
[5 empty] | 2019-11-15 | 7 | 7635.5 | 1821 | -128 | 0 | 0 | 1949 | 932.4815 | 932.4815 | 932.4815 | 504.864 | 780 | 200 | 1484.864 | 37.12% | 95% | 0% | -146.4531 | 786.0284 | -2750 | -200 | -2163.9716 | 54.1% | 31.15% | 95% | 0% | 1949 | -128
[5 empty] | 2019-11-15 | 8 | 7636 | 1783 | -130 | 0 | 0 | 1913 | 876.0923 | 876.0923 | 876.0923 | 504.864 | 780 | 200 | 1484.864 | 37.12% | 95% | 0% | -148.7414 | 727.3509 | -2750 | -200 | -2222.6491 | 55.57% | 31.15% | 95% | 0% | 1913 | -130
[5 empty] | 2019-11-15 | 9 | 7636.5 | 1770 | -130 | 0 | 0 | 1900 | 855.7296 | 855.7296 | 855.7296 | 504.864 | 780 | 200 | 1484.864 | 37.12% | 95% | 0% | -148.7414 | 706.9882 | -2750 | -200 | -2243.0118 | 56.08% | 31.14% | 95% | 0% | 1900 | -130
[5 empty] | 2019-11-15 | 10 | 7637 | 1790 | -130 | 0 | 0 | 1920 | 887.0569 | 887.0569 | 887.0569 | 504.864 | 780 | 200 | 1484.864 | 37.12% | 95% | 0% | -148.7414 | 738.3155 | -2750 | -200 | -2211.6845 | 55.29% | 31.13% | 95% | 0% | 1920 | -130
[5 empty] | 2019-11-15 | 11 | 7637.5 | 1863 | -130 | 0 | 0 | 1993 | 1001.4015 | 1001.4015 | 1001.4015 | 503.2976 | 780 | 200 | 1483.2976 | 37.08% | 95% | 0% | -148.7414 | 852.6601 | -2750 | -200 | -2097.3399 | 52.43% | 31.13% | 95% | 0% | 1993 | -130
[5 empty] | 2019-11-15 | 12 | 7638 | 1959 | -130 | 0 | 0 | 2089 | 1151.7725 | 1151.7725 | 1151.7725 | 503.2976 | 780 | 200 | 1483.2976 | 37.08% | 95% | 0% | -148.7414 | 1003.031 | -2750 | -200 | -1946.969 | 48.67% | 31.12% | 95% | 0% | 2089 | -130
[5 empty] | 2019-11-15 | 13 | 7638.5 | 2205 | -131 | 0 | 0 | 2336 | 1538.6645 | 1538.6645 | 1538.6645 | 503.2976 | 780 | 200 | 1483.2976 | 37.08% | 95% | 0% | -149.8856 | 1388.7789 | -2750 | -200 | -1561.2211 | 39.03% | 31.11% | 95% | 0% | 2336 | -131
[5 empty] | 2019-11-15 | 14 | 7639 | 2451 | -131 | 0 | 0 | 2582 | 1923.9901 | 1923.9901 | 1923.9901 | 503.2976 | 780 | 200 | 1483.2976 | 37.08% | 95% | 0% | -149.8856 | 1774.1045 | -2750 | -200 | -1175.8955 | 29.4% | 31.1% | 95% | 0% | 2582 | -131
[5 empty] | 2019-11-15 | 15 | 7639.5 | 2714 | -130 | 0 | 0 | 2844 | 2334.3776 | 2334.3776 | 2334.3776 | 503.2976 | 780 | 200 | 1483.2976 | 37.08% | 95% | 0% | -148.7414 | 2185.6362 | -2750 | -200 | -764.3638 | 19.11% | 31.09% | 95% | 0% | 2844 | -130
[5 empty] | 2019-11-15 | 16 | 7640 | 2855 | -130 | 0 | 0 | 2985 | 2555.235 | 2555.235 | 2555.235 | 503.2976 | 780 | 200 | 1483.2976 | 37.08% | 95% | 0% | -148.7414 | 2406.4935 | -2750 | -200 | -543.5065 | 13.59% | 31.08% | 95% | 0% | 2985 | -130
[5 empty] | 2019-11-15 | 17 | 7640.5 | 2896 | -140 | 0 | 0 | 3036 | 2635.1195 | 2635.1195 | 2635.1195 | 501.7312 | 780 | 200 | 1481.7312 | 37.04% | 95% | 0% | -160.1831 | 2474.9365 | -2750 | -200 | -475.0635 | 11.88% | 31.07% | 95% | 0% | 3036 | -140
[5 empty] | 2019-11-15 | 18 | 7641 | 2877 | -161 | 0 | 0 | 3038 | 2638.2523 | 2638.2523 | 2638.2523 | 501.7312 | 780 | 200 | 1481.7312 | 37.04% | 95% | 0% | -184.2105 | 2454.0417 | -2750 | -200 | -495.9583 | 12.4% | 31.06% | 95% | 0% | 3038 | -161
[5 empty] | 2019-11-15 | 19 | 7641.5 | 2881 | -186 | 1 | 0 | 3067 | 2683.6768 | 2683.6768 | 2683.6768 | 501.7312 | 780 | 200 | 1481.7312 | 37.04% | 95% | 0% | -212.8146 | 2470.8622 | -3550 | -400 | -1479.1378 | 36.98% | 31.03% | 95% | 0% | 3067 | -186
[5 empty] | 2019-11-15 | 20 | 7642 | 2868 | -208 | 1 | 0 | 3076 | 2697.7741 | 2697.7741 | 2697.7741 | 501.7312 | 780 | 200 | 1481.7312 | 37.04% | 95% | 0% | -237.9863 | 2459.7878 | -3550 | -400 | -1490.2122 | 37.26% | 31.03% | 95% | 0% | 3076 | -208
[5 empty] | 2019-11-15 | 21 | 7642.5 | 2842 | -225 | 1 | 0 | 3067 | 2683.6768 | 2683.6768 | 2683.6768 | 501.7312 | 780 | 200 | 1481.7312 | 37.04% | 95% | 0% | -257.4371 | 2426.2398 | -3550 | -400 | -1523.7602 | 38.09% | 31.03% | 95% | 0% | 3067 | -225
[5 empty] | 2019-11-15 | 22 | 7643 | 2844 | -227 | 1 | 0 | 3071 | 2689.9423 | 2689.9423 | 2689.9423 | 501.7312 | 780 | 200 | 1481.7312 | 37.04% | 95% | 0% | -259.7254 | 2430.2169 | -3550 | -400 | -1519.7831 | 37.99% | 31.01% | 95% | 0% | 3071 | -227
[5 empty] | 2019-11-15 | 23 | 7643.5 | 2840 | -232 | 1 | 0 | 3072 | 2691.5087 | 2691.5087 | 2691.5087 | 501.7312 | 780 | 200 | 1481.7312 | 37.04% | 95% | 0% | -265.4462 | 2426.0624 | -3550 | -400 | -1523.9376 | 38.1% | 31.01% | 95% | 0% | 3072 | -232
[5 empty] | 2019-11-15 | 24 | 7644 | 2814 | -239 | 1 | 0 | 3053 | 2661.7477 | 2661.7477 | 2661.7477 | 501.7312 | 780 | 200 | 1481.7312 | 37.04% | 95% | 0% | -273.4554 | 2388.2924 | -3550 | -400 | -1561.7076 | 39.04% | 31% | 95% | 0% | 3053 | -239
[5 empty] | 2019-11-15 | 25 | 7644.5 | 2815 | -244 | 1 | 0 | 3059 | 2671.1459 | 2671.1459 | 2671.1459 | 500.1649 | 780 | 200 | 1480.1649 | 37% | 95% | 0% | -279.1762 | 2391.9697 | -3550 | -400 | -1558.0303 | 38.95% | 30.97% | 95% | 0% | 3059 | -244
[5 empty] | 2019-11-15 | 26 | 7645 | 2785 | -249 | 1 | 0 | 3034 | 2631.9868 | 2631.9868 | 2631.9868 | 500.1649 | 780 | 200 | 1480.1649 | 37% | 95% | 0% | -284.897 | 2347.0898 | -3550 | -400 | -1602.9102 | 40.07% | 30.96% | 95% | 0% | 3034 | -249
[5 empty] | 2019-11-15 | 27 | 7645.5 | 2798 | -222 | 1 | 0 | 3020 | 2610.0577 | 2610.0577 | 2610.0577 | 500.1649 | 780 | 200 | 1480.1649 | 37% | 95% | 0% | -254.0046 | 2356.0531 | -3550 | -400 | -1593.9469 | 39.85% | 30.96% | 95% | 0% | 3020 | -222
[5 empty] | 2019-11-15 | 28 | 7646 | 2797 | -211 | 1 | 0 | 3008 | 2591.2613 | 2591.2613 | 2591.2613 | 500.1649 | 780 | 200 | 1480.1649 | 37% | 95% | 0% | -241.4188 | 2349.8426 | -3550 | -400 | -1600.1574 | 40% | 30.95% | 95% | 0% | 3008 | -211
[5 empty] | 2019-11-15 | 29 | 7646.5 | 2819 | -190 | 1 | 0 | 3009 | 2592.8277 | 2592.8277 | 2592.8277 | 500.1649 | 780 | 200 | 1480.1649 | 37% | 95% | 0% | -217.3913 | 2375.4364 | -3550 | -400 | -1574.5636 | 39.36% | 30.94% | 95% | 0% | 3009 | -190
[5 empty] | 2019-11-15 | 30 | 7647 | 2824 | -186 | 1 | 0 | 3010 | 2594.3941 | 2594.3941 | 2594.3941 | 500.1649 | 780 | 200 | 1480.1649 | 37% | 95% | 0% | -212.8146 | 2381.5794 | -3550 | -400 | -1568.4206 | 39.21% | 30.93% | 95% | 0% | 3010 | -186
[5 empty] | 2019-11-15 | 31 | 7647.5 | 2872 | -166 | 1 | 0 | 3038 | 2638.2523 | 2638.2523 | 2638.2523 | 500.1649 | 780 | 200 | 1480.1649 | 37% | 95% | 0% | -189.9314 | 2448.3209 | -3550 | -400 | -1501.6791 | 37.54% | 30.93% | 95% | 0% | 3038 | -166
[5 empty] | 2019-11-15 | 32 | 7648 | 2936 | -150 | 1 | 0 | 3086 | 2713.4378 | 2713.4378 | 2713.4378 | 500.1649 | 780 | 200 | 1480.1649 | 37% | 95% | 0% | -171.6247 | 2541.813 | -3550 | -400 | -1408.187 | 35.2% | 30.92% | 95% | 0% | 3086 | -150
[5 empty] | 2019-11-15 | 33 | 7648.5 | 3039 | -145 | 1 | 0 | 3184 | 2866.9415 | 2866.9415 | 2866.9415 | 500.1649 | 780 | 200 | 1480.1649 | 37% | 95% | 0% | -165.9039 | 2701.0376 | -3550 | -400 | -1248.9624 | 31.22% | 30.91% | 95% | 0% | 3184 | -145
[5 empty] | 2019-11-15 | 34 | 7649 | 3151 | -144 | 0 | 0 | 3295 | 3040.8079 | 3040.8079 | 3040.8079 | 500.1649 | 780 | 200 | 1480.1649 | 37% | 95% | 0% | -164.7597 | 2876.0482 | -2750 | -200 | -73.9518 | 1.849% | 30.91% | 95% | 0% | 3295 | -144
[5 empty] | 2019-11-15 | 35 | 7649.5 | 3187 | -143 | 0 | 0 | 3330 | 3095.6307 | 3095.6307 | 3095.6307 | 500.1649 | 780 | 200 | 1480.1649 | 37% | 95% | 0% | -163.6156 | 2932.0151 | -2750 | -200 | -17.9849 | 0.4496% | 30.87% | 95% | 0% | 3330 | -143
[5 empty] | 2019-11-15 | 36 | 7650 | 3158 | -142 | 0 | 0 | 3300 | 3048.6397 | 3048.6397 | 3048.6397 | 498.5985 | 780 | 200 | 1478.5985 | 36.96% | 95% | 0% | -162.4714 | 2886.1683 | -2750 | -200 | -63.8317 | 1.596% | 30.87% | 95% | 0% | 3300 | -142
[5 empty] | 2019-11-15 | 37 | 7650.5 | 3120 | -142 | 0 | 0 | 3262 | 2989.1179 | 2989.1179 | 2989.1179 | 498.5985 | 780 | 200 | 1478.5985 | 36.96% | 95% | 0% | -162.4714 | 2826.6465 | -2750 | -200 | -123.3535 | 3.084% | 30.87% | 95% | 0% | 3262 | -142
[5 empty] | 2019-11-15 | 38 | 7651 | 3052 | -141 | 0 | 0 | 3193 | 2881.0387 | 2881.0387 | 2881.0387 | 498.5985 | 780 | 200 | 1478.5985 | 36.96% | 95% | 0% | -161.3272 | 2719.7115 | -2750 | -200 | -230.2885 | 5.757% | 30.86% | 95% | 0% | 3193 | -141
[5 empty] | 2019-11-15 | 39 | 7651.5 | 2975 | -139 | 0 | 0 | 3114 | 2757.296 | 2757.296 | 2757.296 | 498.5985 | 780 | 200 | 1478.5985 | 36.96% | 95% | 0% | -159.0389 | 2598.2571 | -2750 | -200 | -351.7429 | 8.794% | 30.85% | 95% | 0% | 3114 | -139
[5 empty] | 2019-11-15 | 40 | 7652 | 2901 | -137 | 0 | 0 | 3038 | 2638.2523 | 2638.2523 | 2638.2523 | 498.5985 | 780 | 200 | 1478.5985 | 36.96% | 95% | 0% | -156.7506 | 2481.5017 | -2750 | -200 | -468.4983 | 11.71% | 30.84% | 95% | 0% | 3038 | -137
[5 empty] | 2019-11-15 | 41 | 7652.5 | 2793 | -135 | 0 | 0 | 2928 | 2465.9522 | 2465.9522 | 2465.9522 | 498.5985 | 780 | 200 | 1478.5985 | 36.96% | 95% | 0% | -154.4622 | 2311.4899 | -2750 | -200 | -638.5101 | 15.96% | 30.84% | 95% | 0% | 2928 | -135
[5 empty] | 2019-11-15 | 42 | 7653 | 2690 | -133 | 0 | 0 | 2823 | 2301.4839 | 2301.4839 | 2301.4839 | 497.0322 | 780 | 200 | 1477.0322 | 36.93% | 95% | 0% | -152.1739 | 2149.31 | -2750 | -200 | -800.69 | 20.02% | 30.83% | 95% | 0% | 2823 | -133
[5 empty] | 2019-11-15 | 43 | 7653.5 | 2566 | -131 | 0 | 0 | 2697 | 2104.122 | 2104.122 | 2104.122 | 497.0322 | 780 | 200 | 1477.0322 | 36.93% | 95% | 0% | -149.8856 | 1954.2364 | -2750 | -200 | -995.7636 | 24.89% | 30.82% | 95% | 0% | 2697 | -131
[5 empty] | 2019-11-15 | 44 | 7654 | 2448 | -129 | 0 | 0 | 2577 | 1916.1583 | 1916.1583 | 1916.1583 | 497.0322 | 780 | 200 | 1477.0322 | 36.93% | 95% | 0% | -147.5973 | 1768.561 | -2750 | -200 | -1181.439 | 29.54% | 30.81% | 95% | 0% | 2577 | -129
[5 empty] | 2019-11-15 | 45 | 7654.5 | 2303 | -125 | 0 | 0 | 2428 | 1682.77 | 1682.77 | 1682.77 | 497.0322 | 780 | 200 | 1477.0322 | 36.93% | 95% | 0% | -143.0206 | 1539.7494 | -2750 | -200 | -1410.2506 | 35.26% | 30.81% | 95% | 0% | 2428 | -125
[5 empty] | 2019-11-15 | 46 | 7655 | 2195 | -122 | 0 | 0 | 2317 | 1508.9035 | 1508.9035 | 1508.9035 | 497.0322 | 780 | 200 | 1477.0322 | 36.93% | 95% | 0% | -139.5881 | 1369.3154 | -2750 | -200 | -1580.6846 | 39.52% | 30.8% | 95% | 0% | 2317 | -122
[5 empty] | 2019-11-15 | 47 | 7655.5 | 2081 | -114 | 0 | 0 | 2195 | 1317.8071 | 1317.8071 | 1317.8071 | 495.4658 | 780 | 200 | 1475.4658 | 36.89% | 95% | 0% | -130.4348 | 1187.3723 | -2750 | -200 | -1762.6277 | 44.07% | 30.78% | 95% | 0% | 2195 | -114
[5 empty] | 2019-11-15 | 48 | 7656 | 1995 | -106 | 0 | 0 | 2101 | 1170.5688 | 1170.5688 | 1170.5688 | 495.4658 | 780 | 200 | 1475.4658 | 36.89% | 95% | 0% | -121.2815 | 1049.2874 | -2750 | -200 | -1900.7126 | 47.52% | 30.78% | 95% | 0% | 2101 | -106
[5 empty] | 2019-11-16 | 1 | 7656.5 | 1977 | -103 | 0 | 0 | 2080 | 1137.6752 | 1137.6752 | 1137.6752 | 495.4658 | 780 | 200 | 1475.4658 | 36.89% | 95% | 0% | -117.849 | 1019.8262 | -2750 | -200 | -1930.1738 | 48.25% | 30.77% | 95% | 0% | 2080 | -103
[5 empty] | 2019-11-16 | 2 | 7657 | 1984 | -100 | 0 | 0 | 2084 | 1143.9406 | 1143.9406 | 1143.9406 | 495.4658 | 780 | 200 | 1475.4658 | 36.89% | 95% | 0% | -114.4165 | 1029.5242 | -2750 | -200 | -1920.4758 | 48.01% | 30.76% | 95% | 0% | 2084 | -100
[5 empty] | 2019-11-16 | 3 | 7657.5 | 1959 | -96 | 0 | 0 | 2055 | 1098.5161 | 1098.5161 | 1098.5161 | 495.4658 | 780 | 200 | 1475.4658 | 36.89% | 95% | 0% | -109.8398 | 988.6763 | -2750 | -200 | -1961.3237 | 49.03% | 30.76% | 95% | 0% | 2055 | -96
[5 empty] | 2019-11-16 | 4 | 7658 | 1909 | -92 | 0 | 0 | 2001 | 1013.9324 | 1013.9324 | 1013.9324 | 495.4658 | 780 | 200 | 1475.4658 | 36.89% | 95% | 0% | -105.2632 | 908.6692 | -2750 | -200 | -2041.3308 | 51.03% | 30.74% | 95% | 0% | 2001 | -92
[5 empty] | 2019-11-16 | 5 | 7658.5 | 1874 | -90 | 0 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 495.4658 | 780 | 200 | 1475.4658 | 36.89% | 95% | 0% | -102.9748 | 853.0021 | -2750 | -200 | -2096.9979 | 52.42% | 30.74% | 95% | 0% | 1964 | -90
[5 empty] | 2019-11-16 | 6 | 7659 | 1861 | -87 | 0 | 0 | 1948 | 930.9151 | 930.9151 | 930.9151 | 495.4658 | 780 | 200 | 1475.4658 | 36.89% | 95% | 0% | -99.5423 | 831.3728 | -2750 | -200 | -2118.6272 | 52.97% | 30.73% | 95% | 0% | 1948 | -87
[5 empty] | 2019-11-16 | 7 | 7659.5 | 1840 | -82 | 0 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 495.4658 | 780 | 200 | 1475.4658 | 36.89% | 95% | 0% | -93.8215 | 796.3681 | -2750 | -200 | -2153.6319 | 53.84% | 30.72% | 95% | 0% | 1922 | -82
[5 empty] | 2019-11-16 | 8 | 7660 | 1814 | -77 | 0 | 0 | 1891 | 841.6323 | 841.6323 | 841.6323 | 495.4658 | 780 | 200 | 1475.4658 | 36.89% | 95% | 0% | -88.1007 | 753.5316 | -2750 | -200 | -2196.4684 | 54.91% | 30.68% | 95% | 0% | 1891 | -77
[5 empty] | 2019-11-16 | 9 | 7660.5 | 1791 | -74 | 0 | 0 | 1865 | 800.9068 | 800.9068 | 800.9068 | 495.4658 | 780 | 200 | 1475.4658 | 36.89% | 95% | 0% | -84.6682 | 716.2387 | -2750 | -200 | -2233.7613 | 55.84% | 30.67% | 95% | 0% | 1865 | -74
[5 empty] | 2019-11-16 | 10 | 7661 | 1785 | -70 | 0 | 0 | 1855 | 785.2432 | 785.2432 | 785.2432 | 495.4658 | 780 | 200 | 1475.4658 | 36.89% | 95% | 0% | -80.0915 | 705.1517 | -2750 | -200 | -2244.8483 | 56.12% | 30.66% | 95% | 0% | 1855 | -70
[5 empty] | 2019-11-16 | 11 | 7661.5 | 1812 | -67 | 0 | 0 | 1879 | 822.8359 | 822.8359 | 822.8359 | 493.8994 | 780 | 200 | 1473.8994 | 36.85% | 95% | 0% | -76.659 | 746.1769 | -2750 | -200 | -2203.8231 | 55.1% | 30.66% | 95% | 0% | 1879 | -67
[5 empty] | 2019-11-16 | 12 | 7662 | 1863 | -64 | 0 | 0 | 1927 | 898.0214 | 898.0214 | 898.0214 | 493.8994 | 780 | 200 | 1473.8994 | 36.85% | 95% | 0% | -73.2265 | 824.7949 | -2750 | -200 | -2125.2051 | 53.13% | 30.65% | 95% | 0% | 1927 | -64
[5 empty] | 2019-11-16 | 13 | 7662.5 | 1992 | -60 | 0 | 0 | 2052 | 1093.817 | 1093.817 | 1093.817 | 493.8994 | 780 | 200 | 1473.8994 | 36.85% | 95% | 0% | -68.6499 | 1025.1671 | -2750 | -200 | -1924.8329 | 48.12% | 30.62% | 95% | 0% | 2052 | -60
[5 empty] | 2019-11-16 | 14 | 7663 | 2092 | -57 | 0 | 0 | 2149 | 1245.7543 | 1245.7543 | 1245.7543 | 493.8994 | 780 | 200 | 1473.8994 | 36.85% | 95% | 0% | -65.2174 | 1180.5369 | -2750 | -200 | -1769.4631 | 44.24% | 30.61% | 95% | 0% | 2149 | -57
[5 empty] | 2019-11-16 | 15 | 7663.5 | 2215 | -53 | 0 | 0 | 2268 | 1432.1517 | 1432.1517 | 1432.1517 | 493.8994 | 780 | 200 | 1473.8994 | 36.85% | 95% | 0% | -60.6407 | 1371.511 | -2750 | -200 | -1578.489 | 39.46% | 30.61% | 95% | 0% | 2268 | -53
[5 empty] | 2019-11-16 | 16 | 7664 | 2295 | -51 | 0 | 0 | 2346 | 1554.3281 | 1554.3281 | 1554.3281 | 493.8994 | 780 | 200 | 1473.8994 | 36.85% | 95% | 0% | -58.3524 | 1495.9757 | -2750 | -200 | -1454.0243 | 36.35% | 30.6% | 95% | 0% | 2346 | -51
[5 empty] | 2019-11-16 | 17 | 7664.5 | 2460 | -61 | 0 | 0 | 2521 | 1828.4419 | 1828.4419 | 1828.4419 | 493.8994 | 780 | 200 | 1473.8994 | 36.85% | 95% | 0% | -69.7941 | 1758.6478 | -2750 | -200 | -1191.3522 | 29.78% | 30.6% | 95% | 0% | 2521 | -61
[5 empty] | 2019-11-16 | 18 | 7665 | 2530 | -84 | 0 | 0 | 2614 | 1974.1138 | 1974.1138 | 1974.1138 | 493.8994 | 780 | 200 | 1473.8994 | 36.85% | 95% | 0% | -96.1098 | 1878.0039 | -2750 | -200 | -1071.9961 | 26.8% | 30.6% | 95% | 0% | 2614 | -84
[5 empty] | 2019-11-16 | 19 | 7665.5 | 2570 | -116 | 1 | 0 | 2686 | 2086.892 | 2086.892 | 2086.892 | 493.8994 | 780 | 200 | 1473.8994 | 36.85% | 95% | 0% | -132.7231 | 1954.1689 | -3550 | -400 | -1995.8311 | 49.9% | 30.6% | 95% | 0% | 2686 | -116
[5 empty] | 2019-11-16 | 20 | 7666 | 2574 | -145 | 1 | 0 | 2719 | 2138.582 | 2138.582 | 2138.582 | 493.8994 | 780 | 200 | 1473.8994 | 36.85% | 95% | 0% | -165.9039 | 1972.6781 | -3550 | -400 | -1977.3219 | 49.43% | 30.59% | 95% | 0% | 2719 | -145
[5 empty] | 2019-11-16 | 21 | 7666.5 | 2574 | -169 | 1 | 0 | 2743 | 2176.1748 | 2176.1748 | 2176.1748 | 492.3331 | 780 | 200 | 1472.3331 | 36.81% | 95% | 0% | -193.3638 | 1982.8109 | -3550 | -400 | -1967.1891 | 49.18% | 30.58% | 95% | 0% | 2743 | -169
[5 empty] | 2019-11-16 | 22 | 7667 | 2516 | -218 | 1 | 0 | 2734 | 2162.0775 | 2162.0775 | 2162.0775 | 492.3331 | 780 | 200 | 1472.3331 | 36.81% | 95% | 0% | -249.4279 | 1912.6496 | -3550 | -400 | -2037.3504 | 50.93% | 30.58% | 95% | 0% | 2734 | -218
[5 empty] | 2019-11-16 | 23 | 7667.5 | 2502 | -227 | 1 | 0 | 2729 | 2154.2457 | 2154.2457 | 2154.2457 | 492.3331 | 780 | 200 | 1472.3331 | 36.81% | 95% | 0% | -259.7254 | 1894.5203 | -3550 | -400 | -2055.4797 | 51.39% | 30.58% | 95% | 0% | 2729 | -227
[5 empty] | 2019-11-16 | 24 | 7668 | 2525 | -227 | 1 | 0 | 2752 | 2190.2721 | 2190.2721 | 2190.2721 | 492.3331 | 780 | 200 | 1472.3331 | 36.81% | 95% | 0% | -259.7254 | 1930.5467 | -3550 | -400 | -2019.4533 | 50.49% | 30.57% | 95% | 0% | 2752 | -227
[5 empty] | 2019-11-16 | 25 | 7668.5 | 2551 | -216 | 1 | 0 | 2767 | 2213.7675 | 2213.7675 | 2213.7675 | 492.3331 | 780 | 200 | 1472.3331 | 36.81% | 95% | 0% | -247.1396 | 1966.6279 | -3550 | -400 | -1983.3721 | 49.58% | 30.57% | 95% | 0% | 2767 | -216
[5 empty] | 2019-11-16 | 26 | 7669 | 2565 | -191 | 1 | 0 | 2756 | 2196.5375 | 2196.5375 | 2196.5375 | 492.3331 | 780 | 200 | 1472.3331 | 36.81% | 95% | 0% | -218.5355 | 1978.002 | -3550 | -400 | -1971.998 | 49.3% | 30.55% | 95% | 0% | 2756 | -191
[5 empty] | 2019-11-16 | 27 | 7669.5 | 2597 | -167 | 1 | 0 | 2764 | 2209.0684 | 2209.0684 | 2209.0684 | 492.3331 | 780 | 200 | 1472.3331 | 36.81% | 95% | 0% | -191.0755 | 2017.9929 | -3550 | -400 | -1932.0071 | 48.3% | 30.55% | 95% | 0% | 2764 | -167
[5 empty] | 2019-11-16 | 28 | 7670 | 2630 | -132 | 1 | 0 | 2762 | 2205.9357 | 2205.9357 | 2205.9357 | 492.3331 | 780 | 200 | 1472.3331 | 36.81% | 95% | 0% | -151.0297 | 2054.9059 | -3550 | -400 | -1895.0941 | 47.38% | 30.53% | 95% | 0% | 2762 | -132
[5 empty] | 2019-11-16 | 29 | 7670.5 | 2689 | -98 | 1 | 0 | 2787 | 2245.0948 | 2245.0948 | 2245.0948 | 492.3331 | 780 | 200 | 1472.3331 | 36.81% | 95% | 0% | -112.1281 | 2132.9667 | -3550 | -400 | -1817.0333 | 45.43% | 30.53% | 95% | 0% | 2787 | -98
[5 empty] | 2019-11-16 | 30 | 7671 | 2736 | -71 | 1 | 0 | 2807 | 2276.4221 | 2276.4221 | 2276.4221 | 492.3331 | 780 | 200 | 1472.3331 | 36.81% | 95% | 0% | -81.2357 | 2195.1864 | -3550 | -400 | -1754.8136 | 43.87% | 30.53% | 95% | 0% | 2807 | -71
[5 empty] | 2019-11-16 | 31 | 7671.5 | 2794 | -46 | 1 | 0 | 2840 | 2328.1121 | 2328.1121 | 2328.1121 | 490.7667 | 780 | 200 | 1470.7667 | 36.77% | 95% | 0% | -52.6316 | 2275.4805 | -3550 | -400 | -1674.5195 | 41.86% | 30.52% | 95% | 0% | 2840 | -46
[5 empty] | 2019-11-16 | 32 | 7672 | 2862 | -34 | 1 | 0 | 2896 | 2415.8285 | 2415.8285 | 2415.8285 | 490.7667 | 780 | 200 | 1470.7667 | 36.77% | 95% | 0% | -38.9016 | 2376.9269 | -3550 | -400 | -1573.0731 | 39.33% | 30.52% | 95% | 0% | 2896 | -34
[5 empty] | 2019-11-16 | 33 | 7672.5 | 2971 | -30 | 1 | 0 | 3001 | 2580.2968 | 2580.2968 | 2580.2968 | 490.7667 | 780 | 200 | 1470.7667 | 36.77% | 95% | 0% | -34.3249 | 2545.9718 | -3550 | -400 | -1404.0282 | 35.1% | 30.51% | 95% | 0% | 3001 | -30
[5 empty] | 2019-11-16 | 34 | 7673 | 3077 | -30 | 0 | 0 | 3107 | 2746.3314 | 2746.3314 | 2746.3314 | 490.7667 | 780 | 200 | 1470.7667 | 36.77% | 95% | 0% | -34.3249 | 2712.0065 | -2750 | -200 | -237.9935 | 5.95% | 30.48% | 95% | 0% | 3107 | -30
[5 empty] | 2019-11-16 | 35 | 7673.5 | 3127 | -30 | 0 | 0 | 3157 | 2824.6496 | 2824.6496 | 2824.6496 | 490.7667 | 780 | 200 | 1470.7667 | 36.77% | 95% | 0% | -34.3249 | 2790.3247 | -2750 | -200 | -159.6753 | 3.992% | 30.47% | 95% | 0% | 3157 | -30
[5 empty] | 2019-11-16 | 36 | 7674 | 3116 | -30 | 0 | 0 | 3146 | 2807.4196 | 2807.4196 | 2807.4196 | 490.7667 | 780 | 200 | 1470.7667 | 36.77% | 95% | 0% | -34.3249 | 2773.0947 | -2750 | -200 | -176.9053 | 4.423% | 30.46% | 95% | 0% | 3146 | -30
[5 empty] | 2019-11-16 | 37 | 7674.5 | 3070 | -29 | 0 | 0 | 3099 | 2733.8005 | 2733.8005 | 2733.8005 | 490.7667 | 780 | 200 | 1470.7667 | 36.77% | 95% | 0% | -33.1808 | 2700.6197 | -2750 | -200 | -249.3803 | 6.235% | 30.46% | 95% | 0% | 3099 | -29
[5 empty] | 2019-11-16 | 38 | 7675 | 3035 | -28 | 0 | 0 | 3063 | 2677.4114 | 2677.4114 | 2677.4114 | 490.7667 | 780 | 200 | 1470.7667 | 36.77% | 95% | 0% | -32.0366 | 2645.3748 | -2750 | -200 | -304.6252 | 7.616% | 30.45% | 95% | 0% | 3063 | -28
[5 empty] | 2019-11-16 | 39 | 7675.5 | 2977 | -28 | 0 | 0 | 3005 | 2586.5622 | 2586.5622 | 2586.5622 | 490.7667 | 780 | 200 | 1470.7667 | 36.77% | 95% | 0% | -32.0366 | 2554.5256 | -2750 | -200 | -395.4744 | 9.887% | 30.44% | 95% | 0% | 3005 | -28
[5 empty] | 2019-11-16 | 40 | 7676 | 2879 | -28 | 0 | 0 | 2907 | 2433.0585 | 2433.0585 | 2433.0585 | 490.7667 | 780 | 200 | 1470.7667 | 36.77% | 95% | 0% | -32.0366 | 2401.0219 | -2750 | -200 | -548.9781 | 13.72% | 30.44% | 95% | 0% | 2907 | -28
[5 empty] | 2019-11-16 | 41 | 7676.5 | 2801 | -27 | 0 | 0 | 2828 | 2309.3157 | 2309.3157 | 2309.3157 | 489.2003 | 780 | 200 | 1469.2003 | 36.73% | 95% | 0% | -30.8924 | 2278.4233 | -2750 | -200 | -671.5767 | 16.79% | 30.43% | 95% | 0% | 2828 | -27
[5 empty] | 2019-11-16 | 42 | 7677 | 2709 | -27 | 0 | 0 | 2736 | 2165.2102 | 2165.2102 | 2165.2102 | 489.2003 | 780 | 200 | 1469.2003 | 36.73% | 95% | 0% | -30.8924 | 2134.3178 | -2750 | -200 | -815.6822 | 20.39% | 30.41% | 95% | 0% | 2736 | -27
[5 empty] | 2019-11-16 | 43 | 7677.5 | 2615 | -27 | 0 | 0 | 2642 | 2017.972 | 2017.972 | 2017.972 | 489.2003 | 780 | 200 | 1469.2003 | 36.73% | 95% | 0% | -30.8924 | 1987.0795 | -2750 | -200 | -962.9205 | 24.07% | 30.41% | 95% | 0% | 2642 | -27
[5 empty] | 2019-11-16 | 44 | 7678 | 2509 | -27 | 0 | 0 | 2536 | 1851.9373 | 1851.9373 | 1851.9373 | 489.2003 | 780 | 200 | 1469.2003 | 36.73% | 95% | 0% | -30.8924 | 1821.0449 | -2750 | -200 | -1128.9551 | 28.22% | 30.41% | 95% | 0% | 2536 | -27
[5 empty] | 2019-11-16 | 45 | 7678.5 | 2391 | -27 | 0 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 489.2003 | 780 | 200 | 1469.2003 | 36.73% | 95% | 0% | -30.8924 | 1636.2139 | -2750 | -200 | -1313.7861 | 32.84% | 30.41% | 95% | 0% | 2418 | -27
[5 empty] | 2019-11-16 | 46 | 7679 | 2308 | -27 | 0 | 0 | 2335 | 1537.0981 | 1537.0981 | 1537.0981 | 489.2003 | 780 | 200 | 1469.2003 | 36.73% | 95% | 0% | -30.8924 | 1506.2057 | -2750 | -200 | -1443.7943 | 36.09% | 30.4% | 95% | 0% | 2335 | -27
[5 empty] | 2019-11-16 | 47 | 7679.5 | 2198 | -26 | 0 | 0 | 2224 | 1363.2317 | 1363.2317 | 1363.2317 | 487.634 | 780 | 200 | 1467.634 | 36.69% | 95% | 0% | -29.7483 | 1333.4834 | -2750 | -200 | -1616.5166 | 40.41% | 30.4% | 95% | 0% | 2224 | -26
[5 empty] | 2019-11-16 | 48 | 7680 | 2122 | -26 | 0 | 0 | 2148 | 1244.188 | 1244.188 | 1244.188 | 487.634 | 780 | 200 | 1467.634 | 36.69% | 95% | 0% | -29.7483 | 1214.4397 | -2750 | -200 | -1735.5603 | 43.39% | 30.39% | 95% | 0% | 2148 | -26
[5 empty] | 2019-11-17 | 1 | 7680.5 | 2107 | -26 | 0 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 487.634 | 780 | 200 | 1467.634 | 36.69% | 95% | 0% | -29.7483 | 1190.9442 | -2750 | -200 | -1759.0558 | 43.98% | 30.38% | 95% | 0% | 2133 | -26
[5 empty] | 2019-11-17 | 2 | 7681 | 2116 | -26 | 0 | 0 | 2142 | 1234.7898 | 1234.7898 | 1234.7898 | 487.634 | 780 | 200 | 1467.634 | 36.69% | 95% | 0% | -29.7483 | 1205.0415 | -2750 | -200 | -1744.9585 | 43.62% | 30.37% | 95% | 0% | 2142 | -26
[5 empty] | 2019-11-17 | 3 | 7681.5 | 2090 | -26 | 0 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 487.634 | 780 | 200 | 1467.634 | 36.69% | 95% | 0% | -29.7483 | 1164.316 | -2750 | -200 | -1785.684 | 44.64% | 30.36% | 95% | 0% | 2116 | -26
[5 empty] | 2019-11-17 | 4 | 7682 | 2036 | -26 | 0 | 0 | 2062 | 1109.4806 | 1109.4806 | 1109.4806 | 487.634 | 780 | 200 | 1467.634 | 36.69% | 95% | 0% | -29.7483 | 1079.7323 | -2750 | -200 | -1870.2677 | 46.76% | 30.35% | 95% | 0% | 2062 | -26
[5 empty] | 2019-11-17 | 5 | 7682.5 | 1982 | -26 | 0 | 0 | 2008 | 1024.8969 | 1024.8969 | 1024.8969 | 487.634 | 780 | 200 | 1467.634 | 36.69% | 95% | 0% | -29.7483 | 995.1487 | -2750 | -200 | -1954.8513 | 48.87% | 30.35% | 95% | 0% | 2008 | -26
[5 empty] | 2019-11-17 | 6 | 7683 | 1952 | -25 | 0 | 0 | 1977 | 976.3397 | 976.3397 | 976.3397 | 487.634 | 780 | 200 | 1467.634 | 36.69% | 95% | 0% | -28.6041 | 947.7355 | -2750 | -200 | -2002.2645 | 50.06% | 30.34% | 95% | 0% | 1977 | -25
[5 empty] | 2019-11-17 | 7 | 7683.5 | 1909 | -26 | 0 | 0 | 1935 | 910.5523 | 910.5523 | 910.5523 | 487.634 | 780 | 200 | 1467.634 | 36.69% | 95% | 0% | -29.7483 | 880.8041 | -2750 | -200 | -2069.1959 | 51.73% | 30.34% | 95% | 0% | 1935 | -26
[5 empty] | 2019-11-17 | 8 | 7684 | 1883 | -27 | 0 | 0 | 1910 | 871.3932 | 871.3932 | 871.3932 | 486.0676 | 780 | 200 | 1466.0676 | 36.65% | 95% | 0% | -30.8924 | 840.5008 | -2750 | -200 | -2109.4992 | 52.74% | 30.33% | 95% | 0% | 1910 | -27
[5 empty] | 2019-11-17 | 9 | 7684.5 | 1859 | -27 | 0 | 0 | 1886 | 833.8005 | 833.8005 | 833.8005 | 486.0676 | 780 | 200 | 1466.0676 | 36.65% | 95% | 0% | -30.8924 | 802.908 | -2750 | -200 | -2147.092 | 53.68% | 30.32% | 95% | 0% | 1886 | -27
[5 empty] | 2019-11-17 | 10 | 7685 | 1842 | -27 | 0 | 0 | 1869 | 807.1723 | 807.1723 | 807.1723 | 486.0676 | 780 | 200 | 1466.0676 | 36.65% | 95% | 0% | -30.8924 | 776.2799 | -2750 | -200 | -2173.7201 | 54.34% | 30.3% | 95% | 0% | 1869 | -27
[5 empty] | 2019-11-17 | 11 | 7685.5 | 1850 | -28 | 0 | 0 | 1878 | 821.2696 | 821.2696 | 821.2696 | 486.0676 | 780 | 200 | 1466.0676 | 36.65% | 95% | 0% | -32.0366 | 789.233 | -2750 | -200 | -2160.767 | 54.02% | 30.3% | 95% | 0% | 1878 | -28
[5 empty] | 2019-11-17 | 12 | 7686 | 1870 | -28 | 0 | 0 | 1898 | 852.5969 | 852.5969 | 852.5969 | 486.0676 | 780 | 200 | 1466.0676 | 36.65% | 95% | 0% | -32.0366 | 820.5603 | -2750 | -200 | -2129.4397 | 53.24% | 30.29% | 95% | 0% | 1898 | -28
[5 empty] | 2019-11-17 | 13 | 7686.5 | 1935 | -28 | 0 | 0 | 1963 | 954.4106 | 954.4106 | 954.4106 | 486.0676 | 780 | 200 | 1466.0676 | 36.65% | 95% | 0% | -32.0366 | 922.3739 | -2750 | -200 | -2027.6261 | 50.69% | 30.29% | 95% | 0% | 1963 | -28
[5 empty] | 2019-11-17 | 14 | 7687 | 1996 | -28 | 0 | 0 | 2024 | 1049.9588 | 1049.9588 | 1049.9588 | 484.5012 | 780 | 200 | 1464.5012 | 36.61% | 95% | 0% | -32.0366 | 1017.9222 | -2750 | -200 | -1932.0778 | 48.3% | 30.28% | 95% | 0% | 2024 | -28
[5 empty] | 2019-11-17 | 15 | 7687.5 | 2086 | -29 | 0 | 0 | 2115 | 1192.4979 | 1192.4979 | 1192.4979 | 484.5012 | 780 | 200 | 1464.5012 | 36.61% | 95% | 0% | -33.1808 | 1159.3172 | -2750 | -200 | -1790.6828 | 44.77% | 30.28% | 95% | 0% | 2115 | -29
[5 empty] | 2019-11-17 | 16 | 7688 | 2135 | -31 | 0 | 0 | 2166 | 1272.3825 | 1272.3825 | 1272.3825 | 484.5012 | 780 | 200 | 1464.5012 | 36.61% | 95% | 0% | -35.4691 | 1236.9134 | -2750 | -200 | -1713.0866 | 42.83% | 30.26% | 95% | 0% | 2166 | -31
[5 empty] | 2019-11-17 | 17 | 7688.5 | 2265 | -43 | 0 | 0 | 2308 | 1494.8063 | 1494.8063 | 1494.8063 | 484.5012 | 780 | 200 | 1464.5012 | 36.61% | 95% | 0% | -49.1991 | 1445.6072 | -2750 | -200 | -1504.3928 | 37.61% | 30.25% | 95% | 0% | 2308 | -43
[5 empty] | 2019-11-17 | 18 | 7689 | 2354 | -64 | 1 | 0 | 2418 | 1667.1063 | 1667.1063 | 1667.1063 | 484.5012 | 780 | 200 | 1464.5012 | 36.61% | 95% | 0% | -73.2265 | 1593.8798 | -3550 | -400 | -2356.1202 | 58.9% | 30.24% | 95% | 0% | 2418 | -64
[5 empty] | 2019-11-17 | 19 | 7689.5 | 2436 | -92 | 1 | 0 | 2528 | 1839.4064 | 1839.4064 | 1839.4064 | 484.5012 | 780 | 200 | 1464.5012 | 36.61% | 95% | 0% | -105.2632 | 1734.1433 | -3550 | -400 | -2215.8567 | 55.4% | 30.22% | 95% | 0% | 2528 | -92
[5 empty] | 2019-11-17 | 20 | 7690 | 2474 | -121 | 1 | 0 | 2595 | 1944.3528 | 1944.3528 | 1944.3528 | 484.5012 | 780 | 200 | 1464.5012 | 36.61% | 95% | 0% | -138.4439 | 1805.9089 | -3550 | -400 | -2144.0911 | 53.6% | 30.2% | 95% | 0% | 2595 | -121
[5 empty] | 2019-11-17 | 21 | 7690.5 | 2471 | -162 | 1 | 0 | 2633 | 2003.8747 | 2003.8747 | 2003.8747 | 484.5012 | 780 | 200 | 1464.5012 | 36.61% | 95% | 0% | -185.3547 | 1818.52 | -3550 | -400 | -2131.48 | 53.29% | 30.19% | 95% | 0% | 2633 | -162
[5 empty] | 2019-11-17 | 22 | 7691 | 2464 | -199 | 1 | 0 | 2663 | 2050.8656 | 2050.8656 | 2050.8656 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -227.6888 | 1823.1768 | -3550 | -400 | -2126.8232 | 53.17% | 30.18% | 95% | 0% | 2663 | -199
[5 empty] | 2019-11-17 | 23 | 7691.5 | 2497 | -201 | 1 | 0 | 2698 | 2105.6884 | 2105.6884 | 2105.6884 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -229.9771 | 1875.7113 | -3550 | -400 | -2074.2887 | 51.86% | 30.17% | 95% | 0% | 2698 | -201
[5 empty] | 2019-11-17 | 24 | 7692 | 2531 | -198 | 1 | 0 | 2729 | 2154.2457 | 2154.2457 | 2154.2457 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -226.5446 | 1927.701 | -3550 | -400 | -2022.299 | 50.56% | 30.16% | 95% | 0% | 2729 | -198
[5 empty] | 2019-11-17 | 25 | 7692.5 | 2585 | -181 | 1 | 0 | 2766 | 2212.2012 | 2212.2012 | 2212.2012 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -207.0938 | 2005.1073 | -3550 | -400 | -1944.8927 | 48.62% | 30.15% | 95% | 0% | 2766 | -181
[5 empty] | 2019-11-17 | 26 | 7693 | 2617 | -167 | 1 | 0 | 2784 | 2240.3957 | 2240.3957 | 2240.3957 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -191.0755 | 2049.3202 | -3550 | -400 | -1900.6798 | 47.52% | 30.15% | 95% | 0% | 2784 | -167
[5 empty] | 2019-11-17 | 27 | 7693.5 | 2629 | -140 | 1 | 0 | 2769 | 2216.9002 | 2216.9002 | 2216.9002 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -160.1831 | 2056.7172 | -3550 | -400 | -1893.2828 | 47.33% | 30.13% | 95% | 0% | 2769 | -140
[5 empty] | 2019-11-17 | 28 | 7694 | 2653 | -127 | 1 | 0 | 2780 | 2234.1303 | 2234.1303 | 2234.1303 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -145.3089 | 2088.8213 | -3550 | -400 | -1861.1787 | 46.53% | 30.12% | 95% | 0% | 2780 | -127
[5 empty] | 2019-11-17 | 29 | 7694.5 | 2695 | -110 | 1 | 0 | 2805 | 2273.2894 | 2273.2894 | 2273.2894 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -125.8581 | 2147.4312 | -3550 | -400 | -1802.5688 | 45.06% | 30.12% | 95% | 0% | 2805 | -110
[5 empty] | 2019-11-17 | 30 | 7695 | 2718 | -99 | 1 | 0 | 2817 | 2292.0857 | 2292.0857 | 2292.0857 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -113.2723 | 2178.8134 | -3550 | -400 | -1771.1866 | 44.28% | 30.1% | 95% | 0% | 2817 | -99
[5 empty] | 2019-11-17 | 31 | 7695.5 | 2782 | -83 | 1 | 0 | 2865 | 2367.2712 | 2367.2712 | 2367.2712 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -94.9657 | 2272.3056 | -3550 | -400 | -1677.6944 | 41.94% | 30.09% | 95% | 0% | 2865 | -83
[5 empty] | 2019-11-17 | 32 | 7696 | 2853 | -68 | 1 | 0 | 2921 | 2454.9876 | 2454.9876 | 2454.9876 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -77.8032 | 2377.1844 | -3550 | -400 | -1572.8156 | 39.32% | 30.08% | 95% | 0% | 2921 | -68
[5 empty] | 2019-11-17 | 33 | 7696.5 | 2950 | -65 | 1 | 0 | 3015 | 2602.2259 | 2602.2259 | 2602.2259 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -74.3707 | 2527.8552 | -3550 | -400 | -1422.1448 | 35.55% | 30.08% | 95% | 0% | 3015 | -65
[5 empty] | 2019-11-17 | 34 | 7697 | 3089 | -67 | 1 | 0 | 3156 | 2823.0833 | 2823.0833 | 2823.0833 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -76.659 | 2746.4242 | -3550 | -400 | -1203.5758 | 30.09% | 30.06% | 95% | 0% | 3156 | -67
[5 empty] | 2019-11-17 | 35 | 7697.5 | 3145 | -69 | 0 | 0 | 3214 | 2913.9324 | 2913.9324 | 2913.9324 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -78.9474 | 2834.985 | -2750 | -200 | -115.015 | 2.875% | 30.05% | 95% | 0% | 3214 | -69
[5 empty] | 2019-11-17 | 36 | 7698 | 3115 | -71 | 0 | 0 | 3186 | 2870.0742 | 2870.0742 | 2870.0742 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -81.2357 | 2788.8385 | -2750 | -200 | -161.1615 | 4.029% | 30.05% | 95% | 0% | 3186 | -71
[5 empty] | 2019-11-17 | 37 | 7698.5 | 3040 | -74 | 0 | 0 | 3114 | 2757.296 | 2757.296 | 2757.296 | 482.9349 | 780 | 200 | 1462.9349 | 36.57% | 95% | 0% | -84.6682 | 2672.6278 | -2750 | -200 | -277.3722 | 6.934% | 30.05% | 95% | 0% | 3114 | -74
[5 empty] | 2019-11-17 | 38 | 7699 | 3011 | -76 | 0 | 0 | 3087 | 2715.0041 | 2715.0041 | 2715.0041 | 481.3685 | 780 | 200 | 1461.3685 | 36.53% | 95% | 0% | -86.9565 | 2628.0476 | -2750 | -200 | -321.9524 | 8.049% | 30.05% | 95% | 0% | 3087 | -76
[5 empty] | 2019-11-17 | 39 | 7699.5 | 2953 | -78 | 0 | 0 | 3031 | 2627.2877 | 2627.2877 | 2627.2877 | 481.3685 | 780 | 200 | 1461.3685 | 36.53% | 95% | 0% | -89.2449 | 2538.0429 | -2750 | -200 | -411.9571 | 10.3% | 30.05% | 95% | 0% | 3031 | -78
[5 empty] | 2019-11-17 | 40 | 7700 | 2866 | -79 | 0 | 0 | 2945 | 2492.5804 | 2492.5804 | 2492.5804 | 481.3685 | 780 | 200 | 1461.3685 | 36.53% | 95% | 0% | -90.389 | 2402.1914 | -2750 | -200 | -547.8086 | 13.7% | 30.04% | 95% | 0% | 2945 | -79
[5 empty] | 2019-11-17 | 41 | 7700.5 | 2793 | -81 | 0 | 0 | 2874 | 2381.3685 | 2381.3685 | 2381.3685 | 481.3685 | 780 | 200 | 1461.3685 | 36.53% | 95% | 0% | -92.6773 | 2288.6912 | -2750 | -200 | -661.3088 | 16.53% | 29.99% | 95% | 0% | 2874 | -81
[5 empty] | 2019-11-17 | 42 | 7701 | 2678 | -82 | 0 | 0 | 2760 | 2202.803 | 2202.803 | 2202.803 | 481.3685 | 780 | 200 | 1461.3685 | 36.53% | 95% | 0% | -93.8215 | 2108.9815 | -2750 | -200 | -841.0185 | 21.03% | 29.99% | 95% | 0% | 2760 | -82
[5 empty] | 2019-11-17 | 43 | 7701.5 | 2555 | -83 | 0 | 0 | 2638 | 2011.7065 | 2011.7065 | 2011.7065 | 481.3685 | 780 | 200 | 1461.3685 | 36.53% | 95% | 0% | -94.9657 | 1916.7408 | -2750 | -200 | -1033.2592 | 25.83% | 29.98% | 95% | 0% | 2638 | -83
[5 empty] | 2019-11-17 | 44 | 7702 | 2425 | -84 | 0 | 0 | 2509 | 1809.6455 | 1809.6455 | 1809.6455 | 481.3685 | 780 | 200 | 1461.3685 | 36.53% | 95% | 0% | -96.1098 | 1713.5357 | -2750 | -200 | -1236.4643 | 30.91% | 29.97% | 95% | 0% | 2509 | -84
[5 empty] | 2019-11-17 | 45 | 7702.5 | 2295 | -84 | 0 | 0 | 2379 | 1606.0181 | 1606.0181 | 1606.0181 | 481.3685 | 780 | 200 | 1461.3685 | 36.53% | 95% | 0% | -96.1098 | 1509.9083 | -2750 | -200 | -1440.0917 | 36% | 29.97% | 95% | 0% | 2379 | -84
[5 empty] | 2019-11-17 | 46 | 7703 | 2173 | -85 | 0 | 0 | 2258 | 1416.488 | 1416.488 | 1416.488 | 481.3685 | 780 | 200 | 1461.3685 | 36.53% | 95% | 0% | -97.254 | 1319.234 | -2750 | -200 | -1630.766 | 40.77% | 29.95% | 95% | 0% | 2258 | -85
[5 empty] | 2019-11-17 | 47 | 7703.5 | 2054 | -83 | 0 | 0 | 2137 | 1226.958 | 1226.958 | 1226.958 | 479.8021 | 780 | 200 | 1459.8021 | 36.5% | 95% | 0% | -94.9657 | 1131.9923 | -2750 | -200 | -1818.0077 | 45.45% | 29.93% | 95% | 0% | 2137 | -83
[5 empty] | 2019-11-17 | 48 | 7704 | 1948 | -82 | 0 | 0 | 2030 | 1059.357 | 1059.357 | 1059.357 | 479.8021 | 780 | 200 | 1459.8021 | 36.5% | 95% | 0% | -93.8215 | 965.5355 | -2750 | -200 | -1984.4645 | 49.61% | 29.93% | 95% | 0% | 2030 | -82
[5 empty] | 2019-11-18 | 1 | 7704.5 | 1939 | -82 | 0 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 479.8021 | 780 | 200 | 1459.8021 | 36.5% | 95% | 0% | -93.8215 | 951.4382 | -2750 | -200 | -1998.5618 | 49.96% | 29.92% | 95% | 0% | 2021 | -82
[5 empty] | 2019-11-18 | 2 | 7705 | 1961 | -83 | 0 | 0 | 2044 | 1081.2861 | 1081.2861 | 1081.2861 | 479.8021 | 780 | 200 | 1459.8021 | 36.5% | 95% | 0% | -94.9657 | 986.3204 | -2750 | -200 | -1963.6796 | 49.09% | 29.92% | 95% | 0% | 2044 | -83
[5 empty] | 2019-11-18 | 3 | 7705.5 | 1938 | -83 | 0 | 0 | 2021 | 1045.2597 | 1045.2597 | 1045.2597 | 479.8021 | 780 | 200 | 1459.8021 | 36.5% | 95% | 0% | -94.9657 | 950.294 | -2750 | -200 | -1999.706 | 49.99% | 29.92% | 95% | 0% | 2021 | -83
[5 empty] | 2019-11-18 | 4 | 7706 | 1904 | -84 | 0 | 0 | 1988 | 993.5697 | 993.5697 | 993.5697 | 479.8021 | 780 | 200 | 1459.8021 | 36.5% | 95% | 0% | -96.1098 | 897.4598 | -2750 | -200 | -2052.5402 | 51.31% | 29.88% | 95% | 0% | 1988 | -84
[5 empty] | 2019-11-18 | 5 | 7706.5 | 1882 | -84 | 0 | 0 | 1966 | 959.1096 | 959.1096 | 959.1096 | 479.8021 | 780 | 200 | 1459.8021 | 36.5% | 95% | 0% | -96.1098 | 862.9998 | -2750 | -200 | -2087.0002 | 52.18% | 29.87% | 95% | 0% | 1966 | -84
[5 empty] | 2019-11-18 | 6 | 7707 | 1869 | -84 | 0 | 0 | 1953 | 938.7469 | 938.7469 | 938.7469 | 478.2358 | 780 | 200 | 1458.2358 | 36.46% | 95% | 0% | -96.1098 | 842.6371 | -2750 | -200 | -2107.3629 | 52.68% | 29.87% | 95% | 0% | 1953 | -84
[5 empty] | 2019-11-18 | 7 | 7707.5 | 1845 | -83 | 0 | 0 | 1928 | 899.5878 | 899.5878 | 899.5878 | 478.2358 | 780 | 200 | 1458.2358 | 36.46% | 95% | 0% | -94.9657 | 804.6221 | -2750 | -200 | -2145.3779 | 53.63% | 29.86% | 95% | 0% | 1928 | -83
[5 empty] | 2019-11-18 | 8 | 7708 | 1813 | -82 | 0 | 0 | 1895 | 847.8978 | 847.8978 | 847.8978 | 478.2358 | 780 | 200 | 1458.2358 | 36.46% | 95% | 0% | -93.8215 | 754.0763 | -2750 | -200 | -2195.9237 | 54.9% | 29.85% | 95% | 0% | 1895 | -82
[5 empty] | 2019-11-18 | 9 | 7708.5 | 1813 | -81 | 0 | 0 | 1894 | 846.3314 | 846.3314 | 846.3314 | 478.2358 | 780 | 200 | 1458.2358 | 36.46% | 95% | 0% | -92.6773 | 753.6541 | -2750 | -200 | -2196.3459 | 54.91% | 29.85% | 95% | 0% | 1894 | -81
[5 empty] | 2019-11-18 | 10 | 7709 | 1829 | -79 | 0 | 0 | 1908 | 868.2605 | 868.2605 | 868.2605 | 478.2358 | 780 | 200 | 1458.2358 | 36.46% | 95% | 0% | -90.389 | 777.8715 | -2750 | -200 | -2172.1285 | 54.3% | 29.83% | 95% | 0% | 1908 | -79
[5 empty] | 2019-11-18 | 11 | 7709.5 | 1893 | -78 | 0 | 0 | 1971 | 966.9415 | 966.9415 | 966.9415 | 478.2358 | 780 | 200 | 1458.2358 | 36.46% | 95% | 0% | -89.2449 | 877.6966 | -2750 | -200 | -2072.3034 | 51.81% | 29.81% | 95% | 0% | 1971 | -78
[5 empty] | 2019-11-18 | 12 | 7710 | 2016 | -78 | 0 | 0 | 2094 | 1159.6043 | 1159.6043 | 1159.6043 | 478.2358 | 780 | 200 | 1458.2358 | 36.46% | 95% | 0% | -89.2449 | 1070.3594 | -2750 | -200 | -1879.6406 | 46.99% | 29.81% | 95% | 0% | 2094 | -78
[5 empty] | 2019-11-18 | 13 | 7710.5 | 2291 | -76 | 0 | 0 | 2367 | 1587.2218 | 1587.2218 | 1587.2218 | 476.6694 | 780 | 200 | 1456.6694 | 36.42% | 95% | 0% | -86.9565 | 1500.2652 | -2750 | -200 | -1449.7348 | 36.24% | 29.8% | 95% | 0% | 2367 | -76
[5 empty] | 2019-11-18 | 14 | 7711 | 2541 | -74 | 0 | 0 | 2615 | 1975.6801 | 1975.6801 | 1975.6801 | 476.6694 | 780 | 200 | 1456.6694 | 36.42% | 95% | 0% | -84.6682 | 1891.0119 | -2750 | -200 | -1058.9881 | 26.47% | 29.79% | 95% | 0% | 2615 | -74
[5 empty] | 2019-11-18 | 15 | 7711.5 | 2828 | -73 | 0 | 0 | 2901 | 2423.6603 | 2423.6603 | 2423.6603 | 476.6694 | 780 | 200 | 1456.6694 | 36.42% | 95% | 0% | -83.524 | 2340.1363 | -2750 | -200 | -609.8637 | 15.25% | 29.78% | 95% | 0% | 2901 | -73
[5 empty] | 2019-11-18 | 16 | 7712 | 2947 | -76 | 0 | 0 | 3023 | 2614.7568 | 2614.7568 | 2614.7568 | 476.6694 | 780 | 200 | 1456.6694 | 36.42% | 95% | 0% | -86.9565 | 2527.8003 | -2750 | -200 | -422.1997 | 10.55% | 29.78% | 95% | 0% | 3023 | -76
[5 empty] | 2019-11-18 | 17 | 7712.5 | 2950 | -122 | 0 | 0 | 3072 | 2691.5087 | 2691.5087 | 2691.5087 | 476.6694 | 780 | 200 | 1456.6694 | 36.42% | 95% | 0% | -139.5881 | 2551.9206 | -2750 | -200 | -398.0794 | 9.952% | 29.77% | 95% | 0% | 3072 | -122
[5 empty] | 2019-11-18 | 18 | 7713 | 2875 | -194 | 0 | 0 | 3069 | 2686.8096 | 2686.8096 | 2686.8096 | 476.6694 | 780 | 200 | 1456.6694 | 36.42% | 95% | 0% | -221.968 | 2464.8416 | -2750 | -200 | -485.1584 | 12.13% | 29.77% | 95% | 0% | 3069 | -194
[5 empty] | 2019-11-18 | 19 | 7713.5 | 2788 | -271 | 1 | 0 | 3059 | 2671.1459 | 2671.1459 | 2671.1459 | 476.6694 | 780 | 200 | 1456.6694 | 36.42% | 95% | 0% | -310.0686 | 2361.0773 | -3550 | -400 | -1588.9227 | 39.72% | 29.77% | 95% | 0% | 3059 | -271
[5 empty] | 2019-11-18 | 20 | 7714 | 2691 | -341 | 1 | 0 | 3032 | 2628.8541 | 2628.8541 | 2628.8541 | 476.6694 | 780 | 200 | 1456.6694 | 36.42% | 95% | 0% | -390.1602 | 2238.6939 | -3550 | -400 | -1711.3061 | 42.78% | 29.77% | 95% | 0% | 3032 | -341
[5 empty] | 2019-11-18 | 21 | 7714.5 | 2568 | -404 | 1 | 0 | 2972 | 2534.8722 | 2534.8722 | 2534.8722 | 476.6694 | 780 | 200 | 1456.6694 | 36.42% | 95% | 0% | -462.2426 | 2072.6297 | -3550 | -400 | -1877.3703 | 46.93% | 29.76% | 95% | 0% | 2972 | -404
[5 empty] | 2019-11-18 | 22 | 7715 | 2504 | -443 | 1 | 0 | 2947 | 2495.7131 | 2495.7131 | 2495.7131 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -506.865 | 1988.8481 | -3550 | -400 | -1961.1519 | 49.03% | 29.71% | 95% | 0% | 2947 | -443
[5 empty] | 2019-11-18 | 23 | 7715.5 | 2461 | -460 | 1 | 0 | 2921 | 2454.9876 | 2454.9876 | 2454.9876 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -526.3158 | 1928.6718 | -3550 | -400 | -2021.3282 | 50.53% | 29.7% | 95% | 0% | 2921 | -460
[5 empty] | 2019-11-18 | 24 | 7716 | 2448 | -467 | 1 | 0 | 2915 | 2445.5894 | 2445.5894 | 2445.5894 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -534.3249 | 1911.2645 | -3550 | -400 | -2038.7355 | 50.97% | 29.7% | 95% | 0% | 2915 | -467
[5 empty] | 2019-11-18 | 25 | 7716.5 | 2470 | -453 | 1 | 0 | 2923 | 2458.1204 | 2458.1204 | 2458.1204 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -518.3066 | 1939.8137 | -3550 | -400 | -2010.1863 | 50.25% | 29.7% | 95% | 0% | 2923 | -453
[5 empty] | 2019-11-18 | 26 | 7717 | 2490 | -423 | 1 | 0 | 2913 | 2442.4567 | 2442.4567 | 2442.4567 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -483.9817 | 1958.475 | -3550 | -400 | -1991.525 | 49.79% | 29.7% | 95% | 0% | 2913 | -423
[5 empty] | 2019-11-18 | 27 | 7717.5 | 2545 | -384 | 1 | 0 | 2929 | 2467.5185 | 2467.5185 | 2467.5185 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -439.3593 | 2028.1593 | -3550 | -400 | -1921.8407 | 48.05% | 29.69% | 95% | 0% | 2929 | -384
[5 empty] | 2019-11-18 | 28 | 7718 | 2606 | -339 | 1 | 0 | 2945 | 2492.5804 | 2492.5804 | 2492.5804 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -387.8719 | 2104.7085 | -3550 | -400 | -1845.2915 | 46.13% | 29.68% | 95% | 0% | 2945 | -339
[5 empty] | 2019-11-18 | 29 | 7718.5 | 2711 | -283 | 1 | 0 | 2994 | 2569.3322 | 2569.3322 | 2569.3322 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -323.7986 | 2245.5336 | -3550 | -400 | -1704.4664 | 42.61% | 29.65% | 95% | 0% | 2994 | -283
[5 empty] | 2019-11-18 | 30 | 7719 | 2842 | -211 | 1 | 0 | 3053 | 2661.7477 | 2661.7477 | 2661.7477 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -241.4188 | 2420.329 | -3550 | -400 | -1529.671 | 38.24% | 29.65% | 95% | 0% | 3053 | -211
[5 empty] | 2019-11-18 | 31 | 7719.5 | 2991 | -133 | 1 | 0 | 3124 | 2772.9596 | 2772.9596 | 2772.9596 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -152.1739 | 2620.7857 | -3550 | -400 | -1329.2143 | 33.23% | 29.64% | 95% | 0% | 3124 | -133
[5 empty] | 2019-11-18 | 32 | 7720 | 3141 | -72 | 1 | 0 | 3213 | 2912.366 | 2912.366 | 2912.366 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -82.3799 | 2829.9862 | -3550 | -400 | -1120.0138 | 28% | 29.64% | 95% | 0% | 3213 | -72
[5 empty] | 2019-11-18 | 33 | 7720.5 | 3302 | -54 | 0 | 0 | 3356 | 3136.3561 | 3136.3561 | 3136.3561 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -61.7849 | 3074.5712 | -2750 | -200 | 124.5712 | -3.114% | 29.64% | 95% | 0% | 3356 | -54
[5 empty] | 2019-11-18 | 34 | 7721 | 3399 | -52 | 0 | 0 | 3451 | 3285.1608 | 3285.1608 | 3285.1608 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -59.4966 | 3225.6642 | -2750 | -200 | 275.6642 | -6.892% | 29.63% | 95% | 0% | 3451 | -52
[5 empty] | 2019-11-18 | 35 | 7721.5 | 3429 | -52 | 0 | 0 | 3481 | 3332.1517 | 3332.1517 | 3332.1517 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -59.4966 | 3272.6551 | -2750 | -200 | 322.6551 | -8.066% | 29.62% | 95% | 0% | 3481 | -52
[5 empty] | 2019-11-18 | 36 | 7722 | 3428 | -51 | 0 | 0 | 3479 | 3329.019 | 3329.019 | 3329.019 | 475.1031 | 780 | 200 | 1455.1031 | 36.38% | 95% | 0% | -58.3524 | 3270.6666 | -2750 | -200 | 320.6666 | -8.017% | 29.61% | 95% | 0% | 3479 | -51
[5 empty] | 2019-11-18 | 37 | 7722.5 | 3406 | -51 | 0 | 0 | 3457 | 3294.5589 | 3294.5589 | 3294.5589 | 473.5367 | 780 | 200 | 1453.5367 | 36.34% | 95% | 0% | -58.3524 | 3236.2065 | -2750 | -200 | 286.2065 | -7.155% | 29.61% | 95% | 0% | 3457 | -51
[5 empty] | 2019-11-18 | 38 | 7723 | 3390 | -51 | 0 | 0 | 3441 | 3269.4971 | 3269.4971 | 3269.4971 | 473.5367 | 780 | 200 | 1453.5367 | 36.34% | 95% | 0% | -58.3524 | 3211.1447 | -2750 | -200 | 261.1447 | -6.529% | 29.6% | 95% | 0% | 3441 | -51
[5 empty] | 2019-11-18 | 39 | 7723.5 | 3392 | -51 | 0 | 0 | 3443 | 3272.6298 | 3272.6298 | 3272.6298 | 473.5367 | 780 | 200 | 1453.5367 | 36.34% | 95% | 0% | -58.3524 | 3214.2774 | -2750 | -200 | 264.2774 | -6.607% | 29.6% | 95% | 0% | 3443 | -51
[5 empty] | 2019-11-18 | 40 | 7724 | 3331 | -52 | 0 | 0 | 3383 | 3178.648 | 3178.648 | 3178.648 | 473.5367 | 780 | 200 | 1453.5367 | 36.34% | 95% | 0% | -59.4966 | 3119.1514 | -2750 | -200 | 169.1514 | -4.229% | 29.6% | 95% | 0% | 3383 | -52
[5 empty] | 2019-11-18 | 41 | 7724.5 | 3202 | -52 | 0 | 0 | 3254 | 2976.587 | 2976.587 | 2976.587 | 473.5367 | 780 | 200 | 1453.5367 | 36.34% | 95% | 0% | -59.4966 | 2917.0904 | -2750 | -200 | -32.9096 | 0.8227% | 29.6% | 95% | 0% | 3254 | -52
[5 empty] | 2019-11-18 | 42 | 7725 | 3098 | -52 | 0 | 0 | 3150 | 2813.6851 | 2813.6851 | 2813.6851 | 473.5367 | 780 | 200 | 1453.5367 | 36.34% | 95% | 0% | -59.4966 | 2754.1885 | -2750 | -200 | -195.8115 | 4.895% | 29.59% | 95% | 0% | 3150 | -52
[5 empty] | 2019-11-18 | 43 | 7725.5 | 2981 | -52 | 0 | 0 | 3033 | 2630.4204 | 2630.4204 | 2630.4204 | 473.5367 | 780 | 200 | 1453.5367 | 36.34% | 95% | 0% | -59.4966 | 2570.9239 | -2750 | -200 | -379.0761 | 9.477% | 29.58% | 95% | 0% | 3033 | -52
[5 empty] | 2019-11-18 | 44 | 7726 | 2811 | -52 | 0 | 0 | 2863 | 2364.1385 | 2364.1385 | 2364.1385 | 473.5367 | 780 | 200 | 1453.5367 | 36.34% | 95% | 0% | -59.4966 | 2304.6419 | -2750 | -200 | -645.3581 | 16.13% | 29.58% | 95% | 0% | 2863 | -52
[5 empty] | 2019-11-18 | 45 | 7726.5 | 2626 | -52 | 0 | 0 | 2678 | 2074.3611 | 2074.3611 | 2074.3611 | 473.5367 | 780 | 200 | 1453.5367 | 36.34% | 95% | 0% | -59.4966 | 2014.8645 | -2750 | -200 | -935.1355 | 23.38% | 29.57% | 95% | 0% | 2678 | -52
[5 empty] | 2019-11-18 | 46 | 7727 | 2499 | -51 | 0 | 0 | 2550 | 1873.8664 | 1873.8664 | 1873.8664 | 473.5367 | 780 | 200 | 1453.5367 | 36.34% | 95% | 0% | -58.3524 | 1815.514 | -2750 | -200 | -1134.486 | 28.36% | 29.56% | 95% | 0% | 2550 | -51
[5 empty] | 2019-11-18 | 47 | 7727.5 | 2334 | -50 | 0 | 0 | 2384 | 1613.85 | 1613.85 | 1613.85 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -57.2082 | 1556.6417 | -2750 | -200 | -1393.3583 | 34.83% | 29.55% | 95% | 0% | 2384 | -50
[5 empty] | 2019-11-18 | 48 | 7728 | 2225 | -50 | 0 | 0 | 2275 | 1443.1162 | 1443.1162 | 1443.1162 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -57.2082 | 1385.908 | -2750 | -200 | -1564.092 | 39.1% | 29.54% | 95% | 0% | 2275 | -50
[5 empty] | 2019-11-19 | 1 | 7728.5 | 2206 | -49 | 0 | 0 | 2255 | 1411.789 | 1411.789 | 1411.789 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -56.0641 | 1355.7249 | -2750 | -200 | -1594.2751 | 39.86% | 29.54% | 95% | 0% | 2255 | -49
[5 empty] | 2019-11-19 | 2 | 7729 | 2206 | -48 | 0 | 0 | 2254 | 1410.2226 | 1410.2226 | 1410.2226 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -54.9199 | 1355.3027 | -2750 | -200 | -1594.6973 | 39.87% | 29.54% | 95% | 0% | 2254 | -48
[5 empty] | 2019-11-19 | 3 | 7729.5 | 2191 | -48 | 0 | 0 | 2239 | 1386.7271 | 1386.7271 | 1386.7271 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -54.9199 | 1331.8072 | -2750 | -200 | -1618.1928 | 40.45% | 29.52% | 95% | 0% | 2239 | -48
[5 empty] | 2019-11-19 | 4 | 7730 | 2152 | -47 | 0 | 0 | 2199 | 1324.0725 | 1324.0725 | 1324.0725 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -53.7757 | 1270.2968 | -2750 | -200 | -1679.7032 | 41.99% | 29.52% | 95% | 0% | 2199 | -47
[5 empty] | 2019-11-19 | 5 | 7730.5 | 2130 | -48 | 0 | 0 | 2178 | 1291.1789 | 1291.1789 | 1291.1789 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -54.9199 | 1236.259 | -2750 | -200 | -1713.741 | 42.84% | 29.49% | 95% | 0% | 2178 | -48
[5 empty] | 2019-11-19 | 6 | 7731 | 2124 | -48 | 0 | 0 | 2172 | 1281.7807 | 1281.7807 | 1281.7807 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -54.9199 | 1226.8608 | -2750 | -200 | -1723.1392 | 43.08% | 29.49% | 95% | 0% | 2172 | -48
[5 empty] | 2019-11-19 | 7 | 7731.5 | 2090 | -50 | 0 | 0 | 2140 | 1231.657 | 1231.657 | 1231.657 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -57.2082 | 1174.4488 | -2750 | -200 | -1775.5512 | 44.39% | 29.48% | 95% | 0% | 2140 | -50
[5 empty] | 2019-11-19 | 8 | 7732 | 2063 | -53 | 0 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -60.6407 | 1133.4236 | -2750 | -200 | -1816.5764 | 45.41% | 29.47% | 95% | 0% | 2116 | -53
[5 empty] | 2019-11-19 | 9 | 7732.5 | 2062 | -54 | 0 | 0 | 2116 | 1194.0643 | 1194.0643 | 1194.0643 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -61.7849 | 1132.2794 | -2750 | -200 | -1817.7206 | 45.44% | 29.45% | 95% | 0% | 2116 | -54
[5 empty] | 2019-11-19 | 10 | 7733 | 2074 | -54 | 0 | 0 | 2128 | 1212.8607 | 1212.8607 | 1212.8607 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -61.7849 | 1151.0758 | -2750 | -200 | -1798.9242 | 44.97% | 29.43% | 95% | 0% | 2128 | -54
[5 empty] | 2019-11-19 | 11 | 7733.5 | 2149 | -55 | 0 | 0 | 2204 | 1331.9044 | 1331.9044 | 1331.9044 | 471.9703 | 780 | 200 | 1451.9703 | 36.3% | 95% | 0% | -62.9291 | 1268.9753 | -2750 | -200 | -1681.0247 | 42.03% | 29.41% | 95% | 0% | 2204 | -55
[5 empty] | 2019-11-19 | 12 | 7734 | 2266 | -56 | 0 | 0 | 2322 | 1516.7354 | 1516.7354 | 1516.7354 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -64.0732 | 1452.6621 | -2750 | -200 | -1497.3379 | 37.43% | 29.41% | 95% | 0% | 2322 | -56
[5 empty] | 2019-11-19 | 13 | 7734.5 | 2519 | -56 | 0 | 0 | 2575 | 1913.0256 | 1913.0256 | 1913.0256 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -64.0732 | 1848.9523 | -2750 | -200 | -1101.0477 | 27.53% | 29.4% | 95% | 0% | 2575 | -56
[5 empty] | 2019-11-19 | 14 | 7735 | 2754 | -56 | 0 | 0 | 2810 | 2281.1212 | 2281.1212 | 2281.1212 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -64.0732 | 2217.048 | -2750 | -200 | -732.952 | 18.32% | 29.39% | 95% | 0% | 2810 | -56
[5 empty] | 2019-11-19 | 15 | 7735.5 | 3012 | -58 | 0 | 0 | 3070 | 2688.3759 | 2688.3759 | 2688.3759 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -66.3616 | 2622.0144 | -2750 | -200 | -327.9856 | 8.2% | 29.39% | 95% | 0% | 3070 | -58
[5 empty] | 2019-11-19 | 16 | 7736 | 3109 | -67 | 0 | 0 | 3176 | 2854.4106 | 2854.4106 | 2854.4106 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -76.659 | 2777.7515 | -2750 | -200 | -172.2485 | 4.306% | 29.38% | 95% | 0% | 3176 | -67
[5 empty] | 2019-11-19 | 17 | 7736.5 | 3123 | -104 | 0 | 0 | 3227 | 2934.2951 | 2934.2951 | 2934.2951 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -118.9931 | 2815.302 | -2750 | -200 | -134.698 | 3.367% | 29.38% | 95% | 0% | 3227 | -104
[5 empty] | 2019-11-19 | 18 | 7737 | 3082 | -151 | 1 | 0 | 3233 | 2943.6933 | 2943.6933 | 2943.6933 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -172.7689 | 2770.9244 | -3550 | -400 | -1179.0756 | 29.48% | 29.37% | 95% | 0% | 3233 | -151
[5 empty] | 2019-11-19 | 19 | 7737.5 | 3052 | -194 | 1 | 0 | 3246 | 2964.0561 | 2964.0561 | 2964.0561 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -221.968 | 2742.0881 | -3550 | -400 | -1207.9119 | 30.2% | 29.37% | 95% | 0% | 3246 | -194
[5 empty] | 2019-11-19 | 20 | 7738 | 3044 | -220 | 1 | 0 | 3264 | 2992.2506 | 2992.2506 | 2992.2506 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -251.7162 | 2740.5344 | -3550 | -400 | -1209.4656 | 30.24% | 29.37% | 95% | 0% | 3264 | -220
[5 empty] | 2019-11-19 | 21 | 7738.5 | 2991 | -249 | 1 | 0 | 3240 | 2954.6579 | 2954.6579 | 2954.6579 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -284.897 | 2669.7608 | -3550 | -400 | -1280.2392 | 32.01% | 29.35% | 95% | 0% | 3240 | -249
[5 empty] | 2019-11-19 | 22 | 7739 | 2965 | -252 | 1 | 0 | 3217 | 2918.6315 | 2918.6315 | 2918.6315 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -288.3295 | 2630.302 | -3550 | -400 | -1319.698 | 32.99% | 29.34% | 95% | 0% | 3217 | -252
[5 empty] | 2019-11-19 | 23 | 7739.5 | 2950 | -249 | 1 | 0 | 3199 | 2890.4369 | 2890.4369 | 2890.4369 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -284.897 | 2605.5399 | -3550 | -400 | -1344.4601 | 33.61% | 29.34% | 95% | 0% | 3199 | -249
[5 empty] | 2019-11-19 | 24 | 7740 | 2940 | -254 | 1 | 0 | 3194 | 2882.6051 | 2882.6051 | 2882.6051 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -290.6178 | 2591.9873 | -3550 | -400 | -1358.0127 | 33.95% | 29.32% | 95% | 0% | 3194 | -254
[5 empty] | 2019-11-19 | 25 | 7740.5 | 2980 | -253 | 1 | 0 | 3233 | 2943.6933 | 2943.6933 | 2943.6933 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -289.4737 | 2654.2196 | -3550 | -400 | -1295.7804 | 32.39% | 29.31% | 95% | 0% | 3233 | -253
[5 empty] | 2019-11-19 | 26 | 7741 | 3007 | -235 | 1 | 0 | 3242 | 2957.7906 | 2957.7906 | 2957.7906 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -268.8787 | 2688.9119 | -3550 | -400 | -1261.0881 | 31.53% | 29.31% | 95% | 0% | 3242 | -235
[5 empty] | 2019-11-19 | 27 | 7741.5 | 3061 | -201 | 1 | 0 | 3262 | 2989.1179 | 2989.1179 | 2989.1179 | 470.404 | 780 | 200 | 1450.404 | 36.26% | 95% | 0% | -229.9771 | 2759.1408 | -3550 | -400 | -1190.8592 | 29.77% | 29.3% | 95% | 0% | 3262 | -201
[5 empty] | 2019-11-19 | 28 | 7742 | 3056 | -194 | 1 | 0 | 3250 | 2970.3215 | 2970.3215 | 2970.3215 | 468.8376 | 780 | 200 | 1448.8376 | 36.22% | 95% | 0% | -221.968 | 2748.3536 | -3550 | -400 | -1201.6464 | 30.04% | 29.25% | 95% | 0% | 3250 | -194
[5 empty] | 2019-11-19 | 29 | 7742.5 | 3079 | -170 | 1 | 0 | 3249 | 2968.7552 | 2968.7552 | 2968.7552 | 468.8376 | 780 | 200 | 1448.8376 | 36.22% | 95% | 0% | -194.508 | 2774.2471 | -3550 | -400 | -1175.7529 | 29.39% | 29.25% | 95% | 0% | 3249 | -170
[5 empty] | 2019-11-19 | 30 | 7743 | 3111 | -141 | 1 | 0 | 3252 | 2973.4542 | 2973.4542 | 2973.4542 | 468.8376 | 780 | 200 | 1448.8376 | 36.22% | 95% | 0% | -161.3272 | 2812.127 | -3550 | -400 | -1137.873 | 28.45% | 29.24% | 95% | 0% | 3252 | -141
[5 empty] | 2019-11-19 | 31 | 7743.5 | 3144 | -116 | 1 | 0 | 3260 | 2985.9852 | 2985.9852 | 2985.9852 | 468.8376 | 780 | 200 | 1448.8376 | 36.22% | 95% | 0% | -132.7231 | 2853.262 | -3550 | -400 | -1096.738 | 27.42% | 29.23% | 95% | 0% | 3260 | -116
[5 empty] | 2019-11-19 | 32 | 7744 | 3246 | -102 | 1 | 0 | 3348 | 3123.8252 | 3123.8252 | 3123.8252 | 468.8376 | 780 | 200 | 1448.8376 | 36.22% | 95% | 0% | -116.7048 | 3007.1204 | -3550 | -400 | -942.8796 | 23.57% | 29.23% | 95% | 0% | 3348 | -102
[5 empty] | 2019-11-19 | 33 | 7744.5 | 3338 | -100 | 1 | 0 | 3438 | 3264.798 | 3264.798 | 3264.798 | 468.8376 | 780 | 200 | 1448.8376 | 36.22% | 95% | 0% | -114.4165 | 3150.3815 | -3550 | -400 | -799.6185 | 19.99% | 29.22% | 95% | 0% | 3438 | -100
[5 empty] | 2019-11-19 | 34 | 7745 | 3353 | -102 | 1 | 0 | 3455 | 3291.4262 | 3291.4262 | 3291.4262 | 468.8376 | 780 | 200 | 1448.8376 | 36.22% | 95% | 0% | -116.7048 | 3174.7214 | -3550 | -400 | -775.2786 | 19.38% | 29.22% | 95% | 0% | 3455 | -102
[5 empty] | 2019-11-19 | 35 | 7745.5 | 3361 | -104 | 0 | 0 | 3465 | 3307.0899 | 3307.0899 | 3307.0899 | 468.8376 | 780 | 200 | 1448.8376 | 36.22% | 95% | 0% | -118.9931 | 3188.0967 | -2750 | -200 | 238.0967 | -5.952% | 29.21% | 95% | 0% | 3465 | -104
[5 empty] | 2019-11-19 | 36 | 7746 | 3346 | -106 | 0 | 0 | 3452 | 3286.7271 | 3286.7271 | 3286.7271 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -121.2815 | 3165.4457 | -2750 | -200 | 215.4457 | -5.386% | 29.21% | 95% | 0% | 3452 | -106
[5 empty] | 2019-11-19 | 37 | 7746.5 | 3332 | -107 | 0 | 0 | 3439 | 3266.3644 | 3266.3644 | 3266.3644 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -122.4256 | 3143.9388 | -2750 | -200 | 193.9388 | -4.848% | 29.18% | 95% | 0% | 3439 | -107
[5 empty] | 2019-11-19 | 38 | 7747 | 3333 | -109 | 0 | 0 | 3442 | 3271.0635 | 3271.0635 | 3271.0635 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -124.714 | 3146.3495 | -2750 | -200 | 196.3495 | -4.909% | 29.16% | 95% | 0% | 3442 | -109
[5 empty] | 2019-11-19 | 39 | 7747.5 | 3305 | -111 | 0 | 0 | 3416 | 3230.338 | 3230.338 | 3230.338 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -127.0023 | 3103.3357 | -2750 | -200 | 153.3357 | -3.833% | 29.16% | 95% | 0% | 3416 | -111
[5 empty] | 2019-11-19 | 40 | 7748 | 3233 | -112 | 0 | 0 | 3345 | 3119.1261 | 3119.1261 | 3119.1261 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -128.1465 | 2990.9797 | -2750 | -200 | 40.9797 | -1.024% | 29.16% | 95% | 0% | 3345 | -112
[5 empty] | 2019-11-19 | 41 | 7748.5 | 3122 | -114 | 0 | 0 | 3236 | 2948.3924 | 2948.3924 | 2948.3924 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -130.4348 | 2817.9576 | -2750 | -200 | -132.0424 | 3.301% | 29.14% | 95% | 0% | 3236 | -114
[5 empty] | 2019-11-19 | 42 | 7749 | 2998 | -116 | 0 | 0 | 3114 | 2757.296 | 2757.296 | 2757.296 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -132.7231 | 2624.5728 | -2750 | -200 | -325.4272 | 8.136% | 29.12% | 95% | 0% | 3114 | -116
[5 empty] | 2019-11-19 | 43 | 7749.5 | 2853 | -117 | 0 | 0 | 2970 | 2531.7395 | 2531.7395 | 2531.7395 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -133.8673 | 2397.8722 | -2750 | -200 | -552.1278 | 13.8% | 29.12% | 95% | 0% | 2970 | -117
[5 empty] | 2019-11-19 | 44 | 7750 | 2680 | -118 | 0 | 0 | 2798 | 2262.3248 | 2262.3248 | 2262.3248 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -135.0114 | 2127.3134 | -2750 | -200 | -822.6866 | 20.57% | 29.11% | 95% | 0% | 2798 | -118
[5 empty] | 2019-11-19 | 45 | 7750.5 | 2493 | -119 | 0 | 0 | 2612 | 1970.981 | 1970.981 | 1970.981 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -136.1556 | 1834.8254 | -2750 | -200 | -1115.1746 | 27.88% | 29.11% | 95% | 0% | 2612 | -119
[5 empty] | 2019-11-19 | 46 | 7751 | 2315 | -119 | 0 | 0 | 2434 | 1692.1682 | 1692.1682 | 1692.1682 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -136.1556 | 1556.0126 | -2750 | -200 | -1393.9874 | 34.85% | 29.09% | 95% | 0% | 2434 | -119
[5 empty] | 2019-11-19 | 47 | 7751.5 | 2149 | -123 | 0 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -140.7323 | 1297.6849 | -2750 | -200 | -1652.3151 | 41.31% | 29.09% | 95% | 0% | 2272 | -123
[5 empty] | 2019-11-19 | 48 | 7752 | 2030 | -126 | 0 | 0 | 2156 | 1256.7189 | 1256.7189 | 1256.7189 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -144.1648 | 1112.5541 | -2750 | -200 | -1837.4459 | 45.94% | 29.08% | 95% | 0% | 2156 | -126
[5 empty] | 2019-11-20 | 1 | 7752.5 | 2003 | -126 | 0 | 0 | 2129 | 1214.427 | 1214.427 | 1214.427 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -144.1648 | 1070.2623 | -2750 | -200 | -1879.7377 | 46.99% | 29.06% | 95% | 0% | 2129 | -126
[5 empty] | 2019-11-20 | 2 | 7753 | 2028 | -126 | 0 | 0 | 2154 | 1253.5862 | 1253.5862 | 1253.5862 | 467.2712 | 780 | 200 | 1447.2712 | 36.18% | 95% | 0% | -144.1648 | 1109.4214 | -2750 | -200 | -1840.5786 | 46.01% | 29.02% | 95% | 0% | 2154 | -126
[5 empty] | 2019-11-20 | 3 | 7753.5 | 2007 | -126 | 0 | 0 | 2133 | 1220.6925 | 1220.6925 | 1220.6925 | 465.7049 | 780 | 200 | 1445.7049 | 36.14% | 95% | 0% | -144.1648 | 1076.5277 | -2750 | -200 | -1873.4723 | 46.84% | 29.01% | 95% | 0% | 2133 | -126
[5 empty] | 2019-11-20 | 4 | 7754 | 1961 | -126 | 0 | 0 | 2087 | 1148.6397 | 1148.6397 | 1148.6397 | 465.7049 | 780 | 200 | 1445.7049 | 36.14% | 95% | 0% | -144.1648 | 1004.475 | -2750 | -200 | -1945.525 | 48.64% | 28.99% | 95% | 0% | 2087 | -126
[5 empty] | 2019-11-20 | 5 | 7754.5 | 1934 | -126 | 0 | 0 | 2060 | 1106.3479 | 1106.3479 | 1106.3479 | 465.7049 | 780 | 200 | 1445.7049 | 36.14% | 95% | 0% | -144.1648 | 962.1831 | -2750 | -200 | -1987.8169 | 49.7% | 28.99% | 95% | 0% | 2060 | -126
[5 empty] | 2019-11-20 | 6 | 7755 | 1909 | -125 | 0 | 0 | 2034 | 1065.6224 | 1065.6224 | 1065.6224 | 465.7049 | 780 | 200 | 1445.7049 | 36.14% | 95% | 0% | -143.0206 | 922.6018 | -2750 | -200 | -2027.3982 | 50.68% | 28.99% | 95% | 0% | 2034 | -125
[5 empty] | 2019-11-20 | 7 | 7755.5 | 1874 | -126 | 0 | 0 | 2000 | 1012.366 | 1012.366 | 1012.366 | 465.7049 | 780 | 200 | 1445.7049 | 36.14% | 95% | 0% | -144.1648 | 868.2013 | -2750 | -200 | -2081.7987 | 52.04% | 28.97% | 95% | 0% | 2000 | -126
[5 empty] | 2019-11-20 | 8 | 7756 | 1852 | -127 | 0 | 0 | 1979 | 979.4724 | 979.4724 | 979.4724 | 465.7049 | 780 | 200 | 1445.7049 | 36.14% | 95% | 0% | -145.3089 | 834.1635 | -2750 | -200 | -2115.8365 | 52.9% | 28.92% | 95% | 0% | 1979 | -127
[5 empty] | 2019-11-20 | 9 | 7756.5 | 1828 | -128 | 0 | 0 | 1956 | 943.446 | 943.446 | 943.446 | 464.1385 | 780 | 200 | 1444.1385 | 36.1% | 95% | 0% | -146.4531 | 796.9929 | -2750 | -200 | -2153.0071 | 53.83% | 28.91% | 95% | 0% | 1956 | -128
[5 empty] | 2019-11-20 | 10 | 7757 | 1834 | -130 | 0 | 0 | 1964 | 955.9769 | 955.9769 | 955.9769 | 464.1385 | 780 | 200 | 1444.1385 | 36.1% | 95% | 0% | -148.7414 | 807.2355 | -2750 | -200 | -2142.7645 | 53.57% | 28.91% | 95% | 0% | 1964 | -130
[5 empty] | 2019-11-20 | 11 | 7757.5 | 1915 | -131 | 0 | 0 | 2046 | 1084.4188 | 1084.4188 | 1084.4188 | 464.1385 | 780 | 200 | 1444.1385 | 36.1% | 95% | 0% | -149.8856 | 934.5332 | -2750 | -200 | -2015.4668 | 50.39% | 28.91% | 95% | 0% | 2046 | -131
[5 empty] | 2019-11-20 | 12 | 7758 | 2023 | -132 | 0 | 0 | 2155 | 1255.1525 | 1255.1525 | 1255.1525 | 464.1385 | 780 | 200 | 1444.1385 | 36.1% | 95% | 0% | -151.0297 | 1104.1228 | -2750 | -200 | -1845.8772 | 46.15% | 28.89% | 95% | 0% | 2155 | -132
[5 empty] | 2019-11-20 | 13 | 7758.5 | 2278 | -134 | 0 | 0 | 2412 | 1657.7082 | 1657.7082 | 1657.7082 | 464.1385 | 780 | 200 | 1444.1385 | 36.1% | 95% | 0% | -153.3181 | 1504.3901 | -2750 | -200 | -1445.6099 | 36.14% | 28.88% | 95% | 0% | 2412 | -134
[5 empty] | 2019-11-20 | 14 | 7759 | 2522 | -136 | 0 | 0 | 2658 | 2043.0338 | 2043.0338 | 2043.0338 | 462.5721 | 780 | 200 | 1442.5721 | 36.06% | 95% | 0% | -155.6064 | 1887.4274 | -2750 | -200 | -1062.5726 | 26.56% | 28.88% | 95% | 0% | 2658 | -136
[5 empty] | 2019-11-20 | 15 | 7759.5 | 2790 | -138 | 0 | 0 | 2928 | 2465.9522 | 2465.9522 | 2465.9522 | 462.5721 | 780 | 200 | 1442.5721 | 36.06% | 95% | 0% | -157.8947 | 2308.0574 | -2750 | -200 | -641.9426 | 16.05% | 28.87% | 95% | 0% | 2928 | -138
[5 empty] | 2019-11-20 | 16 | 7760 | 2871 | -143 | 0 | 0 | 3014 | 2600.6595 | 2600.6595 | 2600.6595 | 462.5721 | 780 | 200 | 1442.5721 | 36.06% | 95% | 0% | -163.6156 | 2437.044 | -2750 | -200 | -512.956 | 12.82% | 28.87% | 95% | 0% | 3014 | -143
[5 empty] | 2019-11-20 | 17 | 7760.5 | 2899 | -161 | 0 | 0 | 3060 | 2672.7123 | 2672.7123 | 2672.7123 | 462.5721 | 780 | 200 | 1442.5721 | 36.06% | 95% | 0% | -184.2105 | 2488.5018 | -2750 | -200 | -461.4982 | 11.54% | 28.87% | 95% | 0% | 3060 | -161
[5 empty] | 2019-11-20 | 18 | 7761 | 2851 | -197 | 0 | 0 | 3048 | 2653.9159 | 2653.9159 | 2653.9159 | 462.5721 | 780 | 200 | 1442.5721 | 36.06% | 95% | 0% | -225.4005 | 2428.5155 | -2750 | -200 | -521.4845 | 13.04% | 28.87% | 95% | 0% | 3048 | -197
[5 empty] | 2019-11-20 | 19 | 7761.5 | 2827 | -239 | 1 | 0 | 3066 | 2682.1105 | 2682.1105 | 2682.1105 | 462.5721 | 780 | 200 | 1442.5721 | 36.06% | 95% | 0% | -273.4554 | 2408.6551 | -3550 | -400 | -1541.3449 | 38.53% | 28.86% | 95% | 0% | 3066 | -239
[5 empty] | 2019-11-20 | 20 | 7762 | 2802 | -276 | 1 | 0 | 3078 | 2700.9068 | 2700.9068 | 2700.9068 | 462.5721 | 780 | 200 | 1442.5721 | 36.06% | 95% | 0% | -315.7895 | 2385.1174 | -3550 | -400 | -1564.8826 | 39.12% | 28.85% | 95% | 0% | 3078 | -276
[5 empty] | 2019-11-20 | 21 | 7762.5 | 2756 | -320 | 1 | 0 | 3076 | 2697.7741 | 2697.7741 | 2697.7741 | 462.5721 | 780 | 200 | 1442.5721 | 36.06% | 95% | 0% | -366.1327 | 2331.6414 | -3550 | -400 | -1618.3586 | 40.46% | 28.85% | 95% | 0% | 3076 | -320
[5 empty] | 2019-11-20 | 22 | 7763 | 2720 | -332 | 1 | 0 | 3052 | 2660.1814 | 2660.1814 | 2660.1814 | 462.5721 | 780 | 200 | 1442.5721 | 36.06% | 95% | 0% | -379.8627 | 2280.3187 | -3550 | -400 | -1669.6813 | 41.74% | 28.83% | 95% | 0% | 3052 | -332
[5 empty] | 2019-11-20 | 23 | 7763.5 | 2701 | -339 | 1 | 0 | 3040 | 2641.385 | 2641.385 | 2641.385 | 462.5721 | 780 | 200 | 1442.5721 | 36.06% | 95% | 0% | -387.8719 | 2253.5131 | -3550 | -400 | -1696.4869 | 42.41% | 28.83% | 95% | 0% | 3040 | -339
[5 empty] | 2019-11-20 | 24 | 7764 | 2681 | -350 | 1 | 0 | 3031 | 2627.2877 | 2627.2877 | 2627.2877 | 462.5721 | 780 | 200 | 1442.5721 | 36.06% | 95% | 0% | -400.4577 | 2226.8301 | -3550 | -400 | -1723.1699 | 43.08% | 28.81% | 95% | 0% | 3031 | -350
[5 empty] | 2019-11-20 | 25 | 7764.5 | 2687 | -348 | 1 | 0 | 3035 | 2633.5532 | 2633.5532 | 2633.5532 | 461.0058 | 780 | 200 | 1441.0058 | 36.03% | 95% | 0% | -398.1693 | 2235.3838 | -3550 | -400 | -1714.6162 | 42.87% | 28.78% | 95% | 0% | 3035 | -348
[5 empty] | 2019-11-20 | 26 | 7765 | 2693 | -340 | 1 | 0 | 3033 | 2630.4204 | 2630.4204 | 2630.4204 | 461.0058 | 780 | 200 | 1441.0058 | 36.03% | 95% | 0% | -389.016 | 2241.4044 | -3550 | -400 | -1708.5956 | 42.71% | 28.77% | 95% | 0% | 3033 | -340
[5 empty] | 2019-11-20 | 27 | 7765.5 | 2734 | -316 | 1 | 0 | 3050 | 2657.0486 | 2657.0486 | 2657.0486 | 461.0058 | 780 | 200 | 1441.0058 | 36.03% | 95% | 0% | -361.5561 | 2295.4926 | -3550 | -400 | -1654.5074 | 41.36% | 28.76% | 95% | 0% | 3050 | -316
[5 empty] | 2019-11-20 | 28 | 7766 | 2765 | -288 | 1 | 0 | 3053 | 2661.7477 | 2661.7477 | 2661.7477 | 461.0058 | 780 | 200 | 1441.0058 | 36.03% | 95% | 0% | -329.5195 | 2332.2283 | -3550 | -400 | -1617.7717 | 40.44% | 28.75% | 95% | 0% | 3053 | -288
[5 empty] | 2019-11-20 | 29 | 7766.5 | 2813 | -255 | 1 | 0 | 3068 | 2685.2432 | 2685.2432 | 2685.2432 | 461.0058 | 780 | 200 | 1441.0058 | 36.03% | 95% | 0% | -291.762 | 2393.4812 | -3550 | -400 | -1556.5188 | 38.91% | 28.74% | 95% | 0% | 3068 | -255
[5 empty] | 2019-11-20 | 30 | 7767 | 2842 | -221 | 1 | 0 | 3063 | 2677.4114 | 2677.4114 | 2677.4114 | 461.0058 | 780 | 200 | 1441.0058 | 36.03% | 95% | 0% | -252.8604 | 2424.551 | -3550 | -400 | -1525.449 | 38.14% | 28.73% | 95% | 0% | 3063 | -221
[5 empty] | 2019-11-20 | 31 | 7767.5 | 2920 | -188 | 1 | 0 | 3108 | 2747.8978 | 2747.8978 | 2747.8978 | 459.4394 | 780 | 200 | 1439.4394 | 35.99% | 95% | 0% | -215.103 | 2532.7948 | -3550 | -400 | -1417.2052 | 35.43% | 28.73% | 95% | 0% | 3108 | -188
[5 empty] | 2019-11-20 | 32 | 7768 | 3043 | -165 | 1 | 0 | 3208 | 2904.5342 | 2904.5342 | 2904.5342 | 459.4394 | 780 | 200 | 1439.4394 | 35.99% | 95% | 0% | -188.7872 | 2715.747 | -3550 | -400 | -1234.253 | 30.86% | 28.71% | 95% | 0% | 3208 | -165
[5 empty] | 2019-11-20 | 33 | 7768.5 | 3180 | -159 | 0 | 0 | 3339 | 3109.7279 | 3109.7279 | 3109.7279 | 459.4394 | 780 | 200 | 1439.4394 | 35.99% | 95% | 0% | -181.9222 | 2927.8058 | -2750 | -200 | -22.1942 | 0.5549% | 28.7% | 95% | 0% | 3339 | -159
[5 empty] | 2019-11-20 | 34 | 7769 | 3263 | -159 | 0 | 0 | 3422 | 3239.7362 | 3239.7362 | 3239.7362 | 459.4394 | 780 | 200 | 1439.4394 | 35.99% | 95% | 0% | -181.9222 | 3057.814 | -2750 | -200 | 107.814 | -2.695% | 28.69% | 95% | 0% | 3422 | -159
[5 empty] | 2019-11-20 | 35 | 7769.5 | 3258 | -159 | 0 | 0 | 3417 | 3231.9044 | 3231.9044 | 3231.9044 | 459.4394 | 780 | 200 | 1439.4394 | 35.99% | 95% | 0% | -181.9222 | 3049.9822 | -2750 | -200 | 99.9822 | -2.5% | 28.67% | 95% | 0% | 3417 | -159
[5 empty] | 2019-11-20 | 36 | 7770 | 3233 | -160 | 0 | 0 | 3393 | 3194.3116 | 3194.3116 | 3194.3116 | 459.4394 | 780 | 200 | 1439.4394 | 35.99% | 95% | 0% | -183.0664 | 3011.2453 | -2750 | -200 | 61.2453 | -1.531% | 28.67% | 95% | 0% | 3393 | -160
[5 empty] | 2019-11-20 | 37 | 7770.5 | 3214 | -161 | 0 | 0 | 3375 | 3166.1171 | 3166.1171 | 3166.1171 | 459.4394 | 780 | 200 | 1439.4394 | 35.99% | 95% | 0% | -184.2105 | 2981.9065 | -2750 | -200 | 31.9065 | -0.7977% | 28.67% | 95% | 0% | 3375 | -161
[5 empty] | 2019-11-20 | 38 | 7771 | 3194 | -161 | 0 | 0 | 3355 | 3134.7898 | 3134.7898 | 3134.7898 | 459.4394 | 780 | 200 | 1439.4394 | 35.99% | 95% | 0% | -184.2105 | 2950.5793 | -2750 | -200 | 0.57925 | -0.01448% | 28.65% | 95% | 0% | 3355 | -161
[5 empty] | 2019-11-20 | 39 | 7771.5 | 3178 | -160 | 0 | 0 | 3338 | 3108.1616 | 3108.1616 | 3108.1616 | 459.4394 | 780 | 200 | 1439.4394 | 35.99% | 95% | 0% | -183.0664 | 2925.0952 | -2750 | -200 | -24.9048 | 0.6226% | 28.64% | 95% | 0% | 3338 | -160
[5 empty] | 2019-11-20 | 40 | 7772 | 3111 | -158 | 0 | 0 | 3269 | 3000.0824 | 3000.0824 | 3000.0824 | 459.4394 | 780 | 200 | 1439.4394 | 35.99% | 95% | 0% | -180.778 | 2819.3044 | -2750 | -200 | -130.6956 | 3.267% | 28.64% | 95% | 0% | 3269 | -158
[5 empty] | 2019-11-20 | 41 | 7772.5 | 2996 | -158 | 0 | 0 | 3154 | 2819.9505 | 2819.9505 | 2819.9505 | 459.4394 | 780 | 200 | 1439.4394 | 35.99% | 95% | 0% | -180.778 | 2639.1725 | -2750 | -200 | -310.8275 | 7.771% | 28.62% | 95% | 0% | 3154 | -158
[5 empty] | 2019-11-20 | 42 | 7773 | 2863 | -158 | 0 | 0 | 3021 | 2611.6241 | 2611.6241 | 2611.6241 | 457.873 | 780 | 200 | 1437.873 | 35.95% | 95% | 0% | -180.778 | 2430.846 | -2750 | -200 | -519.154 | 12.98% | 28.59% | 95% | 0% | 3021 | -158
[5 empty] | 2019-11-20 | 43 | 7773.5 | 2711 | -156 | 0 | 0 | 2867 | 2370.404 | 2370.404 | 2370.404 | 457.873 | 780 | 200 | 1437.873 | 35.95% | 95% | 0% | -178.4897 | 2191.9143 | -2750 | -200 | -758.0857 | 18.95% | 28.59% | 95% | 0% | 2867 | -156
[5 empty] | 2019-11-20 | 44 | 7774 | 2531 | -155 | 0 | 0 | 2686 | 2086.892 | 2086.892 | 2086.892 | 457.873 | 780 | 200 | 1437.873 | 35.95% | 95% | 0% | -177.3455 | 1909.5465 | -2750 | -200 | -1040.4535 | 26.01% | 28.59% | 95% | 0% | 2686 | -155
[5 empty] | 2019-11-20 | 45 | 7774.5 | 2363 | -153 | 0 | 0 | 2516 | 1820.6101 | 1820.6101 | 1820.6101 | 457.873 | 780 | 200 | 1437.873 | 35.95% | 95% | 0% | -175.0572 | 1645.5528 | -2750 | -200 | -1304.4472 | 32.61% | 28.58% | 95% | 0% | 2516 | -153
[5 empty] | 2019-11-20 | 46 | 7775 | 2225 | -152 | 0 | 0 | 2377 | 1602.8854 | 1602.8854 | 1602.8854 | 456.3067 | 780 | 200 | 1436.3067 | 35.91% | 95% | 0% | -173.913 | 1428.9724 | -2750 | -200 | -1521.0276 | 38.03% | 28.58% | 95% | 0% | 2377 | -152
[5 empty] | 2019-11-20 | 47 | 7775.5 | 2057 | -152 | 0 | 0 | 2209 | 1339.7362 | 1339.7362 | 1339.7362 | 456.3067 | 780 | 200 | 1436.3067 | 35.91% | 95% | 0% | -173.913 | 1165.8231 | -2750 | -200 | -1784.1769 | 44.6% | 28.58% | 95% | 0% | 2209 | -152
[5 empty] | 2019-11-20 | 48 | 7776 | 1953 | -152 | 0 | 0 | 2105 | 1176.8343 | 1176.8343 | 1176.8343 | 456.3067 | 780 | 200 | 1436.3067 | 35.91% | 95% | 0% | -173.913 | 1002.9213 | -2750 | -200 | -1947.0787 | 48.68% | 28.57% | 95% | 0% | 2105 | -152
[5 empty] | 2019-11-21 | 1 | 7776.5 | 1929 | -153 | 0 | 0 | 2082 | 1140.8079 | 1140.8079 | 1140.8079 | 456.3067 | 780 | 200 | 1436.3067 | 35.91% | 95% | 0% | -175.0572 | 965.7507 | -2750 | -200 | -1984.2493 | 49.61% | 28.57% | 95% | 0% | 2082 | -153
[5 empty] | 2019-11-21 | 2 | 7777 | 1954 | -153 | 0 | 0 | 2107 | 1179.967 | 1179.967 | 1179.967 | 456.3067 | 780 | 200 | 1436.3067 | 35.91% | 95% | 0% | -175.0572 | 1004.9098 | -2750 | -200 | -1945.0902 | 48.63% | 28.57% | 95% | 0% | 2107 | -153
[5 empty] | 2019-11-21 | 3 | 7777.5 | 1946 | -152 | 0 | 0 | 2098 | 1165.8697 | 1165.8697 | 1165.8697 | 456.3067 | 780 | 200 | 1436.3067 | 35.91% | 95% | 0% | -173.913 | 991.9567 | -2750 | -200 | -1958.0433 | 48.95% | 28.56% | 95% | 0% | 2098 | -152
[5 empty] | 2019-11-21 | 4 | 7778 | 1892 | -151 | 0 | 0 | 2043 | 1079.7197 | 1079.7197 | 1079.7197 | 456.3067 | 780 | 200 | 1436.3067 | 35.91% | 95% | 0% | -172.7689 | 906.9508 | -2750 | -200 | -2043.0492 | 51.08% | 28.56% | 95% | 0% | 2043 | -151
[5 empty] | 2019-11-21 | 5 | 7778.5 | 1847 | -150 | 0 | 0 | 1997 | 1007.6669 | 1007.6669 | 1007.6669 | 456.3067 | 780 | 200 | 1436.3067 | 35.91% | 95% | 0% | -171.6247 | 836.0422 | -2750 | -200 | -2113.9578 | 52.85% | 28.56% | 95% | 0% | 1997 | -150
[5 empty] | 2019-11-21 | 6 | 7779 | 1828 | -150 | 0 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 456.3067 | 780 | 200 | 1436.3067 | 35.91% | 95% | 0% | -171.6247 | 806.2813 | -2750 | -200 | -2143.7187 | 53.59% | 28.56% | 95% | 0% | 1978 | -150
[5 empty] | 2019-11-21 | 7 | 7779.5 | 1806 | -150 | 0 | 0 | 1956 | 943.446 | 943.446 | 943.446 | 454.7403 | 780 | 200 | 1434.7403 | 35.87% | 95% | 0% | -171.6247 | 771.8213 | -2750 | -200 | -2178.1787 | 54.45% | 28.54% | 95% | 0% | 1956 | -150
[5 empty] | 2019-11-21 | 8 | 7780 | 1765 | -150 | 0 | 0 | 1915 | 879.2251 | 879.2251 | 879.2251 | 454.7403 | 780 | 200 | 1434.7403 | 35.87% | 95% | 0% | -171.6247 | 707.6003 | -2750 | -200 | -2242.3997 | 56.06% | 28.53% | 95% | 0% | 1915 | -150
[5 empty] | 2019-11-21 | 9 | 7780.5 | 1751 | -150 | 0 | 0 | 1901 | 857.296 | 857.296 | 857.296 | 454.7403 | 780 | 200 | 1434.7403 | 35.87% | 95% | 0% | -171.6247 | 685.6712 | -2750 | -200 | -2264.3288 | 56.61% | 28.52% | 95% | 0% | 1901 | -150
[5 empty] | 2019-11-21 | 10 | 7781 | 1771 | -151 | 0 | 0 | 1922 | 890.1896 | 890.1896 | 890.1896 | 454.7403 | 780 | 200 | 1434.7403 | 35.87% | 95% | 0% | -172.7689 | 717.4207 | -2750 | -200 | -2232.5793 | 55.81% | 28.5% | 95% | 0% | 1922 | -151
[5 empty] | 2019-11-21 | 11 | 7781.5 | 1828 | -150 | 0 | 0 | 1978 | 977.906 | 977.906 | 977.906 | 454.7403 | 780 | 200 | 1434.7403 | 35.87% | 95% | 0% | -171.6247 | 806.2813 | -2750 | -200 | -2143.7187 | 53.59% | 28.5% | 95% | 0% | 1978 | -150
[5 empty] | 2019-11-21 | 12 | 7782 | 1958 | -150 | 0 | 0 | 2108 | 1181.5334 | 1181.5334 | 1181.5334 | 454.7403 | 780 | 200 | 1434.7403 | 35.87% | 95% | 0% | -171.6247 | 1009.9087 | -2750 | -200 | -1940.0913 | 48.5% | 28.5% | 95% | 0% | 2108 | -150
[5 empty] | 2019-11-21 | 13 | 7782.5 | 2202 | -150 | 0 | 0 | 2352 | 1563.7263 | 1563.7263 | 1563.7263 | 454.7403 | 780 | 200 | 1434.7403 | 35.87% | 95% | 0% | -171.6247 | 1392.1016 | -2750 | -200 | -1557.8984 | 38.95% | 28.47% | 95% | 0% | 2352 | -150
[5 empty] | 2019-11-21 | 14 | 7783 | 2452 | -150 | 0 | 0 | 2602 | 1955.3174 | 1955.3174 | 1955.3174 | 454.7403 | 780 | 200 | 1434.7403 | 35.87% | 95% | 0% | -171.6247 | 1783.6927 | -2750 | -200 | -1166.3073 | 29.16% | 28.46% | 95% | 0% | 2602 | -150
[5 empty] | 2019-11-21 | 15 | 7783.5 | 2732 | -150 | 0 | 0 | 2882 | 2393.8994 | 2393.8994 | 2393.8994 | 454.7403 | 780 | 200 | 1434.7403 | 35.87% | 95% | 0% | -171.6247 | 2222.2747 | -2750 | -200 | -727.7253 | 18.19% | 28.45% | 95% | 0% | 2882 | -150
[5 empty] | 2019-11-21 | 16 | 7784 | 2882 | -150 | 0 | 0 | 3032 | 2628.8541 | 2628.8541 | 2628.8541 | 454.7403 | 780 | 200 | 1434.7403 | 35.87% | 95% | 0% | -171.6247 | 2457.2294 | -2750 | -200 | -492.7706 | 12.32% | 28.45% | 95% | 0% | 3032 | -150
[5 empty] | 2019-11-21 | 17 | 7784.5 | 2947 | -158 | 0 | 0 | 3105 | 2743.1987 | 2743.1987 | 2743.1987 | 454.7403 | 780 | 200 | 1434.7403 | 35.87% | 95% | 0% | -180.778 | 2562.4206 | -2750 | -200 | -387.5794 | 9.689% | 28.45% | 95% | 0% | 3105 | -158
[5 empty] | 2019-11-21 | 18 | 7785 | 2952 | -175 | 0 | 0 | 3127 | 2777.6587 | 2777.6587 | 2777.6587 | 453.1739 | 780 | 200 | 1433.1739 | 35.83% | 95% | 0% | -200.2288 | 2577.4299 | -2750 | -200 | -372.5701 | 9.314% | 28.44% | 95% | 0% | 3127 | -175
[5 empty] | 2019-11-21 | 19 | 7785.5 | 2984 | -188 | 0 | 0 | 3172 | 2848.1451 | 2848.1451 | 2848.1451 | 453.1739 | 780 | 200 | 1433.1739 | 35.83% | 95% | 0% | -215.103 | 2633.0421 | -2750 | -200 | -316.9579 | 7.924% | 28.44% | 95% | 0% | 3172 | -188
[5 empty] | 2019-11-21 | 20 | 7786 | 2979 | -211 | 1 | 0 | 3190 | 2876.3397 | 2876.3397 | 2876.3397 | 453.1739 | 780 | 200 | 1433.1739 | 35.83% | 95% | 0% | -241.4188 | 2634.9209 | -3550 | -400 | -1315.0791 | 32.88% | 28.43% | 95% | 0% | 3190 | -211
[5 empty] | 2019-11-21 | 21 | 7786.5 | 2958 | -230 | 1 | 0 | 3188 | 2873.2069 | 2873.2069 | 2873.2069 | 453.1739 | 780 | 200 | 1433.1739 | 35.83% | 95% | 0% | -263.1579 | 2610.049 | -3550 | -400 | -1339.951 | 33.5% | 28.41% | 95% | 0% | 3188 | -230
[5 empty] | 2019-11-21 | 22 | 7787 | 2970 | -222 | 1 | 0 | 3192 | 2879.4724 | 2879.4724 | 2879.4724 | 453.1739 | 780 | 200 | 1433.1739 | 35.83% | 95% | 0% | -254.0046 | 2625.4678 | -3550 | -400 | -1324.5322 | 33.11% | 28.41% | 95% | 0% | 3192 | -222
[5 empty] | 2019-11-21 | 23 | 7787.5 | 2996 | -225 | 1 | 0 | 3221 | 2924.8969 | 2924.8969 | 2924.8969 | 453.1739 | 780 | 200 | 1433.1739 | 35.83% | 95% | 0% | -257.4371 | 2667.4599 | -3550 | -400 | -1282.5401 | 32.06% | 28.38% | 95% | 0% | 3221 | -225
[5 empty] | 2019-11-21 | 24 | 7788 | 3007 | -228 | 1 | 0 | 3235 | 2946.8261 | 2946.8261 | 2946.8261 | 453.1739 | 780 | 200 | 1433.1739 | 35.83% | 95% | 0% | -260.8696 | 2685.9565 | -3550 | -400 | -1264.0435 | 31.6% | 28.38% | 95% | 0% | 3235 | -228
[5 empty] | 2019-11-21 | 25 | 7788.5 | 3042 | -216 | 1 | 0 | 3258 | 2982.8524 | 2982.8524 | 2982.8524 | 453.1739 | 780 | 200 | 1433.1739 | 35.83% | 95% | 0% | -247.1396 | 2735.7128 | -3550 | -400 | -1214.2872 | 30.36% | 28.37% | 95% | 0% | 3258 | -216
[5 empty] | 2019-11-21 | 26 | 7789 | 3033 | -203 | 1 | 0 | 3236 | 2948.3924 | 2948.3924 | 2948.3924 | 453.1739 | 780 | 200 | 1433.1739 | 35.83% | 95% | 0% | -232.2654 | 2716.127 | -3550 | -400 | -1233.873 | 30.85% | 28.36% | 95% | 0% | 3236 | -203
[5 empty] | 2019-11-21 | 27 | 7789.5 | 3045 | -195 | 1 | 0 | 3240 | 2954.6579 | 2954.6579 | 2954.6579 | 451.6076 | 780 | 200 | 1431.6076 | 35.79% | 95% | 0% | -223.1121 | 2731.5457 | -3550 | -400 | -1218.4543 | 30.46% | 28.36% | 95% | 0% | 3240 | -195
[5 empty] | 2019-11-21 | 28 | 7790 | 3047 | -181 | 1 | 0 | 3228 | 2935.8615 | 2935.8615 | 2935.8615 | 451.6076 | 780 | 200 | 1431.6076 | 35.79% | 95% | 0% | -207.0938 | 2728.7677 | -3550 | -400 | -1221.2323 | 30.53% | 28.35% | 95% | 0% | 3228 | -181
[5 empty] | 2019-11-21 | 29 | 7790.5 | 3072 | -167 | 1 | 0 | 3239 | 2953.0915 | 2953.0915 | 2953.0915 | 451.6076 | 780 | 200 | 1431.6076 | 35.79% | 95% | 0% | -191.0755 | 2762.016 | -3550 | -400 | -1187.984 | 29.7% | 28.35% | 95% | 0% | 3239 | -167
[5 empty] | 2019-11-21 | 30 | 7791 | 3077 | -156 | 1 | 0 | 3233 | 2943.6933 | 2943.6933 | 2943.6933 | 451.6076 | 780 | 200 | 1431.6076 | 35.79% | 95% | 0% | -178.4897 | 2765.2036 | -3550 | -400 | -1184.7964 | 29.62% | 28.35% | 95% | 0% | 3233 | -156
[5 empty] | 2019-11-21 | 31 | 7791.5 | 3099 | -145 | 1 | 0 | 3244 | 2960.9233 | 2960.9233 | 2960.9233 | 451.6076 | 780 | 200 | 1431.6076 | 35.79% | 95% | 0% | -165.9039 | 2795.0194 | -3550 | -400 | -1154.9806 | 28.87% | 28.35% | 95% | 0% | 3244 | -145
[5 empty] | 2019-11-21 | 32 | 7792 | 3162 | -139 | 1 | 0 | 3301 | 3050.2061 | 3050.2061 | 3050.2061 | 451.6076 | 780 | 200 | 1431.6076 | 35.79% | 95% | 0% | -159.0389 | 2891.1672 | -3550 | -400 | -1058.8328 | 26.47% | 28.35% | 95% | 0% | 3301 | -139
[5 empty] | 2019-11-21 | 33 | 7792.5 | 3244 | -137 | 1 | 0 | 3381 | 3175.5153 | 3175.5153 | 3175.5153 | 451.6076 | 780 | 200 | 1431.6076 | 35.79% | 95% | 0% | -156.7506 | 3018.7647 | -3550 | -400 | -931.2353 | 23.28% | 28.34% | 95% | 0% | 3381 | -137
[5 empty] | 2019-11-21 | 34 | 7793 | 3296 | -135 | 1 | 0 | 3431 | 3253.8335 | 3253.8335 | 3253.8335 | 450.0412 | 780 | 200 | 1430.0412 | 35.75% | 95% | 0% | -154.4622 | 3099.3712 | -3550 | -400 | -850.6288 | 21.27% | 28.31% | 95% | 0% | 3431 | -135
[5 empty] | 2019-11-21 | 35 | 7793.5 | 3304 | -135 | 0 | 0 | 3439 | 3266.3644 | 3266.3644 | 3266.3644 | 450.0412 | 780 | 200 | 1430.0412 | 35.75% | 95% | 0% | -154.4622 | 3111.9021 | -2750 | -200 | 161.9021 | -4.048% | 28.31% | 95% | 0% | 3439 | -135
[5 empty] | 2019-11-21 | 36 | 7794 | 3272 | -134 | 0 | 0 | 3406 | 3214.6744 | 3214.6744 | 3214.6744 | 450.0412 | 780 | 200 | 1430.0412 | 35.75% | 95% | 0% | -153.3181 | 3061.3563 | -2750 | -200 | 111.3563 | -2.784% | 28.3% | 95% | 0% | 3406 | -134
[5 empty] | 2019-11-21 | 37 | 7794.5 | 3241 | -133 | 0 | 0 | 3374 | 3164.5507 | 3164.5507 | 3164.5507 | 450.0412 | 780 | 200 | 1430.0412 | 35.75% | 95% | 0% | -152.1739 | 3012.3768 | -2750 | -200 | 62.3768 | -1.559% | 28.29% | 95% | 0% | 3374 | -133
[5 empty] | 2019-11-21 | 38 | 7795 | 3224 | -133 | 0 | 0 | 3357 | 3137.9225 | 3137.9225 | 3137.9225 | 450.0412 | 780 | 200 | 1430.0412 | 35.75% | 95% | 0% | -152.1739 | 2985.7486 | -2750 | -200 | 35.7486 | -0.8937% | 28.28% | 95% | 0% | 3357 | -133
[5 empty] | 2019-11-21 | 39 | 7795.5 | 3208 | -132 | 0 | 0 | 3340 | 3111.2943 | 3111.2943 | 3111.2943 | 450.0412 | 780 | 200 | 1430.0412 | 35.75% | 95% | 0% | -151.0297 | 2960.2646 | -2750 | -200 | 10.2646 | -0.2566% | 28.28% | 95% | 0% | 3340 | -132
[5 empty] | 2019-11-21 | 40 | 7796 | 3126 | -130 | 0 | 0 | 3256 | 2979.7197 | 2979.7197 | 2979.7197 | 450.0412 | 780 | 200 | 1430.0412 | 35.75% | 95% | 0% | -148.7414 | 2830.9783 | -2750 | -200 | -119.0217 | 2.976% | 28.28% | 95% | 0% | 3256 | -130
[5 empty] | 2019-11-21 | 41 | 7796.5 | 3044 | -129 | 0 | 0 | 3173 | 2849.7115 | 2849.7115 | 2849.7115 | 450.0412 | 780 | 200 | 1430.0412 | 35.75% | 95% | 0% | -147.5973 | 2702.1142 | -2750 | -200 | -247.8858 | 6.197% | 28.26% | 95% | 0% | 3173 | -129
[5 empty] | 2019-11-21 | 42 | 7797 | 2927 | -127 | 0 | 0 | 3054 | 2663.3141 | 2663.3141 | 2663.3141 | 450.0412 | 780 | 200 | 1430.0412 | 35.75% | 95% | 0% | -145.3089 | 2518.0052 | -2750 | -200 | -431.9948 | 10.8% | 28.26% | 95% | 0% | 3054 | -127
[5 empty] | 2019-11-21 | 43 | 7797.5 | 2776 | -125 | 0 | 0 | 2901 | 2423.6603 | 2423.6603 | 2423.6603 | 450.0412 | 780 | 200 | 1430.0412 | 35.75% | 95% | 0% | -143.0206 | 2280.6398 | -2750 | -200 | -669.3602 | 16.73% | 28.26% | 95% | 0% | 2901 | -125
[5 empty] | 2019-11-21 | 44 | 7798 | 2620 | -124 | 0 | 0 | 2744 | 2177.7411 | 2177.7411 | 2177.7411 | 448.4749 | 780 | 200 | 1428.4749 | 35.71% | 95% | 0% | -141.8764 | 2035.8647 | -2750 | -200 | -914.1353 | 22.85% | 28.25% | 95% | 0% | 2744 | -124
[5 empty] | 2019-11-21 | 45 | 7798.5 | 2452 | -122 | 0 | 0 | 2574 | 1911.4592 | 1911.4592 | 1911.4592 | 448.4749 | 780 | 200 | 1428.4749 | 35.71% | 95% | 0% | -139.5881 | 1771.8711 | -2750 | -200 | -1178.1289 | 29.45% | 28.25% | 95% | 0% | 2574 | -122
[5 empty] | 2019-11-21 | 46 | 7799 | 2311 | -120 | 0 | 0 | 2431 | 1687.4691 | 1687.4691 | 1687.4691 | 448.4749 | 780 | 200 | 1428.4749 | 35.71% | 95% | 0% | -137.2998 | 1550.1693 | -2750 | -200 | -1399.8307 | 35% | 28.23% | 95% | 0% | 2431 | -120
[5 empty] | 2019-11-21 | 47 | 7799.5 | 2154 | -118 | 0 | 0 | 2272 | 1438.4171 | 1438.4171 | 1438.4171 | 448.4749 | 780 | 200 | 1428.4749 | 35.71% | 95% | 0% | -135.0114 | 1303.4057 | -2750 | -200 | -1646.5943 | 41.16% | 28.22% | 95% | 0% | 2272 | -118
[5 empty] | 2019-11-21 | 48 | 7800 | 2060 | -117 | 0 | 0 | 2177 | 1289.6125 | 1289.6125 | 1289.6125 | 448.4749 | 780 | 200 | 1428.4749 | 35.71% | 95% | 0% | -133.8673 | 1155.7453 | -2750 | -200 | -1794.2547 | 44.86% | 28.22% | 95% | 0% | 2177 | -117
[5 empty] | 2019-11-22 | 1 | 7800.5 | 2027 | -118 | 0 | 0 | 2145 | 1239.4889 | 1239.4889 | 1239.4889 | 448.4749 | 780 | 200 | 1428.4749 | 35.71% | 95% | 0% | -135.0114 | 1104.4774 | -2750 | -200 | -1845.5226 | 46.14% | 28.21% | 95% | 0% | 2145 | -118
[5 empty] | 2019-11-22 | 2 | 7801 | 2045 | -119 | 0 | 0 | 2164 | 1269.2498 | 1269.2498 | 1269.2498 | 448.4749 | 780 | 200 | 1428.4749 | 35.71% | 95% | 0% | -136.1556 | 1133.0942 | -2750 | -200 | -1816.9058 | 45.42% | 28.2% | 95% | 0% | 2164 | -119
[5 empty] | 2019-11-22 | 3 | 7801.5 | 2021 | -118 | 0 | 0 | 2139 | 1230.0907 | 1230.0907 | 1230.0907 | 448.4749 | 780 | 200 | 1428.4749 | 35.71% | 95% | 0% | -135.0114 | 1095.0792 | -2750 | -200 | -1854.9208 | 46.37% | 28.16% | 95% | 0% | 2139 | -118
[5 empty] | 2019-11-22 | 4 | 7802 | 1967 | -118 | 0 | 0 | 2085 | 1145.507 | 1145.507 | 1145.507 | 448.4749 | 780 | 200 | 1428.4749 | 35.71% | 95% | 0% | -135.0114 | 1010.4956 | -2750 | -200 | -1939.5044 | 48.49% | 28.14% | 95% | 0% | 2085 | -118
[5 empty] | 2019-11-22 | 5 | 7802.5 | 1922 | -119 | 0 | 0 | 2041 | 1076.587 | 1076.587 | 1076.587 | 446.9085 | 780 | 200 | 1426.9085 | 35.67% | 95% | 0% | -136.1556 | 940.4314 | -2750 | -200 | -2009.5686 | 50.24% | 28.14% | 95% | 0% | 2041 | -119
[5 empty] | 2019-11-22 | 6 | 7803 | 1900 | -120 | 0 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 446.9085 | 780 | 200 | 1426.9085 | 35.67% | 95% | 0% | -137.2998 | 906.3936 | -2750 | -200 | -2043.6064 | 51.09% | 28.13% | 95% | 0% | 2020 | -120
[5 empty] | 2019-11-22 | 7 | 7803.5 | 1872 | -120 | 0 | 0 | 1992 | 999.8351 | 999.8351 | 999.8351 | 446.9085 | 780 | 200 | 1426.9085 | 35.67% | 95% | 0% | -137.2998 | 862.5353 | -2750 | -200 | -2087.4647 | 52.19% | 28.12% | 95% | 0% | 1992 | -120
[5 empty] | 2019-11-22 | 8 | 7804 | 1840 | -121 | 0 | 0 | 1961 | 951.2778 | 951.2778 | 951.2778 | 446.9085 | 780 | 200 | 1426.9085 | 35.67% | 95% | 0% | -138.4439 | 812.8339 | -2750 | -200 | -2137.1661 | 53.43% | 28.11% | 95% | 0% | 1961 | -121
[5 empty] | 2019-11-22 | 9 | 7804.5 | 1830 | -121 | 0 | 0 | 1951 | 935.6142 | 935.6142 | 935.6142 | 446.9085 | 780 | 200 | 1426.9085 | 35.67% | 95% | 0% | -138.4439 | 797.1702 | -2750 | -200 | -2152.8298 | 53.82% | 28.09% | 95% | 0% | 1951 | -121
[5 empty] | 2019-11-22 | 10 | 7805 | 1834 | -121 | 0 | 0 | 1955 | 941.8796 | 941.8796 | 941.8796 | 446.9085 | 780 | 200 | 1426.9085 | 35.67% | 95% | 0% | -138.4439 | 803.4357 | -2750 | -200 | -2146.5643 | 53.66% | 28.09% | 95% | 0% | 1955 | -121
[5 empty] | 2019-11-22 | 11 | 7805.5 | 1900 | -120 | 1 | 0 | 2020 | 1043.6933 | 1043.6933 | 1043.6933 | 446.9085 | 780 | 200 | 1426.9085 | 35.67% | 95% | 0% | -137.2998 | 906.3936 | -3550 | -400 | -3043.6064 | 76.09% | 28.06% | 95% | 0% | 2020 | -120
[5 empty] | 2019-11-22 | 12 | 7806 | 1995 | -118 | 1 | 0 | 2113 | 1189.3652 | 1189.3652 | 1189.3652 | 445.3421 | 780 | 200 | 1425.3421 | 35.63% | 95% | 0% | -135.0114 | 1054.3538 | -3550 | -400 | -2895.6462 | 72.39% | 28.06% | 95% | 0% | 2113 | -118
[5 empty] | 2019-11-22 | 13 | 7806.5 | 2248 | -119 | 1 | 0 | 2367 | 1587.2218 | 1587.2218 | 1587.2218 | 445.3421 | 780 | 200 | 1425.3421 | 35.63% | 95% | 0% | -136.1556 | 1451.0662 | -3550 | -400 | -2498.9338 | 62.47% | 28.05% | 95% | 0% | 2367 | -119
[5 empty] | 2019-11-22 | 14 | 7807 | 2487 | -120 | 1 | 0 | 2607 | 1963.1492 | 1963.1492 | 1963.1492 | 445.3421 | 780 | 200 | 1425.3421 | 35.63% | 95% | 0% | -137.2998 | 1825.8494 | -3550 | -400 | -2124.1506 | 53.1% | 28.05% | 95% | 0% | 2607 | -120
[5 empty] | 2019-11-22 | 15 | 7807.5 | 2749 | -120 | 1 | 0 | 2869 | 2373.5367 | 2373.5367 | 2373.5367 | 445.3421 | 780 | 200 | 1425.3421 | 35.63% | 95% | 0% | -137.2998 | 2236.2369 | -3550 | -400 | -1713.7631 | 42.84% | 28.03% | 95% | 0% | 2869 | -120
[5 empty] | 2019-11-22 | 16 | 7808 | 2881 | -122 | 1 | 0 | 3003 | 2583.4295 | 2583.4295 | 2583.4295 | 445.3421 | 780 | 200 | 1425.3421 | 35.63% | 95% | 0% | -139.5881 | 2443.8414 | -3550 | -400 | -1506.1586 | 37.65% | 28.03% | 95% | 0% | 3003 | -122
[5 empty] | 2019-11-22 | 17 | 7808.5 | 2945 | -133 | 1 | 0 | 3078 | 2700.9068 | 2700.9068 | 2700.9068 | 443.7758 | 780 | 200 | 1423.7758 | 35.59% | 95% | 0% | -152.1739 | 2548.7329 | -3550 | -400 | -1401.2671 | 35.03% | 28.02% | 95% | 0% | 3078 | -133
[5 empty] | 2019-11-22 | 18 | 7809 | 2917 | -164 | 1 | 0 | 3081 | 2705.6059 | 2705.6059 | 2705.6059 | 443.7758 | 780 | 200 | 1423.7758 | 35.59% | 95% | 0% | -187.643 | 2517.9629 | -3550 | -400 | -1432.0371 | 35.8% | 28.02% | 95% | 0% | 3081 | -164
[5 empty] | 2019-11-22 | 19 | 7809.5 | 2931 | -199 | 1 | 0 | 3130 | 2782.3578 | 2782.3578 | 2782.3578 | 443.7758 | 780 | 200 | 1423.7758 | 35.59% | 95% | 0% | -227.6888 | 2554.669 | -3550 | -400 | -1395.331 | 34.88% | 28% | 95% | 0% | 3130 | -199
[5 empty] | 2019-11-22 | 20 | 7810 | 2903 | -209 | 1 | 0 | 3112 | 2754.1632 | 2754.1632 | 2754.1632 | 443.7758 | 780 | 200 | 1423.7758 | 35.59% | 95% | 0% | -239.1304 | 2515.0328 | -3550 | -400 | -1434.9672 | 35.87% | 28% | 95% | 0% | 3112 | -209
[5 empty] | 2019-11-22 | 21 | 7810.5 | 2882 | -220 | 1 | 0 | 3102 | 2738.4996 | 2738.4996 | 2738.4996 | 443.7758 | 780 | 200 | 1423.7758 | 35.59% | 95% | 0% | -251.7162 | 2486.7833 | -3550 | -400 | -1463.2167 | 36.58% | 27.97% | 95% | 0% | 3102 | -220
[5 empty] | 2019-11-22 | 22 | 7811 | 2863 | -217 | 1 | 0 | 3080 | 2704.0396 | 2704.0396 | 2704.0396 | 443.7758 | 780 | 200 | 1423.7758 | 35.59% | 95% | 0% | -248.2838 | 2455.7558 | -3550 | -400 | -1494.2442 | 37.36% | 27.97% | 95% | 0% | 3080 | -217
[5 empty] | 2019-11-22 | 23 | 7811.5 | 2912 | -206 | 1 | 0 | 3118 | 2763.5614 | 2763.5614 | 2763.5614 | 443.7758 | 780 | 200 | 1423.7758 | 35.59% | 95% | 0% | -235.6979 | 2527.8635 | -3550 | -400 | -1422.1365 | 35.55% | 27.96% | 95% | 0% | 3118 | -206
[5 empty] | 2019-11-22 | 24 | 7812 | 2914 | -199 | 1 | 0 | 3113 | 2755.7296 | 2755.7296 | 2755.7296 | 443.7758 | 780 | 200 | 1423.7758 | 35.59% | 95% | 0% | -227.6888 | 2528.0408 | -3550 | -400 | -1421.9592 | 35.55% | 27.96% | 95% | 0% | 3113 | -199
[5 empty] | 2019-11-22 | 25 | 7812.5 | 2897 | -203 | 1 | 0 | 3100 | 2735.3669 | 2735.3669 | 2735.3669 | 443.7758 | 780 | 200 | 1423.7758 | 35.59% | 95% | 0% | -232.2654 | 2503.1014 | -3550 | -400 | -1446.8986 | 36.17% | 27.95% | 95% | 0% | 3100 | -203
[5 empty] | 2019-11-22 | 26 | 7813 | 2884 | -188 | 1 | 0 | 3072 | 2691.5087 | 2691.5087 | 2691.5087 | 443.7758 | 780 | 200 | 1423.7758 | 35.59% | 95% | 0% | -215.103 | 2476.4057 | -3550 | -400 | -1473.5943 | 36.84% | 27.89% | 95% | 0% | 3072 | -188
[5 empty] | 2019-11-22 | 27 | 7813.5 | 2910 | -173 | 1 | 0 | 3083 | 2708.7387 | 2708.7387 | 2708.7387 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -197.9405 | 2510.7982 | -3550 | -400 | -1439.2018 | 35.98% | 27.89% | 95% | 0% | 3083 | -173
[5 empty] | 2019-11-22 | 28 | 7814 | 2948 | -165 | 1 | 0 | 3113 | 2755.7296 | 2755.7296 | 2755.7296 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -188.7872 | 2566.9424 | -3550 | -400 | -1383.0576 | 34.58% | 27.88% | 95% | 0% | 3113 | -165
[5 empty] | 2019-11-22 | 29 | 7814.5 | 2959 | -148 | 1 | 0 | 3107 | 2746.3314 | 2746.3314 | 2746.3314 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -169.3364 | 2576.995 | -3550 | -400 | -1373.005 | 34.33% | 27.84% | 95% | 0% | 3107 | -148
[5 empty] | 2019-11-22 | 30 | 7815 | 2961 | -130 | 1 | 0 | 3091 | 2721.2696 | 2721.2696 | 2721.2696 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -148.7414 | 2572.5282 | -3550 | -400 | -1377.4718 | 34.44% | 27.84% | 95% | 0% | 3091 | -130
[5 empty] | 2019-11-22 | 31 | 7815.5 | 2989 | -124 | 1 | 0 | 3113 | 2755.7296 | 2755.7296 | 2755.7296 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -141.8764 | 2613.8532 | -3550 | -400 | -1336.1468 | 33.4% | 27.84% | 95% | 0% | 3113 | -124
[5 empty] | 2019-11-22 | 32 | 7816 | 3038 | -122 | 1 | 0 | 3160 | 2829.3487 | 2829.3487 | 2829.3487 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -139.5881 | 2689.7606 | -3550 | -400 | -1260.2394 | 31.51% | 27.83% | 95% | 0% | 3160 | -122
[5 empty] | 2019-11-22 | 33 | 7816.5 | 3122 | -124 | 1 | 0 | 3246 | 2964.0561 | 2964.0561 | 2964.0561 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -141.8764 | 2822.1796 | -3550 | -400 | -1127.8204 | 28.2% | 27.83% | 95% | 0% | 3246 | -124
[5 empty] | 2019-11-22 | 34 | 7817 | 3185 | -126 | 1 | 0 | 3311 | 3065.8697 | 3065.8697 | 3065.8697 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -144.1648 | 2921.705 | -3550 | -400 | -1028.295 | 25.71% | 27.82% | 95% | 0% | 3311 | -126
[5 empty] | 2019-11-22 | 35 | 7817.5 | 3192 | -129 | 0 | 0 | 3321 | 3081.5334 | 3081.5334 | 3081.5334 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -147.5973 | 2933.9361 | -2750 | -200 | -16.0639 | 0.4016% | 27.81% | 95% | 0% | 3321 | -129
[5 empty] | 2019-11-22 | 36 | 7818 | 3180 | -131 | 0 | 0 | 3311 | 3065.8697 | 3065.8697 | 3065.8697 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -149.8856 | 2915.9842 | -2750 | -200 | -34.0158 | 0.8504% | 27.8% | 95% | 0% | 3311 | -131
[5 empty] | 2019-11-22 | 37 | 7818.5 | 3130 | -133 | 0 | 0 | 3263 | 2990.6843 | 2990.6843 | 2990.6843 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -152.1739 | 2838.5103 | -2750 | -200 | -111.4897 | 2.787% | 27.79% | 95% | 0% | 3263 | -133
[5 empty] | 2019-11-22 | 38 | 7819 | 3090 | -135 | 0 | 0 | 3225 | 2931.1624 | 2931.1624 | 2931.1624 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -154.4622 | 2776.7002 | -2750 | -200 | -173.2998 | 4.332% | 27.78% | 95% | 0% | 3225 | -135
[5 empty] | 2019-11-22 | 39 | 7819.5 | 3010 | -137 | 0 | 0 | 3147 | 2808.986 | 2808.986 | 2808.986 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -156.7506 | 2652.2354 | -2750 | -200 | -297.7646 | 7.444% | 27.77% | 95% | 0% | 3147 | -137
[5 empty] | 2019-11-22 | 40 | 7820 | 2906 | -138 | 0 | 0 | 3044 | 2647.6505 | 2647.6505 | 2647.6505 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -157.8947 | 2489.7557 | -2750 | -200 | -460.2443 | 11.51% | 27.74% | 95% | 0% | 3044 | -138
[5 empty] | 2019-11-22 | 41 | 7820.5 | 2794 | -139 | 0 | 0 | 2933 | 2473.784 | 2473.784 | 2473.784 | 442.2094 | 780 | 200 | 1422.2094 | 35.56% | 95% | 0% | -159.0389 | 2314.7451 | -2750 | -200 | -635.2549 | 15.88% | 27.73% | 95% | 0% | 2933 | -139
[5 empty] | 2019-11-22 | 42 | 7821 | 2679 | -140 | 0 | 0 | 2819 | 2295.2185 | 2295.2185 | 2295.2185 | 440.643 | 780 | 200 | 1420.643 | 35.52% | 95% | 0% | -160.1831 | 2135.0354 | -2750 | -200 | -814.9646 | 20.37% | 27.72% | 95% | 0% | 2819 | -140
[5 empty] | 2019-11-22 | 43 | 7821.5 | 2550 | -140 | 0 | 0 | 2690 | 2093.1575 | 2093.1575 | 2093.1575 | 440.643 | 780 | 200 | 1420.643 | 35.52% | 95% | 0% | -160.1831 | 1932.9744 | -2750 | -200 | -1017.0256 | 25.43% | 27.72% | 95% | 0% | 2690 | -140
[5 empty] | 2019-11-22 | 44 | 7822 | 2412 | -141 | 0 | 0 | 2553 | 1878.5655 | 1878.5655 | 1878.5655 | 440.643 | 780 | 200 | 1420.643 | 35.52% | 95% | 0% | -161.3272 | 1717.2383 | -2750 | -200 | -1232.7617 | 30.82% | 27.72% | 95% | 0% | 2553 | -141
[5 empty] | 2019-11-22 | 45 | 7822.5 | 2281 | -140 | 0 | 0 | 2421 | 1671.8054 | 1671.8054 | 1671.8054 | 440.643 | 780 | 200 | 1420.643 | 35.52% | 95% | 0% | -160.1831 | 1511.6224 | -2750 | -200 | -1438.3776 | 35.96% | 27.72% | 95% | 0% | 2421 | -140
[5 empty] | 2019-11-22 | 46 | 7823 | 2159 | -139 | 0 | 0 | 2298 | 1479.1426 | 1479.1426 | 1479.1426 | 440.643 | 780 | 200 | 1420.643 | 35.52% | 95% | 0% | -159.0389 | 1320.1037 | -2750 | -200 | -1629.8963 | 40.75% | 27.7% | 95% | 0% | 2298 | -139
[5 empty] | 2019-11-22 | 47 | 7823.5 | 2025 | -139 | 0 | 0 | 2164 | 1269.2498 | 1269.2498 | 1269.2498 | 440.643 | 780 | 200 | 1420.643 | 35.52% | 95% | 0% | -159.0389 | 1110.2109 | -2750 | -200 | -1839.7891 | 45.99% | 27.69% | 95% | 0% | 2164 | -139