## Operational, Safety and Reporti
Operational, Safety and Reporting Issues
Meeting Raised | Topic | Description | Outcome | Status
IWG 72 | Heavy duty metal clad cut-outs | Members noted that meter tails would not be able to be changed on a heavy-duty metal clad cut-out. The only time this would be allowed is with the smaller 100amp cut-outs where the meter tails would fit in as standard. It was noted that the majority of the smart meter work would be on single-phase cut-outs, and may only be a small number of the heavy-duty metal clad cut-outs. | It was agreed for MOPs to contact the relevant DNO for support if they come across these heavy-duty metal clad cut-outs where support is needed to change the meter tails. | Closed
IWG 72 | B07 examples | Group members were asked if they could discuss, and clarify, service termination requirements regarding meter supply neutrals which are connected to the service side of the cut-out. | This was taken to STIG and an email was sent out to DNOs. A unanimous decision was not able to be reached. It was agreed that this is an example that should go into each DNOs local information for meter operators, so that meter operators have a solution. | Closed
IWG 72 | Unknown fuse ratings at de-energised sites | One member stated that when a new Supplier attends a de-energised site, the fuse-rating may not be known and queried whether the lowest (60amp) should be installed or what is stated on the fuse carrier (i.e., 80amp) should be installed. | The DNO majority view is that if you get to site and there is no fuse, MEMs should default to a 60 amp to restore supply. IDNOs are unanimous that the only cut out fuses they have on their networks are 80A or 100A. The default on DNO networks should be 60-amps if the supplier or MEM cannot determine what the previous fuse rating was. | Closed
IWG 72 | Load limit the amp fuse | One member provided a scenario where the DNO have been given permission to load limit the amp fuse to 80amp, however when attending a site it has a 60amp fuse. It was queried whether the DNO would be allowed to upgrade the 60amp fuse to an 80amp fuse – members stated that this would not be allowed and would need to be reverted back to the DNO. | One member stated that on the de-energisation flow (D0134/J1011), there is a maximum power requirement data item. If the Supplier sends a change in the de-energisation status, the maximum requirement will be included within the data flow and may help with the above scenario. | Closed
IWG 74 | The Electrical Contractors feedback on the SIP role | Following the release of a YouTube video ‘Should Electricians Cut Fuse & Meter Seals?’, which highlighted that a number of electricians are struggling to find SIPs to support them, members discussed the possibility of completing a piece of work to review the progress to date on the introduction of SIPs (i.e. the benefits, gaps still remaining etc.). | The Chair of the IWG took an action to discuss this with the Retail Energy Code (REC) and subsequently the DCUSA Panel. The DCUSA Panel provided approval for a guidance video to be created to explain what a SIP is and what the requirements of becoming a SIP are (e.g., to become a MEM). Work will continue into 2025 to develop and release this video. | Ongoing
IWG 74 | The Energy UK Safety and Quality Issue Contacts | The group discussed whether the Energy UK Safety and Quality Issue Contacts could become a part of DCUSA. | The Chair referred this to REC who are undertaking a review of their contacts. Updates will be provided when possible | Ongoing
IWG 75 | Meter sticker | A member presented a picture of a meter with 25mm tails and a sticker on the meter that stated 40 amps maximum. The member asked what the 40 amps sticker means (whether this is the rating of the meter or the accuracy of the meter) and that the fuse is not really there to protect the meter. | The group agreed this should be sent to the asset team for advice | Closed
IWG 75 | 100amp fuses being replaced with 80amp on domestic properties | A member noted they had received queries around 100-amp fuses on domestic properties and whether this could be replaced with an 80 amp fuse. | Members discussed their different internal policies on the matter and one member agreed to take this away within their company to assess whether a Change Proposal should be raised. | Closed
IWG 76 | Ground subsidence issues and damaged equipment | GTC have experienced damaged equipment due to ongoing ground settlement, with meters being pulled off the board. There are standard solutions for these types of situations for gas and water, however not for electricity. To ensure GTC are compliant with safety obligations they are proposing to install a non-standard service termination arrangement on all affected plots. | Members discussed and raised questions. Members thanked GTC for the awareness. GTC agreed to return to the IWG with an update once the work is underway. | Ongoing
IWG 77 | Unhinged metal clad cutouts | One member highlighted concerns around unhinged metal clad cut outs and asked for feedback. The member acknowledged there is always a risk whilst working on a cut out, however there are further risks due to the heavy metal lid which can easily catch or be dropped into the bottom of the cut out whilst being removed. The member noted that some designs are also missing fuse phase barriers and some are 60 or 70 years old. | Members discussed an Electricity North West procedure document online which states that this type of cut out may only be worked on or changed if dead. Members noted that the service termination guide suggests a B08 however this references lifting the lid which is where the risk lies. Members raised concerns that the guidance is not clear and agreed that clarity should be sought regarding this issue. | Closed
IWG 77 | Different types/mix of main fuse carriers | A member presented a picture of a meter with different types of main fuse carriers and asked for feedback. | Members agreed that it depends how the fuse carriers fit and that if they don't they should be reporting as an A code. If it appears to fit and there are no signs of degradation/overheating then it is fine. | Closed
IWG 79 | Reporting safety incidents following a Safe Isolation Provider (SIP) visit | A member highlighted the obligation in 30.18 of DCUSA for DNOs to report to the Supplier if they discover safety incidents attributed to Meter Operator work and asked if there is an equivalent for SIP work. | Members discussed and the Chair took an action to investigate whether this is covered under the REC. | Ongoing
IWG 79 | A Code queries | A member presented a set of images to the group and asked for opinions on whether the situations should be reported as A codes. These can be found as Attachment 3 of the IWG 79 minutes. | Regarding signs of overheating/discolouration members felt fit should also be considered when assessing risk. The group agreed education on risk assessing the whole cut out is important. DNO members agreed if there is a concern it should be reported and they would be very unlikely to be reported as a misreport. Regarding freshly leaking bitumen, members agreed these situations should be reported as an A01. | Closed
IWG 77 & 79 | Supplier meter disposal process | IWG 77 - A member highlighted that at the time of the meeting, UK Power Networks had suspended the acceptance of meters for disposal due to asbestos being discovered within the bakerlite of a 1971 meter. IWG 79 - The member shared slides regarding the updated meter disposal process. Attachment 4 of the IWG 79 minutes. | IWG 77 - The member raised this for awareness and noted that disposal would be reinstated once further investigation had been completed and procedures had been reviewed. IWG 79 - The member advised that UKPN nominated Sackers Limited to manage disposal of these meters. These do not need to be segregated. To ensure asset tracking, Meter Operators will provide the serial numbers of the meters and meters sent to the waste contractor must have a hazardous waste consignment note and the serial numbers. UKPN will retain these serial numbers and meters returned to Sackers Limited must be transported and stored in line with the Hazardous Waste Regulations. | Closed
IWG 79 | B07 query | A member presented three scenarios and asked – ‘Can we disconnect the cable from the connector block and the incoming neutral in the meter and then replace it with another cable from the spare port from the neutral side of the cut out into the incoming side of the meter. This will effectively treat it the same as scenario 3 (treat as PME). In doing this you do not have to disconnect or disturb the earth.’ | Members noted a new C21 code is due to be introduced but B07 is appropriate for now. Three DNOs agreed if there is a spare port and it is possible to get a cable from the cut out to the metre and remove the one from the block to the metre, that is fine. The member agreed to pick this up with the remaining DNOs in their bilaterals. | Ongoing
IWG 79 | Unhinged metal clad cut out embargo | A member highlighted Electricity North West (ENW) guidance stating unhinged metal clad cut outs are not to be worked on and asked members if they are aware of an embargo. | Members were not aware of an embargo. Two DNO members suggested a risk assessment should be made and if it appears unsafe once the lid is off, it can be escalated to an A code. The member agreed to contact ENW for further information. | Ongoing
IWG 79 | Policy for cut out fuse replacement | A member highlighted a request from their Dispatch Manager to ask Meter Operators what their policy is for replacing cut out fuses that have blown, particularly ones which may be as a result of a meter fault. | Members noted there is an obligation to report it to the DNO as the fault may still be there. One member noted if there is a blown fuse they do not put another fuse in in case there is an issue from the network side. One member noted it is a case by case situation but it would need to be investigated before they put a fuse in. | Closed
IWG 80 | 63A fuses | A member asked if a 63A fuse a suitable replacement for 60A fuse. | Members agreed it is. | Closed
IWG 80 | B08 query | A member presented a picture to the group and asked if a metal unhinged neutral block on a non PME supply is classed as a B08. | The group agreed that it should not be reported as an unhinged cut out. | Closed
IWG 80 | Asbestos meter boards | Regarding asbestos meter boards, a member explained that currently if there is space, they will fit a new board adjacent to the asbestos board with the new metre on and then strand the existing metre. The meter will be left on the board until it can be removed. The member noted they have another current solution where they fit a board over the existing asbestos board. If they can get fixings on the wall around the board, they can overboard it. The member explained sometimes these solutions are not possible due to the length of the tails and a lack of space. In these cases the member proposed to leave the existing metre as part of the installation but label 'do not read'. The member asked for the IWG's thoughts. The member noted that on some DNOs websites’ there are links to get the back board replaced, with asbestos being one of the possible reasons listed. The member questioned whether they can tell customers to take this route with the DNO or whether it should be raised as a C16. | Members agreed that if the old meter is SMETS1 they would need to ensure it was taken off DCC to ensure there would not be two meters on one MPAN. One member suggested that the UK Metering Forum (UKMF) may wish to be informed of these meters as they will be a stranded asset for the MAP. Members questioned what would happen if a stranded meter became faulty and how this would be dealt with. The member that raised the query agreed that they are considering this. DNOs advised they do replace meter boards for customers but would charge. DNOs advised if the cut out was damaged they would deal with the asbestos at the same time, but if the equipment is healthy, they would not. DNOs agreed if the usual solutions were not possible and there was no other option, Suppliers should contact them to discuss. | Closed
IWG 80 | Hexagon key sizes for heavy duty cutouts | A member advised that a MEM had come across a 5mm screw when they usually carry 3mm, 6mm and 10mm keys. Therefore, the MEM was unable to complete their work and have had to source the right key. The member asked if any other DNOs are using this type of cut out with 5mm screws and whether it would be possible for DNOs to share details of new assets ahead of implementation to avoid these situations. | A member advised they have contacted the manufacturer who advised the 5mm screws are on the incoming side which is not matching up with what the MEM found. The member agreed to follow up with this. Members suggested that an asset glossary could be proposed at the next EOMF. | Closed
IWG 80 | Cable colours | A member highlighted a couple of recent cases where cut outs and cabling from the cut outs to the meters had been changed and the insulation colours of the live and neutral cables were the same. The member advised they had to swap them which is costing Suppliers time and money. The member advised that when swapping the cut out and tails, it must comply with the Consolidated Metering Code of Practice (CoMCoP). | The group noted this. | Closed
IWG 81 | Cat A03 Defective Fuse Contacts | A member noted they are seeing an increase in situations where MOPs are being asked by their companies to take pictures of fuse ratings, and rather than relying on the label are taking the fuses out. The member advised they are seeing an increase in A03s caused by MOPs taking the fuse carriers apart and when putting them back together snapping one of the screws, breaking the housing or losing the screw that holds the two halves together. The member advised they were flagging this for information and to ask that if MOPs are opening the carrier, they take care when putting it back together. The member added it could be an issue with training in a particular area as it was only in the SPN area. | One member advised that from their company’s point of view, they check what the fuse size is and put a sticker on the front of the cut out to help people in future, including electricians. The member added that they physically check the fuse, spinning it around if necessary, but do not take it out of the fuse carrier. The member noted it is a mandatory requirement from their business to open the carrier to check the connections are tight on the fuse. | Closed
IWG 82 | Incoming DNO supply cable only secured on a single terminal screw in the cut-out when there are 2 present by design | One member asked the following question - When a MEM finds an incoming DNO supply cable only secured on a single terminal screw in the cut-out when there are 2 present by design; what action should the MEM take and which code would this be reported under. | As all DNOs were not on the call, members agreed to agreed to take this matter away and provide feedback at the next meeting. | Ongoing

## 2025 Work Plan
2025 Work Plan
1 | Extra Validation Across the DTN
2 | Improving Customer Journey via Online Forms
3 | Cage Clamp Isolators Guidance
4 | Radio Teleswitch Service Switch-off
5 | SIP Issues Obligations for DNOs to report safety issues following SIP work Recognising reports as coming from a SIP as opposed to the Supplier or Meter Operator. Ability for SIPs to report different work types (e.g. High Earth Loop Impedance)