Single Dwelling Meter Moves Guidance Document

Scope

Overview

General Requirements

Site Requirements

Meter Location

Meter Board, Size and Space Requirements

Point of Isolation Requirements

Cabling Requirements

Equipment Demarcation Zones and Ownership

Appendix 1

Single Dwelling Meter Move Equipment Demarcation Zones and Ownership

Appendix 2

Example Layout Drawings

Scope

This document applies to LV connections provided by a licensed electricity distributor to a single dwelling.

This document provides guidance to the supplier, customer and electrician for a single dwelling whole current electricity meter move that will be required siting more than three metres from the main DNO cutout/service position to a remote location within the building.

It gives clear guidance on the requirements, ownership, demarcation zones and all the relevant equipment needed to be installed when completing such an activity.

The scope of this document does NOT apply to installations within multiple occupancy buildings. For installations with multiple occupancy buildings please use the ENA EREC G87 – Guidelines for the Provision of Low Voltage Connections to Multiple Occupancy Buildings document.

Additional site requirements concerning the accessibility, fireproofing, or other aspects of any meter positions, as required by Building Regulations or other Regulations, Codes, Guidelines etc, are beyond the scope of this document although may be referred to.

This document excludes the requirements for wiring within individual dwellings, which is covered under BS7671 – The IET Wiring Regulations.

Overview

In certain circumstances a customer may require their electricity meter moving from the main DNO service position/cutout to a remote location within a single dwelling building.

Any electricity meter move above three metres in length will require the service of a fully qualified electrician and will need to be installed to BS7671 – The IET Wiring Regulations.

Any electricity meter move less than three metres from the DNO/service position within the same room can be carried out by the electricity supplier.

General Requirements

Site Requirements

Before any work is conducted on the installation, the cutout and meter position will need to be inspected by the customers electrician/supplier for any signs of overheating and/or damage to the equipment. The equipment must be safe for continued use.

Any signs of overheating and/or damage to the Distribution Network Operator (DNO) cutout must be reported to the relevant DNO.

Any signs of overheating and/or damage to the supplier’s equipment must be reported to the relevant supplier.

A photo of the DNO/metering equipment shall be emailed to the relevant supplier before any work is carried out.

All DNO/supplier equipment SHALL always remain accessible in case of an emergency; no equipment is to be covered.

An electrician shall install the relevant equipment listed in this document to BS7671, provide certification to the customer of works completed and facilitate the electricity supplier moving the meter to another suitable location.

Where a Smart meter is to be moved to another location within a single dwelling building, consideration should be given to the location of the meter position that may impede any signals required to communicate with the Smart metering equipment.

Whilst metering work is being conducted on a supply, no other work, testing or alterations should be undertaken on that supply.

The supplier will leave the metering installation energised after the meter move, ready for the electrician to self-test and connect.

The supplier will install a meter and isolator to the remote red link cutout position.

Meter locations should:

- Comply with Building Regulations,

- Comply with ESQCR,

- Not be a confined space, as defined in the Confined Space Regulations 1997,

- Be installed no higher than 1800mm above floor level to avoid working at height concerns,

- Be accessible by customers, DNO staff, meter readers and meter operator staff.

- Have adequate physical access and egress, and clear of obstructions.

- Not be used as a storage area.

- Have adequate lighting in accordance with Health and Safety Executive guidance document HSG 38,

- Be weatherproof, dry, have a non-corrosive atmosphere and be naturally ventilated,

- Not have an ambient temperature which normally exceeds 30°C.

The following are examples of metering installation locations that are likely to be unacceptable:

- A bathroom, washroom or toilet.

Meter Board, Size and Space Requirements

All metering equipment requires mounting on a wooden backboard, which should be manufactured from fire-retardant, resin-impregnated chipboard in accordance with BS EN 312:2010.

Where the meter installation is an external meter box, the box should comply with the requirements of ENA TS 12-3 or BS 8567.

All meter boards, meter boxes, meter cabinets, meter cupboards SHALL be provided and fitted by the customer/electrician and will remain the responsibility of the customer. The supplier will take no responsibility for any such equipment. The supplier reserves the right to refuse to install a meter where the meter board requirements have not been met.

The meter board must be able to accommodate all metering equipment and achieve a 25mm clearance from the edge of the board to maintain the relevant fireproof rating.

Space requirements,

| Supply Type | Minimum Space Required |
| --- | --- |
| Single phase metering with cut-out | 350mm wide x 500mm high |
| Three phase metering with cut-out | 500mm wide x 700mm high |

Point of Isolation Requirements

Switched fused Isolator and 25mm tails

A suitable main switched fused sealable isolator shall be installed at the existing meter position by the customers electrician.

The switched fused isolator shall have the customers 25mm tails supplied by the customers electrician. The 25mm tails will be installed into the DNO cutout by the electricity supplier only and the DNO cutout fuse and main switched fused isolator sealed with metering seals by the supplier after the completion of metering work.

Red Link Cutout

To allow meter work to be undertaken safely, a local point of isolation at the new meter position must be provided by the customer/electrician. This must be a red link cutout with a separate associated earth test point. (See Appendix 1).

Cabling Requirements

The supplier SHALL only accept insulated and sheathed 7 or 19 stranded circular soft drawn copper cables conforming to BS 6181Y/BS 6004. Any cable provided should be sized appropriately for the distribution fuse rating, with a minimum of 16mm2 and not exceeding 25mm2.

The supplier SHALL NOT connect any other cable directly into the DNO cutout. Where these requirements have not been met, the supplier reserves the right to refuse to install a meter.

The cable from the customers main switched fused isolator to the red link cutout must be installed to BS7671 and will generally be a SWA (steel wired armoured) cable to provide additional protection.

Equipment Demarcation Zones and Ownership

Appendix 1/2 provides information on equipment demarcation zones and ownership. This diagram highlights who is responsible for maintaining the different types of equipment within the installation.

Equipment SHALL be maintained in good working order for continued use by the relevant owner of the equipment.

The supplier may de energise equipment that is deemed to be in an unsafe condition.

Any amendments to the customers consumer unit will be done by the customers electrician.

Appendix 1

Appendix 2